## Pivot Equ - BY SAIDI
Operating Unit Abbreviation | AEP-KYP
Major Cause Name | (All)
Minor Cause Code | EQF
Sum of SAIDI | Column Labels
Row Labels | 2020 | 2021 | 2022 | 2023 | 2024
ARRESTER | 12.878 | 5.0756 | 0.23809 | 4.6012 | 4.2012
BREAKER | 0.034893 |  | 6.6145 |  | 0.54184
CABLE TERMINATOR |  | 0.0027801 | 0.095533 | 0.0017446 | 0.00058169
CAPACITOR |  | 0.084648
CIRCUIT SWITCHER | 0.85273 | 0.00034752
CONDUCTOR OVERHEAD | 15.82 | 3.7975 | 9.6631 | 3.2558 | 5.0434
CONDUCTOR UG | 0.27044 | 0.72612 | 2.2038 | 0.38197 | 0.46008
CONN/CLAMP | 3.9464 | 5.6423 | 6.8611 | 2.6873 | 6.7711
CROSSARM | 5.2342 | 4.6554 | 7.9775 | 5.8865 | 3.2329
CUTOUT | 10.7191 | 13.964 | 11.4124 | 10.4459 | 13.2392
FUSE | 0.9629 | 0.59621 | 0.92397 | 0.60049 | 0.95933
GUY/ANCHOR | 0.055574 | 0.0095354 | 0.0065425 | 0.020385 | 0.85389
INSULATOR | 12.1645 | 8.7221 | 28.3943 | 8.1512 | 12.3679
JUMPER/RISER | 1.8164 | 0.42502 | 5.0535 | 0.84558 | 0.81374
METERING | 0.070216 | 0.0033837 | 0.034292 | 0.0064896 | 0.32272
MOAB | 0.0088989
OTHER EQUIPMENT | 0.2462 | 0.12053 | 1.116 | 0.20616 | 2.6111
PEDESTAL |  |  | 0.00061104 | 0.0013363
POLE | 6.2097 | 8.7955 | 12.434 | 3.1475 | 2.0365
POLE HARDWARE | 1.791 | 0.33426 | 0.26385 | 0.0038975 | 0.41447
RECLOSER, LINE/OCR/BR | 2.0631 | 0.82311 | 4.476 |  | 4.0274
REGULATOR | 1.3235 | 0.40336 | 1.3903 | 2.9633 | 0.63516
RELAY | 3.9028
SECTIONALIZER |  |  | 0.51044
SPLICE, OH | 0.58365 | 0.39085 | 6.7386 | 0.28212 | 0.66392
SPLICE, UG | 0.038461 |  |  | 0.0082157 | 0.0032364
STATIC WIRE | 0.20068 |  | 0.023757
SWITCH, OH | 1.1224 | 2.275 | 0.1936 | 1.1852 | 0.51524
TRANSFORMER, GROUNDING |  | 0.0028167 |  | 0.0066072 | 0.010972
TRANSFORMER, OH | 2.4485 | 1.8005 | 2.2573 | 1.4914 | 2.3943
TRANSFORMER, POWER - LTC |  | 3.9091 | 0.0029873 |  | 0.0076114
TRANSFORMER, STATION SERVICE | 2.1978 | 9.163 |  | 1.4017
TRANSFORMER, UG | 0.12209 | 0.23653 | 0.020763 | 0.023533 | 0.029357
Grand Total | 87.0841 | 71.9596 | 108.9066 | 47.6055 | 62.1571

## OPUNIT SUMMARY
Operating Unit Abbreviation | Year | Customer Counts Operating Unit | Number of Interruptions | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-AP | 2025 | 1058812 | 14204 | 656565 | 159020834 | 150.188 | 0.6201 | 242.2012
AEP-AP | 2024 | 1058812 | 46288 | 1983136 | 445483276 | 420.7388 | 1.873 | 224.6358
AEP-AP | 2023 | 1056376 | 43525 | 1699752 | 403305050 | 381.7817 | 1.609 | 237.2729
AEP-AP | 2021 | 1054192 | 42724 | 1763043 | 455450593 | 432.0376 | 1.6724 | 258.3321
AEP-AP | 2020 | 1051986 | 41300 | 1902474 | 436107305 | 414.5562 | 1.8085 | 229.2317
AEP-AP | 2022 | 1054752 | 50061 | 2145786 | 593569097 | 562.757 | 2.0344 | 276.6208
AEP-I&M | 2022 | 606813 | 15937 | 513651 | 88317934 | 145.5439 | 0.84647 | 171.9415
AEP-I&M | 2023 | 609949 | 15351 | 496775 | 74513535 | 122.1635 | 0.81445 | 149.9945
AEP-I&M | 2020 | 599151 | 13671 | 580214 | 102974352 | 171.8671 | 0.96839 | 177.4765
AEP-I&M | 2025 | 614045 | 5810 | 164740 | 20822323 | 33.9101 | 0.26829 | 126.3951
AEP-I&M | 2024 | 614045 | 19760 | 538675 | 74277318 | 120.964 | 0.87726 | 137.8889
AEP-I&M | 2021 | 603608 | 14103 | 578050 | 110959478 | 183.8271 | 0.95766 | 191.9548
AEP-KYP | 2023 | 161642 | 8755 | 298663 | 53625916 | 331.7573 | 1.8477 | 179.5533
AEP-KYP | 2025 | 161599 | 2923 | 120768 | 23637125 | 146.2702 | 0.74733 | 195.7234
AEP-KYP | 2024 | 161599 | 9537 | 350744 | 65584414 | 405.8467 | 2.1705 | 186.9866
AEP-KYP | 2020 | 165077 | 9165 | 331826 | 65600673 | 397.3944 | 2.0101 | 197.696
AEP-KYP | 2021 | 164021 | 8435 | 303745 | 65956314 | 402.1212 | 1.8519 | 217.1437
AEP-KYP | 2022 | 162018 | 9704 | 370882 | 79488727 | 490.6166 | 2.2891 | 214.3235
AEP-OH | 2022 | 1518267 | 36993 | 1667862 | 241297717 | 158.9297 | 1.0985 | 144.6749
AEP-OH | 2023 | 1524255 | 33435 | 1320985 | 199550801 | 130.9169 | 0.86664 | 151.0621
AEP-OH | 2025 | 1535393 | 11166 | 478639 | 76343575 | 49.7225 | 0.31174 | 159.5014
AEP-OH | 2020 | 1499447 | 36366 | 1691242 | 223538024 | 149.0803 | 1.1279 | 132.1739
AEP-OH | 2024 | 1535393 | 34618 | 1394917 | 221014181 | 143.9463 | 0.90851 | 158.4425
AEP-OH | 2021 | 1509795 | 38663 | 1760418 | 232604558 | 154.0637 | 1.166 | 132.1303
AEP-PSO | 2025 | 579031 | 4722 | 197313 | 20272526 | 35.0111 | 0.34076 | 102.743
AEP-PSO | 2022 | 570502 | 16528 | 705277 | 61099585 | 107.0979 | 1.2362 | 86.632
AEP-PSO | 2021 | 565565 | 14954 | 631311 | 63535693 | 112.3402 | 1.1162 | 100.6409
AEP-PSO | 2020 | 559804 | 14899 | 554599 | 50607447 | 90.4021 | 0.9907 | 91.2505
AEP-PSO | 2023 | 572956 | 15531 | 650014 | 79343738 | 138.4814 | 1.1345 | 122.0647
AEP-PSO | 2024 | 579031 | 17842 | 754357 | 73095527 | 126.2377 | 1.3028 | 96.8978
AEP-SEP | 2023 | 551114 | 17510 | 696798 | 100930114 | 183.1384 | 1.2643 | 144.8485
AEP-SEP | 2021 | 546634 | 14237 | 651606 | 88060072 | 161.0951 | 1.192 | 135.1431
AEP-SEP | 2022 | 550071 | 16774 | 726518 | 112903499 | 205.2526 | 1.3208 | 155.4036
AEP-SEP | 2025 | 554297 | 4672 | 244458 | 28731023 | 51.8333 | 0.44102 | 117.5295
AEP-SEP | 2024 | 554297 | 17402 | 682318 | 91707580 | 165.4485 | 1.231 | 134.4059
AEP-SEP | 2020 | 543859 | 15233 | 653453 | 94635008 | 174.0065 | 1.2015 | 144.823
AEP-TX | 2021 | 1079632 | 36017 | 1345928 | 159480578 | 147.7175 | 1.2467 | 118.4912
AEP-TX | 2024 | 1112283 | 34166 | 1378687 | 154370891 | 138.7874 | 1.2395 | 111.9695
AEP-TX | 2022 | 1090914 | 34599 | 1371690 | 152887350 | 140.1461 | 1.2574 | 111.4591
AEP-TX | 2023 | 1099391 | 33685 | 1364980 | 161763422 | 147.1391 | 1.2416 | 118.5097
AEP-TX | 2020 | 1064875 | 34909 | 1321901 | 155456654 | 145.9858 | 1.2414 | 117.6008
AEP-TX | 2025 | 1112283 | 10074 | 376483 | 38440172 | 34.5597 | 0.33848 | 102.1033
AEP Total | 2023 | 5575683 | 43525 | 1699752 | 403305050 | 72.3329 | 0.30485 | 237.2729
AEP Total | 2022 | 5553337 | 50061 | 2145786 | 593569097 | 106.8851 | 0.3864 | 276.6208
AEP Total | 2024 | 5615460 | 46288 | 1983136 | 445483276 | 79.3316 | 0.35316 | 224.6358
AEP Total | 2020 | 5484199 | 41300 | 1902474 | 436107305 | 79.5207 | 0.3469 | 229.2317
AEP Total | 2021 | 5523447 | 42724 | 1763043 | 455450593 | 82.4577 | 0.31919 | 258.3321
AEP Total | 2025 | 5615460 | 14204 | 656565 | 159020834 | 28.3184 | 0.11692 | 242.2012
AEP Total | 2020 | 5484199 | 13671 | 580214 | 102974352 | 18.7766 | 0.1058 | 177.4765
AEP Total | 2022 | 5553337 | 15937 | 513651 | 88317934 | 15.9036 | 0.092494 | 171.9415
AEP Total | 2023 | 5575683 | 15351 | 496775 | 74513535 | 13.364 | 0.089097 | 149.9945
AEP Total | 2021 | 5523447 | 14103 | 578050 | 110959478 | 20.0888 | 0.10465 | 191.9548
AEP Total | 2024 | 5615460 | 19760 | 538675 | 74277318 | 13.2273 | 0.095927 | 137.8889
AEP Total | 2025 | 5615460 | 5810 | 164740 | 20822323 | 3.708 | 0.029337 | 126.3951
AEP Total | 2021 | 5523447 | 8435 | 303745 | 65956314 | 11.9412 | 0.054992 | 217.1437
AEP Total | 2023 | 5575683 | 8755 | 298663 | 53625916 | 9.6178 | 0.053565 | 179.5533
AEP Total | 2024 | 5615460 | 9537 | 350744 | 65584414 | 11.6793 | 0.06246 | 186.9866
AEP Total | 2025 | 5615460 | 2923 | 120768 | 23637125 | 4.2093 | 0.021506 | 195.7234
AEP Total | 2022 | 5553337 | 9704 | 370882 | 79488727 | 14.3137 | 0.066785 | 214.3235
AEP Total | 2020 | 5484199 | 9165 | 331826 | 65600673 | 11.9618 | 0.060506 | 197.696
AEP Total | 2022 | 5553337 | 36993 | 1667862 | 241297717 | 43.4509 | 0.30034 | 144.6749
AEP Total | 2024 | 5615460 | 34618 | 1394917 | 221014181 | 39.3582 | 0.24841 | 158.4425
AEP Total | 2020 | 5484199 | 36366 | 1691242 | 223538024 | 40.7604 | 0.30838 | 132.1739
AEP Total | 2021 | 5523447 | 38663 | 1760418 | 232604558 | 42.1122 | 0.31872 | 132.1303
AEP Total | 2025 | 5615460 | 11166 | 478639 | 76343575 | 13.5952 | 0.085236 | 159.5014
AEP Total | 2023 | 5575683 | 33435 | 1320985 | 199550801 | 35.7895 | 0.23692 | 151.0621
AEP Total | 2020 | 5484199 | 14899 | 554599 | 50607447 | 9.2279 | 0.10113 | 91.2505
AEP Total | 2024 | 5615460 | 17842 | 754357 | 73095527 | 13.0168 | 0.13434 | 96.8978
AEP Total | 2021 | 5523447 | 14954 | 631311 | 63535693 | 11.5029 | 0.1143 | 100.6409
AEP Total | 2025 | 5615460 | 4722 | 197313 | 20272526 | 3.6101 | 0.035137 | 102.743
AEP Total | 2023 | 5575683 | 15531 | 650014 | 79343738 | 14.2303 | 0.11658 | 122.0647
AEP Total | 2022 | 5553337 | 16528 | 705277 | 61099585 | 11.0023 | 0.127 | 86.632
AEP Total | 2024 | 5615460 | 17402 | 682318 | 91707580 | 16.3313 | 0.12151 | 134.4059
AEP Total | 2020 | 5484199 | 15233 | 653453 | 94635008 | 17.2559 | 0.11915 | 144.823
AEP Total | 2023 | 5575683 | 17510 | 696798 | 100930114 | 18.1018 | 0.12497 | 144.8485
AEP Total | 2021 | 5523447 | 14237 | 651606 | 88060072 | 15.943 | 0.11797 | 135.1431
AEP Total | 2022 | 5553337 | 16774 | 726518 | 112903499 | 20.3307 | 0.13083 | 155.4036
AEP Total | 2025 | 5615460 | 4672 | 244458 | 28731023 | 5.1164 | 0.043533 | 117.5295
AEP Total | 2023 | 5575683 | 33685 | 1364980 | 161763422 | 29.0123 | 0.24481 | 118.5097
AEP Total | 2024 | 5615460 | 34166 | 1378687 | 154370891 | 27.4903 | 0.24552 | 111.9695
AEP Total | 2022 | 5553337 | 34599 | 1371690 | 152887350 | 27.5307 | 0.247 | 111.4591
AEP Total | 2020 | 5484199 | 34909 | 1321901 | 155456654 | 28.3463 | 0.24104 | 117.6008
AEP Total | 2021 | 5523447 | 36017 | 1345928 | 159480578 | 28.8734 | 0.24368 | 118.4912
AEP Total | 2025 | 5615460 | 10074 | 376483 | 38440172 | 6.8454 | 0.067044 | 102.1033

## 2020-2025 OPUNIT WITH MCC&CC
Operating Unit Abbreviation | Year | Customer Counts Operating Unit | Major Cause Name | Minor Cause Code | Equipment Name | Number of Interruptions | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 18 | 8552 | 0.0081124 | 1.7075e-05 | 475.1111
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | FUSE | 287 | 2439 | 632060 | 0.59833 | 0.0023088 | 259.1472
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | V | CUTOUT | 1 | 1 | 1000 | 0.00094809 | 9.4809e-07 | 1000
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 29 | 2348 | 0.0022261 | 2.7495e-05 | 80.9655
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 1 | 101 | 9.5808e-05 | 9.4859e-07 | 101
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | PEDESTAL | 7 | 16 | 2045 | 0.0019388 | 1.5169e-05 | 127.8125
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FW | ARRESTER | 2 | 39 | 510 | 0.00048378 | 3.6995e-05 | 13.0769
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | WFS | NONE | 1 | 145 | 164399 | 0.15563 | 0.00013726 | 1133.7862
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | NONE | 218 | 16680 | 4972150 | 4.7068 | 0.01579 | 298.0905
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | NONE | 858 | 20406 | 3224003 | 3.0449 | 0.019273 | 157.9929
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 20 | 13808 | 3665500 | 3.4699 | 0.013071 | 265.4621
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | NONE | 1920 | 65504 | 14656799 | 13.8427 | 0.061866 | 223.7543
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | FUSE | 950 | 4954 | 545083 | 0.51481 | 0.0046788 | 110.0289
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 15 | 547 | 443784 | 0.4201 | 0.00051781 | 811.3053
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | NONE | 28 | 2384 | 721857 | 0.68333 | 0.0022568 | 302.7924
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | CONDUCTOR UG | 95 | 130 | 58904 | 0.055632 | 0.00012278 | 453.1077
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 1 | 582 | 0.00055094 | 9.4663e-07 | 582
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | WL | NONE | 2 | 242 | 45880 | 0.043432 | 0.00022909 | 189.5868
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 6 | 1278 | 0.0012098 | 5.6798e-06 | 213
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 159 | 215127 | 0.20407 | 0.00015083 | 1353
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FW | POLE | 1 | 19 | 2774 | 0.0026314 | 1.8023e-05 | 146
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | CUTOUT | 23 | 266 | 93110 | 0.087938 | 0.00025122 | 350.0376
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CE | CONDUCTOR UG | 1 | 2 | 356 | 0.00033752 | 1.8962e-06 | 178
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 8 | 54 | 15913 | 0.015127 | 5.1331e-05 | 294.6852
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 1 | 158 | 0.00015019 | 9.5058e-07 | 158
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 6 | 16 | 3862 | 0.0036559 | 1.5146e-05 | 241.375
AEP-AP | 2023 | 1056376 | PARTIAL POWER | WL | NONE | 3 | 6 | 411 | 0.00038907 | 5.6798e-06 | 68.5
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | CONDUCTOR OVERHEAD | 2 | 377 | 57967 | 0.054873 | 0.00035688 | 153.7586
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | STATIC WIRE | 1 | 181 | 170502 | 0.16165 | 0.0001716 | 942
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 3 | 311 | 0.00029563 | 2.8517e-06 | 103.6667
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 18 | 665 | 253807 | 0.23971 | 0.00062806 | 381.6647
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | AB | INSULATOR | 1 | 65 | 11460 | 0.010823 | 6.139e-05 | 176.3077
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | NONE | 342 | 14311 | 4289186 | 4.0509 | 0.013516 | 299.7125
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | NONE | 316 | 7771 | 940917 | 0.88865 | 0.0073394 | 121.0806
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | POLE | 171 | 9353 | 2360110 | 2.229 | 0.0088335 | 252.3372
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | SCO | NONE | 3 | 2511 | 277046 | 0.26166 | 0.0023715 | 110.3329
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | INSULATOR | 3 | 1166 | 126316 | 0.1193 | 0.0011012 | 108.3328
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | CONN/CLAMP | 5 | 685 | 177384 | 0.16753 | 0.00064695 | 258.9547
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | METERING | 2 | 2 | 356 | 0.00033623 | 1.8889e-06 | 178
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 38 | 3790 | 0.0035795 | 3.5889e-05 | 99.7368
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 2 | 270 | 0.000255 | 1.8889e-06 | 135
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 4 | 716 | 319801 | 0.30204 | 0.00067623 | 446.6494
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | EQF | SPLICE, OH | 2 | 338 | 340028 | 0.32322 | 0.0003213 | 1006
AEP-AP | 2025 | 1058812 | PARTIAL POWER | CE | NONE | 1 | 3 | 501 | 0.00047317 | 2.8334e-06 | 167
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 230 | 0.00021863 | 1.9012e-06 | 115
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OU | CUTOUT | 2 | 69 | 4661 | 0.0044021 | 6.5167e-05 | 67.5507
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 4 | 5 | 1302 | 0.0012377 | 4.7529e-06 | 260.4
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | O | ARRESTER | 1 | 10 | 2060 | 0.0019501 | 9.4663e-06 | 206
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | WU | NONE | 28 | 18639 | 3293862 | 3.1109 | 0.017604 | 176.7188
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 5 | 3575 | 0.0033912 | 4.743e-06 | 715
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 1 | 5 | 265 | 0.00025124 | 4.7405e-06 | 53
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 1 | 50 | 52112 | 0.049433 | 4.743e-05 | 1042.24
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | WU | NONE | 1 | 1 | 94 | 8.8983e-05 | 9.4663e-07 | 94
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | TOR | POLE HARDWARE | 2 | 2201 | 656092 | 0.62203 | 0.0020867 | 298.0881
AEP-AP | 2021 | 1054192 | SUBTRANSMISSION LINE | SO | NONE | 2 | 809 | 4854 | 0.0046045 | 0.00076741 | 6
AEP-AP | 2022 | 1054752 | DISTRIBUTION SOURCE | TOR | CROSSARM | 1 | 1 | 486 | 0.00046077 | 9.4809e-07 | 486
AEP-AP | 2020 | 1051986 | DISTRIBUTION SOURCE | EQF | INSULATOR | 3 | 2007 | 374551 | 0.35604 | 0.0019078 | 186.6223
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | WW | STATIC WIRE | 1 | 1865 | 85790 | 0.081212 | 0.0017655 | 46
AEP-AP | 2025 | 1058812 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 1 | 596 | 333965 | 0.31541 | 0.0005629 | 560.344
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | F | NONE | 4 | 488 | 10697 | 0.010103 | 0.00046089 | 21.9201
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | INSULATOR | 1 | 12 | 14786 | 0.013965 | 1.1333e-05 | 1232.1667
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 490 | 136102 | 0.12854 | 0.00046278 | 277.7592
AEP-AP | 2024 | 1058812 | PARTIAL POWER | UG | SPLICE, UG | 1 | 1 | 137 | 0.00012939 | 9.4445e-07 | 137
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CE | NONE | 34 | 649 | 86915 | 0.082403 | 0.00061531 | 133.9214
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | V | METERING | 15 | 31 | 3033 | 0.0028756 | 2.9391e-05 | 97.8387
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | CROSSARM | 193 | 76031 | 9836573 | 9.326 | 0.072084 | 129.3758
AEP-AP | 2022 | 1054752 | PARTIAL POWER | A | NONE | 20 | 126 | 9517 | 0.009023 | 0.00011946 | 75.5317
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | O | NONE | 92 | 1398 | 562736 | 0.53381 | 0.0013261 | 402.5293
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | NONE | 210 | 7990 | 6868650 | 6.5121 | 0.0075752 | 859.6558
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | ARRESTER | 8 | 2124 | 323629 | 0.30764 | 0.002019 | 152.3677
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | OL | NONE | 44 | 2771 | 830664 | 0.78796 | 0.0026286 | 299.7705
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | POLE HARDWARE | 1 | 1 | 372 | 0.00035269 | 9.4809e-07 | 372
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OL | FUSE | 27 | 1289 | 322294 | 0.30556 | 0.0012221 | 250.0341
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | FUSE | 847 | 5036 | 642079 | 0.60781 | 0.0047672 | 127.4978
AEP-AP | 2023 | 1056376 | PARTIAL POWER | CO | CONN/CLAMP | 3 | 6 | 6092 | 0.0057669 | 5.6798e-06 | 1015.3333
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | FUSE | 4 | 11 | 1367 | 0.0012967 | 1.0435e-05 | 124.2727
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 11 | 235 | 0.0002228 | 1.0429e-05 | 21.3636
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | REGULATOR | 10 | 2938 | 267630 | 0.25374 | 0.0027855 | 91.0926
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | AO | OTHER EQUIPMENT | 3 | 3432 | 372374 | 0.35304 | 0.0032538 | 108.5006
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | FUSE | 72 | 552 | 77280 | 0.073156 | 0.00052254 | 140
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | SWITCH, OH | 6 | 568 | 97511 | 0.092449 | 0.00053852 | 171.6743
AEP-AP | 2020 | 1051986 | SUBTRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 1 | 12 | 2196 | 0.0020875 | 1.1407e-05 | 183
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | V | NONE | 3 | 3522 | 210404 | 0.19959 | 0.0033409 | 59.7399
AEP-AP | 2020 | 1051986 | PARTIAL POWER | WL | NONE | 11 | 67 | 11685 | 0.011108 | 6.3689e-05 | 174.403
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | EQF | POLE | 3 | 2304 | 397950 | 0.37671 | 0.002181 | 172.7214
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 6 | 251 | 28609 | 0.027082 | 0.0002376 | 113.9801
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VIN | ARRESTER | 8 | 34 | 8998 | 0.0085533 | 3.232e-05 | 264.6471
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | ARRESTER | 15 | 713 | 166888 | 0.15798 | 0.00067495 | 234.0645
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WL | NONE | 5 | 23 | 6560 | 0.0062228 | 2.1818e-05 | 285.2174
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 84 | 1988 | 654345 | 0.618 | 0.0018776 | 329.1474
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | INSULATOR | 2 | 156 | 39012 | 0.03693 | 0.00014767 | 250.0769
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | CROSSARM | 1 | 4 | 776 | 0.0007329 | 3.7778e-06 | 194
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | O | NONE | 5 | 1544 | 126481 | 0.11973 | 0.0014616 | 81.9177
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 2 | 751 | 0.00071239 | 1.8972e-06 | 375.5
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 18 | 1351 | 349619 | 0.3302 | 0.001276 | 258.7853
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | CUTOUT | 1017 | 42894 | 6570215 | 6.2053 | 0.040511 | 153.1733
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | POLE | 943 | 6832 | 1092116 | 1.0315 | 0.0064525 | 159.853
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 2 | 138 | 181826 | 0.17212 | 0.00013064 | 1317.5797
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | INSULATOR | 4 | 88 | 13553 | 0.012849 | 8.3432e-05 | 154.0114
AEP-AP | 2022 | 1054752 | PARTIAL POWER | OU | NONE | 1 | 1 | 38 | 3.6027e-05 | 9.4809e-07 | 38
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | POLE | 2 | 60 | 6585 | 0.0062596 | 5.7035e-05 | 109.75
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | EQF | ARRESTER | 7 | 5803 | 3555508 | 3.358 | 0.0054807 | 612.7017
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERO | NONE | 5 | 7 | 509 | 0.00048073 | 6.6112e-06 | 72.7143
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 6 | 131 | 38650 | 0.036503 | 0.00012372 | 295.0382
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | SWITCH, OH | 3 | 2978 | 177190 | 0.16799 | 0.0028234 | 59.4997
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 3 | 26 | 4064 | 0.003853 | 2.465e-05 | 156.3077
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | CE | OTHER EQUIPMENT | 1 | 441 | 98435 | 0.093325 | 0.00041811 | 223.2086
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WI | CONN/CLAMP | 2 | 3 | 320 | 0.00030355 | 2.8458e-06 | 106.6667
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 3 | 201 | 31394 | 0.029719 | 0.00019027 | 156.1891
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | CUTOUT | 7 | 505 | 77246 | 0.072955 | 0.00047695 | 152.9624
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | CONN/CLAMP | 5 | 435 | 74566 | 0.070424 | 0.00041084 | 171.4161
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 5 | 17 | 3123 | 0.0029495 | 1.6056e-05 | 183.7059
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 24 | 666 | 341095 | 0.32215 | 0.00062901 | 512.1547
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 6 | 212 | 0.00020022 | 5.6667e-06 | 35.3333
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 1 | 2 | 202 | 0.00019078 | 1.8889e-06 | 101
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | EQF | CROSSARM | 8 | 3546 | 329537 | 0.31123 | 0.003349 | 92.932
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 8 | 1964 | 0.0018549 | 7.5556e-06 | 245.5
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | WL | INSULATOR | 1 | 1 | 645 | 0.00061313 | 9.5058e-07 | 645
AEP-AP | 2024 | 1058812 | PARTIAL POWER | ERF | NONE | 2 | 2 | 560 | 0.00052889 | 1.8889e-06 | 280
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | EQF | ARRESTER | 4 | 2260 | 399800 | 0.37925 | 0.0021438 | 176.9027
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 124 | 13020 | 0.012351 | 0.00011763 | 105
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | CIRCUIT SWITCHER | 1 | 1 | 35 | 3.327e-05 | 9.5058e-07 | 35
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CE | ARRESTER | 1 | 2 | 290 | 0.00027509 | 1.8972e-06 | 145
AEP-AP | 2025 | 1058812 | TRANSMISSION STATION | V | NONE | 2 | 696 | 34158 | 0.032261 | 0.00065734 | 49.0776
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | CROSSARM | 1 | 840 | 180240 | 0.17133 | 0.00079849 | 214.5714
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WFS | GUY/ANCHOR | 1 | 132 | 88308 | 0.083724 | 0.00012515 | 669
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | WL | SWITCH, OH | 2 | 638 | 553784 | 0.52532 | 0.0006052 | 868
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 79 | 30336 | 0.028761 | 7.4899e-05 | 384
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | RELAY | 1 | 1305 | 129195 | 0.1223 | 0.0012354 | 99
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | SWITCH, OH | 1 | 29 | 2407 | 0.0022785 | 2.7452e-05 | 83
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 9 | 531 | 0.00050151 | 8.5001e-06 | 59
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | TIR | NONE | 2 | 190 | 31644 | 0.029886 | 0.00017945 | 166.5474
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 225 | 0.0002125 | 9.4445e-07 | 225
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CE | SPLICE, OH | 1 | 1 | 354 | 0.00033434 | 9.4445e-07 | 354
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 11 | 5291 | 0.0049971 | 1.0389e-05 | 481
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | METERING | 1 | 6 | 552 | 0.00052472 | 5.7035e-06 | 92
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | ARRESTER | 307 | 13643 | 2126301 | 2.0159 | 0.012935 | 155.8529
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | FUSE | 1087 | 7090 | 1198440 | 1.1368 | 0.0067255 | 169.0324
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | FUSE | 187 | 815 | 197951 | 0.18768 | 0.00077269 | 242.8847
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | NONE | 2885 | 22667 | 2817468 | 2.6712 | 0.02149 | 124.2982
AEP-AP | 2020 | 1051986 | PARTIAL POWER | ABI | NONE | 25 | 61 | 5424 | 0.005156 | 5.7986e-05 | 88.918
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 4 | 28 | 5308 | 0.0050351 | 2.6561e-05 | 189.5714
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | NONE | 2882 | 35645 | 4311746 | 4.0987 | 0.033884 | 120.9636
AEP-AP | 2022 | 1054752 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 3 | 312 | 0.0002958 | 2.8443e-06 | 104
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 73 | 13613 | 0.012913 | 6.9247e-05 | 186.4795
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | NONE | 9 | 33 | 14500 | 0.013747 | 3.1287e-05 | 439.3939
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 25 | 1201 | 164741 | 0.15627 | 0.0011393 | 137.1699
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | ARRESTER | 41 | 1580 | 354091 | 0.33589 | 0.0014988 | 224.1082
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 21 | 254 | 51010 | 0.048362 | 0.00024081 | 200.8268
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 5 | 4588 | 747487 | 0.70869 | 0.0043498 | 162.9222
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | CONDUCTOR UG | 67 | 188 | 88783 | 0.084174 | 0.00017824 | 472.25
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WI | NONE | 70 | 1335 | 495003 | 0.47054 | 0.001269 | 370.7888
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 1 | 1 | 60 | 5.6916e-05 | 9.4859e-07 | 60
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TR | POLE | 11 | 1235 | 545551 | 0.51859 | 0.001174 | 441.7417
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 7 | 1117 | 135646 | 0.1286 | 0.001059 | 121.4378
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 25 | 1096 | 788269 | 0.74775 | 0.0010397 | 719.2235
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | POLE HARDWARE | 5 | 2017 | 260089 | 0.24659 | 0.0019123 | 128.9484
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 25 | 252 | 45089 | 0.042748 | 0.00023892 | 178.9246
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | CUTOUT | 4 | 28 | 6822 | 0.0064679 | 2.6547e-05 | 243.6429
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 127 | 53120 | 0.050363 | 0.00012041 | 418.2677
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | ARRESTER | 17 | 3727 | 547295 | 0.51889 | 0.0035335 | 146.846
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 3 | 162 | 28462 | 0.026985 | 0.00015359 | 175.6914
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 116 | 4251 | 2731942 | 2.5901 | 0.0040303 | 642.6587
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | F | NONE | 77 | 879 | 123541 | 0.11713 | 0.00083337 | 140.5472
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 145 | 156802 | 0.14874 | 0.00013755 | 1081.3931
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | UG | NONE | 84 | 1673 | 303368 | 0.28838 | 0.0015903 | 181.3317
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | NONE | 35 | 149 | 15453 | 0.014659 | 0.00014134 | 103.7114
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | METERING | 2 | 65 | 10140 | 0.0096136 | 6.1626e-05 | 156
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | SPLICE, OH | 74 | 3033 | 552293 | 0.5239 | 0.0028771 | 182.0946
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | POLE | 4 | 41 | 9686 | 0.0091881 | 3.8892e-05 | 236.2439
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 137 | 21149 | 0.020051 | 0.00012989 | 154.3723
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 13 | 1419 | 585337 | 0.55495 | 0.0013453 | 412.4996
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SO | NONE | 12 | 1945 | 163787 | 0.15528 | 0.001844 | 84.2093
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | POLE | 10 | 575 | 262376 | 0.24889 | 0.00054544 | 456.3061
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 7 | 52 | 32037 | 0.030374 | 4.9301e-05 | 616.0962
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ABI | FUSE | 63 | 233 | 30119 | 0.028571 | 0.00022102 | 129.2661
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ABI | NONE | 693 | 6775 | 1112716 | 1.055 | 0.0064233 | 164.2385
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | POLE | 374 | 98238 | 22515430 | 21.3467 | 0.093138 | 229.1927
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | FUSE | 29 | 391 | 43509 | 0.04125 | 0.0003707 | 111.2762
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | NONE | 1164 | 8210 | 1384016 | 1.3129 | 0.007788 | 168.5769
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | ARRESTER | 7 | 25 | 4081 | 0.0038692 | 2.3702e-05 | 163.24
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 36 | 22325 | 0.021177 | 3.4149e-05 | 620.1389
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | ARRESTER | 3 | 37 | 38632 | 0.036646 | 3.5098e-05 | 1044.1081
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | CUTOUT | 8 | 121 | 119685 | 0.11353 | 0.00011478 | 989.1322
AEP-AP | 2021 | 1054192 | TRANSMISSION STATION | U | NONE | 4 | 2627 | 310743 | 0.29477 | 0.002492 | 118.2882
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | CONN/CLAMP | 29 | 263 | 38141 | 0.036256 | 0.00025 | 145.0228
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 944 | 8343 | 2102349 | 1.9985 | 0.0079307 | 251.9896
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | CUTOUT | 2712 | 122834 | 20078324 | 19.0861 | 0.11676 | 163.459
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OU | POLE | 2 | 462 | 25135 | 0.02383 | 0.00043802 | 54.4048
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 16 | 3339 | 218360 | 0.20702 | 0.0031657 | 65.3968
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | FUSE | 141 | 2055 | 597159 | 0.56616 | 0.0019483 | 290.5883
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | CUTOUT | 2701 | 84440 | 14170323 | 13.4141 | 0.079934 | 167.8153
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | ARRESTER | 8 | 225 | 87010 | 0.08271 | 0.00021388 | 386.7111
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 2610 | 322215 | 0.30549 | 0.0024745 | 123.454
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 8 | 19 | 1451 | 0.0013793 | 1.8061e-05 | 76.3684
AEP-AP | 2023 | 1056376 | PARTIAL POWER | WL | ARRESTER | 1 | 4 | 404 | 0.00038244 | 3.7865e-06 | 101
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CO | SPLICE, OH | 3 | 15 | 4527 | 0.004292 | 1.4221e-05 | 301.8
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | NONE | 2410 | 14343 | 1602639 | 1.5136 | 0.013546 | 111.7367
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | NONE | 5 | 15 | 3876 | 0.0036691 | 1.4199e-05 | 258.4
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VIN | CUTOUT | 6 | 19 | 2408 | 0.002289 | 1.8061e-05 | 126.7368
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | SWITCH, OH | 11 | 587 | 100228 | 0.094879 | 0.00055567 | 170.7462
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | TR | NONE | 4 | 88 | 42900 | 0.040611 | 8.3304e-05 | 487.5
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | AO | NONE | 3 | 850 | 229132 | 0.2169 | 0.00080464 | 269.5671
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 22 | 12870 | 0.012183 | 2.0826e-05 | 585
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 6 | 33 | 15528 | 0.014699 | 3.1239e-05 | 470.5455
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 28 | 60 | 38570 | 0.036428 | 5.6667e-05 | 642.8333
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 1964 | 548866 | 0.51957 | 0.0018592 | 279.4633
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 1 | 89 | 35511 | 0.033616 | 8.425e-05 | 399
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 14 | 240 | 35741 | 0.033756 | 0.00022667 | 148.9208
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 12 | 1224 | 619165 | 0.58477 | 0.001156 | 505.8538
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 1260 | 85225 | 0.081013 | 0.0011977 | 67.6389
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 6 | 1664 | 0.0015752 | 5.6798e-06 | 277.3333
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 17 | 796 | 289052 | 0.273 | 0.00075179 | 363.1307
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WL | ARRESTER | 9 | 110 | 35617 | 0.033639 | 0.00010389 | 323.7909
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | V | RECLOSER, LINE/OCR/BR | 1 | 44 | 24242 | 0.022996 | 4.1738e-05 | 550.9545
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | CROSSARM | 3 | 4119 | 959645 | 0.90843 | 0.0038992 | 232.9801
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 7 | 6552 | 0.0062023 | 6.6264e-06 | 936
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | REGULATOR | 12 | 1929 | 186361 | 0.17601 | 0.0018219 | 96.6102
AEP-AP | 2020 | 1051986 | PARTIAL POWER | WU | FUSE | 1 | 2 | 132 | 0.00012548 | 1.9012e-06 | 66
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | CONN/CLAMP | 7 | 33 | 3799 | 0.003588 | 3.1167e-05 | 115.1212
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | ARRESTER | 1 | 681 | 110322 | 0.10443 | 0.00064466 | 162
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FW | NONE | 8 | 97 | 59229 | 0.055939 | 9.1612e-05 | 610.6082
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | CUTOUT | 8 | 16 | 14448 | 0.013645 | 1.5111e-05 | 903
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WU | OTHER EQUIPMENT | 1 | 1 | 97 | 9.1612e-05 | 9.4445e-07 | 97
AEP-AP | 2021 | 1054192 | TRANSMISSION STATION | EQF | TRANSFORMER, GROUNDING | 1 | 196 | 49000 | 0.046481 | 0.00018592 | 250
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | WU | NONE | 1 | 1311 | 301530 | 0.28663 | 0.0012462 | 230
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 1 | 315 | 0.0002975 | 9.4445e-07 | 315
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | CUTOUT | 1 | 2 | 140 | 0.00013222 | 1.8889e-06 | 70
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 1 | 77 | 7.3195e-05 | 9.5058e-07 | 77
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 3 | 74 | 3443 | 0.0032518 | 6.989e-05 | 46.527
AEP-AP | 2020 | 1051986 | DISTRIBUTION SOURCE | A | NONE | 3 | 3108 | 342156 | 0.32525 | 0.0029544 | 110.0888
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | ERF | NONE | 3 | 3970 | 283716 | 0.26913 | 0.0037659 | 71.465
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CE | METERING | 1 | 3 | 33 | 3.1369e-05 | 2.8517e-06 | 11
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 1 | 993 | 0.00094001 | 9.4663e-07 | 993
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 4 | 4 | 353 | 0.00033339 | 3.7778e-06 | 88.25
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 3 | 239 | 0.00022572 | 2.8334e-06 | 79.6667
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 1 | 627 | 0.00059217 | 9.4445e-07 | 627
AEP-AP | 2025 | 1058812 | SUBTRANSMISSION LINE | WU | POLE | 1 | 90 | 66600 | 0.062901 | 8.5001e-05 | 740
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | OV | NONE | 1 | 993 | 84405 | 0.080066 | 0.00094195 | 85
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | V | REGULATOR | 1 | 512 | 198656 | 0.18844 | 0.00048568 | 388
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 2 | 418 | 0.00039651 | 1.8972e-06 | 209
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 48 | 2928 | 0.002776 | 4.5508e-05 | 61
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | POLE HARDWARE | 1 | 174 | 45868 | 0.043487 | 0.00016497 | 263.6092
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 3 | 42 | 7449 | 0.0070809 | 3.9924e-05 | 177.3571
AEP-AP | 2023 | 1056376 | PARTIAL POWER | CO | SPLICE, OH | 1 | 1 | 74 | 7.0051e-05 | 9.4663e-07 | 74
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 1 | 172 | 0.00016245 | 9.4445e-07 | 172
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | RECLOSER, LINE/OCR/BR | 1 | 2 | 98 | 9.2557e-05 | 1.8889e-06 | 49
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | SWITCH, OH | 2 | 446 | 39566 | 0.037368 | 0.00042123 | 88.713
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 2 | 2872 | 0.0027125 | 1.8889e-06 | 1436
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 37 | 3.4945e-05 | 9.4445e-07 | 37
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 777 | 9325 | 2727112 | 2.5855 | 0.0088409 | 292.4517
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 11 | 63 | 19809 | 0.018791 | 5.9761e-05 | 314.4286
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | CUTOUT | 6 | 167 | 210845 | 0.1999 | 0.00015833 | 1262.5449
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 28 | 8443 | 2359845 | 2.2385 | 0.008009 | 279.5031
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | CABLE TERMINATOR | 1 | 1 | 244 | 0.00023133 | 9.4809e-07 | 244
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 27 | 382 | 60091 | 0.057002 | 0.00036236 | 157.3063
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | FO | NONE | 50 | 5098 | 1020616 | 0.97018 | 0.0048461 | 200.1993
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 22 | 463 | 154848 | 0.1472 | 0.00044012 | 334.4449
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 101 | 13650 | 0.012922 | 9.561e-05 | 135.1485
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | CROSSARM | 166 | 40916 | 7263996 | 6.8763 | 0.038732 | 177.5344
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 6 | 72 | 98464 | 0.093353 | 6.8262e-05 | 1367.5556
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | CONN/CLAMP | 26 | 121 | 10365 | 0.0098118 | 0.00011454 | 85.6612
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | O | CUTOUT | 1 | 3 | 381 | 0.00036141 | 2.8458e-06 | 127
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 20 | 239 | 24239 | 0.023041 | 0.00022719 | 101.4184
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | NONE | 2821 | 182833 | 42877623 | 40.496 | 0.17268 | 234.518
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | FUSE | 57 | 603 | 55443 | 0.052363 | 0.00056951 | 91.9453
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WFS | POLE | 13 | 1125 | 728229 | 0.68778 | 0.0010625 | 647.3147
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 65 | 1041 | 368033 | 0.34759 | 0.00098318 | 353.5379
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | INSULATOR | 24 | 4398 | 614621 | 0.58048 | 0.0041537 | 139.7501
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 22 | 1893 | 982934 | 0.92834 | 0.0017879 | 519.2467
AEP-AP | 2021 | 1054192 | PARTIAL POWER | VIN | FUSE | 1 | 1 | 353 | 0.00033485 | 9.4859e-07 | 353
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OL | NONE | 15 | 4200 | 956607 | 0.90347 | 0.0039667 | 227.7636
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | SPLICE, OH | 1 | 12 | 287 | 0.00027106 | 1.1333e-05 | 23.9167
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FW | FUSE | 2 | 8 | 6204 | 0.0058594 | 7.5556e-06 | 775.5
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | SPLICE, OH | 2 | 46 | 9661 | 0.0091454 | 4.3545e-05 | 210.0217
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | METERING | 16 | 30 | 975 | 0.00092084 | 2.8334e-05 | 32.5
AEP-AP | 2023 | 1056376 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 12 | 3771 | 0.0035698 | 1.136e-05 | 314.25
AEP-AP | 2023 | 1056376 | PARTIAL POWER | WU | FUSE | 2 | 10 | 231 | 0.00021867 | 9.4663e-06 | 23.1
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | OU | FUSE | 2 | 10 | 643 | 0.00060995 | 9.4859e-06 | 64.3
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 81 | 7.6836e-05 | 9.4859e-07 | 81
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | TRANSFORMER, STATION SERVICE | 1 | 2 | 166 | 0.00015714 | 1.8933e-06 | 83
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 2 | 4 | 1012 | 0.00096199 | 3.8023e-06 | 253
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 1 | 243 | 0.00023003 | 9.4663e-07 | 243
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OL | FUSE | 8 | 341 | 48180 | 0.045504 | 0.00032206 | 141.2903
AEP-AP | 2024 | 1058812 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 12 | 916 | 0.00086512 | 1.1333e-05 | 76.3333
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WL | FUSE | 38 | 405 | 83420 | 0.078786 | 0.0003825 | 205.9753
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ABI | FUSE | 15 | 54 | 6441 | 0.0060832 | 5.1001e-05 | 119.2778
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WFS | NONE | 25 | 1613 | 2284313 | 2.1574 | 0.0015234 | 1416.1891
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 2 | 13 | 1579 | 0.0014947 | 1.2306e-05 | 121.4615
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | METERING | 3 | 6 | 974 | 0.0009199 | 5.6667e-06 | 162.3333
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TOR | CONN/CLAMP | 4 | 4 | 1379 | 0.0013024 | 3.7778e-06 | 344.75
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OU | FUSE | 3 | 15 | 2946 | 0.0027824 | 1.4167e-05 | 196.4
AEP-AP | 2020 | 1051986 | SUBTRANSMISSION LINE | TOR | NONE | 5 | 113 | 36846 | 0.035025 | 0.00010742 | 326.0708
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 1 | 3 | 576 | 0.0005461 | 2.8443e-06 | 192
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 1 | 258 | 0.00024474 | 9.4859e-07 | 258
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 3560 | 78320 | 0.07414 | 0.00337 | 22
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | POLE | 7 | 250 | 218700 | 0.20655 | 0.00023611 | 874.8
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | R | NONE | 18 | 14091 | 2557198 | 2.4152 | 0.013308 | 181.4774
AEP-AP | 2024 | 1058812 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 31 | 2.9278e-05 | 9.4445e-07 | 31
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WL | POLE | 1 | 1 | 3188 | 0.0030109 | 9.4445e-07 | 3188
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | NONE | 4 | 50 | 6191 | 0.0058471 | 4.7223e-05 | 123.82
AEP-AP | 2025 | 1058812 | PARTIAL POWER | A | FUSE | 2 | 3 | 215 | 0.00020306 | 2.8334e-06 | 71.6667
AEP-AP | 2024 | 1058812 | PARTIAL POWER | VA | NONE | 2 | 4 | 247 | 0.00023328 | 3.7778e-06 | 61.75
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | INSULATOR | 1 | 7 | 5866 | 0.0055402 | 6.6112e-06 | 838
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | CIRCUIT SWITCHER | 1 | 6 | 660 | 0.00062738 | 5.7035e-06 | 110
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | EQF | SWITCH, OH | 1 | 13 | 11284 | 0.010704 | 1.2332e-05 | 868
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 44 | 4356 | 0.004114 | 4.1556e-05 | 99
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 1 | 104 | 4264 | 0.0040272 | 9.8223e-05 | 41
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | RELAY | 1 | 750 | 94500 | 0.089251 | 0.00070834 | 126
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | PEDESTAL | 1 | 3 | 630 | 0.00059501 | 2.8334e-06 | 210
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 108 | 6926 | 2581727 | 2.4477 | 0.0065665 | 372.7587
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 16 | 1577 | 751050 | 0.71244 | 0.0014959 | 476.2524
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SO | CONN/CLAMP | 1 | 3 | 8832 | 0.0083735 | 2.8443e-06 | 2944
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 7 | 21 | 1948 | 0.0018469 | 1.991e-05 | 92.7619
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WFS | NONE | 41 | 5374 | 1810871 | 1.7214 | 0.0051084 | 336.9689
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | SPLICE, UG | 9 | 16 | 7592 | 0.0071979 | 1.5169e-05 | 474.5
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | FW | NONE | 51 | 2137 | 240301 | 0.22843 | 0.0020314 | 112.4478
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | INSULATOR | 2 | 635 | 34804 | 0.033015 | 0.00060236 | 54.8094
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 147 | 6973 | 1901981 | 1.808 | 0.0066284 | 272.7637
AEP-AP | 2021 | 1054192 | DISTRIBUTION SOURCE | V | NONE | 1 | 1433 | 230813 | 0.21895 | 0.0013593 | 161.0698
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 7 | 16219 | 0.015385 | 6.6402e-06 | 2317
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 2 | 648 | 0.00061469 | 1.8972e-06 | 324
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | JUMPER/RISER | 1 | 105 | 13755 | 0.013041 | 9.9549e-05 | 131
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | V | METERING | 3 | 3 | 388 | 0.00036883 | 2.8517e-06 | 129.3333
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | METERING | 8 | 8 | 858 | 0.00081221 | 7.5731e-06 | 107.25
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 9 | 113 | 18105 | 0.017139 | 0.00010697 | 160.2212
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CE | INSULATOR | 1 | 4 | 232 | 0.00021996 | 3.7924e-06 | 58
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 213 | 764 | 77508 | 0.073372 | 0.00072323 | 101.4503
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 3 | 5401 | 724700 | 0.68602 | 0.0051128 | 134.1789
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | CROSSARM | 12 | 2406 | 607419 | 0.57368 | 0.0022724 | 252.4601
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 534 | 539354 | 0.51163 | 0.00050655 | 1010.0262
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 4926 | 751440 | 0.71431 | 0.0046826 | 152.5457
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | ABX | NONE | 3 | 180 | 50221 | 0.047614 | 0.00017066 | 279.0056
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 1 | 264 | 0.00025043 | 9.4859e-07 | 264
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | POLE | 7 | 794 | 418180 | 0.39495 | 0.0007499 | 526.6751
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FO | NONE | 26 | 2991 | 517939 | 0.48917 | 0.0028249 | 173.1658
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | NONE | 62 | 5941 | 553833 | 0.52307 | 0.005611 | 93.2222
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 7 | 734 | 0.00069323 | 6.6112e-06 | 104.8571
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | O | NONE | 2 | 321 | 22256 | 0.021101 | 0.00030434 | 69.3333
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | CROSSARM | 2 | 100 | 25721 | 0.024386 | 9.4809e-05 | 257.21
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 8 | 150 | 22061 | 0.020884 | 0.00014199 | 147.0733
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 5 | 215 | 0.00020438 | 4.7529e-06 | 43
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | ARRESTER | 4 | 14 | 1783 | 0.0016949 | 1.3308e-05 | 127.3571
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | ARRESTER | 11 | 8291 | 1176232 | 1.1181 | 0.0078813 | 141.8685
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | SPLICE, OH | 2 | 2 | 387 | 0.00036635 | 1.8933e-06 | 193.5
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 2 | 3 | 311 | 0.00029486 | 2.8443e-06 | 103.6667
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | BREAKER | 3 | 1627 | 95430 | 0.090714 | 0.0015466 | 58.654
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 34 | 555 | 99250 | 0.093737 | 0.00052417 | 178.8288
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | SPLICE, UG | 6 | 102 | 49682 | 0.046922 | 9.6334e-05 | 487.0784
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | PEDESTAL | 5 | 19 | 1362 | 0.0012863 | 1.7945e-05 | 71.6842
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | INSULATOR | 2 | 50 | 3682 | 0.0034927 | 4.743e-05 | 73.64
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 11 | 1009 | 0.00095295 | 1.0389e-05 | 91.7273
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | ARRESTER | 5 | 26 | 1043 | 0.00099146 | 2.4715e-05 | 40.1154
AEP-AP | 2020 | 1051986 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 704 | 155864 | 0.14816 | 0.00066921 | 221.3977
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WFS | RECLOSER, LINE/OCR/BR | 2 | 1508 | 2513810 | 2.3846 | 0.0014305 | 1666.9828
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 23 | 21735 | 0.020618 | 2.1818e-05 | 945
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | JUMPER/RISER | 1 | 18 | 108 | 0.00010245 | 1.7075e-05 | 6
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 81 | 84417 | 0.079912 | 7.6677e-05 | 1042.1852
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | FUSE | 4 | 22 | 4137 | 0.0039072 | 2.0778e-05 | 188.0455
AEP-AP | 2024 | 1058812 | SUBTRANSMISSION LINE | WU | NONE | 5 | 1856 | 299988 | 0.28333 | 0.0017529 | 161.6315
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 664 | 117276 | 0.11102 | 0.00062856 | 176.6205
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 9 | 2421 | 0.0022953 | 8.5328e-06 | 269
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | AO | INSULATOR | 3 | 808 | 177796 | 0.16792 | 0.00076312 | 220.0446
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | POLE | 1 | 7 | 511 | 0.00048575 | 6.6541e-06 | 73
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 2038 | 0.0019373 | 9.5058e-07 | 2038
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | CROSSARM | 2 | 356 | 84932 | 0.080214 | 0.00033623 | 238.573
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FO | POLE HARDWARE | 1 | 65 | 7194 | 0.0067944 | 6.139e-05 | 110.6769
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | METERING | 4 | 6 | 200 | 0.00018889 | 5.6667e-06 | 33.3333
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 2 | 381 | 0.00035984 | 1.8889e-06 | 190.5
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WFS | JUMPER/RISER | 1 | 2 | 5662 | 0.0053475 | 1.8889e-06 | 2831
AEP-AP | 2025 | 1058812 | PARTIAL POWER | VIN | NONE | 1 | 4 | 284 | 0.00026823 | 3.7778e-06 | 71
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | WU | NONE | 1 | 982 | 154174 | 0.14595 | 0.00092959 | 157
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | EQF | ARRESTER | 4 | 4290 | 359494 | 0.33953 | 0.0040517 | 83.7981
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 293 | 9083 | 0.0085785 | 0.00027673 | 31
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | F | CONDUCTOR OVERHEAD | 2 | 132 | 10296 | 0.0097241 | 0.00012467 | 78
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 119 | 9163 | 0.008674 | 0.00011265 | 77
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 24 | 2856 | 0.0026974 | 2.2667e-05 | 119
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 88 | 635 | 68872 | 0.065297 | 0.00060204 | 108.4598
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 5536 | 258692 | 89775807 | 84.9847 | 0.24489 | 347.0374
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 45 | 143 | 16047 | 0.015222 | 0.00013565 | 112.2168
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | FUSE | 137 | 512 | 114043 | 0.10818 | 0.00048568 | 222.7402
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | U | NONE | 50 | 24573 | 4160395 | 3.9444 | 0.023297 | 169.3076
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | UG | NONE | 81 | 1618 | 258186 | 0.24491 | 0.0015348 | 159.5711
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | NONE | 3421 | 65476 | 10165360 | 9.663 | 0.06224 | 155.2532
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FW | NONE | 66 | 4518 | 132038 | 0.12525 | 0.0042857 | 29.2249
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 7 | 15 | 1012 | 0.00095947 | 1.4221e-05 | 67.4667
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | NONE | 512 | 93415 | 18522696 | 17.6074 | 0.088799 | 198.284
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | F | POLE | 7 | 1679 | 265334 | 0.25169 | 0.0015927 | 158.031
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ABI | ARRESTER | 7 | 150 | 28848 | 0.027365 | 0.00014229 | 192.32
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | PEDESTAL | 13 | 84 | 16418 | 0.015574 | 7.9682e-05 | 195.4524
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ABI | CUTOUT | 8 | 30 | 6372 | 0.0060444 | 2.8458e-05 | 212.4
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 7 | 16 | 9118 | 0.0086447 | 1.5169e-05 | 569.875
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | SCO | NONE | 2 | 184 | 10484 | 0.0099659 | 0.00017491 | 56.9783
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | REGULATOR | 18 | 5953 | 832770 | 0.79162 | 0.0056588 | 139.8908
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | PEDESTAL | 5 | 24 | 3926 | 0.0037242 | 2.2766e-05 | 163.5833
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ABI | NONE | 544 | 4530 | 331076 | 0.31341 | 0.0042882 | 73.0852
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 866 | 8924 | 2081687 | 1.9706 | 0.0084477 | 233.2684
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FO | METERING | 1 | 15 | 810 | 0.00076836 | 1.4229e-05 | 54
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 1877 | 30032 | 0.028488 | 0.0017805 | 16
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 5 | 2130 | 210490 | 0.19956 | 0.0020194 | 98.8216
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | NONE | 52 | 1978 | 229314 | 0.21708 | 0.0018724 | 115.9323
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | TOR | NONE | 47 | 19074 | 3337532 | 3.1594 | 0.018056 | 174.9781
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | U | NONE | 27 | 16292 | 1561774 | 1.4846 | 0.015487 | 95.8614
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 7 | 3616 | 1019307 | 0.96639 | 0.0034283 | 281.888
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | SPLICE, OH | 6 | 24 | 1962 | 0.001865 | 2.2814e-05 | 81.75
AEP-AP | 2022 | 1054752 | SUBTRANSMISSION LINE | TOR | NONE | 1 | 1 | 131 | 0.0001242 | 9.4809e-07 | 131
AEP-AP | 2022 | 1054752 | PARTIAL POWER | O | CONN/CLAMP | 2 | 9 | 2495 | 0.0023655 | 8.5328e-06 | 277.2222
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | REGULATOR | 7 | 7372 | 312020 | 0.29598 | 0.006993 | 42.325
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | PEDESTAL | 4 | 75 | 7419 | 0.0070376 | 7.1145e-05 | 98.92
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | NONE | 554 | 3846 | 348677 | 0.32931 | 0.0036324 | 90.6596
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | INSULATOR | 228 | 53730 | 9236750 | 8.7237 | 0.050746 | 171.9105
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | TOR | NONE | 56 | 24965 | 2497125 | 2.3584 | 0.023578 | 100.025
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 16 | 244 | 33838 | 0.032032 | 0.00023098 | 138.6803
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | FW | NONE | 2 | 2171 | 931892 | 0.88216 | 0.0020551 | 429.2455
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FO | FUSE | 7 | 34 | 4628 | 0.004381 | 3.2186e-05 | 136.1176
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 15 | 490 | 45647 | 0.043112 | 0.00046278 | 93.1571
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | TRANSFORMER, OH | 3 | 6 | 1404 | 0.0013291 | 5.6798e-06 | 234
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 3 | 841 | 0.00079944 | 2.8517e-06 | 280.3333
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | U | CONDUCTOR OVERHEAD | 1 | 9 | 3519 | 0.0033451 | 8.5552e-06 | 391
AEP-AP | 2023 | 1056376 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 17 | 7872 | 0.0074519 | 1.6093e-05 | 463.0588
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 2 | 1568 | 0.0014843 | 1.8933e-06 | 784
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | METERING | 5 | 5 | 698 | 0.00066212 | 4.743e-06 | 139.6
AEP-AP | 2024 | 1058812 | PARTIAL POWER | A | FUSE | 8 | 10 | 988 | 0.00093312 | 9.4445e-06 | 98.8
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | POLE | 249 | 22937 | 8527152 | 8.0535 | 0.021663 | 371.764
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 51 | 1140 | 685253 | 0.64719 | 0.0010767 | 601.0991
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | INSULATOR | 82 | 18771 | 2854198 | 2.6957 | 0.017728 | 152.0536
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ABI | NONE | 36 | 488 | 18792 | 0.017748 | 0.00046089 | 38.5082
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | FUSE | 57 | 674 | 491136 | 0.46386 | 0.00063656 | 728.6884
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | EQF | CUTOUT | 1 | 51 | 2754 | 0.002607 | 4.8278e-05 | 54
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | SWITCH, UG | 3 | 11 | 13470 | 0.012722 | 1.0389e-05 | 1224.5455
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 3 | 73 | 24441 | 0.023083 | 6.8945e-05 | 334.8082
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 18 | 2060 | 538398 | 0.50849 | 0.0019456 | 261.3583
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 5 | 117 | 48696 | 0.045991 | 0.0001105 | 416.2051
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 20 | 27 | 7723 | 0.007294 | 2.55e-05 | 286.037
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 15 | 65 | 8970 | 0.0084718 | 6.139e-05 | 138
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | BREAKER | 2 | 574 | 108754 | 0.10271 | 0.00054212 | 189.4669
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 2 | 12 | 1.1333e-05 | 1.8889e-06 | 6
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | STATIC WIRE | 1 | 2 | 66 | 6.2738e-05 | 1.9012e-06 | 33
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 7 | 1813 | 0.0017123 | 6.6112e-06 | 259
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | EQF | INSULATOR | 5 | 2015 | 183826 | 0.17362 | 0.0019031 | 91.2288
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | FUSE | 1 | 4 | 396 | 0.00037487 | 3.7865e-06 | 99
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 9 | 1485 | 0.0014087 | 8.5373e-06 | 165
AEP-AP | 2020 | 1051986 | PARTIAL POWER | O | CONN/CLAMP | 1 | 5 | 75 | 7.1294e-05 | 4.7529e-06 | 15
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 963 | 65604 | 0.06196 | 0.00090951 | 68.1246
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | AF | NONE | 3 | 2244 | 84399 | 0.080018 | 0.0021275 | 37.611
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1470 | 52387 | 20545623 | 19.5303 | 0.049798 | 392.1893
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TOR | NONE | 126 | 283 | 67606 | 0.064265 | 0.00026901 | 238.8905
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | CUTOUT | 16 | 198 | 38825 | 0.036829 | 0.00018782 | 196.0859
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WFS | TRANSFORMER, OH | 1 | 9 | 1441 | 0.0013698 | 8.5552e-06 | 160.1111
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 14 | 1453 | 2696981 | 2.557 | 0.0013776 | 1856.1466
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | O | NONE | 1 | 83 | 2573 | 0.0024407 | 7.8733e-05 | 31
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | ARRESTER | 6 | 193 | 29088 | 0.027578 | 0.00018298 | 150.715
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | POLE | 10 | 323 | 159895 | 0.15136 | 0.00030576 | 495.031
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | POLE | 2 | 93 | 28671 | 0.027197 | 8.8219e-05 | 308.2903
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | V | NONE | 4 | 1625 | 634733 | 0.6021 | 0.0015415 | 390.6049
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 8 | 1640 | 0.0015549 | 7.5847e-06 | 205
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 21 | 2373 | 0.002251 | 1.992e-05 | 113
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | SPLICE, OH | 56 | 782 | 152146 | 0.14463 | 0.00074336 | 194.5601
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 3 | 4 | 3195 | 0.0030308 | 3.7944e-06 | 798.75
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | CAPACITOR | 1 | 71 | 8520 | 0.008082 | 6.735e-05 | 120
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | NONE | 871 | 4581 | 800700 | 0.75797 | 0.0043365 | 174.7872
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CO | NONE | 16 | 30 | 4492 | 0.00427 | 2.8517e-05 | 149.7333
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | POLE | 5 | 81 | 20109 | 0.019036 | 7.6677e-05 | 248.2593
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | TIR | NONE | 6 | 5453 | 1808540 | 1.7147 | 0.0051699 | 331.6596
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | POLE | 2373 | 23911 | 4559000 | 4.3058 | 0.022583 | 190.6654
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 27 | 86 | 16354 | 0.015481 | 8.141e-05 | 190.1628
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | FUSE | 31 | 384 | 151907 | 0.14347 | 0.00036267 | 395.5911
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | NONE | 13 | 125 | 13334 | 0.012593 | 0.00011806 | 106.672
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 5 | 845 | 170980 | 0.16253 | 0.00080324 | 202.3432
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | UB | NONE | 1 | 103 | 2678 | 0.0025457 | 9.791e-05 | 26
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | METERING | 2 | 2 | 136 | 0.00012874 | 1.8933e-06 | 68
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | CAPACITOR | 3 | 745 | 200367 | 0.18967 | 0.00070524 | 268.949
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 14 | 1259 | 1154483 | 1.0904 | 0.0011891 | 916.9841
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 167 | 60693 | 0.057573 | 0.00015842 | 363.4311
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 36 | 5021 | 640631 | 0.60505 | 0.0047421 | 127.5903
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | INSULATOR | 18 | 1461 | 239810 | 0.22701 | 0.001383 | 164.141
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | CROSSARM | 52 | 6928 | 1125857 | 1.0633 | 0.0065432 | 162.5082
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 3 | 1628 | 0.0015435 | 2.8443e-06 | 542.6667
AEP-AP | 2024 | 1058812 | SUBTRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 9 | 5418 | 0.0051171 | 8.5001e-06 | 602
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 2 | 281 | 0.00026641 | 1.8962e-06 | 140.5
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | CUTOUT | 5 | 54 | 26898 | 0.025463 | 5.1118e-05 | 498.1111
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 6 | 3328 | 1428097 | 1.354 | 0.0031552 | 429.1157
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 55 | 37070 | 0.035146 | 5.2145e-05 | 674
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 8 | 44 | 10059 | 0.0095003 | 4.1556e-05 | 228.6136
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | METERING | 2 | 19 | 1205 | 0.0011407 | 1.7986e-05 | 63.4211
AEP-AP | 2020 | 1051986 | PARTIAL POWER | UG | CONDUCTOR UG | 5 | 5 | 1987 | 0.0018888 | 4.7529e-06 | 397.4
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 2 | 23 | 5495 | 0.0052125 | 2.1818e-05 | 238.913
AEP-AP | 2024 | 1058812 | PARTIAL POWER | ABI | NONE | 5 | 8 | 600 | 0.00056667 | 7.5556e-06 | 75
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | CUTOUT | 2 | 59 | 8035 | 0.0076379 | 5.6084e-05 | 136.1864
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WFS | CONDUCTOR OVERHEAD | 3 | 5 | 1488 | 0.0014053 | 4.7223e-06 | 297.6
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 3 | 237 | 0.0002247 | 2.8443e-06 | 79
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | ERF | NONE | 3 | 2846 | 93070 | 0.0879 | 0.0026879 | 32.702
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 532 | 23593 | 3385222 | 3.1972 | 0.022283 | 143.4842
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | ARRESTER | 93 | 3803 | 884494 | 0.83536 | 0.0035918 | 232.578
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | SWITCH, OH | 8 | 1784 | 168707 | 0.15934 | 0.0016849 | 94.5667
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OU | METERING | 1 | 3 | 351 | 0.0003315 | 2.8334e-06 | 117
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | SPLICE, OH | 3 | 16 | 6871 | 0.0064893 | 1.5111e-05 | 429.4375
AEP-AP | 2020 | 1051986 | SUBTRANSMISSION LINE | EQF | CROSSARM | 3 | 282 | 104950 | 0.099764 | 0.00026806 | 372.1631
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WFS | ARRESTER | 1 | 108 | 92340 | 0.087777 | 0.00010266 | 855
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 19 | 5073 | 0.0048122 | 1.8023e-05 | 267
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 3 | 1706 | 53538 | 0.050786 | 0.0016183 | 31.3822
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 1 | 122 | 0.00011549 | 9.4663e-07 | 122
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | INSULATOR | 2 | 3880 | 467916 | 0.44294 | 0.0036729 | 120.5969
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | CUTOUT | 3 | 16 | 8992 | 0.0085298 | 1.5178e-05 | 562
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 6 | 6437 | 2082336 | 1.9667 | 0.0060795 | 323.4948
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 2 | 36 | 55304 | 0.052232 | 3.4e-05 | 1536.2222
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 4 | 1200 | 0.001136 | 3.7865e-06 | 300
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 178 | 18294 | 0.017278 | 0.00016811 | 102.7753
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | EQF | STATIC WIRE | 2 | 849 | 891462 | 0.84195 | 0.00080184 | 1050.0141
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FO | FUSE | 4 | 58 | 4352 | 0.0041103 | 5.4778e-05 | 75.0345
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 6 | 2322 | 0.002193 | 5.6667e-06 | 387
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 1 | 595 | 0.00056195 | 9.4445e-07 | 595
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 94 | 13254 | 0.012518 | 8.8779e-05 | 141
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | EQF | INSULATOR | 1 | 274 | 54800 | 0.051875 | 0.00025938 | 200
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | R | NONE | 1 | 1625 | 123500 | 0.11664 | 0.0015347 | 76
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 3 | 531 | 0.00050151 | 2.8334e-06 | 177
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | INSULATOR | 1 | 1 | 1281 | 0.0012098 | 9.4445e-07 | 1281
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | V | NONE | 1 | 439 | 21950 | 0.020731 | 0.00041462 | 50
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | SWITCH, UG | 2 | 19 | 743 | 0.00070173 | 1.7945e-05 | 39.1053
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 144 | 17568 | 0.0167 | 0.00013688 | 122
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | JUMPER/RISER | 1 | 66 | 71346 | 0.067383 | 6.2334e-05 | 1081
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | NONE | 1837 | 56762 | 16187860 | 15.3557 | 0.053844 | 285.1883
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 37 | 679 | 486841 | 0.46181 | 0.0006441 | 716.9971
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | POLE | 2413 | 28854 | 5783412 | 5.4748 | 0.027314 | 200.4371
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ABI | FUSE | 78 | 418 | 55925 | 0.053022 | 0.0003963 | 133.7919
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | POLE | 6 | 47 | 7082 | 0.0067144 | 4.456e-05 | 150.6809
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 57 | 6451 | 610322 | 0.57895 | 0.0061194 | 94.6089
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CE | NONE | 3 | 16 | 2236 | 0.0021255 | 1.5209e-05 | 139.75
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | F | NONE | 5 | 3406 | 521660 | 0.49458 | 0.0032292 | 153.1591
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | METERING | 44 | 75 | 17825 | 0.016944 | 7.1294e-05 | 237.6667
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | FUSE | 5 | 28 | 4403 | 0.0041767 | 2.6561e-05 | 157.25
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | FUSE | 13 | 131 | 13734 | 0.013021 | 0.0001242 | 104.8397
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | TRANSFORMER, OH | 20 | 53 | 27335 | 0.025984 | 5.0381e-05 | 515.7547
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 113 | 2482 | 2285943 | 2.1684 | 0.0023544 | 921.0085
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 38 | 843 | 261430 | 0.24851 | 0.00080134 | 310.1186
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 31 | 10558 | 1705500 | 1.6212 | 0.010036 | 161.5363
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 98 | 1021 | 103773 | 0.098235 | 0.00096651 | 101.6386
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 5 | 231 | 97451 | 0.09225 | 0.00021867 | 421.8658
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | EQF | BREAKER | 5 | 5440 | 1338613 | 1.2691 | 0.0051576 | 246.0686
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | R | NONE | 3 | 2396 | 390902 | 0.37081 | 0.0022728 | 163.1477
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | CUTOUT | 7 | 277 | 188124 | 0.17836 | 0.00026262 | 679.148
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | FUSE | 172 | 1628 | 436803 | 0.41349 | 0.0015411 | 268.3065
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | SPLICE, OH | 50 | 925 | 155624 | 0.14732 | 0.00087564 | 168.2422
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 30 | 2874 | 606230 | 0.57388 | 0.0027206 | 210.936
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | FUSE | 21 | 220 | 297402 | 0.28196 | 0.00020858 | 1351.8273
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | METERING | 41 | 91 | 6917 | 0.0065479 | 8.6144e-05 | 76.011
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CE | NONE | 3 | 4 | 705 | 0.00066876 | 3.7944e-06 | 176.25
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FO | POLE | 1 | 8 | 2848 | 0.0027002 | 7.5847e-06 | 356
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | POLE | 21 | 1341 | 1039176 | 0.98372 | 0.0012694 | 774.9262
AEP-AP | 2023 | 1056376 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 1 | 5 | 135 | 0.0001278 | 4.7332e-06 | 27
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | CONDUCTOR UG | 8 | 149 | 40293 | 0.038302 | 0.00014164 | 270.4228
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | REGULATOR | 1 | 68 | 12920 | 0.012282 | 6.464e-05 | 190
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | AO | NONE | 5 | 5465 | 576934 | 0.54699 | 0.0051813 | 105.5689
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | INSULATOR | 2 | 120 | 30965 | 0.029358 | 0.00011377 | 258.0417
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TIR | FUSE | 1 | 1 | 141 | 0.00013403 | 9.5058e-07 | 141
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | RECLOSER, LINE/OCR/BR | 2 | 93 | 38147 | 0.036186 | 8.8219e-05 | 410.1828
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | POLE | 4 | 47 | 14035 | 0.013286 | 4.4492e-05 | 298.617
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | SWITCH, OH | 8 | 2493 | 567211 | 0.53694 | 0.00236 | 227.5215
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 822 | 799692 | 0.75701 | 0.00077813 | 972.8613
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 217 | 0.00020542 | 9.4663e-07 | 217
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 189 | 0.0001785 | 9.4445e-07 | 189
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 21 | 53 | 2203 | 0.0020854 | 5.0172e-05 | 41.566
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TR | FUSE | 3 | 13 | 8547 | 0.0081076 | 1.2332e-05 | 657.4615
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 8 | 1364 | 231080 | 0.21875 | 0.0012912 | 169.4135
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 4 | 1734 | 121756 | 0.11526 | 0.0016415 | 70.2168
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | CROSSARM | 2 | 753 | 86396 | 0.081911 | 0.00071391 | 114.7357
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 3 | 31 | 7135 | 0.0067542 | 2.9346e-05 | 230.1613
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | TOR | POLE | 1 | 305 | 53091 | 0.050142 | 0.00028806 | 174.0689
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERO | METERING | 2 | 2 | 25 | 2.3611e-05 | 1.8889e-06 | 12.5
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | AO | NONE | 3 | 968 | 144631 | 0.1366 | 0.00091423 | 149.4122
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 3 | 75 | 7.1145e-05 | 2.8458e-06 | 25
AEP-AP | 2024 | 1058812 | PARTIAL POWER | ERF | METERING | 1 | 1 | 135 | 0.0001275 | 9.4445e-07 | 135
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | POLE | 21 | 1582 | 346510 | 0.32726 | 0.0014941 | 219.0329
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | POLE | 9 | 453 | 70460 | 0.066546 | 0.00042784 | 155.5408
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 10 | 4314 | 491078 | 0.4638 | 0.0040744 | 113.8336
AEP-AP | 2025 | 1058812 | PARTIAL POWER | A | NONE | 5 | 18 | 2866 | 0.0027068 | 1.7e-05 | 159.2222
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | SWITCH, OH | 1 | 42 | 17346 | 0.016383 | 3.9667e-05 | 413
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | O | NONE | 4 | 193 | 43311 | 0.040905 | 0.00018228 | 224.4093
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 459 | 119544 | 0.1129 | 0.0004335 | 260.4444
AEP-AP | 2025 | 1058812 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 11 | 27 | 6332 | 0.0059803 | 2.55e-05 | 234.5185
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 2 | 352 | 38708 | 0.036558 | 0.00033245 | 109.9659
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 5 | 82 | 17859 | 0.016867 | 7.7445e-05 | 217.7927
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CE | POLE | 2 | 10 | 1302 | 0.0012297 | 9.4445e-06 | 130.2
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | METERING | 2 | 5 | 3498 | 0.0033164 | 4.7405e-06 | 699.6
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 78 | 24414 | 0.023147 | 7.3951e-05 | 313
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 4 | 19 | 2243 | 0.0021184 | 1.7945e-05 | 118.0526
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | U | NONE | 18 | 16977 | 1842473 | 1.7401 | 0.016034 | 108.5276
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 13 | 2206 | 0.0020835 | 1.2278e-05 | 169.6923
AEP-AP | 2025 | 1058812 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 2 | 760 | 0.00071779 | 1.8889e-06 | 380
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 1143 | 138057 | 0.13069 | 0.001082 | 120.7848
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | FUSE | 1 | 4 | 684 | 0.00064601 | 3.7778e-06 | 171
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | OU | NONE | 2 | 999 | 228447 | 0.21576 | 0.00094351 | 228.6757
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 2 | 7 | 1549 | 0.001463 | 6.6112e-06 | 221.2857
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | RECLOSER, LINE/OCR/BR | 1 | 114 | 49476 | 0.046728 | 0.00010767 | 434
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 164 | 42232 | 0.039886 | 0.00015489 | 257.5122
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 188 | 786 | 75850 | 0.071913 | 0.0007452 | 96.5013
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 58 | 3741 | 569726 | 0.53932 | 0.0035414 | 152.2924
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | POLE | 254 | 21740 | 10525738 | 9.9846 | 0.020622 | 484.1646
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 249 | 9412 | 3707550 | 3.517 | 0.0089282 | 393.9173
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 5 | 540 | 0.00051224 | 4.743e-06 | 108
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 10 | 747 | 179298 | 0.17008 | 0.0007086 | 240.0241
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | ARRESTER | 1 | 21 | 31788 | 0.030138 | 1.991e-05 | 1513.7143
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | ARRESTER | 18 | 1926 | 207796 | 0.19711 | 0.001827 | 107.8899
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 14 | 2037 | 509122 | 0.48269 | 0.0019313 | 249.9372
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | CE | METERING | 1 | 1272 | 145008 | 0.13784 | 0.0012091 | 114
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | FUSE | 162 | 2528 | 980467 | 0.93202 | 0.0024031 | 387.843
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | FUSE | 8 | 85 | 16354 | 0.015513 | 8.063e-05 | 192.4
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 142 | 341 | 54989 | 0.052272 | 0.00032415 | 161.2581
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 16 | 1074 | 176716 | 0.16798 | 0.0010209 | 164.54
AEP-AP | 2020 | 1051986 | PARTIAL POWER | U | NONE | 52 | 107 | 13487 | 0.012821 | 0.00010171 | 126.0467
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | METERING | 64 | 300 | 22423 | 0.02127 | 0.00028458 | 74.7433
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 51 | 2358 | 520817 | 0.49404 | 0.0022368 | 220.8723
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 2 | 222 | 0.00021059 | 1.8972e-06 | 111
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | F | POLE | 15 | 328 | 79735 | 0.075596 | 0.00031097 | 243.0945
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TR | CROSSARM | 4 | 2114 | 595846 | 0.56522 | 0.0020053 | 281.8571
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CO | CONN/CLAMP | 19 | 72 | 14498 | 0.013753 | 6.8299e-05 | 201.3611
AEP-AP | 2021 | 1054192 | PARTIAL POWER | VIN | NONE | 9 | 69 | 8020 | 0.0076077 | 6.5453e-05 | 116.2319
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 5 | 87 | 75787 | 0.071891 | 8.2528e-05 | 871.1149
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | V | OTHER EQUIPMENT | 1 | 547 | 67828 | 0.064307 | 0.00051861 | 124
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 674 | 0.00063901 | 1.8962e-06 | 337
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 30 | 487 | 126878 | 0.12011 | 0.00046101 | 260.5298
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | ARRESTER | 9 | 237 | 59559 | 0.05638 | 0.00022435 | 251.3038
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | ERF | NONE | 4 | 781 | 171309 | 0.16242 | 0.00074046 | 219.3457
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | AB | NONE | 9 | 5009 | 694140 | 0.65811 | 0.004749 | 138.5786
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 6490 | 323783 | 102420422 | 96.7315 | 0.3058 | 316.3243
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 5 | 334 | 57606 | 0.054616 | 0.00031666 | 172.4731
AEP-AP | 2020 | 1051986 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 194 | 0.00018441 | 9.5058e-07 | 194
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 4 | 1432 | 0.0013556 | 3.7865e-06 | 358
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | SWITCH, OH | 31 | 11596 | 1219164 | 1.1541 | 0.010977 | 105.1366
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 267 | 1074 | 162427 | 0.1534 | 0.0010143 | 151.2356
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | ARRESTER | 275 | 9606 | 1785331 | 1.6862 | 0.0090724 | 185.8558
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | CUTOUT | 24 | 171 | 35229 | 0.033272 | 0.0001615 | 206.0175
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 70 | 850 | 214059 | 0.20217 | 0.00080279 | 251.8341
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | VIN | NONE | 2 | 2565 | 327768 | 0.31075 | 0.0024319 | 127.7848
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | WW | CROSSARM | 1 | 22 | 22044 | 0.0209 | 2.0858e-05 | 1002
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | SCO | NONE | 2 | 1019 | 7610 | 0.0072039 | 0.00096462 | 7.4681
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FW | CROSSARM | 1 | 23 | 1380 | 0.0013064 | 2.1773e-05 | 60
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | SPLICE, UG | 3 | 4 | 1167 | 0.0011022 | 3.7778e-06 | 291.75
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | TR | CONDUCTOR OVERHEAD | 1 | 38 | 5738 | 0.0054401 | 3.6027e-05 | 151
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TOR | FUSE | 1 | 3 | 63 | 5.9761e-05 | 2.8458e-06 | 21
AEP-AP | 2023 | 1056376 | PARTIAL POWER | ABI | NONE | 7 | 36 | 3054 | 0.002891 | 3.4079e-05 | 84.8333
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 1 | 397 | 0.00037495 | 9.4445e-07 | 397
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 37 | 8177 | 0.0077567 | 3.5098e-05 | 221
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 81 | 23490 | 0.022185 | 7.6501e-05 | 290
AEP-AP | 2025 | 1058812 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 420 | 0.00039667 | 1.8889e-06 | 210
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VIN | NONE | 56 | 786 | 93785 | 0.088576 | 0.00074234 | 119.3193
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | NONE | 163 | 8184 | 8164718 | 7.7112 | 0.0077294 | 997.6439
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | CUTOUT | 15 | 61 | 15363 | 0.01451 | 5.7612e-05 | 251.8525
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FO | BREAKER | 1 | 2 | 1522 | 0.001443 | 1.8962e-06 | 761
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | CROSSARM | 2 | 23 | 1693 | 0.001606 | 2.1818e-05 | 73.6087
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | CONN/CLAMP | 2 | 2 | 180 | 0.00017 | 1.8889e-06 | 90
AEP-AP | 2020 | 1051986 | SUBTRANSMISSION LINE | U | NONE | 5 | 1087 | 81403 | 0.07738 | 0.0010333 | 74.8878
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 306 | 324798 | 0.30676 | 0.000289 | 1061.4314
AEP-AP | 2022 | 1054752 | SUBTRANSMISSION LINE | OL | NONE | 1 | 853 | 49474 | 0.046906 | 0.00080872 | 58
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | V | TRANSFORMER, GROUNDING | 2 | 1205 | 180750 | 0.17137 | 0.0011424 | 150
AEP-AP | 2024 | 1058812 | PARTIAL POWER | ABI | FUSE | 5 | 17 | 4251 | 0.0040149 | 1.6056e-05 | 250.0588
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 73 | 6.9104e-05 | 9.4663e-07 | 73
AEP-AP | 2021 | 1054192 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 101 | 9.5808e-05 | 9.4859e-07 | 101
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | TIN | NONE | 12 | 10001 | 931980 | 0.88021 | 0.0094455 | 93.1887
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | RECLOSER, LINE/OCR/BR | 1 | 244 | 29524 | 0.028006 | 0.00023146 | 121
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WH | NONE | 1 | 2 | 80 | 7.5888e-05 | 1.8972e-06 | 40
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 3 | 2 | 326 | 0.00030789 | 1.8889e-06 | 163
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | FW | NONE | 2 | 336 | 15981 | 0.015093 | 0.00031734 | 47.5625
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | O | NONE | 3 | 609 | 129572 | 0.12237 | 0.00057517 | 212.7619
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 7 | 343 | 0.00032469 | 6.6264e-06 | 49
AEP-AP | 2024 | 1058812 | SUBTRANSMISSION LINE | TOR | NONE | 1 | 242 | 418579 | 0.39533 | 0.00022856 | 1729.6653
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | U | NONE | 3 | 3320 | 314040 | 0.2966 | 0.0031356 | 94.5904
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 158 | 24332 | 0.02298 | 0.00014922 | 154
AEP-AP | 2023 | 1056376 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 5 | 981 | 0.00092865 | 4.7332e-06 | 196.2
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 1401 | 0.0013232 | 9.4445e-07 | 1401
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 14 | 1568 | 0.0014905 | 1.3308e-05 | 112
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 1 | 94 | 32900 | 0.031073 | 8.8779e-05 | 350
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 2420 | 543779 | 0.51357 | 0.0022856 | 224.7021
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | METERING | 1 | 1 | 140 | 0.0001328 | 9.4859e-07 | 140
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 2 | 936 | 0.00088605 | 1.8933e-06 | 468
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | WL | TRANSFORMER, GROUNDING | 1 | 3 | 60 | 5.6667e-05 | 2.8334e-06 | 20
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 6 | 131 | 91711 | 0.086617 | 0.00012372 | 700.084
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | METERING | 70 | 336 | 58897 | 0.05584 | 0.00031856 | 175.2887
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 857 | 8265 | 1274302 | 1.2063 | 0.0078239 | 154.1805
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | CUTOUT | 20 | 2137 | 169903 | 0.16108 | 0.0020261 | 79.5054
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | FUSE | 34 | 516 | 192886 | 0.18287 | 0.00048921 | 373.8101
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERO | NONE | 3 | 7 | 2571 | 0.0024375 | 6.6366e-06 | 367.2857
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 10 | 290 | 97791 | 0.092715 | 0.00027495 | 337.2103
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 75 | 2472 | 2018163 | 1.9134 | 0.0023437 | 816.409
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | FUSE | 19 | 47 | 6103 | 0.0057893 | 4.4584e-05 | 129.8511
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | REGULATOR | 15 | 14948 | 2144325 | 2.0341 | 0.01418 | 143.4523
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | R | NONE | 7 | 3764 | 433489 | 0.41207 | 0.003578 | 115.1671
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 17 | 76 | 6422 | 0.0061046 | 7.2244e-05 | 84.5
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | U | NONE | 9 | 3794 | 564335 | 0.53532 | 0.003599 | 148.7441
AEP-AP | 2021 | 1054192 | SUBTRANSMISSION LINE | SCO | NONE | 1 | 5 | 7740 | 0.0073421 | 4.743e-06 | 1548
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | V | NONE | 1 | 104 | 22568 | 0.021396 | 9.8601e-05 | 217
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 6 | 118 | 29685 | 0.028101 | 0.0001117 | 251.5678
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | CUTOUT | 7 | 47 | 7445 | 0.0070585 | 4.456e-05 | 158.4043
AEP-AP | 2022 | 1054752 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 202 | 0.00019151 | 9.4809e-07 | 202
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CE | METERING | 3 | 9 | 351 | 0.00033278 | 8.5328e-06 | 39
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | CUTOUT | 32 | 99 | 14602 | 0.01388 | 9.4108e-05 | 147.4949
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | CUTOUT | 2818 | 102071 | 16264604 | 15.3612 | 0.096401 | 159.346
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | CROSSARM | 3 | 75 | 8082 | 0.0076826 | 7.1294e-05 | 107.76
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | NETWORK TRANSFORMER | 9 | 182 | 206998 | 0.19677 | 0.00017301 | 1137.3516
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 16 | 3493 | 0.0033134 | 1.5178e-05 | 218.3125
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 4 | 33 | 13960 | 0.01327 | 3.1369e-05 | 423.0303
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | ARRESTER | 17 | 155 | 75135 | 0.071422 | 0.00014734 | 484.7419
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 1 | 1533 | 311168 | 0.29502 | 0.0014534 | 202.9798
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 8 | 3088 | 0.0029277 | 7.5847e-06 | 386
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | INSULATOR | 3 | 3598 | 472265 | 0.44706 | 0.003406 | 131.2576
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 95 | 2363 | 778822 | 0.73726 | 0.0022369 | 329.5904
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | CONN/CLAMP | 3 | 83 | 6035 | 0.0057248 | 7.8733e-05 | 72.7108
AEP-AP | 2024 | 1058812 | PARTIAL POWER | U | CONDUCTOR UG | 3 | 4 | 2616 | 0.0024707 | 3.7778e-06 | 654
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 45 | 339 | 51370 | 0.048517 | 0.00032017 | 151.5339
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 3 | 10 | 6669 | 0.0063394 | 9.5058e-06 | 666.9
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 1 | 1037 | 0.00098575 | 9.5058e-07 | 1037
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | ABI | REGULATOR | 3 | 3555 | 486778 | 0.4608 | 0.0033653 | 136.9277
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | CUTOUT | 9 | 12 | 1688 | 0.0015942 | 1.1333e-05 | 140.6667
AEP-AP | 2024 | 1058812 | PARTIAL POWER | SCO | JUMPER/RISER | 1 | 1 | 218 | 0.00020589 | 9.4445e-07 | 218
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | INSULATOR | 1 | 36 | 9684 | 0.0091672 | 3.4079e-05 | 269
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | CONN/CLAMP | 6 | 42 | 21639 | 0.020516 | 3.982e-05 | 515.2143
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 3 | 237 | 0.00022482 | 2.8458e-06 | 79
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 25 | 21500 | 0.020384 | 2.3702e-05 | 860
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 1 | 191 | 0.00018118 | 9.4859e-07 | 191
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 1398 | 315948 | 0.29909 | 0.0013234 | 226
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | CUTOUT | 24 | 979 | 365046 | 0.34477 | 0.00092462 | 372.8764
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | CUTOUT | 30 | 570 | 144499 | 0.13647 | 0.00053834 | 253.507
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 4 | 351 | 0.00033365 | 3.8023e-06 | 87.75
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | POLE | 4 | 1167 | 202094 | 0.19211 | 0.0011093 | 173.174
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 29 | 405 | 37663 | 0.035571 | 0.0003825 | 92.9951
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | CONN/CLAMP | 14 | 225 | 43526 | 0.041108 | 0.0002125 | 193.4489
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WL | NONE | 64 | 1342 | 430430 | 0.40652 | 0.0012675 | 320.7377
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 12 | 50 | 17430 | 0.016462 | 4.7223e-05 | 348.6
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OL | FUSE | 10 | 323 | 54635 | 0.0516 | 0.00030506 | 169.1486
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | WW | POLE | 1 | 90 | 29700 | 0.02805 | 8.5001e-05 | 330
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 754 | 180960 | 0.17202 | 0.00071674 | 240
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 36 | 30348 | 0.028728 | 3.4079e-05 | 843
AEP-AP | 2021 | 1054192 | TRANSMISSION STATION | EQF | MOAB | 2 | 1476 | 96638 | 0.09167 | 0.0014001 | 65.4729
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 1 | 408 | 0.00038703 | 9.4859e-07 | 408
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 132 | 172128 | 0.16257 | 0.00012467 | 1304
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 46 | 13054 | 0.012409 | 4.3727e-05 | 283.7826
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | NONE | 6802 | 339167 | 118893494 | 112.7218 | 0.32156 | 350.5456
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | FUSE | 450 | 5817 | 2045473 | 1.9393 | 0.005515 | 351.6371
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | CUTOUT | 228 | 2128 | 209713 | 0.19883 | 0.0020175 | 98.5493
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | POLE | 433 | 113290 | 26990712 | 25.5503 | 0.10724 | 238.2444
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | CONN/CLAMP | 101 | 622 | 175208 | 0.16611 | 0.00058971 | 281.6849
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | FUSE | 93 | 1153 | 302642 | 0.28708 | 0.0010937 | 262.4822
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FO | FUSE | 10 | 738 | 39184 | 0.03715 | 0.00069969 | 53.0949
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | ARRESTER | 25 | 985 | 300343 | 0.28475 | 0.00093387 | 304.9168
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 3 | 6 | 2213 | 0.0020981 | 5.6885e-06 | 368.8333
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | CUTOUT | 21 | 896 | 71542 | 0.067828 | 0.00084949 | 79.846
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | NONE | 153 | 15315 | 6435050 | 6.1042 | 0.014528 | 420.1796
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | POLE | 2 | 45 | 2270 | 0.0021522 | 4.2664e-05 | 50.4444
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 33 | 919 | 97755 | 0.09273 | 0.00087176 | 106.3711
AEP-AP | 2022 | 1054752 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 16 | 19082 | 0.018091 | 1.5169e-05 | 1192.625
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TOR | NONE | 58 | 109 | 35964 | 0.034115 | 0.0001034 | 329.945
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 23 | 924 | 203941 | 0.19346 | 0.0008765 | 220.7154
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | INSULATOR | 6 | 504 | 45530 | 0.043167 | 0.00047784 | 90.3373
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | CONN/CLAMP | 418 | 1066 | 180689 | 0.17176 | 0.0010133 | 169.5019
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | CE | NONE | 4 | 1860 | 168961 | 0.16028 | 0.0017644 | 90.8392
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WT | NONE | 3 | 23 | 13198 | 0.012546 | 2.1863e-05 | 573.8261
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 3 | 3 | 317 | 0.00030054 | 2.8443e-06 | 105.6667
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 45 | 282 | 129485 | 0.12309 | 0.00026806 | 459.1667
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 93 | 38683 | 0.036771 | 8.8404e-05 | 415.9462
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | CUTOUT | 8 | 50 | 17402 | 0.016542 | 4.7529e-05 | 348.04
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 1 | 571 | 0.00054278 | 9.5058e-07 | 571
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 19 | 20634 | 0.019614 | 1.8061e-05 | 1086
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 18 | 3042 | 0.0028856 | 1.7075e-05 | 169
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 13 | 978 | 0.00092772 | 1.2332e-05 | 75.2308
AEP-AP | 2021 | 1054192 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 9 | 10440 | 0.0099033 | 8.5373e-06 | 1160
AEP-AP | 2020 | 1051986 | PARTIAL POWER | F | NONE | 1 | 7 | 1554 | 0.0014772 | 6.6541e-06 | 222
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 3 | 3456 | 0.0032783 | 2.8458e-06 | 1152
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 5 | 650 | 0.00061659 | 4.743e-06 | 130
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | EQF | INSULATOR | 4 | 7204 | 823660 | 0.7809 | 0.00683 | 114.3337
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | ARRESTER | 28 | 105 | 3733 | 0.0035338 | 9.9396e-05 | 35.5524
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 28 | 2819 | 876945 | 0.83014 | 0.0026686 | 311.0837
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | WL | CONDUCTOR OVERHEAD | 3 | 1522 | 293383 | 0.27815 | 0.001443 | 192.7615
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 80 | 7.5847e-05 | 9.4809e-07 | 80
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 2 | 28 | 12411 | 0.011749 | 2.6506e-05 | 443.25
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | CUTOUT | 85 | 1534 | 380411 | 0.35928 | 0.0014488 | 247.9863
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 27 | 102 | 4725 | 0.0044728 | 9.6557e-05 | 46.3235
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 26 | 1212 | 500518 | 0.47272 | 0.0011447 | 412.9686
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ABI | POLE | 1 | 1 | 186 | 0.00017634 | 9.4809e-07 | 186
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | CUTOUT | 49 | 1223 | 120822 | 0.11437 | 0.0011577 | 98.7915
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | SPLICE, OH | 2 | 7 | 509 | 0.00048184 | 6.6264e-06 | 72.7143
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | V | NONE | 3 | 1397 | 120292 | 0.11387 | 0.0013224 | 86.1074
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | SWITCH, OH | 15 | 763 | 178039 | 0.16815 | 0.00072062 | 233.3408
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | CUTOUT | 8 | 194 | 5793 | 0.0054712 | 0.00018322 | 29.8608
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | ARRESTER | 5 | 617 | 91236 | 0.086168 | 0.00058273 | 147.8703
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 1 | 180 | 0.00017075 | 9.4859e-07 | 180
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | POLE | 11 | 150 | 83706 | 0.079057 | 0.00014167 | 558.04
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 1 | 104 | 9.845e-05 | 9.4663e-07 | 104
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 2 | 248 | 0.00023422 | 1.8889e-06 | 124
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | FUSE | 1 | 19 | 3002 | 0.0028353 | 1.7945e-05 | 158
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 267 | 0.00025217 | 9.4445e-07 | 267
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | WFS | NONE | 1 | 124 | 523404 | 0.49433 | 0.00011711 | 4221
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FO | INSULATOR | 1 | 1720 | 531671 | 0.50214 | 0.0016245 | 309.111
AEP-AP | 2024 | 1058812 | PARTIAL POWER | A | CUTOUT | 1 | 7 | 889 | 0.00083962 | 6.6112e-06 | 127
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | CONN/CLAMP | 3 | 14 | 312 | 0.00029535 | 1.3253e-05 | 22.2857
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 9 | 3438 | 0.003247 | 8.5001e-06 | 382
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 1 | 407 | 0.00038528 | 9.4663e-07 | 407
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1073 | 311170 | 0.29389 | 0.0010134 | 290
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 8 | 520 | 0.00049327 | 7.5888e-06 | 65
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 1 | 1 | 48 | 4.5533e-05 | 9.4859e-07 | 48
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CE | ARRESTER | 1 | 3 | 432 | 0.00041065 | 2.8517e-06 | 144
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 881 | 26208 | 5504802 | 5.2218 | 0.024861 | 210.0428
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 68 | 5754 | 922341 | 0.87493 | 0.0054582 | 160.2956
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | V | NONE | 52 | 970 | 284715 | 0.26994 | 0.00091965 | 293.5206
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | EQF | ARRESTER | 4 | 3425 | 1231089 | 1.1672 | 0.0032472 | 359.442
AEP-AP | 2022 | 1054752 | PARTIAL POWER | U | NONE | 50 | 241 | 37839 | 0.035875 | 0.00022849 | 157.0083
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 18 | 237 | 75683 | 0.071792 | 0.00022482 | 319.3376
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 28 | 373 | 125291 | 0.11879 | 0.00035364 | 335.9008
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | PEDESTAL | 2 | 498 | 67872 | 0.064349 | 0.00047215 | 136.2892
AEP-AP | 2022 | 1054752 | DISTRIBUTION SOURCE | EQF | CROSSARM | 3 | 2242 | 475116 | 0.45045 | 0.0021256 | 211.9161
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WFS | NONE | 50 | 2882 | 5879610 | 5.5774 | 0.0027338 | 2040.1145
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | ARRESTER | 31 | 2587 | 735524 | 0.69771 | 0.002454 | 284.3154
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | POLE | 18 | 1154 | 482711 | 0.45765 | 0.0010941 | 418.2938
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TR | NONE | 143 | 7284 | 2122048 | 2.013 | 0.0069096 | 291.33
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | SWITCH, OH | 6 | 413 | 46384 | 0.043976 | 0.00039156 | 112.3099
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 28 | 46 | 23916 | 0.022687 | 4.3635e-05 | 519.913
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 5 | 149 | 34392 | 0.032607 | 0.00014127 | 230.8188
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | FUSE | 5 | 32 | 3171 | 0.0030064 | 3.0339e-05 | 99.0938
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | NONE | 2013 | 65103 | 15226246 | 14.4738 | 0.061886 | 233.8793
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | AO | ARRESTER | 2 | 3710 | 394290 | 0.37382 | 0.0035174 | 106.2776
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 30 | 2360 | 743444 | 0.70671 | 0.0022434 | 315.0186
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 9 | 1109 | 0.0010514 | 8.5328e-06 | 123.2222
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | NONE | 2758 | 58704 | 8726658 | 8.2609 | 0.055571 | 148.6553
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 201 | 2861 | 748308 | 0.70837 | 0.0027083 | 261.5547
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 94 | 5818 | 1472156 | 1.3936 | 0.0055075 | 253.0347
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | ARRESTER | 4 | 135 | 83589 | 0.07925 | 0.00012799 | 619.1778
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SO | NONE | 15 | 268 | 68427 | 0.065046 | 0.00025476 | 255.3246
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 522 | 38958 | 0.036936 | 0.0004949 | 74.6322
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | NONE | 439 | 9174 | 2269863 | 2.1487 | 0.0086844 | 247.4235
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | ABI | TRANSFORMER, STATION SERVICE | 4 | 2242 | 313401 | 0.29668 | 0.0021224 | 139.7864
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 151 | 3375 | 753280 | 0.71144 | 0.0031875 | 223.1941
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1428 | 45901 | 6495455 | 6.1347 | 0.043351 | 141.5101
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | CROSSARM | 179 | 64061 | 19994496 | 18.8839 | 0.060503 | 312.1165
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | FUSE | 9 | 162 | 13379 | 0.012718 | 0.00015399 | 82.5864
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | O | ARRESTER | 1 | 2 | 554 | 0.00052524 | 1.8962e-06 | 277
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | INSULATOR | 1 | 437 | 10925 | 0.010385 | 0.0004154 | 25
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | CUTOUT | 4 | 104 | 16558 | 0.01574 | 9.8861e-05 | 159.2115
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 4 | 6212 | 0.005905 | 3.8023e-06 | 1553
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 5 | 29 | 7950 | 0.0075257 | 2.7452e-05 | 274.1379
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | POLE | 56 | 1090 | 443351 | 0.41872 | 0.0010295 | 406.744
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | PEDESTAL | 1 | 1 | 553 | 0.00052349 | 9.4663e-07 | 553
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 3 | 469 | 0.00044397 | 2.8399e-06 | 156.3333
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 1 | 1 | 274 | 0.00025978 | 9.4809e-07 | 274
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 29 | 1027 | 328100 | 0.30988 | 0.00096996 | 319.4742
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | JUMPER/RISER | 1 | 53 | 30327 | 0.028709 | 5.0172e-05 | 572.2075
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | FUSE | 172 | 851 | 78728 | 0.074355 | 0.00080373 | 92.5123
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 2 | 236 | 0.00022289 | 1.8889e-06 | 118
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | CUTOUT | 113 | 1286 | 72006 | 0.068006 | 0.0012146 | 55.9922
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERO | NONE | 1 | 1 | 66 | 6.2478e-05 | 9.4663e-07 | 66
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 9 | 603 | 0.0005732 | 8.5552e-06 | 67
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 30 | 8055 | 0.0076569 | 2.8517e-05 | 268.5
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 132 | 0.00012515 | 9.4809e-07 | 132
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CF | CONN/CLAMP | 3 | 7 | 753 | 0.00071429 | 6.6402e-06 | 107.5714
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 4 | 63 | 9354 | 0.0088918 | 5.9887e-05 | 148.4762
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 2 | 862 | 0.00081769 | 1.8972e-06 | 431
AEP-AP | 2023 | 1056376 | PARTIAL POWER | WW | NONE | 5 | 11 | 2168 | 0.0020523 | 1.0413e-05 | 197.0909
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 3 | 1056 | 0.00099734 | 2.8334e-06 | 352
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 3 | 480 | 0.00045438 | 2.8399e-06 | 160
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | CROSSARM | 2 | 1414 | 170768 | 0.16128 | 0.0013355 | 120.7694
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 1 | 1 | 60 | 5.6667e-05 | 9.4445e-07 | 60
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WFS | METERING | 3 | 3 | 355 | 0.00033528 | 2.8334e-06 | 118.3333
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 1 | 177 | 1947 | 0.0018431 | 0.00016755 | 11
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | ERF | NONE | 1 | 189 | 18522 | 0.017493 | 0.0001785 | 98
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | ERF | NONE | 12 | 6935 | 276161 | 0.26082 | 0.0065498 | 39.8213
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 232 | 0.00022007 | 9.4859e-07 | 232
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 77 | 1309 | 0.0012443 | 7.3195e-05 | 17
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | SPLICE, OH | 3 | 11 | 8708 | 0.0082604 | 1.0435e-05 | 791.6364
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 3 | 972 | 0.00092203 | 2.8458e-06 | 324
AEP-AP | 2021 | 1054192 | PARTIAL POWER | OL | CONN/CLAMP | 1 | 13 | 14937 | 0.014169 | 1.2332e-05 | 1149
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 51 | 26637 | 0.025254 | 4.8353e-05 | 522.2941
AEP-AP | 2020 | 1051986 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 98 | 9.3157e-05 | 9.5058e-07 | 98
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 2 | 296 | 300736 | 0.28587 | 0.00028137 | 1016
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | WU | NONE | 21 | 17873 | 4126052 | 3.9119 | 0.016945 | 230.8539
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | SPLICE, OH | 8 | 9 | 1543 | 0.0014629 | 8.5328e-06 | 171.4444
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | NONE | 946 | 22910 | 4693879 | 4.4526 | 0.021732 | 204.8834
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 68 | 3008 | 761420 | 0.72189 | 0.0028519 | 253.1316
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 23 | 174 | 37525 | 0.035577 | 0.00016497 | 215.6609
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OL | NONE | 68 | 2750 | 1040513 | 0.9865 | 0.0026072 | 378.3684
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 4 | 896 | 0.00084949 | 3.7924e-06 | 224
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CO | CONDUCTOR UG | 3 | 5 | 2285 | 0.0021721 | 4.7529e-06 | 457
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | CROSSARM | 74 | 25360 | 7712989 | 7.3318 | 0.024107 | 304.1399
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | ARRESTER | 34 | 2520 | 851442 | 0.80937 | 0.0023955 | 337.8738
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 5 | 31 | 12226 | 0.011598 | 2.9406e-05 | 394.3871
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TR | POLE | 4 | 103 | 32338 | 0.030676 | 9.7705e-05 | 313.9612
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 2 | 24 | 2.2766e-05 | 1.8972e-06 | 12
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | METERING | 15 | 23 | 2866 | 0.0027187 | 2.1818e-05 | 124.6087
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | OU | NONE | 40 | 1856 | 437126 | 0.41466 | 0.0017606 | 235.5205
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 71 | 10295 | 1417924 | 1.3479 | 0.0097863 | 137.7294
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 57 | 18243 | 0.017296 | 5.4041e-05 | 320.0526
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | POLE | 561 | 41744 | 20874194 | 19.7602 | 0.039516 | 500.0526
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | SCO | RECLOSER, LINE/OCR/BR | 1 | 13 | 2145 | 0.0020337 | 1.2325e-05 | 165
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 16 | 4896 | 0.0046418 | 1.5169e-05 | 306
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | SPLICE, OH | 18 | 24 | 3992 | 0.0037868 | 2.2766e-05 | 166.3333
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | O | FUSE | 7 | 151 | 25783 | 0.024509 | 0.00014354 | 170.7483
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | CABLE TERMINATOR | 12 | 23 | 4982 | 0.0047358 | 2.1863e-05 | 216.6087
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CO | NONE | 14 | 40 | 5735 | 0.0054402 | 3.7944e-05 | 143.375
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | ARRESTER | 5 | 13 | 2145 | 0.0020347 | 1.2332e-05 | 165
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | FUSE | 31 | 221 | 30682 | 0.029045 | 0.00020921 | 138.8326
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | NONE | 32 | 735 | 176725 | 0.16729 | 0.00069577 | 240.4422
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | AB | NONE | 21 | 15877 | 1983566 | 1.8855 | 0.015092 | 124.9333
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | CUTOUT | 9 | 189 | 29793 | 0.028203 | 0.00017891 | 157.6349
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 998 | 43364 | 11403263 | 10.7699 | 0.040955 | 262.9661
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | NONE | 262 | 11354 | 4390173 | 4.1463 | 0.010723 | 386.6631
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 55 | 2179 | 470248 | 0.44515 | 0.0020627 | 215.8091
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 1 | 54 | 2700 | 0.0025666 | 5.1331e-05 | 50
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 55 | 5120 | 901554 | 0.85148 | 0.0048356 | 176.0848
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 16 | 102 | 17501 | 0.016529 | 9.6334e-05 | 171.5784
AEP-AP | 2023 | 1056376 | SUBTRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 839 | 288616 | 0.27321 | 0.00079422 | 344
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 3 | 607 | 0.00057461 | 2.8399e-06 | 202.3333
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 49 | 23599 | 0.02234 | 4.6385e-05 | 481.6122
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 1 | 1 | 70 | 6.6402e-05 | 9.4859e-07 | 70
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | ARRESTER | 28 | 506 | 108222 | 0.10245 | 0.000479 | 213.8775
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | CABLE TERMINATOR | 5 | 17 | 4975 | 0.0047167 | 1.6118e-05 | 292.6471
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 7 | 30 | 5091 | 0.0048082 | 2.8334e-05 | 169.7
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 24 | 339 | 14125 | 0.01334 | 0.00032017 | 41.6667
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 2 | 3 | 113 | 0.00010672 | 2.8334e-06 | 37.6667
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TR | NONE | 21 | 692 | 333542 | 0.31502 | 0.00065356 | 481.9971
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 6 | 2940 | 705305 | 0.67045 | 0.0027947 | 239.8997
AEP-AP | 2022 | 1054752 | DISTRIBUTION SOURCE | EQF | BREAKER | 2 | 1470 | 238740 | 0.22635 | 0.0013937 | 162.4082
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | INSULATOR | 2 | 269 | 61594 | 0.058397 | 0.00025504 | 228.974
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ERF | FUSE | 10 | 27 | 3067 | 0.0028966 | 2.55e-05 | 113.5926
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | VA | GUY/ANCHOR | 1 | 822 | 247422 | 0.2347 | 0.00077974 | 301
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 855 | 64980 | 0.061769 | 0.00081275 | 76
AEP-AP | 2024 | 1058812 | PARTIAL POWER | V | METERING | 1 | 1 | 71 | 6.7056e-05 | 9.4445e-07 | 71
AEP-AP | 2025 | 1058812 | DISTRIBUTION SOURCE | OU | NONE | 1 | 242 | 20812 | 0.019656 | 0.00022856 | 86
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | EQF | REGULATOR | 1 | 3 | 630 | 0.00059501 | 2.8334e-06 | 210
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 226 | 29601 | 0.027957 | 0.00021345 | 130.9779
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 2 | 2978 | 0.0028126 | 1.8889e-06 | 1489
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WU | NONE | 2 | 2 | 82 | 7.7445e-05 | 1.8889e-06 | 41
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 1 | 116 | 0.00010956 | 9.4445e-07 | 116
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TR | CUTOUT | 2 | 82 | 23691 | 0.022473 | 7.7785e-05 | 288.9146
AEP-AP | 2023 | 1056376 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 86 | 8.141e-05 | 9.4663e-07 | 86
AEP-AP | 2022 | 1054752 | SUBTRANSMISSION LINE | VA | NONE | 1 | 1 | 268 | 0.00025409 | 9.4809e-07 | 268
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OU | TRANSFORMER, OH | 1 | 3 | 423 | 0.00040104 | 2.8443e-06 | 141
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1224 | 52940 | 10553657 | 10.0058 | 0.050192 | 199.3513
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | INSULATOR | 245 | 47841 | 7838038 | 7.4312 | 0.045358 | 163.8352
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | NONE | 1907 | 35981 | 5033317 | 4.7647 | 0.034061 | 139.8882
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 424 | 4885 | 710783 | 0.67389 | 0.0046314 | 145.5032
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | V | POLE | 5 | 124 | 29942 | 0.028388 | 0.00011756 | 241.4677
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | CONDUCTOR UG | 128 | 291 | 125989 | 0.11951 | 0.00027604 | 432.9519
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | SWITCH, OH | 26 | 10047 | 1431059 | 1.3568 | 0.0095255 | 142.4364
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 54 | 790 | 298628 | 0.28313 | 0.00074899 | 378.0101
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 5 | 35 | 7984 | 0.0075696 | 3.3183e-05 | 228.1143
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 1609 | 743413 | 0.70482 | 0.0015255 | 462.0342
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | NONE | 1077 | 25788 | 5244668 | 4.9855 | 0.024514 | 203.3763
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERO | NONE | 7 | 12 | 3633 | 0.0034535 | 1.1407e-05 | 302.75
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TIR | NONE | 36 | 154 | 40622 | 0.038615 | 0.00014639 | 263.7792
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | R | NONE | 3 | 1100 | 89075 | 0.084496 | 0.0010435 | 80.9773
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | FUSE | 5 | 52 | 56579 | 0.053783 | 4.943e-05 | 1088.0577
AEP-AP | 2020 | 1051986 | PARTIAL POWER | FO | NONE | 4 | 6 | 1345 | 0.0012785 | 5.7035e-06 | 224.1667
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 9 | 1264 | 791198 | 0.75053 | 0.001199 | 625.9478
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | NONE | 1819 | 67602 | 14446374 | 13.6754 | 0.063994 | 213.6974
AEP-AP | 2022 | 1054752 | PARTIAL POWER | A | FUSE | 5 | 10 | 502 | 0.00047594 | 9.4809e-06 | 50.2
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 5 | 6925 | 0.0065655 | 4.7405e-06 | 1385
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | CROSSARM | 6 | 1021 | 130622 | 0.12384 | 0.000968 | 127.9354
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 9 | 3393 | 0.0032169 | 8.5328e-06 | 377
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 11 | 26 | 901 | 0.00085468 | 2.4663e-05 | 34.6538
AEP-AP | 2020 | 1051986 | PARTIAL POWER | WW | OTHER EQUIPMENT | 1 | 11 | 627 | 0.00059602 | 1.0456e-05 | 57
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 47 | 24534 | 0.023322 | 4.4677e-05 | 522
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 30 | 14772 | 0.014013 | 2.8458e-05 | 492.4
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | POLE | 3 | 7 | 4457 | 0.0042256 | 6.6366e-06 | 636.7143
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | CONN/CLAMP | 115 | 231 | 53613 | 0.050752 | 0.00021867 | 232.0909
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WFS | POLE | 16 | 494 | 345236 | 0.32681 | 0.00046764 | 698.8583
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 611 | 43992 | 0.041644 | 0.00057839 | 72
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | POLE | 23 | 429 | 284458 | 0.26928 | 0.00040611 | 663.0723
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 921 | 10445 | 1738218 | 1.6417 | 0.0098648 | 166.4163
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | TRANSFORMER, OH | 4 | 4404 | 692395 | 0.65544 | 0.004169 | 157.2196
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | NONE | 48 | 355 | 38167 | 0.036047 | 0.00033528 | 107.5127
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | ARRESTER | 3 | 21 | 8314 | 0.0078703 | 1.9879e-05 | 395.9048
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | AF | NONE | 2 | 374 | 143658 | 0.13656 | 0.00035552 | 384.1123
AEP-AP | 2020 | 1051986 | PARTIAL POWER | UG | NONE | 3 | 3 | 2061 | 0.0019592 | 2.8517e-06 | 687
AEP-AP | 2021 | 1054192 | PARTIAL POWER | VA | METERING | 1 | 1 | 104 | 9.8654e-05 | 9.4859e-07 | 104
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | FUSE | 253 | 2324 | 737220 | 0.69627 | 0.0021949 | 317.2203
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | METERING | 10 | 38 | 10483 | 0.0099007 | 3.5889e-05 | 275.8684
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 155 | 84010 | 0.079527 | 0.00014673 | 542
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WH | NONE | 1 | 50 | 26500 | 0.02519 | 4.7529e-05 | 530
AEP-AP | 2023 | 1056376 | SUBTRANSMISSION LINE | EQF | CROSSARM | 3 | 1121 | 373717 | 0.35377 | 0.0010612 | 333.3782
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 35 | 1333 | 312378 | 0.29503 | 0.001259 | 234.3421
AEP-AP | 2023 | 1056376 | PARTIAL POWER | CE | NONE | 2 | 11 | 2735 | 0.002589 | 1.0413e-05 | 248.6364
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 13 | 111 | 36805 | 0.034761 | 0.00010483 | 331.5766
AEP-AP | 2024 | 1058812 | PARTIAL POWER | A | NONE | 13 | 26 | 5390 | 0.0050906 | 2.4556e-05 | 207.3077
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | NONE | 44 | 1232 | 145861 | 0.13776 | 0.0011636 | 118.3937
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | CROSSARM | 6 | 378 | 50269 | 0.047477 | 0.000357 | 132.9868
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 1 | 173 | 0.00016411 | 9.4859e-07 | 173
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 23 | 323 | 105234 | 0.099389 | 0.00030506 | 325.8019
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | FUSE | 3 | 34 | 7491 | 0.0070912 | 3.2186e-05 | 220.3235
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OU | FUSE | 4 | 78 | 16389 | 0.015514 | 7.3837e-05 | 210.1154
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 509 | 302692 | 0.28588 | 0.00048073 | 594.6798
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WFS | METERING | 2 | 2 | 321 | 0.00030317 | 1.8889e-06 | 160.5
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | TOR | NONE | 36 | 30265 | 4152093 | 3.9215 | 0.028584 | 137.1912
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 290 | 2801 | 439536 | 0.41512 | 0.0026454 | 156.9211
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 15 | 7922 | 0.007482 | 1.4167e-05 | 528.1333
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | POLE | 34 | 239 | 364683 | 0.34443 | 0.00022572 | 1525.8703
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 40 | 812 | 172532 | 0.16295 | 0.0007669 | 212.4778
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | JUMPER/RISER | 2 | 7 | 805 | 0.00076029 | 6.6112e-06 | 115
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | CROSSARM | 4 | 1462 | 316380 | 0.29881 | 0.0013808 | 216.4022
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | NONE | 6 | 1029 | 48334 | 0.045849 | 0.0009761 | 46.9718
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 422 | 28300 | 0.026901 | 0.00040115 | 67.0616
AEP-AP | 2020 | 1051986 | PARTIAL POWER | ERF | TRANSFORMER, GROUNDING | 1 | 1 | 265 | 0.0002519 | 9.5058e-07 | 265
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FO | CUTOUT | 3 | 35 | 1844 | 0.0017416 | 3.3056e-05 | 52.6857
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | OL | FUSE | 1 | 84 | 7026 | 0.0066788 | 7.9849e-05 | 83.6429
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | CUTOUT | 2 | 109 | 18361 | 0.017417 | 0.0001034 | 168.4495
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 7 | 497 | 0.00047244 | 6.6541e-06 | 71
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 4 | 312 | 0.00029658 | 3.8023e-06 | 78
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | CONN/CLAMP | 2 | 2 | 423 | 0.0003995 | 1.8889e-06 | 211.5
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | EQF | INSULATOR | 6 | 2674 | 167832 | 0.15851 | 0.0025255 | 62.7644
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 3 | 809 | 0.00076406 | 2.8334e-06 | 269.6667
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | F | NONE | 2 | 2044 | 42924 | 0.04054 | 0.0019305 | 21
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 1 | 87 | 8.2168e-05 | 9.4445e-07 | 87
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 1127 | 1166548 | 1.1018 | 0.0010644 | 1035.0914
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 5 | 155 | 0.00014639 | 4.7223e-06 | 31
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TR | FUSE | 1 | 31 | 2976 | 0.0028107 | 2.9278e-05 | 96
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | REGULATOR | 1 | 144 | 40320 | 0.03808 | 0.000136 | 280
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 173 | 0.00016339 | 9.4445e-07 | 173
AEP-AP | 2024 | 1058812 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 41 | 3.8723e-05 | 9.4445e-07 | 41
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 40 | 11320 | 0.010732 | 3.7924e-05 | 283
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 3 | 387 | 0.00036711 | 2.8458e-06 | 129
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | O | JUMPER/RISER | 2 | 26 | 3114 | 0.0029524 | 2.465e-05 | 119.7692
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | FUSE | 997 | 7973 | 1014219 | 0.96009 | 0.0075475 | 127.2067
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | NONE | 1073 | 11377 | 2328218 | 2.2074 | 0.010786 | 204.6425
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | FUSE | 31 | 98 | 23561 | 0.022338 | 9.2913e-05 | 240.4184
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | CUTOUT | 3331 | 127319 | 22341360 | 21.1816 | 0.12071 | 175.4755
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 407 | 16891 | 6618502 | 6.2749 | 0.016014 | 391.836
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | NONE | 2893 | 23966 | 3148626 | 2.9868 | 0.022734 | 131.3789
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1422 | 32314 | 4931766 | 4.6686 | 0.030589 | 152.6201
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | SCO | NONE | 7 | 2528 | 223594 | 0.21199 | 0.0023968 | 88.447
AEP-AP | 2022 | 1054752 | PARTIAL POWER | U | FUSE | 9 | 32 | 2612 | 0.0024764 | 3.0339e-05 | 81.625
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | SPLICE, OH | 68 | 1127 | 267025 | 0.25316 | 0.0010685 | 236.9343
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | CROSSARM | 150 | 60401 | 10809308 | 10.2536 | 0.057296 | 178.9591
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | POLE | 232 | 55738 | 14346519 | 13.609 | 0.052873 | 257.3921
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 3 | 522 | 0.0004949 | 2.8443e-06 | 174
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | BREAKER | 3 | 486 | 130623 | 0.12384 | 0.00046077 | 268.7716
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SO | CUTOUT | 1 | 36 | 11880 | 0.011293 | 3.4221e-05 | 330
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 29 | 1923 | 853166 | 0.81101 | 0.001828 | 443.6641
AEP-AP | 2021 | 1054192 | PARTIAL POWER | A | FUSE | 5 | 15 | 1072 | 0.0010169 | 1.4229e-05 | 71.4667
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | NONE | 222 | 10508 | 4385813 | 4.1691 | 0.0099887 | 417.3785
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 266 | 17766 | 0.016853 | 0.00025233 | 66.7895
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | CAPACITOR | 4 | 2056 | 126705 | 0.12044 | 0.0019544 | 61.6269
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WFS | POLE | 26 | 3419 | 2593921 | 2.4593 | 0.0032415 | 758.6783
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 5 | 25 | 18004 | 0.017114 | 2.3765e-05 | 720.16
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | WU | NONE | 4 | 3575 | 63214 | 0.059964 | 0.0033912 | 17.6822
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 696 | 13188 | 2921403 | 2.7655 | 0.012484 | 221.5198
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 83 | 6815 | 3418806 | 3.2364 | 0.0064513 | 501.659
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 86 | 1251 | 372570 | 0.35416 | 0.0011892 | 297.8177
AEP-AP | 2022 | 1054752 | PARTIAL POWER | VIN | FUSE | 3 | 5 | 626 | 0.0005935 | 4.7405e-06 | 125.2
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | FUSE | 178 | 2097 | 678545 | 0.64233 | 0.0019851 | 323.5789
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CF | INSULATOR | 3 | 620 | 187571 | 0.17783 | 0.00058782 | 302.5339
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 498 | 105122 | 0.099927 | 0.00047339 | 211.0884
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 559 | 150084 | 0.14237 | 0.00053026 | 268.4866
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | CUTOUT | 20 | 648 | 219548 | 0.20783 | 0.00061342 | 338.8086
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | JUMPER/RISER | 10 | 165 | 34718 | 0.033002 | 0.00015685 | 210.4121
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | CUTOUT | 27 | 164 | 56876 | 0.053717 | 0.00015489 | 346.8049
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 3 | 16 | 3452 | 0.0032745 | 1.5178e-05 | 215.75
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | SPLICE, OH | 14 | 24 | 8109 | 0.0076586 | 2.2667e-05 | 337.875
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | A | NONE | 5 | 3564 | 469574 | 0.4452 | 0.003379 | 131.7548
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 2 | 7 | 691 | 0.00065262 | 6.6112e-06 | 98.7143
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | AF | NONE | 1 | 5 | 370 | 0.00035025 | 4.7332e-06 | 74
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | FUSE | 4 | 9 | 781 | 0.00073932 | 8.5197e-06 | 86.7778
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 58 | 66364 | 0.062678 | 5.4778e-05 | 1144.2069
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WFS | POLE | 36 | 2928 | 879958 | 0.83108 | 0.0027654 | 300.5321
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | NONE | 54 | 2700 | 1272313 | 1.2016 | 0.00255 | 471.227
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | METERING | 4 | 10 | 880 | 0.00083112 | 9.4445e-06 | 88
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 2 | 1885 | 151707 | 0.14328 | 0.0017803 | 80.4812
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 1 | 294 | 0.00027767 | 9.4445e-07 | 294
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WFS | FUSE | 3 | 5 | 5064 | 0.0047827 | 4.7223e-06 | 1012.8
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | METERING | 9 | 11 | 951 | 0.00089818 | 1.0389e-05 | 86.4545
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | INSULATOR | 11 | 1673 | 147727 | 0.13952 | 0.0015801 | 88.3007
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | BE | POLE | 5 | 4334 | 1698720 | 1.6044 | 0.0040933 | 391.952
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | TOR | SWITCH, OH | 1 | 182 | 50960 | 0.048129 | 0.00017189 | 280
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 1 | 5 | 3045 | 0.0028869 | 4.7405e-06 | 609
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | REGULATOR | 3 | 2338 | 25718 | 0.024345 | 0.0022132 | 11
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | ERF | NONE | 2 | 3379 | 533873 | 0.50643 | 0.0032053 | 157.9973
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | ARRESTER | 7 | 197 | 178907 | 0.17007 | 0.00018726 | 908.1574
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 1 | 67 | 6.3424e-05 | 9.4663e-07 | 67
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 6 | 4918 | 1152264 | 1.0883 | 0.0046448 | 234.2952
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 6 | 3441 | 194578 | 0.18458 | 0.0032641 | 56.5469
AEP-AP | 2021 | 1054192 | PARTIAL POWER | O | CONN/CLAMP | 1 | 8 | 392 | 0.00037185 | 7.5888e-06 | 49
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | CIRCUIT SWITCHER | 1 | 4 | 140 | 0.0001328 | 3.7944e-06 | 35
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | VA | POLE | 1 | 302 | 35758 | 0.03385 | 0.00028588 | 118.404
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 0 | 0 | 0 | 0
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | SWITCH, OH | 1 | 6 | 9114 | 0.0086078 | 5.6667e-06 | 1519
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 2 | 142 | 11007 | 0.010396 | 0.00013411 | 77.5141
AEP-AP | 2024 | 1058812 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 242 | 0.00022856 | 9.4445e-07 | 242
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | F | NONE | 2 | 152 | 27749 | 0.026208 | 0.00014356 | 182.5592
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 1 | 24 | 2.2719e-05 | 9.4663e-07 | 24
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 2 | 322 | 0.00030609 | 1.9012e-06 | 161
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | EQF | TRANSFORMER, OH | 1 | 1 | 74 | 6.989e-05 | 9.4445e-07 | 74
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 1790 | 184131 | 0.1739 | 0.0016906 | 102.8665
AEP-AP | 2024 | 1058812 | SUBTRANSMISSION LINE | EQF | POLE | 1 | 5 | 1805 | 0.0017047 | 4.7223e-06 | 361
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | ARRESTER | 1 | 1 | 147 | 0.00013883 | 9.4445e-07 | 147
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 1 | 63 | 43659 | 0.041234 | 5.9501e-05 | 693
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OL | POLE | 1 | 36 | 5472 | 0.0051879 | 3.4131e-05 | 152
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | WFS | NONE | 1 | 4 | 496 | 0.00047149 | 3.8023e-06 | 124
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | ERF | NONE | 5 | 1084 | 119210 | 0.11332 | 0.0010304 | 109.9723
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SO | FUSE | 2 | 7 | 374 | 0.00035404 | 6.6264e-06 | 53.4286
AEP-AP | 2020 | 1051986 | PARTIAL POWER | VA | CONN/CLAMP | 1 | 1 | 259 | 0.0002462 | 9.5058e-07 | 259
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 11 | 30 | 878 | 0.00083242 | 2.8443e-05 | 29.2667
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 47 | 1672 | 294565 | 0.27927 | 0.0015852 | 176.1752
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | INSULATOR | 196 | 32927 | 4950846 | 4.6963 | 0.031234 | 150.3582
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 70 | 5201 | 0.004931 | 6.6366e-05 | 74.3
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | POLE | 11 | 344 | 49353 | 0.046791 | 0.00032614 | 143.468
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | FUSE | 246 | 3076 | 1185825 | 1.1249 | 0.0029179 | 385.5088
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 45 | 432 | 54465 | 0.051638 | 0.00040957 | 126.0764
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 7 | 41 | 31366 | 0.029738 | 3.8872e-05 | 765.0244
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | FUSE | 1102 | 11378 | 1569980 | 1.4924 | 0.010816 | 137.9838
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERO | NONE | 10 | 2257 | 182779 | 0.17338 | 0.002141 | 80.9832
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 13 | 212 | 55938 | 0.053174 | 0.00020152 | 263.8585
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SO | POLE | 2 | 21 | 2793 | 0.002648 | 1.991e-05 | 133
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 11 | 848 | 477956 | 0.45315 | 0.00080398 | 563.6274
AEP-AP | 2021 | 1054192 | PARTIAL POWER | OL | NONE | 3 | 48 | 14252 | 0.013519 | 4.5533e-05 | 296.9167
AEP-AP | 2021 | 1054192 | PARTIAL POWER | UG | NONE | 4 | 5 | 1716 | 0.0016278 | 4.743e-06 | 343.2
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ABI | FUSE | 139 | 440 | 47572 | 0.045033 | 0.00041652 | 108.1182
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 476 | 20931 | 9380337 | 8.8797 | 0.019814 | 448.1552
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | NONE | 114 | 12923 | 1543428 | 1.4611 | 0.012233 | 119.4326
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 45 | 1187 | 278441 | 0.26358 | 0.0011237 | 234.5754
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | F | FUSE | 5 | 38 | 3501 | 0.0033193 | 3.6027e-05 | 92.1316
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | CROSSARM | 65 | 9391 | 1824251 | 1.7269 | 0.0088898 | 194.2552
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 2 | 110 | 0.00010429 | 1.8962e-06 | 55
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 22 | 443 | 104072 | 0.098929 | 0.00042111 | 234.9255
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | WL | NONE | 3 | 2308 | 269172 | 0.25533 | 0.0021894 | 116.6256
AEP-AP | 2022 | 1054752 | PARTIAL POWER | OL | CONN/CLAMP | 1 | 10 | 1370 | 0.0012989 | 9.4809e-06 | 137
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | POLE | 19 | 971 | 779012 | 0.73744 | 0.00091918 | 802.2781
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | POLE | 24 | 3237 | 389302 | 0.37006 | 0.003077 | 120.2663
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 13 | 801 | 210185 | 0.19897 | 0.00075825 | 262.4032
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 14 | 6776 | 0.0064144 | 1.3253e-05 | 484
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | ARRESTER | 9 | 1114 | 192453 | 0.18218 | 0.0010545 | 172.7585
AEP-AP | 2023 | 1056376 | PARTIAL POWER | UG | NONE | 2 | 2 | 289 | 0.00027358 | 1.8933e-06 | 144.5
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 639 | 67125 | 0.063543 | 0.0006049 | 105.0469
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | TIR | NONE | 2 | 26 | 247 | 0.00023382 | 2.4612e-05 | 9.5
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 7 | 1256 | 200631 | 0.18992 | 0.001189 | 159.7381
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | SPLICE, OH | 2 | 2 | 2752 | 0.0025991 | 1.8889e-06 | 1376
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 13 | 287 | 9918 | 0.0093671 | 0.00027106 | 34.5575
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 5 | 12 | 3130 | 0.0029691 | 1.1383e-05 | 260.8333
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | METERING | 1 | 14 | 210 | 0.00019962 | 1.3308e-05 | 15
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | ARRESTER | 6 | 274 | 107265 | 0.10131 | 0.00025878 | 391.4781
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | FUSE | 2 | 32 | 7947 | 0.0075056 | 3.0223e-05 | 248.3438
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 23 | 1366 | 159570 | 0.15071 | 0.0012901 | 116.8155
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ERF | NONE | 38 | 1811 | 190666 | 0.18008 | 0.0017104 | 105.2822
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | VIN | NONE | 1 | 594 | 4752 | 0.0045077 | 0.00056346 | 8
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OU | NONE | 11 | 758 | 23082 | 0.0218 | 0.0007159 | 30.4512
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FW | POLE | 2 | 21 | 1179 | 0.0011135 | 1.9834e-05 | 56.1429
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | FUSE | 5 | 12 | 2321 | 0.0021921 | 1.1333e-05 | 193.4167
AEP-AP | 2025 | 1058812 | TRANSMISSION STATION | EQF | ARRESTER | 1 | 68 | 9792 | 0.0092481 | 6.4223e-05 | 144
AEP-AP | 2025 | 1058812 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 54 | 5.1001e-05 | 9.4445e-07 | 54
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 5 | 1985 | 0.0018747 | 4.7223e-06 | 397
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 4 | 5 | 87 | 8.2168e-05 | 4.7223e-06 | 17.4
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | JUMPER/RISER | 2 | 4 | 828 | 0.00078502 | 3.7924e-06 | 207
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | UB | NONE | 1 | 65 | 205393 | 0.19483 | 6.1659e-05 | 3159.8923
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 1 | 1 | 78 | 7.3667e-05 | 9.4445e-07 | 78
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | OU | NONE | 1 | 529 | 138069 | 0.1304 | 0.00049962 | 261
AEP-AP | 2024 | 1058812 | SUBTRANSMISSION LINE | EQF | CONN/CLAMP | 2 | 761 | 310210 | 0.29298 | 0.00071873 | 407.6347
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 11 | 3080 | 0.0029089 | 1.0389e-05 | 280
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 29 | 12304 | 0.011621 | 2.7389e-05 | 424.2759
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 2 | 17 | 3518 | 0.0033303 | 1.6093e-05 | 206.9412
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 609 | 75454 | 0.071427 | 0.0005765 | 123.8982
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | F | POLE | 4 | 1819 | 573835 | 0.54196 | 0.001718 | 315.4673
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 134 | 124044 | 0.11791 | 0.00012738 | 925.7015
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | ABI | NONE | 3 | 1486 | 531656 | 0.50538 | 0.0014126 | 357.7766
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 845 | 59791 | 0.05647 | 0.00079806 | 70.7586
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | WFS | NONE | 6 | 2904 | 2315470 | 2.1953 | 0.0027533 | 797.3382
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 1 | 333 | 0.00031571 | 9.4809e-07 | 333
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 19 | 20235 | 0.019235 | 1.8061e-05 | 1065
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | FO | FUSE | 1 | 17 | 9775 | 0.0092919 | 1.616e-05 | 575
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | O | INSULATOR | 1 | 1431 | 508721 | 0.48257 | 0.0013574 | 355.5003
AEP-AP | 2020 | 1051986 | DISTRIBUTION SOURCE | U | NONE | 2 | 497 | 57652 | 0.054803 | 0.00047244 | 116
AEP-AP | 2021 | 1054192 | PARTIAL POWER | OU | CONN/CLAMP | 1 | 1 | 124 | 0.00011763 | 9.4859e-07 | 124
AEP-AP | 2021 | 1054192 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 99 | 9.3911e-05 | 9.4859e-07 | 99
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 370 | 21830 | 0.020751 | 0.00035172 | 59
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | CROSSARM | 1 | 384 | 73344 | 0.06943 | 0.00036351 | 191
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | O | POLE HARDWARE | 1 | 3 | 831 | 0.00078786 | 2.8443e-06 | 277
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | F | METERING | 1 | 4 | 200 | 0.00018889 | 3.7778e-06 | 50
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | NONE | 847 | 20595 | 4722505 | 4.4774 | 0.019526 | 229.3035
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | NONE | 3241 | 60045 | 10150699 | 9.6289 | 0.056958 | 169.0515
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 106 | 1385 | 473224 | 0.44866 | 0.0013131 | 341.678
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | POLE | 326 | 29417 | 8905782 | 8.4435 | 0.02789 | 302.7427
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | WU | NONE | 1 | 1584 | 543312 | 0.51511 | 0.0015018 | 343
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | FUSE | 97 | 1894 | 606649 | 0.57546 | 0.0017966 | 320.3004
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | PEDESTAL | 14 | 61 | 8815 | 0.0083574 | 5.7834e-05 | 144.5082
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | CUTOUT | 58 | 1575 | 667606 | 0.63295 | 0.0014932 | 423.8768
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 505 | 200520 | 0.19011 | 0.00047879 | 397.0693
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | CUTOUT | 17 | 1000 | 261759 | 0.24817 | 0.00094809 | 261.759
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 8 | 698 | 135666 | 0.12862 | 0.00066177 | 194.3639
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | NONE | 8617 | 548680 | 168627766 | 160.2947 | 0.52157 | 307.3335
AEP-AP | 2022 | 1054752 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 2172 | 225784 | 0.21406 | 0.0020593 | 103.9521
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | POLE | 145 | 35539 | 7441657 | 7.0739 | 0.033783 | 209.3941
AEP-AP | 2020 | 1051986 | PARTIAL POWER | A | NONE | 37 | 154 | 42723 | 0.040612 | 0.00014639 | 277.4221
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | POLE | 161 | 14371 | 5524103 | 5.2511 | 0.013661 | 384.3924
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | OU | NONE | 17 | 10919 | 957543 | 0.90832 | 0.010358 | 87.6951
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | FUSE | 56 | 699 | 247062 | 0.23485 | 0.00066446 | 353.4506
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | CROSSARM | 129 | 40068 | 7052053 | 6.7036 | 0.038088 | 176.0021
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VIN | FUSE | 66 | 185 | 47653 | 0.045298 | 0.00017586 | 257.5838
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 14 | 54 | 26076 | 0.024736 | 5.1224e-05 | 482.8889
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 159 | 18138 | 0.017206 | 0.00015083 | 114.0755
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 6 | 150 | 43328 | 0.041101 | 0.00014229 | 288.8533
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 5 | 367 | 32313 | 0.030636 | 0.00034795 | 88.0463
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | SWITCH, OH | 3 | 448 | 17567 | 0.016664 | 0.00042497 | 39.2121
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 5270 | 706489 | 0.66725 | 0.0049773 | 134.0586
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 9 | 501 | 0.00047317 | 8.5001e-06 | 55.6667
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | WL | TRANSFORMER, STATION SERVICE | 1 | 996 | 93624 | 0.088997 | 0.00094678 | 94
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | AB | INSULATOR | 2 | 1619 | 233136 | 0.22115 | 0.0015358 | 144
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CE | CONDUCTOR UG | 1 | 3 | 1068 | 0.0010152 | 2.8517e-06 | 356
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 2 | 230 | 0.00021722 | 1.8889e-06 | 115
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 9 | 1002 | 210697 | 0.19899 | 0.00094634 | 210.2764
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 253 | 8596 | 2884658 | 2.7244 | 0.0081185 | 335.5814
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WW | NONE | 4 | 10 | 3167 | 0.0029911 | 9.4445e-06 | 316.7
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | FUSE | 7 | 110 | 24920 | 0.023536 | 0.00010389 | 226.5455
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 3 | 727 | 379262 | 0.3582 | 0.00068662 | 521.6809
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TR | POLE | 6 | 1400 | 365432 | 0.34513 | 0.0013222 | 261.0229
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 2 | 756 | 0.00071401 | 1.8889e-06 | 378
AEP-AP | 2024 | 1058812 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 2 | 215 | 0.00020306 | 1.8889e-06 | 107.5
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | F | POLE | 10 | 171 | 43487 | 0.041072 | 0.0001615 | 254.3099
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OL | NONE | 14 | 525 | 78207 | 0.073863 | 0.00049584 | 148.9657
AEP-AP | 2021 | 1054192 | SUBTRANSMISSION LINE | TOR | NONE | 2 | 11 | 121 | 0.00011478 | 1.0435e-05 | 11
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | METERING | 2 | 4 | 58 | 5.4778e-05 | 3.7778e-06 | 14.5
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 60 | 14820 | 0.013997 | 5.6667e-05 | 247
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | OL | NONE | 11 | 673 | 73965 | 0.07031 | 0.00063974 | 109.9034
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | CABLE TERMINATOR | 1 | 14 | 462 | 0.00043825 | 1.328e-05 | 33
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 98 | 50078 | 0.047296 | 9.2557e-05 | 511
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 2 | 136 | 0.00012845 | 1.8889e-06 | 68
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | ARRESTER | 2 | 2 | 150 | 0.00014167 | 1.8889e-06 | 75
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 1 | 116 | 0.00010956 | 9.4445e-07 | 116
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 3 | 383 | 32290 | 0.030567 | 0.00036256 | 84.3081
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 3 | 72 | 6.8262e-05 | 2.8443e-06 | 24
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WL | METERING | 1 | 1 | 60 | 5.6885e-05 | 9.4809e-07 | 60
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 580 | 0.00054989 | 9.4809e-07 | 580
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 108 | 0.000102 | 1.8889e-06 | 54
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 18 | 2520 | 0.00238 | 1.7e-05 | 140
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 13 | 10244 | 0.009675 | 1.2278e-05 | 788
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 1 | 45 | 4.25e-05 | 9.4445e-07 | 45
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | EQF | INSULATOR | 4 | 298 | 23476 | 0.022316 | 0.00028327 | 78.7785
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | U | NONE | 2 | 2107 | 143276 | 0.13563 | 0.0019946 | 68
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 1 | 57 | 125805 | 0.11934 | 5.407e-05 | 2207.1053
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 2 | 2940 | 0.0027947 | 1.9012e-06 | 1470
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 185 | 66230 | 0.062825 | 0.00017549 | 358
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 1 | 649 | 0.00061564 | 9.4859e-07 | 649
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 5 | 2385 | 0.0022612 | 4.7405e-06 | 477
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | POLE | 321 | 14713 | 2160567 | 2.0495 | 0.013957 | 146.8475
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | F | INSULATOR | 1 | 2 | 82 | 7.7785e-05 | 1.8972e-06 | 41
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | UG | NONE | 46 | 1191 | 203595 | 0.19303 | 0.0011292 | 170.9446
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 35 | 919 | 234826 | 0.22264 | 0.00087129 | 255.5234
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | METERING | 2 | 5 | 228 | 0.00021616 | 4.7405e-06 | 45.6
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | ARRESTER | 29 | 24994 | 4069329 | 3.8601 | 0.023709 | 162.8122
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FW | NONE | 33 | 2480 | 43942 | 0.041661 | 0.0023513 | 17.7185
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 8 | 168 | 66961 | 0.063485 | 0.00015928 | 398.5774
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | CUTOUT | 14 | 258 | 86976 | 0.082505 | 0.00024474 | 337.1163
AEP-AP | 2022 | 1054752 | PARTIAL POWER | VIN | NONE | 2 | 7 | 557 | 0.00052809 | 6.6366e-06 | 79.5714
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | CROSSARM | 7 | 1533 | 571709 | 0.54203 | 0.0014534 | 372.9348
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 4 | 363 | 17640 | 0.016733 | 0.00034434 | 48.595
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 48 | 120 | 27195 | 0.025851 | 0.00011407 | 226.625
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 25 | 11775 | 0.011164 | 2.3702e-05 | 471
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 43 | 1464 | 438561 | 0.41689 | 0.0013917 | 299.5635
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 8 | 98 | 95246 | 0.090539 | 9.3157e-05 | 971.898
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 16 | 2531 | 310414 | 0.29446 | 0.0024009 | 122.6448
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | CUTOUT | 6 | 364 | 37454 | 0.035529 | 0.00034529 | 102.8956
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OU | FUSE | 3 | 39 | 2865 | 0.0027163 | 3.6976e-05 | 73.4615
AEP-AP | 2021 | 1054192 | PARTIAL POWER | ERF | NONE | 4 | 7 | 894 | 0.00084804 | 6.6402e-06 | 127.7143
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 18 | 1890 | 0.0017928 | 1.7075e-05 | 105
AEP-AP | 2021 | 1054192 | PARTIAL POWER | F | CONDUCTOR OVERHEAD | 1 | 3 | 228 | 0.00021628 | 2.8458e-06 | 76
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WW | CABLE TERMINATOR | 1 | 3 | 477 | 0.00045224 | 2.8443e-06 | 159
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CF | NONE | 1 | 1 | 104 | 9.8601e-05 | 9.4809e-07 | 104
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | NONE | 2674 | 77419 | 9545189 | 9.015 | 0.073119 | 123.2926
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | F | NONE | 49 | 568 | 55358 | 0.052283 | 0.00053645 | 97.4613
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 44 | 4727 | 400393 | 0.37903 | 0.0044747 | 84.7034
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FO | NONE | 31 | 2824 | 251217 | 0.23781 | 0.0026733 | 88.9579
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | CUTOUT | 14 | 227 | 57117 | 0.054069 | 0.00021489 | 251.6167
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | R | BREAKER | 1 | 928 | 310880 | 0.29429 | 0.00087848 | 335
AEP-AP | 2023 | 1056376 | SUBTRANSMISSION LINE | WW | NONE | 1 | 558 | 64170 | 0.060745 | 0.00052822 | 115
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 886 | 261488 | 0.24857 | 0.00084222 | 295.1332
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | METERING | 30 | 39 | 4089 | 0.0038619 | 3.6834e-05 | 104.8462
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 17 | 18802 | 0.017873 | 1.616e-05 | 1106
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 7 | 507 | 105337 | 0.099486 | 0.00047884 | 207.7653
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 13 | 7472 | 1313827 | 1.2409 | 0.007057 | 175.8334
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 74 | 5402 | 0.005135 | 7.0343e-05 | 73
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 13 | 3003 | 0.0028486 | 1.2332e-05 | 231
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | BREAKER | 5 | 5457 | 571598 | 0.54193 | 0.0051737 | 104.7458
AEP-AP | 2021 | 1054192 | TRANSMISSION STATION | EQF | SWITCH, OH | 1 | 4 | 716 | 0.00067919 | 3.7944e-06 | 179
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 7 | 2254 | 0.0021426 | 6.6541e-06 | 322
AEP-AP | 2023 | 1056376 | SUBTRANSMISSION LINE | SCO | NONE | 6 | 2928 | 23088 | 0.021856 | 0.0027717 | 7.8852
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 2 | 7 | 600 | 0.00056667 | 6.6112e-06 | 85.7143
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 618 | 286752 | 0.27082 | 0.00058367 | 464
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | TIN | NONE | 2 | 2641 | 541768 | 0.51168 | 0.0024943 | 205.1374
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 1 | 1 | 1149 | 0.0010852 | 9.4445e-07 | 1149
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | GUY/ANCHOR | 1 | 14 | 756 | 0.00071864 | 1.3308e-05 | 54
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | POLE | 1 | 3 | 816 | 0.00077245 | 2.8399e-06 | 272
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | R | NONE | 1 | 3 | 18 | 1.7e-05 | 2.8334e-06 | 6
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 42 | 4956 | 0.0046987 | 3.982e-05 | 118
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | RELAY | 3 | 2618 | 451508 | 0.4292 | 0.0024886 | 172.4629
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 1 | 1 | 385 | 0.00036597 | 9.5058e-07 | 385
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 50 | 4850 | 0.0045912 | 4.7332e-05 | 97
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | JUMPER/RISER | 1 | 7 | 3269 | 0.0030874 | 6.6112e-06 | 467
AEP-AP | 2022 | 1054752 | PARTIAL POWER | TOR | FUSE | 1 | 2 | 90 | 8.5328e-05 | 1.8962e-06 | 45
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | EQF | INSULATOR | 1 | 254 | 33782 | 0.031906 | 0.00023989 | 133
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 11 | 737 | 0.00069606 | 1.0389e-05 | 67
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 2 | 9 | 5984 | 0.0056516 | 8.5001e-06 | 664.8889
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 3 | 636 | 0.00060331 | 2.8458e-06 | 212
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 13 | 1482 | 0.0014088 | 1.2358e-05 | 114
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 2 | 26 | 2.4612e-05 | 1.8933e-06 | 13
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | ERF | POLE HARDWARE | 2 | 827 | 19021 | 0.018034 | 0.00078407 | 23
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | TRANSFORMER, GROUNDING | 1 | 271 | 41192 | 0.038904 | 0.00025595 | 152
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | FUSE | 513 | 2547 | 294722 | 0.27942 | 0.0024148 | 115.7134
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1137 | 35696 | 5833448 | 5.5336 | 0.033861 | 163.4202
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 119 | 2303 | 758692 | 0.71931 | 0.0021835 | 329.4364
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FO | NONE | 40 | 3316 | 439668 | 0.41684 | 0.0031439 | 132.5899
AEP-AP | 2021 | 1054192 | PARTIAL POWER | A | NONE | 31 | 121 | 16557 | 0.015706 | 0.00011478 | 136.8347
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 26 | 85 | 56446 | 0.053544 | 8.063e-05 | 664.0706
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 56 | 1514 | 873115 | 0.82779 | 0.0014354 | 576.6942
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | FUSE | 271 | 2035 | 349468 | 0.3315 | 0.0019304 | 171.7287
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | CUTOUT | 38 | 721 | 272008 | 0.25803 | 0.00068394 | 377.2649
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | INSULATOR | 23 | 1305 | 402675 | 0.38177 | 0.0012373 | 308.5632
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | JUMPER/RISER | 2 | 8 | 2044 | 0.0019389 | 7.5888e-06 | 255.5
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 7 | 31 | 3309 | 0.0031389 | 2.9406e-05 | 106.7419
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | FUSE | 17 | 45 | 10171 | 0.009643 | 4.2664e-05 | 226.0222
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TR | NONE | 190 | 11433 | 2429476 | 2.3094 | 0.010868 | 212.4968
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | CUTOUT | 22 | 1631 | 382154 | 0.36327 | 0.0015504 | 234.3066
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 2 | 73 | 9782 | 0.0092986 | 6.9393e-05 | 134
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | CUTOUT | 16 | 87 | 7740 | 0.0073575 | 8.2701e-05 | 88.9655
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | CUTOUT | 11 | 95 | 18200 | 0.017264 | 9.0116e-05 | 191.5789
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | CUTOUT | 12 | 49 | 15172 | 0.014392 | 4.6481e-05 | 309.6327
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | WU | NONE | 3 | 638 | 443544 | 0.42052 | 0.00060488 | 695.21
AEP-AP | 2021 | 1054192 | PARTIAL POWER | U | FUSE | 3 | 8 | 2307 | 0.0021884 | 7.5888e-06 | 288.375
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 2 | 25 | 2741 | 0.0026001 | 2.3715e-05 | 109.64
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | CUTOUT | 5 | 19 | 9576 | 0.0090837 | 1.8023e-05 | 504
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 75 | 11025 | 0.010458 | 7.1145e-05 | 147
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | WL | ARRESTER | 1 | 1006 | 1259512 | 1.1941 | 0.00095378 | 1252
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | U | NONE | 6 | 6934 | 1793271 | 1.7002 | 0.0065741 | 258.62
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | EQF | METERING | 1 | 5 | 1420 | 0.0013463 | 4.7405e-06 | 284
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 6 | 3882 | 0.0036805 | 5.6885e-06 | 647
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | INSULATOR | 8 | 2162 | 336518 | 0.31989 | 0.0020552 | 155.6512
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 28 | 3442 | 456213 | 0.43187 | 0.0032583 | 132.543
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 4 | 1180 | 289685 | 0.27537 | 0.0011217 | 245.4958
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 28 | 419 | 45450 | 0.043024 | 0.00039664 | 108.4726
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | O | NONE | 29 | 939 | 108156 | 0.10238 | 0.00088889 | 115.1821
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 761 | 8703 | 3056138 | 2.8864 | 0.0082196 | 351.1591
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 10 | 5600 | 0.0053093 | 9.4809e-06 | 560
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | R | NONE | 3 | 2994 | 105688 | 0.10047 | 0.002846 | 35.2999
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 35 | 11919 | 2326735 | 2.2026 | 0.011283 | 195.2123
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 2 | 4 | 700 | 0.00066264 | 3.7865e-06 | 175
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | FUSE | 47 | 446 | 114011 | 0.10838 | 0.00042396 | 255.63
AEP-AP | 2020 | 1051986 | PARTIAL POWER | U | ARRESTER | 1 | 15 | 2100 | 0.0019962 | 1.4259e-05 | 140
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | FUSE | 1 | 14 | 544 | 0.00051604 | 1.328e-05 | 38.8571
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 4 | 442 | 24365 | 0.023161 | 0.00042016 | 55.1244
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | FUSE | 825 | 6114 | 914202 | 0.86342 | 0.0057744 | 149.526
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | OU | TRANSFORMER, OH | 1 | 4 | 180 | 0.0001711 | 3.8023e-06 | 45
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | FUSE | 15 | 166 | 19122 | 0.018102 | 0.00015714 | 115.1928
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 3 | 225 | 104968 | 0.099366 | 0.00021299 | 466.5244
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 4 | 1818 | 66022 | 0.062628 | 0.0017245 | 36.3157
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | CROSSARM | 2 | 912 | 110170 | 0.10473 | 0.00086693 | 120.8004
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 459 | 114770 | 0.1091 | 0.00043632 | 250.0436
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 264 | 0.00025095 | 9.5058e-07 | 264
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 1209 | 558558 | 0.53096 | 0.0011493 | 462
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 10 | 196 | 92255 | 0.087131 | 0.00018511 | 470.6888
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | SPLICE, OH | 2 | 6 | 3452 | 0.0032678 | 5.6798e-06 | 575.3333
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | FUSE | 218 | 1349 | 122246 | 0.11546 | 0.0012741 | 90.6197
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 3 | 196 | 2697 | 0.0025531 | 0.00018554 | 13.7602
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | POLE | 39 | 2180 | 900989 | 0.85094 | 0.0020589 | 413.2977
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 4 | 280 | 45349 | 0.042929 | 0.00026506 | 161.9607
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 1 | 1 | 468 | 0.00044371 | 9.4809e-07 | 468
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 6 | 5948 | 0.0056422 | 5.6916e-06 | 991.3333
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 37 | 15430 | 0.014629 | 3.5079e-05 | 417.027
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 1 | 322 | 0.00030545 | 9.4859e-07 | 322
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | CONDUCTOR UG | 34 | 48 | 18135 | 0.017128 | 4.5334e-05 | 377.8125
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ABI | CUTOUT | 7 | 1013 | 101932 | 0.09627 | 0.00095673 | 100.6239
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | NONE | 253 | 4513 | 3555945 | 3.3584 | 0.0042623 | 787.9337
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | REGULATOR | 7 | 3812 | 532409 | 0.50284 | 0.0036003 | 139.6666
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 8 | 451 | 93524 | 0.088329 | 0.00042595 | 207.3703
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | NONE | 25 | 5820 | 1096959 | 1.036 | 0.0054967 | 188.4809
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | SPLICE, OH | 4 | 15 | 65120 | 0.061503 | 1.4167e-05 | 4341.3333
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WI | CONN/CLAMP | 1 | 2 | 2312 | 0.0021836 | 1.8889e-06 | 1156
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WL | NONE | 2 | 3 | 172 | 0.00016245 | 2.8334e-06 | 57.3333
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 3 | 537 | 0.00050717 | 2.8334e-06 | 179
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | INSULATOR | 2 | 16 | 1752 | 0.0016547 | 1.5111e-05 | 109.5
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 3 | 33 | 4475 | 0.0042264 | 3.1167e-05 | 135.6061
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | EQF | CROSSARM | 2 | 41 | 5224 | 0.0049338 | 3.8723e-05 | 127.4146
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | POLE | 3 | 32 | 3250 | 0.0030695 | 3.0223e-05 | 101.5625
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 2 | 84 | 7.9334e-05 | 1.8889e-06 | 42
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 3 | 3285 | 0.0031025 | 2.8334e-06 | 1095
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TR | NONE | 2 | 2 | 386 | 0.00036693 | 1.9012e-06 | 193
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | F | FUSE | 1 | 3 | 171 | 0.0001615 | 2.8334e-06 | 57
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | PEDESTAL | 1 | 5 | 225 | 0.0002125 | 4.7223e-06 | 45
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 1 | 747 | 60507 | 0.057146 | 0.00070551 | 81
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 10 | 100 | 9.4663e-05 | 9.4663e-06 | 10
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 3 | 3544 | 0.0033689 | 2.8517e-06 | 1181.3333
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | PEDESTAL | 1 | 13 | 1950 | 0.0018498 | 1.2332e-05 | 150
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | EQF | ARRESTER | 3 | 1903 | 154143 | 0.14653 | 0.001809 | 81
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 74 | 12136 | 0.011462 | 6.989e-05 | 164
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | PEDESTAL | 1 | 1 | 138 | 0.00013118 | 9.5058e-07 | 138
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | NONE | 3276 | 89444 | 11652480 | 11.0535 | 0.084846 | 130.2768
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1160 | 9009 | 3933013 | 3.7289 | 0.0085413 | 436.5649
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 62 | 177 | 107312 | 0.10174 | 0.00016781 | 606.2825
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 835 | 11720 | 2449141 | 2.3232 | 0.011118 | 208.9711
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CO | CONN/CLAMP | 18 | 46 | 5275 | 0.0050012 | 4.3612e-05 | 114.6739
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 19 | 81 | 3875 | 0.0036738 | 7.6795e-05 | 47.8395
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | POLE | 232 | 20583 | 6459937 | 6.1279 | 0.019525 | 313.8482
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 36 | 79 | 24997 | 0.023699 | 7.4899e-05 | 316.4177
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FO | NONE | 43 | 1211 | 182783 | 0.17339 | 0.0011487 | 150.9356
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 2 | 1338 | 0.0012685 | 1.8962e-06 | 669
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | SCO | NONE | 7 | 5498 | 108522 | 0.10289 | 0.0052126 | 19.7385
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 14 | 483 | 312523 | 0.29646 | 0.00045817 | 647.0455
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 56 | 2023 | 566397 | 0.53841 | 0.001923 | 279.9787
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 357 | 0.00033847 | 9.4809e-07 | 357
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TIR | NONE | 12 | 24 | 17184 | 0.016301 | 2.2766e-05 | 716
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | POLE | 14 | 1751 | 1851379 | 1.7599 | 0.0016645 | 1057.3267
AEP-AP | 2022 | 1054752 | SUBTRANSMISSION LINE | WU | NONE | 3 | 60 | 6000 | 0.0056885 | 5.6885e-05 | 100
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | CROSSARM | 139 | 41856 | 15018199 | 14.2167 | 0.039622 | 358.8064
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 37 | 82 | 11821 | 0.01119 | 7.7624e-05 | 144.1585
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | CUTOUT | 695 | 3224 | 262071 | 0.24808 | 0.0030519 | 81.2875
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | EQF | BREAKER | 1 | 13 | 2262 | 0.0021446 | 1.2325e-05 | 174
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | INSULATOR | 5 | 37 | 2144 | 0.0020296 | 3.5025e-05 | 57.9459
AEP-AP | 2021 | 1054192 | PARTIAL POWER | UG | CONDUCTOR UG | 4 | 5 | 1134 | 0.0010757 | 4.743e-06 | 226.8
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | FUSE | 24 | 252 | 236492 | 0.22433 | 0.00023905 | 938.4603
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | U | NONE | 9 | 6629 | 726714 | 0.68899 | 0.0062849 | 109.6265
AEP-AP | 2022 | 1054752 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 4 | 9 | 10477 | 0.0099331 | 8.5328e-06 | 1164.1111
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | BREAKER | 1 | 1 | 370 | 0.00035079 | 9.4809e-07 | 370
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | SWITCH, OH | 24 | 14587 | 1768192 | 1.6808 | 0.013866 | 121.217
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | FUSE | 12 | 227 | 189252 | 0.17952 | 0.00021533 | 833.7093
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | SPLICE, UG | 8 | 276 | 116158 | 0.11042 | 0.00026236 | 420.8623
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | POLE | 4 | 9 | 2078 | 0.0019671 | 8.5197e-06 | 230.8889
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FO | FUSE | 6 | 178 | 25304 | 0.024003 | 0.00016885 | 142.1573
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 3 | 3 | 460 | 0.00043635 | 2.8458e-06 | 153.3333
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | CUTOUT | 10 | 139 | 13742 | 0.013063 | 0.00013213 | 98.8633
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | V | NONE | 4 | 4034 | 436737 | 0.41515 | 0.0038347 | 108.264
AEP-AP | 2020 | 1051986 | PARTIAL POWER | VA | NONE | 9 | 11 | 1548 | 0.0014715 | 1.0456e-05 | 140.7273
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 44 | 866 | 196851 | 0.18635 | 0.00081978 | 227.3106
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 4 | 83 | 24941 | 0.023646 | 7.8691e-05 | 300.494
AEP-AP | 2020 | 1051986 | TRANSMISSION STATION | ERF | NONE | 5 | 2986 | 38818 | 0.0369 | 0.0028384 | 13
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 148 | 3935 | 2292614 | 2.1653 | 0.0037164 | 582.6211
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 6 | 1003 | 341369 | 0.32315 | 0.00094947 | 340.348
AEP-AP | 2020 | 1051986 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 2 | 173 | 0.00016445 | 1.9012e-06 | 86.5
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | WW | NONE | 3 | 368 | 34225 | 0.032324 | 0.00034756 | 93.0027
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | F | CROSSARM | 1 | 496 | 238080 | 0.22631 | 0.00047149 | 480
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 3 | 2898 | 0.002749 | 2.8458e-06 | 966
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WFS | NONE | 15 | 1783 | 352627 | 0.33381 | 0.0016878 | 197.7717
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | OU | NONE | 5 | 3049 | 250560 | 0.23719 | 0.0028863 | 82.1778
AEP-AP | 2024 | 1058812 | PARTIAL POWER | U | CONN/CLAMP | 3 | 3 | 466 | 0.00044012 | 2.8334e-06 | 155.3333
AEP-AP | 2023 | 1056376 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 289 | 0.00027358 | 9.4663e-07 | 289
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 53 | 17650 | 0.016708 | 5.0172e-05 | 333.0189
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 2 | 406 | 0.00038433 | 1.8933e-06 | 203
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 246 | 0.00023287 | 9.4663e-07 | 246
AEP-AP | 2022 | 1054752 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 3 | 15 | 2840 | 0.0026926 | 1.4221e-05 | 189.3333
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 11 | 54 | 42679 | 0.040308 | 5.1001e-05 | 790.3519
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | SCO | NONE | 6 | 1793 | 190451 | 0.18029 | 0.0016973 | 106.2192
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | POLE | 10 | 287 | 132938 | 0.12584 | 0.00027168 | 463.1986
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 3488 | 639887 | 0.60574 | 0.0033019 | 183.4538
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | FUSE | 17 | 35 | 5224 | 0.0049452 | 3.3132e-05 | 149.2571
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 2 | 11 | 416 | 0.00039462 | 1.0435e-05 | 37.8182
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 5 | 8 | 1042 | 0.00098843 | 7.5888e-06 | 130.25
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | PEDESTAL | 4 | 30 | 964 | 0.00091255 | 2.8399e-05 | 32.1333
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 47 | 6165 | 0.0058226 | 4.4389e-05 | 131.1702
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TOR | NONE | 19 | 41 | 24775 | 0.023399 | 3.8723e-05 | 604.2683
AEP-AP | 2023 | 1056376 | PARTIAL POWER | VIN | NONE | 6 | 9 | 2279 | 0.0021574 | 8.5197e-06 | 253.2222
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | REGULATOR | 1 | 405 | 36045 | 0.034121 | 0.00038339 | 89
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | ARRESTER | 9 | 487 | 305825 | 0.28884 | 0.00045995 | 627.9774
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 38 | 2774 | 0.002626 | 3.5972e-05 | 73
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 239 | 41825 | 0.039654 | 0.00022659 | 175
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | SPLICE, OH | 9 | 30 | 30624 | 0.028923 | 2.8334e-05 | 1020.8
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | NONE | 18 | 1472 | 203699 | 0.19238 | 0.0013902 | 138.3825
AEP-AP | 2025 | 1058812 | PARTIAL POWER | U | NONE | 8 | 18 | 1546 | 0.0014601 | 1.7e-05 | 85.8889
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 66 | 4950 | 0.004693 | 6.2574e-05 | 75
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | V | NONE | 5 | 4201 | 1141490 | 1.0822 | 0.0039829 | 271.7186
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 4 | 10 | 19849 | 0.018829 | 9.4859e-06 | 1984.9
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | R | NONE | 3 | 2547 | 65205 | 0.061725 | 0.0024111 | 25.6007
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 3 | 1212 | 0.0011447 | 2.8334e-06 | 404
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | CUTOUT | 2 | 6 | 2022 | 0.0019097 | 5.6667e-06 | 337
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 4 | 934 | 0.00088784 | 3.8023e-06 | 233.5
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | TRANSFORMER, GROUNDING | 1 | 2 | 1008 | 0.00095201 | 1.8889e-06 | 504
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FW | CROSSARM | 1 | 4 | 540 | 0.00051001 | 3.7778e-06 | 135
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | METERING | 2 | 2 | 176 | 0.00016622 | 1.8889e-06 | 88
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 473 | 351912 | 0.33364 | 0.00044845 | 744
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 4 | 3624 | 0.0034306 | 3.7865e-06 | 906
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 40 | 5520 | 0.0052254 | 3.7865e-05 | 138
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | FO | NONE | 1 | 463 | 84266 | 0.080102 | 0.00044012 | 182
AEP-AP | 2020 | 1051986 | PARTIAL POWER | U | FUSE | 1 | 1 | 134 | 0.00012738 | 9.5058e-07 | 134
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 498 | 0.00047339 | 9.5058e-07 | 498
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 2 | 7 | 4685 | 0.0044535 | 6.6541e-06 | 669.2857
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | INSULATOR | 1 | 1 | 132 | 0.00012467 | 9.4445e-07 | 132
AEP-AP | 2020 | 1051986 | TRANSMISSION STATION | AO | NONE | 1 | 8 | 2728 | 0.0025932 | 7.6047e-06 | 341
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 1 | 110 | 0.00010413 | 9.4663e-07 | 110
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | SCO | POLE | 1 | 245 | 220500 | 0.20873 | 0.00023192 | 900
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 1015 | 140193 | 0.13241 | 0.00095862 | 138.1212
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | NONE | 379 | 49408 | 10405576 | 9.8707 | 0.046868 | 210.6051
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | FUSE | 307 | 2375 | 362196 | 0.34358 | 0.0022529 | 152.5036
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | NONE | 348 | 18842 | 11416705 | 10.8241 | 0.017864 | 605.9179
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TR | NONE | 6 | 7 | 775 | 0.00073516 | 6.6402e-06 | 110.7143
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 80 | 8931 | 1289124 | 1.2175 | 0.0084349 | 144.3426
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 49 | 2159 | 251392 | 0.23743 | 0.0020391 | 116.4391
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TOR | CONN/CLAMP | 6 | 7 | 4023 | 0.0038242 | 6.6541e-06 | 574.7143
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | METERING | 1 | 1 | 157 | 0.00014862 | 9.4663e-07 | 157
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERO | FUSE | 1 | 28 | 1792 | 0.0016964 | 2.6506e-05 | 64
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 248 | 32943 | 0.031185 | 0.00023476 | 132.8347
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | POLE | 4 | 29 | 22394 | 0.021232 | 2.7495e-05 | 772.2069
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | FUSE | 441 | 3862 | 526947 | 0.49768 | 0.0036475 | 136.4441
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 26 | 325 | 136058 | 0.1285 | 0.00030695 | 418.64
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 7 | 204 | 48093 | 0.045422 | 0.00019267 | 235.75
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | EQF | FUSE | 1 | 513 | 39240 | 0.03706 | 0.00048451 | 76.4912
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | CONN/CLAMP | 1 | 4 | 88 | 8.3112e-05 | 3.7778e-06 | 22
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 21 | 126 | 0.000119 | 1.9834e-05 | 6
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | FUSE | 1 | 3 | 231 | 0.00021817 | 2.8334e-06 | 77
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | EQF | INSULATOR | 3 | 1927 | 371770 | 0.35247 | 0.001827 | 192.9268
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | ARRESTER | 6 | 13 | 163 | 0.00015395 | 1.2278e-05 | 12.5385
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | METERING | 1 | 5 | 5665 | 0.0053503 | 4.7223e-06 | 1133
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | POLE | 9 | 222 | 59390 | 0.056091 | 0.00020967 | 267.5225
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 2 | 132 | 5713 | 0.0054307 | 0.00012548 | 43.2803
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 21 | 1104 | 0.0010494 | 1.9962e-05 | 52.5714
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 79 | 24648 | 0.02343 | 7.5096e-05 | 312
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 1 | 4 | 680 | 0.00064504 | 3.7944e-06 | 170
AEP-AP | 2025 | 1058812 | TRANSMISSION STATION | AO | NONE | 3 | 3133 | 373559 | 0.35281 | 0.002959 | 119.2336
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 34 | 16167 | 0.015269 | 3.2111e-05 | 475.5
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | WFS | NONE | 2 | 433 | 223288 | 0.2117 | 0.00041052 | 515.6767
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 3 | 11 | 1053 | 0.00099451 | 1.0389e-05 | 95.7273
AEP-AP | 2022 | 1054752 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 296 | 0.00028063 | 9.4809e-07 | 296
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 1 | 124 | 0.00011787 | 9.5058e-07 | 124
AEP-AP | 2023 | 1056376 | PARTIAL POWER | A | TRANSFORMER, OH | 1 | 13 | 3783 | 0.0035811 | 1.2306e-05 | 291
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 1 | 83 | 7.839e-05 | 9.4445e-07 | 83
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 3 | 411 | 0.00038817 | 2.8334e-06 | 137
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | CUTOUT | 3 | 6 | 950 | 0.00089723 | 5.6667e-06 | 158.3333
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | FW | CIRCUIT SWITCHER | 4 | 3049 | 24392 | 0.023037 | 0.0028796 | 8
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | TRANSFORMER, UG | 1 | 4 | 2816 | 0.0026698 | 3.7924e-06 | 704
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 1619 | 238760 | 0.22637 | 0.001535 | 147.4737
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 1 | 999 | 0.00094351 | 9.4445e-07 | 999
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 2 | 284 | 0.00026823 | 1.8889e-06 | 142
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 160 | 85760 | 0.081351 | 0.00015178 | 536
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 2 | 424 | 0.00040199 | 1.8962e-06 | 212
AEP-AP | 2021 | 1054192 | PARTIAL POWER | VA | NONE | 2 | 10 | 1212 | 0.0011497 | 9.4859e-06 | 121.2
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | BE | NONE | 1 | 1 | 52 | 4.9112e-05 | 9.4445e-07 | 52
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | FUSE | 1 | 10 | 200 | 0.00019012 | 9.5058e-06 | 20
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 3 | 5484 | 0.0052021 | 2.8458e-06 | 1828
AEP-AP | 2020 | 1051986 | PARTIAL POWER | WH | NONE | 1 | 7 | 1148 | 0.0010913 | 6.6541e-06 | 164
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 1 | 64 | 6.0678e-05 | 9.4809e-07 | 64
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 6 | 300 | 0.00028334 | 5.6667e-06 | 50
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WFS | OTHER EQUIPMENT | 1 | 1 | 79 | 7.4612e-05 | 9.4445e-07 | 79
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | ARRESTER | 1 | 5 | 230 | 0.00021773 | 4.7332e-06 | 46
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | NONE | 2474 | 22931 | 2667385 | 2.525 | 0.021707 | 116.3222
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | POLE | 1384 | 25540 | 5383738 | 5.1043 | 0.024214 | 210.7963
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 590 | 7876 | 2771553 | 2.6291 | 0.0074711 | 351.8986
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | ARRESTER | 34 | 548 | 176399 | 0.16724 | 0.00051955 | 321.896
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 43 | 277 | 89736 | 0.085123 | 0.00026276 | 323.9567
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WFS | NONE | 25 | 1465 | 699606 | 0.66329 | 0.001389 | 477.5468
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | METERING | 12 | 33 | 1612 | 0.0015283 | 3.1287e-05 | 48.8485
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | NONE | 3142 | 76856 | 11688881 | 11.1113 | 0.073058 | 152.0881
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | CONN/CLAMP | 54 | 653 | 119231 | 0.1131 | 0.00061943 | 182.5896
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TOR | TRANSFORMER, OH | 1 | 1 | 1470 | 0.0013974 | 9.5058e-07 | 1470
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | TOR | NONE | 27 | 11848 | 4510328 | 4.2785 | 0.011239 | 380.6826
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | CUTOUT | 9 | 193 | 25620 | 0.024303 | 0.00018308 | 132.7461
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | NONE | 933 | 19787 | 25172554 | 23.8785 | 0.01877 | 1272.1764
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 4 | 4 | 1345 | 0.0012759 | 3.7944e-06 | 336.25
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 11 | 73 | 25509 | 0.024198 | 6.9247e-05 | 349.4384
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 2 | 81 | 115582 | 0.10958 | 7.6795e-05 | 1426.9383
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | FUSE | 172 | 2015 | 572780 | 0.54334 | 0.0019114 | 284.2581
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | V | NONE | 56 | 1787 | 555957 | 0.52738 | 0.0016951 | 311.1119
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 8 | 124 | 19103 | 0.018111 | 0.00011756 | 154.0565
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 793 | 34947 | 6245398 | 5.9368 | 0.03322 | 178.7106
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CE | NONE | 58 | 810 | 96908 | 0.092119 | 0.00076997 | 119.6395
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | FUSE | 28 | 131 | 18236 | 0.017335 | 0.00012453 | 139.2061
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 529 | 9400 | 3017055 | 2.868 | 0.0089355 | 320.9633
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | OL | FUSE | 13 | 1560 | 106606 | 0.10113 | 0.0014798 | 68.3372
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 9 | 505 | 49707 | 0.047152 | 0.00047904 | 98.4297
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1 | 238 | 0.00022577 | 9.4859e-07 | 238
AEP-AP | 2021 | 1054192 | PARTIAL POWER | O | NONE | 5 | 8 | 5849 | 0.0055483 | 7.5888e-06 | 731.125
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CO | CONN/CLAMP | 40 | 146 | 36669 | 0.034857 | 0.00013879 | 251.1575
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 4 | 13 | 3398 | 0.0032216 | 1.2325e-05 | 261.3846
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | METERING | 68 | 90 | 9596 | 0.0090839 | 8.5197e-05 | 106.6222
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 26 | 1113 | 268339 | 0.25454 | 0.0010558 | 241.0952
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 77 | 3593 | 1582021 | 1.4976 | 0.0034013 | 440.3064
AEP-AP | 2022 | 1054752 | PARTIAL POWER | TOR | POLE | 1 | 1 | 150 | 0.00014221 | 9.4809e-07 | 150
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 139 | 48677 | 0.046272 | 0.00013213 | 350.1942
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 80 | 4320 | 0.0040895 | 7.5731e-05 | 54
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 21 | 264 | 98104 | 0.092868 | 0.00024991 | 371.6061
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | POLE | 733 | 84705 | 34209583 | 32.3094 | 0.08 | 403.8673
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 5 | 3470 | 0.0032899 | 4.7405e-06 | 694
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | CROSSARM | 5 | 1997 | 506829 | 0.47978 | 0.0018904 | 253.7952
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | NONE | 777 | 6212 | 834191 | 0.78786 | 0.005867 | 134.287
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 10 | 13 | 425 | 0.00040139 | 1.2278e-05 | 32.6923
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | PEDESTAL | 29 | 99 | 15302 | 0.014452 | 9.3501e-05 | 154.5657
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | V | CONDUCTOR OVERHEAD | 2 | 1121 | 169491 | 0.16045 | 0.0010612 | 151.1963
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 4 | 10 | 2361 | 0.0022443 | 9.5058e-06 | 236.1
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | ARRESTER | 8 | 1417 | 170905 | 0.16178 | 0.0013414 | 120.6104
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | TOR | POLE | 1 | 330 | 87120 | 0.082471 | 0.00031239 | 264
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 4 | 13 | 7084 | 0.0067059 | 1.2306e-05 | 544.9231
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 77 | 24975 | 0.023642 | 7.2891e-05 | 324.3506
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 13 | 29 | 13193 | 0.01246 | 2.7389e-05 | 454.931
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | REGULATOR | 7 | 4599 | 166492 | 0.15761 | 0.0043536 | 36.2018
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 48 | 2694 | 0.0025502 | 4.5438e-05 | 56.125
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | CONN/CLAMP | 6 | 44 | 2647 | 0.0025057 | 4.1652e-05 | 60.1591
AEP-AP | 2021 | 1054192 | SUBTRANSMISSION LINE | U | NONE | 8 | 795 | 150056 | 0.14234 | 0.00075413 | 188.7497
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 3 | 946 | 0.00089345 | 2.8334e-06 | 315.3333
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | POLE | 2 | 60 | 17786 | 0.016872 | 5.6916e-05 | 296.4333
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | SWITCH, OH | 9 | 6299 | 496371 | 0.47184 | 0.0059877 | 78.8016
AEP-AP | 2024 | 1058812 | PARTIAL POWER | VIN | FUSE | 3 | 18 | 2495 | 0.0023564 | 1.7e-05 | 138.6111
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WFS | TRANSFORMER, OH | 2 | 4 | 1425 | 0.0013458 | 3.7778e-06 | 356.25
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 6 | 59 | 43491 | 0.04117 | 5.5851e-05 | 737.1356
AEP-AP | 2020 | 1051986 | PARTIAL POWER | VIN | NONE | 15 | 92 | 19840 | 0.01886 | 8.7454e-05 | 215.6522
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | FUSE | 115 | 1032 | 232736 | 0.21981 | 0.00097468 | 225.5194
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 26 | 1356 | 187476 | 0.17706 | 0.0012807 | 138.2566
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | CONN/CLAMP | 5 | 216 | 45374 | 0.042854 | 0.000204 | 210.0648
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 37 | 3561 | 644516 | 0.60872 | 0.0033632 | 180.993
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 43 | 43008 | 0.040775 | 4.0768e-05 | 1000.186
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | F | NONE | 25 | 3721 | 849678 | 0.80248 | 0.0035143 | 228.3467
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 8 | 28 | 1500 | 0.0014259 | 2.6616e-05 | 53.5714
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 1225 | 154764 | 0.14681 | 0.001162 | 126.338
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 2 | 13836 | 0.013125 | 1.8972e-06 | 6918
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | EQF | CONN/CLAMP | 5 | 2122 | 18893 | 0.017844 | 0.0020041 | 8.9034
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 3 | 106 | 11508 | 0.010894 | 0.00010034 | 108.566
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | SPLICE, UG | 8 | 237 | 93502 | 0.088308 | 0.00022384 | 394.5232
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 572 | 318104 | 0.30043 | 0.00054023 | 556.1259
AEP-AP | 2024 | 1058812 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 3 | 277 | 0.00026161 | 2.8334e-06 | 92.3333
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 1 | 1574 | 0.0014866 | 9.4445e-07 | 1574
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 653 | 139742 | 0.13198 | 0.00061673 | 214
AEP-AP | 2025 | 1058812 | PARTIAL POWER | CO | NONE | 1 | 1 | 241 | 0.00022761 | 9.4445e-07 | 241
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | ABI | NONE | 1 | 1540 | 214060 | 0.20306 | 0.0014608 | 139
AEP-AP | 2021 | 1054192 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 147 | 0.00013944 | 9.4859e-07 | 147
AEP-AP | 2024 | 1058812 | PARTIAL POWER | UG | CONDUCTOR UG | 3 | 4 | 732 | 0.00069134 | 3.7778e-06 | 183
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | FUSE | 306 | 1616 | 245389 | 0.23229 | 0.0015298 | 151.8496
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | CROSSARM | 1 | 305 | 91039 | 0.086359 | 0.00028932 | 298.4885
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1012 | 10141 | 2728054 | 2.5765 | 0.0095777 | 269.0123
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | NONE | 47 | 1075 | 227694 | 0.21644 | 0.0010219 | 211.8084
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | CUTOUT | 16 | 111 | 44185 | 0.041827 | 0.00010508 | 398.0631
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 7 | 1185 | 0.0011264 | 6.6541e-06 | 169.2857
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | CUTOUT | 4 | 7 | 3760 | 0.0035593 | 6.6264e-06 | 537.1429
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 1 | 3477 | 1109079 | 1.0543 | 0.0033052 | 318.9758
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 162 | 11719 | 1770675 | 1.6723 | 0.011068 | 151.0944
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | O | FUSE | 1 | 2 | 220 | 0.00020826 | 1.8933e-06 | 110
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 12 | 155 | 100669 | 0.095297 | 0.00014673 | 649.4774
AEP-AP | 2020 | 1051986 | SUBTRANSMISSION LINE | EQF | OTHER EQUIPMENT | 1 | 1 | 350 | 0.0003327 | 9.5058e-07 | 350
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 2 | 260 | 0.0002465 | 1.8962e-06 | 130
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | SPLICE, UG | 2 | 4 | 730 | 0.00069104 | 3.7865e-06 | 182.5
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WW | NONE | 3 | 6 | 661 | 0.00062669 | 5.6885e-06 | 110.1667
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 3 | 96 | 14475 | 0.013671 | 9.0668e-05 | 150.7812
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | WL | NONE | 11 | 9841 | 867194 | 0.82434 | 0.0093547 | 88.1205
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 8 | 2300 | 284046 | 0.27001 | 0.0021863 | 123.4983
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 508 | 70735 | 0.06696 | 0.00048089 | 139.2421
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 636 | 15342 | 2132221 | 2.0138 | 0.01449 | 138.9793
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | CROSSARM | 11 | 657 | 46939 | 0.044332 | 0.00062051 | 71.4444
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | CONN/CLAMP | 61 | 170 | 28176 | 0.026611 | 0.00016056 | 165.7412
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | SPLICE, OH | 7 | 18 | 6960 | 0.0065734 | 1.7e-05 | 386.6667
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | INSULATOR | 6 | 203 | 6705 | 0.0063326 | 0.00019172 | 33.0296
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | CABLE TERMINATOR | 6 | 7 | 978 | 0.00092368 | 6.6112e-06 | 139.7143
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | F | POLE | 12 | 3356 | 737778 | 0.6968 | 0.0031696 | 219.8385
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 135 | 17550 | 0.016575 | 0.0001275 | 130
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | POLE | 1 | 1 | 58 | 5.4778e-05 | 9.4445e-07 | 58
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 1 | 0 | 0 | 0 | 0
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | BE | CONDUCTOR OVERHEAD | 2 | 427 | 142565 | 0.13465 | 0.00040328 | 333.8759
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 1436 | 0.0013562 | 9.4445e-07 | 1436
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | ERF | NONE | 2 | 1994 | 33898 | 0.032223 | 0.0018955 | 17
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 98 | 4606 | 0.0043692 | 9.2962e-05 | 47
AEP-AP | 2023 | 1056376 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 18 | 2418 | 0.002289 | 1.7039e-05 | 134.3333
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 1 | 20 | 1040 | 0.0009845 | 1.8933e-05 | 52
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | ARRESTER | 2 | 5 | 443 | 0.00041839 | 4.7223e-06 | 88.6
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 2 | 256 | 0.00024271 | 1.8962e-06 | 128
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | V | TRANSFORMER, POWER - NON LTC | 1 | 1552 | 107268 | 0.1017 | 0.0014714 | 69.116
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 4 | 13 | 3459 | 0.0032794 | 1.2325e-05 | 266.0769
AEP-AP | 2023 | 1056376 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 108 | 0.00010224 | 9.4663e-07 | 108
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 5 | 730 | 0.00068945 | 4.7223e-06 | 146
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 1218 | 0.0011578 | 9.5058e-07 | 1218
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | BE | NONE | 1 | 47 | 4747 | 0.0044833 | 4.4389e-05 | 101
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | AO | NONE | 3 | 2241 | 403741 | 0.38132 | 0.0021165 | 180.1611
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 1 | 136 | 0.00012845 | 9.4445e-07 | 136
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | V | TRANSFORMER, GROUNDING | 4 | 3027 | 314233 | 0.29678 | 0.0028589 | 103.81
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | O | NONE | 1 | 69 | 621 | 0.00058651 | 6.5167e-05 | 9
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | ARRESTER | 1 | 4 | 508 | 0.00047978 | 3.7778e-06 | 127
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 1369 | 0.001293 | 9.4445e-07 | 1369
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 1 | 276 | 0.00026067 | 9.4445e-07 | 276
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | ABI | NONE | 1 | 1627 | 218018 | 0.20591 | 0.0015366 | 134
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 326 | 92062 | 0.087329 | 0.00030924 | 282.3988
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 2 | 1442 | 0.001365 | 1.8933e-06 | 721
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 2 | 574 | 0.00054212 | 1.8889e-06 | 287
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 282 | 0.00026736 | 9.4809e-07 | 282
AEP-AP | 2022 | 1054752 | PARTIAL POWER | ABI | FUSE | 1 | 5 | 300 | 0.00028443 | 4.7405e-06 | 60
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 156 | 0.00014767 | 1.8933e-06 | 78
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 1 | 181 | 0.0001716 | 9.4809e-07 | 181
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1120 | 39674 | 7393142 | 6.9986 | 0.037557 | 186.3473
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | NONE | 3639 | 173393 | 44430841 | 42.0597 | 0.16414 | 256.2436
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 106 | 5602 | 791934 | 0.75082 | 0.0053112 | 141.3663
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | NONE | 98 | 6855 | 1160746 | 1.1005 | 0.0064992 | 169.3284
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | CUTOUT | 18 | 34 | 6797 | 0.0064442 | 3.2235e-05 | 199.9118
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | F | NONE | 114 | 3719 | 576497 | 0.54686 | 0.0035278 | 155.014
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OU | NONE | 41 | 1619 | 205455 | 0.19479 | 0.001535 | 126.9024
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1074 | 40998 | 6151000 | 5.847 | 0.038972 | 150.0317
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | F | NONE | 89 | 2661 | 646815 | 0.61485 | 0.0025295 | 243.0722
AEP-AP | 2020 | 1051986 | PARTIAL POWER | WW | NONE | 6 | 22 | 8123 | 0.0077216 | 2.0913e-05 | 369.2273
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 1 | 3 | 90 | 8.5373e-05 | 2.8458e-06 | 30
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | V | NONE | 10 | 4759 | 1068936 | 1.0161 | 0.0045238 | 224.6136
AEP-AP | 2020 | 1051986 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 268 | 0.00025476 | 9.5058e-07 | 268
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | WW | NONE | 5 | 3105 | 793065 | 0.75387 | 0.0029516 | 255.4155
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | POLE | 42 | 2187 | 1583493 | 1.4955 | 0.0020655 | 724.048
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | FW | POLE | 2 | 41 | 8736 | 0.0083043 | 3.8974e-05 | 213.0732
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WI | NONE | 7 | 514 | 101825 | 0.096391 | 0.00048657 | 198.1031
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | SCO | CROSSARM | 1 | 4 | 1208 | 0.0011453 | 3.7924e-06 | 302
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 6 | 476 | 147583 | 0.14029 | 0.00045248 | 310.0483
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WT | NONE | 2 | 2 | 1046 | 0.00099018 | 1.8933e-06 | 523
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | CUTOUT | 18 | 234 | 86049 | 0.081269 | 0.000221 | 367.7308
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 7 | 4614 | 0.0043768 | 6.6402e-06 | 659.1429
AEP-AP | 2024 | 1058812 | PARTIAL POWER | U | NONE | 23 | 34 | 3055 | 0.0028853 | 3.2111e-05 | 89.8529
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 4 | 178 | 98238 | 0.092781 | 0.00016811 | 551.8989
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 10 | 412 | 65711 | 0.062061 | 0.00038912 | 159.4927
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 9 | 144 | 30730 | 0.029023 | 0.000136 | 213.4028
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | CROSSARM | 2 | 656 | 230235 | 0.21745 | 0.00061956 | 350.968
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 3 | 1935 | 0.0018355 | 2.8458e-06 | 645
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FW | NONE | 20 | 3194 | 43970 | 0.041528 | 0.0030166 | 13.7664
AEP-AP | 2023 | 1056376 | DISTRIBUTION SOURCE | OU | NONE | 1 | 251 | 33634 | 0.031839 | 0.0002376 | 134
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 65 | 6.1788e-05 | 9.5058e-07 | 65
AEP-AP | 2020 | 1051986 | TRANSMISSION STATION | EQF | ARRESTER | 2 | 774 | 273219 | 0.25972 | 0.00073575 | 352.9961
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | NONE | 552 | 18888 | 2367631 | 2.2361 | 0.017839 | 125.3511
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 1 | 47 | 4.4492e-05 | 9.4663e-07 | 47
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | CROSSARM | 2 | 1529 | 218146 | 0.20603 | 0.0014441 | 142.6723
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | V | NONE | 17 | 7199 | 713837 | 0.67419 | 0.0067991 | 99.1578
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | CROSSARM | 1 | 70 | 6720 | 0.0063746 | 6.6402e-05 | 96
AEP-AP | 2025 | 1058812 | PARTIAL POWER | UG | CONDUCTOR UG | 1 | 4 | 768 | 0.00072534 | 3.7778e-06 | 192
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WI | FUSE | 3 | 42 | 24513 | 0.023302 | 3.9924e-05 | 583.6429
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | EQF | CROSSARM | 13 | 9261 | 2716681 | 2.5717 | 0.0087668 | 293.3464
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WL | FUSE | 1 | 13 | 1508 | 0.0014305 | 1.2332e-05 | 116
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | EQF | CONN/CLAMP | 2 | 648 | 67454 | 0.063707 | 0.00061201 | 104.0957
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | EQF | RECLOSER, LINE/OCR/BR | 2 | 1066 | 287724 | 0.27174 | 0.0010068 | 269.9099
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | METERING | 1 | 4 | 184 | 0.00017418 | 3.7865e-06 | 46
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | U | POLE | 1 | 573 | 237795 | 0.22459 | 0.00054117 | 415
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 154 | 0.00014578 | 9.4663e-07 | 154
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WI | FUSE | 6 | 36 | 5020 | 0.0047412 | 3.4e-05 | 139.4444
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TR | NONE | 1 | 5 | 675 | 0.00063898 | 4.7332e-06 | 135
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 18 | 216 | 0.0002049 | 1.7075e-05 | 12
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 1 | 137 | 0.00012996 | 9.4859e-07 | 137
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | O | NONE | 1 | 524 | 123314 | 0.11646 | 0.00049489 | 235.3321
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | JUMPER/RISER | 1 | 2 | 270 | 0.000255 | 1.8889e-06 | 135
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CE | ARRESTER | 1 | 1 | 1885 | 0.0017803 | 9.4445e-07 | 1885
AEP-AP | 2025 | 1058812 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 1 | 364 | 0.00034378 | 9.4445e-07 | 364
AEP-AP | 2024 | 1058812 | SUBTRANSMISSION LINE | VA | POLE | 3 | 912 | 273908 | 0.25869 | 0.00086134 | 300.3377
AEP-AP | 2023 | 1056376 | PARTIAL POWER | CO | CABLE TERMINATOR | 1 | 1 | 59 | 5.5851e-05 | 9.4663e-07 | 59
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | FW | NONE | 2 | 1042 | 32302 | 0.030508 | 0.00098412 | 31
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | AF | NONE | 1 | 32 | 1472 | 0.0013963 | 3.0355e-05 | 46
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TR | ARRESTER | 1 | 2 | 196 | 0.00018592 | 1.8972e-06 | 98
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | F | INSULATOR | 1 | 717 | 170646 | 0.16117 | 0.00067717 | 238
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | UG | METERING | 1 | 1 | 113 | 0.00010713 | 9.4809e-07 | 113
AEP-AP | 2023 | 1056376 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 6 | 3090 | 0.0029251 | 5.6798e-06 | 515
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | POLE | 584 | 51245 | 25617754 | 24.2879 | 0.048585 | 499.9074
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 60 | 4219 | 559047 | 0.53003 | 0.004 | 132.507
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | CROSSARM | 112 | 39032 | 13180364 | 12.5028 | 0.037026 | 337.681
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | POLE | 22 | 2819 | 1854497 | 1.7582 | 0.0026727 | 657.8563
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | NONE | 73 | 876 | 1754108 | 1.6639 | 0.00083097 | 2002.4064
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 851 | 78550 | 0.074512 | 0.00080725 | 92.3032
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | TOR | NONE | 93 | 46220 | 11091031 | 10.5429 | 0.043936 | 239.9617
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | EQF | POLE | 3 | 215 | 62035 | 0.058969 | 0.00020438 | 288.5349
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | FUSE | 117 | 628 | 60558 | 0.057565 | 0.00059697 | 96.4299
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 3 | 3 | 215 | 0.00020438 | 2.8517e-06 | 71.6667
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | AB | NONE | 27 | 15200 | 2401268 | 2.2778 | 0.014419 | 157.9782
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 12 | 625 | 0.00059287 | 1.1383e-05 | 52.0833
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | V | CONDUCTOR OVERHEAD | 1 | 92 | 66884 | 0.063446 | 8.7271e-05 | 727
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | TRANSFORMER, OH | 9 | 22 | 16214 | 0.01538 | 2.0869e-05 | 737
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 3 | 362 | 22762 | 0.021592 | 0.00034339 | 62.8785
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | POLE | 3 | 84 | 17503 | 0.016603 | 7.9682e-05 | 208.369
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 2 | 1305 | 1502182 | 1.4242 | 0.0012373 | 1151.0973
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | NONE | 120 | 16011 | 1726236 | 1.6341 | 0.015157 | 107.8156
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CF | NONE | 2 | 1784 | 199752 | 0.18938 | 0.0016914 | 111.9686
AEP-AP | 2022 | 1054752 | DISTRIBUTION SOURCE | EQF | ARRESTER | 1 | 1000 | 293736 | 0.27849 | 0.00094809 | 293.736
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | O | NONE | 1 | 28 | 224 | 0.00021237 | 2.6547e-05 | 8
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | FUSE | 1 | 2 | 25824 | 0.024496 | 1.8972e-06 | 12912
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | SO | NONE | 1 | 1 | 454 | 0.00043066 | 9.4859e-07 | 454
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | ABI | NONE | 4 | 2248 | 406646 | 0.38406 | 0.0021231 | 180.8923
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 82 | 12546 | 0.011849 | 7.7445e-05 | 153
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 1 | 406 | 103362 | 0.097621 | 0.00038345 | 254.5862
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 32 | 3232 | 0.0030525 | 3.0223e-05 | 101
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | FUSE | 184 | 1583 | 616788 | 0.58477 | 0.0015008 | 389.6323
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | AO | BREAKER | 3 | 4036 | 1080790 | 1.0247 | 0.0038265 | 267.7874
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OU | NONE | 39 | 3932 | 425438 | 0.40273 | 0.0037222 | 108.1989
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 34 | 940 | 136229 | 0.12916 | 0.0008912 | 144.9245
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | CONN/CLAMP | 4 | 11 | 796 | 0.00075468 | 1.0429e-05 | 72.3636
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | CUTOUT | 3 | 4 | 1299 | 0.0012316 | 3.7924e-06 | 324.75
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | ABI | OTHER EQUIPMENT | 2 | 1197 | 167679 | 0.15906 | 0.0011355 | 140.0827
AEP-AP | 2022 | 1054752 | PARTIAL POWER | O | FUSE | 1 | 4 | 1124 | 0.0010657 | 3.7924e-06 | 281
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 23 | 1581 | 85658 | 0.081425 | 0.0015029 | 54.1796
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | O | NONE | 37 | 629 | 81660 | 0.077625 | 0.00059792 | 129.8251
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 36 | 2008 | 1230094 | 1.1693 | 0.0019088 | 612.5966
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WU | NONE | 9 | 29 | 6417 | 0.0060871 | 2.7509e-05 | 221.2759
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | AF | NONE | 7 | 1515 | 399380 | 0.37885 | 0.0014371 | 263.6172
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 8 | 800 | 0.00075888 | 7.5888e-06 | 100
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | JUMPER/RISER | 4 | 15 | 6753 | 0.0063926 | 1.4199e-05 | 450.2
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | POLE | 28 | 1798 | 2985429 | 2.832 | 0.0017056 | 1660.4166
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 58 | 56363 | 0.053437 | 5.4989e-05 | 971.7759
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WL | FUSE | 3 | 10 | 964 | 0.00091396 | 9.4809e-06 | 96.4
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 9 | 119 | 113829 | 0.10792 | 0.00011282 | 956.5462
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 168 | 9744 | 0.009224 | 0.00015903 | 58
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 13 | 2169 | 802818 | 0.76114 | 0.0020564 | 370.1328
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 3 | 27 | 2.5598e-05 | 2.8443e-06 | 9
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TIR | NONE | 7 | 122 | 16495 | 0.015615 | 0.00011549 | 135.2049
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 7 | 343 | 0.00032519 | 6.6366e-06 | 49
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | PEDESTAL | 20 | 260 | 42350 | 0.04009 | 0.00024612 | 162.8846
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1289 | 50990 | 8182287 | 7.7278 | 0.048158 | 160.4685
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OL | FUSE | 4 | 157 | 19493 | 0.018453 | 0.00014862 | 124.1592
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | POLE | 3 | 12 | 3788 | 0.0035933 | 1.1383e-05 | 315.6667
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 10 | 220 | 29516 | 0.027941 | 0.00020826 | 134.1636
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 3 | 4 | 4420 | 0.0041906 | 3.7924e-06 | 1105
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CE | NONE | 2 | 12 | 2385 | 0.0022612 | 1.1377e-05 | 198.75
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 9 | 32 | 8613 | 0.0081874 | 3.0419e-05 | 269.1562
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 3 | 16 | 1642 | 0.0015544 | 1.5146e-05 | 102.625
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 131 | 31422 | 0.029791 | 0.0001242 | 239.8626
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 24 | 3105 | 300067 | 0.28405 | 0.0029393 | 96.6399
AEP-AP | 2023 | 1056376 | PARTIAL POWER | VA | NONE | 1 | 1 | 84 | 7.9517e-05 | 9.4663e-07 | 84
AEP-AP | 2023 | 1056376 | PARTIAL POWER | UG | CONDUCTOR UG | 6 | 15 | 4828 | 0.0045703 | 1.4199e-05 | 321.8667
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | TOR | CROSSARM | 1 | 57 | 57114 | 0.054066 | 5.3958e-05 | 1002
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 3 | 1668 | 0.001579 | 2.8399e-06 | 556
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 3 | 7 | 2928 | 0.0027654 | 6.6112e-06 | 418.2857
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 23 | 3245 | 0.0030648 | 2.1722e-05 | 141.087
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ABI | CUTOUT | 9 | 113 | 22244 | 0.021057 | 0.00010697 | 196.8496
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 2 | 2 | 54 | 5.1118e-05 | 1.8933e-06 | 27
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 6 | 93 | 28360 | 0.026785 | 8.7834e-05 | 304.9462
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 111 | 777 | 67698 | 0.063938 | 0.00073384 | 87.1274
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | POLE | 17 | 353 | 148874 | 0.1406 | 0.00033339 | 421.7394
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | REGULATOR | 5 | 1387 | 60626 | 0.057259 | 0.00131 | 43.7102
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WU | NONE | 6 | 27 | 4403 | 0.0041584 | 2.55e-05 | 163.0741
AEP-AP | 2025 | 1058812 | PARTIAL POWER | EQF | SPLICE, OH | 5 | 7 | 1248 | 0.0011787 | 6.6112e-06 | 178.2857
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | ARRESTER | 3 | 23 | 9160 | 0.0086512 | 2.1722e-05 | 398.2609
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 9 | 1440 | 0.00136 | 8.5001e-06 | 160
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | ARRESTER | 11 | 1398 | 184814 | 0.17455 | 0.0013203 | 132.1989
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 1466 | 0.0013846 | 9.4445e-07 | 1466
AEP-AP | 2025 | 1058812 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 1272 | 0.0012013 | 9.4445e-07 | 1272
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | POLE HARDWARE | 2 | 1142 | 182132 | 0.17202 | 0.0010786 | 159.4851
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 8 | 6317 | 949536 | 0.89679 | 0.0059661 | 150.3144
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FO | POLE | 1 | 11 | 5236 | 0.0049452 | 1.0389e-05 | 476
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 1 | 86 | 8.1223e-05 | 9.4445e-07 | 86
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 49 | 4655 | 0.004425 | 4.6579e-05 | 95
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | FUSE | 189 | 1078 | 140107 | 0.13318 | 0.0010247 | 129.9694
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | CAPACITOR | 1 | 584 | 51392 | 0.048724 | 0.00055368 | 88
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | POLE | 2 | 101 | 17691 | 0.016782 | 9.5808e-05 | 175.1584
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | O | FUSE | 12 | 127 | 29770 | 0.028225 | 0.00012041 | 234.4094
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | CROSSARM | 15 | 4561 | 477466 | 0.45198 | 0.0043176 | 104.6845
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | CONN/CLAMP | 7 | 16 | 8160 | 0.0077364 | 1.5169e-05 | 510
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WT | FUSE | 1 | 3 | 915 | 0.0008675 | 2.8443e-06 | 305
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | SPLICE, OH | 2 | 2 | 1294 | 0.0012301 | 1.9012e-06 | 647
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 3 | 504 | 0.00047809 | 2.8458e-06 | 168
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | V | METERING | 9 | 9 | 1196 | 0.0011345 | 8.5373e-06 | 132.8889
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CE | POLE | 2 | 18 | 4594 | 0.0043555 | 1.7066e-05 | 255.2222
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | PEDESTAL | 6 | 43 | 15410 | 0.014648 | 4.0875e-05 | 358.3721
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 89 | 1955 | 316663 | 0.29976 | 0.0018507 | 161.976
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 53 | 772 | 186558 | 0.1766 | 0.0007308 | 241.6554
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 100 | 888 | 105234 | 0.099389 | 0.00083868 | 118.5068
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | POLE | 384 | 27214 | 5730240 | 5.412 | 0.025702 | 210.5622
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | CROSSARM | 181 | 56415 | 9109637 | 8.6036 | 0.053281 | 161.4754
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 340 | 1064 | 106482 | 0.10057 | 0.0010049 | 100.0771
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | U | NONE | 16 | 9943 | 1177086 | 1.1143 | 0.0094124 | 118.3834
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FW | NONE | 25 | 713 | 41921 | 0.039684 | 0.00067495 | 58.7952
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | POLE | 2 | 30 | 5091 | 0.0048193 | 2.8399e-05 | 169.7
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | FUSE | 447 | 3925 | 930254 | 0.87858 | 0.003707 | 237.0074
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 19 | 1124 | 85451 | 0.080705 | 0.0010616 | 76.024
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 84 | 2091 | 450557 | 0.42553 | 0.0019749 | 215.4744
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | FO | NONE | 7 | 395 | 71038 | 0.067247 | 0.00037392 | 179.843
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | REGULATOR | 8 | 2999 | 101305 | 0.095899 | 0.002839 | 33.7796
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 19 | 2831 | 0.0026799 | 1.7986e-05 | 149
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | ARRESTER | 5 | 15 | 2115 | 0.0019975 | 1.4167e-05 | 141
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | CUTOUT | 12 | 37 | 57290 | 0.054108 | 3.4945e-05 | 1548.3784
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 1 | 234 | 0.000221 | 9.4445e-07 | 234
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | OTHER EQUIPMENT | 1 | 1 | 258 | 0.00024367 | 9.4445e-07 | 258
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 3 | 1371 | 0.0012978 | 2.8399e-06 | 457
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | CROSSARM | 16 | 4430 | 525472 | 0.49628 | 0.0041839 | 118.6167
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VIN | FUSE | 23 | 101 | 12818 | 0.012106 | 9.539e-05 | 126.9109
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 6 | 106 | 47207 | 0.044585 | 0.00010011 | 445.3491
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 49 | 767 | 1277767 | 1.2068 | 0.0007244 | 1665.9283
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 65 | 6890 | 0.0065073 | 6.139e-05 | 106
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | TIN | NONE | 4 | 1949 | 142585 | 0.13467 | 0.0018407 | 73.158
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ERF | INSULATOR | 1 | 1 | 181 | 0.00017095 | 9.4445e-07 | 181
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | INSULATOR | 2 | 2 | 231 | 0.00021958 | 1.9012e-06 | 115.5
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | CROSSARM | 3 | 854 | 206867 | 0.19538 | 0.00080656 | 242.233
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 2 | 8 | 510 | 0.00048278 | 7.5731e-06 | 63.75
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 3 | 861 | 0.00081318 | 2.8334e-06 | 287
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 13 | 1014 | 0.00095989 | 1.2306e-05 | 78
AEP-AP | 2025 | 1058812 | PARTIAL POWER | TR | NONE | 1 | 5 | 259 | 0.00024461 | 4.7223e-06 | 51.8
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 3 | 10 | 3933 | 0.0037145 | 9.4445e-06 | 393.3
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 4 | 1305 | 0.0012325 | 3.7778e-06 | 326.25
AEP-AP | 2025 | 1058812 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 6 | 33 | 13050 | 0.012325 | 3.1167e-05 | 395.4545
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | POLE | 2 | 161 | 8458 | 0.0079882 | 0.00015206 | 52.5342
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | WI | CONDUCTOR OVERHEAD | 1 | 28 | 14560 | 0.013751 | 2.6445e-05 | 520
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 1 | 220 | 0.00020913 | 9.5058e-07 | 220
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 2 | 46 | 4.3545e-05 | 1.8933e-06 | 23
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | METERING | 1 | 1 | 20 | 1.8972e-05 | 9.4859e-07 | 20
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 4 | 296 | 0.0002802 | 3.7865e-06 | 74
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 220 | 159720 | 0.15143 | 0.00020858 | 726
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | TRANSFORMER, GROUNDING | 1 | 1 | 22 | 2.0869e-05 | 9.4859e-07 | 22
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 3 | 24 | 2.2667e-05 | 2.8334e-06 | 8
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TOR | FUSE | 1 | 2 | 290 | 0.00027452 | 1.8933e-06 | 145
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | WL | RELAY | 2 | 606 | 199044 | 0.18799 | 0.00057234 | 328.4554
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 4 | 396 | 0.00037643 | 3.8023e-06 | 99
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | NONE | 2781 | 40411 | 7238420 | 6.8627 | 0.038313 | 179.12
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1650 | 53337 | 9311041 | 8.8277 | 0.050568 | 174.57
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 406 | 1384 | 152193 | 0.14407 | 0.0013101 | 109.966
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | FUSE | 8 | 76 | 10268 | 0.00972 | 7.1944e-05 | 135.1053
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 8 | 7296 | 580215 | 0.55154 | 0.0069355 | 79.5251
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CO | CONDUCTOR UG | 5 | 25 | 13915 | 0.0132 | 2.3715e-05 | 556.6
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | FUSE | 486 | 5569 | 1398148 | 1.3235 | 0.0052718 | 251.0591
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | METERING | 3 | 5 | 947 | 0.00089832 | 4.743e-06 | 189.4
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | CABLE TERMINATOR | 12 | 19 | 6787 | 0.0064381 | 1.8023e-05 | 357.2105
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 3 | 811 | 96509 | 0.09174 | 0.00077092 | 119
AEP-AP | 2023 | 1056376 | PARTIAL POWER | ERF | NONE | 1 | 0 | 0 | 0 | 0
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | CUTOUT | 342 | 1676 | 108809 | 0.10277 | 0.0015829 | 64.9218
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | NONE | 1534 | 57009 | 9646077 | 9.1103 | 0.053842 | 169.2027
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | ARRESTER | 4 | 55 | 49209 | 0.046583 | 5.2065e-05 | 894.7091
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | F | FUSE | 2 | 35 | 15231 | 0.014448 | 3.3201e-05 | 435.1714
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 5 | 8 | 1044 | 0.00099241 | 7.6047e-06 | 130.5
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | F | CUTOUT | 2 | 16 | 821 | 0.0007754 | 1.5111e-05 | 51.3125
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | POLE | 3 | 14 | 14613 | 0.013891 | 1.3308e-05 | 1043.7857
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | TRANSFORMER, POWER - NON LTC | 5 | 3441 | 694827 | 0.65775 | 0.0032574 | 201.9259
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 8 | 1044 | 0.00098828 | 7.5731e-06 | 130.5
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | CUTOUT | 6 | 16 | 2426 | 0.0022965 | 1.5146e-05 | 151.625
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 314 | 335122 | 0.31724 | 0.00029724 | 1067.2675
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 23 | 8211 | 0.0077728 | 2.1773e-05 | 357
AEP-AP | 2023 | 1056376 | SUBTRANSMISSION LINE | WU | NONE | 6 | 4506 | 58578 | 0.055452 | 0.0042655 | 13
AEP-AP | 2023 | 1056376 | PARTIAL POWER | WU | NONE | 10 | 28 | 5270 | 0.0049888 | 2.6506e-05 | 188.2143
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 6 | 408 | 0.00038682 | 5.6885e-06 | 68
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 17 | 1.6126e-05 | 9.4859e-07 | 17
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 5 | 222 | 54566 | 0.051535 | 0.00020967 | 245.7928
AEP-AP | 2023 | 1056376 | PARTIAL POWER | ABI | FUSE | 1 | 2 | 128 | 0.00012117 | 1.8933e-06 | 64
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | CUTOUT | 3 | 6 | 1655 | 0.0015631 | 5.6667e-06 | 275.8333
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 8 | 157 | 12359 | 0.011673 | 0.00014828 | 78.7197
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | CONN/CLAMP | 6 | 331 | 25839 | 0.024404 | 0.00031261 | 78.0634
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 39 | 2593 | 1243784 | 1.1747 | 0.002449 | 479.6699
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 12 | 3497 | 0.0033028 | 1.1333e-05 | 291.4167
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 6 | 189 | 152911 | 0.14442 | 0.0001785 | 809.0529
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | PEDESTAL | 4 | 50 | 1972 | 0.0018625 | 4.7223e-05 | 39.44
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 760 | 42797 | 0.04042 | 0.00071779 | 56.3118
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | POLE | 4 | 1367 | 616017 | 0.5818 | 0.0012911 | 450.6342
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | FUSE | 20 | 65 | 99296 | 0.093781 | 6.139e-05 | 1527.6308
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 17 | 686 | 0.0006521 | 1.616e-05 | 40.3529
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | WW | NONE | 1 | 273 | 92274 | 0.087149 | 0.00025784 | 338
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | INSULATOR | 1 | 208 | 62368 | 0.059162 | 0.00019731 | 299.8462
AEP-AP | 2021 | 1054192 | SUBTRANSMISSION LINE | WI | NONE | 1 | 953 | 81958 | 0.077745 | 0.00090401 | 86
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | WU | NONE | 6 | 2252 | 221241 | 0.21031 | 0.0021407 | 98.242
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | SCO | NONE | 4 | 2078 | 1287736 | 1.2215 | 0.0019712 | 619.6997
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | ARRESTER | 1 | 1 | 7 | 6.6112e-06 | 9.4445e-07 | 7
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 1168 | 237507 | 0.22483 | 0.0011057 | 203.345
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | CAPACITOR | 2 | 19 | 16930 | 0.016093 | 1.8061e-05 | 891.0526
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CE | METERING | 2 | 11 | 510 | 0.00048167 | 1.0389e-05 | 46.3636
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | TIR | NONE | 16 | 16288 | 1274728 | 1.2039 | 0.015383 | 78.2618
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 4 | 3799 | 386985 | 0.36549 | 0.003588 | 101.865
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 18 | 198 | 0.000187 | 1.7e-05 | 11
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | POLE | 4 | 131 | 12011 | 0.011344 | 0.00012372 | 91.687
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 404 | 46930 | 0.044425 | 0.00038244 | 116.1634
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 1 | 14 | 3318 | 0.0031337 | 1.3222e-05 | 237
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | GUY/ANCHOR | 2 | 4 | 264 | 0.00024934 | 3.7778e-06 | 66
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 1 | 210 | 0.00019962 | 9.5058e-07 | 210
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 1 | 275 | 0.00026032 | 9.4663e-07 | 275
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 8 | 280 | 0.00026616 | 7.6047e-06 | 35
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | UG | POLE | 1 | 2 | 438 | 0.00041548 | 1.8972e-06 | 219
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | WL | NONE | 1 | 790 | 161950 | 0.15331 | 0.00074784 | 205
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | EQF | CONDUCTOR UG | 2 | 0 | 0 | 0 | 0
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 6 | 6141 | 705277 | 0.66764 | 0.0058133 | 114.8473
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 861 | 139584 | 0.13241 | 0.00081674 | 162.1185
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | INSULATOR | 4 | 78 | 43520 | 0.041283 | 7.399e-05 | 557.9487
AEP-AP | 2020 | 1051986 | PARTIAL POWER | ERF | NONE | 10 | 15 | 2023 | 0.001923 | 1.4259e-05 | 134.8667
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 5 | 76 | 6906 | 0.006551 | 7.2093e-05 | 90.8684
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | REGULATOR | 2 | 240 | 50655 | 0.048026 | 0.00022754 | 211.0625
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | CUTOUT | 12 | 1659 | 465828 | 0.44281 | 0.001577 | 280.7884
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | METERING | 3 | 3 | 297 | 0.00028115 | 2.8399e-06 | 99
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 173 | 6390 | 2298690 | 2.171 | 0.0060351 | 359.7324
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 1 | 1106 | 0.0010486 | 9.4809e-07 | 1106
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | V | POLE HARDWARE | 1 | 1 | 201 | 0.00019057 | 9.4809e-07 | 201
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | CONN/CLAMP | 4 | 9 | 2314 | 0.0021905 | 8.5197e-06 | 257.1111
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | POLE HARDWARE | 4 | 620 | 162194 | 0.15354 | 0.00058691 | 261.6032
AEP-AP | 2024 | 1058812 | PARTIAL POWER | VIN | NONE | 5 | 7 | 1149 | 0.0010852 | 6.6112e-06 | 164.1429
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | FUSE | 207 | 1740 | 523549 | 0.49447 | 0.0016434 | 300.8902
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | METERING | 73 | 138 | 13672 | 0.012913 | 0.00013033 | 99.0725
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 140 | 23520 | 0.022265 | 0.00013253 | 168
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ABI | POLE | 3 | 1126 | 146982 | 0.13914 | 0.0010659 | 130.5346
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | OV | NONE | 1 | 82 | 12382 | 0.011745 | 7.7785e-05 | 151
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | POLE | 4 | 1407 | 139811 | 0.13255 | 0.001334 | 99.3682
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | SPLICE, OH | 6 | 11 | 2038 | 0.0019248 | 1.0389e-05 | 185.2727
AEP-AP | 2024 | 1058812 | PARTIAL POWER | U | FUSE | 16 | 36 | 3038 | 0.0028693 | 3.4e-05 | 84.3889
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | METERING | 34 | 48 | 7944 | 0.0075027 | 4.5334e-05 | 165.5
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | NONE | 350 | 2620 | 197671 | 0.18669 | 0.0024745 | 75.4469
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 10 | 35 | 5649 | 0.0053352 | 3.3056e-05 | 161.4
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | SPLICE, OH | 36 | 939 | 145815 | 0.13772 | 0.00088684 | 155.2875
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 4 | 140 | 0.00013222 | 3.7778e-06 | 35
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | CUTOUT | 18 | 255 | 82275 | 0.077705 | 0.00024084 | 322.6471
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OU | POLE | 2 | 240 | 133335 | 0.12593 | 0.00022667 | 555.5625
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 1 | 363 | 0.00034284 | 9.4445e-07 | 363
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | EQF | ARRESTER | 1 | 45 | 3375 | 0.0031875 | 4.25e-05 | 75
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 268 | 0.0002537 | 9.4663e-07 | 268
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 26 | 22958 | 0.021766 | 2.465e-05 | 883
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | EQF | RELAY | 3 | 2327 | 1011663 | 0.95547 | 0.0021977 | 434.7499
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 2 | 19 | 868 | 0.00081979 | 1.7945e-05 | 45.6842
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 555 | 0.00052538 | 9.4663e-07 | 555
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 107 | 14507 | 0.01379 | 0.00010171 | 135.5794
AEP-AP | 2025 | 1058812 | PARTIAL POWER | TIR | NONE | 2 | 2 | 67 | 6.3278e-05 | 1.8889e-06 | 33.5
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | SPLICE, UG | 1 | 1 | 91 | 8.5945e-05 | 9.4445e-07 | 91
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | METERING | 1 | 1 | 118 | 0.00011145 | 9.4445e-07 | 118
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | F | FUSE | 3 | 12 | 1862 | 0.0017586 | 1.1333e-05 | 155.1667
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WI | METERING | 1 | 1 | 124 | 0.00011711 | 9.4445e-07 | 124
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 9 | 351 | 0.0003315 | 8.5001e-06 | 39
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | POLE HARDWARE | 2 | 6 | 3394 | 0.0032055 | 5.6667e-06 | 565.6667
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | FW | POLE | 2 | 3 | 380 | 0.00035972 | 2.8399e-06 | 126.6667
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 142 | 46588 | 0.044 | 0.00013411 | 328.0845
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 38 | 17363 | 0.016436 | 3.5972e-05 | 456.9211
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 2 | 522 | 343326 | 0.32426 | 0.00049301 | 657.7126
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | F | CUTOUT | 2 | 403 | 58420 | 0.055533 | 0.00038308 | 144.9628
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | ARRESTER | 1 | 1 | 99 | 9.4108e-05 | 9.5058e-07 | 99
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CO | FUSE | 1 | 2 | 136 | 0.00012894 | 1.8962e-06 | 68
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 208 | 10816 | 0.01026 | 0.00019731 | 52
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | EQF | SWITCH, OH | 1 | 2057 | 460768 | 0.43517 | 0.0019427 | 224
AEP-AP | 2022 | 1054752 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 2 | 566 | 0.00053662 | 1.8962e-06 | 283
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 14 | 4228 | 0.0040107 | 1.328e-05 | 302
AEP-AP | 2021 | 1054192 | PARTIAL POWER | FO | NONE | 1 | 6 | 54 | 5.1224e-05 | 5.6916e-06 | 9
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 134 | 3752 | 0.0035591 | 0.00012711 | 28
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 43 | 9288 | 0.008829 | 4.0875e-05 | 216
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1 | 270 | 0.00025598 | 9.4809e-07 | 270
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | U | CONDUCTOR OVERHEAD | 1 | 53 | 19907 | 0.018801 | 5.0056e-05 | 375.6038
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 39 | 6006 | 0.0057092 | 3.7073e-05 | 154
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | O | ARRESTER | 1 | 2 | 150 | 0.00014199 | 1.8933e-06 | 75
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 1 | 118 | 0.00011145 | 9.4445e-07 | 118
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 42 | 13188 | 0.012455 | 3.9667e-05 | 314
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | CUTOUT | 3 | 23 | 2800 | 0.0026445 | 2.1722e-05 | 121.7391
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | ARRESTER | 7 | 12307 | 2651931 | 2.5143 | 0.011668 | 215.4815
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 29 | 16948 | 0.016068 | 2.7495e-05 | 584.4138
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 2 | 1492 | 0.0014146 | 1.8962e-06 | 746
AEP-AP | 2020 | 1051986 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 223 | 0.00021198 | 9.5058e-07 | 223
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | O | CUTOUT | 1 | 93 | 92652 | 0.087707 | 8.8037e-05 | 996.2581
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 122 | 42368 | 0.04019 | 0.00011573 | 347.2787
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 5 | 850 | 0.0008063 | 4.743e-06 | 170
AEP-AP | 2020 | 1051986 | SUBTRANSMISSION LINE | EQF | INSULATOR | 2 | 12 | 1692 | 0.0016084 | 1.1407e-05 | 141
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | RELAY | 6 | 594 | 68310 | 0.064798 | 0.00056346 | 115
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | F | CUTOUT | 2 | 225 | 41790 | 0.039642 | 0.00021343 | 185.7333
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | EQF | MOAB | 3 | 1189 | 10956 | 0.010393 | 0.0011279 | 9.2145
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | BREAKER | 1 | 1 | 174 | 0.00016506 | 9.4859e-07 | 174
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | ERF | OTHER EQUIPMENT | 4 | 4008 | 185314 | 0.17502 | 0.0037854 | 46.236
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 1 | 45 | 4.25e-05 | 9.4445e-07 | 45
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 195 | 60567 | 0.057574 | 0.00018536 | 310.6
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | NONE | 202 | 12325 | 1133069 | 1.0748 | 0.011691 | 91.9326
AEP-AP | 2022 | 1054752 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 26 | 51 | 43092 | 0.040855 | 4.8353e-05 | 844.9412
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 43 | 6966 | 889186 | 0.84348 | 0.0066079 | 127.6466
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | CUTOUT | 18 | 267 | 84346 | 0.079968 | 0.00025314 | 315.9026
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 24 | 925 | 138146 | 0.13097 | 0.00087698 | 149.347
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 562 | 101972 | 0.096679 | 0.00053283 | 181.4448
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 79 | 10270 | 0.0097369 | 7.4899e-05 | 130
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | CROSSARM | 22 | 3577 | 467065 | 0.44305 | 0.0033931 | 130.5745
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | V | NONE | 72 | 8028 | 1017659 | 0.96737 | 0.0076313 | 126.7637
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 26 | 4281 | 801841 | 0.76222 | 0.0040694 | 187.3023
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | OU | NONE | 37 | 3070 | 382273 | 0.36338 | 0.0029183 | 124.5189
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 126 | 3309 | 0.0031389 | 0.00011952 | 26.2619
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 9 | 1867 | 301890 | 0.28637 | 0.001771 | 161.6979
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | ARRESTER | 6 | 212 | 97290 | 0.092289 | 0.0002011 | 458.9151
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | WL | NONE | 9 | 4740 | 3026464 | 2.8709 | 0.0044963 | 638.4945
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WFS | POLE | 6 | 224 | 126550 | 0.1203 | 0.00021293 | 564.9554
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 7 | 763 | 0.00072339 | 6.6366e-06 | 109
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 2 | 104 | 66389 | 0.063108 | 9.8861e-05 | 638.3558
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | INSULATOR | 3 | 11 | 867 | 0.00082243 | 1.0435e-05 | 78.8182
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | INSULATOR | 4 | 506 | 115969 | 0.10995 | 0.00047973 | 229.1877
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | FUSE | 69 | 555 | 77567 | 0.073259 | 0.00052417 | 139.7604
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | AB | NONE | 6 | 2627 | 494605 | 0.46821 | 0.0024868 | 188.2775
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | SPLICE, OH | 83 | 2999 | 348529 | 0.32917 | 0.0028324 | 116.2151
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 10 | 3140 | 1254283 | 1.1873 | 0.0029724 | 399.4532
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 2 | 68 | 20678 | 0.019529 | 6.4223e-05 | 304.0882
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | REGULATOR | 1 | 635 | 138734 | 0.13133 | 0.00060111 | 218.4787
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | REGULATOR | 8 | 1348 | 53656 | 0.050898 | 0.0012787 | 39.8042
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | FUSE | 19 | 42 | 4639 | 0.0043813 | 3.9667e-05 | 110.4524
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | CUTOUT | 53 | 653 | 58851 | 0.055582 | 0.00061673 | 90.124
AEP-AP | 2023 | 1056376 | PARTIAL POWER | O | CONN/CLAMP | 3 | 10 | 1678 | 0.0015884 | 9.4663e-06 | 167.8
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 2 | 197 | 22346 | 0.021197 | 0.00018687 | 113.4315
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 5 | 3739 | 0.0035468 | 4.743e-06 | 747.8
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 9 | 19 | 1080 | 0.00102 | 1.7945e-05 | 56.8421
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 1214 | 234037 | 0.22104 | 0.0011466 | 192.7817
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | POLE | 2 | 21 | 5142 | 0.0048564 | 1.9834e-05 | 244.8571
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 34 | 510 | 0.00048167 | 3.2111e-05 | 15
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 14 | 715 | 79161 | 0.074764 | 0.00067529 | 110.7147
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | BE | OTHER EQUIPMENT | 2 | 0 | 0 | 0 | 0
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | SCO | NONE | 11 | 6609 | 1007374 | 0.95142 | 0.0062419 | 152.4246
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WU | SPLICE, OH | 1 | 2 | 5586 | 0.0052757 | 1.8889e-06 | 2793
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 2 | 1852 | 0.0017568 | 1.8972e-06 | 926
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 4 | 216 | 0.000204 | 3.7778e-06 | 54
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 7 | 1843 | 0.0017406 | 6.6112e-06 | 263.2857
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | ARRESTER | 8 | 202 | 25926 | 0.024486 | 0.00019078 | 128.3465
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 464 | 6032 | 0.005697 | 0.00043823 | 13
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | VA | NONE | 1 | 1 | 60 | 5.6798e-05 | 9.4663e-07 | 60
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 24 | 698 | 0.00066075 | 2.2719e-05 | 29.0833
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 1 | 203 | 0.00019172 | 9.4445e-07 | 203
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | VA | NONE | 4 | 928 | 191883 | 0.18122 | 0.00087645 | 206.7705
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | POLE HARDWARE | 1 | 8 | 11920 | 0.011258 | 7.5556e-06 | 1490
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | METERING | 4 | 5 | 986 | 0.00093338 | 4.7332e-06 | 197.2
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 7 | 11557 | 0.010915 | 6.6112e-06 | 1651
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | VA | STATIC WIRE | 1 | 8 | 4000 | 0.0037778 | 7.5556e-06 | 500
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 33 | 3370 | 688111 | 0.65239 | 0.0031951 | 204.1872
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | CONN/CLAMP | 64 | 266 | 44143 | 0.041852 | 0.00025219 | 165.9511
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 9 | 118 | 14651 | 0.01389 | 0.00011187 | 124.161
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | CROSSARM | 41 | 3369 | 528790 | 0.50134 | 0.0031941 | 156.9576
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 62 | 140 | 85024 | 0.080653 | 0.0001328 | 607.3143
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WL | NONE | 4 | 11 | 6396 | 0.006064 | 1.0429e-05 | 581.4545
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | NONE | 2029 | 69858 | 18311426 | 17.4065 | 0.066406 | 262.1235
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 17 | 2438 | 0.0023175 | 1.616e-05 | 143.4118
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 3109 | 1071232 | 1.0162 | 0.0029492 | 344.5584
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 3 | 4 | 5864 | 0.0055742 | 3.8023e-06 | 1466
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 3 | 5 | 3213 | 0.0030478 | 4.743e-06 | 642.6
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | CROSSARM | 6 | 2306 | 229168 | 0.21739 | 0.0021875 | 99.379
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WT | NONE | 3 | 198 | 90077 | 0.085446 | 0.00018782 | 454.9343
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | NONE | 1072 | 32112 | 7411748 | 7.0162 | 0.030398 | 230.8093
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 11 | 1954 | 0.0018536 | 1.0435e-05 | 177.6364
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 31 | 1457 | 0.001385 | 2.9468e-05 | 47
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 4 | 177 | 115930 | 0.10997 | 0.0001679 | 654.9718
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 156 | 0.0001479 | 9.4809e-07 | 156
AEP-AP | 2023 | 1056376 | PARTIAL POWER | VIN | FUSE | 2 | 2 | 198 | 0.00018743 | 1.8933e-06 | 99
AEP-AP | 2020 | 1051986 | PARTIAL POWER | WU | NONE | 23 | 90 | 28325 | 0.026925 | 8.5552e-05 | 314.7222
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | EQF | ARRESTER | 9 | 5968 | 848987 | 0.80492 | 0.0056582 | 142.2565
AEP-AP | 2023 | 1056376 | PARTIAL POWER | U | NONE | 26 | 66 | 7952 | 0.0075276 | 6.2478e-05 | 120.4848
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 11 | 111 | 14099 | 0.013347 | 0.00010508 | 127.018
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 5 | 23 | 4468 | 0.0042296 | 2.1773e-05 | 194.2609
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 9 | 117 | 0.00011099 | 8.5373e-06 | 13
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | TRANSFORMER, GROUNDING | 3 | 1836 | 1063585 | 1.0068 | 0.001738 | 579.2947
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | TR | NONE | 9 | 4262 | 1201847 | 1.1401 | 0.0040429 | 281.9913
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | A | NONE | 11 | 5618 | 679540 | 0.64179 | 0.0053059 | 120.9576
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TOR | NONE | 14 | 35 | 15109 | 0.014303 | 3.3132e-05 | 431.6857
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | REGULATOR | 1 | 552 | 79065 | 0.075158 | 0.00052472 | 143.2337
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 4 | 1592 | 97321 | 0.092512 | 0.0015133 | 61.1313
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | POLE | 14 | 4693 | 1004969 | 0.95134 | 0.0044425 | 214.1421
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | FUSE | 301 | 1210 | 223949 | 0.21151 | 0.0011428 | 185.0818
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | CUTOUT | 7 | 51 | 25310 | 0.023959 | 4.8278e-05 | 496.2745
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 1556 | 39891 | 0.037762 | 0.001473 | 25.6369
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OL | NONE | 6 | 332 | 22549 | 0.021346 | 0.00031428 | 67.9187
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 3 | 297 | 131803 | 0.12477 | 0.00028115 | 443.7811
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WL | INSULATOR | 8 | 3586 | 458219 | 0.43377 | 0.0033946 | 127.78
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 103 | 16418 | 0.015506 | 9.7279e-05 | 159.3981
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 251 | 11295 | 0.010714 | 0.0002381 | 45
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | F | POLE | 2 | 329 | 36810 | 0.034991 | 0.00031274 | 111.8845
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 1 | 1556 | 0.001473 | 9.4663e-07 | 1556
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | TR | NONE | 15 | 10294 | 750767 | 0.71367 | 0.0097853 | 72.9325
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | NONE | 974 | 56987 | 13979646 | 13.2031 | 0.053822 | 245.3129
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 41 | 1700 | 477666 | 0.45113 | 0.0016056 | 280.98
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | AB | NONE | 7 | 5168 | 881314 | 0.83236 | 0.0048809 | 170.5329
AEP-AP | 2025 | 1058812 | PARTIAL POWER | U | FUSE | 3 | 10 | 2689 | 0.0025396 | 9.4445e-06 | 268.9
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 29 | 4092 | 0.0038647 | 2.7389e-05 | 141.1034
AEP-AP | 2020 | 1051986 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 4 | 4 | 786 | 0.00074716 | 3.8023e-06 | 196.5
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 11 | 2453 | 0.0023269 | 1.0435e-05 | 223
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | FUSE | 5 | 22 | 10581 | 0.0099933 | 2.0778e-05 | 480.9545
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | UG | NONE | 3 | 12 | 1273 | 0.0012023 | 1.1333e-05 | 106.0833
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 7 | 399 | 0.00037829 | 6.6366e-06 | 57
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 3 | 1179 | 0.0011135 | 2.8334e-06 | 393
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | OU | GUY/ANCHOR | 1 | 1 | 278 | 0.00026371 | 9.4859e-07 | 278
AEP-AP | 2023 | 1056376 | SUBTRANSMISSION LINE | U | NONE | 4 | 3494 | 171206 | 0.16207 | 0.0033075 | 49
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 5 | 6 | 289 | 0.00027295 | 5.6667e-06 | 48.1667
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WW | CONN/CLAMP | 4 | 327 | 43973 | 0.041531 | 0.00030884 | 134.474
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 1 | 906 | 0.00085568 | 9.4445e-07 | 906
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 55 | 5.1945e-05 | 9.4445e-07 | 55
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | AB | NONE | 2 | 756 | 69525 | 0.065663 | 0.00071401 | 91.9643
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 906 | 30804 | 0.029093 | 0.00085568 | 34
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | INSULATOR | 4 | 8 | 533 | 0.00050339 | 7.5556e-06 | 66.625
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | EQF | POLE | 1 | 189 | 18333 | 0.017315 | 0.0001785 | 97
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 2 | 6 | 12436 | 0.011745 | 5.6667e-06 | 2072.6667
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WI | ARRESTER | 1 | 2 | 150 | 0.00014167 | 1.8889e-06 | 75
AEP-AP | 2023 | 1056376 | PARTIAL POWER | U | FUSE | 6 | 36 | 2321 | 0.0021971 | 3.4079e-05 | 64.4722
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | NONE | 7310 | 375526 | 109857527 | 104.2102 | 0.35622 | 292.5431
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | CROSSARM | 161 | 43501 | 18605661 | 17.6398 | 0.041243 | 427.7065
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | NONE | 1228 | 46529 | 13729985 | 13.0173 | 0.044114 | 295.0845
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 43 | 13676 | 2348065 | 2.2262 | 0.012966 | 171.6924
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 8 | 94 | 27820 | 0.026376 | 8.912e-05 | 295.9574
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | ARRESTER | 293 | 27352 | 3653498 | 3.4657 | 0.025946 | 133.5733
AEP-AP | 2022 | 1054752 | PARTIAL POWER | ABI | NONE | 7 | 8 | 824 | 0.00078123 | 7.5847e-06 | 103
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | POLE | 16 | 721 | 290289 | 0.27522 | 0.00068357 | 402.62
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | R | NONE | 3 | 4003 | 656492 | 0.62241 | 0.0037952 | 164
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VIN | NONE | 1403 | 9661 | 1676699 | 1.5938 | 0.0091836 | 173.5534
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 31 | 4838 | 1564200 | 1.483 | 0.0045869 | 323.3154
AEP-AP | 2022 | 1054752 | PARTIAL POWER | TIR | NONE | 9 | 102 | 14409 | 0.013661 | 9.6705e-05 | 141.2647
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | SPLICE, OH | 18 | 23 | 4198 | 0.0039905 | 2.1863e-05 | 182.5217
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | ARRESTER | 313 | 23546 | 3371720 | 3.2051 | 0.022382 | 143.1971
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | NONE | 831 | 9921 | 1317721 | 1.2526 | 0.0094307 | 132.8214
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | INSULATOR | 18 | 1305 | 356773 | 0.33843 | 0.0012379 | 273.3893
AEP-AP | 2021 | 1054192 | TRANSMISSION STATION | SCO | NONE | 3 | 3782 | 54957 | 0.052132 | 0.0035876 | 14.5312
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 5 | 581 | 23861 | 0.022622 | 0.00055084 | 41.0688
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | FUSE | 64 | 568 | 91882 | 0.087341 | 0.00053993 | 161.7641
AEP-AP | 2022 | 1054752 | PARTIAL POWER | CO | CONDUCTOR UG | 3 | 20 | 15860 | 0.015037 | 1.8962e-05 | 793
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ERF | POLE | 1 | 584 | 36208 | 0.034347 | 0.00055398 | 62
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 61 | 15737 | 0.01492 | 5.7834e-05 | 257.9836
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 1 | 145 | 0.00013747 | 9.4809e-07 | 145
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | METERING | 15 | 45 | 12709 | 0.012081 | 4.2776e-05 | 282.4222
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | SCO | NONE | 8 | 4942 | 525654 | 0.49863 | 0.004688 | 106.3646
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WFS | POLE | 16 | 1185 | 1054649 | 1.0004 | 0.0011241 | 889.9992
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | ARRESTER | 5 | 42 | 6589 | 0.0062503 | 3.9841e-05 | 156.881
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | BREAKER | 5 | 66 | 29331 | 0.027823 | 6.2607e-05 | 444.4091
AEP-AP | 2022 | 1054752 | PARTIAL POWER | ERF | NONE | 1 | 5 | 2590 | 0.0024556 | 4.7405e-06 | 518
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | ARRESTER | 9 | 16 | 2277 | 0.0021588 | 1.5169e-05 | 142.3125
AEP-AP | 2022 | 1054752 | DISTRIBUTION SOURCE | EQF | INSULATOR | 1 | 1084 | 53116 | 0.050359 | 0.0010277 | 49
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | FUSE | 1271 | 10529 | 1442150 | 1.362 | 0.0099442 | 136.9693
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | NONE | 429 | 7408 | 1433861 | 1.3542 | 0.0069965 | 193.5558
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | AO | NONE | 3 | 374 | 160756 | 0.15249 | 0.00035477 | 429.8289
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 358 | 175774 | 0.16709 | 0.00034031 | 490.9888
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 1 | 34 | 4454 | 0.0042339 | 3.232e-05 | 131
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | NONE | 266 | 15216 | 1688634 | 1.5948 | 0.014371 | 110.9775
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 7 | 36 | 10975 | 0.010389 | 3.4079e-05 | 304.8611
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | POLE | 14 | 640 | 414209 | 0.3921 | 0.00060584 | 647.2016
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WU | REGULATOR | 1 | 257 | 98431 | 0.093178 | 0.00024328 | 383
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 1 | 1 | 207 | 0.0001955 | 9.4445e-07 | 207
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | CUTOUT | 15 | 307 | 73933 | 0.069987 | 0.00029062 | 240.8241
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 3 | 4 | 1375 | 0.0013043 | 3.7944e-06 | 343.75
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | POLE HARDWARE | 2 | 256 | 203512 | 0.19221 | 0.00024178 | 794.9688
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SO | NONE | 6 | 21 | 4847 | 0.0045778 | 1.9834e-05 | 230.8095
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | A | INSULATOR | 3 | 234 | 108238 | 0.10223 | 0.000221 | 462.5556
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WI | NONE | 14 | 153 | 108739 | 0.1027 | 0.0001445 | 710.7124
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 9 | 3253 | 512509 | 0.48718 | 0.0030922 | 157.5496
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WFS | NONE | 18 | 1649 | 279498 | 0.26397 | 0.0015574 | 169.4955
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | POLE | 132 | 23229 | 5629016 | 5.3164 | 0.021939 | 242.3271
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | CROSSARM | 73 | 19598 | 3340086 | 3.1546 | 0.018509 | 170.4299
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | U | CONDUCTOR UG | 13 | 55 | 20573 | 0.01943 | 5.1945e-05 | 374.0545
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | CROSSARM | 62 | 20185 | 5998292 | 5.6651 | 0.019064 | 297.1658
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WI | NONE | 2 | 6 | 7323 | 0.0069162 | 5.6667e-06 | 1220.5
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 20 | 142 | 72998 | 0.068943 | 0.00013411 | 514.0704
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CE | FUSE | 4 | 6 | 965 | 0.0009114 | 5.6667e-06 | 160.8333
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | POLE | 21 | 1714 | 558951 | 0.5279 | 0.0016188 | 326.1091
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | F | CUTOUT | 3 | 86 | 21404 | 0.020215 | 8.1223e-05 | 248.8837
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 2 | 2554 | 0.0024227 | 1.8972e-06 | 1277
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | U | NONE | 3 | 321 | 56001 | 0.053234 | 0.00030514 | 174.4579
AEP-AP | 2025 | 1058812 | PARTIAL POWER | FO | NONE | 1 | 17 | 1360 | 0.0012845 | 1.6056e-05 | 80
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | V | GUY/ANCHOR | 1 | 1 | 17 | 1.6126e-05 | 9.4859e-07 | 17
AEP-AP | 2020 | 1051986 | SUBTRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 1 | 463 | 0.00044012 | 9.5058e-07 | 463
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | ARRESTER | 4 | 36 | 46630 | 0.044233 | 3.4149e-05 | 1295.2778
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 8 | 7056 | 0.0066794 | 7.5731e-06 | 882
AEP-AP | 2023 | 1056376 | PARTIAL POWER | CO | NONE | 1 | 1 | 229 | 0.00021678 | 9.4663e-07 | 229
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WFS | CUTOUT | 1 | 200 | 4800 | 0.0045533 | 0.00018972 | 24
AEP-AP | 2023 | 1056376 | PARTIAL POWER | A | FUSE | 8 | 42 | 2806 | 0.0026563 | 3.9759e-05 | 66.8095
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | EQF | POLE HARDWARE | 3 | 2373 | 238452 | 0.22521 | 0.0022412 | 100.4855
AEP-AP | 2025 | 1058812 | TRANSMISSION STATION | EQF | CIRCUIT SWITCHER | 2 | 570 | 115551 | 0.10913 | 0.00053834 | 202.7211
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | V | NONE | 2 | 412 | 10716 | 0.010121 | 0.00038912 | 26.0097
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 6 | 14472 | 0.013668 | 5.6667e-06 | 2412
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | WU | NONE | 3 | 5558 | 107420 | 0.10145 | 0.0052493 | 19.3271
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | O | NONE | 68 | 4700 | 982708 | 0.9317 | 0.004456 | 209.0868
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 9 | 93 | 22386 | 0.021224 | 8.8172e-05 | 240.7097
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | POLE | 359 | 37868 | 10823397 | 10.2458 | 0.035847 | 285.8191
AEP-AP | 2021 | 1054192 | PARTIAL POWER | U | NONE | 47 | 137 | 17238 | 0.016352 | 0.00012996 | 125.8248
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 90 | 1333 | 174672 | 0.16569 | 0.0012645 | 131.0368
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 28 | 7586 | 718248 | 0.68133 | 0.007196 | 94.6807
AEP-AP | 2022 | 1054752 | PARTIAL POWER | WU | NONE | 18 | 78 | 35887 | 0.034024 | 7.3951e-05 | 460.0897
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | POLE | 6 | 330 | 296733 | 0.28148 | 0.00031304 | 899.1909
AEP-AP | 2022 | 1054752 | PARTIAL POWER | SCO | NONE | 1 | 1 | 75 | 7.1107e-05 | 9.4809e-07 | 75
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | INSULATOR | 183 | 43344 | 7666078 | 7.2872 | 0.041202 | 176.866
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | POLE | 199 | 22373 | 4939114 | 4.695 | 0.021267 | 220.7623
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 96 | 16164 | 0.015365 | 9.1256e-05 | 168.375
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | CUTOUT | 8 | 157 | 71909 | 0.068355 | 0.00014924 | 458.0191
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 13 | 1070 | 658070 | 0.62424 | 0.001015 | 615.0187
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SO | NONE | 15 | 66 | 10316 | 0.0097857 | 6.2607e-05 | 156.303
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 15 | 9060 | 0.0085943 | 1.4229e-05 | 604
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 14 | 54 | 20413 | 0.019404 | 5.1331e-05 | 378.0185
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | BE | NONE | 1 | 1050 | 140700 | 0.13347 | 0.00099602 | 134
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 2 | 40 | 3.7924e-05 | 1.8962e-06 | 20
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | U | FUSE | 577 | 4037 | 623169 | 0.58991 | 0.0038216 | 154.3644
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | CONDUCTOR UG | 62 | 136 | 57327 | 0.054268 | 0.00012874 | 421.5221
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | SPLICE, OH | 20 | 161 | 84695 | 0.079991 | 0.00015206 | 526.0559
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 472 | 60888 | 0.057639 | 0.00044681 | 129
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | PEDESTAL | 3 | 11 | 896 | 0.00084818 | 1.0413e-05 | 81.4545
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | CONN/CLAMP | 4 | 13 | 899 | 0.00085102 | 1.2306e-05 | 69.1538
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | CROSSARM | 3 | 234 | 11733 | 0.011153 | 0.00022244 | 50.141
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OU | POLE | 5 | 217 | 32247 | 0.030526 | 0.00020542 | 148.6037
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | SPLICE, OH | 2 | 8 | 7466 | 0.0070513 | 7.5556e-06 | 933.25
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 8 | 29 | 1306 | 0.0012363 | 2.7452e-05 | 45.0345
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | WU | NONE | 6 | 1547 | 71088 | 0.067294 | 0.0014644 | 45.9522
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 47 | 115 | 4048 | 0.0038232 | 0.00010861 | 35.2
AEP-AP | 2020 | 1051986 | TRANSMISSION STATION | EQF | BREAKER | 9 | 5135 | 723705 | 0.68794 | 0.0048812 | 140.9357
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 1 | 958 | 0.00091066 | 9.5058e-07 | 958
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 296 | 2628 | 579201 | 0.54703 | 0.002482 | 220.3961
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 10 | 9203 | 827903 | 0.78192 | 0.0086918 | 89.9601
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | CUTOUT | 6 | 135 | 14922 | 0.014093 | 0.0001275 | 110.5333
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | V | REGULATOR | 3 | 688 | 136696 | 0.1291 | 0.00064978 | 198.686
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | CE | NONE | 16 | 95 | 17468 | 0.016498 | 8.9723e-05 | 183.8737
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 4 | 1443 | 585398 | 0.55288 | 0.0013628 | 405.6812
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | FUSE | 3 | 164 | 22124 | 0.021031 | 0.0001559 | 134.9024
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | CONN/CLAMP | 3 | 52 | 13483 | 0.012817 | 4.943e-05 | 259.2885
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 5 | 2151 | 0.0020447 | 4.7529e-06 | 430.2
AEP-AP | 2023 | 1056376 | PARTIAL POWER | FO | NONE | 1 | 1 | 919 | 0.00086996 | 9.4663e-07 | 919
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 3 | 22 | 410 | 0.00038723 | 2.0778e-05 | 18.6364
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 72 | 6.8001e-05 | 9.4445e-07 | 72
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | GUY/ANCHOR | 1 | 1 | 868 | 0.00081979 | 9.4445e-07 | 868
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | POLE | 2 | 6 | 3680 | 0.0034756 | 5.6667e-06 | 613.3333
AEP-AP | 2025 | 1058812 | PARTIAL POWER | WU | FUSE | 3 | 47 | 7298 | 0.0068926 | 4.4389e-05 | 155.2766
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OU | POLE | 4 | 334 | 68066 | 0.064285 | 0.00031545 | 203.7904
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 6 | 1698 | 0.0016037 | 5.6667e-06 | 283
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | EQF | SPLICE, OH | 1 | 1 | 149 | 0.00014127 | 9.4809e-07 | 149
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 1 | 1878 | 0.0017805 | 9.4809e-07 | 1878
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 14 | 784 | 0.00074526 | 1.3308e-05 | 56
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | EQF | FUSE | 1 | 464 | 120176 | 0.11424 | 0.00044107 | 259
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 1227 | 217875 | 0.20667 | 0.0011639 | 177.5672
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 859 | 38770 | 0.036777 | 0.00081484 | 45.1339
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | U | NONE | 4 | 2464 | 398023 | 0.37756 | 0.0023373 | 161.5353
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WI | FUSE | 1 | 1 | 1564 | 0.0014836 | 9.4859e-07 | 1564
AEP-AP | 2023 | 1056376 | DISTRIBUTION SOURCE | WU | NONE | 1 | 1442 | 333102 | 0.31533 | 0.001365 | 231
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 3 | 243 | 0.00023039 | 2.8443e-06 | 81
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | O | NONE | 1 | 2348 | 147924 | 0.14061 | 0.002232 | 63
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | INSULATOR | 2 | 17 | 2827 | 0.0026803 | 1.6118e-05 | 166.2941
AEP-AP | 2021 | 1054192 | DISTRIBUTION SOURCE | TOR | NONE | 1 | 1413 | 804336 | 0.76299 | 0.0013404 | 569.2399
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 95 | 43700 | 0.041432 | 9.0069e-05 | 460
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | TOR | CROSSARM | 2 | 385 | 47740 | 0.045088 | 0.00036362 | 124
AEP-AP | 2020 | 1051986 | DISTRIBUTION SOURCE | EQF | FUSE | 1 | 821 | 113298 | 0.1077 | 0.00078043 | 138
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 1110 | 64380 | 0.061038 | 0.0010524 | 58
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 27 | 2.5666e-05 | 9.5058e-07 | 27
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 2977 | 0.0028116 | 9.4445e-07 | 2977
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | WFS | NONE | 2 | 368 | 88890 | 0.083953 | 0.00034756 | 241.5489
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OU | CROSSARM | 2 | 448 | 71428 | 0.067461 | 0.00042312 | 159.4375
AEP-AP | 2022 | 1054752 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 50 | 4.7405e-05 | 9.4809e-07 | 50
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 15 | 5535 | 0.0052396 | 1.4199e-05 | 369
AEP-AP | 2023 | 1056376 | PARTIAL POWER | OU | NONE | 1 | 1 | 114 | 0.00010792 | 9.4663e-07 | 114
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 2 | 5 | 714 | 0.00067434 | 4.7223e-06 | 142.8
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 153 | 14994 | 0.014253 | 0.00014544 | 98
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | CE | NONE | 3 | 1498 | 152642 | 0.1451 | 0.001424 | 101.8972
AEP-AP | 2020 | 1051986 | PARTIAL POWER | OU | NONE | 1 | 1 | 104 | 9.8861e-05 | 9.5058e-07 | 104
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | ARRESTER | 1 | 1 | 98 | 9.277e-05 | 9.4663e-07 | 98
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 1 | 206 | 0.00019456 | 9.4445e-07 | 206
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 9 | 675 | 0.00064164 | 8.5552e-06 | 75
AEP-AP | 2021 | 1054192 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 224 | 0.00021249 | 9.4859e-07 | 224
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | O | NONE | 12 | 7112 | 1077995 | 1.0205 | 0.0067325 | 151.5741
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | VA | CONDUCTOR OVERHEAD | 1 | 623 | 56070 | 0.053078 | 0.00058975 | 90
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 1 | 1 | 71 | 6.7491e-05 | 9.5058e-07 | 71
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | EQF | BREAKER | 1 | 954 | 216173 | 0.20417 | 0.00090101 | 226.5964
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 5678 | 273209 | 114451850 | 108.5107 | 0.25903 | 418.9168
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | FUSE | 213 | 2490 | 823765 | 0.781 | 0.0023607 | 330.8293
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | CUTOUT | 2848 | 97930 | 18208912 | 17.2729 | 0.092896 | 185.938
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | ABI | NONE | 808 | 10524 | 1232926 | 1.1695 | 0.009983 | 117.1537
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 56 | 7322 | 749265 | 0.71037 | 0.0069419 | 102.3306
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | NONE | 202 | 25860 | 8042964 | 7.6255 | 0.024518 | 311.0195
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | NONE | 198 | 15767 | 1134211 | 1.0753 | 0.014949 | 71.9358
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | FUSE | 19 | 229 | 24009 | 0.022763 | 0.00021711 | 104.8428
AEP-AP | 2022 | 1054752 | PARTIAL POWER | EQF | TRANSFORMER, OH | 8 | 49 | 13704 | 0.012993 | 4.6456e-05 | 279.6735
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 54 | 620 | 164653 | 0.15619 | 0.00058813 | 265.5694
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 84 | 2515 | 422713 | 0.40098 | 0.0023857 | 168.0767
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 5 | 143 | 4908 | 0.0046532 | 0.00013558 | 34.3217
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | ARRESTER | 35 | 123 | 6694 | 0.0063465 | 0.00011662 | 54.4228
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | CONDUCTOR UG | 225 | 448 | 182970 | 0.17393 | 0.00042586 | 408.4152
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 29 | 854 | 250275 | 0.23791 | 0.0008118 | 293.0621
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | CUTOUT | 90 | 1108 | 224482 | 0.21294 | 0.001051 | 202.6011
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 1712 | 285585 | 0.27076 | 0.0016231 | 166.8137
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | WL | NONE | 6 | 6589 | 496148 | 0.47039 | 0.006247 | 75.2994
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WT | NONE | 6 | 108 | 81303 | 0.077083 | 0.00010239 | 752.8056
AEP-AP | 2021 | 1054192 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 2 | 11 | 878 | 0.00083287 | 1.0435e-05 | 79.8182
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 4 | 2346 | 0.0022254 | 3.7944e-06 | 586.5
AEP-AP | 2022 | 1054752 | PARTIAL POWER | O | NONE | 4 | 11 | 3327 | 0.0031543 | 1.0429e-05 | 302.4545
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | METERING | 25 | 26 | 5168 | 0.0048922 | 2.4612e-05 | 198.7692
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 6 | 1889 | 159327 | 0.15114 | 0.0017919 | 84.3446
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 22 | 360 | 86866 | 0.08223 | 0.00034079 | 241.2944
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WW | CROSSARM | 3 | 325 | 302509 | 0.28696 | 0.00030829 | 930.7969
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 13 | 130 | 8572 | 0.0081145 | 0.00012306 | 65.9385
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 9 | 15 | 2635 | 0.0024944 | 1.4199e-05 | 175.6667
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | FUSE | 26 | 595 | 203925 | 0.19304 | 0.00056325 | 342.7311
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | UG | NONE | 28 | 329 | 106974 | 0.10127 | 0.00031144 | 325.1489
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 3 | 357 | 159155 | 0.15097 | 0.00033865 | 445.8123
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | POLE HARDWARE | 2 | 21 | 28727 | 0.02725 | 1.992e-05 | 1367.9524
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | EQF | ARRESTER | 10 | 7480 | 1570803 | 1.487 | 0.0070808 | 210.0004
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VA | ARRESTER | 3 | 773 | 140586 | 0.13364 | 0.0007348 | 181.8706
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | PEDESTAL | 11 | 130 | 33321 | 0.031543 | 0.00012306 | 256.3154
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | CAPACITOR | 5 | 4845 | 411279 | 0.38933 | 0.0045864 | 84.8873
AEP-AP | 2021 | 1054192 | PARTIAL POWER | CO | METERING | 1 | 1 | 97 | 9.2014e-05 | 9.4859e-07 | 97
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TOR | METERING | 10 | 14 | 2406 | 0.0022811 | 1.3273e-05 | 171.8571
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 227 | 0.00021578 | 9.5058e-07 | 227
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | FUSE | 3 | 9 | 438 | 0.00041463 | 8.5197e-06 | 48.6667
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WW | ARRESTER | 2 | 45 | 9414 | 0.0089116 | 4.2598e-05 | 209.2
AEP-AP | 2023 | 1056376 | SUBTRANSMISSION LINE | TOR | NONE | 5 | 1892 | 471321 | 0.44617 | 0.001791 | 249.1126
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | SPLICE, UG | 7 | 23 | 5511 | 0.0052169 | 2.1773e-05 | 239.6087
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | EQF | BREAKER | 5 | 1767 | 319148 | 0.30142 | 0.0016689 | 180.6157
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | FUSE | 2 | 50 | 15600 | 0.014798 | 4.743e-05 | 312
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | WFS | NONE | 3 | 1394 | 428052 | 0.40605 | 0.0013223 | 307.0674
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OU | NONE | 37 | 1718 | 149448 | 0.14115 | 0.0016226 | 86.9895
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 25 | 959 | 287401 | 0.27144 | 0.00090573 | 299.6882
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | PEDESTAL | 10 | 39 | 8912 | 0.008417 | 3.6834e-05 | 228.5128
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 121 | 86783 | 0.082494 | 0.00011502 | 717.2149
AEP-AP | 2023 | 1056376 | PARTIAL POWER | WL | FUSE | 1 | 1 | 80 | 7.5731e-05 | 9.4663e-07 | 80
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 1 | 73 | 6.8945e-05 | 9.4445e-07 | 73
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 14 | 210 | 0.00019834 | 1.3222e-05 | 15
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 120 | 0.00011333 | 9.4445e-07 | 120
AEP-AP | 2022 | 1054752 | PARTIAL POWER | A | INSULATOR | 1 | 19 | 456 | 0.00043233 | 1.8014e-05 | 24
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | V | REGULATOR | 1 | 65 | 26390 | 0.02502 | 6.1626e-05 | 406
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | EQF | TRANSFORMER, POWER - NON LTC | 1 | 349 | 3141 | 0.002978 | 0.00033088 | 9
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 15 | 15465 | 0.014701 | 1.4259e-05 | 1031
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 1000 | 149000 | 0.14134 | 0.00094859 | 149
AEP-AP | 2021 | 1054192 | PARTIAL POWER | TOR | POLE | 1 | 72 | 28728 | 0.027251 | 6.8299e-05 | 399
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1795 | 67947 | 0.064454 | 0.0017027 | 37.8535
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | F | NONE | 1 | 1 | 73 | 6.9247e-05 | 9.4859e-07 | 73
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SO | POLE | 1 | 2 | 250 | 0.00023715 | 1.8972e-06 | 125
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 1 | 512 | 0.00048468 | 9.4663e-07 | 512
AEP-AP | 2023 | 1056376 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 57 | 5.3958e-05 | 9.4663e-07 | 57
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | WU | NETWORK LIMITER | 1 | 866 | 5196 | 0.0049263 | 0.00082105 | 6
AEP-AP | 2020 | 1051986 | DISTRIBUTION SOURCE | VA | NONE | 3 | 734 | 194040 | 0.18445 | 0.00069773 | 264.3597
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 2 | 42 | 16100 | 0.015272 | 3.9841e-05 | 383.3333
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | AF | MOAB | 1 | 170 | 1530 | 0.0014513 | 0.00016126 | 9
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 277 | 70912 | 0.066973 | 0.00026161 | 256
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 3 | 258 | 0.00024423 | 2.8399e-06 | 86
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | NONE | 3393 | 98463 | 13816561 | 13.0993 | 0.093352 | 140.3224
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | FUSE | 1204 | 12747 | 1933846 | 1.8335 | 0.012085 | 151.7099
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2617 | 116159 | 50009130 | 47.4384 | 0.11019 | 430.5231
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WU | NONE | 1796 | 56447 | 12976479 | 12.3094 | 0.053545 | 229.8878
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | FUSE | 459 | 3156 | 494768 | 0.46908 | 0.0029922 | 156.7706
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TIR | ARRESTER | 7 | 30 | 14552 | 0.013797 | 2.8443e-05 | 485.0667
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | ARRESTER | 289 | 23115 | 4112493 | 3.893 | 0.021881 | 177.9145
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 83 | 252 | 87823 | 0.083308 | 0.00023905 | 348.504
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | O | FUSE | 6 | 17 | 2179 | 0.002067 | 1.6126e-05 | 128.1765
AEP-AP | 2022 | 1054752 | PARTIAL POWER | UG | CONDUCTOR UG | 1 | 1 | 265 | 0.00025124 | 9.4809e-07 | 265
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VIN | CUTOUT | 11 | 441 | 74165 | 0.070315 | 0.00041811 | 168.1746
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | CUTOUT | 18 | 2125 | 417671 | 0.3962 | 0.0020158 | 196.5511
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 5 | 8090 | 0.00767 | 4.7405e-06 | 1618
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 22 | 14059 | 0.013329 | 2.0858e-05 | 639.0455
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | NONE | 261 | 17432 | 1718575 | 1.6336 | 0.016571 | 98.5874
AEP-AP | 2020 | 1051986 | PARTIAL POWER | WU | TRANSFORMER, OH | 1 | 1 | 1539 | 0.0014629 | 9.5058e-07 | 1539
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | EQF | SPLICE, OH | 2 | 250 | 33000 | 0.031304 | 0.00023715 | 132
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 8 | 299 | 99708 | 0.094781 | 0.00028422 | 333.4716
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | EQF | STATIC WIRE | 8 | 8648 | 409473 | 0.38842 | 0.0082034 | 47.3489
AEP-AP | 2022 | 1054752 | PARTIAL POWER | TOR | NONE | 20 | 81 | 40906 | 0.038783 | 7.6795e-05 | 505.0123
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | CUTOUT | 4 | 396 | 52238 | 0.049526 | 0.00037544 | 131.9141
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 242 | 4840 | 0.0045888 | 0.00022944 | 20
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WI | NONE | 12 | 21 | 15314 | 0.014527 | 1.992e-05 | 729.2381
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 3 | 7 | 1367 | 0.001296 | 6.6366e-06 | 195.2857
AEP-AP | 2021 | 1054192 | DISTRIBUTION STATION | EQF | CUTOUT | 7 | 3738 | 453262 | 0.42996 | 0.0035458 | 121.2579
AEP-AP | 2020 | 1051986 | PARTIAL POWER | O | NONE | 1 | 1 | 80 | 7.6047e-05 | 9.5058e-07 | 80
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 32 | 13502 | 0.012808 | 3.0355e-05 | 421.9375
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | ARRESTER | 8 | 55 | 10227 | 0.0097013 | 5.2173e-05 | 185.9455
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WH | FUSE | 1 | 3 | 1605 | 0.0015217 | 2.8443e-06 | 535
AEP-AP | 2022 | 1054752 | PARTIAL POWER | UG | NONE | 2 | 2 | 587 | 0.00055653 | 1.8962e-06 | 293.5
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | BE | CUTOUT | 1 | 11 | 3377 | 0.0032017 | 1.0429e-05 | 307
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | INSULATOR | 3 | 91 | 11496 | 0.010928 | 8.6503e-05 | 126.3297
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | U | POLE | 4 | 248 | 311016 | 0.29565 | 0.00023574 | 1254.0968
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | NONE | 59 | 1354 | 170836 | 0.16172 | 0.0012817 | 126.1713
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SO | NONE | 4 | 16 | 2442 | 0.0023117 | 1.5146e-05 | 152.625
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 157 | 12448 | 2263653 | 2.1379 | 0.011757 | 181.8487
AEP-AP | 2023 | 1056376 | PARTIAL POWER | EQF | CABLE TERMINATOR | 5 | 18 | 3924 | 0.0037146 | 1.7039e-05 | 218
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | FO | FUSE | 11 | 108 | 22175 | 0.020943 | 0.000102 | 205.3241
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | INSULATOR | 1 | 27 | 13554 | 0.012884 | 2.5666e-05 | 502
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | CE | NONE | 3 | 995 | 10111 | 0.0095861 | 0.00094335 | 10.1618
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TIR | POLE | 5 | 47 | 49770 | 0.047311 | 4.4677e-05 | 1058.9362
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TOR | FUSE | 430 | 5288 | 1571998 | 1.4847 | 0.0049943 | 297.2765
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | V | POLE | 2 | 27 | 3687 | 0.0034975 | 2.5612e-05 | 136.5556
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 71 | 3190 | 428020 | 0.40425 | 0.0030128 | 134.1755
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | SWITCH, OH | 25 | 6461 | 664055 | 0.62717 | 0.0061021 | 102.779
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TIR | NONE | 8 | 35 | 10237 | 0.0096684 | 3.3056e-05 | 292.4857
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | CONN/CLAMP | 142 | 273 | 40387 | 0.038144 | 0.00025784 | 147.9377
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WTO | FUSE | 1 | 3 | 315 | 0.00029943 | 2.8517e-06 | 105
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | A | NONE | 3 | 1675 | 412325 | 0.39195 | 0.0015922 | 246.1642
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WT | NONE | 4 | 952 | 119333 | 0.1127 | 0.00089912 | 125.3498
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 26 | 2915 | 441654 | 0.41712 | 0.0027531 | 151.5108
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | ARRESTER | 34 | 1349 | 240908 | 0.22753 | 0.0012741 | 178.5827
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 4 | 5 | 208 | 0.0001969 | 4.7332e-06 | 41.6
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 45 | 76 | 12464 | 0.011772 | 7.1779e-05 | 164
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WU | FUSE | 3 | 6 | 1200 | 0.0011333 | 5.6667e-06 | 200
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 3 | 98 | 33739 | 0.031865 | 9.2557e-05 | 344.2755
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 2352 | 0.0022358 | 1.9012e-06 | 1176
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | BREAKER | 6 | 2972 | 1266766 | 1.2042 | 0.0028251 | 426.2335
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 1517 | 389403 | 0.36777 | 0.0014327 | 256.6928
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | EQF | ARRESTER | 3 | 3528 | 3216899 | 3.0382 | 0.003332 | 911.8194
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 3 | 3921 | 373446 | 0.35499 | 0.0037272 | 95.2425
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | NONE | 2786 | 88753 | 25589811 | 24.2614 | 0.084146 | 288.3262
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | CONN/CLAMP | 219 | 576 | 124076 | 0.1177 | 0.00054639 | 215.4097
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 21 | 29655 | 0.028131 | 1.992e-05 | 1412.1429
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | POLE | 9 | 1958 | 727521 | 0.68976 | 0.0018564 | 371.5633
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | SWITCH, OH | 20 | 8998 | 1523979 | 1.4456 | 0.0085354 | 169.3686
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 2 | 2 | 229 | 0.00021723 | 1.8972e-06 | 114.5
AEP-AP | 2021 | 1054192 | PARTIAL POWER | ABI | NONE | 15 | 79 | 8028 | 0.0076153 | 7.4939e-05 | 101.6203
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 7 | 163 | 28992 | 0.027502 | 0.00015462 | 177.865
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | VA | CROSSARM | 6 | 832 | 102764 | 0.09743 | 0.00078881 | 123.5144
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WL | METERING | 3 | 20 | 5441 | 0.0051586 | 1.8962e-05 | 272.05
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | EQF | REGULATOR | 2 | 1198 | 226422 | 0.21467 | 0.0011358 | 189
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | FUSE | 37 | 103 | 13621 | 0.012948 | 9.791e-05 | 132.2427
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | F | CUTOUT | 6 | 93 | 16769 | 0.015899 | 8.8172e-05 | 180.3118
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 8 | 168 | 27851 | 0.026419 | 0.00015936 | 165.7798
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 4 | 330 | 0.00031287 | 3.7924e-06 | 82.5
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | TOR | NONE | 31 | 21007 | 3960171 | 3.7546 | 0.019917 | 188.5167
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 14 | 39 | 34454 | 0.032665 | 3.6976e-05 | 883.4359
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 3 | 688 | 46740 | 0.044314 | 0.00065229 | 67.936
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | EQF | INSULATOR | 220 | 45912 | 9728852 | 9.2096 | 0.043462 | 211.9022
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WL | CUTOUT | 13 | 214 | 122152 | 0.11612 | 0.00020342 | 570.8037
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SCO | SECTIONALIZER | 1 | 35 | 630 | 0.0005973 | 3.3183e-05 | 18
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | CUTOUT | 67 | 1796 | 574982 | 0.5443 | 0.0017002 | 320.1459
AEP-AP | 2020 | 1051986 | PARTIAL POWER | CO | METERING | 1 | 4 | 460 | 0.00043727 | 3.8023e-06 | 115
AEP-AP | 2022 | 1054752 | PARTIAL POWER | VA | FUSE | 1 | 3 | 258 | 0.00024461 | 2.8443e-06 | 86
AEP-AP | 2023 | 1056376 | DISTRIBUTION STATION | AO | NONE | 15 | 13631 | 2053746 | 1.9441 | 0.012904 | 150.6673
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 25 | 347 | 88753 | 0.084016 | 0.00032848 | 255.7723
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WI | RECLOSER, LINE/OCR/BR | 1 | 160 | 36160 | 0.034283 | 0.00015169 | 226
AEP-AP | 2022 | 1054752 | DISTRIBUTION STATION | AO | NONE | 7 | 6558 | 563775 | 0.53451 | 0.0062176 | 85.9675
AEP-AP | 2023 | 1056376 | TRANSMISSION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 1525 | 52129 | 0.049347 | 0.0014436 | 34.183
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | POLE | 491 | 101772 | 21199178 | 20.0217 | 0.096119 | 208.3007
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 9 | 1581 | 370987 | 0.35265 | 0.0015029 | 234.6534
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | TR | OTHER EQUIPMENT | 1 | 11 | 704 | 0.00066746 | 1.0429e-05 | 64
AEP-AP | 2023 | 1056376 | PARTIAL POWER | A | NONE | 8 | 10 | 925 | 0.00087564 | 9.4663e-06 | 92.5
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 30 | 17277 | 0.016355 | 2.8399e-05 | 575.9
AEP-AP | 2024 | 1058812 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 2 | 2 | 204 | 0.00019267 | 1.8889e-06 | 102
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 3 | 17 | 9313 | 0.0088343 | 1.6126e-05 | 547.8235
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 2 | 4 | 2905 | 0.0027542 | 3.7924e-06 | 726.25
AEP-AP | 2024 | 1058812 | PARTIAL POWER | TR | FUSE | 1 | 2 | 142 | 0.00013411 | 1.8889e-06 | 71
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 89 | 98968 | 0.093686 | 8.425e-05 | 1112
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VA | FUSE | 17 | 227 | 22670 | 0.021411 | 0.00021439 | 99.8678
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | TR | FUSE | 2 | 6 | 3426 | 0.0032567 | 5.7035e-06 | 571
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 32 | 11697 | 0.011073 | 3.0292e-05 | 365.5312
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2247 | 114610 | 35181617 | 33.2274 | 0.10824 | 306.9681
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 68 | 4478 | 1288469 | 1.2169 | 0.0042293 | 287.7331
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 64 | 370 | 71164 | 0.067211 | 0.00034945 | 192.3351
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | FO | NONE | 6 | 69 | 6941 | 0.0065555 | 6.5167e-05 | 100.5942
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | CONN/CLAMP | 3 | 25 | 399 | 0.00037684 | 2.3611e-05 | 15.96
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | FUSE | 15 | 179 | 95729 | 0.090412 | 0.00016906 | 534.7989
AEP-AP | 2022 | 1054752 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 3 | 21 | 7975 | 0.007561 | 1.991e-05 | 379.7619
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 2 | 533 | 0.00050533 | 1.8962e-06 | 266.5
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 3 | 9 | 1002 | 0.00095248 | 8.5552e-06 | 111.3333
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 2 | 1554 | 0.0014733 | 1.8962e-06 | 777
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | VIN | POLE | 2 | 788 | 162691 | 0.15465 | 0.00074906 | 206.4607
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 3 | 921 | 0.00087549 | 2.8517e-06 | 307
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | FUSE | 2 | 8 | 488 | 0.00046089 | 7.5556e-06 | 61
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | SCO | NONE | 2 | 7 | 13760 | 0.012996 | 6.6112e-06 | 1965.7143
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | TOR | INSULATOR | 2 | 1284 | 29532 | 0.027892 | 0.0012127 | 23
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | FUSE | 2 | 77 | 8789 | 0.0083547 | 7.3195e-05 | 114.1429
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | WFS | FUSE | 1 | 11 | 110 | 0.00010413 | 1.0413e-05 | 10
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | V | PEDESTAL | 2 | 6 | 214 | 0.00020211 | 5.6667e-06 | 35.6667
AEP-AP | 2020 | 1051986 | PARTIAL POWER | EQF | CROSSARM | 3 | 14 | 6329 | 0.0060162 | 1.3308e-05 | 452.0714
AEP-AP | 2024 | 1058812 | TRANSMISSION LINE | WL | NONE | 3 | 3571 | 776632 | 0.73349 | 0.0033726 | 217.4831
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ABI | POLE | 1 | 4 | 1008 | 0.00095201 | 3.7778e-06 | 252
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ABI | SWITCH, OH | 1 | 969 | 234498 | 0.22147 | 0.00091518 | 242
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | OU | FUSE | 1 | 8 | 1008 | 0.00095201 | 7.5556e-06 | 126
AEP-AP | 2024 | 1058812 | PARTIAL POWER | OL | NONE | 1 | 1 | 285 | 0.00026917 | 9.4445e-07 | 285
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 34 | 15733 | 0.014916 | 3.2235e-05 | 462.7353
AEP-AP | 2022 | 1054752 | TRANSMISSION LINE | V | NONE | 3 | 1750 | 113753 | 0.10785 | 0.0016592 | 65.0017
AEP-AP | 2023 | 1056376 | TRANSMISSION LINE | EQF | ARRESTER | 3 | 1758 | 462086 | 0.43743 | 0.0016642 | 262.8476
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ERF | BREAKER | 2 | 2 | 286 | 0.00027187 | 1.9012e-06 | 143
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 17 | 1840 | 54450 | 0.051426 | 0.0017378 | 29.5924
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | TOR | FUSE | 125 | 1375 | 378218 | 0.35721 | 0.0012986 | 275.0676
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WFS | TRANSFORMER, UG | 3 | 19 | 3004 | 0.0028371 | 1.7945e-05 | 158.1053
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WU | TRANSFORMER, STATION SERVICE | 1 | 83 | 23987 | 0.022655 | 7.839e-05 | 289
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 14 | 6230 | 0.0059066 | 1.3273e-05 | 445
AEP-AP | 2024 | 1058812 | TRANSMISSION STATION | WU | NONE | 3 | 1822 | 366262 | 0.34592 | 0.0017208 | 201.022
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CE | CABLE TERMINATOR | 1 | 3 | 90 | 8.5552e-05 | 2.8517e-06 | 30
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 5 | 20 | 17857 | 0.016939 | 1.8972e-05 | 892.85
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 5 | 8 | 6443 | 0.0061246 | 7.6047e-06 | 805.375
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | CE | METERING | 8 | 1468 | 188297 | 0.17784 | 0.0013865 | 128.2677
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 13 | 1339 | 0.0012702 | 1.2332e-05 | 103
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | TIR | NONE | 4 | 4598 | 64372 | 0.061063 | 0.0043616 | 14
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | V | NONE | 8 | 3690 | 388396 | 0.36682 | 0.003485 | 105.2564
AEP-AP | 2025 | 1058812 | TRANSMISSION LINE | WI | NONE | 5 | 5392 | 349799 | 0.33037 | 0.0050925 | 64.8737
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 7 | 13 | 13822 | 0.013054 | 1.2278e-05 | 1063.2308
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 9 | 1577 | 150940 | 0.14256 | 0.0014894 | 95.7134
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | SCO | BREAKER | 1 | 3 | 693 | 0.00065602 | 2.8399e-06 | 231
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | F | CUTOUT | 1 | 4 | 112 | 0.00010602 | 3.7865e-06 | 28
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 1953 | 262277 | 0.24771 | 0.0018445 | 134.2944
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | OL | RECLOSER, LINE/OCR/BR | 1 | 27 | 2889 | 0.0027348 | 2.5559e-05 | 107
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | VIN | CONDUCTOR UG | 1 | 30 | 5120 | 0.0048356 | 2.8334e-05 | 170.6667
AEP-AP | 2023 | 1056376 | DISTRIBUTION LINE | V | CROSSARM | 1 | 0 | 0 | 0 | 0
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 386 | 0.00036693 | 1.9012e-06 | 193
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 27 | 2808 | 0.0026622 | 2.5598e-05 | 104
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 726 | 34848 | 0.033057 | 0.00068868 | 48
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 3196 | 60724 | 0.057723 | 0.0030381 | 19
AEP-AP | 2021 | 1054192 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 331 | 0.00031398 | 9.4859e-07 | 331
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | V | TRANSFORMER, GROUNDING | 1 | 620 | 304243 | 0.28845 | 0.00058782 | 490.7145
AEP-AP | 2020 | 1051986 | TRANSMISSION LINE | EQF | CROSSARM | 1 | 456 | 212952 | 0.20243 | 0.00043347 | 467
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 161 | 52325 | 0.049739 | 0.00015304 | 325
AEP-AP | 2020 | 1051986 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 123 | 0.00011692 | 9.5058e-07 | 123
AEP-AP | 2024 | 1058812 | PARTIAL POWER | A | CONN/CLAMP | 1 | 1 | 261 | 0.0002465 | 9.4445e-07 | 261
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 1 | 785 | 0.00074621 | 9.5058e-07 | 785
AEP-AP | 2021 | 1054192 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 1 | 1086 | 0.0010302 | 9.4859e-07 | 1086
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1495 | 55647 | 0.052786 | 0.0014181 | 37.2221
AEP-AP | 2021 | 1054192 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 5 | 19810 | 0.018792 | 4.743e-06 | 3962
AEP-AP | 2020 | 1051986 | DISTRIBUTION LINE | SCO | INSULATOR | 2 | 1565 | 70581 | 0.067093 | 0.0014877 | 45.0997
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WU | NONE | 605 | 25481 | 6866141 | 6.4848 | 0.024066 | 269.4612
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | FUSE | 174 | 1817 | 251892 | 0.2379 | 0.0017161 | 138.6307
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 392 | 4290 | 1140980 | 1.0776 | 0.0040517 | 265.9627
AEP-AP | 2024 | 1058812 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 4 | 5 | 2247 | 0.0021222 | 4.7223e-06 | 449.4
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | CO | INSULATOR | 1 | 96 | 19968 | 0.018942 | 9.1065e-05 | 208
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | WI | OTHER EQUIPMENT | 1 | 3 | 435 | 0.00041084 | 2.8334e-06 | 145
AEP-AP | 2025 | 1058812 | PARTIAL POWER | TOR | NONE | 8 | 22 | 3575 | 0.0033764 | 2.0778e-05 | 162.5
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | ERF | NONE | 3 | 2657 | 120718 | 0.11445 | 0.0025191 | 45.4339
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 6 | 1734 | 0.001644 | 5.6885e-06 | 289
AEP-AP | 2022 | 1054752 | TRANSMISSION STATION | R | NONE | 3 | 2096 | 393585 | 0.37315 | 0.0019872 | 187.7791
AEP-AP | 2020 | 1051986 | PARTIAL POWER | A | FUSE | 2 | 10 | 865 | 0.00082225 | 9.5058e-06 | 86.5
AEP-AP | 2024 | 1058812 | PARTIAL POWER | EQF | TRANSFORMER, OH | 5 | 13 | 3484 | 0.0032905 | 1.2278e-05 | 268
AEP-AP | 2020 | 1051986 | DISTRIBUTION STATION | EQF | CUTOUT | 4 | 5628 | 410321 | 0.39004 | 0.0053499 | 72.9071
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 312 | 22152 | 0.020922 | 0.00029467 | 71
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | U | INSULATOR | 1 | 534 | 399894 | 0.37768 | 0.00050434 | 748.8652
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | SCO | RELAY | 1 | 1 | 9 | 8.5001e-06 | 9.4445e-07 | 9
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 5 | 610 | 0.00057612 | 4.7223e-06 | 122
AEP-AP | 2024 | 1058812 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 2057 | 231923 | 0.21904 | 0.0019427 | 112.7482
AEP-AP | 2025 | 1058812 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 196 | 83692 | 0.079043 | 0.00018511 | 427
AEP-AP | 2024 | 1058812 | SUBTRANSMISSION LINE | EQF | GUY/ANCHOR | 1 | 3 | 186 | 0.00017567 | 2.8334e-06 | 62
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 54 | 7506 | 0.0071201 | 5.1224e-05 | 139
AEP-AP | 2021 | 1054192 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 22 | 31514 | 0.029894 | 2.0869e-05 | 1432.4545
AEP-AP | 2021 | 1054192 | TRANSMISSION LINE | ABI | NONE | 6 | 5321 | 677861 | 0.64301 | 0.0050475 | 127.3935
AEP-AP | 2024 | 1058812 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 3 | 1396 | 0.0013185 | 2.8334e-06 | 465.3333
AEP-AP | 2020 | 1051986 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 21 | 1995 | 0.0018964 | 1.9962e-05 | 95
AEP-AP | 2022 | 1054752 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 30 | 26771 | 0.025381 | 2.8443e-05 | 892.3667
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 17 | 2130 | 0.0034688 | 2.7685e-05 | 125.2941
AEP-I&M | 2020 | 599151 | TRANSMISSION STATION | SCO | MOAB | 1 | 1165 | 266785 | 0.44527 | 0.0019444 | 229
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 202 | 25856 | 0.042108 | 0.00032897 | 128
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | O | POLE | 1 | 8 | 1216 | 0.0019936 | 1.3116e-05 | 152
AEP-I&M | 2023 | 609949 | PARTIAL POWER | O | METERING | 1 | 1 | 87 | 0.00014263 | 1.6395e-06 | 87
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 1 | 148 | 0.0002439 | 1.648e-06 | 148
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | NONE | 180 | 9496 | 1701302 | 2.7706 | 0.015465 | 179.1599
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | POLE | 786 | 3581 | 386425 | 0.62931 | 0.0058318 | 107.9098
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | NONE | 161 | 11920 | 690514 | 1.1245 | 0.019412 | 57.929
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | CUTOUT | 28 | 223 | 24303 | 0.039579 | 0.00036317 | 108.9821
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | NONE | 78 | 666 | 115169 | 0.18756 | 0.0010846 | 172.9264
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 24 | 2208 | 125831 | 0.20492 | 0.0035958 | 56.9887
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | FO | NONE | 9 | 2978 | 317485 | 0.51704 | 0.0048498 | 106.6101
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | SWITCH, OH | 4 | 856 | 215469 | 0.3509 | 0.001394 | 251.7161
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | JUMPER/RISER | 5 | 17 | 1896 | 0.0030877 | 2.7685e-05 | 111.5294
AEP-I&M | 2025 | 614045 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 2 | 176 | 0.00028662 | 3.2571e-06 | 88
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 470 | 156607 | 0.25945 | 0.00077865 | 333.2064
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 3 | 8 | 1728 | 0.002833 | 1.3116e-05 | 216
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WI | METERING | 3 | 3 | 429 | 0.00071073 | 4.9701e-06 | 143
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CO | CUTOUT | 1 | 1 | 85 | 0.00014082 | 1.6567e-06 | 85
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 14 | 2.28e-05 | 1.6285e-06 | 14
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | F | CROSSARM | 1 | 706 | 7766 | 0.012647 | 0.0011498 | 11
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1 | 111 | 0.00018077 | 1.6285e-06 | 111
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | METERING | 1 | 1 | 66 | 0.00011016 | 1.669e-06 | 66
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 5 | 1763 | 0.0028711 | 8.1427e-06 | 352.6
AEP-I&M | 2024 | 614045 | PARTIAL POWER | OU | NONE | 2 | 2 | 178 | 0.00028988 | 3.2571e-06 | 89
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 486 | 84660 | 0.13787 | 0.00079147 | 174.1975
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OL | NONE | 1 | 10 | 270 | 0.00043971 | 1.6285e-05 | 27
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 14 | 3598 | 0.0058595 | 2.28e-05 | 257
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 3 | 168 | 0.0002736 | 4.8856e-06 | 56
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 1 | 102 | 0.00016611 | 1.6285e-06 | 102
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 1 | 164 | 0.00026887 | 1.6395e-06 | 164
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TR | NONE | 2 | 2 | 520 | 0.00085253 | 3.279e-06 | 260
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 980 | 124494 | 0.20516 | 0.001615 | 127.0347
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | ARRESTER | 1 | 923 | 17537 | 0.02927 | 0.0015405 | 19
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 4 | 119 | 104951 | 0.17517 | 0.00019861 | 881.9412
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 1 | 1 | 164 | 0.0002717 | 1.6567e-06 | 164
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TR | FUSE | 1 | 4 | 384 | 0.00063281 | 6.5918e-06 | 96
AEP-I&M | 2021 | 603608 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 96 | 0.00015904 | 1.6567e-06 | 96
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 1 | 337 | 0.00055251 | 1.6395e-06 | 337
AEP-I&M | 2021 | 603608 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 69 | 0.00011431 | 1.6567e-06 | 69
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 388 | 22730 | 0.037458 | 0.00063941 | 58.5825
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 4 | 80 | 0.00013028 | 6.5142e-06 | 20
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | AF | CUTOUT | 1 | 398 | 4776 | 0.0078302 | 0.00065251 | 12
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 85 | 5525 | 0.0090581 | 0.00013936 | 65
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 33 | 324 | 38369 | 0.062905 | 0.00053119 | 118.4228
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | FUSE | 62 | 1861 | 404366 | 0.6749 | 0.0031061 | 217.2843
AEP-I&M | 2021 | 603608 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 234 | 0.00038767 | 1.6567e-06 | 234
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | INSULATOR | 42 | 7491 | 1278165 | 2.0955 | 0.012281 | 170.6268
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 8 | 49 | 7425 | 0.012173 | 8.0335e-05 | 151.5306
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OU | FUSE | 1 | 16 | 800 | 0.0013184 | 2.6367e-05 | 50
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 217 | 9124 | 3197632 | 5.2425 | 0.014959 | 350.4638
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | F | NONE | 18 | 3143 | 170563 | 0.27963 | 0.0051529 | 54.2676
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 3 | 320 | 86965 | 0.14515 | 0.00053409 | 271.7656
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 5 | 977 | 0.0015911 | 8.1427e-06 | 195.4
AEP-I&M | 2023 | 609949 | PARTIAL POWER | OU | NONE | 1 | 0 | 0 | 0 | 0
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 23 | 1858 | 406278 | 0.66164 | 0.0030258 | 218.6642
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 10 | 7800 | 0.012788 | 1.6395e-05 | 780
AEP-I&M | 2022 | 606813 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 2 | 2 | 590 | 0.00097229 | 3.2959e-06 | 295
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 304 | 93766 | 0.1565 | 0.00050738 | 308.4408
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | EQF | ARRESTER | 7 | 8004 | 1628439 | 2.6698 | 0.013122 | 203.4531
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 65 | 1246 | 225357 | 0.367 | 0.0020292 | 180.8644
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | FUSE | 9 | 137 | 18577 | 0.030253 | 0.00022311 | 135.5985
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | WFS | NONE | 1 | 7 | 13832 | 0.022916 | 1.1597e-05 | 1976
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 12 | 22 | 1736 | 0.0028272 | 3.5828e-05 | 78.9091
AEP-I&M | 2024 | 614045 | SUBTRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 1 | 1097 | 211721 | 0.3448 | 0.0017865 | 193
AEP-I&M | 2024 | 614045 | DISTRIBUTION SOURCE | EQF | CROSSARM | 2 | 2391 | 33474 | 0.054514 | 0.0038939 | 14
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | ERF | CONDUCTOR OVERHEAD | 1 | 1846 | 88608 | 0.1468 | 0.0030583 | 48
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ABI | POLE | 1 | 1279 | 670042 | 1.1101 | 0.0021189 | 523.8796
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 1 | 6 | 1080 | 0.0017892 | 9.9402e-06 | 180
AEP-I&M | 2024 | 614045 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 306 | 0.00049833 | 1.6285e-06 | 306
AEP-I&M | 2024 | 614045 | PARTIAL POWER | FW | NONE | 1 | 1 | 16 | 2.6057e-05 | 1.6285e-06 | 16
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 175 | 6825 | 0.011115 | 0.000285 | 39
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 619 | 0.0010201 | 1.648e-06 | 619
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 435 | 0.00071686 | 1.648e-06 | 435
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 534 | 0.00087548 | 1.6395e-06 | 534
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 1 | 166 | 0.00027501 | 1.6567e-06 | 166
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | CE | NONE | 1 | 3 | 18 | 2.9314e-05 | 4.8856e-06 | 6
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UB | NONE | 1 | 1 | 133 | 0.00022198 | 1.669e-06 | 133
AEP-I&M | 2023 | 609949 | PARTIAL POWER | WU | FUSE | 1 | 1 | 53 | 8.6893e-05 | 1.6395e-06 | 53
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 145 | 0.00023614 | 1.6285e-06 | 145
AEP-I&M | 2020 | 599151 | PARTIAL POWER | UG | NONE | 2 | 3 | 597 | 0.00099641 | 5.0071e-06 | 199
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | CUTOUT | 4 | 42 | 7082 | 0.011533 | 6.8399e-05 | 168.619
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 40 | 3452 | 0.0057615 | 6.6761e-05 | 86.3
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 13 | 1053 | 0.0017149 | 2.1171e-05 | 81
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 4 | 37 | 8834 | 0.014387 | 6.0256e-05 | 238.7568
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 1540 | 53900 | 0.089961 | 0.0025703 | 35
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 1 | 119 | 38318 | 0.063954 | 0.00019861 | 322
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 4 | 1560 | 0.0025576 | 6.5579e-06 | 390
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 2 | 276 | 0.00045484 | 3.2959e-06 | 138
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 8 | 7712 | 0.012559 | 1.3028e-05 | 964
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 5 | 3250 | 454519 | 0.74903 | 0.0053559 | 139.852
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | SWITCH, OH | 1 | 1 | 26 | 4.3074e-05 | 1.6567e-06 | 26
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | FUSE | 1 | 2 | 252 | 0.0004206 | 3.3381e-06 | 126
AEP-I&M | 2021 | 603608 | PARTIAL POWER | F | CONDUCTOR UG | 1 | 1 | 1462 | 0.0024221 | 1.6567e-06 | 1462
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | EQF | RELAY | 2 | 2672 | 350032 | 0.58421 | 0.0044596 | 131
AEP-I&M | 2020 | 599151 | PARTIAL POWER | WL | FUSE | 3 | 4 | 745 | 0.0012434 | 6.6761e-06 | 186.25
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 7 | 2548 | 0.0041495 | 1.14e-05 | 364
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 322 | 11592 | 0.019103 | 0.00053064 | 36
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | EQF | SWITCH, OH | 3 | 3083 | 561715 | 0.9306 | 0.0051076 | 182.1975
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 2 | 216 | 0.00035413 | 3.279e-06 | 108
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | EQF | BREAKER | 3 | 3703 | 1012695 | 1.6902 | 0.0061804 | 273.4796
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 2 | 76 | 24196 | 0.039669 | 0.0001246 | 318.3684
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | AB | NONE | 5 | 2993 | 320878 | 0.5316 | 0.0049585 | 107.2095
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | VA | STATIC WIRE | 6 | 4975 | 1305465 | 2.1789 | 0.0083034 | 262.405
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | ARRESTER | 2 | 45 | 2691 | 0.0044914 | 7.5106e-05 | 59.8
AEP-I&M | 2020 | 599151 | TRANSMISSION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 1719 | 403965 | 0.67423 | 0.0028691 | 235
AEP-I&M | 2023 | 609949 | PARTIAL POWER | A | SPLICE, OH | 1 | 1 | 134 | 0.00021969 | 1.6395e-06 | 134
AEP-I&M | 2021 | 603608 | PARTIAL POWER | OL | NONE | 1 | 1 | 183 | 0.00030318 | 1.6567e-06 | 183
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | POLE | 21 | 2074 | 557228 | 0.90747 | 0.0033776 | 268.6731
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 61 | 7217 | 0.011832 | 0.00010001 | 118.3115
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 9 | 93 | 17505 | 0.028508 | 0.00015145 | 188.2258
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 2 | 58 | 9.5581e-05 | 3.2959e-06 | 29
AEP-I&M | 2022 | 606813 | PARTIAL POWER | VA | NONE | 1 | 6 | 480 | 0.00079102 | 9.8877e-06 | 80
AEP-I&M | 2023 | 609949 | TRANSMISSION LINE | FW | NONE | 1 | 1499 | 113924 | 0.18678 | 0.0024576 | 76
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | CUTOUT | 4 | 648 | 92801 | 0.15489 | 0.0010815 | 143.2114
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 597 | 0.00098905 | 1.6567e-06 | 597
AEP-I&M | 2021 | 603608 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 105 | 0.00017395 | 1.6567e-06 | 105
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 19 | 4997 | 0.0081925 | 3.115e-05 | 263
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 89 | 57494 | 0.094747 | 0.00014667 | 646
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | PEDESTAL | 1 | 4 | 2192 | 0.0036585 | 6.6761e-06 | 548
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | NONE | 271 | 16917 | 4056388 | 6.6847 | 0.027878 | 239.7818
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 324 | 4863 | 1612242 | 2.671 | 0.0080566 | 331.5324
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | FUSE | 33 | 438 | 82892 | 0.1366 | 0.0007218 | 189.2511
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 260 | 14852 | 4687914 | 7.7665 | 0.024605 | 315.6419
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | NONE | 28 | 365 | 121090 | 0.19955 | 0.0006015 | 331.7534
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | CONN/CLAMP | 14 | 14 | 1967 | 0.0032587 | 2.3194e-05 | 140.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 29 | 278 | 88362 | 0.14562 | 0.00045813 | 317.8489
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 4 | 616 | 335064 | 0.5551 | 0.0010205 | 543.9351
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 663 | 16932 | 4191859 | 6.8725 | 0.02776 | 247.5702
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 10 | 2754 | 268325 | 0.44454 | 0.0045626 | 97.431
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | NONE | 45 | 2619 | 120405 | 0.1974 | 0.0042938 | 45.9737
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TR | CROSSARM | 3 | 692 | 127911 | 0.21191 | 0.0011464 | 184.8425
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 1 | 1 | 145 | 0.00024022 | 1.6567e-06 | 145
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | NONE | 210 | 4991 | 1332961 | 2.1854 | 0.0081827 | 267.0729
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | METERING | 18 | 33 | 3090 | 0.005066 | 5.4103e-05 | 93.6364
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | REGULATOR | 5 | 2783 | 155665 | 0.25653 | 0.0045863 | 55.9342
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | ARRESTER | 4 | 5 | 1198 | 0.0019641 | 8.1974e-06 | 239.6
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | CUTOUT | 13 | 965 | 10512 | 0.017545 | 0.0016106 | 10.8933
AEP-I&M | 2020 | 599151 | PARTIAL POWER | A | FUSE | 9 | 16 | 1897 | 0.0031661 | 2.6704e-05 | 118.5625
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 110 | 407550 | 0.67519 | 0.00018224 | 3705
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERF | FUSE | 4 | 13 | 381 | 0.00062464 | 2.1313e-05 | 29.3077
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 10 | 122 | 430099 | 0.71255 | 0.00020212 | 3525.4016
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | CUTOUT | 5 | 190 | 44392 | 0.074092 | 0.00031712 | 233.6421
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | SWITCH, OH | 1 | 1 | 60 | 0.00010014 | 1.669e-06 | 60
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VIN | NONE | 102 | 651 | 88176 | 0.1436 | 0.0010602 | 135.447
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 20 | 217 | 11491 | 0.018839 | 0.00035577 | 52.9539
AEP-I&M | 2023 | 609949 | PARTIAL POWER | O | NONE | 4 | 5 | 746 | 0.0012231 | 8.1974e-06 | 149.2
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 16 | 1648 | 0.0026838 | 2.6057e-05 | 103
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 3 | 108 | 24744 | 0.040567 | 0.00017706 | 229.1111
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | O | CONDUCTOR UG | 2 | 2 | 454 | 0.00075774 | 3.3381e-06 | 227
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | PEDESTAL | 1 | 1 | 11 | 1.8127e-05 | 1.648e-06 | 11
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | CUTOUT | 4 | 67 | 10129 | 0.016606 | 0.00010985 | 151.1791
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 3 | 19 | 999 | 0.0016269 | 3.0942e-05 | 52.5789
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | AF | NONE | 1 | 1432 | 492648 | 0.80769 | 0.0023477 | 344.0279
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 60 | 11100 | 0.018292 | 9.8877e-05 | 185
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | CUTOUT | 184 | 2135 | 146951 | 0.24217 | 0.0035184 | 68.8295
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 128 | 175 | 41769 | 0.068833 | 0.00028839 | 238.68
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 2 | 209 | 0.00034625 | 3.3134e-06 | 104.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | PEDESTAL | 79 | 437 | 28093 | 0.046296 | 0.00072016 | 64.286
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | METERING | 3 | 3 | 800 | 0.0013184 | 4.9439e-06 | 266.6667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | POLE | 70 | 6480 | 1975291 | 3.2725 | 0.010735 | 304.8289
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 4 | 4 | 791 | 0.0013035 | 6.5918e-06 | 197.75
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | CONN/CLAMP | 611 | 830 | 124284 | 0.20743 | 0.0013853 | 149.7398
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 91 | 5892 | 763304 | 1.274 | 0.0098339 | 129.5492
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | POLE | 68 | 2116 | 179543 | 0.29966 | 0.0035317 | 84.8502
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 23 | 448 | 305395 | 0.50595 | 0.0007422 | 681.6853
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | F | CIRCUIT SWITCHER | 1 | 137 | 32469 | 0.053792 | 0.00022697 | 237
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 16 | 28 | 4893 | 0.0081063 | 4.6388e-05 | 174.75
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | SPLICE, OH | 9 | 1909 | 423766 | 0.69476 | 0.0031298 | 221.9832
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 2 | 289 | 0.00047879 | 3.3134e-06 | 144.5
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 19 | 17913 | 0.02952 | 3.1311e-05 | 942.7895
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | CROSSARM | 17 | 901 | 91137 | 0.15099 | 0.0014927 | 101.1509
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TIR | NONE | 2 | 15 | 936 | 0.0015622 | 2.5035e-05 | 62.4
AEP-I&M | 2020 | 599151 | PARTIAL POWER | WW | NONE | 1 | 1 | 111 | 0.00018526 | 1.669e-06 | 111
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | ABI | NONE | 6 | 4515 | 882560 | 1.4621 | 0.00748 | 195.4729
AEP-I&M | 2024 | 614045 | TRANSMISSION STATION | ERF | NONE | 2 | 1059 | 20121 | 0.032768 | 0.0017246 | 19
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 7 | 489 | 443558 | 0.72721 | 0.00080171 | 907.0716
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 3 | 2549 | 114705 | 0.18806 | 0.004179 | 45
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | BREAKER | 2 | 2111 | 361851 | 0.59631 | 0.0034788 | 171.4121
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 305 | 0.00050263 | 1.648e-06 | 305
AEP-I&M | 2022 | 606813 | PARTIAL POWER | OL | FUSE | 1 | 1 | 116 | 0.00019116 | 1.648e-06 | 116
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 77 | 4389 | 0.0073254 | 0.00012852 | 57
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CF | CONN/CLAMP | 1 | 1 | 116 | 0.00019218 | 1.6567e-06 | 116
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 231 | 63756 | 0.10641 | 0.00038555 | 276
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CE | FUSE | 1 | 5 | 280 | 0.00046733 | 8.3451e-06 | 56
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 1 | 299 | 0.00049904 | 1.669e-06 | 299
AEP-I&M | 2025 | 614045 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 1 | 72 | 0.00011726 | 1.6285e-06 | 72
AEP-I&M | 2025 | 614045 | TRANSMISSION LINE | EQF | INSULATOR | 6 | 3884 | 92573 | 0.15076 | 0.0063253 | 23.8344
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 2 | 56 | 24776 | 0.040349 | 9.1199e-05 | 442.4286
AEP-I&M | 2024 | 614045 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 1 | 1026 | 0.0016709 | 1.6285e-06 | 1026
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 1 | 57 | 9.2827e-05 | 1.6285e-06 | 57
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | CONN/CLAMP | 1 | 403 | 29822 | 0.049145 | 0.00066413 | 74
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 90 | 18450 | 0.030794 | 0.00015021 | 205
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | CROSSARM | 1 | 199 | 52735 | 0.086905 | 0.00032794 | 265
AEP-I&M | 2022 | 606813 | TRANSMISSION STATION | SCO | SWITCH, OH | 1 | 351 | 19305 | 0.031814 | 0.00057843 | 55
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 207 | 24426 | 0.040467 | 0.00034294 | 118
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | SCO | CONDUCTOR OVERHEAD | 1 | 39 | 351 | 0.00057843 | 6.427e-05 | 9
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | POLE | 67 | 9146 | 1909784 | 3.1472 | 0.015072 | 208.8108
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | NONE | 1191 | 15159 | 1544665 | 2.5591 | 0.025114 | 101.8976
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 7 | 1039 | 95941 | 0.15811 | 0.0017122 | 92.3397
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | FUSE | 405 | 3391 | 391641 | 0.64883 | 0.0056179 | 115.4942
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CO | CABLE TERMINATOR | 15 | 30 | 3182 | 0.0052438 | 4.9439e-05 | 106.0667
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | CROSSARM | 42 | 13277 | 1389291 | 2.2895 | 0.02188 | 104.6389
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | NONE | 300 | 13569 | 1309460 | 2.1694 | 0.02248 | 96.5038
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | NONE | 32 | 32 | 10122 | 0.016769 | 5.3015e-05 | 316.3125
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | CONN/CLAMP | 38 | 141 | 21148 | 0.035297 | 0.00023533 | 149.9858
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | POLE | 295 | 49183 | 10775284 | 17.9843 | 0.082088 | 219.0855
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | CUTOUT | 3 | 5 | 953 | 0.0015906 | 8.3451e-06 | 190.6
AEP-I&M | 2022 | 606813 | PARTIAL POWER | FW | METERING | 1 | 6 | 377 | 0.00062128 | 9.8877e-06 | 62.8333
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 11 | 239 | 26657 | 0.04393 | 0.00039386 | 111.5356
AEP-I&M | 2021 | 603608 | PARTIAL POWER | UG | CONDUCTOR UG | 28 | 31 | 7960 | 0.013187 | 5.1358e-05 | 256.7742
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 2 | 450 | 0.00074552 | 3.3134e-06 | 225
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | JUMPER/RISER | 8 | 43 | 3657 | 0.0060266 | 7.0862e-05 | 85.0465
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | CUTOUT | 3 | 23 | 24141 | 0.039994 | 3.8104e-05 | 1049.6087
AEP-I&M | 2022 | 606813 | SUBTRANSMISSION LINE | TOR | NONE | 1 | 958 | 189885 | 0.31292 | 0.0015787 | 198.2098
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TR | NONE | 28 | 1826 | 460136 | 0.76798 | 0.0030476 | 251.9912
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WI | NONE | 24 | 632 | 127450 | 0.21003 | 0.0010415 | 201.6614
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CO | METERING | 1 | 1 | 157 | 0.00025873 | 1.648e-06 | 157
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | CROSSARM | 2 | 2 | 387 | 0.00063776 | 3.2959e-06 | 193.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | METERING | 2 | 2 | 224 | 0.00036914 | 3.2959e-06 | 112
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ABI | NONE | 194 | 2845 | 356933 | 0.59573 | 0.0047484 | 125.4598
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | O | CONDUCTOR UG | 2 | 2 | 440 | 0.0007251 | 3.2959e-06 | 220
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ABI | ARRESTER | 3 | 6 | 512 | 0.00084375 | 9.8877e-06 | 85.3333
AEP-I&M | 2020 | 599151 | TRANSMISSION STATION | SCO | NONE | 7 | 4603 | 63792 | 0.10647 | 0.0076825 | 13.8588
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 7 | 1167 | 90337 | 0.14811 | 0.0019133 | 77.4096
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 33 | 3344 | 0.0054824 | 5.4103e-05 | 101.3333
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 55 | 1897 | 719959 | 1.2016 | 0.0031661 | 379.525
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 74 | 21386 | 0.03543 | 0.0001226 | 289
AEP-I&M | 2020 | 599151 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 162 | 0.00027038 | 1.669e-06 | 162
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | POLE | 6 | 2700 | 1199360 | 1.9532 | 0.0043971 | 444.2074
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | CROSSARM | 3 | 169 | 12871 | 0.021102 | 0.00027707 | 76.1598
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 1 | 112 | 0.0001824 | 1.6285e-06 | 112
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 4 | 1003 | 369588 | 0.60593 | 0.0016444 | 368.4826
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | CUTOUT | 2 | 11 | 516 | 0.00084597 | 1.8034e-05 | 46.9091
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OU | FUSE | 1 | 8 | 2056 | 0.0034315 | 1.3352e-05 | 257
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | ARRESTER | 47 | 4396 | 726749 | 1.1835 | 0.0071591 | 165.3205
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WL | NONE | 5 | 5 | 440 | 0.00071656 | 8.1427e-06 | 88
AEP-I&M | 2025 | 614045 | PARTIAL POWER | UG | CONDUCTOR OVERHEAD | 1 | 1 | 60 | 9.7713e-05 | 1.6285e-06 | 60
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | CUTOUT | 719 | 24503 | 2984820 | 4.9188 | 0.04038 | 121.8145
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | NONE | 53 | 2862 | 299607 | 0.49374 | 0.0047164 | 104.6845
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | SWITCH, OH | 7 | 2131 | 105360 | 0.17363 | 0.0035118 | 49.4416
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CE | FUSE | 1 | 8 | 1376 | 0.0022676 | 1.3184e-05 | 172
AEP-I&M | 2022 | 606813 | PARTIAL POWER | U | FUSE | 13 | 19 | 1240 | 0.0020435 | 3.1311e-05 | 65.2632
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | EQF | CROSSARM | 2 | 212 | 67474 | 0.11178 | 0.00035122 | 318.2736
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UB | CUTOUT | 1 | 2 | 674 | 0.0011107 | 3.2959e-06 | 337
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | SPLICE, OH | 12 | 12 | 2340 | 0.0038767 | 1.988e-05 | 195
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | CONDUCTOR UG | 331 | 435 | 119368 | 0.19923 | 0.00072603 | 274.4092
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FO | FUSE | 7 | 339 | 31383 | 0.052379 | 0.0005658 | 92.5752
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | CROSSARM | 12 | 7116 | 691362 | 1.1454 | 0.011789 | 97.156
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 5 | 7 | 362 | 0.00059973 | 1.1597e-05 | 51.7143
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | INSULATOR | 60 | 12205 | 1783501 | 2.9767 | 0.02037 | 146.1287
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | BREAKER | 2 | 1614 | 464612 | 0.77545 | 0.0026938 | 287.8637
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 7 | 602 | 0.00099207 | 1.1536e-05 | 86
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | CABLE TERMINATOR | 23 | 37 | 4379 | 0.0073087 | 6.1754e-05 | 118.3514
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 27 | 80 | 14588 | 0.024348 | 0.00013352 | 182.35
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 1 | 56 | 9352 | 0.015412 | 9.2285e-05 | 167
AEP-I&M | 2020 | 599151 | PARTIAL POWER | VA | TRANSFORMER, UG | 1 | 1 | 66 | 0.00011016 | 1.669e-06 | 66
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 3 | 445 | 0.00073723 | 4.9701e-06 | 148.3333
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | CUTOUT | 1 | 1 | 55 | 9.1119e-05 | 1.6567e-06 | 55
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 1117 | 0.0018408 | 1.648e-06 | 1117
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | FUSE | 3 | 103 | 8518 | 0.014217 | 0.00017191 | 82.699
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 199 | 65159 | 0.10683 | 0.00032626 | 327.4322
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | UG | NONE | 35 | 208 | 30181 | 0.049151 | 0.00033874 | 145.101
AEP-I&M | 2023 | 609949 | TRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 730 | 273020 | 0.44761 | 0.0011968 | 374
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | PEDESTAL | 115 | 472 | 23708 | 0.03861 | 0.00076867 | 50.2288
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FO | FUSE | 1 | 3 | 282 | 0.00046719 | 4.9701e-06 | 94
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 241 | 32048 | 0.052814 | 0.00039716 | 132.9793
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CE | NONE | 1 | 1 | 402 | 0.00066248 | 1.648e-06 | 402
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | METERING | 1 | 1 | 138 | 0.00022742 | 1.648e-06 | 138
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | CUTOUT | 5 | 122 | 24741 | 0.040292 | 0.00019868 | 202.7951
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 6 | 6 | 901 | 0.0014927 | 9.9402e-06 | 150.1667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 2 | 1619 | 0.0026822 | 3.3134e-06 | 809.5
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | CONDUCTOR UG | 143 | 163 | 30946 | 0.050397 | 0.00026545 | 189.8528
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | UG | NONE | 10 | 25 | 3324 | 0.0054133 | 4.0714e-05 | 132.96
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 27 | 141 | 65304 | 0.10635 | 0.00022962 | 463.1489
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VIN | NONE | 3 | 58 | 5641 | 0.0091866 | 9.4456e-05 | 97.2586
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 7 | 198 | 16075 | 0.026179 | 0.00032245 | 81.1869
AEP-I&M | 2020 | 599151 | DISTRIBUTION SOURCE | A | CONDUCTOR OVERHEAD | 1 | 1282 | 161965 | 0.27032 | 0.0021397 | 126.3378
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CE | POLE | 1 | 2 | 706 | 0.0011783 | 3.3381e-06 | 353
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1 | 177 | 0.00029324 | 1.6567e-06 | 177
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 3 | 18 | 2266 | 0.0036903 | 2.9314e-05 | 125.8889
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WI | NONE | 1 | 69 | 8211 | 0.013704 | 0.00011516 | 119
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 561 | 59466 | 0.096843 | 0.00091361 | 106
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 12 | 120 | 0.00019543 | 1.9543e-05 | 10
AEP-I&M | 2025 | 614045 | PARTIAL POWER | UG | CONDUCTOR UG | 4 | 10 | 2329 | 0.0037929 | 1.6285e-05 | 232.9
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 6 | 2757 | 350543 | 0.57088 | 0.0044899 | 127.1465
AEP-I&M | 2024 | 614045 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 14 | 3443 | 0.0056071 | 2.28e-05 | 245.9286
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 84 | 0.0001368 | 1.6285e-06 | 84
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | REGULATOR | 3 | 2265 | 189545 | 0.30868 | 0.0036887 | 83.6843
AEP-I&M | 2025 | 614045 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 1 | 1 | 503 | 0.00081916 | 1.6285e-06 | 503
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | POLE | 1 | 4 | 164 | 0.00026708 | 6.5142e-06 | 41
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 3 | 3 | 66 | 0.00010748 | 4.8856e-06 | 22
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 19 | 3.1311e-05 | 1.648e-06 | 19
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 8 | 1456 | 0.0023994 | 1.3184e-05 | 182
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 1 | 454 | 0.00074817 | 1.648e-06 | 454
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 10 | 760 | 0.0012685 | 1.669e-05 | 76
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 66 | 0.00010934 | 1.6567e-06 | 66
AEP-I&M | 2020 | 599151 | PARTIAL POWER | WU | CUTOUT | 1 | 3 | 216 | 0.00036051 | 5.0071e-06 | 72
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 20 | 5660 | 0.0093769 | 3.3134e-05 | 283
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TOR | INSULATOR | 1 | 1 | 132 | 0.00021753 | 1.648e-06 | 132
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 1 | 343 | 0.00056234 | 1.6395e-06 | 343
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 1 | 352 | 0.0005875 | 1.669e-06 | 352
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WI | POLE | 1 | 102 | 51510 | 0.084886 | 0.00016809 | 505
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 1 | 125 | 0.00020357 | 1.6285e-06 | 125
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 66 | 0.00010748 | 1.6285e-06 | 66
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | SCO | REGULATOR | 3 | 5134 | 40221 | 0.066634 | 0.0085055 | 7.8342
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FO | FUSE | 7 | 155 | 12455 | 0.020284 | 0.00025242 | 80.3548
AEP-I&M | 2023 | 609949 | PARTIAL POWER | CO | CONDUCTOR UG | 1 | 1 | 195 | 0.0003197 | 1.6395e-06 | 195
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 448 | 0.00073828 | 1.648e-06 | 448
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WI | NONE | 20 | 3773 | 2661377 | 4.3633 | 0.0061858 | 705.3742
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 6 | 4097 | 0.006838 | 1.0014e-05 | 682.8333
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | EQF | SWITCH, OH | 6 | 6742 | 876195 | 1.4516 | 0.01117 | 129.9607
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | FUSE | 3 | 45 | 3498 | 0.0056967 | 7.3285e-05 | 77.7333
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 19 | 1387 | 0.0022588 | 3.0942e-05 | 73
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TR | FUSE | 3 | 26 | 4144 | 0.0067487 | 4.2342e-05 | 159.3846
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 25 | 4800 | 0.007817 | 4.0714e-05 | 192
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 44 | 572 | 0.00093153 | 7.1656e-05 | 13
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | NONE | 1757 | 14932 | 1264201 | 2.0833 | 0.024607 | 84.6639
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | NONE | 4 | 4 | 631 | 0.0010399 | 6.5918e-06 | 157.75
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CE | METERING | 2 | 6 | 436 | 0.00071851 | 9.8877e-06 | 72.6667
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | POLE | 42 | 2072 | 158871 | 0.26181 | 0.0034146 | 76.6752
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERF | NONE | 28 | 1280 | 32630 | 0.054058 | 0.0021206 | 25.4922
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CO | CONDUCTOR UG | 17 | 17 | 3499 | 0.0057968 | 2.8164e-05 | 205.8235
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 1 | 2 | 1542 | 0.0025546 | 3.3134e-06 | 771
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | NONE | 703 | 30473 | 7806452 | 13.0292 | 0.05086 | 256.176
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ABI | FUSE | 52 | 159 | 13616 | 0.022558 | 0.00026342 | 85.6352
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 1 | 1 | 250 | 0.00041418 | 1.6567e-06 | 250
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 52 | 8.5694e-05 | 1.648e-06 | 52
AEP-I&M | 2021 | 603608 | PARTIAL POWER | UG | PEDESTAL | 1 | 1 | 163 | 0.00027004 | 1.6567e-06 | 163
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 197 | 7190 | 0.011912 | 0.00032637 | 36.4975
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | NETWORK PROTECTOR | 1 | 2 | 56 | 9.2285e-05 | 3.2959e-06 | 28
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 44 | 5508 | 0.0090303 | 7.2137e-05 | 125.1818
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | NONE | 194 | 3007 | 484390 | 0.79415 | 0.0049299 | 161.0875
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | CONN/CLAMP | 379 | 600 | 64416 | 0.1049 | 0.00097713 | 107.36
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | NONE | 205 | 9888 | 2185648 | 3.5594 | 0.016103 | 221.0405
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 8 | 8 | 1761 | 0.0028871 | 1.3116e-05 | 220.125
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 2 | 2 | 1369 | 0.002268 | 3.3134e-06 | 684.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OL | FUSE | 6 | 974 | 135879 | 0.22679 | 0.0016256 | 139.5062
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 20 | 266 | 35372 | 0.057605 | 0.00043319 | 132.9774
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 7 | 161 | 9492 | 0.015842 | 0.00026871 | 58.9565
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 12 | 4902 | 0.0079831 | 1.9543e-05 | 408.5
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | AO | NONE | 6 | 5620 | 400726 | 0.65698 | 0.0092139 | 71.3036
AEP-I&M | 2023 | 609949 | PARTIAL POWER | WW | NONE | 1 | 1 | 566 | 0.00092795 | 1.6395e-06 | 566
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 1 | 76 | 0.0001246 | 1.6395e-06 | 76
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | SWITCH, OH | 2 | 294 | 55933 | 0.092175 | 0.0004845 | 190.2483
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 1177 | 56392 | 0.091837 | 0.0019168 | 47.9116
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | NONE | 41 | 4114 | 323782 | 0.52729 | 0.0066998 | 78.7025
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | CUTOUT | 432 | 2229 | 99176 | 0.16151 | 0.00363 | 44.4935
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 4 | 46 | 9271 | 0.015098 | 7.4913e-05 | 201.5435
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | CONN/CLAMP | 132 | 177 | 16825 | 0.0274 | 0.00028825 | 95.0565
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | FUSE | 11 | 11 | 1240 | 0.0020194 | 1.7914e-05 | 112.7273
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | A | FUSE | 71 | 1306 | 75124 | 0.12234 | 0.0021269 | 57.5222
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | ARRESTER | 8 | 72 | 6571 | 0.010701 | 0.00011726 | 91.2639
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 6 | 21 | 1669 | 0.002718 | 3.4199e-05 | 79.4762
AEP-I&M | 2020 | 599151 | TRANSMISSION STATION | R | NONE | 2 | 2 | 301 | 0.00050238 | 3.3381e-06 | 150.5
AEP-I&M | 2025 | 614045 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 394 | 27580 | 0.044915 | 0.00064165 | 70
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 2 | 739 | 0.0012334 | 3.3381e-06 | 369.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | CUTOUT | 4 | 19 | 2281 | 0.0038071 | 3.1712e-05 | 120.0526
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | REGULATOR | 2 | 81 | 13994 | 0.023184 | 0.00013419 | 172.7654
AEP-I&M | 2024 | 614045 | PARTIAL POWER | UG | CONDUCTOR UG | 7 | 12 | 3285 | 0.0053498 | 1.9543e-05 | 273.75
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 214 | 0.00035717 | 1.669e-06 | 214
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 6 | 2028 | 0.0033027 | 9.7713e-06 | 338
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | ARRESTER | 4 | 4 | 376 | 0.00061233 | 6.5142e-06 | 94
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 281 | 12557 | 0.02045 | 0.00045762 | 44.6868
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | NONE | 395 | 26922 | 4979791 | 8.1643 | 0.044138 | 184.9711
AEP-I&M | 2023 | 609949 | PARTIAL POWER | ABI | NONE | 13 | 24 | 2140 | 0.0035085 | 3.9348e-05 | 89.1667
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 10 | 456 | 106725 | 0.17813 | 0.00076108 | 234.0461
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | CUTOUT | 4 | 29 | 7583 | 0.012656 | 4.8402e-05 | 261.4828
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 458 | 9698 | 742153 | 1.2086 | 0.015794 | 76.5264
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 12 | 4773 | 0.0079074 | 1.988e-05 | 397.75
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 2 | 1168 | 0.0019248 | 3.2959e-06 | 584
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 8 | 639 | 0.0010406 | 1.3028e-05 | 79.875
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | NONE | 80 | 774 | 165267 | 0.26914 | 0.0012605 | 213.5233
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | METERING | 4 | 4 | 518 | 0.00084359 | 6.5142e-06 | 129.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | CONN/CLAMP | 6 | 59 | 2033 | 0.0033931 | 9.8473e-05 | 34.4576
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 23 | 1725 | 0.0028092 | 3.7457e-05 | 75
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 1 | 314 | 0.00052021 | 1.6567e-06 | 314
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | POLE | 2 | 17 | 2209 | 0.0036869 | 2.8373e-05 | 129.9412
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 5 | 12 | 2218 | 0.0036121 | 1.9543e-05 | 184.8333
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 5 | 3005 | 0.0050154 | 8.3451e-06 | 601
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 1 | 87 | 0.00014521 | 1.669e-06 | 87
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERO | TRANSFORMER, OH | 1 | 1 | 500 | 0.00081974 | 1.6395e-06 | 500
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 939 | 0.0015292 | 1.6285e-06 | 939
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 205 | 15580 | 0.025373 | 0.00033385 | 76
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | CE | METERING | 1 | 8 | 1360 | 0.0022148 | 1.3028e-05 | 170
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 4 | 76 | 0.00012377 | 6.5142e-06 | 19
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | CUTOUT | 8 | 885 | 78121 | 0.12874 | 0.0014584 | 88.2723
AEP-I&M | 2022 | 606813 | PARTIAL POWER | U | NONE | 60 | 234 | 20650 | 0.03403 | 0.00038562 | 88.2479
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VIN | FUSE | 35 | 263 | 27620 | 0.045516 | 0.00043341 | 105.019
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 12 | 1240 | 330523 | 0.54758 | 0.0020543 | 266.5508
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 5 | 4390 | 139674 | 0.23018 | 0.0072345 | 31.8164
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 5 | 884 | 0.0014568 | 8.2398e-06 | 176.8
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 31 | 14288 | 0.023546 | 5.1087e-05 | 460.9032
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 13 | 224 | 44777 | 0.074182 | 0.0003711 | 199.8973
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 17 | 22 | 3022 | 0.0049801 | 3.6255e-05 | 137.3636
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 9 | 11 | 5064 | 0.0083452 | 1.8127e-05 | 460.3636
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | VA | POLE | 2 | 2681 | 522054 | 0.86032 | 0.0044182 | 194.7236
AEP-I&M | 2021 | 603608 | PARTIAL POWER | FO | NONE | 2 | 21 | 2673 | 0.0044284 | 3.4791e-05 | 127.2857
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 1 | 115 | 0.00018951 | 1.648e-06 | 115
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 13 | 30160 | 0.049702 | 2.1423e-05 | 2320
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | POLE | 14 | 1965 | 1016662 | 1.6843 | 0.0032554 | 517.3852
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 1473 | 183950 | 0.30475 | 0.0024403 | 124.8812
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 15 | 2475 | 0.0040787 | 2.4719e-05 | 165
AEP-I&M | 2022 | 606813 | TRANSMISSION STATION | R | NONE | 2 | 2677 | 708739 | 1.168 | 0.0044116 | 264.7512
AEP-I&M | 2020 | 599151 | PARTIAL POWER | WL | NONE | 8 | 10 | 3470 | 0.0057915 | 1.669e-05 | 347
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | CROSSARM | 42 | 886 | 41370 | 0.067825 | 0.0014526 | 46.693
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 1 | 291 | 0.00047955 | 1.648e-06 | 291
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 467 | 27257 | 3581100 | 5.832 | 0.044389 | 131.3828
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | NONE | 388 | 16412 | 3737107 | 6.086 | 0.026728 | 227.7058
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | FUSE | 11 | 207 | 87799 | 0.14654 | 0.00034549 | 424.1498
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | SPLICE, OH | 6 | 77 | 10092 | 0.016719 | 0.00012757 | 131.0649
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 12 | 63 | 5849 | 0.0095893 | 0.00010329 | 92.8413
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TR | FUSE | 6 | 129 | 94798 | 0.15822 | 0.0002153 | 734.8682
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | PEDESTAL | 16 | 138 | 7201 | 0.012019 | 0.00023033 | 52.1812
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | NONE | 219 | 5850 | 705317 | 1.1486 | 0.009527 | 120.567
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | ARRESTER | 16 | 158 | 29016 | 0.047254 | 0.00025731 | 183.6456
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | AF | POLE | 1 | 567 | 6804 | 0.011213 | 0.00093439 | 12
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 5 | 18 | 2358 | 0.0039356 | 3.0043e-05 | 131
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CE | CONN/CLAMP | 2 | 2 | 207 | 0.00034294 | 3.3134e-06 | 103.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | NONE | 135 | 13505 | 1664573 | 2.7108 | 0.021994 | 123.2561
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | FW | POLE | 1 | 281 | 170005 | 0.28374 | 0.000469 | 605
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | ERF | NONE | 1 | 655 | 34060 | 0.056427 | 0.0010851 | 52
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 2625 | 693000 | 1.1481 | 0.0043488 | 264
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERO | CUTOUT | 1 | 37 | 814 | 0.0013414 | 6.0974e-05 | 22
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | INSULATOR | 3 | 1057 | 136571 | 0.22626 | 0.0017511 | 129.2062
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 185 | 1639 | 114740 | 0.18686 | 0.0026692 | 70.0061
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | METERING | 13 | 13 | 882 | 0.0014364 | 2.1171e-05 | 67.8462
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TR | NONE | 12 | 107 | 9261 | 0.015082 | 0.00017425 | 86.5514
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 13 | 1943 | 336550 | 0.54809 | 0.0031643 | 173.2115
AEP-I&M | 2024 | 614045 | PARTIAL POWER | A | CONN/CLAMP | 1 | 1 | 34 | 5.5371e-05 | 1.6285e-06 | 34
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TR | NONE | 22 | 1326 | 149219 | 0.24301 | 0.0021595 | 112.5332
AEP-I&M | 2020 | 599151 | PARTIAL POWER | WU | NONE | 2 | 2 | 1605 | 0.0026788 | 3.3381e-06 | 802.5
AEP-I&M | 2025 | 614045 | PARTIAL POWER | FO | NONE | 2 | 2 | 77 | 0.0001254 | 3.2571e-06 | 38.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | PEDESTAL | 1 | 4 | 472 | 0.00078778 | 6.6761e-06 | 118
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 105 | 0.00017395 | 3.3134e-06 | 52.5
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | PEDESTAL | 1 | 10 | 150 | 0.00024851 | 1.6567e-05 | 15
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WL | TRANSFORMER, OH | 2 | 2 | 484 | 0.00078822 | 3.2571e-06 | 242
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | METERING | 1 | 1 | 13 | 2.1171e-05 | 1.6285e-06 | 13
AEP-I&M | 2020 | 599151 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 5 | 5 | 996 | 0.0016624 | 8.3451e-06 | 199.2
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | SWITCH, OH | 1 | 311 | 8708 | 0.014181 | 0.00050648 | 28
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 1 | 1 | 68 | 0.00011148 | 1.6395e-06 | 68
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | FUSE | 3 | 19 | 3115 | 0.0050729 | 3.0942e-05 | 163.9474
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1 | 31 | 5.0485e-05 | 1.6285e-06 | 31
AEP-I&M | 2025 | 614045 | PARTIAL POWER | ABI | NONE | 1 | 1 | 70 | 0.000114 | 1.6285e-06 | 70
AEP-I&M | 2025 | 614045 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 109 | 0.00017751 | 1.6285e-06 | 109
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | ARRESTER | 2 | 79 | 9633 | 0.015688 | 0.00012866 | 121.9367
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 1 | 1 | 342 | 0.0005636 | 1.648e-06 | 342
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OL | FUSE | 2 | 3 | 231 | 0.00038068 | 4.9439e-06 | 77
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 1 | 587 | 0.00097972 | 1.669e-06 | 587
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 1 | 1396 | 0.0022734 | 1.6285e-06 | 1396
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 5 | 6775 | 0.011165 | 8.2398e-06 | 1355
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 56 | 5432 | 0.0089992 | 9.2775e-05 | 97
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 130 | 42846 | 0.069777 | 0.00021171 | 329.5846
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 516 | 0.00085486 | 1.6567e-06 | 516
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 2 | 42 | 6188 | 0.010198 | 6.9214e-05 | 147.3333
AEP-I&M | 2024 | 614045 | DISTRIBUTION STATION | AO | SWITCH, OH | 2 | 552 | 74520 | 0.12136 | 0.00089896 | 135
AEP-I&M | 2024 | 614045 | DISTRIBUTION STATION | EQF | TRANSFORMER, GROUNDING | 1 | 558 | 74772 | 0.12177 | 0.00090873 | 134
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | SCO | BREAKER | 1 | 2517 | 114752 | 0.18911 | 0.0041479 | 45.5908
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 1 | 1 | 83 | 0.00013517 | 1.6285e-06 | 83
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CE | NONE | 1 | 1 | 258 | 0.00043061 | 1.669e-06 | 258
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 2 | 10 | 6429 | 0.01073 | 1.669e-05 | 642.9
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 2 | 16 | 2730 | 0.0044459 | 2.6057e-05 | 170.625
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 1 | 39 | 6.3513e-05 | 1.6285e-06 | 39
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 2 | 306 | 0.00050168 | 3.279e-06 | 153
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ABI | CUTOUT | 1 | 2 | 156 | 0.00025708 | 3.2959e-06 | 78
AEP-I&M | 2023 | 609949 | PARTIAL POWER | ABI | CUTOUT | 1 | 4 | 452 | 0.00074105 | 6.5579e-06 | 113
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 2 | 137 | 19571 | 0.032086 | 0.00022461 | 142.854
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 1 | 75 | 0.00012425 | 1.6567e-06 | 75
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 1 | 10 | 15420 | 0.025112 | 1.6285e-05 | 1542
AEP-I&M | 2024 | 614045 | DISTRIBUTION STATION | SCO | TRANSFORMER, POWER - LTC | 4 | 1839 | 446877 | 0.72776 | 0.0029949 | 243
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WI | METERING | 1 | 1 | 149 | 0.00024685 | 1.6567e-06 | 149
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | EQF | BREAKER | 3 | 2207 | 617109 | 1.017 | 0.003637 | 279.6144
AEP-I&M | 2021 | 603608 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 2 | 146 | 0.00024188 | 3.3134e-06 | 73
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 1 | 303 | 0.00049676 | 1.6395e-06 | 303
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | U | NONE | 773 | 21509 | 3162218 | 5.2389 | 0.035634 | 147.0184
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | INSULATOR | 55 | 13892 | 1990929 | 3.281 | 0.022893 | 143.3148
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1502 | 46318 | 13081910 | 21.6729 | 0.076735 | 282.4368
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | POLE | 317 | 57678 | 9406103 | 15.5831 | 0.095555 | 163.0796
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | CONDUCTOR UG | 3 | 30 | 9367 | 0.015436 | 4.9439e-05 | 312.2333
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | NONE | 661 | 13419 | 1749172 | 2.9194 | 0.022397 | 130.3504
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | FUSE | 129 | 2902 | 537079 | 0.8964 | 0.0048435 | 185.072
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 2 | 518 | 16252 | 0.026925 | 0.00085817 | 31.3745
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 5 | 41 | 11917 | 0.01989 | 6.843e-05 | 290.6585
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | JUMPER/RISER | 6 | 34 | 6368 | 0.010628 | 5.6747e-05 | 187.2941
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 4 | 133 | 60215 | 0.099758 | 0.00022034 | 452.7444
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CF | NONE | 2 | 8 | 584 | 0.00096752 | 1.3254e-05 | 73
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 25 | 353 | 154697 | 0.25819 | 0.00058917 | 438.2351
AEP-I&M | 2021 | 603608 | PARTIAL POWER | O | NONE | 2 | 2 | 263 | 0.00043571 | 3.3134e-06 | 131.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VIN | NONE | 78 | 559 | 106467 | 0.1777 | 0.00093299 | 190.4597
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 2168 | 126707 | 0.20992 | 0.0035917 | 58.4442
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 265 | 2018 | 331787 | 0.54396 | 0.0033085 | 164.4138
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | CUTOUT | 34 | 2685 | 382347 | 0.62685 | 0.004402 | 142.4011
AEP-I&M | 2024 | 614045 | TRANSMISSION STATION | EQF | INSULATOR | 6 | 2918 | 462555 | 0.75329 | 0.0047521 | 158.5178
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | FUSE | 34 | 341 | 45029 | 0.073332 | 0.00055533 | 132.0499
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | INSULATOR | 21 | 7292 | 771850 | 1.257 | 0.011875 | 105.8489
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | V | METERING | 5 | 5 | 488 | 0.00079473 | 8.1427e-06 | 97.6
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | CUTOUT | 3 | 6 | 3387 | 0.0055159 | 9.7713e-06 | 564.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION SOURCE | CE | INSULATOR | 1 | 1281 | 156387 | 0.26101 | 0.002138 | 122.082
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | POLE HARDWARE | 3 | 431 | 39567 | 0.064437 | 0.0007019 | 91.8028
AEP-I&M | 2024 | 614045 | TRANSMISSION STATION | ERO | NONE | 2 | 2884 | 60564 | 0.098631 | 0.0046967 | 21
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | SWITCH, OH | 1 | 498 | 4212 | 0.0070299 | 0.00083118 | 8.4578
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 2 | 239 | 22252 | 0.036238 | 0.00038922 | 93.1046
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 4 | 712 | 0.0011733 | 6.5918e-06 | 178
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 251 | 4267 | 0.006949 | 0.00040876 | 17
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 10 | 1530 | 0.0025084 | 1.6395e-05 | 153
AEP-I&M | 2024 | 614045 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 6 | 798 | 0.0012996 | 9.7713e-06 | 133
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 50 | 8.1974e-05 | 1.6395e-06 | 50
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 52 | 57262 | 0.093254 | 8.4684e-05 | 1101.1923
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | ARRESTER | 1 | 1 | 12 | 1.9543e-05 | 1.6285e-06 | 12
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 3 | 511 | 45247 | 0.073687 | 0.00083219 | 88.546
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 224 | 16784 | 0.027334 | 0.00036479 | 74.9286
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 5 | 540 | 0.00087941 | 8.1427e-06 | 108
AEP-I&M | 2023 | 609949 | PARTIAL POWER | ERF | METERING | 1 | 1 | 20 | 3.279e-05 | 1.6395e-06 | 20
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 167 | 20708 | 0.034126 | 0.00027521 | 124
AEP-I&M | 2020 | 599151 | PARTIAL POWER | UB | CONDUCTOR UG | 2 | 2 | 427 | 0.00071268 | 3.3381e-06 | 213.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CF | NONE | 2 | 913 | 139335 | 0.23255 | 0.0015238 | 152.6123
AEP-I&M | 2023 | 609949 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 250 | 0.00040987 | 1.6395e-06 | 250
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 1 | 1448 | 0.0024168 | 1.669e-06 | 1448
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | AB | CUTOUT | 3 | 3265 | 1294248 | 2.1329 | 0.0053806 | 396.4006
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 8 | 1520 | 0.0025049 | 1.3184e-05 | 190
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 6 | 7578 | 0.012555 | 9.9402e-06 | 1263
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 203 | 0.00033453 | 1.648e-06 | 203
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 1 | 128 | 0.00021364 | 1.669e-06 | 128
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 1 | 382 | 0.00063757 | 1.669e-06 | 382
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 37 | 29526 | 0.04928 | 6.1754e-05 | 798
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 2 | 5 | 477 | 0.00078607 | 8.2398e-06 | 95.4
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | SPLICE, OH | 6 | 50 | 9379 | 0.015456 | 8.2398e-05 | 187.58
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 904 | 193994 | 0.31969 | 0.0014898 | 214.5951
AEP-I&M | 2022 | 606813 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 9 | 9 | 1233 | 0.0020319 | 1.4832e-05 | 137
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 96 | 837 | 76045 | 0.12467 | 0.0013722 | 90.8542
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 6 | 989 | 72096 | 0.11944 | 0.0016385 | 72.8979
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WI | CONN/CLAMP | 12 | 16 | 6248 | 0.010351 | 2.6507e-05 | 390.5
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | FUSE | 18 | 55 | 4012 | 0.0065776 | 9.0171e-05 | 72.9455
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ABI | FUSE | 55 | 195 | 18531 | 0.030929 | 0.00032546 | 95.0308
AEP-I&M | 2023 | 609949 | PARTIAL POWER | UG | CONDUCTOR UG | 18 | 96 | 23511 | 0.038546 | 0.00015739 | 244.9062
AEP-I&M | 2023 | 609949 | PARTIAL POWER | A | NONE | 72 | 119 | 11058 | 0.018129 | 0.0001951 | 92.9244
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 11 | 11 | 1317 | 0.0021592 | 1.8034e-05 | 119.7273
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | CUTOUT | 7 | 3813 | 860838 | 1.4368 | 0.006364 | 225.764
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | NONE | 51 | 1684 | 712383 | 1.189 | 0.0028106 | 423.0303
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 680 | 150960 | 0.2501 | 0.0011266 | 222
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 5 | 959 | 66038 | 0.11022 | 0.0016006 | 68.8613
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | CROSSARM | 2 | 338 | 20481 | 0.034183 | 0.00056413 | 60.5947
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 19 | 1130 | 172432 | 0.2827 | 0.0018526 | 152.5947
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 8 | 1448 | 0.0023989 | 1.3254e-05 | 181
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 404 | 74100 | 0.12368 | 0.00067429 | 183.4158
AEP-I&M | 2020 | 599151 | PARTIAL POWER | U | FUSE | 7 | 26 | 2093 | 0.0034933 | 4.3395e-05 | 80.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 57 | 9391 | 557298 | 0.90758 | 0.015294 | 59.3438
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | REGULATOR | 9 | 4483 | 369602 | 0.60191 | 0.0073008 | 82.4452
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FO | NONE | 22 | 806 | 27037 | 0.044031 | 0.0013126 | 33.5447
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | FUSE | 2 | 10 | 1211 | 0.0019957 | 1.648e-05 | 121.1
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | CUTOUT | 4 | 8 | 939 | 0.0015395 | 1.3116e-05 | 117.375
AEP-I&M | 2022 | 606813 | PARTIAL POWER | O | CONN/CLAMP | 2 | 2 | 340 | 0.0005603 | 3.2959e-06 | 170
AEP-I&M | 2023 | 609949 | PARTIAL POWER | UG | NONE | 5 | 6 | 1097 | 0.0017985 | 9.8369e-06 | 182.8333
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 39 | 14235 | 0.023459 | 6.427e-05 | 365
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TOR | SPLICE, OH | 5 | 5 | 568 | 0.00092501 | 8.1427e-06 | 113.6
AEP-I&M | 2020 | 599151 | PARTIAL POWER | OL | CONN/CLAMP | 3 | 3 | 736 | 0.0012284 | 5.0071e-06 | 245.3333
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 17 | 24 | 6392 | 0.01041 | 3.9085e-05 | 266.3333
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | CAPACITOR | 5 | 2650 | 220350 | 0.36505 | 0.0043903 | 83.1509
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 281 | 33810 | 0.055061 | 0.00045762 | 120.3203
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 17 | 2206 | 0.0036547 | 2.8164e-05 | 129.7647
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 3721 | 807457 | 1.315 | 0.0060598 | 217
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 2612 | 60064 | 0.097817 | 0.0042538 | 22.9954
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TR | NONE | 2 | 2 | 147 | 0.00024535 | 3.3381e-06 | 73.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 4 | 4 | 633 | 0.0010309 | 6.5142e-06 | 158.25
AEP-I&M | 2020 | 599151 | PARTIAL POWER | VA | CUTOUT | 1 | 1 | 75 | 0.00012518 | 1.669e-06 | 75
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CE | METERING | 4 | 4 | 2700 | 0.0045064 | 6.6761e-06 | 675
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WL | CUTOUT | 1 | 1 | 80 | 0.00013254 | 1.6567e-06 | 80
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | UG | POLE | 1 | 7 | 854 | 0.0013908 | 1.14e-05 | 122
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 188 | 0.00030617 | 1.6285e-06 | 188
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 379 | 0.00062457 | 1.648e-06 | 379
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 87 | 5534 | 0.0090729 | 0.00014263 | 63.6092
AEP-I&M | 2023 | 609949 | PARTIAL POWER | WL | CUTOUT | 1 | 1 | 63 | 0.00010329 | 1.6395e-06 | 63
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OL | POLE | 1 | 26 | 3666 | 0.0061187 | 4.3395e-05 | 141
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | AB | INSULATOR | 1 | 1427 | 573654 | 0.95744 | 0.0023817 | 402
AEP-I&M | 2023 | 609949 | SUBTRANSMISSION LINE | EQF | OTHER EQUIPMENT | 1 | 44 | 15400 | 0.025248 | 7.2137e-05 | 350
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 25 | 2199 | 0.0035812 | 4.0714e-05 | 87.96
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 17 | 1377 | 0.0022813 | 2.8164e-05 | 81
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | ARRESTER | 1 | 342 | 23256 | 0.038528 | 0.00056659 | 68
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | BREAKER | 1 | 137 | 10412 | 0.017158 | 0.00022577 | 76
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 2 | 198 | 0.00033047 | 3.3381e-06 | 99
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | EQF | INSULATOR | 3 | 3160 | 939416 | 1.5563 | 0.0052352 | 297.2835
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | FUSE | 1 | 2 | 450 | 0.00074158 | 3.2959e-06 | 225
AEP-I&M | 2022 | 606813 | PARTIAL POWER | A | CUTOUT | 1 | 53 | 12137 | 0.020001 | 8.7342e-05 | 229
AEP-I&M | 2023 | 609949 | PARTIAL POWER | WU | CABLE TERMINATOR | 1 | 1 | 67 | 0.00010985 | 1.6395e-06 | 67
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 2 | 520 | 67160 | 0.11011 | 0.00085253 | 129.1538
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | R | NONE | 1 | 1480 | 433640 | 0.72376 | 0.0024702 | 293
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | NONE | 870 | 25219 | 2932971 | 4.8334 | 0.04156 | 116.3001
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 229 | 4962 | 332675 | 0.54823 | 0.0081771 | 67.0445
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 75 | 1390 | 878838 | 1.4483 | 0.0022907 | 632.2576
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | ARRESTER | 42 | 2371 | 200216 | 0.32825 | 0.0038872 | 84.4437
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | REGULATOR | 2 | 157 | 2307 | 0.003822 | 0.0002601 | 14.6943
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TOR | CONN/CLAMP | 7 | 13 | 9726 | 0.016028 | 2.1423e-05 | 748.1538
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VIN | CABLE TERMINATOR | 1 | 1 | 93 | 0.00015326 | 1.648e-06 | 93
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 8 | 96 | 28624 | 0.047171 | 0.0001582 | 298.1667
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 103 | 10918 | 0.017992 | 0.00016974 | 106
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | NONE | 1389 | 19502 | 2279749 | 3.7376 | 0.031973 | 116.8982
AEP-I&M | 2021 | 603608 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 380 | 0.00062955 | 3.3134e-06 | 190
AEP-I&M | 2020 | 599151 | TRANSMISSION STATION | ERF | NONE | 12 | 6531 | 227893 | 0.38036 | 0.0109 | 34.894
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FO | NONE | 20 | 2452 | 313169 | 0.51343 | 0.00402 | 127.7198
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | CUTOUT | 752 | 4018 | 116735 | 0.19011 | 0.0065435 | 29.053
AEP-I&M | 2023 | 609949 | PARTIAL POWER | WL | NONE | 4 | 4 | 683 | 0.0011198 | 6.5579e-06 | 170.75
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 3 | 28 | 3633 | 0.0060636 | 4.6733e-05 | 129.75
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | CROSSARM | 65 | 986 | 39039 | 0.063577 | 0.0016057 | 39.5933
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 154 | 34804 | 0.05668 | 0.0002508 | 226
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 56 | 5936 | 0.0099074 | 9.3466e-05 | 106
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 47 | 3384 | 0.005648 | 7.8444e-05 | 72
AEP-I&M | 2023 | 609949 | PARTIAL POWER | O | FUSE | 1 | 2 | 142 | 0.00023281 | 3.279e-06 | 71
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WW | POLE | 4 | 115 | 14460 | 0.023707 | 0.00018854 | 125.7391
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ABI | CUTOUT | 3 | 3 | 223 | 0.0003656 | 4.9184e-06 | 74.3333
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 7 | 749 | 95232 | 0.15509 | 0.0012198 | 127.1455
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 99 | 4950 | 0.0081154 | 0.00016231 | 50
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | CROSSARM | 5 | 2309 | 641399 | 1.0516 | 0.0037856 | 277.7822
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | SPLICE, OH | 8 | 10 | 1034 | 0.0016839 | 1.6285e-05 | 103.4
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 82 | 100 | 14401 | 0.023453 | 0.00016285 | 144.01
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | CROSSARM | 6 | 1593 | 512021 | 0.83385 | 0.0025943 | 321.4193
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | SPLICE, OH | 1 | 14 | 1929 | 0.0031626 | 2.2953e-05 | 137.7857
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | BREAKER | 1 | 211 | 31650 | 0.051543 | 0.00034362 | 150
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 5 | 53 | 16357 | 0.026638 | 8.6313e-05 | 308.6226
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 121 | 21748 | 0.03603 | 0.00020046 | 179.7355
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | CUTOUT | 3 | 223 | 15717 | 0.025596 | 0.00036317 | 70.4798
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 5 | 965 | 0.0016106 | 8.3451e-06 | 193
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ABI | CUTOUT | 4 | 13 | 1124 | 0.0018621 | 2.1537e-05 | 86.4615
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 8 | 1.3184e-05 | 1.648e-06 | 8
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | NONE | 13 | 1044 | 201356 | 0.33607 | 0.0017425 | 192.8697
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | AB | NONE | 8 | 7297 | 1211528 | 2.0221 | 0.012179 | 166.031
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TOR | CONN/CLAMP | 9 | 14 | 2370 | 0.0038856 | 2.2953e-05 | 169.2857
AEP-I&M | 2021 | 603608 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 77 | 0.00012757 | 1.6567e-06 | 77
AEP-I&M | 2022 | 606813 | PARTIAL POWER | VA | CONDUCTOR UG | 4 | 4 | 963 | 0.001587 | 6.5918e-06 | 240.75
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CO | CABLE TERMINATOR | 5 | 13 | 1270 | 0.0021197 | 2.1697e-05 | 97.6923
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | EQF | ARRESTER | 8 | 3626 | 507491 | 0.84702 | 0.0060519 | 139.9589
AEP-I&M | 2020 | 599151 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 118 | 0.00019695 | 1.669e-06 | 118
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 27 | 10415 | 0.017163 | 4.4495e-05 | 385.7407
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | EQF | REGULATOR | 1 | 490 | 9800 | 0.016356 | 0.00081782 | 20
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 386 | 18142 | 0.029743 | 0.00063284 | 47
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | TRANSFORMER, GROUNDING | 1 | 53 | 3657 | 0.0059956 | 8.6893e-05 | 69
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 19 | 1615 | 0.0026478 | 3.115e-05 | 85
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 3 | 198 | 0.00032629 | 4.9439e-06 | 66
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | POLE | 19 | 2541 | 1321924 | 2.1673 | 0.0041659 | 520.2377
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | AF | NONE | 1 | 73 | 9271 | 0.015359 | 0.00012094 | 127
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | F | CONN/CLAMP | 3 | 14 | 724 | 0.0011995 | 2.3194e-05 | 51.7143
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 5 | 1010 | 0.0016644 | 8.2398e-06 | 202
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CE | METERING | 1 | 1 | 161 | 0.00026673 | 1.6567e-06 | 161
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | CUTOUT | 29 | 126 | 36552 | 0.059527 | 0.0002052 | 290.0952
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | ARRESTER | 5 | 116 | 36871 | 0.060046 | 0.00018891 | 317.8534
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | METERING | 30 | 106 | 7299 | 0.011887 | 0.00017263 | 68.8585
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | SWITCH, OH | 7 | 4518 | 914126 | 1.4887 | 0.0073578 | 202.3298
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 1 | 109 | 0.00018192 | 1.669e-06 | 109
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | V | METERING | 3 | 3 | 310 | 0.00050485 | 4.8856e-06 | 103.3333
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 2 | 232 | 0.00037782 | 3.2571e-06 | 116
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TR | FUSE | 2 | 1833 | 71616 | 0.11663 | 0.0029851 | 39.0704
AEP-I&M | 2023 | 609949 | SUBTRANSMISSION LINE | ERF | CONDUCTOR OVERHEAD | 1 | 73 | 1752 | 0.0028724 | 0.00011968 | 24
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 1 | 44 | 7.2137e-05 | 1.6395e-06 | 44
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TR | NONE | 1 | 1 | 163 | 0.00026545 | 1.6285e-06 | 163
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TIR | NONE | 3 | 14 | 4729 | 0.0077531 | 2.2953e-05 | 337.7857
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 12 | 252 | 0.00041315 | 1.9674e-05 | 21
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 1 | 232 | 0.00038436 | 1.6567e-06 | 232
AEP-I&M | 2021 | 603608 | PARTIAL POWER | VIN | NONE | 3 | 3 | 572 | 0.00094763 | 4.9701e-06 | 190.6667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | POLE | 2 | 32 | 23116 | 0.038296 | 5.3015e-05 | 722.375
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 379 | 18468 | 3262729 | 5.3492 | 0.030278 | 176.6693
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | ARRESTER | 5 | 38 | 3860 | 0.0063949 | 6.2955e-05 | 101.5789
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 309 | 4272 | 1031024 | 1.6903 | 0.0070039 | 241.3446
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | NONE | 3 | 39 | 1644 | 0.0027439 | 6.5092e-05 | 42.1538
AEP-I&M | 2021 | 603608 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 7 | 7 | 1778 | 0.0029456 | 1.1597e-05 | 254
AEP-I&M | 2021 | 603608 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 1 | 558 | 0.00092444 | 1.6567e-06 | 558
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | SCO | NONE | 1 | 717 | 10755 | 0.017724 | 0.0011816 | 15
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 2 | 2 | 803 | 0.0013303 | 3.3134e-06 | 401.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | ARRESTER | 3 | 16 | 1444 | 0.0023796 | 2.6367e-05 | 90.25
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WI | FUSE | 1 | 4 | 532 | 0.00087671 | 6.5918e-06 | 133
AEP-I&M | 2020 | 599151 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 352 | 0.0005875 | 1.669e-06 | 352
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | BREAKER | 1 | 1772 | 299468 | 0.49097 | 0.0029052 | 169
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 1 | 206 | 0.00033948 | 1.648e-06 | 206
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 25 | 402 | 124660 | 0.20438 | 0.00065907 | 310.0995
AEP-I&M | 2022 | 606813 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 2 | 295 | 0.00048615 | 3.2959e-06 | 147.5
AEP-I&M | 2022 | 606813 | PARTIAL POWER | U | BREAKER | 1 | 2 | 198 | 0.00032629 | 3.2959e-06 | 99
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 2 | 78 | 0.00012788 | 3.279e-06 | 39
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CO | CONDUCTOR UG | 14 | 15 | 3256 | 0.0054344 | 2.5035e-05 | 217.0667
AEP-I&M | 2020 | 599151 | PARTIAL POWER | UB | CONN/CLAMP | 2 | 2 | 274 | 0.00045731 | 3.3381e-06 | 137
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1018 | 31735 | 7440858 | 12.1178 | 0.051682 | 234.4685
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VIN | FUSE | 27 | 267 | 31942 | 0.052019 | 0.00043482 | 119.633
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 58 | 696 | 0.0011335 | 9.4456e-05 | 12
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | PEDESTAL | 8 | 64 | 5098 | 0.0084459 | 0.00010603 | 79.6562
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | METERING | 15 | 15 | 1247 | 0.0020308 | 2.4428e-05 | 83.1333
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | SCO | NONE | 2 | 2687 | 34931 | 0.05787 | 0.0044516 | 13
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | NONE | 686 | 4833 | 438761 | 0.71454 | 0.0078708 | 90.7844
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 9 | 1741 | 202689 | 0.33009 | 0.0028353 | 116.421
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | CONN/CLAMP | 3 | 3 | 433 | 0.00070516 | 4.8856e-06 | 144.3333
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | F | NONE | 1 | 22 | 1518 | 0.0024721 | 3.5828e-05 | 69
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 7 | 612 | 76455 | 0.12451 | 0.00099667 | 124.9265
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | TRANSFORMER, STATION SERVICE | 1 | 1 | 94 | 0.00015411 | 1.6395e-06 | 94
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ABI | CUTOUT | 8 | 44 | 12721 | 0.021232 | 7.3437e-05 | 289.1136
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 6 | 102 | 0.00016611 | 9.7713e-06 | 17
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERF | METERING | 1 | 4 | 160 | 0.00026057 | 6.5142e-06 | 40
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 1 | 66 | 0.00010934 | 1.6567e-06 | 66
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 10 | 2144 | 0.0034916 | 1.6285e-05 | 214.4
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 3 | 159 | 0.00025894 | 4.8856e-06 | 53
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | INSULATOR | 2 | 270 | 9794 | 0.016346 | 0.00045064 | 36.2741
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 2 | 18 | 7109 | 0.011715 | 2.9663e-05 | 394.9444
AEP-I&M | 2022 | 606813 | TRANSMISSION STATION | SCO | BREAKER | 2 | 2674 | 16044 | 0.02644 | 0.0044066 | 6
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 144 | 26352 | 0.042915 | 0.00023451 | 183
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 33 | 22770 | 0.037723 | 5.4671e-05 | 690
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 1 | 40 | 6.5142e-05 | 1.6285e-06 | 40
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 1 | 104 | 0.00016937 | 1.6285e-06 | 104
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | F | CUTOUT | 1 | 2 | 190 | 0.00030942 | 3.2571e-06 | 95
AEP-I&M | 2024 | 614045 | TRANSMISSION LINE | FO | NONE | 1 | 19 | 1957 | 0.0031871 | 3.0942e-05 | 103
AEP-I&M | 2020 | 599151 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 389 | 0.00064925 | 3.3381e-06 | 194.5
AEP-I&M | 2022 | 606813 | PARTIAL POWER | OL | METERING | 1 | 1 | 159 | 0.00026202 | 1.648e-06 | 159
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 1 | 103 | 0.00016974 | 1.648e-06 | 103
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | ARRESTER | 1 | 15 | 2115 | 0.0034854 | 2.4719e-05 | 141
AEP-I&M | 2020 | 599151 | DISTRIBUTION SOURCE | TIR | CROSSARM | 1 | 580 | 56968 | 0.095081 | 0.00096804 | 98.2207
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | NONE | 150 | 2300 | 1265180 | 2.085 | 0.0037903 | 550.0783
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | FUSE | 135 | 2974 | 530454 | 0.87416 | 0.004901 | 178.3638
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 210 | 889 | 90938 | 0.14909 | 0.0014575 | 102.2925
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | NONE | 161 | 4051 | 639483 | 1.0538 | 0.0066759 | 157.8581
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FO | NONE | 28 | 554 | 43024 | 0.071278 | 0.00091781 | 77.6606
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | POLE HARDWARE | 2 | 335 | 20905 | 0.03445 | 0.00055206 | 62.403
AEP-I&M | 2021 | 603608 | PARTIAL POWER | U | FUSE | 12 | 56 | 5485 | 0.009087 | 9.2775e-05 | 97.9464
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | FUSE | 94 | 1045 | 297355 | 0.49263 | 0.0017313 | 284.5502
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | FUSE | 48 | 1600 | 320367 | 0.53075 | 0.0026507 | 200.2294
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 9 | 152 | 38023 | 0.06266 | 0.00025049 | 250.1513
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 118 | 241 | 30903 | 0.051578 | 0.00040224 | 128.2282
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | GUY/ANCHOR | 2 | 9 | 1061 | 0.0017485 | 1.4832e-05 | 117.8889
AEP-I&M | 2021 | 603608 | PARTIAL POWER | A | FUSE | 18 | 52 | 4407 | 0.0073011 | 8.6149e-05 | 84.75
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | V | METERING | 19 | 19 | 1894 | 0.0031611 | 3.1712e-05 | 99.6842
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | CUTOUT | 20 | 1931 | 658607 | 1.0911 | 0.0031991 | 341.0704
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 7 | 65 | 7334 | 0.01215 | 0.00010769 | 112.8308
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 52 | 8.6789e-05 | 1.669e-06 | 52
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WW | FUSE | 1 | 1 | 242 | 0.0003988 | 1.648e-06 | 242
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | GUY/ANCHOR | 1 | 7 | 1260 | 0.0020657 | 1.1476e-05 | 180
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 1152 | 0.0018984 | 1.648e-06 | 1152
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 27 | 945 | 0.001539 | 4.3971e-05 | 35
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 9 | 1989 | 0.0032392 | 1.4657e-05 | 221
AEP-I&M | 2023 | 609949 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 3 | 2936 | 407138 | 0.6675 | 0.0048135 | 138.671
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | EQF | CUTOUT | 4 | 2292 | 208572 | 0.34811 | 0.0038254 | 91
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | NONE | 782 | 31985 | 6064317 | 9.9937 | 0.05271 | 189.5988
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 65 | 4957 | 600390 | 0.98942 | 0.0081689 | 121.1196
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | V | METERING | 15 | 16 | 1244 | 0.0020501 | 2.6367e-05 | 77.75
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 49 | 814 | 71358 | 0.11822 | 0.0013486 | 87.6634
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CF | CONN/CLAMP | 3 | 3 | 378 | 0.00062293 | 4.9439e-06 | 126
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 28 | 76 | 8709 | 0.014352 | 0.00012524 | 114.5921
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 12 | 729 | 84829 | 0.13979 | 0.0012014 | 116.3635
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 1 | 269 | 0.0004433 | 1.648e-06 | 269
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | UG | NONE | 25 | 139 | 25979 | 0.04304 | 0.00023028 | 186.8993
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 81 | 2098 | 122536 | 0.20301 | 0.0034758 | 58.4061
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 40 | 566 | 77846 | 0.12993 | 0.00094467 | 137.5371
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | ARRESTER | 33 | 891 | 144681 | 0.23969 | 0.0014761 | 162.3805
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 18 | 4668 | 0.0077335 | 2.9821e-05 | 259.3333
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 47 | 4096 | 549080 | 0.90966 | 0.0067859 | 134.0527
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 1 | 1178 | 0.0019516 | 1.6567e-06 | 1178
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ERF | METERING | 1 | 1 | 67 | 0.00011041 | 1.648e-06 | 67
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | ARRESTER | 8 | 967 | 91294 | 0.14967 | 0.0015854 | 94.4095
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 9 | 159 | 28831 | 0.046953 | 0.00025894 | 181.327
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WI | RECLOSER, LINE/OCR/BR | 1 | 65 | 73060 | 0.12104 | 0.00010769 | 1124
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 4 | 4145 | 453539 | 0.74357 | 0.0067957 | 109.4183
AEP-I&M | 2020 | 599151 | TRANSMISSION LINE | SCO | NONE | 1 | 1179 | 17685 | 0.029517 | 0.0019678 | 15
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | POLE HARDWARE | 2 | 52 | 2258 | 0.0037019 | 8.5253e-05 | 43.4231
AEP-I&M | 2024 | 614045 | TRANSMISSION LINE | EQF | CONN/CLAMP | 3 | 2191 | 282464 | 0.46001 | 0.0035681 | 128.9201
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 17 | 81 | 20662 | 0.033649 | 0.00013191 | 255.0864
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 7 | 60 | 3260 | 0.005441 | 0.00010014 | 54.3333
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 7 | 51 | 3233 | 0.0052651 | 8.3056e-05 | 63.3922
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 26 | 123 | 25351 | 0.041285 | 0.00020031 | 206.1057
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | MOAB | 1 | 29 | 10527 | 0.017144 | 4.7228e-05 | 363
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | CROSSARM | 6 | 1714 | 654908 | 1.0665 | 0.0027913 | 382.0933
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | O | NONE | 6 | 884 | 36785 | 0.059906 | 0.0014396 | 41.612
AEP-I&M | 2024 | 614045 | PARTIAL POWER | A | FUSE | 22 | 48 | 3979 | 0.00648 | 7.817e-05 | 82.8958
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 10 | 1899 | 119533 | 0.1995 | 0.0031695 | 62.9452
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1 | 136 | 0.00022297 | 1.6395e-06 | 136
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 1 | 535 | 0.00088166 | 1.648e-06 | 535
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 33 | 3051 | 0.0049687 | 5.3742e-05 | 92.4545
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OU | NONE | 4 | 911 | 55761 | 0.090809 | 0.0014836 | 61.2086
AEP-I&M | 2020 | 599151 | PARTIAL POWER | ABI | FUSE | 2 | 2 | 203 | 0.00033881 | 3.3381e-06 | 101.5
AEP-I&M | 2020 | 599151 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 80 | 0.00013352 | 1.669e-06 | 80
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WU | FUSE | 1 | 1 | 77 | 0.0001254 | 1.6285e-06 | 77
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 455 | 0.00074099 | 1.6285e-06 | 455
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 178 | 16616 | 0.02706 | 0.00028988 | 93.3483
AEP-I&M | 2024 | 614045 | TRANSMISSION STATION | SCO | NONE | 1 | 4 | 140 | 0.000228 | 6.5142e-06 | 35
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 36 | 5220 | 0.0086023 | 5.9326e-05 | 145
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 2 | 422 | 13150 | 0.021415 | 0.00068725 | 31.1611
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CE | OTHER EQUIPMENT | 2 | 2 | 317 | 0.00052908 | 3.3381e-06 | 158.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 6 | 3780 | 0.0061559 | 9.7713e-06 | 630
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | CROSSARM | 2 | 126 | 54306 | 0.090638 | 0.0002103 | 431
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 1 | 122 | 0.00020362 | 1.669e-06 | 122
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | FUSE | 292 | 3606 | 377452 | 0.62202 | 0.0059425 | 104.6733
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | FUSE | 166 | 1465 | 220082 | 0.36269 | 0.0024143 | 150.2266
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | CONN/CLAMP | 7 | 40 | 1405 | 0.0023154 | 6.5918e-05 | 35.125
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | CONN/CLAMP | 42 | 808 | 106855 | 0.17609 | 0.0013315 | 132.2463
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 15 | 542 | 22524 | 0.037119 | 0.00089319 | 41.5572
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 24 | 6600 | 0.010876 | 3.9551e-05 | 275
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 39 | 4961 | 0.0081755 | 6.427e-05 | 127.2051
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FO | NONE | 13 | 1061 | 54563 | 0.089917 | 0.0017485 | 51.426
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VIN | NONE | 85 | 762 | 151224 | 0.25053 | 0.0012624 | 198.4567
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | POLE | 14 | 303 | 360925 | 0.59479 | 0.00049933 | 1191.1716
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | POLE | 72 | 5458 | 2432844 | 4.0305 | 0.0090423 | 445.7391
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 30 | 6000 | 0.010014 | 5.0071e-05 | 200
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 4 | 17 | 7911 | 0.013106 | 2.8164e-05 | 465.3529
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 28 | 149 | 39881 | 0.066563 | 0.00024869 | 267.6577
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | FUSE | 121 | 1770 | 227881 | 0.38034 | 0.0029542 | 128.7463
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 2 | 48 | 4672 | 0.0077977 | 8.0113e-05 | 97.3333
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 46 | 2504 | 459613 | 0.76711 | 0.0041792 | 183.5515
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 19 | 54 | 15645 | 0.02565 | 8.8532e-05 | 289.7222
AEP-I&M | 2020 | 599151 | TRANSMISSION LINE | SCO | INSULATOR | 3 | 1296 | 405648 | 0.67704 | 0.0021631 | 313
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | AO | REGULATOR | 11 | 12602 | 1723643 | 2.8768 | 0.021033 | 136.7754
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 20 | 282 | 37818 | 0.063119 | 0.00047067 | 134.1064
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | CROSSARM | 8 | 1569 | 252986 | 0.41477 | 0.0025723 | 161.2403
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | FUSE | 1 | 1 | 130 | 0.00021313 | 1.6395e-06 | 130
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 1 | 222 | 0.00036396 | 1.6395e-06 | 222
AEP-I&M | 2023 | 609949 | PARTIAL POWER | O | SPLICE, OH | 1 | 1 | 148 | 0.00024264 | 1.6395e-06 | 148
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TIR | POLE | 9 | 256 | 118477 | 0.19295 | 0.00041691 | 462.8008
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 18 | 1859 | 129605 | 0.21107 | 0.0030275 | 69.7176
AEP-I&M | 2025 | 614045 | PARTIAL POWER | WU | NONE | 2 | 2 | 535 | 0.00087127 | 3.2571e-06 | 267.5
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 4 | 360 | 0.00058628 | 6.5142e-06 | 90
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 4 | 380 | 0.000623 | 6.5579e-06 | 95
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | VA | POLE | 4 | 2830 | 65090 | 0.10864 | 0.0047234 | 23
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | NONE | 11 | 251 | 16040 | 0.026433 | 0.00041364 | 63.9044
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | ERF | STATIC WIRE | 1 | 1663 | 108095 | 0.17814 | 0.0027405 | 65
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | CUTOUT | 878 | 33063 | 5042742 | 8.4165 | 0.055183 | 152.5192
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 2 | 240 | 0.00040057 | 3.3381e-06 | 120
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 19 | 124 | 16111 | 0.02655 | 0.00020435 | 129.9274
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 34 | 5.603e-05 | 1.648e-06 | 34
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 220 | 5197 | 634932 | 1.0519 | 0.0086099 | 122.1728
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 197 | 250 | 85475 | 0.14161 | 0.00041418 | 341.9
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 43 | 1247 | 433210 | 0.7177 | 0.0020659 | 347.4018
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | CONDUCTOR UG | 391 | 486 | 116320 | 0.19271 | 0.00080516 | 239.3416
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | CROSSARM | 11 | 4853 | 546063 | 0.91139 | 0.0080998 | 112.5207
AEP-I&M | 2021 | 603608 | PARTIAL POWER | ABI | NONE | 13 | 45 | 4210 | 0.0069747 | 7.4552e-05 | 93.5556
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | ARRESTER | 54 | 4010 | 826425 | 1.3793 | 0.0066928 | 206.091
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 5 | 1808 | 223109 | 0.37238 | 0.0030176 | 123.401
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | F | FUSE | 2 | 5 | 112 | 0.00018555 | 8.2835e-06 | 22.4
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 69 | 557 | 53887 | 0.088347 | 0.00091319 | 96.7451
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | CROSSARM | 5 | 887 | 82589 | 0.1361 | 0.0014617 | 93.1105
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 7 | 185 | 54914 | 0.090496 | 0.00030487 | 296.8324
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | V | NONE | 3 | 3 | 274 | 0.00045394 | 4.9701e-06 | 91.3333
AEP-I&M | 2022 | 606813 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 1 | 1755 | 470340 | 0.7751 | 0.0028922 | 268
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 11 | 2640 | 0.0043506 | 1.8127e-05 | 240
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | METERING | 3 | 3 | 427 | 0.00070741 | 4.9701e-06 | 142.3333
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | EQF | POLE | 3 | 3121 | 2246728 | 3.7025 | 0.0051433 | 719.8744
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 133 | 33782 | 0.055385 | 0.00021805 | 254
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 1166 | 235532 | 0.39311 | 0.0019461 | 202
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TOR | CONDUCTOR UG | 2 | 2 | 364 | 0.00059677 | 3.279e-06 | 182
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 67 | 19698 | 0.032634 | 0.000111 | 294
AEP-I&M | 2023 | 609949 | PARTIAL POWER | U | FUSE | 15 | 18 | 1547 | 0.0025363 | 2.9511e-05 | 85.9444
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | POLE | 1422 | 9201 | 1488041 | 2.4233 | 0.014984 | 161.726
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 88 | 7845 | 981932 | 1.5991 | 0.012776 | 125.1666
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | NONE | 5 | 2612 | 264829 | 0.44201 | 0.0043595 | 101.3894
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 4 | 731 | 0.0011985 | 6.5579e-06 | 182.75
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | CROSSARM | 47 | 17898 | 2332425 | 3.7985 | 0.029148 | 130.3176
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | FUSE | 35 | 213 | 35466 | 0.057758 | 0.00034688 | 166.507
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | FUSE | 8 | 57 | 3263 | 0.0054058 | 9.4432e-05 | 57.2456
AEP-I&M | 2023 | 609949 | SUBTRANSMISSION LINE | EQF | POLE | 7 | 3349 | 458702 | 0.75203 | 0.0054906 | 136.9669
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | FUSE | 67 | 723 | 60968 | 0.099289 | 0.0011774 | 84.3264
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 15 | 960 | 118391 | 0.19281 | 0.0015634 | 123.324
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 4 | 4 | 427 | 0.00069539 | 6.5142e-06 | 106.75
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | V | CONDUCTOR UG | 3 | 2284 | 527675 | 0.86511 | 0.0037446 | 231.0311
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 3 | 3 | 389 | 0.0006335 | 4.8856e-06 | 129.6667
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 133 | 4037 | 747301 | 1.217 | 0.0065744 | 185.113
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 12 | 160 | 37123 | 0.060456 | 0.00026057 | 232.0188
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 3 | 2004 | 0.0032636 | 4.8856e-06 | 668
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 5 | 1156 | 205129 | 0.34237 | 0.0019294 | 177.4472
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WI | NONE | 1 | 1 | 116 | 0.00019116 | 1.648e-06 | 116
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | AO | REGULATOR | 1 | 555 | 172605 | 0.28596 | 0.00091947 | 311
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 1 | 183 | 0.00030543 | 1.669e-06 | 183
AEP-I&M | 2020 | 599151 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 1 | 285 | 0.00047567 | 1.669e-06 | 285
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CF | CONN/CLAMP | 3 | 8 | 1458 | 0.0024334 | 1.3352e-05 | 182.25
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | TRANSFORMER, GROUNDING | 1 | 1 | 53 | 8.6313e-05 | 1.6285e-06 | 53
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | BREAKER | 5 | 4475 | 102979 | 0.16771 | 0.0072877 | 23.0121
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | POLE HARDWARE | 5 | 159 | 15303 | 0.024922 | 0.00025894 | 96.2453
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 3 | 3 | 291 | 0.00047391 | 4.8856e-06 | 97
AEP-I&M | 2024 | 614045 | PARTIAL POWER | ERF | SPLICE, OH | 1 | 1 | 49 | 7.9799e-05 | 1.6285e-06 | 49
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | F | INSULATOR | 1 | 26 | 650 | 0.0010586 | 4.2342e-05 | 25
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 16 | 3648 | 0.0059409 | 2.6057e-05 | 228
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | POLE | 1 | 4 | 308 | 0.00050159 | 6.5142e-06 | 77
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 3 | 232 | 109361 | 0.1793 | 0.00038036 | 471.3836
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 3 | 520 | 0.00085694 | 4.9439e-06 | 173.3333
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 1 | 109 | 0.00017963 | 1.648e-06 | 109
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WU | FUSE | 1 | 3 | 183 | 0.00030158 | 4.9439e-06 | 61
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | VA | NONE | 1 | 186 | 31308 | 0.051868 | 0.00030815 | 168.3226
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | INSULATOR | 41 | 5280 | 523584 | 0.85268 | 0.0085987 | 99.1636
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | ARRESTER | 1 | 3 | 207 | 0.00034549 | 5.0071e-06 | 69
AEP-I&M | 2020 | 599151 | DISTRIBUTION SOURCE | TOR | CROSSARM | 1 | 1015 | 124802 | 0.2083 | 0.0016941 | 122.9576
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | FUSE | 2 | 11 | 475 | 0.00079279 | 1.8359e-05 | 43.1818
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | POLE | 763 | 6019 | 774601 | 1.2699 | 0.009868 | 128.6926
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 107 | 1807 | 230162 | 0.37735 | 0.0029625 | 127.3724
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | FUSE | 49 | 694 | 33439 | 0.055106 | 0.0011437 | 48.183
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | NONE | 35 | 1265 | 31985 | 0.05271 | 0.0020847 | 25.2846
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 52 | 15236 | 0.025242 | 8.6149e-05 | 293
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 239 | 12213 | 2821485 | 4.5949 | 0.019889 | 231.0231
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | EQF | CONDUCTOR UG | 3 | 4119 | 686240 | 1.1454 | 0.0068747 | 166.6035
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CO | POLE HARDWARE | 1 | 1 | 55 | 9.1119e-05 | 1.6567e-06 | 55
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 6 | 1374 | 0.0022763 | 9.9402e-06 | 229
AEP-I&M | 2025 | 614045 | PARTIAL POWER | U | FUSE | 3 | 5 | 766 | 0.0012475 | 8.1427e-06 | 153.2
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | O | POLE HARDWARE | 1 | 3 | 465 | 0.00076236 | 4.9184e-06 | 155
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TIR | FUSE | 9 | 114 | 8294 | 0.013507 | 0.00018565 | 72.7544
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | CABLE TERMINATOR | 14 | 18 | 3292 | 0.0053612 | 2.9314e-05 | 182.8889
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | INSULATOR | 4 | 1623 | 58722 | 0.095631 | 0.0026431 | 36.1811
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | CROSSARM | 10 | 3487 | 552627 | 0.89998 | 0.0056787 | 158.4821
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VIN | POLE | 1 | 25 | 9886 | 0.0161 | 4.0714e-05 | 395.44
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | AF | REGULATOR | 1 | 56 | 2016 | 0.0033648 | 9.3466e-05 | 36
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | CONN/CLAMP | 4 | 30 | 2777 | 0.0046007 | 4.9701e-05 | 92.5667
AEP-I&M | 2021 | 603608 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 93 | 0.00015407 | 1.6567e-06 | 93
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | AF | NONE | 1 | 1 | 64 | 0.00010423 | 1.6285e-06 | 64
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | RECLOSER, LINE/OCR/BR | 1 | 1677 | 276667 | 0.46177 | 0.002799 | 164.9773
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 6 | 6 | 610 | 0.0010053 | 9.8877e-06 | 101.6667
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | POLE | 10 | 2521 | 351322 | 0.57214 | 0.0041056 | 139.3582
AEP-I&M | 2025 | 614045 | PARTIAL POWER | FO | FUSE | 1 | 1 | 65 | 0.00010586 | 1.6285e-06 | 65
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 28 | 3274 | 0.0053319 | 4.5599e-05 | 116.9286
AEP-I&M | 2024 | 614045 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 72 | 0.00011726 | 1.6285e-06 | 72
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | SPLICE, OH | 1 | 34 | 1428 | 0.0023256 | 5.5371e-05 | 42
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1 | 63 | 0.00010329 | 1.6395e-06 | 63
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | V | CUTOUT | 1 | 1 | 48 | 7.817e-05 | 1.6285e-06 | 48
AEP-I&M | 2023 | 609949 | SUBTRANSMISSION LINE | OL | NONE | 1 | 423 | 2961 | 0.0048545 | 0.0006935 | 7
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 1 | 1 | 1254 | 0.0020422 | 1.6285e-06 | 1254
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 3 | 2444 | 137441 | 0.22939 | 0.0040791 | 56.2361
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 12 | 5508 | 0.009193 | 2.0028e-05 | 459
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 1 | 102 | 0.00016723 | 1.6395e-06 | 102
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OL | CONN/CLAMP | 2 | 2 | 213 | 0.00034688 | 3.2571e-06 | 106.5
AEP-I&M | 2025 | 614045 | PARTIAL POWER | WU | SPLICE, OH | 1 | 1 | 498 | 0.00081102 | 1.6285e-06 | 498
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 14 | 2870 | 0.0047053 | 2.2953e-05 | 205
AEP-I&M | 2021 | 603608 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 313 | 0.00051855 | 1.6567e-06 | 313
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 4 | 148 | 0.00024519 | 6.6268e-06 | 37
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | TR | NONE | 3 | 1973 | 279076 | 0.46235 | 0.0032687 | 141.4475
AEP-I&M | 2021 | 603608 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 157 | 0.0002601 | 1.6567e-06 | 157
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 51 | 8.4046e-05 | 1.648e-06 | 51
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 3 | 423 | 0.0006935 | 4.9184e-06 | 141
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OU | FUSE | 1 | 28 | 6664 | 0.010853 | 4.5599e-05 | 238
AEP-I&M | 2020 | 599151 | PARTIAL POWER | FO | FUSE | 1 | 1 | 131 | 0.00021864 | 1.669e-06 | 131
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | NONE | 65 | 3313 | 420267 | 0.69626 | 0.0054887 | 126.8539
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | CONN/CLAMP | 466 | 569 | 77947 | 0.12845 | 0.00093769 | 136.9895
AEP-I&M | 2022 | 606813 | PARTIAL POWER | UG | CONDUCTOR UG | 20 | 44 | 18431 | 0.030373 | 7.251e-05 | 418.8864
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 468 | 7116 | 932150 | 1.5282 | 0.011667 | 130.9935
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TR | NONE | 18 | 152 | 10926 | 0.018006 | 0.00025049 | 71.8816
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | O | NONE | 38 | 608 | 82444 | 0.13586 | 0.001002 | 135.5987
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 5 | 145 | 0.00023895 | 8.2398e-06 | 29
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 41 | 1242 | 170552 | 0.28106 | 0.0020468 | 137.3205
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TOR | NONE | 34 | 72 | 21974 | 0.036212 | 0.00011865 | 305.1944
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | V | METERING | 11 | 19 | 1843 | 0.0030533 | 3.1477e-05 | 97
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 1 | 307 | 0.00050861 | 1.6567e-06 | 307
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 35 | 6090 | 0.010036 | 5.7678e-05 | 174
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | CROSSARM | 3 | 170 | 6569 | 0.010825 | 0.00028015 | 38.6412
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | POLE | 270 | 6513 | 844563 | 1.3992 | 0.01079 | 129.6734
AEP-I&M | 2021 | 603608 | PARTIAL POWER | VA | NONE | 6 | 106 | 8794 | 0.014569 | 0.00017561 | 82.9623
AEP-I&M | 2022 | 606813 | SUBTRANSMISSION LINE | EQF | INSULATOR | 2 | 813 | 380884 | 0.62768 | 0.0013398 | 468.492
AEP-I&M | 2021 | 603608 | SUBTRANSMISSION LINE | ERF | NONE | 5 | 2396 | 102700 | 0.17014 | 0.0039695 | 42.8631
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 3 | 345 | 0.00056562 | 4.9184e-06 | 115
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | ABI | NONE | 1 | 10 | 640 | 0.0010682 | 1.669e-05 | 64
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | CUTOUT | 132 | 1570 | 100546 | 0.16657 | 0.002601 | 64.042
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 5 | 5 | 772 | 0.001279 | 8.2835e-06 | 154.4
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 5 | 16 | 3357 | 0.0055322 | 2.6367e-05 | 209.8125
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VIN | POLE | 1 | 43 | 5246 | 0.0086452 | 7.0862e-05 | 122
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TR | NONE | 12 | 1871 | 398224 | 0.65974 | 0.0030997 | 212.8402
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TIR | NONE | 8 | 45 | 5267 | 0.0086798 | 7.4158e-05 | 117.0444
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | CROSSARM | 18 | 5722 | 2586849 | 4.263 | 0.0094296 | 452.0883
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 18 | 196 | 17996 | 0.030036 | 0.00032713 | 91.8163
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | INSULATOR | 4 | 153 | 4321 | 0.0071586 | 0.00025348 | 28.2418
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | EQF | RELAY | 3 | 1968 | 495936 | 0.82162 | 0.0032604 | 252
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERO | NONE | 2 | 2 | 162 | 0.00026839 | 3.3134e-06 | 81
AEP-I&M | 2021 | 603608 | PARTIAL POWER | ABI | FUSE | 9 | 20 | 1979 | 0.0032786 | 3.3134e-05 | 98.95
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 1 | 377 | 0.00062128 | 1.648e-06 | 377
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 22 | 2816 | 0.0046406 | 3.6255e-05 | 128
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 59 | 43520 | 0.071719 | 9.7229e-05 | 737.6271
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 48 | 6532 | 671720 | 1.1211 | 0.010902 | 102.8353
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | SCO | SWITCH, OH | 1 | 238 | 2142 | 0.0035751 | 0.00039723 | 9
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 7 | 203 | 0.00033453 | 1.1536e-05 | 29
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 3 | 69 | 8214 | 0.013608 | 0.00011431 | 119.0435
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CF | CONN/CLAMP | 7 | 10 | 2019 | 0.0033272 | 1.648e-05 | 201.9
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OU | RECLOSER, LINE/OCR/BR | 1 | 434 | 65895 | 0.10859 | 0.00071521 | 151.8318
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | V | METERING | 7 | 7 | 389 | 0.00063776 | 1.1476e-05 | 55.5714
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CE | CONDUCTOR UG | 2 | 2 | 471 | 0.00078031 | 3.3134e-06 | 235.5
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | NONE | 2135 | 23160 | 1795369 | 2.9435 | 0.03797 | 77.5203
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ERF | CONN/CLAMP | 3 | 5 | 355 | 0.00058502 | 8.2398e-06 | 71
AEP-I&M | 2023 | 609949 | PARTIAL POWER | U | NONE | 53 | 122 | 13366 | 0.021913 | 0.00020002 | 109.5574
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 2 | 11 | 2519 | 0.0041299 | 1.8034e-05 | 229
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 2 | 1168 | 0.0019494 | 3.3381e-06 | 584
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 73 | 2052 | 114413 | 0.19096 | 0.0034248 | 55.7568
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | AB | NONE | 5 | 4591 | 307787 | 0.50461 | 0.0075269 | 67.0414
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 42 | 1921 | 172867 | 0.28341 | 0.0031494 | 89.988
AEP-I&M | 2020 | 599151 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 43 | 7.1768e-05 | 1.669e-06 | 43
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 12 | 2142 | 0.0035118 | 1.9674e-05 | 178.5
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | V | NONE | 11 | 198 | 49391 | 0.080976 | 0.00032462 | 249.4495
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 13 | 3071 | 0.0051256 | 2.1697e-05 | 236.2308
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | TRANSFORMER, OH | 23 | 70 | 57899 | 0.094291 | 0.000114 | 827.1286
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | ARRESTER | 14 | 338 | 82102 | 0.13703 | 0.00056413 | 242.9053
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 18 | 2772 | 0.0045143 | 2.9314e-05 | 154
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 716 | 0.001166 | 3.2571e-06 | 358
AEP-I&M | 2022 | 606813 | SUBTRANSMISSION LINE | EQF | POLE | 1 | 75 | 14400 | 0.023731 | 0.0001236 | 192
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 4 | 11 | 13477 | 0.022209 | 1.8127e-05 | 1225.1818
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SO | CROSSARM | 1 | 1 | 75 | 0.0001236 | 1.648e-06 | 75
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | POLE | 1 | 1 | 323 | 0.00052602 | 1.6285e-06 | 323
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | CONDUCTOR UG | 5 | 167 | 101444 | 0.16521 | 0.00027197 | 607.4491
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | F | CUTOUT | 2 | 920 | 224374 | 0.3654 | 0.0014983 | 243.8848
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | EQF | BREAKER | 7 | 3164 | 538025 | 0.89135 | 0.0052418 | 170.0458
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 162 | 0.00026839 | 1.6567e-06 | 162
AEP-I&M | 2020 | 599151 | PARTIAL POWER | WW | CUTOUT | 1 | 2 | 670 | 0.0011182 | 3.3381e-06 | 335
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | EQF | INSULATOR | 1 | 485 | 76145 | 0.12709 | 0.00080948 | 157
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | CUTOUT | 3 | 36 | 8220 | 0.013387 | 5.8628e-05 | 228.3333
AEP-I&M | 2024 | 614045 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 128 | 0.00020845 | 1.6285e-06 | 128
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 3 | 583 | 0.00094944 | 4.8856e-06 | 194.3333
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | A | ARRESTER | 1 | 1 | 51 | 8.3056e-05 | 1.6285e-06 | 51
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 10 | 360 | 0.00058628 | 1.6285e-05 | 36
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 4 | 1400 | 0.00228 | 6.5142e-06 | 350
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 8 | 4032 | 0.0065663 | 1.3028e-05 | 504
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 2 | 378 | 0.00061559 | 3.2571e-06 | 189
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | CROSSARM | 1 | 1 | 78 | 0.00012703 | 1.6285e-06 | 78
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 107 | 1488 | 0.0024233 | 0.00017425 | 13.9065
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 2 | 260 | 0.00042342 | 3.2571e-06 | 130
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 232 | 29464 | 0.048306 | 0.00038036 | 127
AEP-I&M | 2024 | 614045 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 1 | 203 | 0.00033059 | 1.6285e-06 | 203
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 82 | 18614 | 0.030517 | 0.00013444 | 227
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERO | CABLE TERMINATOR | 1 | 1 | 107 | 0.00017633 | 1.648e-06 | 107
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | EQF | CUTOUT | 1 | 1467 | 410760 | 0.68051 | 0.0024304 | 280
AEP-I&M | 2023 | 609949 | TRANSMISSION STATION | ABX | INSULATOR | 6 | 4865 | 842291 | 1.3809 | 0.0079761 | 173.1328
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 33 | 5.3742e-05 | 1.6285e-06 | 33
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | CROSSARM | 1 | 31 | 5177 | 0.0086406 | 5.174e-05 | 167
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 10 | 1680 | 0.0027686 | 1.648e-05 | 168
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 48 | 13680 | 0.022832 | 8.0113e-05 | 285
AEP-I&M | 2020 | 599151 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 1 | 66 | 0.00011016 | 1.669e-06 | 66
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 40 | 2077 | 464229 | 0.76503 | 0.0034228 | 223.5094
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | CONN/CLAMP | 534 | 739 | 98371 | 0.16297 | 0.0012243 | 133.1137
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 85 | 709 | 84247 | 0.13884 | 0.0011684 | 118.8251
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ABI | NONE | 259 | 2426 | 182850 | 0.30133 | 0.0039979 | 75.371
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 24 | 2845 | 517499 | 0.85281 | 0.0046884 | 181.8977
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | ARRESTER | 12 | 74 | 24258 | 0.039976 | 0.00012195 | 327.8108
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 64 | 901 | 90731 | 0.14952 | 0.0014848 | 100.7003
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 8 | 41 | 5333 | 0.0088352 | 6.7925e-05 | 130.0732
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 11 | 111 | 8570 | 0.014198 | 0.00018389 | 77.2072
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 51 | 658 | 57534 | 0.096026 | 0.0010982 | 87.4377
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 1 | 53 | 8.7805e-05 | 1.6567e-06 | 53
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 1509 | 175521 | 0.29079 | 0.0025 | 116.3161
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CF | FUSE | 1 | 8 | 424 | 0.00069873 | 1.3184e-05 | 53
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | SWITCH, OH | 3 | 1107 | 30820 | 0.05106 | 0.001834 | 27.841
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 11 | 757 | 0.0012475 | 1.8127e-05 | 68.8182
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CO | NONE | 2 | 3 | 2098 | 0.0034758 | 4.9701e-06 | 699.3333
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | OU | NONE | 2 | 1429 | 156837 | 0.25846 | 0.0023549 | 109.753
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | CROSSARM | 6 | 1495 | 102708 | 0.17016 | 0.0024768 | 68.701
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | FUSE | 525 | 6605 | 501684 | 0.81702 | 0.010757 | 75.9552
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 19 | 1607 | 0.0026346 | 3.115e-05 | 84.5789
AEP-I&M | 2023 | 609949 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 227 | 0.00037216 | 1.6395e-06 | 227
AEP-I&M | 2020 | 599151 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 3 | 4 | 2368 | 0.0039523 | 6.6761e-06 | 592
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | POLE | 7 | 140 | 29260 | 0.048836 | 0.00023366 | 209
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TOR | NONE | 25 | 27 | 6442 | 0.010562 | 4.4266e-05 | 238.5926
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 2 | 3 | 233 | 0.00038601 | 4.9701e-06 | 77.6667
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 1225 | 155575 | 0.25966 | 0.0020446 | 127
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | CABLE TERMINATOR | 33 | 50 | 4292 | 0.0070367 | 8.1974e-05 | 85.84
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WI | CONN/CLAMP | 1 | 1 | 405 | 0.00067097 | 1.6567e-06 | 405
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 16 | 1268 | 0.0020789 | 2.6232e-05 | 79.25
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 1 | 125 | 0.00020494 | 1.6395e-06 | 125
AEP-I&M | 2022 | 606813 | PARTIAL POWER | UG | CUTOUT | 1 | 1 | 118 | 0.00019446 | 1.648e-06 | 118
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 9 | 11 | 3439 | 0.0057398 | 1.8359e-05 | 312.6364
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 40 | 2168 | 534172 | 0.86992 | 0.0035307 | 246.3893
AEP-I&M | 2020 | 599151 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 109 | 0.00018192 | 1.669e-06 | 109
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | FUSE | 74 | 584 | 39695 | 0.064645 | 0.00095107 | 67.9709
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | FUSE | 11 | 108 | 16642 | 0.027102 | 0.00017588 | 154.0926
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | FUSE | 18 | 123 | 16945 | 0.027596 | 0.00020031 | 137.7642
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 9 | 355 | 98390 | 0.16023 | 0.00057813 | 277.1549
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | FUSE | 8 | 257 | 110810 | 0.18046 | 0.00041854 | 431.1673
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | CAPACITOR | 2 | 1845 | 51855 | 0.084448 | 0.0030047 | 28.1057
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 2 | 8 | 5052 | 0.0082274 | 1.3028e-05 | 631.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 7 | 1575 | 203038 | 0.33066 | 0.002565 | 128.913
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | POLE | 9 | 86 | 44539 | 0.072534 | 0.00014005 | 517.8953
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 11 | 99 | 100336 | 0.1634 | 0.00016123 | 1013.4949
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 41 | 2665 | 0.0043401 | 6.677e-05 | 65
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 4 | 640 | 0.0010423 | 6.5142e-06 | 160
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 1 | 958 | 16286 | 0.026522 | 0.0015601 | 17
AEP-I&M | 2024 | 614045 | SUBTRANSMISSION LINE | U | NONE | 1 | 58 | 8526 | 0.013885 | 9.4456e-05 | 147
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1 | 560 | 0.00091199 | 1.6285e-06 | 560
AEP-I&M | 2025 | 614045 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 5958 | 1006902 | 1.6398 | 0.0097029 | 169
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | ARRESTER | 1 | 2 | 110 | 0.00017914 | 3.2571e-06 | 55
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 2 | 284 | 0.00046802 | 3.2959e-06 | 142
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 2 | 7 | 603 | 0.00098861 | 1.1476e-05 | 86.1429
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 57 | 2109 | 0.00352 | 9.5135e-05 | 37
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 154 | 22022 | 0.036755 | 0.00025703 | 143
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 98 | 0.00016067 | 1.6395e-06 | 98
AEP-I&M | 2024 | 614045 | PARTIAL POWER | VA | NONE | 3 | 3 | 284 | 0.00046251 | 4.8856e-06 | 94.6667
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | CUTOUT | 3 | 2668 | 352915 | 0.58903 | 0.004453 | 132.277
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | ARRESTER | 7 | 1308 | 34687 | 0.057894 | 0.0021831 | 26.5191
AEP-I&M | 2024 | 614045 | PARTIAL POWER | VIN | NONE | 5 | 7 | 933 | 0.0015194 | 1.14e-05 | 133.2857
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | SWITCH, OH | 3 | 701 | 175794 | 0.28629 | 0.0011416 | 250.776
AEP-I&M | 2020 | 599151 | PARTIAL POWER | UG | CONDUCTOR OVERHEAD | 1 | 1 | 123 | 0.00020529 | 1.669e-06 | 123
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 2 | 684 | 266651 | 0.43425 | 0.0011139 | 389.8406
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WT | POLE | 4 | 937 | 556505 | 0.90629 | 0.0015259 | 593.9221
AEP-I&M | 2025 | 614045 | PARTIAL POWER | A | NONE | 3 | 3 | 425 | 0.00069213 | 4.8856e-06 | 141.6667
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TOR | OTHER EQUIPMENT | 1 | 1 | 179 | 0.00029347 | 1.6395e-06 | 179
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 7 | 1338 | 0.002179 | 1.14e-05 | 191.1429
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WU | TRANSFORMER, OH | 2 | 2 | 1421 | 0.0023142 | 3.2571e-06 | 710.5
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 1780 | 221376 | 0.36052 | 0.0028988 | 124.3685
AEP-I&M | 2024 | 614045 | PARTIAL POWER | ERF | METERING | 2 | 2 | 333 | 0.00054231 | 3.2571e-06 | 166.5
AEP-I&M | 2023 | 609949 | DISTRIBUTION SOURCE | SCO | POLE | 1 | 4 | 80 | 0.00013116 | 6.5579e-06 | 20
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | CABLE TERMINATOR | 1 | 39 | 10134 | 0.0167 | 6.427e-05 | 259.8462
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 1 | 96 | 0.00015904 | 1.6567e-06 | 96
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | UG | POLE | 1 | 326 | 21842 | 0.03581 | 0.00053447 | 67
AEP-I&M | 2024 | 614045 | SUBTRANSMISSION LINE | ERF | NONE | 1 | 1319 | 94968 | 0.15466 | 0.0021481 | 72
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | O | FUSE | 2 | 8 | 10422 | 0.017087 | 1.3116e-05 | 1302.75
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | NONE | 837 | 44232 | 9420617 | 15.6072 | 0.073279 | 212.9819
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ABI | NONE | 16 | 39 | 4312 | 0.007106 | 6.427e-05 | 110.5641
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1137 | 30777 | 8649540 | 14.4363 | 0.051368 | 281.0391
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 5 | 183 | 52833 | 0.087529 | 0.00030318 | 288.7049
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | NONE | 705 | 22026 | 4323830 | 7.0888 | 0.036111 | 196.3057
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TR | NONE | 3 | 3 | 372 | 0.00061304 | 4.9439e-06 | 124
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | JUMPER/RISER | 3 | 242 | 4021 | 0.0066616 | 0.00040092 | 16.6157
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | CF | NONE | 3 | 3335 | 926130 | 1.5343 | 0.0055251 | 277.7001
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 9 | 14 | 1696 | 0.0027806 | 2.2953e-05 | 121.1429
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | METERING | 10 | 24 | 2981 | 0.0049754 | 4.0057e-05 | 124.2083
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | PEDESTAL | 1 | 12 | 4116 | 0.0068697 | 2.0028e-05 | 343
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 8 | 3138 | 0.0051713 | 1.3184e-05 | 392.25
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | CONDUCTOR UG | 286 | 352 | 64200 | 0.10455 | 0.00057325 | 182.3864
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | NONE | 2240 | 21164 | 1849246 | 3.0116 | 0.034467 | 87.377
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | POLE | 26 | 1662 | 390387 | 0.64003 | 0.0027248 | 234.8899
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | FUSE | 30 | 405 | 31569 | 0.051757 | 0.00066399 | 77.9481
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 13 | 2522 | 0.0041782 | 2.1537e-05 | 194
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 3 | 20 | 2121 | 0.0035139 | 3.3134e-05 | 106.05
AEP-I&M | 2024 | 614045 | PARTIAL POWER | U | FUSE | 18 | 31 | 2792 | 0.0045469 | 5.0485e-05 | 90.0645
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TOR | CONN/CLAMP | 10 | 16 | 2908 | 0.0048535 | 2.6704e-05 | 181.75
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 777 | 13986 | 0.022777 | 0.0012654 | 18
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | POLE | 1 | 1 | 608 | 0.00099016 | 1.6285e-06 | 608
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | WW | POLE | 1 | 15 | 5204 | 0.008576 | 2.4719e-05 | 346.9333
AEP-I&M | 2020 | 599151 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 161 | 0.00026871 | 3.3381e-06 | 80.5
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | CROSSARM | 4 | 56 | 4878 | 0.007944 | 9.1199e-05 | 87.1071
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 2 | 259 | 0.00042463 | 3.279e-06 | 129.5
AEP-I&M | 2025 | 614045 | PARTIAL POWER | U | NONE | 5 | 13 | 1204 | 0.0019608 | 2.1171e-05 | 92.6154
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | CROSSARM | 1 | 11 | 1650 | 0.0026871 | 1.7914e-05 | 150
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | INSULATOR | 3 | 5 | 315 | 0.00051299 | 8.1427e-06 | 63
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 166 | 18798 | 0.030613 | 0.00027034 | 113.241
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 1 | 6 | 228 | 0.00037131 | 9.7713e-06 | 38
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | CAPACITOR | 1 | 1 | 236 | 0.00039389 | 1.669e-06 | 236
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WW | METERING | 1 | 4 | 32 | 5.2463e-05 | 6.5579e-06 | 8
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CF | FUSE | 3 | 13 | 1500 | 0.0025035 | 2.1697e-05 | 115.3846
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | JUMPER/RISER | 1 | 3 | 93 | 0.00015247 | 4.9184e-06 | 31
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 4 | 392 | 0.00063839 | 6.5142e-06 | 98
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 21 | 7266 | 0.011833 | 3.4199e-05 | 346
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 225 | 0.00037079 | 1.648e-06 | 225
AEP-I&M | 2022 | 606813 | PARTIAL POWER | VIN | CONN/CLAMP | 2 | 2 | 874 | 0.0014403 | 3.2959e-06 | 437
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CO | FUSE | 1 | 1 | 140 | 0.00023071 | 1.648e-06 | 140
AEP-I&M | 2022 | 606813 | PARTIAL POWER | UB | NONE | 1 | 1 | 6 | 9.8877e-06 | 1.648e-06 | 6
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | UG | FUSE | 2 | 8 | 1004 | 0.001646 | 1.3116e-05 | 125.5
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 93 | 0.00015407 | 1.6567e-06 | 93
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | FUSE | 7 | 10 | 1019 | 0.0016793 | 1.648e-05 | 101.9
AEP-I&M | 2020 | 599151 | TRANSMISSION LINE | EQF | GUY/ANCHOR | 1 | 914 | 16452 | 0.027459 | 0.0015255 | 18
AEP-I&M | 2020 | 599151 | PARTIAL POWER | OL | NONE | 2 | 2 | 133 | 0.00022198 | 3.3381e-06 | 66.5
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 112 | 0.00018362 | 3.279e-06 | 56
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 3 | 330 | 0.00054103 | 4.9184e-06 | 110
AEP-I&M | 2020 | 599151 | PARTIAL POWER | VA | NONE | 6 | 24 | 11276 | 0.01882 | 4.0057e-05 | 469.8333
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 211 | 1013 | 131532 | 0.21421 | 0.0016497 | 129.844
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 31 | 38 | 5039 | 0.0082062 | 6.1885e-05 | 132.6053
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 14 | 1410 | 219843 | 0.35802 | 0.0022962 | 155.917
AEP-I&M | 2023 | 609949 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 3 | 645 | 0.0010575 | 4.9184e-06 | 215
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERF | BREAKER | 1 | 1 | 108 | 0.00017588 | 1.6285e-06 | 108
AEP-I&M | 2021 | 603608 | PARTIAL POWER | VA | FUSE | 2 | 2 | 120 | 0.0001988 | 3.3134e-06 | 60
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 4 | 280 | 0.00046388 | 6.6268e-06 | 70
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | CROSSARM | 36 | 303 | 13433 | 0.021876 | 0.00049345 | 44.3333
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 446 | 129984 | 0.21695 | 0.00074439 | 291.4439
AEP-I&M | 2023 | 609949 | PARTIAL POWER | ERF | NONE | 3 | 3 | 373 | 0.00061153 | 4.9184e-06 | 124.3333
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 58 | 9.4456e-05 | 1.6285e-06 | 58
AEP-I&M | 2024 | 614045 | PARTIAL POWER | O | NONE | 1 | 1 | 193 | 0.00031431 | 1.6285e-06 | 193
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 32 | 6402 | 0.010426 | 5.2113e-05 | 200.0625
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 6 | 37 | 4970 | 0.0080939 | 6.0256e-05 | 134.3243
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 4 | 324 | 0.00053677 | 6.6268e-06 | 81
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 3 | 705 | 0.0011767 | 5.0071e-06 | 235
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 2 | 553 | 0.00090059 | 3.2571e-06 | 276.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 17 | 3856 | 0.0064358 | 2.8373e-05 | 226.8235
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | POLE | 1 | 52 | 5148 | 0.0085922 | 8.6789e-05 | 99
AEP-I&M | 2022 | 606813 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 1 | 296 | 0.00048779 | 1.648e-06 | 296
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 2 | 278 | 0.00045578 | 3.279e-06 | 139
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 1 | 80 | 0.00013116 | 1.6395e-06 | 80
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 25 | 3575 | 0.0058914 | 4.1199e-05 | 143
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | INSULATOR | 1 | 10 | 1360 | 0.0022531 | 1.6567e-05 | 136
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | POLE | 1 | 220 | 24522 | 0.040203 | 0.00036069 | 111.4636
AEP-I&M | 2020 | 599151 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 1320 | 0.0022031 | 3.3381e-06 | 660
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | ABI | CONDUCTOR OVERHEAD | 1 | 2441 | 751828 | 1.2548 | 0.0040741 | 308
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1 | 158 | 0.00026371 | 1.669e-06 | 158
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | CUTOUT | 57 | 210 | 36628 | 0.060361 | 0.00034607 | 174.419
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | NONE | 593 | 15896 | 1542175 | 2.5414 | 0.026196 | 97.0165
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | POLE | 11 | 1650 | 200034 | 0.32965 | 0.0027191 | 121.2327
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 109 | 1304 | 243891 | 0.40192 | 0.0021489 | 187.033
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 45 | 737 | 181305 | 0.29878 | 0.0012145 | 246.0041
AEP-I&M | 2022 | 606813 | PARTIAL POWER | A | FUSE | 33 | 76 | 6084 | 0.010026 | 0.00012524 | 80.0526
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 10 | 1304 | 83377 | 0.1374 | 0.0021489 | 63.9394
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 2 | 64 | 5082 | 0.0084194 | 0.00010603 | 79.4062
AEP-I&M | 2022 | 606813 | PARTIAL POWER | A | NONE | 82 | 350 | 39238 | 0.064662 | 0.00057678 | 112.1086
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 7 | 35 | 6238 | 0.01028 | 5.7678e-05 | 178.2286
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | SPLICE, OH | 4 | 39 | 7091 | 0.011835 | 6.5092e-05 | 181.8205
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | NONE | 233 | 9323 | 2169289 | 3.6206 | 0.01556 | 232.6814
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | FUSE | 22 | 60 | 8050 | 0.013436 | 0.00010014 | 134.1667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | CROSSARM | 37 | 18029 | 2195506 | 3.6373 | 0.029869 | 121.7764
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CF | CABLE TERMINATOR | 1 | 1 | 61 | 0.00010106 | 1.6567e-06 | 61
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 227 | 23608 | 0.039111 | 0.00037607 | 104
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | POLE | 62 | 1319 | 101003 | 0.16733 | 0.0021852 | 76.5754
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 5 | 15 | 599 | 0.0009755 | 2.4428e-05 | 39.9333
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | POLE | 59 | 2331 | 1045188 | 1.7021 | 0.0037961 | 448.3861
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 10 | 2356 | 159804 | 0.26025 | 0.0038369 | 67.8285
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | SPLICE, UG | 3 | 3 | 330 | 0.00054103 | 4.9184e-06 | 110
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 2 | 216 | 0.00035177 | 3.2571e-06 | 108
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 7 | 714 | 0.0011917 | 1.1683e-05 | 102
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | A | NONE | 214 | 3498 | 171817 | 0.27981 | 0.0056967 | 49.1186
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | POLE | 29 | 5502 | 438402 | 0.71396 | 0.0089603 | 79.6805
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 4 | 212 | 0.00034525 | 6.5142e-06 | 53
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | ABI | REGULATOR | 1 | 153 | 13444 | 0.022438 | 0.00025536 | 87.8693
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | F | POLE | 4 | 2029 | 219434 | 0.36354 | 0.0033615 | 108.1488
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 7 | 756 | 0.0012312 | 1.14e-05 | 108
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | EQF | INSULATOR | 5 | 6320 | 789141 | 1.3171 | 0.010548 | 124.8641
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 377 | 0.00062128 | 1.648e-06 | 377
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | SPLICE, OH | 12 | 25 | 7355 | 0.012276 | 4.1726e-05 | 294.2
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 15 | 519 | 367673 | 0.60913 | 0.00085983 | 708.4258
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 18 | 246 | 61043 | 0.10188 | 0.00041058 | 248.1423
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 3 | 18 | 630 | 0.0010437 | 2.9821e-05 | 35
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ABI | FUSE | 3 | 17 | 2023 | 0.0032945 | 2.7685e-05 | 119
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 7 | 4247 | 172030 | 0.28016 | 0.0069164 | 40.5062
AEP-I&M | 2025 | 614045 | PARTIAL POWER | TOR | NONE | 3 | 3 | 697 | 0.0011351 | 4.8856e-06 | 232.3333
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | U | CUTOUT | 3 | 14 | 1710 | 0.002833 | 2.3194e-05 | 122.1429
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | METERING | 3 | 3 | 631 | 0.0010532 | 5.0071e-06 | 210.3333
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CE | FUSE | 2 | 4 | 532 | 0.00088137 | 6.6268e-06 | 133
AEP-I&M | 2023 | 609949 | PARTIAL POWER | WL | FUSE | 1 | 1 | 106 | 0.00017379 | 1.6395e-06 | 106
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | AB | ARRESTER | 1 | 435 | 31320 | 0.052274 | 0.00072603 | 72
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 2 | 5 | 3071 | 0.0051256 | 8.3451e-06 | 614.2
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 2 | 305 | 16283 | 0.026518 | 0.00049671 | 53.3869
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 187 | 0.0003098 | 1.6567e-06 | 187
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 107 | 14659 | 0.024466 | 0.00017859 | 137
AEP-I&M | 2025 | 614045 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 1 | 1 | 125 | 0.00020357 | 1.6285e-06 | 125
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 5 | 12 | 590 | 0.00096084 | 1.9543e-05 | 49.1667
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | O | CUTOUT | 2 | 2 | 469 | 0.00078277 | 3.3381e-06 | 234.5
AEP-I&M | 2020 | 599151 | TRANSMISSION LINE | TR | INSULATOR | 4 | 3492 | 1774030 | 2.9609 | 0.0058282 | 508.0269
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | POLE | 2 | 7 | 3372 | 0.005628 | 1.1683e-05 | 481.7143
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ABI | POLE | 1 | 2 | 138 | 0.00023033 | 3.3381e-06 | 69
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERO | NONE | 3 | 3 | 169 | 0.00027522 | 4.8856e-06 | 56.3333
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | REGULATOR | 1 | 13 | 2895 | 0.0047146 | 2.1171e-05 | 222.6923
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 1 | 142 | 0.000237 | 1.669e-06 | 142
AEP-I&M | 2024 | 614045 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 833 | 304599 | 0.49605 | 0.0013566 | 365.6651
AEP-I&M | 2020 | 599151 | PARTIAL POWER | U | ARRESTER | 1 | 1 | 60 | 0.00010014 | 1.669e-06 | 60
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 1 | 179 | 0.00029347 | 1.6395e-06 | 179
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 277 | 303869 | 0.50717 | 0.00046232 | 1097
AEP-I&M | 2020 | 599151 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 474 | 0.00079112 | 1.669e-06 | 474
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | GUY/ANCHOR | 1 | 1 | 127 | 0.0002104 | 1.6567e-06 | 127
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 385 | 63620 | 0.10361 | 0.00062699 | 165.2468
AEP-I&M | 2021 | 603608 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 87 | 0.00014413 | 1.6567e-06 | 87
AEP-I&M | 2021 | 603608 | SUBTRANSMISSION LINE | AF | NONE | 1 | 249 | 10458 | 0.017326 | 0.00041252 | 42
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CF | FUSE | 1 | 1 | 64 | 0.00010603 | 1.6567e-06 | 64
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | CROSSARM | 1 | 83 | 5478 | 0.0090275 | 0.00013678 | 66
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 190 | 67545 | 0.11074 | 0.0003115 | 355.5
AEP-I&M | 2023 | 609949 | PARTIAL POWER | VA | SPLICE, OH | 1 | 1 | 355 | 0.00058202 | 1.6395e-06 | 355
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 1038 | 151111 | 0.25221 | 0.0017325 | 145.579
AEP-I&M | 2024 | 614045 | TRANSMISSION LINE | SCO | POLE | 1 | 83 | 23240 | 0.037847 | 0.00013517 | 280
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WL | NONE | 7 | 7 | 791 | 0.0013035 | 1.1536e-05 | 113
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WU | OTHER EQUIPMENT | 1 | 1 | 169 | 0.0002785 | 1.648e-06 | 169
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 60 | 859 | 91622 | 0.15099 | 0.0014156 | 106.6612
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 3 | 855 | 0.001409 | 4.9439e-06 | 285
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERO | NONE | 13 | 1954 | 86685 | 0.14285 | 0.0032201 | 44.3628
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | ARRESTER | 6 | 607 | 199092 | 0.32809 | 0.0010003 | 327.9934
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 11 | 112 | 69536 | 0.1152 | 0.00018555 | 620.8571
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | EQF | CROSSARM | 1 | 13 | 2392 | 0.0039419 | 2.1423e-05 | 184
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | METERING | 2 | 3 | 409 | 0.00067401 | 4.9439e-06 | 136.3333
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OL | NONE | 6 | 85 | 5340 | 0.0088001 | 0.00014008 | 62.8235
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 199 | 101025 | 0.16648 | 0.00032794 | 507.6633
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 401 | 3703 | 498269 | 0.83163 | 0.0061804 | 134.5582
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 319 | 1909 | 506874 | 0.84599 | 0.0031862 | 265.5181
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TR | CUTOUT | 2 | 41 | 6953 | 0.011458 | 6.7566e-05 | 169.5854
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 22 | 2392 | 0.0039923 | 3.6719e-05 | 108.7273
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | FUSE | 14 | 227 | 19484 | 0.032279 | 0.00037607 | 85.8326
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 1255 | 139335 | 0.23084 | 0.0020792 | 111.0239
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 7 | 47 | 1549 | 0.0025662 | 7.7865e-05 | 32.9574
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | CROSSARM | 15 | 8231 | 776201 | 1.2726 | 0.013495 | 94.3022
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | ERF | NONE | 6 | 4370 | 55946 | 0.092686 | 0.0072398 | 12.8023
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 132 | 7574 | 0.012641 | 0.00022031 | 57.3788
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 1 | 4596 | 0.007574 | 1.648e-06 | 4596
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | INSULATOR | 1 | 2 | 312 | 0.00052074 | 3.3381e-06 | 156
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 3 | 9 | 2342 | 0.0038397 | 1.4755e-05 | 260.2222
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 8 | 1071 | 0.0017559 | 1.3116e-05 | 133.875
AEP-I&M | 2023 | 609949 | TRANSMISSION STATION | SCO | CONDUCTOR OVERHEAD | 2 | 1137 | 6946 | 0.011388 | 0.0018641 | 6.1091
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 1 | 115 | 12535 | 0.020551 | 0.00018854 | 109
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 10 | 49 | 13450 | 0.021904 | 7.9799e-05 | 274.4898
AEP-I&M | 2021 | 603608 | PARTIAL POWER | ERF | NONE | 2 | 2 | 235 | 0.00038933 | 3.3134e-06 | 117.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 9 | 43 | 2160 | 0.0035177 | 7.0027e-05 | 50.2326
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 1056 | 47563 | 0.077458 | 0.0017197 | 45.0407
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 449 | 3803 | 317821 | 0.51759 | 0.0061934 | 83.5711
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 16 | 100 | 24183 | 0.039383 | 0.00016285 | 241.83
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | NONE | 59 | 771 | 209844 | 0.34174 | 0.0012556 | 272.1712
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TIR | NONE | 30 | 2758 | 362227 | 0.5899 | 0.0044915 | 131.3368
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 51 | 3104 | 1039969 | 1.6936 | 0.005055 | 335.0416
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ABI | NONE | 7 | 157 | 14084 | 0.022936 | 0.00025568 | 89.707
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | CUTOUT | 115 | 3182 | 385042 | 0.62706 | 0.005182 | 121.0063
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | FUSE | 3 | 132 | 6901 | 0.011239 | 0.00021497 | 52.2803
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | FUSE | 48 | 989 | 223289 | 0.36364 | 0.0016106 | 225.7725
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 2 | 488 | 0.00079473 | 3.2571e-06 | 244
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | TRANSFORMER, OH | 4 | 15 | 4833 | 0.0078708 | 2.4428e-05 | 322.2
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | POLE | 25 | 961 | 300625 | 0.48958 | 0.001565 | 312.8252
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 7 | 828 | 92068 | 0.14994 | 0.0013484 | 111.1932
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 55 | 3726 | 0.006068 | 8.957e-05 | 67.7455
AEP-I&M | 2021 | 603608 | PARTIAL POWER | UG | NONE | 4 | 4 | 1063 | 0.0017611 | 6.6268e-06 | 265.75
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VIN | POLE HARDWARE | 1 | 38 | 1900 | 0.0031712 | 6.3423e-05 | 50
AEP-I&M | 2023 | 609949 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 133 | 0.00021805 | 1.6395e-06 | 133
AEP-I&M | 2021 | 603608 | PARTIAL POWER | A | CUTOUT | 1 | 1 | 289 | 0.00047879 | 1.6567e-06 | 289
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 57 | 9.3933e-05 | 1.648e-06 | 57
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | CABLE TERMINATOR | 1 | 1 | 190 | 0.00031712 | 1.669e-06 | 190
AEP-I&M | 2023 | 609949 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 217 | 0.00035577 | 1.6395e-06 | 217
AEP-I&M | 2021 | 603608 | PARTIAL POWER | UB | CONN/CLAMP | 1 | 1 | 94 | 0.00015573 | 1.6567e-06 | 94
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 375 | 20250 | 0.032978 | 0.0006107 | 54
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 8 | 152 | 0.00025182 | 1.3254e-05 | 19
AEP-I&M | 2020 | 599151 | PARTIAL POWER | VIN | NONE | 3 | 4 | 776 | 0.0012952 | 6.6761e-06 | 194
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 3 | 177 | 0.00029324 | 4.9701e-06 | 59
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WT | POLE | 4 | 50 | 120983 | 0.19703 | 8.1427e-05 | 2419.66
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 73 | 11023 | 0.017951 | 0.00011888 | 151
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | U | NONE | 1 | 858 | 78936 | 0.12941 | 0.0014067 | 92
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 1 | 2 | 92 | 0.00014983 | 3.2571e-06 | 46
AEP-I&M | 2020 | 599151 | TRANSMISSION STATION | ABI | NONE | 3 | 3023 | 729638 | 1.2178 | 0.0050455 | 241.3622
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | POLE | 1 | 42 | 2730 | 0.0044459 | 6.8399e-05 | 65
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VIN | CONDUCTOR UG | 1 | 1 | 127 | 0.00020683 | 1.6285e-06 | 127
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 1 | 92 | 0.00014983 | 1.6285e-06 | 92
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | JUMPER/RISER | 2 | 6 | 310 | 0.00050485 | 9.7713e-06 | 51.6667
AEP-I&M | 2022 | 606813 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 1 | 12 | 1500 | 0.0024719 | 1.9775e-05 | 125
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | INSULATOR | 3 | 262 | 58450 | 0.096323 | 0.00043176 | 223.0916
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 464 | 18057 | 3138313 | 5.1718 | 0.029757 | 173.8004
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | O | NONE | 18 | 62 | 10862 | 0.017995 | 0.00010272 | 175.1935
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | METERING | 29 | 33 | 2559 | 0.0042395 | 5.4671e-05 | 77.5455
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | METERING | 23 | 24 | 2322 | 0.0038265 | 3.9551e-05 | 96.75
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OL | BREAKER | 1 | 9 | 2385 | 0.0039304 | 1.4832e-05 | 265
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | O | FUSE | 12 | 34 | 4448 | 0.0073301 | 5.603e-05 | 130.8235
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | NONE | 367 | 18691 | 2372810 | 3.9603 | 0.031196 | 126.9493
AEP-I&M | 2021 | 603608 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 10 | 3400 | 0.0056328 | 1.6567e-05 | 340
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | CUTOUT | 7 | 635 | 564355 | 0.93497 | 0.001052 | 888.748
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SO | NONE | 2 | 2 | 367 | 0.0006048 | 3.2959e-06 | 183.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | V | NONE | 8 | 726 | 70342 | 0.1174 | 0.0012117 | 96.8898
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 12 | 34 | 7010 | 0.011613 | 5.6328e-05 | 206.1765
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | POLE | 68 | 6304 | 2633607 | 4.3956 | 0.010522 | 417.7676
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 7 | 1060 | 0.0017468 | 1.1536e-05 | 151.4286
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | POLE | 260 | 37015 | 6441138 | 10.5601 | 0.060685 | 174.0143
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | UB | NONE | 1 | 1 | 68 | 0.00011266 | 1.6567e-06 | 68
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | ARRESTER | 2 | 24 | 5370 | 0.0088965 | 3.9761e-05 | 223.75
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 4 | 23 | 4531 | 0.0075065 | 3.8104e-05 | 197
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | CUTOUT | 59 | 135 | 26663 | 0.044501 | 0.00022532 | 197.5037
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | METERING | 2 | 2 | 205 | 0.00033783 | 3.2959e-06 | 102.5
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 6 | 84 | 52544 | 0.086145 | 0.00013772 | 625.5238
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 15 | 349 | 118564 | 0.19539 | 0.00057514 | 339.7249
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 560 | 0.00092775 | 3.3134e-06 | 280
AEP-I&M | 2020 | 599151 | PARTIAL POWER | A | NONE | 62 | 250 | 23129 | 0.038603 | 0.00041726 | 92.516
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | CIRCUIT SWITCHER | 1 | 1 | 134 | 0.00022083 | 1.648e-06 | 134
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | CABLE TERMINATOR | 1 | 1 | 90 | 0.00014832 | 1.648e-06 | 90
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 77 | 3056 | 348076 | 0.57066 | 0.0050103 | 113.8992
AEP-I&M | 2021 | 603608 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 2 | 491 | 0.00081344 | 3.3134e-06 | 245.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VIN | PEDESTAL | 1 | 2 | 34 | 5.6747e-05 | 3.3381e-06 | 17
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | FUSE | 43 | 1054 | 175681 | 0.28803 | 0.001728 | 166.6803
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | UG | NONE | 29 | 400 | 192334 | 0.31533 | 0.00065579 | 480.835
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 17 | 2182 | 362977 | 0.59509 | 0.0035773 | 166.3506
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 11 | 156 | 12377 | 0.020292 | 0.00025576 | 79.3397
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | POLE | 10 | 3315 | 714718 | 1.1929 | 0.0055328 | 215.6012
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | POLE | 13 | 811 | 131733 | 0.21987 | 0.0013536 | 162.4328
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 25 | 3692 | 0.0061621 | 4.1726e-05 | 147.68
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | CUTOUT | 4 | 18 | 2559 | 0.0041954 | 2.9511e-05 | 142.1667
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ABI | METERING | 1 | 1 | 149 | 0.00024869 | 1.669e-06 | 149
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERF | METERING | 4 | 4 | 227 | 0.00037216 | 6.5579e-06 | 56.75
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 142 | 4954 | 0.008122 | 0.00023281 | 34.8873
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VIN | FUSE | 15 | 84 | 8032 | 0.013168 | 0.00013772 | 95.619
AEP-I&M | 2023 | 609949 | TRANSMISSION LINE | EQF | STATIC WIRE | 5 | 2929 | 65206 | 0.1069 | 0.004802 | 22.2622
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | FUSE | 224 | 3302 | 322019 | 0.52442 | 0.0053775 | 97.5224
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | NONE | 166 | 724 | 50727 | 0.082611 | 0.0011791 | 70.0649
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CE | METERING | 3 | 3 | 266 | 0.00044068 | 4.9701e-06 | 88.6667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 1 | 327 | 0.00054174 | 1.6567e-06 | 327
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | POLE | 1 | 11 | 2372 | 0.0038629 | 1.7914e-05 | 215.6364
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | CUTOUT | 6 | 163 | 31741 | 0.051692 | 0.00026545 | 194.7301
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 5 | 68 | 5144 | 0.0083772 | 0.00011074 | 75.6471
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 1 | 44 | 7.3437e-05 | 1.669e-06 | 44
AEP-I&M | 2023 | 609949 | PARTIAL POWER | U | CONDUCTOR UG | 4 | 4 | 788 | 0.0012919 | 6.5579e-06 | 197
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | METERING | 1 | 1 | 119 | 0.0001938 | 1.6285e-06 | 119
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SO | NONE | 3 | 2961 | 18050 | 0.030126 | 0.004942 | 6.0959
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | BREAKER | 1 | 819 | 109369 | 0.17931 | 0.0013427 | 133.5397
AEP-I&M | 2025 | 614045 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 69 | 0.00011237 | 1.6285e-06 | 69
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | EQF | CONDUCTOR UG | 11 | 6134 | 793067 | 1.3069 | 0.010109 | 129.2903
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | TRANSFORMER, POWER - LTC | 1 | 9 | 1017 | 0.0016562 | 1.4657e-05 | 113
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VIN | FUSE | 1 | 2 | 180 | 0.00029314 | 3.2571e-06 | 90
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | METERING | 3 | 16 | 206 | 0.00034382 | 2.6704e-05 | 12.875
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 1 | 100 | 0.0001669 | 1.669e-06 | 100
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | OL | NONE | 1 | 1440 | 125280 | 0.2091 | 0.0024034 | 87
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TR | FUSE | 2 | 50 | 1963 | 0.0032521 | 8.2835e-05 | 39.26
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 1 | 2 | 164 | 0.00026887 | 3.279e-06 | 82
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 1 | 107 | 0.00017727 | 1.6567e-06 | 107
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 2 | 190 | 0.0003115 | 3.279e-06 | 95
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | TRANSFORMER, OH | 2 | 2 | 283 | 0.00046885 | 3.3134e-06 | 141.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | FUSE | 724 | 6204 | 576941 | 0.95077 | 0.010224 | 92.995
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 339 | 14874 | 2351606 | 3.9249 | 0.024825 | 158.1018
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | CROSSARM | 13 | 64 | 4074 | 0.0067996 | 0.00010682 | 63.6562
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | EQF | POLE | 1 | 1504 | 665155 | 1.102 | 0.0024917 | 442.2573
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WFS | NONE | 3 | 17 | 3216 | 0.0052998 | 2.8015e-05 | 189.1765
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | OTHER EQUIPMENT | 1 | 15 | 1290 | 0.0021259 | 2.4719e-05 | 86
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | SCO | NONE | 10 | 7057 | 145826 | 0.24159 | 0.011691 | 20.664
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 2 | 34 | 6542 | 0.010838 | 5.6328e-05 | 192.4118
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | OU | NONE | 6 | 132 | 16544 | 0.027264 | 0.00021753 | 125.3333
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 1 | 75 | 0.00012296 | 1.6395e-06 | 75
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 3 | 642 | 0.0010636 | 4.9701e-06 | 214
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | AF | NONE | 1 | 330 | 54450 | 0.089731 | 0.00054382 | 165
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 115 | 742 | 67746 | 0.11033 | 0.0012084 | 91.3019
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 7 | 12 | 2874 | 0.0047119 | 1.9674e-05 | 239.5
AEP-I&M | 2020 | 599151 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 4 | 4468 | 0.0074572 | 6.6761e-06 | 1117
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CE | NONE | 5 | 6 | 978 | 0.0016203 | 9.9402e-06 | 163
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | FUSE | 144 | 3521 | 258071 | 0.4231 | 0.0057726 | 73.2948
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | CROSSARM | 47 | 24437 | 2710942 | 4.5246 | 0.040786 | 110.936
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | F | NONE | 8 | 1311 | 196649 | 0.32579 | 0.0021719 | 149.9992
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 17 | 3298 | 0.005435 | 2.8015e-05 | 194
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VIN | FUSE | 22 | 84 | 16414 | 0.027395 | 0.0001402 | 195.4048
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | F | CUTOUT | 5 | 382 | 27338 | 0.04482 | 0.00062628 | 71.5654
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VIN | NONE | 86 | 432 | 43590 | 0.071465 | 0.00070826 | 100.9028
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | CUTOUT | 31 | 83 | 16273 | 0.026679 | 0.00013608 | 196.0602
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 131 | 229 | 37609 | 0.061659 | 0.00037544 | 164.2314
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | FUSE | 27 | 874 | 171181 | 0.28065 | 0.0014329 | 195.8593
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 306 | 13426 | 0.022125 | 0.00050427 | 43.8758
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | POLE | 44 | 2169 | 286441 | 0.46961 | 0.003556 | 132.0613
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 797 | 6981 | 617709 | 1.006 | 0.011369 | 88.4843
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 1 | 105 | 22100 | 0.03642 | 0.00017304 | 210.4762
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ABI | CONDUCTOR UG | 1 | 21 | 3456 | 0.0056953 | 3.4607e-05 | 164.5714
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | CROSSARM | 20 | 7183 | 2193762 | 3.6615 | 0.011989 | 305.4103
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 1 | 60 | 0.00010014 | 1.669e-06 | 60
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | TRANSFORMER, OH | 19 | 67 | 20448 | 0.033524 | 0.00010985 | 305.194
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 17 | 1938 | 46980 | 0.078411 | 0.0032346 | 24.2415
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | CROSSARM | 4 | 546 | 85458 | 0.14263 | 0.00091129 | 156.5165
AEP-I&M | 2020 | 599151 | PARTIAL POWER | A | CUTOUT | 2 | 2 | 333 | 0.00055579 | 3.3381e-06 | 166.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 9 | 216 | 0.00035596 | 1.4832e-05 | 24
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WW | FUSE | 4 | 22 | 3618 | 0.0059316 | 3.6069e-05 | 164.4545
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | CE | NONE | 8 | 109 | 20868 | 0.034213 | 0.0001787 | 191.4495
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 20 | 2080 | 0.0034716 | 3.3381e-05 | 104
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 11 | 2805 | 0.0046816 | 1.8359e-05 | 255
AEP-I&M | 2024 | 614045 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 3 | 495 | 0.00080613 | 4.8856e-06 | 165
AEP-I&M | 2021 | 603608 | SUBTRANSMISSION LINE | VA | POLE | 3 | 1361 | 948617 | 1.5716 | 0.0022548 | 697
AEP-I&M | 2023 | 609949 | PARTIAL POWER | VA | NONE | 5 | 5 | 345 | 0.00056562 | 8.1974e-06 | 69
AEP-I&M | 2023 | 609949 | PARTIAL POWER | ABI | CONDUCTOR OVERHEAD | 1 | 1 | 124 | 0.0002033 | 1.6395e-06 | 124
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 2 | 124 | 0.00020543 | 3.3134e-06 | 62
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 17 | 2788 | 0.0045404 | 2.7685e-05 | 164
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 19 | 66 | 2066 | 0.0033646 | 0.00010748 | 31.303
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 1 | 156 | 0.00025405 | 1.6285e-06 | 156
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 41 | 6439 | 0.010747 | 6.843e-05 | 157.0488
AEP-I&M | 2024 | 614045 | PARTIAL POWER | V | METERING | 1 | 1 | 44 | 7.1656e-05 | 1.6285e-06 | 44
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 4 | 23 | 1685 | 0.0027441 | 3.7457e-05 | 73.2609
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 1 | 814 | 0.0013256 | 1.6285e-06 | 814
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 3 | 591 | 0.00096247 | 4.8856e-06 | 197
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | OU | NONE | 2 | 3 | 212 | 0.00034525 | 4.8856e-06 | 70.6667
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WI | FUSE | 2 | 463 | 21640 | 0.035242 | 0.00075402 | 46.7387
AEP-I&M | 2023 | 609949 | TRANSMISSION STATION | OL | TRANSFORMER, POWER - NON LTC | 1 | 228 | 2736 | 0.0044856 | 0.0003738 | 12
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 1 | 82 | 0.00013354 | 1.6285e-06 | 82
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 1 | 185 | 49210 | 0.080141 | 0.00030128 | 266
AEP-I&M | 2024 | 614045 | PARTIAL POWER | FO | CONDUCTOR UG | 3 | 3 | 506 | 0.00082404 | 4.8856e-06 | 168.6667
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | SPLICE, UG | 1 | 1 | 193 | 0.00031431 | 1.6285e-06 | 193
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | SPLICE, UG | 2 | 4 | 3748 | 0.0062555 | 6.6761e-06 | 937
AEP-I&M | 2022 | 606813 | PARTIAL POWER | O | METERING | 1 | 1 | 48 | 7.9102e-05 | 1.648e-06 | 48
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 176 | 30153 | 0.050326 | 0.00029375 | 171.3239
AEP-I&M | 2022 | 606813 | PARTIAL POWER | FO | NONE | 1 | 1 | 155 | 0.00025543 | 1.648e-06 | 155
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CO | POLE | 1 | 1 | 135 | 0.00022366 | 1.6567e-06 | 135
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TOR | FUSE | 1 | 1 | 119 | 0.0001938 | 1.6285e-06 | 119
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 25 | 20775 | 0.033833 | 4.0714e-05 | 831
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 37 | 9620 | 0.015772 | 6.0661e-05 | 260
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 4 | 324 | 0.00053394 | 6.5918e-06 | 81
AEP-I&M | 2023 | 609949 | TRANSMISSION LINE | SCO | NONE | 3 | 2303 | 36394 | 0.059667 | 0.0037757 | 15.8029
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | CABLE TERMINATOR | 37 | 41 | 6695 | 0.011033 | 6.7566e-05 | 163.2927
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | NONE | 44 | 1180 | 59911 | 0.099255 | 0.0019549 | 50.772
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 22 | 437 | 138973 | 0.22902 | 0.00072016 | 318.016
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 10 | 749 | 160564 | 0.26601 | 0.0012409 | 214.3712
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 47 | 652 | 223012 | 0.36946 | 0.0010802 | 342.0429
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 104 | 2354 | 371937 | 0.61619 | 0.0038999 | 158.0021
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | METERING | 2 | 2 | 741 | 0.0012211 | 3.2959e-06 | 370.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 2 | 57 | 24373 | 0.040166 | 9.3933e-05 | 427.5965
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ABI | ARRESTER | 1 | 1 | 161 | 0.00026532 | 1.648e-06 | 161
AEP-I&M | 2021 | 603608 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 4 | 28 | 5570 | 0.0092278 | 4.6388e-05 | 198.9286
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 3 | 35 | 54788 | 0.090768 | 5.7985e-05 | 1565.3714
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | AF | NONE | 2 | 572 | 166452 | 0.27576 | 0.00094763 | 291
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | FUSE | 20 | 441 | 89904 | 0.15005 | 0.00073604 | 203.8639
AEP-I&M | 2022 | 606813 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 5 | 5 | 709 | 0.0011684 | 8.2398e-06 | 141.8
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | METERING | 3 | 3 | 3170 | 0.0052908 | 5.0071e-06 | 1056.6667
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TR | FUSE | 2 | 17 | 2624 | 0.0043242 | 2.8015e-05 | 154.3529
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | NONE | 844 | 37086 | 6322837 | 10.297 | 0.060396 | 170.4912
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 19 | 411 | 86692 | 0.14469 | 0.00068597 | 210.9294
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | EQF | INSULATOR | 4 | 6187 | 1624214 | 2.6629 | 0.010143 | 262.5204
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 95 | 755 | 159405 | 0.2596 | 0.0012296 | 211.1325
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | POLE | 14 | 2385 | 192686 | 0.31591 | 0.0039102 | 80.7908
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 2663 | 325072 | 0.54255 | 0.0044446 | 122.0698
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | ARRESTER | 7 | 30 | 2706 | 0.0044364 | 4.9184e-05 | 90.2
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 276 | 20838 | 0.034779 | 0.00046065 | 75.5
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | CUTOUT | 9 | 389 | 72492 | 0.12099 | 0.00064925 | 186.3548
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 17 | 5505 | 0.0091202 | 2.8164e-05 | 323.8235
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | POLE | 261 | 38662 | 6153599 | 10.0214 | 0.062963 | 159.164
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | POLE | 4 | 68 | 11621 | 0.019151 | 0.00011206 | 170.8971
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 272 | 0.00045062 | 1.6567e-06 | 272
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 1 | 118 | 0.00019695 | 1.669e-06 | 118
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | FUSE | 49 | 821 | 197123 | 0.32102 | 0.001337 | 240.1011
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 5 | 16 | 10822 | 0.017742 | 2.6232e-05 | 676.375
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 40 | 693 | 171948 | 0.28003 | 0.0011286 | 248.1212
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SO | NONE | 5 | 112 | 15660 | 0.025674 | 0.00018362 | 139.8214
AEP-I&M | 2023 | 609949 | TRANSMISSION LINE | ERF | NONE | 6 | 9276 | 334680 | 0.5487 | 0.015208 | 36.0802
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UG | FUSE | 3 | 45 | 9060 | 0.01493 | 7.4158e-05 | 201.3333
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 194 | 9606 | 0.015749 | 0.00031806 | 49.5155
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 5 | 302 | 12913 | 0.02128 | 0.00049768 | 42.7583
AEP-I&M | 2024 | 614045 | PARTIAL POWER | UG | NONE | 2 | 2 | 622 | 0.001013 | 3.2571e-06 | 311
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 8 | 763 | 257577 | 0.41948 | 0.0012426 | 337.5845
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | METERING | 27 | 27 | 2546 | 0.0041463 | 4.3971e-05 | 94.2963
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 2 | 48 | 6861 | 0.011307 | 7.9102e-05 | 142.9375
AEP-I&M | 2024 | 614045 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 9 | 749 | 0.0012198 | 1.4657e-05 | 83.2222
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | POLE | 47 | 3486 | 538519 | 0.877 | 0.0056771 | 154.4805
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | FUSE | 31 | 327 | 53094 | 0.086466 | 0.00053253 | 162.367
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | GUY/ANCHOR | 1 | 2 | 136 | 0.00022148 | 3.2571e-06 | 68
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | METERING | 5 | 6 | 240 | 0.00039085 | 9.7713e-06 | 40
AEP-I&M | 2025 | 614045 | TRANSMISSION LINE | WW | POLE | 1 | 1 | 1524 | 0.0024819 | 1.6285e-06 | 1524
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | OU | FUSE | 1 | 33 | 660 | 0.0010934 | 5.4671e-05 | 20
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 8 | 1.3116e-05 | 1.6395e-06 | 8
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | CIRCUIT SWITCHER | 1 | 33 | 19635 | 0.032358 | 5.4382e-05 | 595
AEP-I&M | 2021 | 603608 | SUBTRANSMISSION LINE | EQF | INSULATOR | 1 | 1186 | 520654 | 0.86257 | 0.0019649 | 439
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 2 | 1422 | 0.0023734 | 3.3381e-06 | 711
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 1 | 252 | 0.00041528 | 1.648e-06 | 252
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 242 | 56551 | 0.093688 | 0.00040092 | 233.6818
AEP-I&M | 2024 | 614045 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 991 | 378160 | 0.61585 | 0.0016139 | 381.5943
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 31 | 5146 | 0.0084368 | 5.0824e-05 | 166
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | EQF | CUTOUT | 1 | 1 | 298 | 0.00049737 | 1.669e-06 | 298
AEP-I&M | 2023 | 609949 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 238 | 0.0003902 | 1.6395e-06 | 238
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 995 | 87560 | 0.14355 | 0.0016313 | 88
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 305 | 7148 | 786157 | 1.3024 | 0.011842 | 109.9828
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | CUTOUT | 267 | 1750 | 136648 | 0.22403 | 0.0028691 | 78.0846
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | CUTOUT | 6 | 156 | 9745 | 0.016059 | 0.00025708 | 62.4679
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | AB | NONE | 6 | 4629 | 705037 | 1.1619 | 0.0076284 | 152.3087
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | NONE | 129 | 6395 | 2158114 | 3.5754 | 0.010595 | 337.469
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 7 | 595 | 0.00098053 | 1.1536e-05 | 85
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 3 | 513 | 0.0008454 | 4.9439e-06 | 171
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 39 | 462 | 53600 | 0.088799 | 0.0007654 | 116.0173
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 122 | 2982 | 343303 | 0.57298 | 0.004977 | 115.1251
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | POLE HARDWARE | 4 | 78 | 7343 | 0.012165 | 0.00012922 | 94.141
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 2 | 144 | 0.00023731 | 3.2959e-06 | 72
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | INSULATOR | 3 | 2204 | 98319 | 0.16203 | 0.0036321 | 44.6093
AEP-I&M | 2020 | 599151 | PARTIAL POWER | OL | TRANSFORMER, OH | 1 | 12 | 1464 | 0.0024435 | 2.0028e-05 | 122
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WU | METERING | 1 | 1 | 127 | 0.00020683 | 1.6285e-06 | 127
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 313 | 2403 | 792468 | 1.3129 | 0.0039811 | 329.7828
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | FUSE | 185 | 2774 | 353107 | 0.58499 | 0.0045957 | 127.2916
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | FUSE | 106 | 2298 | 498056 | 0.82513 | 0.0038071 | 216.7346
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | INSULATOR | 48 | 7978 | 1370255 | 2.2701 | 0.013217 | 171.7542
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | CUTOUT | 14 | 356 | 106359 | 0.17527 | 0.00058667 | 298.7612
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | CUTOUT | 6 | 47 | 55718 | 0.091821 | 7.7454e-05 | 1185.4894
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | POLE | 3 | 156 | 26360 | 0.043671 | 0.00025845 | 168.9744
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | FUSE | 65 | 718 | 201410 | 0.33616 | 0.0011984 | 280.5153
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | O | NONE | 19 | 337 | 51984 | 0.086763 | 0.00056246 | 154.2552
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 4 | 30 | 8408 | 0.013856 | 4.9439e-05 | 280.2667
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 59 | 15669 | 0.025822 | 9.7229e-05 | 265.5763
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | METERING | 11 | 11 | 908 | 0.0015155 | 1.8359e-05 | 82.5455
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 14 | 1534 | 162072 | 0.2705 | 0.0025603 | 105.6532
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 2 | 10 | 2022 | 0.0033748 | 1.669e-05 | 202.2
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 1 | 348 | 0.00058082 | 1.669e-06 | 348
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 7 | 26 | 1551 | 0.0025428 | 4.2627e-05 | 59.6538
AEP-I&M | 2023 | 609949 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 3 | 185 | 0.0003033 | 4.9184e-06 | 61.6667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CF | CUTOUT | 6 | 553 | 145505 | 0.24106 | 0.00091616 | 263.1193
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 26 | 1056 | 138049 | 0.22482 | 0.0017197 | 130.7282
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 1 | 329 | 0.00054506 | 1.6567e-06 | 329
AEP-I&M | 2021 | 603608 | DISTRIBUTION SOURCE | A | NONE | 1 | 646 | 202844 | 0.33605 | 0.0010702 | 314
AEP-I&M | 2023 | 609949 | SUBTRANSMISSION LINE | TOR | NONE | 2 | 1730 | 130074 | 0.21325 | 0.0028363 | 75.1873
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TR | POLE | 3 | 2048 | 299111 | 0.49922 | 0.0034182 | 146.0503
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 19 | 513 | 0.00084105 | 3.115e-05 | 27
AEP-I&M | 2023 | 609949 | TRANSMISSION LINE | EQF | INSULATOR | 2 | 2939 | 278071 | 0.45589 | 0.0048184 | 94.6142
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TOR | POLE HARDWARE | 1 | 1 | 103 | 0.00016887 | 1.6395e-06 | 103
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 4 | 4 | 333 | 0.00055579 | 6.6761e-06 | 83.25
AEP-I&M | 2023 | 609949 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 2 | 2 | 523 | 0.00085745 | 3.279e-06 | 261.5
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 12 | 863 | 0.0014149 | 1.9674e-05 | 71.9167
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 3 | 205 | 0.00033385 | 4.8856e-06 | 68.3333
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 7 | 30 | 11249 | 0.018636 | 4.9701e-05 | 374.9667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 477 | 39393 | 0.065263 | 0.00079025 | 82.5849
AEP-I&M | 2023 | 609949 | PARTIAL POWER | A | CABLE TERMINATOR | 1 | 2 | 386 | 0.00063284 | 3.279e-06 | 193
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 197 | 4555 | 699413 | 1.139 | 0.007418 | 153.5484
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 2 | 35 | 7742 | 0.012608 | 5.6999e-05 | 221.2
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | ARRESTER | 3 | 1608 | 66004 | 0.10749 | 0.0026187 | 41.0473
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TOR | INSULATOR | 1 | 2 | 6044 | 0.010088 | 3.3381e-06 | 3022
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | PEDESTAL | 1 | 23 | 1150 | 0.0018951 | 3.7903e-05 | 50
AEP-I&M | 2022 | 606813 | PARTIAL POWER | UG | SPLICE, UG | 1 | 1 | 278 | 0.00045813 | 1.648e-06 | 278
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 31 | 1760 | 0.0029158 | 5.1358e-05 | 56.7742
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 1 | 332 | 0.00054431 | 1.6395e-06 | 332
AEP-I&M | 2020 | 599151 | TRANSMISSION LINE | EQF | INSULATOR | 2 | 1284 | 457692 | 0.7639 | 0.002143 | 356.4579
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 3 | 663 | 0.0011066 | 5.0071e-06 | 221
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | POLE | 2 | 16 | 1173 | 0.0019578 | 2.6704e-05 | 73.3125
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | CONDUCTOR UG | 316 | 421 | 111505 | 0.18376 | 0.00069379 | 264.8575
AEP-I&M | 2023 | 609949 | PARTIAL POWER | A | FUSE | 24 | 79 | 7055 | 0.011567 | 0.00012952 | 89.3038
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | CROSSARM | 29 | 1226 | 89912 | 0.14817 | 0.0020204 | 73.3377
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 88 | 2603 | 274081 | 0.45167 | 0.0042896 | 105.2943
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CO | NONE | 1 | 1 | 207 | 0.00034113 | 1.648e-06 | 207
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 45 | 225 | 60930 | 0.10041 | 0.00037079 | 270.8
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WL | FUSE | 3 | 12 | 1204 | 0.0019841 | 1.9775e-05 | 100.3333
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 11 | 51 | 6293 | 0.010371 | 8.4046e-05 | 123.3922
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | AF | REGULATOR | 1 | 1055 | 13715 | 0.022602 | 0.0017386 | 13
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CO | CONDUCTOR UG | 21 | 21 | 5017 | 0.0082678 | 3.4607e-05 | 238.9048
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 50 | 8.2398e-05 | 1.648e-06 | 50
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | NONE | 1283 | 14647 | 1250404 | 2.087 | 0.024446 | 85.3693
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WW | FUSE | 15 | 166 | 108863 | 0.1794 | 0.00027356 | 655.8012
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 10 | 86 | 5543 | 0.0091831 | 0.00014248 | 64.4535
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | CUTOUT | 9 | 85 | 26777 | 0.044692 | 0.00014187 | 315.0235
AEP-I&M | 2022 | 606813 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 5 | 5 | 1137 | 0.0018737 | 8.2398e-06 | 227.4
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 35 | 521 | 216983 | 0.36215 | 0.00086956 | 416.4741
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 40 | 1375 | 354946 | 0.58804 | 0.002278 | 258.1425
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 216 | 11914 | 3436390 | 5.7354 | 0.019885 | 288.4329
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | CABLE TERMINATOR | 26 | 26 | 3023 | 0.0050082 | 4.3074e-05 | 116.2692
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 3 | 27 | 2228 | 0.0036716 | 4.4495e-05 | 82.5185
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 50 | 1545 | 307988 | 0.51404 | 0.0025786 | 199.345
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | JUMPER/RISER | 3 | 1402 | 156104 | 0.25725 | 0.0023104 | 111.3438
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | NONE | 129 | 5124 | 1184572 | 1.9771 | 0.0085521 | 231.1811
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | JUMPER/RISER | 2 | 86 | 7018 | 0.011627 | 0.00014248 | 81.6047
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 6 | 110 | 10735 | 0.017785 | 0.00018224 | 97.5909
AEP-I&M | 2022 | 606813 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 7 | 8680 | 0.014304 | 1.1536e-05 | 1240
AEP-I&M | 2020 | 599151 | PARTIAL POWER | UG | CONDUCTOR UG | 20 | 21 | 5385 | 0.0089877 | 3.505e-05 | 256.4286
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | O | CONDUCTOR UG | 2 | 2 | 335 | 0.000555 | 3.3134e-06 | 167.5
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | CROSSARM | 2 | 2 | 417 | 0.00069085 | 3.3134e-06 | 208.5
AEP-I&M | 2020 | 599151 | PARTIAL POWER | V | METERING | 1 | 1 | 71 | 0.0001185 | 1.669e-06 | 71
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | FUSE | 3 | 59 | 8939 | 0.014809 | 9.7746e-05 | 151.5085
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | NONE | 122 | 11958 | 2085606 | 3.4193 | 0.019605 | 174.4109
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 2 | 34 | 1090 | 0.001787 | 5.5742e-05 | 32.0588
AEP-I&M | 2023 | 609949 | TRANSMISSION STATION | ABX | NONE | 2 | 2 | 308 | 0.00050496 | 3.279e-06 | 154
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 6 | 41 | 4294 | 0.0070399 | 6.7219e-05 | 104.7317
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ABI | FUSE | 51 | 153 | 17129 | 0.028083 | 0.00025084 | 111.9542
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | AO | NONE | 2 | 940 | 119404 | 0.19782 | 0.0015573 | 127.0255
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 351 | 1902 | 386363 | 0.62921 | 0.0030975 | 203.1351
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | NONE | 2264 | 17797 | 1384961 | 2.2555 | 0.028983 | 77.8199
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 1 | 50 | 8.2398e-05 | 1.648e-06 | 50
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | CUTOUT | 9 | 531 | 22558 | 0.037372 | 0.00087971 | 42.4821
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 2 | 168 | 0.00027686 | 3.2959e-06 | 84
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 13 | 10517 | 0.017424 | 2.1537e-05 | 809
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 6 | 9 | 820 | 0.0013444 | 1.4755e-05 | 91.1111
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 3 | 71 | 0.0001164 | 4.9184e-06 | 23.6667
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | CONN/CLAMP | 2 | 22 | 8444 | 0.014093 | 3.6719e-05 | 383.8182
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | EQF | INSULATOR | 1 | 654 | 89598 | 0.14844 | 0.0010835 | 137
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | AO | NONE | 1 | 513 | 85671 | 0.14299 | 0.00085621 | 167
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | AF | POLE | 1 | 859 | 136581 | 0.22392 | 0.0014083 | 159
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 5 | 38 | 1105 | 0.0018116 | 6.23e-05 | 29.0789
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 1 | 76 | 0.00012591 | 1.6567e-06 | 76
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | JUMPER/RISER | 8 | 11 | 1781 | 0.0029199 | 1.8034e-05 | 161.9091
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 8 | 35 | 7815 | 0.012727 | 5.6999e-05 | 223.2857
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 267 | 27016 | 0.043997 | 0.00043482 | 101.1835
AEP-I&M | 2023 | 609949 | PARTIAL POWER | O | CONN/CLAMP | 1 | 1 | 49 | 8.0335e-05 | 1.6395e-06 | 49
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | REGULATOR | 5 | 773 | 74136 | 0.12073 | 0.0012589 | 95.9069
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 6 | 2368 | 428285 | 0.69748 | 0.0038564 | 180.8636
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 24 | 2499 | 0.0040697 | 3.9085e-05 | 104.125
AEP-I&M | 2025 | 614045 | TRANSMISSION STATION | EQF | MOAB | 2 | 1746 | 533814 | 0.86934 | 0.0028434 | 305.7354
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WL | CUTOUT | 3 | 10 | 1255 | 0.0020438 | 1.6285e-05 | 125.5
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | PEDESTAL | 17 | 83 | 7495 | 0.012206 | 0.00013517 | 90.3012
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | SCO | NONE | 1 | 1 | 380 | 0.000623 | 1.6395e-06 | 380
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 7 | 378 | 0.00061972 | 1.1476e-05 | 54
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 10 | 3690 | 0.0060093 | 1.6285e-05 | 369
AEP-I&M | 2020 | 599151 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 156 | 0.00026037 | 1.669e-06 | 156
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 2 | 290 | 0.00047228 | 3.2571e-06 | 145
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 15 | 2682 | 0.0043678 | 2.4428e-05 | 178.8
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 6 | 1068 | 0.0017694 | 9.9402e-06 | 178
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 625 | 34691 | 0.056875 | 0.0010247 | 55.5056
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 1 | 1481 | 0.0024536 | 1.6567e-06 | 1481
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | INSULATOR | 1 | 308 | 12628 | 0.02081 | 0.00050757 | 41
AEP-I&M | 2024 | 614045 | PARTIAL POWER | ABI | FUSE | 5 | 11 | 676 | 0.0011009 | 1.7914e-05 | 61.4545
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 23 | 2208 | 0.00362 | 3.7708e-05 | 96
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | CROSSARM | 1 | 23 | 828 | 0.0013645 | 3.7903e-05 | 36
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 2 | 6 | 1896 | 0.0031645 | 1.0014e-05 | 316
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 97 | 8277 | 0.013479 | 0.00015797 | 85.3299
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 151 | 0.00025202 | 1.669e-06 | 151
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WT | FUSE | 1 | 4 | 268 | 0.00043645 | 6.5142e-06 | 67
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 1 | 61 | 9.9341e-05 | 1.6285e-06 | 61
AEP-I&M | 2025 | 614045 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 41 | 6.677e-05 | 1.6285e-06 | 41
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 121 | 0.00020195 | 1.669e-06 | 121
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 2 | 8 | 1945 | 0.0031675 | 1.3028e-05 | 243.125
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 1 | 239 | 0.00038922 | 1.6285e-06 | 239
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 1 | 54 | 8.7941e-05 | 1.6285e-06 | 54
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 2 | 3318 | 0.0055378 | 3.3381e-06 | 1659
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WT | NONE | 3 | 26 | 28450 | 0.046332 | 4.2342e-05 | 1094.2308
AEP-I&M | 2020 | 599151 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 96 | 0.00016023 | 1.669e-06 | 96
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 2 | 369 | 0.00060093 | 3.2571e-06 | 184.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 1 | 65 | 0.00010586 | 1.6285e-06 | 65
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | TRANSFORMER, OH | 18 | 99 | 31699 | 0.052238 | 0.00016315 | 320.1919
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | CUTOUT | 8 | 375 | 12932 | 0.021311 | 0.00061798 | 34.4853
AEP-I&M | 2022 | 606813 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 5 | 5 | 682 | 0.0011239 | 8.2398e-06 | 136.4
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | NONE | 86 | 6343 | 1110100 | 1.8294 | 0.010453 | 175.0118
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | ARRESTER | 46 | 1520 | 219979 | 0.36252 | 0.0025049 | 144.723
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CF | NONE | 5 | 34 | 2760 | 0.0045484 | 5.603e-05 | 81.1765
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 1 | 787 | 0.0012969 | 1.648e-06 | 787
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WL | NONE | 10 | 15 | 2338 | 0.0038734 | 2.4851e-05 | 155.8667
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | METERING | 7 | 21 | 491 | 0.00080915 | 3.4607e-05 | 23.381
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | NONE | 116 | 2798 | 207116 | 0.34568 | 0.0046699 | 74.0229
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 4 | 1144 | 0.0019094 | 6.6761e-06 | 286
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 1 | 31 | 5.174e-05 | 1.669e-06 | 31
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 9 | 30 | 3316 | 0.0055345 | 5.0071e-05 | 110.5333
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | CROSSARM | 18 | 8940 | 2276736 | 3.7719 | 0.014811 | 254.6685
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 46 | 6432 | 0.0106 | 7.5806e-05 | 139.8261
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 269 | 105398 | 0.17369 | 0.0004433 | 391.8141
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 2 | 20 | 2267 | 0.0037359 | 3.2959e-05 | 113.35
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | METERING | 10 | 24 | 1692 | 0.002774 | 3.9348e-05 | 70.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 2 | 21 | 2279 | 0.0037557 | 3.4607e-05 | 108.5238
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 16 | 635 | 237720 | 0.38974 | 0.0010411 | 374.3622
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | ARRESTER | 7 | 188 | 19554 | 0.032636 | 0.00031378 | 104.0106
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | U | POLE | 3 | 89 | 19405 | 0.032148 | 0.00014745 | 218.0337
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WU | FUSE | 1 | 1 | 61 | 0.00010106 | 1.6567e-06 | 61
AEP-I&M | 2023 | 609949 | TRANSMISSION STATION | EQF | INSULATOR | 1 | 2 | 390 | 0.0006394 | 3.279e-06 | 195
AEP-I&M | 2022 | 606813 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 53 | 8.7342e-05 | 1.648e-06 | 53
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | F | NONE | 24 | 4786 | 348990 | 0.56835 | 0.0077942 | 72.9189
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | O | NONE | 4 | 637 | 44849 | 0.073039 | 0.0010374 | 70.4066
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TR | POLE | 3 | 210 | 61941 | 0.10208 | 0.00034607 | 294.9571
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERO | NONE | 1 | 2 | 68 | 0.00011349 | 3.3381e-06 | 34
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | CE | FUSE | 1 | 12 | 2477 | 0.0040339 | 1.9543e-05 | 206.4167
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 4 | 257 | 72006 | 0.11929 | 0.00042577 | 280.179
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WU | NONE | 5 | 7 | 1779 | 0.0028972 | 1.14e-05 | 254.1429
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 3 | 352 | 69240 | 0.11276 | 0.00057325 | 196.7045
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | CONN/CLAMP | 4 | 59 | 14077 | 0.022925 | 9.6084e-05 | 238.5932
AEP-I&M | 2021 | 603608 | DISTRIBUTION SOURCE | SCO | NONE | 1 | 709 | 7090 | 0.011746 | 0.0011746 | 10
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 8 | 757 | 31479 | 0.051265 | 0.0012328 | 41.5839
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 10 | 979 | 0.0015943 | 1.6285e-05 | 97.9
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 2 | 18 | 1906 | 0.0031577 | 2.9821e-05 | 105.8889
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 73 | 21900 | 0.036282 | 0.00012094 | 300
AEP-I&M | 2020 | 599151 | PARTIAL POWER | OU | CONDUCTOR UG | 2 | 2 | 234 | 0.00039055 | 3.3381e-06 | 117
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 8 | 7136 | 0.011822 | 1.3254e-05 | 892
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | U | ARRESTER | 1 | 9 | 909 | 0.0015059 | 1.491e-05 | 101
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OL | REGULATOR | 1 | 581 | 5810 | 0.0096971 | 0.00096971 | 10
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | AF | POLE | 2 | 816 | 212721 | 0.35504 | 0.0013619 | 260.6875
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 2 | 222 | 0.00036154 | 3.2571e-06 | 111
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | SWITCH, UG | 1 | 9 | 873 | 0.0014571 | 1.5021e-05 | 97
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 2 | 1260 | 0.002052 | 3.2571e-06 | 630
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | POLE | 370 | 62428 | 9533047 | 15.71 | 0.10288 | 152.7047
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | U | FUSE | 167 | 2202 | 349751 | 0.57943 | 0.0036481 | 158.8333
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ABI | CUTOUT | 16 | 49 | 5663 | 0.0093324 | 8.075e-05 | 115.5714
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ERF | NONE | 1 | 1 | 19 | 3.1311e-05 | 1.648e-06 | 19
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CO | CONN/CLAMP | 42 | 91 | 16174 | 0.026796 | 0.00015076 | 177.7363
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | JUMPER/RISER | 2 | 533 | 84626 | 0.13946 | 0.00087836 | 158.773
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 30 | 453 | 70170 | 0.11625 | 0.00075049 | 154.9007
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | SPLICE, UG | 2 | 2 | 309 | 0.00051573 | 3.3381e-06 | 154.5
AEP-I&M | 2020 | 599151 | PARTIAL POWER | U | NONE | 52 | 123 | 10476 | 0.017485 | 0.00020529 | 85.1707
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | O | FUSE | 1 | 1 | 58 | 9.6804e-05 | 1.669e-06 | 58
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | GC | NONE | 4 | 2372 | 729177 | 1.208 | 0.0039297 | 307.4102
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | F | CROSSARM | 2 | 1909 | 101090 | 0.16574 | 0.0031298 | 52.9544
AEP-I&M | 2023 | 609949 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 12 | 2710 | 0.004443 | 1.9674e-05 | 225.8333
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 2 | 16 | 3424 | 0.0055761 | 2.6057e-05 | 214
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 17 | 1516 | 77989 | 0.12701 | 0.0024689 | 51.4439
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 6 | 1801 | 129023 | 0.21012 | 0.002933 | 71.6396
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 10 | 300 | 0.00050071 | 1.669e-05 | 30
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 55 | 189 | 18490 | 0.030112 | 0.0003078 | 97.8307
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 50 | 426 | 33133 | 0.053959 | 0.00069376 | 77.777
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 9 | 89 | 5279 | 0.0085971 | 0.00014494 | 59.3146
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 1038 | 92382 | 0.15045 | 0.0016904 | 89
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 47 | 15308 | 0.02493 | 7.6542e-05 | 325.7021
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | EQF | CROSSARM | 1 | 21 | 6132 | 0.010234 | 3.505e-05 | 292
AEP-I&M | 2025 | 614045 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 10 | 10 | 1943 | 0.0031643 | 1.6285e-05 | 194.3
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 2 | 306 | 0.00049833 | 3.2571e-06 | 153
AEP-I&M | 2025 | 614045 | PARTIAL POWER | ERF | NONE | 2 | 2 | 1012 | 0.0016481 | 3.2571e-06 | 506
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | EQF | RELAY | 1 | 1300 | 122200 | 0.20138 | 0.0021423 | 94
AEP-I&M | 2020 | 599151 | TRANSMISSION STATION | U | NONE | 3 | 3403 | 432181 | 0.72132 | 0.0056797 | 127
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TOR | TRANSFORMER, GROUNDING | 1 | 24 | 5592 | 0.0093332 | 4.0057e-05 | 233
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 4 | 668 | 0.0011149 | 6.6761e-06 | 167
AEP-I&M | 2024 | 614045 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 47 | 7.6542e-05 | 1.6285e-06 | 47
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | FUSE | 2 | 3 | 306 | 0.00051072 | 5.0071e-06 | 102
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | AF | NONE | 2 | 1387 | 264917 | 0.43889 | 0.0022978 | 191
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | FUSE | 372 | 5122 | 559256 | 0.93341 | 0.0085488 | 109.187
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 7 | 1053 | 149884 | 0.25016 | 0.0017575 | 142.34
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 13 | 26 | 3755 | 0.0062209 | 4.3074e-05 | 144.4231
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VIN | FUSE | 32 | 356 | 54275 | 0.089918 | 0.00058979 | 152.4579
AEP-I&M | 2022 | 606813 | TRANSMISSION STATION | SCO | NONE | 1 | 1406 | 8436 | 0.013902 | 0.002317 | 6
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 4 | 1450 | 0.0023895 | 6.5918e-06 | 362.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 12 | 1773 | 0.0029218 | 1.9775e-05 | 147.75
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | CUTOUT | 2 | 3 | 287 | 0.00047296 | 4.9439e-06 | 95.6667
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | FUSE | 1 | 1 | 91 | 0.00014996 | 1.648e-06 | 91
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | FUSE | 10 | 970 | 82671 | 0.13798 | 0.001619 | 85.2278
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 80 | 10710 | 0.017743 | 0.00013254 | 133.875
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | NONE | 855 | 34825 | 3554585 | 5.8277 | 0.057095 | 102.0699
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERF | NONE | 37 | 1071 | 43717 | 0.071673 | 0.0017559 | 40.8189
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 19 | 696 | 0.0011616 | 3.1712e-05 | 36.6316
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | CROSSARM | 6 | 557 | 54363 | 0.090733 | 0.00092965 | 97.5996
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1 | 310 | 0.00051087 | 1.648e-06 | 310
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | REGULATOR | 2 | 317 | 7504 | 0.012366 | 0.0005224 | 23.6719
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 7 | 214 | 6177 | 0.01031 | 0.00035717 | 28.8645
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | POLE | 67 | 5043 | 1141790 | 1.9057 | 0.0084169 | 226.4109
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CE | NONE | 15 | 51 | 17164 | 0.028647 | 8.512e-05 | 336.549
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | FUSE | 489 | 3276 | 287824 | 0.46873 | 0.0053351 | 87.8584
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 11 | 3438 | 0.0056657 | 1.8127e-05 | 312.5455
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 15 | 4490 | 0.0074939 | 2.5035e-05 | 299.3333
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 8 | 413 | 54202 | 0.08827 | 0.00067259 | 131.2397
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | ERF | NONE | 11 | 12139 | 1008963 | 1.6542 | 0.019902 | 83.1175
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 1018 | 82641 | 0.13691 | 0.0016865 | 81.1798
AEP-I&M | 2023 | 609949 | PARTIAL POWER | VIN | NONE | 2 | 2 | 252 | 0.00041315 | 3.279e-06 | 126
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | NONE | 66 | 2482 | 741276 | 1.2072 | 0.004042 | 298.6608
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | AO | ARRESTER | 3 | 2093 | 261092 | 0.42806 | 0.0034314 | 124.7453
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 10 | 2020 | 0.0032897 | 1.6285e-05 | 202
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WI | POLE | 2 | 376 | 357094 | 0.58545 | 0.00061644 | 949.7181
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | METERING | 1 | 2 | 168 | 0.0002804 | 3.3381e-06 | 84
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | POLE | 5 | 158 | 29945 | 0.049094 | 0.00025904 | 189.5253
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 15 | 4410 | 0.0072301 | 2.4592e-05 | 294
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | FUSE | 17 | 81 | 19478 | 0.031721 | 0.00013191 | 240.4691
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | SPLICE, UG | 4 | 4 | 521 | 0.00084847 | 6.5142e-06 | 130.25
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 8 | 91 | 46105 | 0.075084 | 0.0001482 | 506.6484
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 3 | 482 | 37203 | 0.060587 | 0.00078496 | 77.1846
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | V | SPLICE, OH | 1 | 1 | 248 | 0.00040388 | 1.6285e-06 | 248
AEP-I&M | 2023 | 609949 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 1 | 93 | 0.00015247 | 1.6395e-06 | 93
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | FUSE | 132 | 2323 | 271211 | 0.44168 | 0.0037831 | 116.7503
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | CUTOUT | 6 | 59 | 22123 | 0.036028 | 9.6084e-05 | 374.9661
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 2 | 552 | 35360 | 0.058272 | 0.00090967 | 64.058
AEP-I&M | 2023 | 609949 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 87 | 0.00014263 | 1.6395e-06 | 87
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERO | METERING | 2 | 3 | 76 | 0.00012524 | 4.9439e-06 | 25.3333
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 10 | 144 | 30400 | 0.04984 | 0.00023609 | 211.1111
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 5 | 155 | 0.00025242 | 8.1427e-06 | 31
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | METERING | 2 | 2 | 375 | 0.0006107 | 3.2571e-06 | 187.5
AEP-I&M | 2020 | 599151 | PARTIAL POWER | V | CONDUCTOR UG | 2 | 2 | 201 | 0.00033547 | 3.3381e-06 | 100.5
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | NONE | 39 | 1363 | 227707 | 0.37083 | 0.0022197 | 167.0631
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | CUTOUT | 2 | 116 | 3006 | 0.0048954 | 0.00018891 | 25.9138
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 1 | 68 | 0.00011266 | 1.6567e-06 | 68
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | F | CROSSARM | 1 | 82 | 4291 | 0.0069881 | 0.00013354 | 52.3293
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | BE | CONDUCTOR UG | 1 | 8 | 1392 | 0.0022669 | 1.3028e-05 | 174
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | AF | NONE | 1 | 1 | 125 | 0.00020863 | 1.669e-06 | 125
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CE | METERING | 1 | 1 | 150 | 0.00025035 | 1.669e-06 | 150
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERF | POLE | 1 | 288 | 52039 | 0.086213 | 0.00047713 | 180.691
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | O | FUSE | 2 | 301 | 56114 | 0.091384 | 0.00049019 | 186.4252
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | SWITCH, OH | 2 | 46 | 1939 | 0.0032362 | 7.6775e-05 | 42.1522
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | V | POLE | 2 | 31 | 1341 | 0.0021985 | 5.0824e-05 | 43.2581
AEP-I&M | 2023 | 609949 | DISTRIBUTION SOURCE | EQF | CUTOUT | 1 | 912 | 109440 | 0.17942 | 0.0014952 | 120
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 1 | 92 | 0.00015242 | 1.6567e-06 | 92
AEP-I&M | 2024 | 614045 | TRANSMISSION LINE | VA | POLE | 3 | 1962 | 58860 | 0.095856 | 0.0031952 | 30
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | INSULATOR | 2 | 2 | 220 | 0.00036447 | 3.3134e-06 | 110
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 3 | 1638 | 0.0026676 | 4.8856e-06 | 546
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | BREAKER | 1 | 1518 | 119922 | 0.19661 | 0.0024887 | 79
AEP-I&M | 2023 | 609949 | SUBTRANSMISSION LINE | EQF | INSULATOR | 6 | 2181 | 131914 | 0.21627 | 0.0035757 | 60.4833
AEP-I&M | 2020 | 599151 | PARTIAL POWER | FO | METERING | 1 | 1 | 632 | 0.0010548 | 1.669e-06 | 632
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 221 | 0.00036886 | 1.669e-06 | 221
AEP-I&M | 2024 | 614045 | TRANSMISSION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1709 | 121339 | 0.19761 | 0.0027832 | 71
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 13 | 468 | 0.00076216 | 2.1171e-05 | 36
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 155 | 15560 | 0.02534 | 0.00025242 | 100.3871
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 2 | 962 | 0.0015667 | 3.2571e-06 | 481
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | CONDUCTOR UG | 332 | 421 | 96261 | 0.15782 | 0.00069022 | 228.6485
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | MOAB | 1 | 1 | 46 | 7.5806e-05 | 1.648e-06 | 46
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | FUSE | 20 | 230 | 30381 | 0.050332 | 0.00038104 | 132.0913
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | METERING | 29 | 50 | 12060 | 0.019874 | 8.2398e-05 | 241.2
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TOR | TRANSFORMER, OH | 3 | 13 | 5360 | 0.008833 | 2.1423e-05 | 412.3077
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | POLE | 309 | 7574 | 847150 | 1.4139 | 0.012641 | 111.8497
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | CUTOUT | 89 | 972 | 42509 | 0.070949 | 0.0016223 | 43.7335
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 14 | 43 | 6650 | 0.011099 | 7.1768e-05 | 154.6512
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | ARRESTER | 3 | 3 | 243 | 0.00040557 | 5.0071e-06 | 81
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | JUMPER/RISER | 4 | 13 | 3970 | 0.0065771 | 2.1537e-05 | 305.3846
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | NETWORK PROTECTOR | 1 | 3 | 279 | 0.00045978 | 4.9439e-06 | 93
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | FUSE | 151 | 2573 | 253251 | 0.4152 | 0.0042184 | 98.4264
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FO | FUSE | 7 | 156 | 10639 | 0.017533 | 0.00025708 | 68.1987
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | CUTOUT | 4 | 14 | 24836 | 0.040929 | 2.3071e-05 | 1774
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | A | CUTOUT | 37 | 459 | 55236 | 0.09219 | 0.00076608 | 120.3399
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 2 | 2 | 133 | 0.00022198 | 3.3381e-06 | 66.5
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 35 | 452 | 194755 | 0.3193 | 0.00074105 | 430.8739
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | VA | NONE | 1 | 1110 | 6660 | 0.011116 | 0.0018526 | 6
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WW | NONE | 38 | 717 | 111057 | 0.18208 | 0.0011755 | 154.8912
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | CUTOUT | 6 | 153 | 57633 | 0.096191 | 0.00025536 | 376.6863
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ERO | NONE | 6 | 407 | 5773 | 0.0094647 | 0.00066727 | 14.1843
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WU | NONE | 1 | 1 | 64 | 0.00010603 | 1.6567e-06 | 64
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 877 | 133304 | 0.21968 | 0.0014453 | 152
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 2 | 7 | 3945 | 0.0065843 | 1.1683e-05 | 563.5714
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | CUTOUT | 3 | 49 | 14315 | 0.023469 | 8.0335e-05 | 292.1429
AEP-I&M | 2022 | 606813 | PARTIAL POWER | O | NONE | 4 | 4 | 430 | 0.00070862 | 6.5918e-06 | 107.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | CONN/CLAMP | 4 | 6 | 935 | 0.0015227 | 9.7713e-06 | 155.8333
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | FUSE | 11 | 347 | 39491 | 0.064745 | 0.0005689 | 113.8069
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | ARRESTER | 3 | 250 | 41006 | 0.06678 | 0.00040714 | 164.024
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | SPLICE, UG | 1 | 1 | 504 | 0.00082079 | 1.6285e-06 | 504
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | POLE | 3 | 22 | 4011 | 0.006576 | 3.6069e-05 | 182.3182
AEP-I&M | 2023 | 609949 | PARTIAL POWER | FW | OTHER EQUIPMENT | 1 | 1 | 87 | 0.00014263 | 1.6395e-06 | 87
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 5 | 26 | 1295 | 0.002109 | 4.2342e-05 | 49.8077
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | OL | FUSE | 1 | 470 | 32430 | 0.053168 | 0.00077056 | 69
AEP-I&M | 2024 | 614045 | PARTIAL POWER | U | NONE | 67 | 179 | 16292 | 0.026532 | 0.00029151 | 91.0168
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | SPLICE, OH | 6 | 87 | 16153 | 0.026306 | 0.00014168 | 185.6667
AEP-I&M | 2020 | 599151 | PARTIAL POWER | OL | FUSE | 1 | 2 | 204 | 0.00034048 | 3.3381e-06 | 102
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 15 | 570 | 0.00094432 | 2.4851e-05 | 38
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 20 | 2082 | 0.0034134 | 3.279e-05 | 104.1
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 73 | 7165 | 0.011747 | 0.00011968 | 98.1507
AEP-I&M | 2020 | 599151 | PARTIAL POWER | FO | NONE | 3 | 3 | 287 | 0.00047901 | 5.0071e-06 | 95.6667
AEP-I&M | 2023 | 609949 | TRANSMISSION STATION | EQF | BREAKER | 6 | 8106 | 199723 | 0.32744 | 0.01329 | 24.6389
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 46 | 7.5416e-05 | 1.6395e-06 | 46
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 6 | 2298 | 0.0037675 | 9.8369e-06 | 383
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 2 | 542 | 0.0008886 | 3.279e-06 | 271
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 96 | 376 | 80911 | 0.13177 | 0.00061233 | 215.1888
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 14 | 3990 | 0.0065415 | 2.2953e-05 | 285
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | A | CUTOUT | 4 | 35 | 1206 | 0.001964 | 5.6999e-05 | 34.4571
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | SPLICE, OH | 6 | 24 | 3115 | 0.0050729 | 3.9085e-05 | 129.7917
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | CIRCUIT SWITCHER | 2 | 24 | 31518 | 0.052604 | 4.0057e-05 | 1313.25
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 3 | 32 | 1964 | 0.003278 | 5.3409e-05 | 61.375
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 2 | 3 | 1238 | 0.0020663 | 5.0071e-06 | 412.6667
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | RELAY | 1 | 1 | 129 | 0.0002153 | 1.669e-06 | 129
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | METERING | 9 | 15 | 318 | 0.00051788 | 2.4428e-05 | 21.2
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | CROSSARM | 2 | 493 | 4106 | 0.0066868 | 0.00080287 | 8.3286
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 551 | 7714 | 0.012563 | 0.00089733 | 14
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 40 | 31916 | 0.051977 | 6.5142e-05 | 797.9
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 3 | 1092 | 0.0017784 | 4.8856e-06 | 364
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 124 | 121768 | 0.20323 | 0.00020696 | 982
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | POLE | 1 | 28 | 5096 | 0.0085054 | 4.6733e-05 | 182
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 3 | 54 | 9142 | 0.015258 | 9.0128e-05 | 169.2963
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | OL | FUSE | 2 | 2 | 197 | 0.00032082 | 3.2571e-06 | 98.5
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 465 | 365150 | 0.60175 | 0.0007663 | 785.2688
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 15 | 525 | 0.00085499 | 2.4428e-05 | 35
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 2082 | 135354 | 0.22043 | 0.0033906 | 65.0115
AEP-I&M | 2024 | 614045 | DISTRIBUTION STATION | AB | SWITCH, OH | 4 | 4757 | 501956 | 0.81746 | 0.007747 | 105.5194
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 15 | 2520 | 0.0041039 | 2.4428e-05 | 168
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 91 | 69797 | 0.11367 | 0.0001482 | 767
AEP-I&M | 2025 | 614045 | PARTIAL POWER | WW | TRANSFORMER, OH | 1 | 2 | 880 | 0.0014331 | 3.2571e-06 | 440
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 182 | 0.0002964 | 1.6285e-06 | 182
AEP-I&M | 2025 | 614045 | PARTIAL POWER | TOR | POLE | 1 | 1 | 91 | 0.0001482 | 1.6285e-06 | 91
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FO | RECLOSER, LINE/OCR/BR | 1 | 40 | 4520 | 0.007361 | 6.5142e-05 | 113
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 9 | 2643 | 234128 | 0.38788 | 0.0043787 | 88.5842
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | OU | NONE | 4 | 27 | 2749 | 0.0045543 | 4.4731e-05 | 101.8148
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 281 | 0.00046308 | 1.648e-06 | 281
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 100 | 3195 | 242817 | 0.40527 | 0.0053325 | 75.9991
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VA | NONE | 93 | 12541 | 1078135 | 1.7994 | 0.020931 | 85.9688
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 16 | 2117 | 320702 | 0.53131 | 0.0035072 | 151.4889
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 187 | 21824 | 0.036156 | 0.0003098 | 116.7059
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 1212 | 131184 | 0.21619 | 0.0019973 | 108.2376
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TIR | NONE | 5 | 6 | 1025 | 0.0016981 | 9.9402e-06 | 170.8333
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | EQF | INSULATOR | 8 | 9791 | 3323753 | 5.5065 | 0.016221 | 339.4702
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 65 | 73320 | 0.12083 | 0.00010712 | 1128
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 4 | 19 | 1047 | 0.0017254 | 3.1311e-05 | 55.1053
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 1 | 290 | 0.00048044 | 1.6567e-06 | 290
AEP-I&M | 2022 | 606813 | SUBTRANSMISSION LINE | VIN | NONE | 2 | 1615 | 346457 | 0.57095 | 0.0026614 | 214.5245
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OU | NONE | 4 | 492 | 46735 | 0.078002 | 0.00082116 | 94.9898
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 61 | 55435 | 0.091839 | 0.00010106 | 908.7705
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | UG | PEDESTAL | 2 | 11 | 921 | 0.00151 | 1.8034e-05 | 83.7273
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 6 | 60 | 5678 | 0.0093571 | 9.8877e-05 | 94.6333
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OL | NONE | 6 | 2067 | 424307 | 0.70818 | 0.0034499 | 205.2767
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 12 | 3360 | 0.0055087 | 1.9674e-05 | 280
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 5 | 20 | 1183 | 0.0019395 | 3.279e-05 | 59.15
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 20 | 1380 | 0.0023033 | 3.3381e-05 | 69
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 2 | 5 | 154 | 0.0002508 | 8.1427e-06 | 30.8
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | EQF | RELAY | 2 | 2 | 396 | 0.00064923 | 3.279e-06 | 198
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 4 | 15 | 1479 | 0.0024086 | 2.4428e-05 | 98.6
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | POLE | 6 | 864 | 262711 | 0.42784 | 0.0014071 | 304.0637
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WW | POLE | 13 | 711 | 131967 | 0.21491 | 0.0011579 | 185.6076
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | BE | NONE | 1 | 1 | 229 | 0.00037939 | 1.6567e-06 | 229
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | ERF | NONE | 8 | 8685 | 765323 | 1.2773 | 0.014496 | 88.1201
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 1043 | 23989 | 0.039743 | 0.0017279 | 23
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | JUMPER/RISER | 2 | 21 | 7206 | 0.012027 | 3.505e-05 | 343.1429
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 68 | 6811 | 0.011368 | 0.00011349 | 100.1618
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1363 | 241251 | 0.40265 | 0.0022749 | 177
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | POLE | 3 | 190 | 16395 | 0.027364 | 0.00031712 | 86.2895
AEP-I&M | 2021 | 603608 | PARTIAL POWER | VA | CUTOUT | 1 | 1 | 276 | 0.00045725 | 1.6567e-06 | 276
AEP-I&M | 2024 | 614045 | PARTIAL POWER | ERF | NONE | 5 | 5 | 481 | 0.00078333 | 8.1427e-06 | 96.2
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TIR | NONE | 1 | 1 | 35 | 5.6999e-05 | 1.6285e-06 | 35
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | REGULATOR | 3 | 1312 | 43550 | 0.070923 | 0.0021367 | 33.1936
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 14 | 1890 | 0.0031545 | 2.3366e-05 | 135
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 1 | 634 | 0.0010582 | 1.669e-06 | 634
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 51 | 8.3056e-05 | 1.6285e-06 | 51
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | SCO | BREAKER | 1 | 838 | 17598 | 0.029001 | 0.001381 | 21
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 1 | 62 | 0.00010348 | 1.669e-06 | 62
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 965 | 161155 | 0.26699 | 0.0015987 | 167
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WL | CUTOUT | 4 | 46 | 10215 | 0.016636 | 7.4913e-05 | 222.0652
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TR | POLE | 1 | 10 | 1535 | 0.0025166 | 1.6395e-05 | 153.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION STATION | ABI | FUSE | 1 | 552 | 71832 | 0.11698 | 0.00089896 | 130.1304
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 19 | 1520 | 0.0024754 | 3.0942e-05 | 80
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | FUSE | 1 | 1 | 74 | 0.00012051 | 1.6285e-06 | 74
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1146 | 28413 | 7398902 | 12.1931 | 0.046823 | 260.4055
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 319 | 2837 | 561854 | 0.92591 | 0.0046752 | 198.0451
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | POLE | 66 | 1705 | 897923 | 1.4797 | 0.0028098 | 526.6411
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 16 | 279 | 44331 | 0.073055 | 0.00045978 | 158.8925
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 5 | 266 | 9909 | 0.01633 | 0.00043836 | 37.2519
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WW | FUSE | 11 | 167 | 132720 | 0.21988 | 0.00027667 | 794.7305
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WL | FUSE | 3 | 9 | 3227 | 0.0053462 | 1.491e-05 | 358.5556
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | ARRESTER | 20 | 69 | 22829 | 0.037821 | 0.00011431 | 330.8551
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | METERING | 4 | 5 | 856 | 0.0014181 | 8.2835e-06 | 171.2
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | OL | FUSE | 2 | 77 | 5274 | 0.0087375 | 0.00012757 | 68.4935
AEP-I&M | 2022 | 606813 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 4 | 204 | 0.00033618 | 6.5918e-06 | 51
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | REGULATOR | 1 | 295 | 25871 | 0.042634 | 0.00048615 | 87.6983
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 3 | 51 | 4174 | 0.0068786 | 8.4046e-05 | 81.8431
AEP-I&M | 2022 | 606813 | PARTIAL POWER | UB | CONDUCTOR UG | 3 | 3 | 598 | 0.00098548 | 4.9439e-06 | 199.3333
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | F | SWITCH, OH | 1 | 353 | 23298 | 0.038598 | 0.00058482 | 66
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | O | FUSE | 3 | 3 | 1960 | 0.0032471 | 4.9701e-06 | 653.3333
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | ARRESTER | 4 | 57 | 9711 | 0.016088 | 9.4432e-05 | 170.3684
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | PEDESTAL | 2 | 871 | 851566 | 1.4033 | 0.0014354 | 977.6877
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | SWITCH, OH | 3 | 482 | 94467 | 0.15767 | 0.00080447 | 195.9896
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | F | POLE | 9 | 825 | 150217 | 0.24628 | 0.0013526 | 182.0812
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UB | FUSE | 1 | 21 | 1722 | 0.0028741 | 3.505e-05 | 82
AEP-I&M | 2020 | 599151 | PARTIAL POWER | ABI | NONE | 21 | 54 | 4581 | 0.0076458 | 9.0128e-05 | 84.8333
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | CROSSARM | 42 | 11613 | 1365813 | 2.2392 | 0.019039 | 117.6107
AEP-I&M | 2023 | 609949 | PARTIAL POWER | WU | NONE | 7 | 17 | 3812 | 0.0062497 | 2.7871e-05 | 224.2353
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | U | NONE | 1045 | 53616 | 3415622 | 5.5625 | 0.087316 | 63.7053
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WI | NONE | 7 | 399 | 241566 | 0.4002 | 0.00066103 | 605.4286
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | SWITCH, OH | 10 | 6191 | 765717 | 1.2554 | 0.01015 | 123.6823
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 12 | 500 | 144977 | 0.24197 | 0.00083451 | 289.954
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 1 | 154 | 0.00025248 | 1.6395e-06 | 154
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | FUSE | 63 | 1184 | 177098 | 0.29035 | 0.0019411 | 149.576
AEP-I&M | 2020 | 599151 | PARTIAL POWER | EQF | TRANSFORMER, OH | 24 | 117 | 48930 | 0.081666 | 0.00019528 | 418.2051
AEP-I&M | 2020 | 599151 | PARTIAL POWER | O | NONE | 4 | 5 | 816 | 0.0013619 | 8.3451e-06 | 163.2
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 1 | 4 | 236 | 0.00039389 | 6.6761e-06 | 59
AEP-I&M | 2021 | 603608 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 1 | 188 | 0.00031146 | 1.6567e-06 | 188
AEP-I&M | 2024 | 614045 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 108 | 181 | 26340 | 0.042896 | 0.00029477 | 145.5249
AEP-I&M | 2022 | 606813 | PARTIAL POWER | ABI | FUSE | 3 | 3 | 514 | 0.00084705 | 4.9439e-06 | 171.3333
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | ARRESTER | 5 | 22 | 2401 | 0.0039364 | 3.6069e-05 | 109.1364
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 1823 | 285087 | 0.46739 | 0.0029888 | 156.3834
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | POLE | 11 | 824 | 461241 | 0.7601 | 0.0013579 | 559.7585
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WL | FUSE | 65 | 502 | 117512 | 0.19365 | 0.00082727 | 234.0876
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | FUSE | 67 | 1686 | 352837 | 0.58146 | 0.0027785 | 209.2746
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WU | NONE | 5 | 23 | 4240 | 0.0069873 | 3.7903e-05 | 184.3478
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | POLE | 28 | 2962 | 1595172 | 2.6288 | 0.0048812 | 538.5456
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ABI | FUSE | 138 | 821 | 95543 | 0.15745 | 0.001353 | 116.3739
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | ARRESTER | 22 | 127 | 3364 | 0.0055437 | 0.00020929 | 26.4882
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 43 | 948 | 163784 | 0.26991 | 0.0015623 | 172.7679
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 14 | 1233 | 265519 | 0.43989 | 0.0020427 | 215.3439
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | CUTOUT | 3 | 87 | 41978 | 0.069178 | 0.00014337 | 482.5057
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 135 | 325 | 46423 | 0.076503 | 0.00053559 | 142.84
AEP-I&M | 2021 | 603608 | PARTIAL POWER | A | NONE | 69 | 383 | 35006 | 0.057995 | 0.00063452 | 91.3995
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 364 | 15141 | 2324087 | 3.8503 | 0.025084 | 153.4963
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 243 | 17212 | 4188032 | 6.9017 | 0.028365 | 243.3205
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 18 | 2694 | 0.0044396 | 2.9663e-05 | 149.6667
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 172 | 222 | 72485 | 0.12098 | 0.00037052 | 326.509
AEP-I&M | 2022 | 606813 | PARTIAL POWER | CO | CONN/CLAMP | 53 | 97 | 10477 | 0.017266 | 0.00015985 | 108.0103
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | FUSE | 18 | 37 | 4283 | 0.0070957 | 6.1298e-05 | 115.7568
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | EQF | REGULATOR | 5 | 3690 | 260176 | 0.42876 | 0.006081 | 70.5084
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 3 | 43 | 20102 | 0.033127 | 7.0862e-05 | 467.4884
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | ABI | NONE | 219 | 2364 | 292156 | 0.48402 | 0.0039164 | 123.5854
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 311 | 1893 | 218608 | 0.36026 | 0.0031196 | 115.4823
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | EQF | CUTOUT | 767 | 29541 | 3921322 | 6.4965 | 0.048941 | 132.7417
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | TRANSFORMER, OH | 23 | 75 | 20152 | 0.033386 | 0.00012425 | 268.6933
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FO | NONE | 19 | 313 | 28961 | 0.048337 | 0.00052241 | 92.5272
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CO | CONN/CLAMP | 38 | 44 | 5703 | 0.0095185 | 7.3437e-05 | 129.6136
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | CO | CONN/CLAMP | 26 | 290 | 10897 | 0.018053 | 0.00048044 | 37.5759
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 305 | 20081 | 0.033516 | 0.00050905 | 65.8393
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 3 | 37 | 22508 | 0.037566 | 6.1754e-05 | 608.3243
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | FUSE | 242 | 2457 | 384956 | 0.6425 | 0.0041008 | 156.6772
AEP-I&M | 2022 | 606813 | PARTIAL POWER | WW | NONE | 6 | 18 | 3246 | 0.0053493 | 2.9663e-05 | 180.3333
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 274 | 7036 | 1888473 | 3.1519 | 0.011743 | 268.4015
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FW | FUSE | 7 | 303 | 13218 | 0.021783 | 0.00049933 | 43.6238
AEP-I&M | 2022 | 606813 | PARTIAL POWER | UG | NONE | 6 | 17 | 1706 | 0.0028114 | 2.8015e-05 | 100.3529
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | FW | CUTOUT | 64 | 957 | 21610 | 0.035801 | 0.0015855 | 22.581
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 696 | 62606 | 0.10317 | 0.001147 | 89.9511
AEP-I&M | 2022 | 606813 | PARTIAL POWER | TOR | FUSE | 3 | 3 | 1553 | 0.0025593 | 4.9439e-06 | 517.6667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | NONE | 287 | 5538 | 1213213 | 2.0099 | 0.0091748 | 219.0706
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 573 | 6876 | 0.011391 | 0.00094929 | 12
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 936 | 0.0015425 | 1.648e-06 | 936
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | SO | NONE | 1 | 14 | 1050 | 0.0017395 | 2.3194e-05 | 75
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 2 | 226 | 0.00037244 | 3.2959e-06 | 113
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | PEDESTAL | 103 | 431 | 28954 | 0.04747 | 0.00070662 | 67.1787
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 7 | 49 | 2851 | 0.0046983 | 8.075e-05 | 58.1837
AEP-I&M | 2022 | 606813 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 1 | 104 | 0.00017139 | 1.648e-06 | 104
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | ABI | NONE | 218 | 1573 | 144507 | 0.23692 | 0.0025789 | 91.8671
AEP-I&M | 2022 | 606813 | TRANSMISSION LINE | SCO | NONE | 3 | 3457 | 636318 | 1.0486 | 0.005697 | 184.0665
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | NONE | 19 | 819 | 374428 | 0.62493 | 0.0013669 | 457.177
AEP-I&M | 2022 | 606813 | DISTRIBUTION STATION | ABI | NONE | 3 | 3389 | 406291 | 0.66955 | 0.0055849 | 119.8852
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | TIR | POLE | 10 | 399 | 260359 | 0.43455 | 0.00066594 | 652.5288
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 60 | 13593 | 0.022285 | 9.8369e-05 | 226.55
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | SPLICE, OH | 7 | 7 | 747 | 0.0012247 | 1.1476e-05 | 106.7143
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 1 | 1 | 40 | 6.5918e-05 | 1.648e-06 | 40
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 10 | 1920 | 0.0031268 | 1.6285e-05 | 192
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | VA | POLE | 88 | 17605 | 2043233 | 3.3275 | 0.028671 | 116.0598
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | V | NONE | 9 | 10 | 795 | 0.0012947 | 1.6285e-05 | 79.5
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | SCO | METERING | 11 | 21 | 6184 | 0.010071 | 3.4199e-05 | 294.4762
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | TOR | NETWORK TRANSFORMER | 1 | 13 | 611 | 0.0010069 | 2.1423e-05 | 47
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 1 | 108 | 0.00017706 | 1.6395e-06 | 108
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TOR | SPLICE, OH | 3 | 3 | 1016 | 0.0016957 | 5.0071e-06 | 338.6667
AEP-I&M | 2020 | 599151 | SUBTRANSMISSION LINE | EQF | STATIC WIRE | 7 | 4853 | 1394619 | 2.3277 | 0.0080998 | 287.3726
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | SCO | NONE | 3 | 2388 | 441003 | 0.73605 | 0.0039856 | 184.6746
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | REGULATOR | 2 | 460 | 11740 | 0.019248 | 0.00075416 | 25.5217
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | VA | CROSSARM | 11 | 4456 | 657433 | 1.0707 | 0.0072568 | 147.5388
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | FUSE | 78 | 1237 | 202313 | 0.32948 | 0.0020145 | 163.5513
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 27 | 325 | 24064 | 0.040163 | 0.00054243 | 74.0431
AEP-I&M | 2020 | 599151 | PARTIAL POWER | TOR | NONE | 23 | 64 | 14491 | 0.024186 | 0.00010682 | 226.4219
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | O | NONE | 32 | 610 | 56751 | 0.093042 | 0.0010001 | 93.0344
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | METERING | 9 | 9 | 867 | 0.0014214 | 1.4755e-05 | 96.3333
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | FUSE | 15 | 412 | 44607 | 0.07445 | 0.00068764 | 108.2694
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TOR | FUSE | 1 | 1 | 245 | 0.00040589 | 1.6567e-06 | 245
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | FUSE | 19 | 197 | 21410 | 0.035734 | 0.0003288 | 108.6802
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | UG | METERING | 1 | 1 | 83 | 0.00013853 | 1.669e-06 | 83
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TOR | NONE | 25 | 27 | 5447 | 0.0088707 | 4.3971e-05 | 201.7407
AEP-I&M | 2024 | 614045 | PARTIAL POWER | A | NONE | 71 | 268 | 24673 | 0.040181 | 0.00043645 | 92.0634
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 1 | 871 | 36582 | 0.060606 | 0.001443 | 42
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 1 | 113 | 0.00018721 | 1.6567e-06 | 113
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERF | METERING | 6 | 6 | 400 | 0.00065142 | 9.7713e-06 | 66.6667
AEP-I&M | 2022 | 606813 | SUBTRANSMISSION LINE | ERF | NONE | 1 | 255 | 22695 | 0.0374 | 0.00042023 | 89
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 5 | 1345 | 0.0022165 | 8.2398e-06 | 269
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 2 | 55 | 22635 | 0.037778 | 9.1797e-05 | 411.5455
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | PEDESTAL | 3 | 26 | 1272 | 0.002123 | 4.3395e-05 | 48.9231
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | OU | NONE | 1 | 5 | 615 | 0.0010083 | 8.1974e-06 | 123
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 35 | 1820 | 0.0030376 | 5.8416e-05 | 52
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 21 | 16212 | 0.026579 | 3.4429e-05 | 772
AEP-I&M | 2021 | 603608 | SUBTRANSMISSION LINE | EQF | CROSSARM | 2 | 1450 | 133474 | 0.22113 | 0.0024022 | 92.051
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | F | CUTOUT | 1 | 53 | 2515 | 0.0041666 | 8.7805e-05 | 47.4528
AEP-I&M | 2024 | 614045 | PARTIAL POWER | ABI | NONE | 12 | 12 | 1114 | 0.0018142 | 1.9543e-05 | 92.8333
AEP-I&M | 2025 | 614045 | TRANSMISSION STATION | U | TRANSFORMER, STATION SERVICE | 1 | 436 | 71504 | 0.11645 | 0.00071005 | 164
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 9 | 142 | 143579 | 0.23382 | 0.00023125 | 1011.1197
AEP-I&M | 2020 | 599151 | PARTIAL POWER | CO | NONE | 2 | 2 | 243 | 0.00040557 | 3.3381e-06 | 121.5
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 1 | 96 | 0.00015904 | 1.6567e-06 | 96
AEP-I&M | 2021 | 603608 | TRANSMISSION STATION | EQF | POLE | 2 | 2 | 1707 | 0.002828 | 3.3134e-06 | 853.5
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | UG | FUSE | 2 | 65 | 11661 | 0.01899 | 0.00010586 | 179.4
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | U | BREAKER | 1 | 207 | 31671 | 0.051578 | 0.00033711 | 153
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | BE | CONDUCTOR OVERHEAD | 1 | 1 | 51 | 8.3056e-05 | 1.6285e-06 | 51
AEP-I&M | 2021 | 603608 | PARTIAL POWER | TR | NONE | 1 | 1 | 84 | 0.00013916 | 1.6567e-06 | 84
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 5 | 1155 | 0.0019277 | 8.3451e-06 | 231
AEP-I&M | 2020 | 599151 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 200 | 0.00033381 | 1.669e-06 | 200
AEP-I&M | 2020 | 599151 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 2292 | 316428 | 0.52813 | 0.0038254 | 138.0576
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | INSULATOR | 2 | 2 | 157 | 0.0002601 | 3.3134e-06 | 78.5
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 172 | 0.00028495 | 1.6567e-06 | 172
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 58 | 9.509e-05 | 3.279e-06 | 29
AEP-I&M | 2025 | 614045 | DISTRIBUTION STATION | SCO | NONE | 1 | 62 | 434 | 0.00070679 | 0.00010097 | 7
AEP-I&M | 2024 | 614045 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 51 | 8.3056e-05 | 1.6285e-06 | 51
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | WW | REGULATOR | 1 | 175 | 57916 | 0.094319 | 0.000285 | 330.9486
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | A | FUSE | 479 | 7743 | 736331 | 1.2072 | 0.012695 | 95.0963
AEP-I&M | 2021 | 603608 | PARTIAL POWER | CO | CABLE TERMINATOR | 11 | 26 | 2939 | 0.0048691 | 4.3074e-05 | 113.0385
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | WL | NONE | 249 | 3435 | 736871 | 1.2299 | 0.0057331 | 214.5185
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | ARRESTER | 9 | 190 | 16199 | 0.026695 | 0.00031311 | 85.2579
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | NONE | 267 | 20495 | 6775779 | 11.2255 | 0.033954 | 330.6064
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WW | NONE | 17 | 1456 | 220622 | 0.36551 | 0.0024122 | 151.5261
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | FUSE | 18 | 812 | 111067 | 0.18303 | 0.0013381 | 136.782
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 2 | 2 | 403 | 0.00066413 | 3.2959e-06 | 201.5
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | A | CUTOUT | 22 | 662 | 91723 | 0.15196 | 0.0010967 | 138.5544
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 155 | 290 | 44654 | 0.073978 | 0.00048044 | 153.9793
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | CUTOUT | 54 | 159 | 28068 | 0.0465 | 0.00026342 | 176.5283
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 100 | 5466 | 488141 | 0.80871 | 0.0090555 | 89.305
AEP-I&M | 2022 | 606813 | PARTIAL POWER | UB | CONN/CLAMP | 2 | 11 | 1146 | 0.0018886 | 1.8127e-05 | 104.1818
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 2287 | 272158 | 0.4485 | 0.0037689 | 119.0022
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VIN | NONE | 107 | 916 | 129244 | 0.21299 | 0.0015095 | 141.0961
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | SCO | POLE | 390 | 4081 | 472396 | 0.77849 | 0.0067253 | 115.755
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | FO | METERING | 3 | 3 | 1316 | 0.0021687 | 4.9439e-06 | 438.6667
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 4 | 22 | 3388 | 0.0056129 | 3.6447e-05 | 154
AEP-I&M | 2021 | 603608 | PARTIAL POWER | EQF | METERING | 10 | 10 | 1513 | 0.0025066 | 1.6567e-05 | 151.3
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | SCO | REGULATOR | 4 | 758 | 5994 | 0.010004 | 0.0012651 | 7.9077
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | V | NONE | 10 | 18 | 2034 | 0.0033519 | 2.9663e-05 | 113
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 39 | 122 | 50407 | 0.083509 | 0.00020212 | 413.1721
AEP-I&M | 2023 | 609949 | PARTIAL POWER | EQF | CONN/CLAMP | 468 | 741 | 94017 | 0.15414 | 0.0012149 | 126.8785
AEP-I&M | 2022 | 606813 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 23 | 2352 | 0.003876 | 3.7903e-05 | 102.2609
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WW | POLE | 6 | 179 | 25577 | 0.042374 | 0.00029655 | 142.8883
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 359 | 4053 | 418351 | 0.68588 | 0.0066448 | 103.2201
AEP-I&M | 2021 | 603608 | DISTRIBUTION STATION | EQF | ARRESTER | 10 | 7217 | 1687703 | 2.796 | 0.011956 | 233.851
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | POLE | 1 | 1 | 49 | 8.075e-05 | 1.648e-06 | 49
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | UB | NONE | 4 | 54 | 4473 | 0.0073713 | 8.899e-05 | 82.8333
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TR | NONE | 23 | 703 | 103326 | 0.1694 | 0.0011526 | 146.9787
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | ERF | NONE | 19 | 2287 | 94663 | 0.158 | 0.0038171 | 41.3918
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | CUTOUT | 386 | 10531 | 1298807 | 2.1152 | 0.01715 | 123.3318
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 493 | 2042 | 210130 | 0.34221 | 0.0033255 | 102.904
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 345 | 4509 | 1174610 | 1.9129 | 0.0073431 | 260.5034
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | FW | NONE | 96 | 6335 | 1052046 | 1.7133 | 0.010317 | 166.0688
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 110 | 787 | 59714 | 0.097247 | 0.0012817 | 75.8755
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 13 | 163 | 79453 | 0.13026 | 0.00026724 | 487.4417
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 2 | 50 | 8.1974e-05 | 3.279e-06 | 25
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 8 | 195 | 34009 | 0.055757 | 0.0003197 | 174.4051
AEP-I&M | 2021 | 603608 | TRANSMISSION LINE | SCO | NONE | 9 | 8098 | 824816 | 1.3665 | 0.013416 | 101.8543
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | SCO | SWITCH, OH | 3 | 1104 | 7148 | 0.011719 | 0.00181 | 6.4746
AEP-I&M | 2023 | 609949 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 101 | 0.00016559 | 1.6395e-06 | 101
AEP-I&M | 2020 | 599151 | PARTIAL POWER | ERF | NONE | 1 | 4 | 4388 | 0.0073237 | 6.6761e-06 | 1097
AEP-I&M | 2023 | 609949 | DISTRIBUTION STATION | ABI | SWITCH, OH | 1 | 1740 | 432375 | 0.70887 | 0.0028527 | 248.4914
AEP-I&M | 2021 | 603608 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 466 | 0.00077202 | 1.6567e-06 | 466
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | FO | FUSE | 2 | 206 | 32536 | 0.053342 | 0.00033773 | 157.9417
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 10 | 1417 | 0.002365 | 1.669e-05 | 141.7
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TR | POLE | 2 | 17 | 8690 | 0.014152 | 2.7685e-05 | 511.1765
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 1 | 28 | 4.6733e-05 | 1.669e-06 | 28
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 4 | 6 | 450 | 0.00073285 | 9.7713e-06 | 75
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ERO | NONE | 20 | 2100 | 30602 | 0.049837 | 0.0034199 | 14.5724
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | WU | FUSE | 11 | 387 | 43866 | 0.071438 | 0.00063025 | 113.3488
AEP-I&M | 2025 | 614045 | PARTIAL POWER | EQF | CUTOUT | 6 | 9 | 805 | 0.001311 | 1.4657e-05 | 89.4444
AEP-I&M | 2025 | 614045 | DISTRIBUTION LINE | ERF | NONE | 7 | 1070 | 24890 | 0.040534 | 0.0017425 | 23.2617
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 5 | 404 | 0.00066931 | 8.2835e-06 | 80.8
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 115 | 14795 | 0.024693 | 0.00019194 | 128.6522
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | U | BREAKER | 2 | 549 | 118584 | 0.19542 | 0.00090473 | 216
AEP-I&M | 2025 | 614045 | TRANSMISSION LINE | EQF | SWITCH, OH | 1 | 646 | 104006 | 0.16938 | 0.001052 | 161
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 61 | 1159 | 0.0018875 | 9.9341e-05 | 19
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | ABI | CUTOUT | 3 | 6 | 805 | 0.001311 | 9.7713e-06 | 134.1667
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | AF | CUTOUT | 1 | 98 | 17729 | 0.029217 | 0.0001615 | 180.9082
AEP-I&M | 2020 | 599151 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 27 | 18441 | 0.030779 | 4.5064e-05 | 683
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WI | FUSE | 1 | 5 | 3350 | 0.0054923 | 8.1974e-06 | 670
AEP-I&M | 2024 | 614045 | DISTRIBUTION LINE | TOR | INSULATOR | 3 | 163 | 63797 | 0.1039 | 0.00026545 | 391.3926
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 30 | 1768 | 0.0028986 | 4.9184e-05 | 58.9333
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 2 | 280 | 0.00046143 | 3.2959e-06 | 140
AEP-I&M | 2024 | 614045 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 72 | 0.00011726 | 1.6285e-06 | 72
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 1 | 270 | 0.00044495 | 1.648e-06 | 270
AEP-I&M | 2021 | 603608 | PARTIAL POWER | U | NONE | 60 | 161 | 14865 | 0.024627 | 0.00026673 | 92.3292
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 299 | 6424 | 1520756 | 2.5061 | 0.010586 | 236.7304
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | VA | POLE HARDWARE | 3 | 52 | 10918 | 0.017992 | 8.5694e-05 | 209.9615
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | A | CUTOUT | 33 | 381 | 45902 | 0.075644 | 0.00062787 | 120.4777
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | WU | NONE | 220 | 7765 | 1534925 | 2.5295 | 0.012796 | 197.6722
AEP-I&M | 2022 | 606813 | PARTIAL POWER | EQF | ARRESTER | 5 | 5 | 859 | 0.0014156 | 8.2398e-06 | 171.8
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | ERF | METERING | 7 | 7 | 1013 | 0.0016694 | 1.1536e-05 | 144.7143
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WH | NONE | 1 | 1 | 1803 | 0.002987 | 1.6567e-06 | 1803
AEP-I&M | 2023 | 609949 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 100 | 145 | 24943 | 0.040894 | 0.00023772 | 172.0207
AEP-I&M | 2022 | 606813 | DISTRIBUTION LINE | CE | NONE | 6 | 10 | 904 | 0.0014898 | 1.648e-05 | 90.4
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | OL | NONE | 3 | 285 | 17189 | 0.028477 | 0.00047216 | 60.3123
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | EQF | CIRCUIT SWITCHER | 2 | 62 | 40242 | 0.067165 | 0.00010348 | 649.0645
AEP-I&M | 2021 | 603608 | PARTIAL POWER | ERF | METERING | 4 | 4 | 776 | 0.0012856 | 6.6268e-06 | 194
AEP-I&M | 2020 | 599151 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 17 | 33 | 11137 | 0.018588 | 5.5078e-05 | 337.4848
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | TIR | POLE | 10 | 934 | 371617 | 0.61566 | 0.0015474 | 397.8769
AEP-I&M | 2021 | 603608 | DISTRIBUTION LINE | WL | CUTOUT | 8 | 101 | 17680 | 0.029291 | 0.00016733 | 175.0495
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | EQF | CUTOUT | 443 | 13259 | 1427464 | 2.3403 | 0.021738 | 107.66
AEP-I&M | 2023 | 609949 | DISTRIBUTION LINE | WL | FUSE | 58 | 867 | 120774 | 0.19801 | 0.0014214 | 139.301
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | FUSE | 1028 | 7378 | 947259 | 5.8618 | 0.045656 | 128.3897
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 11 | 881 | 97018 | 0.6002 | 0.0054503 | 110.1226
AEP-KYP | 2022 | 162018 | PARTIAL POWER | ERF | NONE | 1 | 3 | 3528 | 0.021775 | 1.8516e-05 | 1176
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | POLE | 161 | 18163 | 5968880 | 36.9364 | 0.1124 | 328.6285
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 4 | 30 | 13504 | 0.083543 | 0.0001856 | 450.1333
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WW | POLE | 9 | 382 | 152779 | 0.94542 | 0.0023639 | 399.945
AEP-KYP | 2024 | 161599 | PARTIAL POWER | U | NONE | 6 | 8 | 843 | 0.0052166 | 4.9505e-05 | 105.375
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 60 | 22260 | 0.13571 | 0.00036581 | 371
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 19 | 1436 | 197125 | 1.2198 | 0.0088862 | 137.2737
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERF | FUSE | 4 | 27 | 1520 | 0.009406 | 0.00016708 | 56.2963
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 3 | 2976 | 0.018144 | 1.829e-05 | 992
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 26 | 8660 | 0.052798 | 0.00015852 | 333.0769
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | CUTOUT | 4 | 8 | 800 | 0.0049505 | 4.9505e-05 | 100
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 95 | 10730 | 0.066399 | 0.00058787 | 112.9474
AEP-KYP | 2024 | 161599 | PARTIAL POWER | TOR | NONE | 2 | 18 | 9216 | 0.05703 | 0.00011139 | 512
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 2 | 7 | 705 | 0.0042982 | 4.2677e-05 | 100.7143
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WW | NONE | 17 | 251 | 140632 | 0.87025 | 0.0015532 | 560.2869
AEP-KYP | 2025 | 161599 | TRANSMISSION LINE | EQF | CONN/CLAMP | 2 | 1144 | 174440 | 1.0795 | 0.0070793 | 152.4825
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 8 | 138 | 0.00085374 | 4.9492e-05 | 17.25
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | O | ARRESTER | 1 | 1 | 1105 | 0.0067369 | 6.0968e-06 | 1105
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 60 | 9600 | 0.058529 | 0.00036581 | 160
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ERO | METERING | 2 | 2 | 169 | 0.0010304 | 1.2194e-05 | 84.5
AEP-KYP | 2020 | 165077 | TRANSMISSION STATION | EQF | MOAB | 2 | 113 | 1469 | 0.0088989 | 0.00068453 | 13
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 194 | 22189 | 0.13731 | 0.0012005 | 114.3763
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 5 | 1535 | 0.0094988 | 3.0941e-05 | 307
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | A | NONE | 3 | 7 | 852 | 0.0052723 | 4.3317e-05 | 121.7143
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 5 | 374 | 46543 | 0.28802 | 0.0023144 | 124.4465
AEP-KYP | 2024 | 161599 | PARTIAL POWER | VIN | FUSE | 3 | 9 | 1559 | 0.0096473 | 5.5693e-05 | 173.2222
AEP-KYP | 2025 | 161599 | PARTIAL POWER | U | NONE | 1 | 3 | 195 | 0.0012067 | 1.8564e-05 | 65
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 3 | 136 | 0.00084159 | 1.8564e-05 | 45.3333
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | ABX | NONE | 1 | 355 | 62835 | 0.38064 | 0.0021505 | 177
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | POLE | 2 | 46 | 15885 | 0.098273 | 0.00028458 | 345.3261
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | ARRESTER | 1 | 9 | 990 | 0.0061104 | 5.5549e-05 | 110
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | JUMPER/RISER | 1 | 9 | 387 | 0.0023942 | 5.5679e-05 | 43
AEP-KYP | 2022 | 162018 | DISTRIBUTION STATION | ABI | NONE | 2 | 1563 | 203705 | 1.2573 | 0.0096471 | 130.3295
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CE | CUTOUT | 1 | 2 | 50 | 0.00030941 | 1.2376e-05 | 25
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | NONE | 41 | 4444 | 525164 | 3.2498 | 0.0275 | 118.1737
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WL | FUSE | 9 | 49 | 7116 | 0.044035 | 0.00030322 | 145.2245
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | WU | NONE | 11 | 9322 | 849703 | 5.2567 | 0.057671 | 91.1503
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | CONN/CLAMP | 32 | 187 | 15756 | 0.097501 | 0.0011572 | 84.2567
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 79 | 32294 | 0.19932 | 0.0004876 | 408.7848
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 12 | 908 | 0.0056188 | 7.4258e-05 | 75.6667
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 2 | 314 | 0.0019144 | 1.2194e-05 | 157
AEP-KYP | 2021 | 164021 | PARTIAL POWER | WL | FUSE | 2 | 11 | 1160 | 0.0070723 | 6.7065e-05 | 105.4545
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 1 | 102 | 0.00062187 | 6.0968e-06 | 102
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | REGULATOR | 6 | 1165 | 102642 | 0.63516 | 0.0072092 | 88.1047
AEP-KYP | 2024 | 161599 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 1269 | 87561 | 0.54184 | 0.0078528 | 69
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 2 | 230 | 0.0014229 | 1.2373e-05 | 115
AEP-KYP | 2024 | 161599 | PARTIAL POWER | O | FUSE | 1 | 1 | 81 | 0.00050124 | 6.1882e-06 | 81
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | ARRESTER | 2 | 73 | 5431 | 0.0329 | 0.00044222 | 74.3973
AEP-KYP | 2020 | 165077 | PARTIAL POWER | WU | NONE | 1 | 2 | 202 | 0.0012237 | 1.2116e-05 | 101
AEP-KYP | 2024 | 161599 | PARTIAL POWER | ABI | NONE | 1 | 1 | 65 | 0.00040223 | 6.1882e-06 | 65
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERF | POLE | 1 | 4 | 1612 | 0.0099753 | 2.4753e-05 | 403
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 8 | 6614 | 0.040918 | 4.9492e-05 | 826.75
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | CONN/CLAMP | 4 | 38 | 1273 | 0.0077612 | 0.00023168 | 33.5
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | CUTOUT | 2 | 20 | 1488 | 0.009014 | 0.00012116 | 74.4
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 2245 | 641170 | 3.9091 | 0.013687 | 285.5991
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 1 | 69 | 0.00042068 | 6.0968e-06 | 69
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 1 | 1 | 112 | 0.00068284 | 6.0968e-06 | 112
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 56 | 5880 | 0.036292 | 0.00034564 | 105
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | FUSE | 1 | 2 | 48 | 0.00029265 | 1.2194e-05 | 24
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CF | CROSSARM | 1 | 2 | 3810 | 0.023516 | 1.2344e-05 | 1905
AEP-KYP | 2020 | 165077 | PARTIAL POWER | A | FUSE | 4 | 6 | 198 | 0.0011994 | 3.6347e-05 | 33
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 212 | 6328 | 447471 | 2.769 | 0.039159 | 70.7129
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | OL | FUSE | 5 | 49 | 6800 | 0.041458 | 0.00029874 | 138.7755
AEP-KYP | 2020 | 165077 | PARTIAL POWER | CO | METERING | 1 | 1 | 75 | 0.00045433 | 6.0578e-06 | 75
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 193 | 46804 | 0.28888 | 0.0011912 | 242.5078
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 1 | 3161 | 0.019561 | 6.1882e-06 | 3161
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | SCO | NONE | 3 | 721 | 15358 | 0.095012 | 0.0044605 | 21.301
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 1 | 25 | 0.0001543 | 6.1722e-06 | 25
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | A | POLE | 1 | 52 | 10504 | 0.065 | 0.00032178 | 202
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 12 | 23 | 508 | 0.0031436 | 0.00014233 | 22.087
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | ARRESTER | 2 | 24 | 246 | 0.0015219 | 0.00014848 | 10.25
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | F | NONE | 10 | 66 | 9223 | 0.057073 | 0.00040842 | 139.7424
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | POLE | 20 | 1163 | 287960 | 1.7819 | 0.0071968 | 247.601
AEP-KYP | 2024 | 161599 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 7 | 728 | 0.004505 | 4.3317e-05 | 104
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 5 | 17 | 12130 | 0.075062 | 0.0001052 | 713.5294
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WFS | POLE | 13 | 615 | 125150 | 0.75813 | 0.0037255 | 203.4959
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 236 | 2832 | 0.017525 | 0.0014604 | 12
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 229 | 39157 | 0.24225 | 0.0014167 | 170.9913
AEP-KYP | 2020 | 165077 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 109 | 0.0006603 | 6.0578e-06 | 109
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | F | CUTOUT | 1 | 48 | 12393 | 0.075074 | 0.00029077 | 258.1875
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | O | NONE | 3 | 822 | 13257 | 0.080825 | 0.0050116 | 16.1277
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 3 | 72 | 0.00044555 | 1.8564e-05 | 24
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WW | POLE | 3 | 450 | 135399 | 0.83787 | 0.0027847 | 300.8867
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | POLE | 1 | 151 | 12303 | 0.076133 | 0.00093441 | 81.4768
AEP-KYP | 2024 | 161599 | DISTRIBUTION STATION | SCO | INSULATOR | 1 | 232 | 1740 | 0.010767 | 0.0014357 | 7.5
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | FUSE | 2 | 2 | 139 | 0.00085793 | 1.2344e-05 | 69.5
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 2 | 24 | 1028 | 0.0062274 | 0.00014539 | 42.8333
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 14 | 5237 | 0.032324 | 8.641e-05 | 374.0714
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | WU | NONE | 1 | 905 | 83260 | 0.50437 | 0.0054823 | 92
AEP-KYP | 2023 | 161642 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 179 | 0.0011074 | 6.1865e-06 | 179
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | UB | TRANSFORMER, OH | 1 | 5 | 1708 | 0.010347 | 3.0289e-05 | 341.6
AEP-KYP | 2023 | 161642 | DISTRIBUTION STATION | SCO | MOAB | 1 | 760 | 136040 | 0.84161 | 0.0047017 | 179
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 2 | 6966 | 0.043107 | 1.2376e-05 | 3483
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WI | FUSE | 2 | 12 | 1533 | 0.0094864 | 7.4258e-05 | 127.75
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ERO | NONE | 6 | 6 | 303 | 0.0018473 | 3.6581e-05 | 50.5
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | POLE | 90 | 1920 | 309065 | 1.912 | 0.011878 | 160.9714
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 11 | 39 | 2616 | 0.015949 | 0.00023777 | 67.0769
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 4 | 284 | 0.0017529 | 2.4689e-05 | 71
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | WU | NONE | 6 | 3393 | 330691 | 2.0411 | 0.020942 | 97.4627
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | METERING | 1 | 3 | 126 | 0.00077769 | 1.8516e-05 | 42
AEP-KYP | 2022 | 162018 | PARTIAL POWER | A | FUSE | 4 | 8 | 560 | 0.0034564 | 4.9377e-05 | 70
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | CONN/CLAMP | 89 | 228 | 25635 | 0.15529 | 0.0013812 | 112.4342
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 2 | 21 | 3223 | 0.019893 | 0.00012962 | 153.4762
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | AB | CUTOUT | 2 | 1106 | 193340 | 1.1788 | 0.006743 | 174.8101
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 1 | 188 | 0.0011462 | 6.0968e-06 | 188
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 5 | 66 | 26738 | 0.16197 | 0.00039981 | 405.1212
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 2 | 124 | 0.000756 | 1.2194e-05 | 62
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ABI | FUSE | 59 | 673 | 144097 | 0.89146 | 0.0041635 | 214.1114
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | NONE | 738 | 12149 | 1522372 | 9.4207 | 0.07518 | 125.3084
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | CONDUCTOR UG | 11 | 36 | 14642 | 0.090607 | 0.00022277 | 406.7222
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | METERING | 1 | 8 | 96 | 0.00059391 | 4.9492e-05 | 12
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | EQF | REGULATOR | 1 | 930 | 191580 | 1.1605 | 0.0056337 | 206
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ERF | NONE | 7 | 435 | 39922 | 0.24698 | 0.0026911 | 91.7747
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | V | FUSE | 1 | 8 | 7264 | 0.044835 | 4.9377e-05 | 908
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TOR | NONE | 3 | 7 | 2336 | 0.014418 | 4.3205e-05 | 333.7143
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TR | FUSE | 10 | 204 | 21365 | 0.13217 | 0.001262 | 104.7304
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 3 | 219 | 0.0013267 | 1.8173e-05 | 73
AEP-KYP | 2021 | 164021 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 55 | 0.00033532 | 6.0968e-06 | 55
AEP-KYP | 2023 | 161642 | DISTRIBUTION STATION | EQF | REGULATOR | 1 | 110 | 67430 | 0.41716 | 0.00068052 | 613
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 122 | 9062 | 0.056062 | 0.00075475 | 74.2787
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WU | POLE | 2 | 45 | 38554 | 0.23506 | 0.00027436 | 856.7556
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 5 | 9 | 5587 | 0.034573 | 5.5693e-05 | 620.7778
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WI | FUSE | 9 | 51 | 81144 | 0.49155 | 0.00030895 | 1591.0588
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | CUTOUT | 8 | 50 | 11377 | 0.070403 | 0.00030941 | 227.54
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 5 | 78 | 9800 | 0.060628 | 0.00048255 | 125.641
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | CUTOUT | 38 | 260 | 11629 | 0.071962 | 0.0016089 | 44.7269
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 95 | 0.00058635 | 6.1722e-06 | 95
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | SWITCH, OH | 5 | 105 | 10087 | 0.061498 | 0.00064016 | 96.0667
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 1 | 20 | 11880 | 0.073325 | 0.00012344 | 594
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | CUTOUT | 5 | 103 | 47208 | 0.29213 | 0.00063738 | 458.3301
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | FUSE | 24 | 200 | 9324 | 0.057698 | 0.0012376 | 46.62
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 2 | 2 | 321 | 0.0019859 | 1.2373e-05 | 160.5
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | SWITCH, OH | 5 | 98 | 12239 | 0.075737 | 0.00060644 | 124.8878
AEP-KYP | 2025 | 161599 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 5 | 3255 | 0.020142 | 3.0941e-05 | 651
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CO | SPLICE, OH | 1 | 6 | 792 | 0.0048286 | 3.6581e-05 | 132
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WFS | FUSE | 1 | 4 | 792 | 0.0048883 | 2.4689e-05 | 198
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 6 | 18 | 5250 | 0.032488 | 0.00011139 | 291.6667
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 90 | 2958 | 0.018305 | 0.00055693 | 32.8667
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | POLE | 3 | 20 | 22425 | 0.13877 | 0.00012376 | 1121.25
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 5 | 430 | 0.0026602 | 3.0933e-05 | 86
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 3 | 1773 | 0.010972 | 1.8564e-05 | 591
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 9 | 6257 | 0.038619 | 5.5549e-05 | 695.2222
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | CUTOUT | 3 | 9 | 1894 | 0.01169 | 5.5549e-05 | 210.4444
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | WU | NONE | 1 | 414 | 31878 | 0.19727 | 0.0025619 | 77
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 2 | 116 | 0.0007027 | 1.2116e-05 | 58
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 2 | 900 | 0.005452 | 1.2116e-05 | 450
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 226 | 2098 | 253554 | 1.565 | 0.012949 | 120.8551
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 30 | 414 | 587942 | 3.6289 | 0.0025553 | 1420.1498
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VIN | FUSE | 234 | 865 | 147346 | 0.89834 | 0.0052737 | 170.3422
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 3 | 11 | 367 | 0.0022652 | 6.7894e-05 | 33.3636
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | CUTOUT | 467 | 1251 | 51577 | 0.31244 | 0.0075783 | 41.2286
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VIN | NONE | 42 | 612 | 55285 | 0.3349 | 0.0037074 | 90.335
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | INSULATOR | 4 | 1368 | 272028 | 1.6479 | 0.008287 | 198.8509
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 31 | 1116 | 50394 | 0.30528 | 0.0067605 | 45.1559
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 254 | 2657 | 372705 | 2.3057 | 0.016438 | 140.2729
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TR | NONE | 7 | 733 | 140949 | 0.85934 | 0.0044689 | 192.2906
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 11 | 31 | 2175 | 0.013176 | 0.00018779 | 70.1613
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | F | FUSE | 6 | 12 | 858 | 0.005231 | 7.3161e-05 | 71.5
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | ARRESTER | 7 | 495 | 70532 | 0.43002 | 0.0030179 | 142.4889
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 7 | 98 | 9174 | 0.055574 | 0.00059366 | 93.6122
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 13 | 4962 | 650816 | 4.0274 | 0.030706 | 131.16
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WW | FUSE | 6 | 31 | 48408 | 0.29324 | 0.00018779 | 1561.5484
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 2 | 1960 | 0.012126 | 1.2373e-05 | 980
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WT | NONE | 1 | 11 | 1034 | 0.0063986 | 6.807e-05 | 94
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | WI | NONE | 1 | 804 | 101304 | 0.61763 | 0.0049018 | 126
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 7 | 1302 | 0.007938 | 4.2677e-05 | 186
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 4 | 220 | 0.001361 | 2.4746e-05 | 55
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | FUSE | 1031 | 7064 | 874953 | 5.4003 | 0.0436 | 123.8608
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ERF | FUSE | 1 | 8 | 1280 | 0.0079004 | 4.9377e-05 | 160
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 6 | 247 | 59564 | 0.36315 | 0.0015059 | 241.1498
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | OU | NONE | 2 | 15 | 2178 | 0.013443 | 9.2582e-05 | 145.2
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 79 | 4009 | 609767 | 3.7176 | 0.024442 | 152.0995
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | POLE | 503 | 9902 | 1790318 | 10.8454 | 0.059984 | 180.8037
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | FUSE | 19 | 75 | 9926 | 0.06013 | 0.00045433 | 132.3467
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WW | FUSE | 11 | 99 | 23404 | 0.14445 | 0.00061104 | 236.404
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | CUTOUT | 65 | 220 | 5311 | 0.032173 | 0.0013327 | 24.1409
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | F | CONN/CLAMP | 1 | 3 | 393 | 0.002396 | 1.829e-05 | 131
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | INSULATOR | 1 | 430 | 38279 | 0.23189 | 0.0026048 | 89.0209
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 57 | 19775 | 0.12056 | 0.00034752 | 346.9298
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WL | POLE | 1 | 3 | 567 | 0.0035087 | 1.8564e-05 | 189
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 2 | 863 | 0.005339 | 1.2373e-05 | 431.5
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 2 | 9 | 606 | 0.003671 | 5.452e-05 | 67.3333
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | O | METERING | 2 | 3 | 486 | 0.0029441 | 1.8173e-05 | 162
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 216 | 0.0013366 | 6.1882e-06 | 216
AEP-KYP | 2025 | 161599 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 6 | 1734 | 0.01073 | 3.7129e-05 | 289
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 128 | 10254 | 0.063453 | 0.00079208 | 80.1094
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WU | TRANSFORMER, OH | 1 | 6 | 816 | 0.0050365 | 3.7033e-05 | 136
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | TOR | NONE | 3 | 2247 | 189944 | 1.1751 | 0.013901 | 84.5323
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 811 | 61636 | 0.38043 | 0.0050056 | 76
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 4 | 212 | 0.0013115 | 2.4746e-05 | 53
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | A | ARRESTER | 2 | 2 | 937 | 0.0057968 | 1.2373e-05 | 468.5
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 6 | 15 | 1564 | 0.0095354 | 9.1452e-05 | 104.2667
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | EQF | INSULATOR | 1 | 520 | 52520 | 0.31815 | 0.00315 | 101
AEP-KYP | 2022 | 162018 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 64 | 0.00039502 | 6.1722e-06 | 64
AEP-KYP | 2020 | 165077 | PARTIAL POWER | WL | FUSE | 1 | 4 | 588 | 0.003562 | 2.4231e-05 | 147
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 2 | 58 | 0.00035882 | 1.2373e-05 | 29
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WI | NONE | 14 | 3072 | 841005 | 5.1908 | 0.018961 | 273.7646
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 63 | 3327 | 712763 | 4.4107 | 0.020588 | 214.2359
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 6 | 13 | 350 | 0.0021659 | 8.0446e-05 | 26.9231
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | OU | NONE | 4 | 2811 | 357950 | 2.2151 | 0.017395 | 127.339
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | AF | POLE | 1 | 27 | 24246 | 0.14688 | 0.00016356 | 898
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WL | ARRESTER | 3 | 3 | 556 | 0.0034406 | 1.8564e-05 | 185.3333
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | F | NONE | 12 | 144 | 16229 | 0.10043 | 0.00089109 | 112.7014
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 2 | 183 | 17777 | 0.11001 | 0.0011324 | 97.1421
AEP-KYP | 2023 | 161642 | SUBTRANSMISSION LINE | SCO | NONE | 3 | 12 | 632 | 0.0039099 | 7.4238e-05 | 52.6667
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 123 | 0.00076114 | 6.1882e-06 | 123
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | CE | CUTOUT | 1 | 18 | 2712 | 0.016782 | 0.00011139 | 150.6667
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | SWITCH, OH | 1 | 936 | 59904 | 0.3707 | 0.0057921 | 64
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 44 | 28556 | 0.17625 | 0.00027157 | 649
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | CUTOUT | 2 | 420 | 102044 | 0.62983 | 0.0025923 | 242.9619
AEP-KYP | 2024 | 161599 | PARTIAL POWER | ERF | NONE | 1 | 1 | 121 | 0.00074877 | 6.1882e-06 | 121
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | OU | FUSE | 2 | 5 | 664 | 0.0041078 | 3.0933e-05 | 132.8
AEP-KYP | 2024 | 161599 | DISTRIBUTION STATION | SCO | NONE | 2 | 623 | 5242 | 0.032438 | 0.0038552 | 8.4141
AEP-KYP | 2024 | 161599 | TRANSMISSION STATION | U | NONE | 1 | 42 | 8904 | 0.055099 | 0.0002599 | 212
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 113 | 336 | 31774 | 0.19611 | 0.0020738 | 94.5655
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | FUSE | 1092 | 5748 | 694182 | 4.2323 | 0.035044 | 120.7693
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VIN | FUSE | 331 | 1455 | 234755 | 1.4489 | 0.0089805 | 161.3436
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | CROSSARM | 18 | 7627 | 1234563 | 7.6199 | 0.047075 | 161.8674
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | SPLICE, OH | 23 | 844 | 1090382 | 6.73 | 0.0052093 | 1291.9218
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 4 | 76 | 4447 | 0.027448 | 0.00046908 | 58.5132
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 4 | 20 | 3029 | 0.018467 | 0.00012194 | 151.45
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 33 | 3300 | 0.020368 | 0.00020368 | 100
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | CUTOUT | 9 | 209 | 27171 | 0.16566 | 0.0012742 | 130.0048
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CE | NONE | 1 | 1 | 533 | 0.0032496 | 6.0968e-06 | 533
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TOR | NONE | 6 | 30 | 17939 | 0.10937 | 0.0001829 | 597.9667
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | INSULATOR | 7 | 72 | 8027 | 0.048626 | 0.00043616 | 111.4861
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | POLE | 90 | 950 | 91839 | 0.55634 | 0.0057549 | 96.6726
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 16 | 64 | 6493 | 0.039586 | 0.00039019 | 101.4531
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | METERING | 2 | 3 | 128 | 0.00078039 | 1.829e-05 | 42.6667
AEP-KYP | 2022 | 162018 | DISTRIBUTION STATION | EQF | BREAKER | 3 | 3195 | 1071661 | 6.6145 | 0.01972 | 335.4182
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 4 | 130 | 26469 | 0.16337 | 0.00080238 | 203.6077
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | CE | NONE | 1 | 785 | 143655 | 0.87583 | 0.004786 | 183
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | FUSE | 11 | 103 | 10369 | 0.063999 | 0.00063573 | 100.6699
AEP-KYP | 2021 | 164021 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 57 | 0.00034752 | 6.0968e-06 | 57
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | F | METERING | 1 | 10 | 1140 | 0.0069059 | 6.0578e-05 | 114
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 137 | 1635 | 236804 | 1.465 | 0.010115 | 144.8343
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | F | SWITCH, OH | 1 | 1237 | 139216 | 0.86126 | 0.0076527 | 112.5432
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WL | FUSE | 46 | 326 | 49887 | 0.30863 | 0.0020168 | 153.0276
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | ARRESTER | 40 | 2021 | 376317 | 2.3281 | 0.012503 | 186.2034
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | CUTOUT | 8 | 20 | 6959 | 0.042952 | 0.00012344 | 347.95
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ABI | FUSE | 73 | 200 | 22197 | 0.13736 | 0.0012376 | 110.985
AEP-KYP | 2020 | 165077 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 2 | 2 | 438 | 0.0026533 | 1.2116e-05 | 219
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | F | NONE | 10 | 74 | 14426 | 0.087952 | 0.00045116 | 194.9459
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CE | FUSE | 7 | 84 | 13303 | 0.082321 | 0.00051981 | 158.369
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TIR | NONE | 45 | 3020 | 412022 | 2.5497 | 0.018688 | 136.4311
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | CUTOUT | 11 | 222 | 48318 | 0.29892 | 0.0013734 | 217.6486
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WFS | POLE | 7 | 1393 | 182417 | 1.1288 | 0.0086201 | 130.9526
AEP-KYP | 2024 | 161599 | PARTIAL POWER | VA | SPLICE, OH | 1 | 1 | 199 | 0.0012314 | 6.1882e-06 | 199
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | CUTOUT | 124 | 354 | 7687 | 0.047568 | 0.0021906 | 21.7147
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VIN | CUTOUT | 5 | 15 | 3778 | 0.023373 | 9.2798e-05 | 251.8667
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 37 | 178 | 15096 | 0.093416 | 0.0011015 | 84.809
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FO | NONE | 2 | 232 | 14648 | 0.090644 | 0.0014357 | 63.1379
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | EQF | ARRESTER | 2 | 1435 | 324127 | 1.9761 | 0.0087489 | 225.8725
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 2 | 36 | 0.00022277 | 1.2376e-05 | 18
AEP-KYP | 2025 | 161599 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 1 | 1399 | 283997 | 1.7574 | 0.0086572 | 203
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WW | NONE | 4 | 668 | 66373 | 0.40466 | 0.0040726 | 99.3608
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | FUSE | 109 | 634 | 63418 | 0.39234 | 0.0039222 | 100.0284
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 1 | 62 | 0.00038356 | 6.1865e-06 | 62
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 6 | 11 | 1809 | 0.011029 | 6.7065e-05 | 164.4545
AEP-KYP | 2023 | 161642 | TRANSMISSION STATION | FW | NONE | 7 | 3061 | 70593 | 0.43672 | 0.018937 | 23.0621
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | REGULATOR | 4 | 565 | 28827 | 0.17839 | 0.0034963 | 51.0212
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | CUTOUT | 309 | 1005 | 32896 | 0.20357 | 0.0062191 | 32.7323
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 14 | 43 | 1764 | 0.010755 | 0.00026216 | 41.0233
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | F | NONE | 13 | 1427 | 109517 | 0.67753 | 0.0088282 | 76.7463
AEP-KYP | 2023 | 161642 | PARTIAL POWER | OL | FUSE | 2 | 5 | 385 | 0.0023818 | 3.0933e-05 | 77
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 32 | 178 | 59706 | 0.36947 | 0.0011015 | 335.427
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 13 | 2912 | 0.018015 | 8.0425e-05 | 224
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 37 | 23347 | 0.14444 | 0.0002289 | 631
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 1 | 562 | 0.0034264 | 6.0968e-06 | 562
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WI | CROSSARM | 2 | 289 | 192950 | 1.1909 | 0.0017838 | 667.6471
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 16 | 1603 | 0.0099196 | 9.9011e-05 | 100.1875
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WL | ARRESTER | 2 | 5 | 1126 | 0.006966 | 3.0933e-05 | 225.2
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | ARRESTER | 5 | 77 | 14990 | 0.09276 | 0.00047649 | 194.6753
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 2 | 35 | 4510 | 0.027909 | 0.00021659 | 128.8571
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | FW | NONE | 1 | 252 | 11018 | 0.068181 | 0.0015594 | 43.7222
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | CONDUCTOR UG | 7 | 26 | 8880 | 0.054951 | 0.00016089 | 341.5385
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WI | NONE | 7 | 274 | 91748 | 0.56775 | 0.0016956 | 334.8467
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | A | ARRESTER | 3 | 18 | 2122 | 0.012855 | 0.00010904 | 117.8889
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 26 | 5070 | 0.030713 | 0.0001575 | 195
AEP-KYP | 2025 | 161599 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 8 | 4417 | 870149 | 5.3846 | 0.027333 | 197
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 2 | 4 | 1608 | 0.0097409 | 2.4231e-05 | 402
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | F | FUSE | 2 | 6 | 345 | 0.0021343 | 3.7119e-05 | 57.5
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ERO | NONE | 1 | 1 | 27 | 0.00016356 | 6.0578e-06 | 27
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | EQF | ARRESTER | 4 | 3282 | 567725 | 3.4392 | 0.019882 | 172.9814
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 356 | 0.0021566 | 1.2116e-05 | 178
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FO | NONE | 4 | 486 | 56294 | 0.34102 | 0.0029441 | 115.8313
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SO | NONE | 5 | 38 | 23084 | 0.14285 | 0.00023515 | 607.4737
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 66 | 12355 | 0.076434 | 0.00040831 | 187.197
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 3 | 145 | 0.00089728 | 1.8564e-05 | 48.3333
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | RECLOSER, LINE/OCR/BR | 1 | 130 | 10010 | 0.061783 | 0.00080238 | 77
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | O | FUSE | 12 | 51 | 5555 | 0.034375 | 0.0003156 | 108.9216
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | AF | RELAY | 1 | 45 | 9000 | 0.05452 | 0.0002726 | 200
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 24 | 4674 | 0.028923 | 0.00014852 | 194.75
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 47 | 5730 | 0.034935 | 0.00028655 | 121.9149
AEP-KYP | 2025 | 161599 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 2 | 4 | 918 | 0.0056807 | 2.4753e-05 | 229.5
AEP-KYP | 2021 | 164021 | PARTIAL POWER | OL | FUSE | 1 | 2 | 186 | 0.001134 | 1.2194e-05 | 93
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 3 | 582 | 0.0035483 | 1.829e-05 | 194
AEP-KYP | 2021 | 164021 | PARTIAL POWER | VIN | FUSE | 3 | 6 | 338 | 0.0020607 | 3.6581e-05 | 56.3333
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | OL | NONE | 3 | 533 | 59694 | 0.3694 | 0.0032983 | 111.9962
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | F | NONE | 2 | 929 | 19717 | 0.12201 | 0.0057488 | 21.2239
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 5 | 977 | 445878 | 2.7592 | 0.0060458 | 456.3746
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | CUTOUT | 1 | 1 | 164 | 0.0010149 | 6.1882e-06 | 164
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 35 | 2145 | 0.013274 | 0.00021659 | 61.2857
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 56 | 4536 | 0.028069 | 0.00034654 | 81
AEP-KYP | 2024 | 161599 | PARTIAL POWER | WU | NONE | 1 | 1 | 112 | 0.00069307 | 6.1882e-06 | 112
AEP-KYP | 2024 | 161599 | PARTIAL POWER | V | CONDUCTOR UG | 1 | 12 | 3504 | 0.021683 | 7.4258e-05 | 292
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 1 | 25 | 0.0001543 | 6.1722e-06 | 25
AEP-KYP | 2022 | 162018 | DISTRIBUTION SOURCE | TIR | NONE | 1 | 924 | 71328 | 0.44025 | 0.0057031 | 77.1948
AEP-KYP | 2021 | 164021 | PARTIAL POWER | VA | SPLICE, OH | 1 | 1 | 528 | 0.0032191 | 6.0968e-06 | 528
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 2 | 9440 | 0.057554 | 1.2194e-05 | 4720
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TOR | FUSE | 1 | 4 | 392 | 0.0023899 | 2.4387e-05 | 98
AEP-KYP | 2023 | 161642 | PARTIAL POWER | CE | NONE | 1 | 3 | 1110 | 0.006867 | 1.856e-05 | 370
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 3 | 11 | 3002 | 0.018529 | 6.7894e-05 | 272.9091
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | FUSE | 56 | 485 | 66397 | 0.40981 | 0.0029935 | 136.901
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | INSULATOR | 5 | 314 | 22108 | 0.13645 | 0.0019381 | 70.4076
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 1 | 117 | 0.00071332 | 6.0968e-06 | 117
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | VIN | NONE | 3 | 2371 | 231789 | 1.4306 | 0.014634 | 97.76
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 7 | 978 | 215212 | 1.3121 | 0.0059627 | 220.0532
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 35 | 332 | 104233 | 0.63549 | 0.0020241 | 313.9548
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WU | FUSE | 6 | 17 | 2849 | 0.017584 | 0.00010493 | 167.5882
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 36 | 1845 | 496001 | 3.024 | 0.011249 | 268.8352
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | CUTOUT | 475 | 19043 | 1766248 | 10.6995 | 0.11536 | 92.7505
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TR | FUSE | 16 | 164 | 20995 | 0.128 | 0.00099987 | 128.0183
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | CROSSARM | 40 | 9932 | 2521497 | 15.5993 | 0.061444 | 253.8761
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | NONE | 192 | 1933 | 88025 | 0.54457 | 0.011959 | 45.538
AEP-KYP | 2021 | 164021 | PARTIAL POWER | A | NONE | 1 | 1 | 40 | 0.00024387 | 6.0968e-06 | 40
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CE | METERING | 2 | 8 | 871 | 0.0052763 | 4.8462e-05 | 108.875
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ERF | FUSE | 2 | 6 | 3393 | 0.020686 | 3.6581e-05 | 565.5
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | FUSE | 181 | 931 | 96140 | 0.59477 | 0.0057596 | 103.2653
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 6 | 33 | 1649 | 0.0099893 | 0.00019991 | 49.9697
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TIR | FUSE | 88 | 606 | 100621 | 0.62249 | 0.003749 | 166.0413
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 30 | 1051 | 942229 | 5.8291 | 0.006502 | 896.5071
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 5 | 14 | 2373 | 0.014468 | 8.5355e-05 | 169.5
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | NONE | 183 | 17101 | 1750252 | 10.8308 | 0.10582 | 102.3479
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | A | FUSE | 402 | 1890 | 247387 | 1.5309 | 0.011696 | 130.8926
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 2 | 484 | 0.0029873 | 1.2344e-05 | 242
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SO | TRANSFORMER, OH | 1 | 3 | 678 | 0.0041945 | 1.856e-05 | 226
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WU | METERING | 1 | 308 | 38192 | 0.23136 | 0.0018658 | 124
AEP-KYP | 2021 | 164021 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 10 | 2680 | 0.016339 | 6.0968e-05 | 268
AEP-KYP | 2023 | 161642 | PARTIAL POWER | CO | NONE | 1 | 1 | 126 | 0.0007795 | 6.1865e-06 | 126
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TIR | FUSE | 1 | 1 | 426 | 0.0026293 | 6.1722e-06 | 426
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 6 | 1230 | 0.0076114 | 3.7129e-05 | 205
AEP-KYP | 2023 | 161642 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 87 | 0.00053823 | 6.1865e-06 | 87
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 1 | 474 | 0.0029332 | 6.1882e-06 | 474
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | POLE | 4 | 1559 | 172563 | 1.0651 | 0.0096224 | 110.6883
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | POLE | 49 | 9053 | 1994580 | 12.3109 | 0.055877 | 220.3225
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | METERING | 5 | 34 | 5255 | 0.032435 | 0.00020985 | 154.5588
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | CUTOUT | 365 | 916 | 21888 | 0.13345 | 0.0055847 | 23.8952
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 13 | 93 | 17551 | 0.10833 | 0.00057401 | 188.7204
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | CUTOUT | 5 | 22 | 4499 | 0.027769 | 0.00013579 | 204.5
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | NONE | 3 | 17 | 2526 | 0.015591 | 0.00010493 | 148.5882
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CE | METERING | 1 | 1 | 116 | 0.00070723 | 6.0968e-06 | 116
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | NONE | 227 | 18435 | 1712745 | 10.3754 | 0.11168 | 92.9072
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 29 | 52 | 13560 | 0.082143 | 0.000315 | 260.7692
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | U | NONE | 9 | 7424 | 498735 | 3.0783 | 0.045822 | 67.1787
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | NONE | 290 | 31655 | 6331449 | 39.1696 | 0.19583 | 200.0142
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 1 | 3 | 921 | 0.0056151 | 1.829e-05 | 307
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WFS | NONE | 4 | 90 | 20709 | 0.12626 | 0.00054871 | 230.1
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WW | NONE | 51 | 778 | 340528 | 2.0628 | 0.004713 | 437.6967
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 4 | 821 | 0.0050055 | 2.4387e-05 | 205.25
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 8 | 170 | 90175 | 0.54978 | 0.0010365 | 530.4412
AEP-KYP | 2021 | 164021 | DISTRIBUTION SOURCE | SCO | NONE | 1 | 24 | 2040 | 0.012437 | 0.00014632 | 85
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 11 | 251 | 14521 | 0.089858 | 0.0015532 | 57.8526
AEP-KYP | 2020 | 165077 | PARTIAL POWER | U | NONE | 4 | 4 | 372 | 0.0022535 | 2.4231e-05 | 93
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 3 | 3 | 618 | 0.0037437 | 1.8173e-05 | 206
AEP-KYP | 2023 | 161642 | DISTRIBUTION STATION | SCO | REGULATOR | 1 | 1072 | 195104 | 1.207 | 0.0066319 | 182
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | ARRESTER | 2 | 11 | 640 | 0.003877 | 6.6636e-05 | 58.1818
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | POLE | 223 | 5873 | 631190 | 3.9059 | 0.036343 | 107.4732
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | SPLICE, OH | 12 | 206 | 45137 | 0.27931 | 0.0012748 | 219.1117
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 1 | 30 | 0.00018564 | 6.1882e-06 | 30
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TR | FUSE | 2 | 64 | 4950 | 0.030631 | 0.00039604 | 77.3438
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 30 | 3390 | 0.020536 | 0.00018173 | 113
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 1 | 83 | 0.0005028 | 6.0578e-06 | 83
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ABI | BREAKER | 1 | 260 | 2860 | 0.017325 | 0.001575 | 11
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 1 | 1 | 263 | 0.0015932 | 6.0578e-06 | 263
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 2 | 210 | 0.0012721 | 1.2116e-05 | 105
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | FUSE | 4 | 27 | 2867 | 0.017741 | 0.00016708 | 106.1852
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | CROSSARM | 2 | 253 | 124533 | 0.77063 | 0.0015656 | 492.2253
AEP-KYP | 2025 | 161599 | TRANSMISSION LINE | SCO | NONE | 1 | 2 | 520 | 0.0032178 | 1.2376e-05 | 260
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WI | POLE | 2 | 737 | 179223 | 1.1091 | 0.0045607 | 243.1791
AEP-KYP | 2025 | 161599 | PARTIAL POWER | U | CONN/CLAMP | 1 | 6 | 828 | 0.0051238 | 3.7129e-05 | 138
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 569 | 108324 | 0.67033 | 0.0035211 | 190.3761
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | V | METERING | 1 | 1 | 40 | 0.00024753 | 6.1882e-06 | 40
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 2 | 6 | 1510 | 0.0093441 | 3.7129e-05 | 251.6667
AEP-KYP | 2021 | 164021 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 101 | 0.00061577 | 6.0968e-06 | 101
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | F | CUTOUT | 1 | 11 | 2521 | 0.01537 | 6.7065e-05 | 229.1818
AEP-KYP | 2021 | 164021 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 1 | 241 | 0.0014693 | 6.0968e-06 | 241
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 22 | 3344 | 0.020388 | 0.00013413 | 152
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 1 | 128 | 0.00079004 | 6.1722e-06 | 128
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 2 | 112 | 0.00069128 | 1.2344e-05 | 56
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WFS | CUTOUT | 2 | 2 | 1020 | 0.0062956 | 1.2344e-05 | 510
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | JUMPER/RISER | 1 | 7 | 1351 | 0.008358 | 4.3306e-05 | 193
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 2 | 50 | 0.00030941 | 1.2376e-05 | 25
AEP-KYP | 2021 | 164021 | PARTIAL POWER | A | FUSE | 5 | 9 | 889 | 0.00542 | 5.4871e-05 | 98.7778
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | FUSE | 13 | 125 | 13784 | 0.085077 | 0.00077152 | 110.272
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 39 | 64 | 8219 | 0.050729 | 0.00039502 | 128.4219
AEP-KYP | 2022 | 162018 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 1 | 302 | 0.001864 | 6.1722e-06 | 302
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 6 | 91 | 16756 | 0.1015 | 0.00055126 | 184.1319
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | POLE | 28 | 2036 | 1025075 | 6.2097 | 0.012334 | 503.475
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | SCO | NONE | 5 | 56 | 11418 | 0.069613 | 0.00034142 | 203.8929
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 1 | 2 | 298 | 0.0018168 | 1.2194e-05 | 149
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | SCO | ARRESTER | 2 | 3777 | 81266 | 0.49546 | 0.023028 | 21.516
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | FW | NONE | 1 | 335 | 2345 | 0.014474 | 0.0020677 | 7
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | V | POLE | 3 | 13 | 943 | 0.0058339 | 8.0425e-05 | 72.5385
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 3 | 551 | 0.0034009 | 1.8516e-05 | 183.6667
AEP-KYP | 2023 | 161642 | TRANSMISSION STATION | SCO | NONE | 5 | 2853 | 191633 | 1.1855 | 0.01765 | 67.1689
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 4 | 429 | 33179 | 0.20526 | 0.002654 | 77.3403
AEP-KYP | 2022 | 162018 | DISTRIBUTION STATION | EQF | INSULATOR | 3 | 2260 | 205727 | 1.2698 | 0.013949 | 91.0296
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | POLE | 25 | 3002 | 505654 | 3.1282 | 0.018572 | 168.439
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | INSULATOR | 29 | 7033 | 787056 | 4.8691 | 0.04351 | 111.909
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TIR | FUSE | 80 | 723 | 159426 | 0.98655 | 0.004474 | 220.5062
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 7 | 533 | 55859 | 0.34557 | 0.0032974 | 104.8011
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | SWITCH, OH | 5 | 126 | 2242 | 0.01387 | 0.0007795 | 17.7937
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | O | NONE | 3 | 1612 | 154766 | 0.95772 | 0.0099753 | 96.0087
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | INSULATOR | 50 | 10441 | 1946843 | 12.0474 | 0.064611 | 186.4614
AEP-KYP | 2023 | 161642 | PARTIAL POWER | VIN | NONE | 1 | 5 | 815 | 0.005042 | 3.0933e-05 | 163
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | CUTOUT | 154 | 3213 | 441716 | 2.7334 | 0.019883 | 137.4777
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ERF | NONE | 7 | 310 | 162729 | 1.007 | 0.0019183 | 524.9323
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 880 | 214360 | 1.3261 | 0.0054441 | 243.5909
AEP-KYP | 2023 | 161642 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 9 | 1611 | 0.0099665 | 5.5679e-05 | 179
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TR | POLE | 5 | 580 | 83858 | 0.51879 | 0.0035882 | 144.5828
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 10 | 34 | 2127 | 0.013162 | 0.0002104 | 62.5588
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | V | POLE | 4 | 779 | 56901 | 0.35211 | 0.0048206 | 73.0436
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | METERING | 6 | 12 | 7478 | 0.046275 | 7.4258e-05 | 623.1667
AEP-KYP | 2024 | 161599 | PARTIAL POWER | CO | CONN/CLAMP | 3 | 5 | 279 | 0.0017265 | 3.0941e-05 | 55.8
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 9 | 1948 | 306922 | 1.8993 | 0.012055 | 157.5575
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 2 | 3380 | 0.020916 | 1.2376e-05 | 1690
AEP-KYP | 2024 | 161599 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 3 | 7 | 911 | 0.0056374 | 4.3317e-05 | 130.1429
AEP-KYP | 2025 | 161599 | PARTIAL POWER | FO | GUY/ANCHOR | 1 | 1 | 167 | 0.0010334 | 6.1882e-06 | 167
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 1 | 201 | 0.0012438 | 6.1882e-06 | 201
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CO | FUSE | 1 | 3 | 417 | 0.0025424 | 1.829e-05 | 139
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 5 | 3026 | 0.018725 | 3.0941e-05 | 605.2
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CO | CONDUCTOR UG | 2 | 4 | 1566 | 0.0095476 | 2.4387e-05 | 391.5
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | ARRESTER | 4 | 542 | 350814 | 2.1388 | 0.0033045 | 647.2583
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TR | FUSE | 1 | 2 | 234 | 0.0014175 | 1.2116e-05 | 117
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 124 | 0.00075116 | 6.0578e-06 | 124
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | POLE | 1 | 8 | 796 | 0.0049258 | 4.9505e-05 | 99.5
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 17 | 34 | 3820 | 0.023632 | 0.00021034 | 112.3529
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | CUTOUT | 14 | 24 | 3234 | 0.019591 | 0.00014539 | 134.75
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 5 | 18 | 974 | 0.0060257 | 0.00011136 | 54.1111
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TR | NONE | 8 | 276 | 43620 | 0.26986 | 0.0017075 | 158.0435
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 56 | 1977 | 435530 | 2.6951 | 0.012234 | 220.2984
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 41 | 651 | 44100 | 0.2729 | 0.0040285 | 67.7419
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | SPLICE, OH | 15 | 25 | 3331 | 0.020613 | 0.0001547 | 133.24
AEP-KYP | 2021 | 164021 | PARTIAL POWER | O | NONE | 3 | 3 | 245 | 0.0014937 | 1.829e-05 | 81.6667
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TOR | NONE | 5 | 18 | 24680 | 0.14951 | 0.00010904 | 1371.1111
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 399 | 19212 | 5250851 | 32.4931 | 0.11889 | 273.311
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | U | NONE | 58 | 4225 | 708725 | 4.3857 | 0.026145 | 167.7456
AEP-KYP | 2024 | 161599 | PARTIAL POWER | TOR | CONN/CLAMP | 7 | 9 | 2229 | 0.013793 | 5.5693e-05 | 247.6667
AEP-KYP | 2025 | 161599 | TRANSMISSION LINE | EQF | INSULATOR | 6 | 6108 | 709224 | 4.3888 | 0.037797 | 116.1139
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 34 | 14926 | 0.091001 | 0.00020729 | 439
AEP-KYP | 2024 | 161599 | PARTIAL POWER | O | NONE | 1 | 1 | 1357 | 0.0083973 | 6.1882e-06 | 1357
AEP-KYP | 2024 | 161599 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 4 | 34 | 8606 | 0.053255 | 0.0002104 | 253.1176
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 188 | 0.0011389 | 6.0578e-06 | 188
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | EQF | ARRESTER | 1 | 3 | 552 | 0.003407 | 1.8516e-05 | 184
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 3 | 10 | 1517 | 0.0093874 | 6.1882e-05 | 151.7
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | EQF | INSULATOR | 4 | 4285 | 528526 | 3.2697 | 0.026509 | 123.3433
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 182 | 0.0011096 | 6.0968e-06 | 182
AEP-KYP | 2020 | 165077 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 104 | 0.00063001 | 6.0578e-06 | 104
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WH | NONE | 1 | 2 | 60 | 0.00037129 | 1.2376e-05 | 30
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CO | CONN/CLAMP | 2 | 14 | 4095 | 0.025341 | 8.6634e-05 | 292.5
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ERF | FUSE | 1 | 9 | 1548 | 0.0095793 | 5.5693e-05 | 172
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ERF | CROSSARM | 1 | 29 | 20909 | 0.12939 | 0.00017946 | 721
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | TIR | NONE | 1 | 2 | 250 | 0.001547 | 1.2376e-05 | 125
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 89 | 50713 | 0.31382 | 0.00055075 | 569.809
AEP-KYP | 2025 | 161599 | PARTIAL POWER | ERF | NONE | 1 | 1 | 74 | 0.00045792 | 6.1882e-06 | 74
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 36 | 5148 | 0.031185 | 0.00021808 | 143
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 3 | 5 | 2304 | 0.014047 | 3.0484e-05 | 460.8
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | OU | POLE | 1 | 163 | 58680 | 0.35776 | 0.00099378 | 360
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 3 | 986 | 0.005973 | 1.8173e-05 | 328.6667
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 2 | 30 | 0.00018516 | 1.2344e-05 | 15
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | REGULATOR | 1 | 150 | 17250 | 0.10647 | 0.00092582 | 115
AEP-KYP | 2023 | 161642 | DISTRIBUTION STATION | SCO | NONE | 1 | 1308 | 18108 | 0.11203 | 0.008092 | 13.844
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 81 | 9153 | 0.05664 | 0.00050124 | 113
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | POLE | 461 | 18003 | 3129993 | 19.0829 | 0.10976 | 173.8595
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | FUSE | 129 | 526 | 97287 | 0.59314 | 0.0032069 | 184.9563
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 16 | 1360 | 0.0083941 | 9.8754e-05 | 85
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WL | FUSE | 62 | 747 | 143173 | 0.88369 | 0.0046106 | 191.664
AEP-KYP | 2022 | 162018 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 9 | 14 | 1630 | 0.010061 | 8.641e-05 | 116.4286
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 378 | 60660 | 0.36983 | 0.0023046 | 160.4762
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 28 | 486 | 336134 | 2.0747 | 0.0029997 | 691.6337
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WU | FUSE | 176 | 1498 | 401772 | 2.4338 | 0.0090746 | 268.2056
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 2 | 616 | 0.0038119 | 1.2376e-05 | 308
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | U | CROSSARM | 1 | 379 | 70494 | 0.43611 | 0.0023447 | 186
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | EQF | CROSSARM | 1 | 698 | 57934 | 0.35758 | 0.0043082 | 83
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | NONE | 90 | 2038 | 186676 | 1.1381 | 0.012425 | 91.5976
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | FUSE | 377 | 4708 | 1278716 | 7.8924 | 0.029058 | 271.6049
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | CUTOUT | 452 | 12850 | 2282264 | 13.9145 | 0.078344 | 177.6081
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | FUSE | 252 | 3521 | 599454 | 3.6547 | 0.021467 | 170.2511
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | SPLICE, OH | 11 | 13 | 1392 | 0.0085916 | 8.0238e-05 | 107.0769
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | INSULATOR | 48 | 16207 | 4333157 | 26.7449 | 0.10003 | 267.3633
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 113 | 3344 | 557703 | 3.4002 | 0.020388 | 166.7772
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 4 | 25 | 2195 | 0.013548 | 0.0001543 | 87.8
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 16 | 1389 | 180525 | 1.1142 | 0.0085731 | 129.9676
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 5 | 706 | 182917 | 1.129 | 0.0043575 | 259.0892
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1097 | 51548 | 15899353 | 96.3148 | 0.31227 | 308.4378
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ABI | NONE | 8 | 388 | 31253 | 0.1929 | 0.0023948 | 80.549
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | CROSSARM | 12 | 3674 | 763591 | 4.6554 | 0.0224 | 207.8364
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 6 | 29 | 10756 | 0.065157 | 0.00017568 | 370.8966
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | SCO | OTHER EQUIPMENT | 1 | 3259 | 302447 | 1.844 | 0.019869 | 92.8036
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | POLE | 4 | 1355 | 190449 | 1.1755 | 0.0083633 | 140.5528
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 5 | 897 | 135007 | 0.82311 | 0.0054688 | 150.5095
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 243 | 42007 | 0.25447 | 0.001472 | 172.8683
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | FUSE | 267 | 2791 | 624969 | 3.8664 | 0.017267 | 223.923
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | ARRESTER | 2 | 2 | 143 | 0.00088467 | 1.2373e-05 | 71.5
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | FUSE | 11 | 88 | 7831 | 0.047438 | 0.00053308 | 88.9886
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | CUTOUT | 481 | 16025 | 2138732 | 13.2348 | 0.099165 | 133.4622
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | FUSE | 76 | 358 | 44132 | 0.2731 | 0.0022154 | 123.2737
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 4 | 75 | 16401 | 0.099354 | 0.00045433 | 218.68
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 2 | 488 | 178476 | 1.0881 | 0.0029752 | 365.7295
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 6 | 173 | 45429 | 0.28112 | 0.0010706 | 262.5954
AEP-KYP | 2023 | 161642 | DISTRIBUTION STATION | FW | NONE | 1 | 2018 | 30270 | 0.18727 | 0.012484 | 15
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | INSULATOR | 12 | 770 | 215344 | 1.3326 | 0.0047649 | 279.6675
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | CROSSARM | 39 | 10157 | 3856194 | 23.801 | 0.062691 | 379.6588
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WI | FUSE | 22 | 160 | 47616 | 0.29389 | 0.00098754 | 297.6
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | NONE | 7 | 1852 | 242983 | 1.4814 | 0.011291 | 131.2003
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TR | POLE | 9 | 361 | 94357 | 0.58239 | 0.0022281 | 261.3767
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | V | POLE | 4 | 34 | 13848 | 0.085472 | 0.00020985 | 407.2941
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | SCO | NONE | 5 | 1591 | 57506 | 0.3506 | 0.0097 | 36.1446
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 37 | 82 | 13110 | 0.079929 | 0.00049994 | 159.878
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | METERING | 2 | 22 | 2170 | 0.01323 | 0.00013413 | 98.6364
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | SPLICE, OH | 29 | 520 | 90037 | 0.54542 | 0.00315 | 173.1481
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | CUTOUT | 3 | 10 | 33742 | 0.20572 | 6.0968e-05 | 3374.2
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | A | CUTOUT | 7 | 55 | 8515 | 0.051914 | 0.00033532 | 154.8182
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 24 | 43 | 11346 | 0.070192 | 0.00026602 | 263.8605
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 1 | 71 | 0.00043287 | 6.0968e-06 | 71
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 4 | 14 | 3475 | 0.021051 | 8.4809e-05 | 248.2143
AEP-KYP | 2022 | 162018 | PARTIAL POWER | O | CONDUCTOR UG | 1 | 6 | 1326 | 0.0081843 | 3.7033e-05 | 221
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VIN | FUSE | 254 | 1048 | 156590 | 0.96875 | 0.0064835 | 149.4179
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | CONDUCTOR UG | 12 | 14 | 3762 | 0.023274 | 8.6611e-05 | 268.7143
AEP-KYP | 2023 | 161642 | PARTIAL POWER | ABI | FUSE | 6 | 8 | 621 | 0.0038418 | 4.9492e-05 | 77.625
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | A | CUTOUT | 4 | 22 | 3890 | 0.024072 | 0.00013614 | 176.8182
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | FUSE | 236 | 1260 | 154332 | 0.95503 | 0.0077971 | 122.4857
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | REGULATOR | 5 | 641 | 26991 | 0.16698 | 0.0039656 | 42.1076
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WW | FUSE | 14 | 111 | 55836 | 0.34543 | 0.0006867 | 503.027
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 9 | 37 | 3572 | 0.022104 | 0.00022896 | 96.5405
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 9 | 1261 | 0.0076389 | 5.452e-05 | 140.1111
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 8 | 2106 | 0.013029 | 4.9492e-05 | 263.25
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | POLE | 44 | 10421 | 2147661 | 13.2901 | 0.064487 | 206.0897
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WW | POLE | 6 | 424 | 117752 | 0.72847 | 0.0026231 | 277.717
AEP-KYP | 2023 | 161642 | PARTIAL POWER | WW | NONE | 1 | 1 | 777 | 0.0048069 | 6.1865e-06 | 777
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 7 | 720 | 0.0044543 | 4.3306e-05 | 102.8571
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FO | PEDESTAL | 1 | 5 | 1280 | 0.0079004 | 3.0861e-05 | 256
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WL | FUSE | 43 | 286 | 61770 | 0.38224 | 0.0017698 | 215.979
AEP-KYP | 2023 | 161642 | PARTIAL POWER | O | FUSE | 1 | 1 | 133 | 0.00082281 | 6.1865e-06 | 133
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | F | POLE | 7 | 114 | 16613 | 0.10129 | 0.00069503 | 145.7281
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | V | NONE | 3 | 6 | 585 | 0.0036191 | 3.7119e-05 | 97.5
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 67 | 0.00041461 | 6.1882e-06 | 67
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SO | FUSE | 1 | 3 | 189 | 0.0011696 | 1.8564e-05 | 63
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | OU | FUSE | 1 | 15 | 2505 | 0.015272 | 9.1452e-05 | 167
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WFS | POLE | 1 | 8 | 36600 | 0.2259 | 4.9377e-05 | 4575
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | SCO | OTHER EQUIPMENT | 1 | 3 | 1320 | 0.0080477 | 1.829e-05 | 440
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FO | RECLOSER, LINE/OCR/BR | 1 | 73 | 2555 | 0.015577 | 0.00044506 | 35
AEP-KYP | 2022 | 162018 | PARTIAL POWER | O | NONE | 1 | 1 | 270 | 0.0016665 | 6.1722e-06 | 270
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | EQF | POLE HARDWARE | 2 | 1032 | 155130 | 0.93974 | 0.0062516 | 150.3198
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 41 | 68 | 20611 | 0.12721 | 0.00041971 | 303.1029
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | FUSE | 12 | 185 | 5526 | 0.034107 | 0.0011418 | 29.8703
AEP-KYP | 2022 | 162018 | DISTRIBUTION STATION | SCO | NONE | 1 | 1296 | 45360 | 0.27997 | 0.0079991 | 35
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 68 | 1340 | 660041 | 4.0739 | 0.0082707 | 492.5679
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 4 | 12 | 1263 | 0.0077002 | 7.3161e-05 | 105.25
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | SWITCH, OH | 1 | 4 | 828 | 0.0051105 | 2.4689e-05 | 207
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | ARRESTER | 40 | 3101 | 508385 | 3.0995 | 0.018906 | 163.9423
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | OU | FUSE | 4 | 25 | 3291 | 0.020313 | 0.0001543 | 131.64
AEP-KYP | 2021 | 164021 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 16 | 1588 | 0.0096817 | 9.7548e-05 | 99.25
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | OU | NONE | 4 | 124 | 13791 | 0.084081 | 0.000756 | 111.2177
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | CUTOUT | 7 | 38 | 8122 | 0.049518 | 0.00023168 | 213.7368
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 5 | 47 | 10984 | 0.066967 | 0.00028655 | 233.7021
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 3 | 148 | 42898 | 0.26477 | 0.00091348 | 289.8514
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 6 | 19 | 1891 | 0.011672 | 0.00011727 | 99.5263
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | SCO | NONE | 4 | 208 | 33141 | 0.20455 | 0.0012838 | 159.3317
AEP-KYP | 2022 | 162018 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 61 | 0.0003765 | 6.1722e-06 | 61
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 6 | 12 | 1649 | 0.010178 | 7.4066e-05 | 137.4167
AEP-KYP | 2022 | 162018 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 8 | 768 | 0.0047402 | 4.9377e-05 | 96
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 30 | 487 | 500672 | 3.033 | 0.0029501 | 1028.0739
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | CUTOUT | 8 | 142 | 25091 | 0.152 | 0.0008602 | 176.6972
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 3 | 1068 | 0.0066072 | 1.856e-05 | 356
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | SPLICE, OH | 26 | 530 | 42087 | 0.26037 | 0.0032789 | 79.4094
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | V | RECLOSER, LINE/OCR/BR | 1 | 17 | 2108 | 0.01277 | 0.00010298 | 124
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 23 | 4002 | 0.024243 | 0.00013933 | 174
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 8 | 272 | 0.0016832 | 4.9505e-05 | 34
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | NONE | 371 | 34841 | 6913189 | 42.7799 | 0.2156 | 198.4211
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | FUSE | 398 | 4373 | 1075209 | 6.6536 | 0.027061 | 245.8745
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | SWITCH, OH | 6 | 2181 | 373149 | 2.275 | 0.013297 | 171.0908
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | EQF | FUSE | 1 | 4 | 456 | 0.0027801 | 2.4387e-05 | 114
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | A | CUTOUT | 6 | 19 | 3022 | 0.018307 | 0.0001151 | 159.0526
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 43 | 8995 | 0.055519 | 0.0002654 | 209.186
AEP-KYP | 2020 | 165077 | TRANSMISSION STATION | EQF | REGULATOR | 2 | 1951 | 25363 | 0.15364 | 0.011819 | 13
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | SPLICE, OH | 2 | 91 | 19758 | 0.12223 | 0.00056297 | 217.1209
AEP-KYP | 2023 | 161642 | TRANSMISSION STATION | EQF | ARRESTER | 2 | 1481 | 367288 | 2.2722 | 0.0091622 | 248
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 14 | 238 | 68348 | 0.42284 | 0.0014724 | 287.1765
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | CROSSARM | 9 | 325 | 14729 | 0.091121 | 0.0020106 | 45.32
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 3 | 690 | 0.0041799 | 1.8173e-05 | 230
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 25 | 316 | 276728 | 1.7124 | 0.0019555 | 875.7215
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 7 | 14 | 2376 | 0.014393 | 8.4809e-05 | 169.7143
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ABI | SWITCH, OH | 3 | 2113 | 332095 | 2.0118 | 0.0128 | 157.1675
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 65 | 23725 | 0.14465 | 0.00039629 | 365
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 2 | 279 | 108883 | 0.66384 | 0.001701 | 390.2616
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 57 | 5786 | 0.03505 | 0.00034529 | 101.5088
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 6 | 336 | 66978 | 0.41447 | 0.0020792 | 199.3393
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 20 | 3100 | 0.019183 | 0.00012376 | 155
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | ARRESTER | 1 | 5 | 480 | 0.0029077 | 3.0289e-05 | 96
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | FUSE | 2 | 4 | 124 | 0.00075116 | 2.4231e-05 | 31
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 4 | 516 | 0.0031459 | 2.4387e-05 | 129
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 5 | 75 | 0.00046411 | 3.0941e-05 | 15
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 242 | 0.0014971 | 1.2373e-05 | 121
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | TOR | NONE | 1 | 19 | 33991 | 0.20591 | 0.0001151 | 1789
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 3 | 561 | 0.0034716 | 1.8564e-05 | 187
AEP-KYP | 2021 | 164021 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 1470 | 0.0089623 | 6.0968e-06 | 1470
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 29 | 5394 | 0.032886 | 0.00017681 | 186
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 600 | 66160 | 0.40336 | 0.0036581 | 110.2667
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 1 | 4465 | 0.027222 | 6.0968e-06 | 4465
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SO | FUSE | 3 | 15 | 2211 | 0.013647 | 9.2582e-05 | 147.4
AEP-KYP | 2021 | 164021 | PARTIAL POWER | O | FUSE | 1 | 1 | 556 | 0.0033898 | 6.0968e-06 | 556
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 2 | 436 | 0.0026582 | 1.2194e-05 | 218
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ERF | NONE | 11 | 32 | 5290 | 0.032046 | 0.00019385 | 165.3125
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CF | FUSE | 3 | 176 | 54206 | 0.33048 | 0.001073 | 307.9886
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WFS | POLE | 13 | 865 | 675523 | 4.1185 | 0.0052737 | 780.9514
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 7 | 1301 | 223468 | 1.3793 | 0.00803 | 171.7663
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | V | NONE | 11 | 584 | 106542 | 0.64541 | 0.0035377 | 182.4349
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | OL | NONE | 2 | 36 | 8532 | 0.052018 | 0.00021948 | 237
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 20 | 112 | 39236 | 0.23768 | 0.00067847 | 350.3214
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | CROSSARM | 22 | 5225 | 922465 | 5.7068 | 0.032325 | 176.5483
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WFS | FUSE | 12 | 49 | 19223 | 0.11865 | 0.00030244 | 392.3061
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | SPLICE, OH | 6 | 145 | 66180 | 0.40942 | 0.00089704 | 456.4138
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | NONE | 164 | 3381 | 139714 | 0.86457 | 0.020922 | 41.3233
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | TOR | NONE | 6 | 3209 | 445340 | 2.7487 | 0.019806 | 138.7784
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 3 | 537 | 0.003274 | 1.829e-05 | 179
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 44 | 2165 | 0.013397 | 0.00027228 | 49.2045
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | GUY/ANCHOR | 2 | 218 | 29708 | 0.18384 | 0.001349 | 136.2752
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | CE | NONE | 9 | 23 | 2282 | 0.014121 | 0.00014233 | 99.2174
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 18 | 756 | 131500 | 0.81374 | 0.0046782 | 173.9418
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TIR | NONE | 12 | 287 | 49445 | 0.30597 | 0.001776 | 172.2822
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | CROSSARM | 7 | 1554 | 354064 | 2.191 | 0.0096164 | 227.8404
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 1 | 88 | 15400 | 0.095298 | 0.00054456 | 175
AEP-KYP | 2025 | 161599 | TRANSMISSION LINE | FW | NONE | 1 | 3 | 816 | 0.0050495 | 1.8564e-05 | 272
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | CUTOUT | 2 | 5 | 11420 | 0.070669 | 3.0941e-05 | 2284
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | CROSSARM | 11 | 259 | 15011 | 0.09289 | 0.0016027 | 57.9575
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 302 | 27180 | 0.16465 | 0.0018294 | 90
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | VIN | NONE | 5 | 163 | 17944 | 0.11104 | 0.0010087 | 110.0859
AEP-KYP | 2021 | 164021 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 74 | 0.00045116 | 6.0968e-06 | 74
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | CROSSARM | 3 | 25 | 1256 | 0.0077723 | 0.0001547 | 50.24
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 1251 | 1502922 | 9.163 | 0.0076271 | 1201.3765
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 194 | 0.0011828 | 6.0968e-06 | 194
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 41 | 13606 | 0.084196 | 0.00025371 | 331.8537
AEP-KYP | 2024 | 161599 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 4 | 387 | 0.0023948 | 2.4753e-05 | 96.75
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | F | POLE | 6 | 1008 | 116487 | 0.72084 | 0.0062377 | 115.5625
AEP-KYP | 2020 | 165077 | PARTIAL POWER | U | CUTOUT | 1 | 4 | 572 | 0.003465 | 2.4231e-05 | 143
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | U | NONE | 3 | 2626 | 52005 | 0.32182 | 0.01625 | 19.8039
AEP-KYP | 2024 | 161599 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 1598 | 362022 | 2.2402 | 0.0098887 | 226.5469
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | U | TRANSFORMER, STATION SERVICE | 1 | 1 | 299 | 0.0018503 | 6.1882e-06 | 299
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 45 | 0.00027847 | 6.1882e-06 | 45
AEP-KYP | 2025 | 161599 | TRANSMISSION LINE | F | NONE | 2 | 987 | 107970 | 0.66814 | 0.0061077 | 109.3921
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 25 | 8000 | 0.049505 | 0.0001547 | 320
AEP-KYP | 2020 | 165077 | PARTIAL POWER | UG | CONDUCTOR UG | 1 | 3 | 1407 | 0.0085233 | 1.8173e-05 | 469
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 1 | 2601 | 0.015756 | 6.0578e-06 | 2601
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 39 | 21762 | 0.13268 | 0.00023777 | 558
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | FW | NONE | 1 | 1042 | 20840 | 0.12706 | 0.0063528 | 20
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 1 | 97 | 0.0005987 | 6.1722e-06 | 97
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FO | POLE | 1 | 1 | 513 | 0.0031663 | 6.1722e-06 | 513
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 2 | 4 | 2302 | 0.013945 | 2.4231e-05 | 575.5
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 2 | 352 | 0.0021323 | 1.2116e-05 | 176
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | EQF | POLE HARDWARE | 1 | 185 | 16280 | 0.10048 | 0.0011418 | 88
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 664 | 0.0040983 | 6.1722e-06 | 664
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | NONE | 307 | 20611 | 1762355 | 10.7447 | 0.12566 | 85.5056
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TR | FUSE | 15 | 203 | 47487 | 0.2931 | 0.0012529 | 233.9261
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | ARRESTER | 1 | 1 | 76 | 0.0004703 | 6.1882e-06 | 76
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 28 | 9116 | 0.056411 | 0.00017327 | 325.5714
AEP-KYP | 2023 | 161642 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 109 | 0.00067433 | 6.1865e-06 | 109
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | F | POLE | 1 | 23 | 4692 | 0.029035 | 0.00014233 | 204
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WW | POLE | 1 | 18 | 30312 | 0.18709 | 0.0001111 | 1684
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 2 | 2 | 219 | 0.0013548 | 1.2373e-05 | 109.5
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 2 | 30 | 0.0001829 | 1.2194e-05 | 15
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | OU | NONE | 3 | 3984 | 913054 | 5.5667 | 0.02429 | 229.1802
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | EQF | INSULATOR | 1 | 375 | 61500 | 0.37959 | 0.0023146 | 164
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | O | NONE | 3 | 38 | 6847 | 0.041478 | 0.0002302 | 180.1842
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 9 | 107 | 3295 | 0.020385 | 0.00066196 | 30.7944
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 2 | 944 | 140522 | 0.85125 | 0.0057185 | 148.8581
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SO | POLE | 2 | 80 | 22076 | 0.13657 | 0.00049492 | 275.95
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | O | NONE | 2 | 118 | 10842 | 0.067074 | 0.00073001 | 91.8814
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | NONE | 10 | 2011 | 202614 | 1.2535 | 0.012441 | 100.7529
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 14 | 1718 | 157651 | 0.97531 | 0.010628 | 91.7643
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | CONN/CLAMP | 3 | 81 | 3543 | 0.021925 | 0.00050124 | 43.7407
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 17 | 2890 | 0.017879 | 0.00010517 | 170
AEP-KYP | 2020 | 165077 | PARTIAL POWER | CO | CONN/CLAMP | 2 | 19 | 3558 | 0.021554 | 0.0001151 | 187.2632
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | FUSE | 74 | 845 | 112728 | 0.69758 | 0.005229 | 133.4059
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 13 | 473 | 169066 | 1.0462 | 0.002927 | 357.4334
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 17 | 70 | 11815 | 0.073113 | 0.00043317 | 168.7857
AEP-KYP | 2025 | 161599 | DISTRIBUTION STATION | SCO | NONE | 2 | 1997 | 47746 | 0.29546 | 0.012358 | 23.9089
AEP-KYP | 2024 | 161599 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 167 | 0.0010334 | 6.1882e-06 | 167
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 18 | 4320 | 0.026733 | 0.00011139 | 240
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 1 | 11 | 6.6636e-05 | 6.0578e-06 | 11
AEP-KYP | 2023 | 161642 | TRANSMISSION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 430 | 39130 | 0.24208 | 0.0026602 | 91
AEP-KYP | 2023 | 161642 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 277 | 0.0017137 | 6.1865e-06 | 277
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ABI | NONE | 2 | 989 | 80654 | 0.4991 | 0.0061201 | 81.5511
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WW | NONE | 26 | 341 | 133091 | 0.82337 | 0.0021096 | 390.2962
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WFS | POLE | 1 | 20 | 11920 | 0.073743 | 0.00012373 | 596
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 1 | 48 | 3504 | 0.021683 | 0.00029703 | 73
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WI | JUMPER/RISER | 1 | 99 | 43893 | 0.27091 | 0.00061104 | 443.3636
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | CONN/CLAMP | 64 | 170 | 39537 | 0.24466 | 0.001052 | 232.5706
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | BE | FUSE | 1 | 6 | 630 | 0.0038885 | 3.7033e-05 | 105
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 5 | 115 | 33324 | 0.20616 | 0.00071145 | 289.7739
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 311 | 0.0019245 | 6.1882e-06 | 311
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | NONE | 37 | 927 | 54690 | 0.33843 | 0.0057364 | 58.9968
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | NONE | 270 | 2832 | 392461 | 2.4286 | 0.017525 | 138.5809
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 403 | 25792 | 0.1596 | 0.0024938 | 64
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 6 | 91 | 36960 | 0.22871 | 0.00056312 | 406.1538
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | FUSE | 9 | 52 | 5335 | 0.033014 | 0.00032178 | 102.5962
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 17 | 1479 | 0.0089595 | 0.00010298 | 87
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | PEDESTAL | 1 | 5 | 175 | 0.0010801 | 3.0861e-05 | 35
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERF | NONE | 15 | 118 | 11337 | 0.070155 | 0.0007302 | 96.0763
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TIR | CROSSARM | 3 | 235 | 74641 | 0.45216 | 0.0014236 | 317.6213
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TIR | NONE | 2 | 5 | 1226 | 0.0074747 | 3.0484e-05 | 245.2
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | VA | NONE | 3 | 494 | 35388 | 0.21899 | 0.0030569 | 71.6356
AEP-KYP | 2024 | 161599 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 263 | 0.0016275 | 6.1882e-06 | 263
AEP-KYP | 2024 | 161599 | PARTIAL POWER | UG | CONDUCTOR UG | 1 | 2 | 664 | 0.0041089 | 1.2376e-05 | 332
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CO | NONE | 2 | 216 | 36300 | 0.22457 | 0.0013363 | 168.0556
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VIN | CUTOUT | 8 | 21 | 3851 | 0.023831 | 0.00012995 | 183.381
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 3 | 429 | 0.0026547 | 1.8564e-05 | 143
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | VA | NONE | 4 | 2270 | 352798 | 2.1832 | 0.014047 | 155.4176
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 2 | 276 | 0.0017079 | 1.2376e-05 | 138
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | BE | CONDUCTOR OVERHEAD | 1 | 2 | 238 | 0.0014728 | 1.2376e-05 | 119
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | INSULATOR | 2 | 6 | 1165 | 0.0071027 | 3.6581e-05 | 194.1667
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 8 | 142 | 0.00086574 | 4.8774e-05 | 17.75
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | O | INSULATOR | 1 | 41 | 1271 | 0.007749 | 0.00024997 | 31
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 2 | 428 | 0.0026417 | 1.2344e-05 | 214
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CF | NONE | 1 | 209 | 33858 | 0.20946 | 0.001293 | 162
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 394 | 22105 | 0.13679 | 0.0024381 | 56.1041
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | CUTOUT | 476 | 1559 | 113730 | 0.70359 | 0.0096448 | 72.9506
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WFS | POLE | 36 | 690 | 898890 | 5.5481 | 0.0042588 | 1302.7391
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | NONE | 75 | 8076 | 1534111 | 9.4688 | 0.049846 | 189.9593
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | WL | ARRESTER | 1 | 409 | 95706 | 0.5835 | 0.0024936 | 234
AEP-KYP | 2022 | 162018 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 6 | 620 | 0.0038267 | 3.7033e-05 | 103.3333
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ABI | FUSE | 55 | 173 | 18033 | 0.10994 | 0.0010547 | 104.237
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | F | FUSE | 6 | 19 | 1790 | 0.010843 | 0.0001151 | 94.2105
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | CROSSARM | 24 | 5572 | 864042 | 5.2342 | 0.033754 | 155.0686
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TIR | NONE | 84 | 4943 | 1095159 | 6.6342 | 0.029944 | 221.5576
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WL | NONE | 8 | 152 | 32276 | 0.19678 | 0.00092671 | 212.3421
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | EQF | JUMPER/RISER | 2 | 1160 | 23499 | 0.14538 | 0.0071764 | 20.2578
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 5 | 3908 | 0.024177 | 3.0933e-05 | 781.6
AEP-KYP | 2021 | 164021 | PARTIAL POWER | O | METERING | 1 | 3 | 204 | 0.0012437 | 1.829e-05 | 68
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WW | NONE | 41 | 1704 | 839868 | 5.1972 | 0.010545 | 492.8803
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 3 | 6 | 216 | 0.0013085 | 3.6347e-05 | 36
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TIR | CROSSARM | 3 | 734 | 209509 | 1.2965 | 0.0045421 | 285.4346
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WU | POLE | 3 | 20 | 75705 | 0.4586 | 0.00012116 | 3785.25
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | NONE | 148 | 8116 | 2081899 | 12.8831 | 0.050223 | 256.5179
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 3 | 1181 | 52664 | 0.32589 | 0.0073082 | 44.5927
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 1 | 2825 | 0.017436 | 6.1722e-06 | 2825
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 1 | 96 | 0.00059253 | 6.1722e-06 | 96
AEP-KYP | 2025 | 161599 | PARTIAL POWER | WU | NONE | 1 | 2 | 2256 | 0.01396 | 1.2376e-05 | 1128
AEP-KYP | 2024 | 161599 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 2 | 470 | 0.0029084 | 1.2376e-05 | 235
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 2 | 3 | 344 | 0.0021287 | 1.8564e-05 | 114.6667
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SO | CUTOUT | 1 | 2 | 74 | 0.00044828 | 1.2116e-05 | 37
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | UB | SECTIONALIZER | 1 | 2 | 5604 | 0.034166 | 1.2194e-05 | 2802
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 2 | 2 | 21 | 0.00012992 | 1.2373e-05 | 10.5
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | METERING | 3 | 886 | 50600 | 0.31312 | 0.0054827 | 57.1106
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 16 | 7920 | 0.048997 | 9.8984e-05 | 495
AEP-KYP | 2023 | 161642 | PARTIAL POWER | WU | FUSE | 2 | 7 | 704 | 0.0043553 | 4.3306e-05 | 100.5714
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 10 | 11030 | 0.068255 | 6.1882e-05 | 1103
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WT | POLE | 1 | 1027 | 218914 | 1.3547 | 0.0063552 | 213.1587
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 2 | 60 | 0.00036347 | 1.2116e-05 | 30
AEP-KYP | 2024 | 161599 | TRANSMISSION STATION | EQF | ARRESTER | 1 | 5 | 1308 | 0.0080941 | 3.0941e-05 | 261.6
AEP-KYP | 2020 | 165077 | TRANSMISSION STATION | EQF | ARRESTER | 3 | 3555 | 1404207 | 8.5064 | 0.021535 | 394.9949
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 7 | 3765 | 858828 | 5.3146 | 0.023298 | 228.1084
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OU | POLE | 1 | 5 | 155 | 0.00093896 | 3.0289e-05 | 31
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 2 | 10 | 5472 | 0.033774 | 6.1722e-05 | 547.2
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 129 | 0.00078648 | 6.0968e-06 | 129
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 7 | 1267 | 0.0077246 | 4.2677e-05 | 181
AEP-KYP | 2023 | 161642 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 129 | 0.00079806 | 6.1865e-06 | 129
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SO | FUSE | 1 | 40 | 15680 | 0.097004 | 0.00024746 | 392
AEP-KYP | 2023 | 161642 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 1 | 1 | 145 | 0.00089704 | 6.1865e-06 | 145
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | JUMPER/RISER | 1 | 7 | 931 | 0.0057463 | 4.3205e-05 | 133
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 129 | 6679 | 1557375 | 9.6124 | 0.041224 | 233.1749
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 183 | 1760 | 352683 | 2.1768 | 0.010863 | 200.3881
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 2 | 558 | 86211 | 0.53211 | 0.0034441 | 154.5
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 124 | 440 | 50183 | 0.30595 | 0.0026826 | 114.0523
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 50 | 1010 | 55542 | 0.34281 | 0.0062339 | 54.9921
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 81 | 2207 | 678903 | 4.1391 | 0.013456 | 307.6135
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 122 | 3943 | 782823 | 4.7422 | 0.023886 | 198.5349
AEP-KYP | 2025 | 161599 | PARTIAL POWER | A | FUSE | 1 | 1 | 99 | 0.00061263 | 6.1882e-06 | 99
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | EQF | POLE | 1 | 20 | 19800 | 0.12221 | 0.00012344 | 990
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 1 | 3 | 3432 | 0.020924 | 1.829e-05 | 1144
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CF | FUSE | 1 | 1 | 37 | 0.00022837 | 6.1722e-06 | 37
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TR | FUSE | 1 | 1 | 28 | 0.00017322 | 6.1865e-06 | 28
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 224 | 42112 | 0.25992 | 0.0013826 | 188
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 304 | 0.0018763 | 1.2344e-05 | 152
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | FUSE | 259 | 2735 | 524802 | 3.2392 | 0.016881 | 191.8837
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | POLE | 111 | 11519 | 5729931 | 34.9341 | 0.070229 | 497.433
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | FUSE | 122 | 440 | 41215 | 0.25128 | 0.0026826 | 93.6705
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ABI | POLE | 1 | 9 | 1942 | 0.011986 | 5.5549e-05 | 215.7778
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 15 | 238 | 55045 | 0.3356 | 0.001451 | 231.2815
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | POLE | 26 | 5618 | 1441905 | 8.791 | 0.034252 | 256.6581
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 10 | 2078 | 207009 | 1.2777 | 0.012826 | 99.6193
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 24 | 1445 | 421995 | 2.6046 | 0.0089188 | 292.0381
AEP-KYP | 2022 | 162018 | DISTRIBUTION STATION | U | NONE | 1 | 1007 | 187193 | 1.1554 | 0.0062154 | 185.8918
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | O | NONE | 22 | 1330 | 259136 | 1.6031 | 0.0082281 | 194.8391
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 64 | 14115 | 0.085506 | 0.0003877 | 220.5469
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | FW | METERING | 1 | 777 | 13986 | 0.08527 | 0.0047372 | 18
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | A | NONE | 22 | 259 | 26313 | 0.16279 | 0.0016023 | 101.5946
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | POLE | 48 | 7668 | 1263326 | 7.8156 | 0.047438 | 164.753
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | NONE | 55 | 7455 | 1135646 | 7.0257 | 0.04612 | 152.3335
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 30 | 64 | 36673 | 0.22688 | 0.00039594 | 573.0156
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | NONE | 10 | 574 | 100426 | 0.60836 | 0.0034772 | 174.9582
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TIR | CONN/CLAMP | 2 | 6 | 321 | 0.0019571 | 3.6581e-05 | 53.5
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CE | METERING | 1 | 3 | 69 | 0.00042698 | 1.8564e-05 | 23
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ABI | NONE | 4 | 11 | 2506 | 0.015508 | 6.807e-05 | 227.8182
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TR | TRANSFORMER, OH | 1 | 1 | 509 | 0.0031489 | 6.1865e-06 | 509
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 8 | 3088 | 0.019109 | 4.9505e-05 | 386
AEP-KYP | 2025 | 161599 | PARTIAL POWER | U | FUSE | 2 | 61 | 18318 | 0.11335 | 0.00037748 | 300.2951
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FO | NONE | 4 | 56 | 11355 | 0.070267 | 0.00034654 | 202.7679
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | UG | RECLOSER, LINE/OCR/BR | 1 | 22 | 7664 | 0.047303 | 0.00013579 | 348.3636
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | V | CONN/CLAMP | 1 | 1 | 111 | 0.0006867 | 6.1865e-06 | 111
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 4 | 4296 | 0.026024 | 2.4231e-05 | 1074
AEP-KYP | 2024 | 161599 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 3 | 2086 | 115029 | 0.71182 | 0.012908 | 55.1433
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 16 | 320 | 0.0019802 | 9.9011e-05 | 20
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FO | POLE | 1 | 1 | 392 | 0.0023899 | 6.0968e-06 | 392
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 320 | 5760 | 0.034893 | 0.0019385 | 18
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 2 | 532 | 0.0032227 | 1.2116e-05 | 266
AEP-KYP | 2021 | 164021 | PARTIAL POWER | WI | NONE | 3 | 11 | 8101 | 0.04939 | 6.7065e-05 | 736.4545
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 3 | 390 | 0.0023625 | 1.8173e-05 | 130
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 32 | 13616 | 0.084258 | 0.00019802 | 425.5
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | METERING | 1 | 1 | 307 | 0.0018597 | 6.0578e-06 | 307
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1089 | 49624 | 16589422 | 101.1421 | 0.30255 | 334.3024
AEP-KYP | 2021 | 164021 | PARTIAL POWER | U | FUSE | 43 | 98 | 8601 | 0.052438 | 0.00059748 | 87.7653
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | NONE | 277 | 23004 | 4997813 | 30.4706 | 0.14025 | 217.2584
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 2 | 2250 | 0.013887 | 1.2344e-05 | 1125
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 26 | 2342 | 490351 | 3.0265 | 0.014455 | 209.3728
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 2 | 4 | 651 | 0.003969 | 2.4387e-05 | 162.75
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | F | FUSE | 9 | 43 | 6474 | 0.039959 | 0.0002654 | 150.5581
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 24 | 1227 | 285256 | 1.7606 | 0.0075732 | 232.4825
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TR | SPLICE, OH | 1 | 1 | 60 | 0.00037033 | 6.1722e-06 | 60
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | O | OTHER EQUIPMENT | 2 | 3254 | 292860 | 1.7741 | 0.019712 | 90
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | ARRESTER | 8 | 291 | 189421 | 1.1475 | 0.0017628 | 650.9313
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TIR | FUSE | 104 | 733 | 145984 | 0.88434 | 0.0044404 | 199.1596
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | OL | FUSE | 6 | 120 | 17478 | 0.10788 | 0.00074066 | 145.65
AEP-KYP | 2021 | 164021 | DISTRIBUTION SOURCE | U | FUSE | 1 | 2 | 108 | 0.00065845 | 1.2194e-05 | 54
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | A | FUSE | 290 | 907 | 82233 | 0.50874 | 0.0056112 | 90.6648
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | UG | NONE | 1 | 1 | 146 | 0.00090113 | 6.1722e-06 | 146
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 1 | 286 | 0.0017437 | 6.0968e-06 | 286
AEP-KYP | 2023 | 161642 | PARTIAL POWER | U | CONN/CLAMP | 3 | 5 | 647 | 0.0040027 | 3.0933e-05 | 129.4
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | F | POLE | 5 | 1026 | 462169 | 2.8592 | 0.0063474 | 450.4571
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 33 | 6349 | 0.038461 | 0.00019991 | 192.3939
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 2 | 170 | 0.0010493 | 1.2344e-05 | 85
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FO | FUSE | 4 | 21 | 2726 | 0.016514 | 0.00012721 | 129.8095
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 9 | 872 | 152169 | 0.9414 | 0.0053946 | 174.5057
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | SCO | NONE | 2 | 97 | 3766 | 0.022814 | 0.0005876 | 38.8247
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | INSULATOR | 6 | 130 | 3311 | 0.020057 | 0.00078751 | 25.4692
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WI | FUSE | 2 | 2 | 176 | 0.0010863 | 1.2344e-05 | 88
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 42 | 504 | 42631 | 0.26381 | 0.0031188 | 84.5853
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 1 | 239 | 53562 | 0.33059 | 0.0014751 | 224.1088
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | FUSE | 8 | 9 | 694 | 0.0042946 | 5.5693e-05 | 77.1111
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 11 | 979 | 0.0059306 | 6.6636e-05 | 89
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 15 | 1183 | 204457 | 1.2652 | 0.0073206 | 172.8292
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | U | NONE | 2 | 2233 | 175896 | 1.0724 | 0.013614 | 78.7712
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 37 | 6413 | 0.039685 | 0.00022896 | 173.3243
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 8 | 117 | 2765 | 0.01711 | 0.00072401 | 23.6325
AEP-KYP | 2025 | 161599 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 415 | 4150 | 0.025681 | 0.0025681 | 10
AEP-KYP | 2025 | 161599 | TRANSMISSION LINE | U | CONDUCTOR OVERHEAD | 2 | 17 | 4788 | 0.029629 | 0.0001052 | 281.6471
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 15 | 135 | 35668 | 0.21607 | 0.0008178 | 264.2074
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 76 | 7112 | 0.043896 | 0.00046908 | 93.5789
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 19 | 38 | 1462 | 0.0088565 | 0.0002302 | 38.4737
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | TRANSFORMER, OH | 8 | 16 | 4274 | 0.026441 | 9.8984e-05 | 267.125
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 2 | 8 | 2391 | 0.014758 | 4.9377e-05 | 298.875
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | METERING | 3 | 15 | 1275 | 0.0078695 | 9.2582e-05 | 85
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VIN | NONE | 33 | 829 | 129762 | 0.80277 | 0.0051286 | 156.5283
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | V | METERING | 8 | 8 | 879 | 0.0054379 | 4.9492e-05 | 109.875
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 67 | 0.0004145 | 6.1865e-06 | 67
AEP-KYP | 2020 | 165077 | DISTRIBUTION SOURCE | U | NONE | 1 | 6 | 696 | 0.0042162 | 3.6347e-05 | 116
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 139 | 6762 | 1059956 | 6.5422 | 0.041736 | 156.7518
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 12 | 27 | 4506 | 0.027812 | 0.00016665 | 166.8889
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 320 | 6275 | 1140467 | 6.9532 | 0.038257 | 181.7477
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 6 | 18 | 1631 | 0.010067 | 0.0001111 | 90.6111
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 14 | 20 | 552 | 0.003407 | 0.00012344 | 27.6
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 26 | 1222 | 153705 | 0.94869 | 0.0075424 | 125.7815
AEP-KYP | 2022 | 162018 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 8 | 1872 | 0.011554 | 4.9377e-05 | 234
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | SPLICE, OH | 9 | 20 | 3448 | 0.021022 | 0.00012194 | 172.4
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | POLE | 73 | 1191 | 117161 | 0.7143 | 0.0072613 | 98.372
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 2 | 144 | 0.00088879 | 1.2344e-05 | 72
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 86 | 3046 | 1063468 | 6.4423 | 0.018452 | 349.1359
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 2 | 731 | 97954 | 0.59338 | 0.0044282 | 134
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 116 | 4489 | 615599 | 3.7292 | 0.027193 | 137.135
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ERF | NONE | 4 | 8 | 528 | 0.0032191 | 4.8774e-05 | 66
AEP-KYP | 2022 | 162018 | PARTIAL POWER | U | METERING | 1 | 1 | 194 | 0.0011974 | 6.1722e-06 | 194
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 42 | 258 | 480406 | 2.9289 | 0.001573 | 1862.0388
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | SWITCH, OH | 3 | 818 | 31367 | 0.1936 | 0.0050488 | 38.346
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | POLE HARDWARE | 2 | 88 | 3158 | 0.019492 | 0.00054315 | 35.8864
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | INSULATOR | 52 | 12008 | 1952423 | 11.8273 | 0.072742 | 162.5935
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 56 | 1304 | 74932 | 0.46357 | 0.0080672 | 57.4632
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SO | NONE | 20 | 210 | 74112 | 0.45849 | 0.0012992 | 352.9143
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | CONDUCTOR UG | 10 | 30 | 5407 | 0.032754 | 0.00018173 | 180.2333
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 155 | 1526 | 377541 | 2.3363 | 0.0094431 | 247.4056
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WFS | NONE | 58 | 1220 | 1192185 | 7.3583 | 0.00753 | 977.2008
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | F | NONE | 22 | 321 | 13990 | 0.086348 | 0.0019813 | 43.5826
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | CONDUCTOR UG | 19 | 41 | 14866 | 0.090635 | 0.00024997 | 362.5854
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SO | POLE | 1 | 5 | 185 | 0.0011418 | 3.0861e-05 | 37
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | POLE | 113 | 7545 | 3380528 | 20.4785 | 0.045706 | 448.0488
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WL | FUSE | 54 | 229 | 38923 | 0.2373 | 0.0013962 | 169.9694
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 23 | 73 | 6692 | 0.0408 | 0.00044506 | 91.6712
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 2 | 3 | 462 | 0.0028167 | 1.829e-05 | 154
AEP-KYP | 2021 | 164021 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 197 | 0.0012011 | 6.0968e-06 | 197
AEP-KYP | 2021 | 164021 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 2 | 2 | 242 | 0.0014754 | 1.2194e-05 | 121
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | ARRESTER | 2 | 8 | 141 | 0.00087027 | 4.9377e-05 | 17.625
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | V | METERING | 6 | 6 | 621 | 0.0038329 | 3.7033e-05 | 103.5
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | CUTOUT | 405 | 14294 | 1682203 | 10.407 | 0.08843 | 117.686
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | V | NONE | 4 | 4 | 369 | 0.0022497 | 2.4387e-05 | 92.25
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WFS | REGULATOR | 1 | 42 | 127144 | 0.77517 | 0.00025606 | 3027.2381
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WW | FUSE | 9 | 160 | 26755 | 0.16312 | 0.00097548 | 167.2188
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WH | NONE | 1 | 3 | 159 | 0.00098137 | 1.8516e-05 | 53
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 14 | 181 | 57981 | 0.3587 | 0.0011198 | 320.337
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 6 | 74 | 13085 | 0.080972 | 0.00045792 | 176.8243
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | CUTOUT | 5 | 549 | 6294 | 0.038938 | 0.0033964 | 11.4645
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | WI | NONE | 1 | 603 | 97686 | 0.59176 | 0.0036528 | 162
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WL | NONE | 10 | 1490 | 108758 | 0.67283 | 0.0092179 | 72.9919
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CE | NONE | 19 | 405 | 88033 | 0.53328 | 0.0024534 | 217.3654
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 20 | 594 | 259289 | 1.6045 | 0.0036758 | 436.5135
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 1 | 2 | 630 | 0.0038975 | 1.2373e-05 | 315
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | FUSE | 13 | 196 | 10273 | 0.063554 | 0.0012126 | 52.4133
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CO | CONN/CLAMP | 6 | 49 | 4078 | 0.024863 | 0.00029874 | 83.2245
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | A | NONE | 22 | 86 | 5380 | 0.033292 | 0.00053218 | 62.5581
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | CUTOUT | 7 | 142 | 15444 | 0.095544 | 0.00087848 | 108.7606
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | VIN | FUSE | 20 | 65 | 6188 | 0.038292 | 0.00040223 | 95.2
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | CROSSARM | 25 | 3535 | 1099262 | 6.8024 | 0.021875 | 310.9652
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | A | POLE | 1 | 10 | 2980 | 0.018436 | 6.1865e-05 | 298
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 1 | 161 | 0.00099629 | 6.1882e-06 | 161
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TOR | ARRESTER | 1 | 4 | 120 | 0.00073161 | 2.4387e-05 | 30
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 101 | 27674 | 0.16872 | 0.00061577 | 274
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 5 | 923 | 239537 | 1.4511 | 0.0055913 | 259.52
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 4 | 24 | 4462 | 0.027612 | 0.00014852 | 185.9167
AEP-KYP | 2025 | 161599 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 100 | 0.00061882 | 6.1882e-06 | 100
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 3 | 188 | 12471 | 0.077173 | 0.0011634 | 66.3351
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ABI | NONE | 14 | 1917 | 176987 | 1.0721 | 0.011613 | 92.325
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TIR | POLE | 6 | 93 | 143419 | 0.8875 | 0.0005755 | 1542.1398
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 15 | 2227 | 0.013578 | 9.1452e-05 | 148.4667
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | INSULATOR | 4 | 1435 | 233749 | 1.4465 | 0.00888 | 162.8913
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 701 | 82701 | 0.51044 | 0.0043267 | 117.9757
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 9 | 153 | 0.00093281 | 5.4871e-05 | 17
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | NONE | 8 | 787 | 364293 | 2.2543 | 0.0048701 | 462.8882
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 597 | 19104 | 0.11647 | 0.0036398 | 32
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 1 | 23 | 5474 | 0.033874 | 0.00014233 | 238
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | CUTOUT | 2 | 10 | 1527 | 0.0092502 | 6.0578e-05 | 152.7
AEP-KYP | 2025 | 161599 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 2 | 214 | 0.0013243 | 1.2376e-05 | 107
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 1 | 1 | 92 | 0.00055732 | 6.0578e-06 | 92
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 1 | 119 | 0.00073639 | 6.1882e-06 | 119
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | V | METERING | 3 | 3 | 224 | 0.0013569 | 1.8173e-05 | 74.6667
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 3 | 429 | 0.0026547 | 1.8564e-05 | 143
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 30 | 32688 | 0.19802 | 0.00018173 | 1089.6
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 1 | 253 | 0.0015652 | 6.1865e-06 | 253
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | INSULATOR | 1 | 9 | 1998 | 0.012361 | 5.5679e-05 | 222
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | AO | NONE | 1 | 1659 | 296961 | 1.7989 | 0.01005 | 179
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 7 | 518 | 0.0031379 | 4.2404e-05 | 74
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | U | NONE | 2 | 847 | 58616 | 0.35508 | 0.0051309 | 69.2043
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 17 | 884 | 0.0053896 | 0.00010365 | 52
AEP-KYP | 2021 | 164021 | PARTIAL POWER | VIN | SPLICE, OH | 1 | 1 | 147 | 0.00089623 | 6.0968e-06 | 147
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 1 | 75 | 0.00046411 | 6.1882e-06 | 75
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | SPLICE, OH | 2 | 191 | 25679 | 0.15849 | 0.0011789 | 134.445
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TOR | NONE | 1 | 1 | 168 | 0.0010393 | 6.1865e-06 | 168
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WU | NONE | 1 | 1 | 253 | 0.0015616 | 6.1722e-06 | 253
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 276 | 0.0016719 | 1.2116e-05 | 138
AEP-KYP | 2024 | 161599 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 156 | 20570 | 0.12729 | 0.00096535 | 131.859
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 138 | 0.00085397 | 6.1882e-06 | 138
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CO | POLE | 1 | 42 | 43048 | 0.26639 | 0.0002599 | 1024.9524
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | CUTOUT | 512 | 14198 | 1844520 | 11.3847 | 0.087632 | 129.9141
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | FUSE | 907 | 5619 | 684972 | 4.2376 | 0.034762 | 121.9028
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | CUTOUT | 52 | 126 | 3629 | 0.022125 | 0.00076819 | 28.8016
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 17 | 642 | 314175 | 1.9391 | 0.0039625 | 489.3692
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 2 | 280 | 0.0017282 | 1.2344e-05 | 140
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 17 | 1644 | 817820 | 5.0477 | 0.010147 | 497.4574
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | CROSSARM | 31 | 4524 | 1300751 | 7.9304 | 0.027582 | 287.5223
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 11 | 2024 | 350442 | 2.1366 | 0.01234 | 173.1433
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | O | NONE | 25 | 873 | 62610 | 0.38172 | 0.0053225 | 71.7182
AEP-KYP | 2021 | 164021 | DISTRIBUTION SOURCE | O | NONE | 1 | 1038 | 90306 | 0.55058 | 0.0063285 | 87
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | SWITCH, OH | 8 | 636 | 56882 | 0.35108 | 0.0039255 | 89.4371
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | V | POLE | 5 | 94 | 46012 | 0.28053 | 0.0005731 | 489.4894
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | FUSE | 7 | 26 | 80099 | 0.48835 | 0.00015852 | 3080.7308
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 913 | 0.0056483 | 6.1865e-06 | 913
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 4 | 1162 | 0.0071887 | 2.4746e-05 | 290.5
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | UG | NONE | 1 | 39 | 5304 | 0.032337 | 0.00023777 | 136
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TIR | CUTOUT | 3 | 10 | 2186 | 0.013527 | 6.1882e-05 | 218.6
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | CROSSARM | 13 | 126 | 11931 | 0.073831 | 0.00077971 | 94.6905
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CE | NONE | 2 | 6 | 196 | 0.0012126 | 3.7119e-05 | 32.6667
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 3 | 4 | 437 | 0.0027042 | 2.4753e-05 | 109.25
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 6 | 445 | 195711 | 1.2111 | 0.0027537 | 439.8
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 2 | 349 | 128552 | 0.7955 | 0.0021597 | 368.3438
AEP-KYP | 2025 | 161599 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 7 | 11 | 2598 | 0.016077 | 6.807e-05 | 236.1818
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 2 | 5 | 555 | 0.0034344 | 3.0941e-05 | 111
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 2 | 404 | 0.0024936 | 1.2344e-05 | 202
AEP-KYP | 2020 | 165077 | PARTIAL POWER | OU | OTHER EQUIPMENT | 1 | 1 | 287 | 0.0017386 | 6.0578e-06 | 287
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 33 | 10230 | 0.061971 | 0.00019991 | 310
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | ARRESTER | 3 | 136 | 4618 | 0.028577 | 0.00084159 | 33.9559
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | F | FUSE | 4 | 10 | 1338 | 0.0082798 | 6.1882e-05 | 133.8
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 4 | 144 | 29947 | 0.18532 | 0.00089109 | 207.9653
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 5 | 790 | 0.0048886 | 3.0941e-05 | 158
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OU | OTHER EQUIPMENT | 1 | 9 | 477 | 0.0028896 | 5.452e-05 | 53
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | TOR | NONE | 11 | 7494 | 1801951 | 11.1508 | 0.046374 | 240.4525
AEP-KYP | 2024 | 161599 | PARTIAL POWER | A | FUSE | 1 | 1 | 56 | 0.00034654 | 6.1882e-06 | 56
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 9 | 31968 | 0.1949 | 5.4871e-05 | 3552
AEP-KYP | 2020 | 165077 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 3 | 318 | 0.0019264 | 1.8173e-05 | 106
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | EQF | CONN/CLAMP | 6 | 3081 | 329667 | 2.0099 | 0.018784 | 107
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | EQF | CONN/CLAMP | 3 | 3382 | 501928 | 3.106 | 0.020928 | 148.4116
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 8 | 1856 | 0.011482 | 4.9492e-05 | 232
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERO | FUSE | 2 | 27 | 4890 | 0.03026 | 0.00016708 | 181.1111
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CE | METERING | 1 | 3 | 45 | 0.00027839 | 1.856e-05 | 15
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | OU | CONDUCTOR OVERHEAD | 1 | 20 | 21080 | 0.1277 | 0.00012116 | 1054
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 7 | 210 | 0.0012962 | 4.3205e-05 | 30
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 8 | 760 | 0.0046908 | 4.9377e-05 | 95
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 1 | 148 | 0.00091348 | 6.1722e-06 | 148
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | SCO | POLE | 1 | 17 | 391 | 0.0023686 | 0.00010298 | 23
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 1891 | 697645 | 4.2262 | 0.011455 | 368.9291
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VIN | POLE | 1 | 94 | 16976 | 0.10502 | 0.00058153 | 180.5957
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 2 | 79 | 18339 | 0.11348 | 0.00048886 | 232.1392
AEP-KYP | 2024 | 161599 | PARTIAL POWER | FO | NONE | 1 | 6 | 852 | 0.0052723 | 3.7129e-05 | 142
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 17 | 815 | 0.0050433 | 0.0001052 | 47.9412
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | O | FUSE | 1 | 27 | 1620 | 0.010025 | 0.00016708 | 60
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 1 | 359 | 0.0022215 | 6.1882e-06 | 359
AEP-KYP | 2020 | 165077 | PARTIAL POWER | VIN | FUSE | 2 | 5 | 578 | 0.0035014 | 3.0289e-05 | 115.6
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 9 | 334 | 0.0020615 | 5.5549e-05 | 37.1111
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1247 | 50625 | 16768254 | 103.4962 | 0.31247 | 331.2248
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | FUSE | 91 | 1212 | 218725 | 1.3335 | 0.0073893 | 180.4662
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | REGULATOR | 4 | 1249 | 225246 | 1.3903 | 0.007709 | 180.3411
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WL | ARRESTER | 4 | 161 | 14000 | 0.08641 | 0.00099372 | 86.9565
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 123 | 9125 | 0.055633 | 0.0007499 | 74.187
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VIN | FUSE | 251 | 1006 | 151578 | 0.91823 | 0.0060941 | 150.674
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 36 | 78 | 21558 | 0.13143 | 0.00047555 | 276.3846
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 1 | 35 | 6825 | 0.041611 | 0.00021339 | 195
AEP-KYP | 2021 | 164021 | PARTIAL POWER | O | SPLICE, OH | 1 | 1 | 118 | 0.00071942 | 6.0968e-06 | 118
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 6 | 1254 | 0.0076454 | 3.6581e-05 | 209
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | TRANSFORMER, OH | 7 | 38 | 7066 | 0.04308 | 0.00023168 | 185.9474
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 6 | 224 | 141090 | 0.86019 | 0.0013657 | 629.8661
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VIN | NONE | 37 | 406 | 60734 | 0.37583 | 0.0025124 | 149.5911
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TIR | SPLICE, OH | 2 | 3 | 497 | 0.0030107 | 1.8173e-05 | 165.6667
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 111 | 0.00067674 | 6.0968e-06 | 111
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | TRANSFORMER, OH | 8 | 23 | 9370 | 0.057983 | 0.00014233 | 407.3913
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | F | FUSE | 9 | 44 | 5570 | 0.034468 | 0.00027228 | 126.5909
AEP-KYP | 2025 | 161599 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 53 | 0.00032797 | 6.1882e-06 | 53
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 2 | 1164 | 0.0072011 | 1.2373e-05 | 582
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | NONE | 22 | 778 | 274829 | 1.7007 | 0.0048144 | 353.2506
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 386 | 50180 | 0.31052 | 0.0023886 | 130
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 3 | 141 | 20991 | 0.12798 | 0.00085965 | 148.8723
AEP-KYP | 2024 | 161599 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 1 | 85 | 0.00052599 | 6.1882e-06 | 85
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 5 | 983 | 0.0060672 | 3.0861e-05 | 196.6
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | A | ARRESTER | 1 | 28 | 2268 | 0.014035 | 0.00017327 | 81
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | INSULATOR | 2 | 22 | 3129 | 0.018955 | 0.00013327 | 142.2273
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SO | CONN/CLAMP | 1 | 27 | 2277 | 0.013882 | 0.00016461 | 84.3333
AEP-KYP | 2023 | 161642 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 2 | 2 | 280 | 0.0017322 | 1.2373e-05 | 140
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | OU | FUSE | 3 | 16 | 907 | 0.0056127 | 9.9011e-05 | 56.6875
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 8 | 1278 | 0.0079085 | 4.9505e-05 | 159.75
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | PEDESTAL | 2 | 4 | 347 | 0.0021473 | 2.4753e-05 | 86.75
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 120 | 3446 | 514923 | 3.1856 | 0.021319 | 149.4263
AEP-KYP | 2020 | 165077 | PARTIAL POWER | WU | FUSE | 3 | 14 | 3400 | 0.020596 | 8.4809e-05 | 242.8571
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | CONN/CLAMP | 3 | 260 | 15210 | 0.093878 | 0.0016048 | 58.5
AEP-KYP | 2022 | 162018 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 1 | 5 | 380 | 0.0023454 | 3.0861e-05 | 76
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 22 | 355 | 79476 | 0.49181 | 0.0021968 | 223.8761
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | OL | FUSE | 4 | 609 | 99844 | 0.61769 | 0.0037676 | 163.9475
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WL | FUSE | 25 | 190 | 25662 | 0.15545 | 0.001151 | 135.0632
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 726 | 0.004481 | 1.8516e-05 | 242
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | VA | FUSE | 3 | 32 | 2127 | 0.013162 | 0.00019802 | 66.4688
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 1 | 58 | 0.00035891 | 6.1882e-06 | 58
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | OU | NONE | 3 | 253 | 35549 | 0.21998 | 0.0015656 | 140.5099
AEP-KYP | 2024 | 161599 | TRANSMISSION STATION | SCO | NONE | 1 | 471 | 122540 | 0.7583 | 0.0029146 | 260.1699
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | EQF | POLE | 1 | 19 | 3116 | 0.019277 | 0.00011754 | 164
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | SWITCH, OH | 7 | 1674 | 62692 | 0.38795 | 0.010359 | 37.4504
AEP-KYP | 2024 | 161599 | TRANSMISSION STATION | F | NONE | 1 | 2632 | 55272 | 0.34203 | 0.016287 | 21
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | OL | FUSE | 2 | 13 | 813 | 0.005031 | 8.0446e-05 | 62.5385
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 37 | 6993 | 0.043274 | 0.00022896 | 189
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OU | FUSE | 1 | 1 | 28 | 0.00016962 | 6.0578e-06 | 28
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | FUSE | 1 | 41 | 1476 | 0.0091337 | 0.00025371 | 36
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | EQF | STATIC WIRE | 1 | 808 | 33128 | 0.20068 | 0.0048947 | 41
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 230 | 23460 | 0.14517 | 0.0014233 | 102
AEP-KYP | 2022 | 162018 | PARTIAL POWER | CE | SPLICE, OH | 1 | 4 | 552 | 0.003407 | 2.4689e-05 | 138
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | F | CROSSARM | 1 | 2 | 192 | 0.0011881 | 1.2376e-05 | 96
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 1 | 63 | 0.00038885 | 6.1722e-06 | 63
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 11 | 1485 | 0.0090537 | 6.7065e-05 | 135
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | AB | NONE | 2 | 1325 | 238526 | 1.4449 | 0.0080266 | 180.0196
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | POLE | 117 | 13618 | 4473111 | 27.6087 | 0.084052 | 328.4705
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 1 | 1301 | 0.00803 | 6.1722e-06 | 1301
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | NONE | 31 | 2404 | 362375 | 2.2366 | 0.014838 | 150.7384
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 16 | 427 | 308575 | 1.9046 | 0.0026355 | 722.6581
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | POLE | 32 | 6109 | 1377964 | 8.4011 | 0.037245 | 225.5629
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | A | FUSE | 303 | 1078 | 108273 | 0.65589 | 0.0065303 | 100.4388
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | FUSE | 145 | 1003 | 156325 | 0.94698 | 0.006076 | 155.8574
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CO | CONN/CLAMP | 5 | 8 | 1186 | 0.0072308 | 4.8774e-05 | 148.25
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 5 | 1120 | 0.0067847 | 3.0289e-05 | 224
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | POLE | 464 | 11673 | 1846939 | 11.4261 | 0.072215 | 158.2232
AEP-KYP | 2022 | 162018 | PARTIAL POWER | VIN | FUSE | 8 | 17 | 2722 | 0.016801 | 0.00010493 | 160.1176
AEP-KYP | 2021 | 164021 | PARTIAL POWER | WU | FUSE | 4 | 34 | 1677 | 0.010224 | 0.00020729 | 49.3235
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | STATIC WIRE | 2 | 37 | 3849 | 0.023757 | 0.00022837 | 104.027
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WW | POLE | 1 | 4 | 572 | 0.0034874 | 2.4387e-05 | 143
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 3 | 25 | 3157 | 0.019124 | 0.00015144 | 126.28
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WFS | TRANSFORMER, UG | 2 | 43 | 19530 | 0.12054 | 0.0002654 | 454.186
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 2 | 517 | 68771 | 0.42447 | 0.003191 | 133.0193
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 181 | 1380 | 400637 | 2.427 | 0.0083597 | 290.3167
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | A | NONE | 42 | 1244 | 138932 | 0.84162 | 0.0075359 | 111.6817
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FO | FUSE | 13 | 191 | 24747 | 0.15088 | 0.0011645 | 129.5654
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | NONE | 165 | 12630 | 1395172 | 8.6312 | 0.078136 | 110.4649
AEP-KYP | 2020 | 165077 | PARTIAL POWER | ABI | FUSE | 6 | 20 | 1217 | 0.0073723 | 0.00012116 | 60.85
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ERF | METERING | 5 | 5 | 386 | 0.0023534 | 3.0484e-05 | 77.2
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | SPLICE, OH | 9 | 16 | 3515 | 0.021746 | 9.8984e-05 | 219.6875
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | CUTOUT | 89 | 323 | 8118 | 0.050222 | 0.0019982 | 25.1331
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WL | NONE | 8 | 417 | 51568 | 0.31911 | 0.0025805 | 123.6643
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 27 | 332 | 74747 | 0.46255 | 0.0020545 | 225.1416
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 1 | 2 | 456 | 0.0027801 | 1.2194e-05 | 228
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | O | NONE | 21 | 2017 | 327681 | 1.985 | 0.012219 | 162.4596
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 6 | 924 | 41130 | 0.24916 | 0.0055974 | 44.513
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 5 | 69 | 27877 | 0.16887 | 0.00041799 | 404.0145
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 4 | 88 | 1241 | 0.0075661 | 0.00053652 | 14.1023
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | EQF | TRANSFORMER, STATION SERVICE | 2 | 1012 | 362814 | 2.1978 | 0.0061305 | 358.5119
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 3 | 739 | 0.004573 | 1.8564e-05 | 246.3333
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 1193 | 120984 | 0.74867 | 0.0073825 | 101.4116
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 20 | 673 | 111831 | 0.69184 | 0.0041635 | 166.1679
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | SCO | POLE | 1 | 324 | 1944 | 0.012027 | 0.0020044 | 6
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | INSULATOR | 13 | 1847 | 445013 | 2.7531 | 0.011426 | 240.9383
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 4 | 109 | 34959 | 0.21627 | 0.00067433 | 320.7248
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 83 | 190 | 25094 | 0.15529 | 0.0011757 | 132.0737
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ERO | NONE | 1 | 297 | 4752 | 0.02933 | 0.0018331 | 16
AEP-KYP | 2024 | 161599 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 9 | 25 | 5706 | 0.03531 | 0.0001547 | 228.24
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | CROSSARM | 10 | 223 | 24783 | 0.15336 | 0.00138 | 111.1345
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 8 | 632 | 137988 | 0.85389 | 0.0039109 | 218.3354
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | SCO | NONE | 3 | 183 | 26226 | 0.16229 | 0.0011324 | 143.3115
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | EQF | RELAY | 2 | 3242 | 644255 | 3.9028 | 0.019639 | 198.7215
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 216 | 0.0013363 | 6.1865e-06 | 216
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 43 | 20683 | 0.12799 | 0.00026609 | 481
AEP-KYP | 2025 | 161599 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 20 | 0.00012376 | 6.1882e-06 | 20
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FO | FUSE | 3 | 7 | 1373 | 0.0084963 | 4.3317e-05 | 196.1429
AEP-KYP | 2024 | 161599 | PARTIAL POWER | WU | FUSE | 2 | 2 | 229 | 0.0014171 | 1.2376e-05 | 114.5
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CE | NONE | 7 | 21 | 1269 | 0.0078528 | 0.00012995 | 60.4286
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | INSULATOR | 16 | 6011 | 670004 | 4.1461 | 0.037197 | 111.463
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 15 | 462 | 117005 | 0.72405 | 0.0028589 | 253.2576
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 114 | 26690 | 0.16512 | 0.00070526 | 234.1228
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 57 | 5415 | 0.0335 | 0.00035263 | 95
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | U | POLE | 2 | 276 | 117335 | 0.72609 | 0.0017079 | 425.1268
AEP-KYP | 2020 | 165077 | TRANSMISSION STATION | UG | NONE | 1 | 486 | 128790 | 0.78018 | 0.0029441 | 265
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 3 | 2991 | 0.018461 | 1.8516e-05 | 997
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 1490 | 27447 | 0.1698 | 0.0092179 | 18.4208
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FO | FUSE | 5 | 59 | 7207 | 0.044598 | 0.0003651 | 122.1525
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | TRANSFORMER, OH | 5 | 16 | 3552 | 0.021517 | 9.6924e-05 | 222
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 5 | 2160 | 0.013366 | 3.0941e-05 | 432
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 9 | 2574 | 0.015924 | 5.5679e-05 | 286
AEP-KYP | 2020 | 165077 | SUBTRANSMISSION LINE | TOR | NONE | 1 | 490 | 126588 | 0.76684 | 0.0029683 | 258.3429
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 9 | 324 | 0.0019627 | 5.452e-05 | 36
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | POLE | 1 | 1 | 157 | 0.00096903 | 6.1722e-06 | 157
AEP-KYP | 2020 | 165077 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 79 | 0.00047856 | 6.0578e-06 | 79
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | F | CUTOUT | 1 | 107 | 9416 | 0.058268 | 0.00066213 | 88
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | POLE | 81 | 2457 | 295705 | 1.8251 | 0.015165 | 120.3521
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | REGULATOR | 5 | 1230 | 153399 | 0.9468 | 0.0075917 | 124.7146
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | F | POLE | 7 | 2441 | 125034 | 0.77173 | 0.015066 | 51.2224
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 28 | 3932 | 1354838 | 8.3623 | 0.024269 | 344.5671
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 4 | 684 | 0.0041702 | 2.4387e-05 | 171
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | NONE | 101 | 13795 | 1208918 | 7.3705 | 0.084105 | 87.6345
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 120 | 11423 | 1903174 | 11.529 | 0.069198 | 166.6089
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WL | ARRESTER | 6 | 1389 | 51352 | 0.31308 | 0.0084684 | 36.9705
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | CROSSARM | 6 | 489 | 20599 | 0.12559 | 0.0029813 | 42.1247
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | CROSSARM | 9 | 364 | 28445 | 0.17557 | 0.0022467 | 78.1456
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 914 | 42605 | 13641497 | 84.3933 | 0.26358 | 320.1854
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 44 | 44364 | 0.27382 | 0.00027157 | 1008.2727
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 6 | 14 | 3022 | 0.018652 | 8.641e-05 | 215.8571
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CE | FUSE | 3 | 13 | 1934 | 0.011791 | 7.9258e-05 | 148.7692
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | CROSSARM | 17 | 1270 | 105597 | 0.6438 | 0.0077429 | 83.1472
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | POLE | 4 | 529 | 32151 | 0.19476 | 0.0032046 | 60.7769
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SO | NONE | 12 | 164 | 31373 | 0.19127 | 0.00099987 | 191.2988
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 2 | 52 | 10060 | 0.062236 | 0.0003217 | 193.4615
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 1 | 75 | 0.00046291 | 6.1722e-06 | 75
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | REGULATOR | 3 | 1358 | 36289 | 0.21983 | 0.0082265 | 26.7224
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | V | POLE | 1 | 132 | 48444 | 0.29346 | 0.00079963 | 367
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FO | NONE | 7 | 694 | 38268 | 0.23675 | 0.0042934 | 55.1412
AEP-KYP | 2023 | 161642 | PARTIAL POWER | O | NONE | 3 | 11 | 2083 | 0.012887 | 6.8052e-05 | 189.3636
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 4 | 512 | 0.0031675 | 2.4746e-05 | 128
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 1 | 408 | 0.0025241 | 6.1865e-06 | 408
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | F | OTHER EQUIPMENT | 1 | 1 | 207 | 0.001254 | 6.0578e-06 | 207
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 2 | 548 | 0.0033197 | 1.2116e-05 | 274
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | CROSSARM | 8 | 77 | 6476 | 0.03923 | 0.00046645 | 84.1039
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | METERING | 3 | 4 | 288 | 0.0017817 | 2.4746e-05 | 72
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 4 | 4 | 1292 | 0.007993 | 2.4746e-05 | 323
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | POLE | 30 | 1979 | 329096 | 2.0365 | 0.012246 | 166.2941
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | EQF | CAPACITOR | 3 | 2314 | 13884 | 0.084648 | 0.014108 | 6
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | METERING | 1 | 1 | 70 | 0.00043317 | 6.1882e-06 | 70
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 299 | 25769 | 0.15946 | 0.0018503 | 86.1839
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 1 | 14 | 3804 | 0.023533 | 8.6611e-05 | 271.7143
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | U | FUSE | 165 | 1215 | 199040 | 1.2317 | 0.0075186 | 163.8189
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 1 | 2 | 960 | 0.0059406 | 1.2376e-05 | 480
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | RECLOSER, LINE/OCR/BR | 1 | 493 | 204825 | 1.2675 | 0.0030508 | 415.4665
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | VA | POLE | 14 | 2398 | 252469 | 1.5623 | 0.014839 | 105.2832
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 2 | 468 | 0.0028953 | 1.2373e-05 | 234
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 1 | 523 | 0.0032364 | 6.1882e-06 | 523
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 2 | 206 | 0.0012559 | 1.2194e-05 | 103
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 6 | 3916 | 0.023722 | 3.6347e-05 | 652.6667
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | SWITCH, OH | 2 | 971 | 191586 | 1.1852 | 0.0060071 | 197.3079
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 4 | 14 | 4174 | 0.025829 | 8.6634e-05 | 298.1429
AEP-KYP | 2022 | 162018 | PARTIAL POWER | O | CONN/CLAMP | 1 | 1 | 1562 | 0.0096409 | 6.1722e-06 | 1562
AEP-KYP | 2021 | 164021 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 4 | 720 | 0.0043897 | 2.4387e-05 | 180
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TR | POLE | 2 | 23 | 14183 | 0.086471 | 0.00014023 | 616.6522
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SO | FUSE | 5 | 15 | 1383 | 0.0084318 | 9.1452e-05 | 92.2
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 86 | 8278 | 0.050146 | 0.00052097 | 96.2558
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 625 | 126146 | 0.77859 | 0.0038576 | 201.8336
AEP-KYP | 2022 | 162018 | PARTIAL POWER | UG | CONDUCTOR OVERHEAD | 1 | 1 | 163 | 0.0010061 | 6.1722e-06 | 163
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 149 | 4910 | 772383 | 4.7796 | 0.030384 | 157.3081
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | REGULATOR | 2 | 186 | 1536 | 0.0093047 | 0.0011267 | 8.2581
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | A | INSULATOR | 1 | 42 | 3276 | 0.019845 | 0.00025443 | 78
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | O | FUSE | 15 | 246 | 62308 | 0.37745 | 0.0014902 | 253.2846
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TIR | POLE | 5 | 58 | 47248 | 0.2923 | 0.00035882 | 814.6207
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 1 | 27 | 13392 | 0.08285 | 0.00016704 | 496
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | O | NONE | 15 | 1972 | 112882 | 0.69853 | 0.012203 | 57.2424
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | CUTOUT | 4 | 11 | 714 | 0.0044183 | 6.807e-05 | 64.9091
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 116 | 3398 | 552742 | 3.4205 | 0.021027 | 162.6669
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 10 | 2169 | 0.013139 | 6.0578e-05 | 216.9
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TR | POLE | 1 | 1 | 258 | 0.0015965 | 6.1882e-06 | 258
AEP-KYP | 2024 | 161599 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 4 | 4456 | 0.027574 | 2.4753e-05 | 1114
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | METERING | 1 | 2 | 312 | 0.0019307 | 1.2376e-05 | 156
AEP-KYP | 2020 | 165077 | PARTIAL POWER | O | CONN/CLAMP | 1 | 1 | 237 | 0.0014357 | 6.0578e-06 | 237
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | TRANSFORMER, OH | 1 | 3 | 1923 | 0.0119 | 1.8564e-05 | 641
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | POLE | 491 | 14721 | 2859585 | 17.6498 | 0.09086 | 194.2521
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | NONE | 363 | 12120 | 1493083 | 9.2155 | 0.074807 | 123.1917
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 11 | 43 | 5117 | 0.031656 | 0.00026602 | 119
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | A | FUSE | 229 | 946 | 86429 | 0.53345 | 0.0058389 | 91.3626
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | CONN/CLAMP | 67 | 251 | 51662 | 0.31887 | 0.0015492 | 205.8247
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 55 | 508 | 27773 | 0.16933 | 0.0030972 | 54.6713
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | NONE | 53 | 4720 | 839247 | 5.18 | 0.029133 | 177.8066
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 136 | 38188 | 0.2357 | 0.00083941 | 280.7941
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | A | FUSE | 215 | 784 | 82380 | 0.50225 | 0.0047799 | 105.0765
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 19 | 2034 | 297827 | 1.8042 | 0.012322 | 146.4243
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 15 | 115 | 5780 | 0.035675 | 0.0007098 | 50.2609
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 16 | 144 | 75103 | 0.45496 | 0.00087232 | 521.5486
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ABI | FUSE | 65 | 220 | 22714 | 0.1376 | 0.0013327 | 103.2455
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CE | NONE | 16 | 92 | 7336 | 0.045279 | 0.00056784 | 79.7391
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | POLE | 130 | 6785 | 3627147 | 22.4394 | 0.041975 | 534.5832
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | INSULATOR | 7 | 62 | 3771 | 0.023329 | 0.00038356 | 60.8226
AEP-KYP | 2023 | 161642 | PARTIAL POWER | WFS | CONDUCTOR OVERHEAD | 1 | 1 | 54 | 0.00033407 | 6.1865e-06 | 54
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 14 | 27 | 804 | 0.004974 | 0.00016704 | 29.7778
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VIN | FUSE | 245 | 964 | 132796 | 0.82176 | 0.0059654 | 137.7552
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 1 | 307 | 0.0018949 | 6.1722e-06 | 307
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 229 | 7767 | 0.047051 | 0.0013872 | 33.917
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 1 | 1 | 822 | 0.0050735 | 6.1722e-06 | 822
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 8 | 246 | 35494 | 0.21501 | 0.0014902 | 144.2846
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | CROSSARM | 16 | 5733 | 522427 | 3.2329 | 0.035477 | 91.1263
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 53 | 2078 | 478742 | 2.9617 | 0.012856 | 230.3859
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CF | POLE | 1 | 7 | 3731 | 0.023082 | 4.3306e-05 | 533
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | CONN/CLAMP | 4 | 12 | 531 | 0.003285 | 7.4238e-05 | 44.25
AEP-KYP | 2023 | 161642 | TRANSMISSION STATION | ERF | NONE | 4 | 3112 | 44531 | 0.27549 | 0.019252 | 14.3094
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | ARRESTER | 39 | 2169 | 315502 | 1.9524 | 0.013422 | 145.4597
AEP-KYP | 2023 | 161642 | PARTIAL POWER | CO | CONN/CLAMP | 7 | 11 | 1186 | 0.0073372 | 6.8052e-05 | 107.8182
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 63 | 1209 | 193995 | 1.2005 | 0.0074815 | 160.4591
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CE | NONE | 6 | 53 | 5051 | 0.030795 | 0.00032313 | 95.3019
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | A | POLE | 1 | 907 | 18140 | 0.10989 | 0.0054944 | 20
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 34 | 1904 | 0.011782 | 0.0002104 | 56
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | OU | POLE | 1 | 63 | 10311 | 0.063789 | 0.00038975 | 163.6667
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 2 | 11 | 383 | 0.0023694 | 6.8052e-05 | 34.8182
AEP-KYP | 2024 | 161599 | PARTIAL POWER | ABI | FUSE | 5 | 9 | 736 | 0.0045545 | 5.5693e-05 | 81.7778
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 15 | 5580 | 0.034521 | 9.2798e-05 | 372
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 161 | 4186 | 0.025358 | 0.0009753 | 26
AEP-KYP | 2021 | 164021 | DISTRIBUTION STATION | SCO | TRANSFORMER, OH | 1 | 1 | 40 | 0.00024387 | 6.0968e-06 | 40
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 389 | 8947 | 0.054199 | 0.0023565 | 23
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | SPLICE, OH | 23 | 1415 | 103958 | 0.64331 | 0.0087562 | 73.4686
AEP-KYP | 2022 | 162018 | PARTIAL POWER | U | NONE | 1 | 1 | 26 | 0.00016048 | 6.1722e-06 | 26
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ABI | NONE | 4 | 13 | 1326 | 0.0082033 | 8.0425e-05 | 102
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 16 | 1686 | 148933 | 0.92138 | 0.01043 | 88.3351
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 21 | 588 | 74218 | 0.45915 | 0.0036377 | 126.2211
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | OU | NONE | 5 | 178 | 4775 | 0.029541 | 0.0011012 | 26.8258
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | SWITCH, OH | 5 | 1532 | 179500 | 1.0874 | 0.0092805 | 117.1671
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | F | NONE | 8 | 3177 | 340785 | 2.1083 | 0.019655 | 107.2663
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 2 | 7 | 494 | 0.0030561 | 4.3306e-05 | 70.5714
AEP-KYP | 2023 | 161642 | PARTIAL POWER | A | FUSE | 2 | 6 | 754 | 0.0046646 | 3.7119e-05 | 125.6667
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WI | TRANSFORMER, OH | 1 | 16 | 4288 | 0.026466 | 9.8754e-05 | 268
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CO | FUSE | 5 | 14 | 1637 | 0.01013 | 8.6634e-05 | 116.9286
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | O | NONE | 3 | 2630 | 205625 | 1.2691 | 0.016233 | 78.1844
AEP-KYP | 2022 | 162018 | PARTIAL POWER | CO | SPLICE, OH | 1 | 10 | 1550 | 0.0095668 | 6.1722e-05 | 155
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 2 | 9 | 890 | 0.005506 | 5.5679e-05 | 98.8889
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 15 | 1328 | 0.0082157 | 9.2798e-05 | 88.5333
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WL | POLE | 1 | 16 | 3244 | 0.020022 | 9.8754e-05 | 202.75
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WW | CIRCUIT SWITCHER | 1 | 18 | 20412 | 0.12365 | 0.00010904 | 1134
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 397 | 0.0024567 | 1.2376e-05 | 198.5
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 7 | 3863 | 0.023905 | 4.3317e-05 | 551.8571
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 72 | 632 | 219703 | 1.3596 | 0.0039109 | 347.6313
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 3 | 6 | 4662 | 0.028849 | 3.7129e-05 | 777
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | FUSE | 7 | 20 | 15385 | 0.095205 | 0.00012376 | 769.25
AEP-KYP | 2025 | 161599 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 1 | 1119 | 226038 | 1.3988 | 0.0069245 | 202
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ABI | FUSE | 8 | 28 | 2445 | 0.01513 | 0.00017327 | 87.3214
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | POLE | 7 | 105 | 102560 | 0.62529 | 0.00064016 | 976.7619
AEP-KYP | 2021 | 164021 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 56 | 0.00034142 | 6.0968e-06 | 56
AEP-KYP | 2020 | 165077 | PARTIAL POWER | O | FUSE | 1 | 5 | 300 | 0.0018173 | 3.0289e-05 | 60
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 1 | 4 | 460 | 0.0027866 | 2.4231e-05 | 115
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TR | NONE | 1 | 7 | 315 | 0.0019082 | 4.2404e-05 | 45
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TR | NONE | 3 | 276 | 9836 | 0.060867 | 0.0017079 | 35.6377
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | METERING | 1 | 6 | 54 | 0.00033416 | 3.7129e-05 | 9
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | CE | FUSE | 1 | 5 | 490 | 0.0030322 | 3.0941e-05 | 98
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | O | BREAKER | 1 | 2 | 194 | 0.0011752 | 1.2116e-05 | 97
AEP-KYP | 2024 | 161599 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 370 | 51800 | 0.32055 | 0.0022896 | 140
AEP-KYP | 2023 | 161642 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 272 | 0.0016827 | 6.1865e-06 | 272
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ABI | SPLICE, OH | 1 | 1 | 130 | 0.00080446 | 6.1882e-06 | 130
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ABI | FUSE | 41 | 117 | 10900 | 0.067276 | 0.00072214 | 93.1624
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 1 | 86 | 0.00053218 | 6.1882e-06 | 86
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 2 | 254 | 0.0015714 | 1.2373e-05 | 127
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | CIRCUIT SWITCHER | 1 | 1618 | 140766 | 0.85273 | 0.0098015 | 87
AEP-KYP | 2024 | 161599 | PARTIAL POWER | O | CONDUCTOR UG | 1 | 1 | 315 | 0.0019493 | 6.1882e-06 | 315
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 197 | 47083 | 0.28705 | 0.0012011 | 239
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 4 | 549 | 23652 | 0.14636 | 0.0033973 | 43.082
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | EQF | CROSSARM | 4 | 2770 | 29038 | 0.17964 | 0.017137 | 10.483
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | CROSSARM | 1 | 789 | 85212 | 0.5162 | 0.0047796 | 108
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | SCO | INSULATOR | 1 | 147 | 5733 | 0.035477 | 0.00090966 | 39
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 63 | 0.00038975 | 6.1865e-06 | 63
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TIR | FUSE | 9 | 149 | 25783 | 0.15955 | 0.00092204 | 173.0403
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 1 | 11 | 770 | 0.0047649 | 6.807e-05 | 70
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | AF | OTHER EQUIPMENT | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | CUTOUT | 4 | 11 | 146 | 0.00090347 | 6.807e-05 | 13.2727
AEP-KYP | 2023 | 161642 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 1 | 83 | 0.00051348 | 6.1865e-06 | 83
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | SECTIONALIZER | 1 | 2 | 4246 | 0.026275 | 1.2376e-05 | 2123
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 2 | 577 | 0.0035706 | 1.2376e-05 | 288.5
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CE | PEDESTAL | 1 | 12 | 840 | 0.0051981 | 7.4258e-05 | 70
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 166 | 54394 | 0.32951 | 0.0010056 | 327.6747
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | NONE | 348 | 40450 | 7330878 | 45.2473 | 0.24966 | 181.2331
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | CUTOUT | 70 | 2210 | 187082 | 1.1547 | 0.01364 | 84.6525
AEP-KYP | 2022 | 162018 | PARTIAL POWER | CO | CONN/CLAMP | 14 | 37 | 5543 | 0.034212 | 0.00022837 | 149.8108
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 148 | 1364 | 288261 | 1.7575 | 0.008316 | 211.335
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 4 | 7 | 1060 | 0.0065425 | 4.3205e-05 | 151.4286
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | FUSE | 13 | 56 | 2327 | 0.014187 | 0.00034142 | 41.5536
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 299 | 92871 | 0.56621 | 0.0018229 | 310.6054
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WI | NONE | 97 | 2081 | 2214708 | 13.5026 | 0.012687 | 1064.2518
AEP-KYP | 2022 | 162018 | PARTIAL POWER | U | CONN/CLAMP | 2 | 5 | 6171 | 0.038088 | 3.0861e-05 | 1234.2
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 2 | 78 | 0.00048255 | 1.2373e-05 | 39
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 4 | 85 | 20154 | 0.12209 | 0.00051491 | 237.1059
AEP-KYP | 2023 | 161642 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 2 | 1819 | 187439 | 1.1596 | 0.011253 | 103.0451
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | POLE | 73 | 2935 | 302995 | 1.875 | 0.018162 | 103.2351
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OU | NONE | 2 | 11 | 1449 | 0.0087777 | 6.6636e-05 | 131.7273
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 10 | 6247 | 0.038647 | 6.1865e-05 | 624.7
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WL | ARRESTER | 5 | 25 | 4269 | 0.025861 | 0.00015144 | 170.76
AEP-KYP | 2024 | 161599 | PARTIAL POWER | WL | NONE | 1 | 1 | 53 | 0.00032797 | 6.1882e-06 | 53
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | V | NONE | 6 | 152 | 34702 | 0.21474 | 0.0009406 | 228.3026
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 132 | 17772 | 0.10835 | 0.00080477 | 134.6364
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | AF | NONE | 3 | 74 | 17242 | 0.10445 | 0.00044828 | 233
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 1 | 1 | 13 | 8.0446e-05 | 6.1882e-06 | 13
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 25 | 877 | 314361 | 1.9453 | 0.005427 | 358.4504
AEP-KYP | 2021 | 164021 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 85 | 0.00051823 | 6.0968e-06 | 85
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | METERING | 2 | 303 | 11284 | 0.068356 | 0.0018355 | 37.2409
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 1 | 1 | 948 | 0.0058664 | 6.1882e-06 | 948
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | ARRESTER | 11 | 1690 | 174089 | 1.0773 | 0.010458 | 103.0112
AEP-KYP | 2023 | 161642 | PARTIAL POWER | U | NONE | 4 | 6 | 705 | 0.0043615 | 3.7119e-05 | 117.5
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CO | POLE | 1 | 1 | 615 | 0.0037255 | 6.0578e-06 | 615
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 2 | 224 | 0.0013657 | 1.2194e-05 | 112
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 16 | 1626 | 0.0098499 | 9.6924e-05 | 101.625
AEP-KYP | 2020 | 165077 | PARTIAL POWER | FO | FUSE | 1 | 1 | 157 | 0.00095107 | 6.0578e-06 | 157
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 2 | 144 | 0.00089109 | 1.2376e-05 | 72
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | CUTOUT | 2 | 8 | 1262 | 0.0078095 | 4.9505e-05 | 157.75
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 46 | 9764 | 0.060421 | 0.00028466 | 212.2609
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 2 | 2080 | 0.012871 | 1.2376e-05 | 1040
AEP-KYP | 2024 | 161599 | TRANSMISSION LINE | ERO | NONE | 3 | 1810 | 373225 | 2.3096 | 0.011201 | 206.2017
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | POLE | 1 | 9 | 738 | 0.0044994 | 5.4871e-05 | 82
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 26 | 0.0001575 | 6.0578e-06 | 26
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | CUTOUT | 647 | 2302 | 100774 | 0.62199 | 0.014208 | 43.7767
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | A | NONE | 29 | 416 | 71441 | 0.44094 | 0.0025676 | 171.7332
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WFS | TRANSFORMER, OH | 3 | 6 | 10216 | 0.063055 | 3.7033e-05 | 1702.6667
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SO | NONE | 9 | 969 | 67369 | 0.41581 | 0.0059808 | 69.5243
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | POLE | 47 | 7824 | 1321385 | 8.1558 | 0.048291 | 168.8887
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | NONE | 467 | 9447 | 1399746 | 8.4794 | 0.057228 | 148.1683
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 99 | 230 | 18617 | 0.11278 | 0.0013933 | 80.9435
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CE | BREAKER | 1 | 8 | 1216 | 0.0074137 | 4.8774e-05 | 152
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 3 | 82 | 19552 | 0.1192 | 0.00049994 | 238.439
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | JUMPER/RISER | 4 | 23 | 2013 | 0.012194 | 0.00013933 | 87.5217
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | V | NONE | 9 | 11 | 1008 | 0.0062215 | 6.7894e-05 | 91.6364
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 121 | 3158 | 414374 | 2.5635 | 0.019537 | 131.2141
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 1 | 239 | 0.0014751 | 6.1722e-06 | 239
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | V | METERING | 6 | 6 | 514 | 0.0031337 | 3.6581e-05 | 85.6667
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | O | FUSE | 10 | 105 | 15066 | 0.091854 | 0.00064016 | 143.4857
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | POLE | 8 | 111 | 71283 | 0.43997 | 0.00068511 | 642.1892
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VIN | CUTOUT | 4 | 332 | 56147 | 0.34655 | 0.0020492 | 169.1175
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | SPLICE, OH | 18 | 41 | 3890 | 0.023565 | 0.00024837 | 94.878
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | FUSE | 27 | 135 | 7644 | 0.04729 | 0.00083518 | 56.6222
AEP-KYP | 2020 | 165077 | DISTRIBUTION STATION | SCO | NONE | 3 | 4006 | 43706 | 0.26476 | 0.024267 | 10.9101
AEP-KYP | 2022 | 162018 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 153 | 0.00094434 | 6.1722e-06 | 153
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1274 | 59129 | 16328514 | 101.0434 | 0.3659 | 276.1507
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 5 | 69 | 38796 | 0.23653 | 0.00042068 | 562.2609
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 992 | 411562 | 2.5461 | 0.006137 | 414.881
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | FUSE | 9 | 33 | 2627 | 0.015914 | 0.00019991 | 79.6061
AEP-KYP | 2021 | 164021 | PARTIAL POWER | CE | FUSE | 1 | 1 | 90 | 0.00054871 | 6.0968e-06 | 90
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | O | POLE | 4 | 226 | 165693 | 1.0102 | 0.0013779 | 733.1549
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 20 | 1036 | 105201 | 0.64139 | 0.0063163 | 101.5454
AEP-KYP | 2021 | 164021 | PARTIAL POWER | FO | FUSE | 2 | 4 | 3289 | 0.020052 | 2.4387e-05 | 822.25
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 7 | 1157 | 0.0070089 | 4.2404e-05 | 165.2857
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | NONE | 773 | 14522 | 1519232 | 9.3987 | 0.089841 | 104.6159
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 217 | 0.001323 | 6.0968e-06 | 217
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 127 | 56535 | 0.34894 | 0.00078386 | 445.1575
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CO | CONN/CLAMP | 4 | 6 | 434 | 0.0026787 | 3.7033e-05 | 72.3333
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | SWITCH, OH | 5 | 227 | 54492 | 0.33712 | 0.0014043 | 240.0529
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 3 | 17 | 3111 | 0.019246 | 0.00010517 | 183
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 9 | 84 | 55451 | 0.34314 | 0.00051981 | 660.131
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 1 | 75 | 0.00046411 | 6.1882e-06 | 75
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | A | FUSE | 39 | 134 | 10096 | 0.062476 | 0.00082921 | 75.3433
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | FUSE | 1 | 2 | 118 | 0.0007302 | 1.2376e-05 | 59
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | POLE | 54 | 3997 | 1455064 | 9.0042 | 0.024734 | 364.039
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WFS | POLE | 23 | 1789 | 325891 | 2.0167 | 0.011071 | 182.1638
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 7 | 84 | 12123 | 0.075019 | 0.00051981 | 144.3214
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | CROSSARM | 34 | 975 | 140901 | 0.86966 | 0.0060178 | 144.5138
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | FUSE | 97 | 812 | 180384 | 1.1134 | 0.0050118 | 222.1478
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 9 | 3625 | 725198 | 4.476 | 0.022374 | 200.0546
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | CUTOUT | 21 | 137 | 85976 | 0.53066 | 0.00084559 | 627.562
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 37 | 14282 | 0.088151 | 0.00022837 | 386
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | ARRESTER | 48 | 1187 | 153445 | 0.92954 | 0.0071906 | 129.2713
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 11 | 5412 | 0.033404 | 6.7894e-05 | 492
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | NONE | 110 | 2359 | 280527 | 1.6994 | 0.01429 | 118.9178
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 2154 | 242616 | 1.4697 | 0.013048 | 112.6351
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 20 | 408 | 113551 | 0.68787 | 0.0024716 | 278.3113
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 8 | 40 | 3936 | 0.023843 | 0.00024231 | 98.4
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | INSULATOR | 44 | 9509 | 1430600 | 8.7221 | 0.057974 | 150.4469
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 5 | 12 | 2472 | 0.015071 | 7.3161e-05 | 206
AEP-KYP | 2022 | 162018 | PARTIAL POWER | O | METERING | 1 | 2 | 218 | 0.0013455 | 1.2344e-05 | 109
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | NONE | 56 | 2768 | 351430 | 2.1426 | 0.016876 | 126.9617
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 12 | 1800 | 350258 | 2.1354 | 0.010974 | 194.5878
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 5 | 24 | 2896 | 0.017875 | 0.00014813 | 120.6667
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | ARRESTER | 2 | 5 | 1740 | 0.01074 | 3.0861e-05 | 348
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WL | FUSE | 1 | 2 | 572 | 0.0035305 | 1.2344e-05 | 286
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 2 | 48 | 0.00029695 | 1.2373e-05 | 24
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ABI | SPLICE, OH | 3 | 1022 | 86943 | 0.53787 | 0.0063226 | 85.0714
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 1 | 3 | 504 | 0.0031108 | 1.8516e-05 | 168
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WFS | NONE | 8 | 695 | 136925 | 0.82946 | 0.0042102 | 197.0144
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CE | FUSE | 5 | 12 | 819 | 0.005055 | 7.4066e-05 | 68.25
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | SECTIONALIZER | 1 | 22 | 2596 | 0.015827 | 0.00013413 | 118
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ABI | NONE | 4 | 111 | 9148 | 0.055773 | 0.00067674 | 82.4144
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 1 | 168 | 0.0010369 | 6.1722e-06 | 168
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 4 | 180 | 0.001111 | 2.4689e-05 | 45
AEP-KYP | 2022 | 162018 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 2 | 8 | 498 | 0.0030737 | 4.9377e-05 | 62.25
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TOR | ARRESTER | 3 | 71 | 33897 | 0.2097 | 0.00043924 | 477.4225
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | NONE | 63 | 10303 | 1322924 | 8.1865 | 0.063757 | 128.4018
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 36 | 509 | 189418 | 1.1721 | 0.0031498 | 372.1375
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SO | NONE | 11 | 90 | 28055 | 0.17361 | 0.00055693 | 311.7222
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 18 | 450 | 0.0027775 | 0.0001111 | 25
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | A | CUTOUT | 5 | 20 | 3026 | 0.01872 | 0.00012373 | 151.3
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | CONDUCTOR UG | 6 | 12 | 2890 | 0.017838 | 7.4066e-05 | 240.8333
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 307 | 114511 | 0.70678 | 0.0018949 | 373
AEP-KYP | 2023 | 161642 | TRANSMISSION LINE | F | POLE | 1 | 9 | 5837 | 0.036111 | 5.5679e-05 | 648.5556
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | UG | NONE | 1 | 3 | 360 | 0.0021808 | 1.8173e-05 | 120
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | FW | NONE | 1 | 12 | 3850 | 0.023322 | 7.2693e-05 | 320.8333
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | METERING | 3 | 3 | 419 | 0.0025382 | 1.8173e-05 | 139.6667
AEP-KYP | 2020 | 165077 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 2 | 3 | 416 | 0.00252 | 1.8173e-05 | 138.6667
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 4 | 152 | 19393 | 0.11998 | 0.00094035 | 127.5855
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 17 | 608 | 0.0037614 | 0.00010517 | 35.7647
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TIR | CUTOUT | 2 | 3 | 1181 | 0.0073063 | 1.856e-05 | 393.6667
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | V | CUTOUT | 1 | 57 | 4047 | 0.025043 | 0.00035272 | 71
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 2 | 8 | 8160 | 0.050495 | 4.9505e-05 | 1020
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | ARRESTER | 3 | 6 | 150 | 0.00090867 | 3.6347e-05 | 25
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WW | FUSE | 4 | 46 | 27644 | 0.17107 | 0.00028466 | 600.9565
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 62 | 42284 | 0.2578 | 0.000378 | 682
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 146 | 38544 | 0.23845 | 0.00090323 | 264
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | UB | FUSE | 1 | 10 | 1180 | 0.0071482 | 6.0578e-05 | 118
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | SWITCH, OH | 4 | 1388 | 29784 | 0.18042 | 0.0084082 | 21.4582
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | POLE | 41 | 11210 | 1352879 | 8.1954 | 0.067908 | 120.685
AEP-KYP | 2023 | 161642 | PARTIAL POWER | U | FUSE | 25 | 72 | 5665 | 0.035047 | 0.00044543 | 78.6806
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 108 | 33264 | 0.20531 | 0.00066659 | 308
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 87 | 0.00052703 | 6.0578e-06 | 87
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 1 | 11 | 6.8052e-05 | 6.1865e-06 | 11
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | PEDESTAL | 2 | 23 | 3927 | 0.024301 | 0.00014233 | 170.7391
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | FUSE | 58 | 435 | 81957 | 0.50716 | 0.0026918 | 188.4069
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 5 | 119 | 44329 | 0.27431 | 0.00073639 | 372.5126
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TR | NONE | 5 | 12 | 4396 | 0.027203 | 7.4258e-05 | 366.3333
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 2 | 415 | 95529 | 0.59115 | 0.0025681 | 230.1904
AEP-KYP | 2021 | 164021 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 1 | 194 | 0.0011828 | 6.0968e-06 | 194
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | EQF | SPLICE, OH | 1 | 3 | 2421 | 0.014666 | 1.8173e-05 | 807
AEP-KYP | 2020 | 165077 | TRANSMISSION LINE | VA | NONE | 2 | 5 | 813 | 0.004925 | 3.0289e-05 | 162.6
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | INSULATOR | 2 | 31 | 1975 | 0.012222 | 0.00019183 | 63.7097
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | F | NONE | 2 | 1212 | 391563 | 2.3873 | 0.0073893 | 323.0718
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 17 | 2227 | 0.013578 | 0.00010365 | 131
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | JUMPER/RISER | 3 | 5 | 977 | 0.0060458 | 3.0941e-05 | 195.4
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 2 | 495 | 13860 | 0.085768 | 0.0030631 | 28
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | ERO | NONE | 1 | 1 | 14 | 8.6634e-05 | 6.1882e-06 | 14
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | A | ARRESTER | 2 | 1172 | 38688 | 0.23941 | 0.0072525 | 33.0102
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CO | NONE | 1 | 5 | 995 | 0.0061413 | 3.0861e-05 | 199
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 5 | 151 | 0.00092061 | 3.0484e-05 | 30.2
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WFS | NONE | 1 | 2 | 27 | 0.00016708 | 1.2376e-05 | 13.5
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | CUTOUT | 1 | 23 | 2257 | 0.01376 | 0.00014023 | 98.1304
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 1 | 239 | 12473 | 0.077185 | 0.001479 | 52.1883
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ERF | NONE | 10 | 889 | 33739 | 0.20824 | 0.005487 | 37.9516
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 17 | 190 | 35118 | 0.21411 | 0.0011584 | 184.8316
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 7 | 399 | 0.0024627 | 4.3205e-05 | 57
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WFS | FUSE | 1 | 1 | 525 | 0.0032008 | 6.0968e-06 | 525
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 37 | 9139 | 0.056554 | 0.00022896 | 247
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CE | FUSE | 1 | 1 | 186 | 0.0011267 | 6.0578e-06 | 186
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | METERING | 3 | 3 | 301 | 0.0018578 | 1.8516e-05 | 100.3333
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 13 | 1150 | 252321 | 1.5574 | 0.007098 | 219.4096
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 12 | 3655 | 0.022559 | 7.4066e-05 | 304.5833
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VIN | NONE | 33 | 302 | 56045 | 0.34592 | 0.001864 | 185.5795
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FO | FUSE | 5 | 35 | 2831 | 0.017473 | 0.00021603 | 80.8857
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 21 | 83 | 63904 | 0.38961 | 0.00050603 | 769.9277
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WU | NONE | 37 | 6043 | 833401 | 5.0811 | 0.036843 | 137.9118
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | ERO | POLE | 1 | 118 | 31947 | 0.19477 | 0.00071942 | 270.7373
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | CROSSARM | 17 | 2904 | 299275 | 1.8129 | 0.017592 | 103.0561
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SO | NONE | 28 | 909 | 196481 | 1.1902 | 0.0055065 | 216.1507
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | INSULATOR | 11 | 190 | 68180 | 0.42082 | 0.0011727 | 358.8421
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 5 | 19 | 298 | 0.0018052 | 0.0001151 | 15.6842
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | INSULATOR | 13 | 912 | 151119 | 0.92134 | 0.0055603 | 165.7007
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 9 | 9498 | 0.058623 | 5.5549e-05 | 1055.3333
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 16 | 9118 | 0.055235 | 9.6924e-05 | 569.875
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | VA | CUTOUT | 4 | 575 | 37124 | 0.22914 | 0.003549 | 64.5635
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 4 | 512 | 0.0031601 | 2.4689e-05 | 128
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | A | CUTOUT | 2 | 2 | 227 | 0.0014011 | 1.2344e-05 | 113.5
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FO | NONE | 3 | 348 | 9968 | 0.060773 | 0.0021217 | 28.6437
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TIR | NONE | 39 | 1593 | 243787 | 1.5082 | 0.0098551 | 153.0364
AEP-KYP | 2021 | 164021 | PARTIAL POWER | VA | POLE | 1 | 5 | 1215 | 0.0074076 | 3.0484e-05 | 243
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 11 | 504 | 212674 | 1.2883 | 0.0030531 | 421.9722
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WI | NONE | 16 | 230 | 340034 | 2.0599 | 0.0013933 | 1478.4087
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 6 | 1668 | 0.010104 | 3.6347e-05 | 278
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 13 | 355 | 111373 | 0.68901 | 0.0021962 | 313.7268
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 17 | 2550 | 0.015776 | 0.00010517 | 150
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CE | METERING | 1 | 2 | 682 | 0.004158 | 1.2194e-05 | 341
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WW | FUSE | 16 | 189 | 62899 | 0.38923 | 0.0011696 | 332.7989
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 6 | 10 | 562 | 0.0034264 | 6.0968e-05 | 56.2
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 4 | 18 | 1044 | 0.0064587 | 0.00011136 | 58
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 7 | 28 | 4821 | 0.029825 | 0.00017322 | 172.1786
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 215 | 14530 | 0.089914 | 0.0013305 | 67.5814
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 3 | 99 | 0.00061104 | 1.8516e-05 | 33
AEP-KYP | 2023 | 161642 | PARTIAL POWER | VIN | FUSE | 5 | 17 | 1606 | 0.0099355 | 0.00010517 | 94.4706
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OL | NONE | 3 | 6 | 3109 | 0.018834 | 3.6347e-05 | 518.1667
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | FUSE | 150 | 1180 | 149560 | 0.92311 | 0.0072831 | 126.7458
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WL | NONE | 8 | 1181 | 166472 | 1.0275 | 0.0072893 | 140.9585
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SO | CUTOUT | 1 | 1 | 172 | 0.0010616 | 6.1722e-06 | 172
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 228 | 0.0014073 | 6.1722e-06 | 228
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | CONN/CLAMP | 88 | 221 | 20003 | 0.12375 | 0.0013672 | 90.5113
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | UB | SPLICE, OH | 1 | 246 | 79212 | 0.48294 | 0.0014998 | 322
AEP-KYP | 2022 | 162018 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 1 | 29 | 836 | 0.0051599 | 0.00017899 | 28.8276
AEP-KYP | 2022 | 162018 | PARTIAL POWER | CE | FUSE | 1 | 1 | 68 | 0.00041971 | 6.1722e-06 | 68
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FO | CUTOUT | 2 | 13 | 338 | 0.0020475 | 7.8751e-05 | 26
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | CO | POLE | 2 | 143 | 15140 | 0.093446 | 0.00088262 | 105.8741
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | POLE | 3 | 52 | 39679 | 0.24547 | 0.0003217 | 763.0577
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | O | FUSE | 7 | 34 | 3976 | 0.024598 | 0.00021034 | 116.9412
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 8 | 17 | 607 | 0.0037465 | 0.00010493 | 35.7059
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 1 | 1 | 52 | 0.000315 | 6.0578e-06 | 52
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TR | FUSE | 10 | 110 | 12869 | 0.079635 | 0.0006807 | 116.9909
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 204 | 32699 | 0.20235 | 0.0012624 | 160.2892
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERO | NONE | 6 | 51 | 8002 | 0.049518 | 0.0003156 | 156.902
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 2 | 13 | 3582 | 0.022166 | 8.0446e-05 | 275.5385
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | UG | FUSE | 1 | 6 | 834 | 0.0051476 | 3.7033e-05 | 139
AEP-KYP | 2023 | 161642 | PARTIAL POWER | TIR | CONN/CLAMP | 2 | 6 | 1014 | 0.0062731 | 3.7119e-05 | 169
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | METERING | 2 | 4 | 1552 | 0.009604 | 2.4753e-05 | 388
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FO | POLE | 1 | 9 | 2565 | 0.015868 | 5.5679e-05 | 285
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 14 | 3710 | 0.022958 | 8.6634e-05 | 265
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 1 | 607 | 0.0036771 | 6.0578e-06 | 607
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 14 | 3134 | 0.018985 | 8.4809e-05 | 223.8571
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 8 | 1576 | 0.0095471 | 4.8462e-05 | 197
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | EQF | CIRCUIT SWITCHER | 1 | 3 | 57 | 0.00034752 | 1.829e-05 | 19
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 5 | 365 | 0.0022587 | 3.0941e-05 | 73
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | SPLICE, OH | 5 | 7 | 536 | 0.0033169 | 4.3317e-05 | 76.5714
AEP-KYP | 2025 | 161599 | PARTIAL POWER | CO | CONDUCTOR UG | 1 | 1 | 537 | 0.003323 | 6.1882e-06 | 537
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | V | POLE | 2 | 21 | 9483 | 0.058682 | 0.00012995 | 451.5714
AEP-KYP | 2022 | 162018 | PARTIAL POWER | TOR | POLE | 1 | 7 | 4445 | 0.027435 | 4.3205e-05 | 635
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 199 | 39203 | 0.24253 | 0.0012311 | 197
AEP-KYP | 2023 | 161642 | DISTRIBUTION STATION | ERO | BREAKER | 1 | 1644 | 274548 | 1.6985 | 0.010171 | 167
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 2 | 1066 | 0.0065966 | 1.2376e-05 | 533
AEP-KYP | 2020 | 165077 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 261 | 0.0015811 | 6.0578e-06 | 261
AEP-KYP | 2024 | 161599 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 1 | 4 | 3120 | 0.019307 | 2.4753e-05 | 780
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WU | FUSE | 165 | 2106 | 441675 | 2.6928 | 0.01284 | 209.7222
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VIN | NONE | 26 | 567 | 80835 | 0.49283 | 0.0034569 | 142.5661
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 1 | 119 | 0.00073449 | 6.1722e-06 | 119
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | CROSSARM | 33 | 10400 | 2259125 | 13.6853 | 0.063001 | 217.2236
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | FUSE | 6 | 25 | 2442 | 0.014793 | 0.00015144 | 97.68
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | FUSE | 8 | 82 | 8089 | 0.049317 | 0.00049994 | 98.6463
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | PEDESTAL | 1 | 5 | 155 | 0.000945 | 3.0484e-05 | 31
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | OL | NONE | 2 | 7 | 760 | 0.0046908 | 4.3205e-05 | 108.5714
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 1 | 102 | 8058 | 0.049128 | 0.00062187 | 79
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | PEDESTAL | 2 | 7 | 256 | 0.0015508 | 4.2404e-05 | 36.5714
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 108 | 265 | 29009 | 0.17946 | 0.0016394 | 109.4679
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | UG | FUSE | 1 | 26 | 728 | 0.0044385 | 0.00015852 | 28
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 3 | 136 | 15007 | 0.092626 | 0.00083941 | 110.3456
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 2 | 94 | 0.00058018 | 1.2344e-05 | 47
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | ERF | FUSE | 4 | 8 | 1208 | 0.0073178 | 4.8462e-05 | 151
AEP-KYP | 2022 | 162018 | TRANSMISSION STATION | SCO | NONE | 3 | 1581 | 85655 | 0.52868 | 0.0097582 | 54.1777
AEP-KYP | 2022 | 162018 | TRANSMISSION LINE | ERF | NONE | 1 | 264 | 14256 | 0.08799 | 0.0016294 | 54
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FO | FUSE | 9 | 173 | 13432 | 0.083097 | 0.0010703 | 77.6416
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 21 | 948 | 182842 | 1.1312 | 0.0058648 | 192.8713
AEP-KYP | 2022 | 162018 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 3 | 817 | 0.0050426 | 1.8516e-05 | 272.3333
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | FUSE | 12 | 13 | 925 | 0.0057225 | 8.0425e-05 | 71.1538
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WU | FUSE | 182 | 2159 | 350413 | 2.1684 | 0.01336 | 162.3034
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 3 | 2494 | 0.015108 | 1.8173e-05 | 831.3333
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | F | CROSSARM | 1 | 253 | 61985 | 0.37549 | 0.0015326 | 245
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 4 | 231 | 0.0014084 | 2.4387e-05 | 57.75
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CE | CROSSARM | 1 | 28 | 10052 | 0.060893 | 0.00016962 | 359
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ERO | NONE | 3 | 3 | 151 | 0.00093416 | 1.856e-05 | 50.3333
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 3 | 5 | 1803 | 0.011154 | 3.0933e-05 | 360.6
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 1 | 57 | 0.00035263 | 6.1865e-06 | 57
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 2 | 15 | 4529 | 0.028019 | 9.2798e-05 | 301.9333
AEP-KYP | 2023 | 161642 | DISTRIBUTION STATION | AB | NONE | 2 | 1040 | 101920 | 0.63053 | 0.006434 | 98
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 3 | 26 | 4972 | 0.030119 | 0.0001575 | 191.2308
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 17 | 852 | 0.0052587 | 0.00010493 | 50.1176
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 1 | 210 | 0.0012721 | 6.0578e-06 | 210
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | CO | CONN/CLAMP | 3 | 7 | 1787 | 0.011055 | 4.3306e-05 | 255.2857
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 2 | 11 | 3364 | 0.020763 | 6.7894e-05 | 305.8182
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | V | CUTOUT | 1 | 2 | 146 | 0.00090347 | 1.2376e-05 | 73
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 151 | 271347 | 1.6543 | 0.00092061 | 1797
AEP-KYP | 2025 | 161599 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 13 | 6281 | 0.038868 | 8.0446e-05 | 483.1538
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 541 | 0.0033478 | 6.1882e-06 | 541
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 8 | 1872 | 0.011413 | 4.8774e-05 | 234
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | V | GUY/ANCHOR | 1 | 4 | 380 | 0.0023168 | 2.4387e-05 | 95
AEP-KYP | 2021 | 164021 | TRANSMISSION LINE | WFS | NONE | 1 | 45 | 21285 | 0.12977 | 0.00027436 | 473
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 26 | 3770 | 0.022838 | 0.0001575 | 145
AEP-KYP | 2024 | 161599 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 94 | 0.00058169 | 6.1882e-06 | 94
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1 | 1 | 61 | 0.00036952 | 6.0578e-06 | 61
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | O | NONE | 6 | 486 | 76052 | 0.47062 | 0.0030074 | 156.4856
AEP-KYP | 2020 | 165077 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 25 | 2167 | 0.013127 | 0.00015144 | 86.68
AEP-KYP | 2024 | 161599 | PARTIAL POWER | ERF | CONN/CLAMP | 3 | 4 | 474 | 0.0029332 | 2.4753e-05 | 118.5
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | V | FUSE | 2 | 5 | 626 | 0.0038738 | 3.0941e-05 | 125.2
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TR | SPLICE, OH | 1 | 1 | 530 | 0.0032797 | 6.1882e-06 | 530
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 1 | 70 | 0.00043306 | 6.1865e-06 | 70
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | A | SPLICE, OH | 1 | 131 | 12090 | 0.074795 | 0.00081043 | 92.2901
AEP-KYP | 2020 | 165077 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 8 | 976 | 0.0059124 | 4.8462e-05 | 122
AEP-KYP | 2024 | 161599 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 636 | 0.0039357 | 1.2376e-05 | 318
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 7 | 592 | 74594 | 0.4616 | 0.0036634 | 126.0034
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | ARRESTER | 1 | 23 | 1863 | 0.011525 | 0.00014229 | 81
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 140 | 15447 | 0.095588 | 0.00086634 | 110.3357
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 1 | 79 | 0.00048886 | 6.1882e-06 | 79
AEP-KYP | 2024 | 161599 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 5 | 515 | 0.0031869 | 3.0941e-05 | 103
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 21 | 2205 | 0.013645 | 0.00012995 | 105
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 31 | 8246 | 0.050896 | 0.00019134 | 266
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 37 | 653 | 145258 | 0.87994 | 0.0039557 | 222.4472
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WL | NONE | 14 | 1115 | 128441 | 0.77807 | 0.0067544 | 115.1937
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TR | NONE | 11 | 450 | 64027 | 0.38786 | 0.002726 | 142.2822
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | A | NONE | 17 | 1061 | 107419 | 0.65491 | 0.0064687 | 101.2432
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 21 | 491 | 69713 | 0.42502 | 0.0029935 | 141.9817
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | O | POLE | 3 | 26 | 3739 | 0.023078 | 0.00016048 | 143.8077
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | TRANSFORMER, OH | 9 | 22 | 13034 | 0.080448 | 0.00013579 | 592.4545
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 4 | 17 | 11910 | 0.072613 | 0.00010365 | 700.5882
AEP-KYP | 2020 | 165077 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 47 | 108 | 10703 | 0.064836 | 0.00065424 | 99.1019
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | U | FUSE | 1203 | 7592 | 811353 | 4.915 | 0.045991 | 106.8695
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 10 | 594 | 307514 | 1.898 | 0.0036663 | 517.7003
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TR | NONE | 3 | 787 | 79038 | 0.48783 | 0.0048575 | 100.4295
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | ARRESTER | 40 | 277 | 37882 | 0.23381 | 0.0017097 | 136.7581
AEP-KYP | 2022 | 162018 | PARTIAL POWER | EQF | CABLE TERMINATOR | 3 | 4 | 471 | 0.0029071 | 2.4689e-05 | 117.75
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | REGULATOR | 9 | 2380 | 199542 | 1.2166 | 0.01451 | 83.8412
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 5 | 407 | 16209 | 0.098823 | 0.0024814 | 39.8256
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WU | NONE | 97 | 7227 | 1999486 | 12.1124 | 0.04378 | 276.6689
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 9 | 299 | 54826 | 0.33426 | 0.0018229 | 183.3645
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | FW | NONE | 109 | 2739 | 149821 | 0.92472 | 0.016906 | 54.6992
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 6 | 372 | 81655 | 0.49783 | 0.002268 | 219.5027
AEP-KYP | 2020 | 165077 | PARTIAL POWER | U | FUSE | 40 | 164 | 16535 | 0.10017 | 0.00099348 | 100.8232
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | NONE | 440 | 32239 | 7094411 | 42.9764 | 0.1953 | 220.0568
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | FUSE | 257 | 3142 | 759608 | 4.6015 | 0.019034 | 241.7594
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | WW | NONE | 18 | 805 | 194986 | 1.2035 | 0.0049686 | 242.2186
AEP-KYP | 2021 | 164021 | PARTIAL POWER | EQF | CONN/CLAMP | 79 | 213 | 38089 | 0.23222 | 0.0012986 | 178.8216
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 24 | 1050 | 354161 | 2.1859 | 0.0064808 | 337.2962
AEP-KYP | 2022 | 162018 | PARTIAL POWER | U | FUSE | 34 | 69 | 5839 | 0.036039 | 0.00042588 | 84.6232
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 16 | 50 | 3807 | 0.023497 | 0.00030861 | 76.14
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | U | NONE | 170 | 12574 | 1101875 | 6.8009 | 0.077609 | 87.6312
AEP-KYP | 2021 | 164021 | PARTIAL POWER | UG | CONDUCTOR UG | 2 | 2 | 598 | 0.0036459 | 1.2194e-05 | 299
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | FW | REGULATOR | 2 | 202 | 1530 | 0.0093281 | 0.0012315 | 7.5743
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WU | FUSE | 182 | 2072 | 355237 | 2.1977 | 0.012818 | 171.4464
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TIR | POLE | 7 | 949 | 206329 | 1.2579 | 0.0057858 | 217.4173
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | F | NONE | 12 | 123 | 14151 | 0.085724 | 0.00074511 | 115.0488
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | SCO | ARRESTER | 3 | 27 | 6734 | 0.041563 | 0.00016665 | 249.4074
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 17 | 581 | 75451 | 0.45707 | 0.0035196 | 129.864
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 3 | 7 | 2275 | 0.014042 | 4.3205e-05 | 325
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | SWITCH, OH | 3 | 438 | 56918 | 0.35131 | 0.0027034 | 129.9498
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | SCO | CROSSARM | 21 | 758 | 111443 | 0.68944 | 0.0046894 | 147.0224
AEP-KYP | 2020 | 165077 | PARTIAL POWER | ERF | NONE | 1 | 2 | 126 | 0.00076328 | 1.2116e-05 | 63
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | SCO | POLE | 514 | 12070 | 2115294 | 13.0898 | 0.074691 | 175.2522
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 6 | 27 | 1492 | 0.0090382 | 0.00016356 | 55.2593
AEP-KYP | 2024 | 161599 | PARTIAL POWER | U | FUSE | 27 | 70 | 8316 | 0.051461 | 0.00043317 | 118.8
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | WL | ARRESTER | 5 | 16 | 4286 | 0.026522 | 9.9011e-05 | 267.875
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 3 | 449 | 0.0027777 | 1.856e-05 | 149.6667
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | CF | POLE | 1 | 22 | 748 | 0.0045604 | 0.00013413 | 34
AEP-KYP | 2024 | 161599 | PARTIAL POWER | TOR | POLE | 1 | 1 | 145 | 0.00089728 | 6.1882e-06 | 145
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 2 | 4 | 291 | 0.0018008 | 2.4753e-05 | 72.75
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 5 | 294 | 0.0018146 | 3.0861e-05 | 58.8
AEP-KYP | 2022 | 162018 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 2 | 344 | 0.0021232 | 1.2344e-05 | 172
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | ERF | FUSE | 1 | 5 | 3880 | 0.024004 | 3.0933e-05 | 776
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 543 | 0.0033593 | 1.856e-05 | 181
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | EQF | METERING | 2 | 4 | 799 | 0.004943 | 2.4746e-05 | 199.75
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | FUSE | 83 | 948 | 175632 | 1.0868 | 0.0058664 | 185.2658
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 36 | 78 | 6821 | 0.042209 | 0.00048268 | 87.4487
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FW | POLE | 8 | 297 | 70459 | 0.43601 | 0.0018379 | 237.2357
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 3 | 44 | 4744 | 0.029357 | 0.00027228 | 107.8182
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | WL | NONE | 4 | 150 | 30208 | 0.18693 | 0.00092822 | 201.3867
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | OU | FUSE | 2 | 5 | 443 | 0.0027414 | 3.0941e-05 | 88.6
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OU | SPLICE, OH | 1 | 617 | 45069 | 0.27302 | 0.0037376 | 73.0454
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 1 | 65 | 0.00039629 | 6.0968e-06 | 65
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | UB | NONE | 1 | 243 | 60750 | 0.36801 | 0.001472 | 250
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERO | CROSSARM | 3 | 1771 | 296081 | 1.8322 | 0.010959 | 167.1829
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 3 | 32 | 3556 | 0.022005 | 0.00019802 | 111.125
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 40 | 0.00024753 | 6.1882e-06 | 40
AEP-KYP | 2025 | 161599 | PARTIAL POWER | O | NONE | 1 | 1 | 94 | 0.00058169 | 6.1882e-06 | 94
AEP-KYP | 2022 | 162018 | TRANSMISSION STATION | FW | NONE | 3 | 1711 | 22747 | 0.1404 | 0.010561 | 13.2946
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 59 | 0.000365 | 6.1865e-06 | 59
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 7 | 3003 | 0.018578 | 4.3306e-05 | 429
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 1 | 67 | 0.0004145 | 6.1865e-06 | 67
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 5 | 2235 | 0.013831 | 3.0941e-05 | 447
AEP-KYP | 2024 | 161599 | PARTIAL POWER | WL | FUSE | 2 | 7 | 658 | 0.0040718 | 4.3317e-05 | 94
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 6 | 2922 | 0.017815 | 3.6581e-05 | 487
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 65 | 0.00039629 | 6.0968e-06 | 65
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 58 | 9574 | 0.057997 | 0.00035135 | 165.069
AEP-KYP | 2022 | 162018 | PARTIAL POWER | VIN | SPLICE, OH | 1 | 1 | 239 | 0.0014751 | 6.1722e-06 | 239
AEP-KYP | 2022 | 162018 | PARTIAL POWER | WFS | CONDUCTOR OVERHEAD | 1 | 2 | 454 | 0.0028022 | 1.2344e-05 | 227
AEP-KYP | 2023 | 161642 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 2 | 358 | 0.0022148 | 1.2373e-05 | 179
AEP-KYP | 2025 | 161599 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 230 | 0.0014233 | 6.1882e-06 | 230
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | ERO | POLE | 1 | 359 | 32310 | 0.19994 | 0.0022215 | 90
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 22 | 7084 | 0.04319 | 0.00013413 | 322
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | OL | FUSE | 2 | 95 | 9846 | 0.059645 | 0.00057549 | 103.6421
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 7 | 105 | 22620 | 0.13791 | 0.00064016 | 215.4286
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | U | CUTOUT | 5 | 115 | 16008 | 0.097597 | 0.00070113 | 139.2
AEP-KYP | 2021 | 164021 | DISTRIBUTION LINE | EQF | METERING | 6 | 7 | 555 | 0.0033837 | 4.2677e-05 | 79.2857
AEP-KYP | 2022 | 162018 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 1 | 300 | 0.0018516 | 6.1722e-06 | 300
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WW | POLE | 5 | 29 | 5810 | 0.035196 | 0.00017568 | 200.3448
AEP-KYP | 2023 | 161642 | PARTIAL POWER | EQF | METERING | 2 | 3 | 250 | 0.0015466 | 1.856e-05 | 83.3333
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | WI | POLE | 2 | 116 | 86986 | 0.52694 | 0.0007027 | 749.8793
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | TIR | POLE | 9 | 1591 | 416242 | 2.5215 | 0.0096379 | 261.6229
AEP-KYP | 2020 | 165077 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 5 | 874 | 0.0052945 | 3.0289e-05 | 174.8
AEP-KYP | 2024 | 161599 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 28 | 64 | 37491 | 0.232 | 0.00039604 | 585.7969
AEP-KYP | 2024 | 161599 | DISTRIBUTION LINE | TOR | CROSSARM | 59 | 10711 | 2680303 | 16.5861 | 0.066281 | 250.2384
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | JUMPER/RISER | 6 | 63 | 12450 | 0.0082462 | 4.1728e-05 | 197.619
AEP-OH | 2022 | 1518267 | PARTIAL POWER | FO | NONE | 3 | 11 | 2028 | 0.0013357 | 7.2451e-06 | 184.3636
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 187 | 7494 | 1063814 | 0.69792 | 0.0049165 | 141.9554
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 13 | 6361 | 0.0042132 | 8.6104e-06 | 489.3077
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | POLE HARDWARE | 2 | 15 | 1254 | 0.00083631 | 1.0004e-05 | 83.6
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 31 | 2418 | 0.0015926 | 2.0418e-05 | 78
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 25 | 333 | 38144 | 0.025439 | 0.00022208 | 114.5465
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | INSULATOR | 4 | 2201 | 220095 | 0.14578 | 0.0014578 | 99.9977
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | CUTOUT | 37 | 2107 | 399827 | 0.26665 | 0.0014052 | 189.7613
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | CABLE TERMINATOR | 7 | 10 | 1503 | 0.00098606 | 6.5606e-06 | 150.3
AEP-OH | 2023 | 1524255 | PARTIAL POWER | ERF | CONN/CLAMP | 9 | 9 | 975 | 0.00063966 | 5.9045e-06 | 108.3333
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | ARRESTER | 1 | 2 | 184 | 0.00012071 | 1.3121e-06 | 92
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 14 | 1231 | 207450 | 0.1361 | 0.00080761 | 168.5215
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERO | NONE | 10 | 380 | 22367 | 0.014917 | 0.00025343 | 58.8605
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | CIRCUIT SWITCHER | 1 | 217 | 5642 | 0.0037627 | 0.00014472 | 26
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 11 | 1984 | 54311 | 0.035373 | 0.0012922 | 27.3745
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 95 | 3697 | 1395504 | 0.90889 | 0.0024079 | 377.4693
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | CUTOUT | 13 | 269 | 33084 | 0.021705 | 0.00017648 | 122.9888
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 2 | 212 | 0.00014139 | 1.3338e-06 | 106
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | INSULATOR | 3 | 2033 | 575179 | 0.37884 | 0.001339 | 282.9213
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VA | CONN/CLAMP | 1 | 1 | 101 | 6.7358e-05 | 6.6691e-07 | 101
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | POLE | 14 | 185 | 66654 | 0.043729 | 0.00012137 | 360.2919
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | SCO | NONE | 18 | 11172 | 2011795 | 1.3103 | 0.0072763 | 180.0747
AEP-OH | 2021 | 1509795 | PARTIAL POWER | U | CONDUCTOR UG | 3 | 4 | 662 | 0.00043847 | 2.6494e-06 | 165.5
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | SPLICE, OH | 13 | 37 | 6527 | 0.0042821 | 2.4274e-05 | 176.4054
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | METERING | 10 | 12 | 2252 | 0.0014667 | 7.8156e-06 | 187.6667
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TOR | SPLICE, OH | 8 | 25 | 10163 | 0.0066675 | 1.6401e-05 | 406.52
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | CUTOUT | 2 | 15 | 2463 | 0.0016313 | 9.9351e-06 | 164.2
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 53 | 16483 | 0.010917 | 3.5104e-05 | 311
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 3691 | 422144 | 0.27494 | 0.0024039 | 114.3712
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TOR | CONN/CLAMP | 21 | 90 | 13371 | 0.0087085 | 5.8617e-05 | 148.5667
AEP-OH | 2024 | 1535393 | PARTIAL POWER | FO | NONE | 4 | 4 | 230 | 0.0001498 | 2.6052e-06 | 57.5
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 2 | 457 | 0.00029982 | 1.3121e-06 | 228.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | INSULATOR | 1 | 1 | 534 | 0.00035172 | 6.5865e-07 | 534
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 7 | 43 | 47236 | 0.030765 | 2.8006e-05 | 1098.5116
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | POLE | 2 | 25 | 12688 | 0.0083569 | 1.6466e-05 | 507.52
AEP-OH | 2020 | 1499447 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 6 | 33 | 2088 | 0.0013925 | 2.2008e-05 | 63.2727
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AB | INSULATOR | 1 | 1470 | 99960 | 0.06558 | 0.00096441 | 68
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 3739 | 123387 | 0.081268 | 0.0024627 | 33
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CE | METERING | 1 | 2 | 226 | 0.00014827 | 1.3121e-06 | 113
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 168 | 20901 | 0.013939 | 0.00011204 | 124.4107
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | F | NONE | 11 | 1288 | 119587 | 0.077887 | 0.00083887 | 92.847
AEP-OH | 2025 | 1535393 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 68 | 4.4288e-05 | 6.513e-07 | 68
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | METERING | 4 | 24 | 9271 | 0.0060382 | 1.5631e-05 | 386.2917
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 21 | 1748 | 330399 | 0.21519 | 0.0011385 | 189.0154
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | POLE | 1 | 7 | 2856 | 0.0018601 | 4.5591e-06 | 408
AEP-OH | 2025 | 1535393 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 5 | 1031 | 0.00067149 | 3.2565e-06 | 206.2
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | TRANSFORMER, OH | 8 | 72 | 18593 | 0.01211 | 4.6894e-05 | 258.2361
AEP-OH | 2021 | 1509795 | PARTIAL POWER | A | FUSE | 5 | 36 | 6997 | 0.0046344 | 2.3844e-05 | 194.3611
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 211 | 0.00014072 | 6.6691e-07 | 211
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CE | METERING | 2 | 38 | 1050 | 0.00070026 | 2.5343e-05 | 27.6316
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 457 | 0.00029982 | 6.5606e-07 | 457
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 3 | 115 | 49616 | 0.032863 | 7.6169e-05 | 431.4435
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 2 | 1768 | 0.0011791 | 1.3338e-06 | 884
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 1 | 279 | 0.00018607 | 6.6691e-07 | 279
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 5 | 1135 | 0.00075695 | 3.3346e-06 | 227
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | CIRCUIT SWITCHER | 1 | 1 | 183 | 0.00012204 | 6.6691e-07 | 183
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 1 | 87 | 5.6663e-05 | 6.513e-07 | 87
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | INSULATOR | 1 | 3 | 276 | 0.00017976 | 1.9539e-06 | 92
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERO | RECLOSER, LINE/OCR/BR | 1 | 49 | 3332 | 0.002186 | 3.2147e-05 | 68
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 4 | 634 | 0.00041594 | 2.6242e-06 | 158.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 32 | 3488 | 0.0022974 | 2.1077e-05 | 109
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | R | OTHER EQUIPMENT | 1 | 4 | 708 | 0.00046632 | 2.6346e-06 | 177
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 1 | 1 | 30 | 1.987e-05 | 6.6234e-07 | 30
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 83 | 3735 | 0.0024909 | 5.5354e-05 | 45
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WI | CUTOUT | 2 | 10 | 33816 | 0.022398 | 6.6234e-06 | 3381.6
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | CAPACITOR | 1 | 10 | 410 | 0.00027156 | 6.6234e-06 | 41
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 9 | 378 | 0.00025037 | 5.9611e-06 | 42
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | OTHER EQUIPMENT | 1 | 589 | 114058 | 0.074829 | 0.00038642 | 193.6469
AEP-OH | 2020 | 1499447 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 259 | 0.00017273 | 6.6691e-07 | 259
AEP-OH | 2025 | 1535393 | PARTIAL POWER | WL | NONE | 1 | 1 | 195 | 0.000127 | 6.513e-07 | 195
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | ARRESTER | 1 | 2 | 156 | 0.0001016 | 1.3026e-06 | 78
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 455 | 2730 | 0.001778 | 0.00029634 | 6
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | SPLICE, OH | 2 | 3 | 1375 | 0.00089554 | 1.9539e-06 | 458.3333
AEP-OH | 2025 | 1535393 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 70 | 4.5591e-05 | 6.513e-07 | 70
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 2542 | 231722 | 0.15348 | 0.0016837 | 91.1574
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | POLE | 8 | 305 | 25261 | 0.016731 | 0.00020201 | 82.823
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 17 | 384 | 113545 | 0.075206 | 0.00025434 | 295.6901
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | SPLICE, OH | 19 | 22 | 2618 | 0.001746 | 1.4672e-05 | 119
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OU | NONE | 14 | 2105 | 247593 | 0.16399 | 0.0013942 | 117.6214
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 4 | 12 | 4435 | 0.0029211 | 7.9037e-06 | 369.5833
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | FUSE | 115 | 2045 | 222103 | 0.14571 | 0.0013416 | 108.6078
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | ARRESTER | 9 | 33 | 7237 | 0.0048264 | 2.2008e-05 | 219.303
AEP-OH | 2022 | 1518267 | PARTIAL POWER | O | CONN/CLAMP | 3 | 3 | 210 | 0.00013832 | 1.9759e-06 | 70
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 12 | 228 | 22555 | 0.015042 | 0.00015206 | 98.9254
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 23 | 136 | 16041 | 0.010625 | 9.0078e-05 | 117.9485
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | INSULATOR | 3 | 53 | 15485 | 0.010159 | 3.4771e-05 | 292.1698
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 4 | 592 | 104291 | 0.068691 | 0.00038992 | 176.1672
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | NONE | 14 | 21 | 3117 | 0.0020449 | 1.3777e-05 | 148.4286
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | POLE | 8 | 4314 | 576583 | 0.38189 | 0.0028573 | 133.6539
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | SPLICE, OH | 31 | 56 | 9269 | 0.006081 | 3.6739e-05 | 165.5179
AEP-OH | 2021 | 1509795 | PARTIAL POWER | OL | NONE | 2 | 2 | 178 | 0.0001179 | 1.3247e-06 | 89
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 17 | 6980 | 833088 | 0.54655 | 0.0045793 | 119.3536
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | INSULATOR | 9 | 618 | 113113 | 0.074209 | 0.00040544 | 183.0307
AEP-OH | 2020 | 1499447 | PARTIAL POWER | V | NONE | 3 | 3 | 197 | 0.00013138 | 2.0007e-06 | 65.6667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | F | POLE | 10 | 3434 | 158618 | 0.10578 | 0.0022902 | 46.1904
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 19 | 770 | 312911 | 0.20529 | 0.00050516 | 406.3779
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 4 | 560 | 24636 | 0.016163 | 0.00036739 | 43.9929
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 15 | 671 | 62913 | 0.041957 | 0.0004475 | 93.7601
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | REGULATOR | 10 | 3489 | 153948 | 0.10027 | 0.0022724 | 44.1238
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | SPLICE, OH | 48 | 896 | 267211 | 0.17403 | 0.00058356 | 298.2266
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 3 | 12 | 2627 | 0.001711 | 7.8156e-06 | 218.9167
AEP-OH | 2024 | 1535393 | PARTIAL POWER | U | CONDUCTOR UG | 10 | 31 | 3667 | 0.0023883 | 2.019e-05 | 118.2903
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | FUSE | 5 | 253 | 15825 | 0.010382 | 0.00016598 | 62.5494
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | INSULATOR | 2 | 61 | 20839 | 0.013672 | 4.002e-05 | 341.623
AEP-OH | 2024 | 1535393 | PARTIAL POWER | OL | NONE | 3 | 13 | 2414 | 0.0015722 | 8.4669e-06 | 185.6923
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 3 | 6 | 652 | 0.00042775 | 3.9363e-06 | 108.6667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | JUMPER/RISER | 4 | 201 | 22568 | 0.015051 | 0.00013405 | 112.2786
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 269 | 0.0001752 | 6.513e-07 | 269
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | CUTOUT | 3 | 14 | 17063 | 0.011113 | 9.1182e-06 | 1218.7857
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 4 | 3795 | 1339615 | 0.87887 | 0.0024897 | 352.9947
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 14 | 1243 | 0.00081548 | 9.1848e-06 | 88.7857
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | CROSSARM | 1 | 237 | 48822 | 0.03203 | 0.00015549 | 206
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 31 | 21876 | 0.014409 | 2.0418e-05 | 705.6774
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 9 | 2836 | 0.0018606 | 5.9045e-06 | 315.1111
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 11 | 10643 | 1334414 | 0.8691 | 0.0069318 | 125.3795
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 13 | 1020 | 0.00067182 | 8.5624e-06 | 78.4615
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | ABI | NONE | 11 | 10271 | 1214787 | 0.81016 | 0.0068499 | 118.2735
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | NETWORK TRANSFORMER | 1 | 1 | 2774 | 0.0018199 | 6.5606e-07 | 2774
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 8 | 175 | 32263 | 0.021013 | 0.00011398 | 184.36
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 165 | 34299 | 0.022502 | 0.00010825 | 207.8727
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UB | CONN/CLAMP | 2 | 2 | 307 | 0.0002022 | 1.3173e-06 | 153.5
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | BE | POLE | 1 | 45 | 5325 | 0.003527 | 2.9805e-05 | 118.3333
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 106 | 14214 | 0.0092576 | 6.9038e-05 | 134.0943
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 28 | 1.8236e-05 | 6.513e-07 | 28
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | SPLICE, UG | 13 | 70 | 17374 | 0.011316 | 4.5591e-05 | 248.2
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | PEDESTAL | 6 | 22 | 1330 | 0.00086623 | 1.4329e-05 | 60.4545
AEP-OH | 2025 | 1535393 | DISTRIBUTION SOURCE | U | NONE | 7 | 1374 | 101012 | 0.065789 | 0.00089488 | 73.5167
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | EQF | ARRESTER | 6 | 5031 | 526218 | 0.34273 | 0.0032767 | 104.5951
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | CROSSARM | 1 | 2 | 80 | 5.2692e-05 | 1.3173e-06 | 40
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | CUTOUT | 2 | 13 | 6177 | 0.0040685 | 8.5624e-06 | 475.1538
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 1 | 10 | 6.6691e-06 | 6.6691e-07 | 10
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 4 | 120 | 7.8156e-05 | 2.6052e-06 | 30
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TR | FUSE | 2 | 6 | 1185 | 0.00077743 | 3.9363e-06 | 197.5
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 3 | 28 | 5145 | 0.0033509 | 1.8236e-05 | 183.75
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | NONE | 2 | 2166 | 69822 | 0.045475 | 0.0014107 | 32.2355
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | SCO | OTHER EQUIPMENT | 1 | 3 | 285 | 0.00018877 | 1.987e-06 | 95
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | ABI | OTHER EQUIPMENT | 1 | 1377 | 247860 | 0.16417 | 0.00091204 | 180
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 1 | 317 | 0.00021141 | 6.6691e-07 | 317
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TR | OTHER EQUIPMENT | 1 | 5 | 3950 | 0.0025726 | 3.2565e-06 | 790
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CF | POLE | 1 | 50 | 5150 | 0.0034346 | 3.3346e-05 | 103
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | METERING | 1 | 21 | 210 | 0.00013777 | 1.3777e-05 | 10
AEP-OH | 2020 | 1499447 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 465 | 130665 | 0.087142 | 0.00031011 | 281
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | FUSE | 1 | 103 | 2060 | 0.0013417 | 6.7084e-05 | 20
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 95 | 6.2326e-05 | 6.5606e-07 | 95
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | UG | CUTOUT | 2 | 5 | 1007 | 0.00065586 | 3.2565e-06 | 201.4
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 1732 | 156604 | 0.102 | 0.001128 | 90.418
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | ABX | INSULATOR | 1 | 901 | 153170 | 0.099759 | 0.00058682 | 170
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 1267 | 0.0008252 | 6.513e-07 | 1267
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 1 | 1 | 183 | 0.00011919 | 6.513e-07 | 183
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 1883 | 30128 | 0.019622 | 0.0012264 | 16
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | AF | NONE | 1 | 695 | 49345 | 0.032138 | 0.00045265 | 71
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | NONE | 91 | 11517 | 557845 | 0.36948 | 0.0076282 | 48.4367
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | GUY/ANCHOR | 1 | 2 | 48 | 3.1615e-05 | 1.3173e-06 | 24
AEP-OH | 2022 | 1518267 | PARTIAL POWER | ABI | CONN/CLAMP | 1 | 1 | 274 | 0.00018047 | 6.5865e-07 | 274
AEP-OH | 2020 | 1499447 | PARTIAL POWER | UG | CONDUCTOR UG | 45 | 55 | 10133 | 0.0067578 | 3.668e-05 | 184.2364
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WT | NONE | 1 | 10 | 4640 | 0.0030561 | 6.5865e-06 | 464
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | METERING | 35 | 41 | 5188 | 0.0034362 | 2.7156e-05 | 126.5366
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | POLE | 3126 | 23155 | 2871197 | 1.9148 | 0.015442 | 123.999
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 4 | 39 | 2166 | 0.0014266 | 2.5687e-05 | 55.5385
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 13 | 4499 | 308433 | 0.20315 | 0.0029632 | 68.5559
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 7 | 805 | 52783 | 0.03496 | 0.00053318 | 65.5689
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | SCO | TRANSFORMER, POWER - NON LTC | 5 | 3966 | 408323 | 0.26894 | 0.0026122 | 102.9559
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WFS | NONE | 3 | 153 | 81192 | 0.053477 | 0.00010077 | 530.6667
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | CUTOUT | 10 | 1309 | 101811 | 0.067434 | 0.00086701 | 77.7777
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | SCO | REGULATOR | 6 | 3926 | 546105 | 0.35969 | 0.0025858 | 139.0996
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VIN | NONE | 178 | 6111 | 461614 | 0.30575 | 0.0040476 | 75.5382
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | NONE | 44 | 3453 | 152585 | 0.1005 | 0.0022743 | 44.1891
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 1806 | 138411 | 0.091675 | 0.0011962 | 76.6395
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | CROSSARM | 59 | 14104 | 3309159 | 2.1918 | 0.0093417 | 234.6256
AEP-OH | 2022 | 1518267 | PARTIAL POWER | A | NONE | 114 | 369 | 31795 | 0.020942 | 0.00024304 | 86.1653
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | FUSE | 7 | 81 | 11853 | 0.0078069 | 5.335e-05 | 146.3333
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 53 | 1387 | 252019 | 0.16599 | 0.00091354 | 181.7008
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 49 | 13387 | 1735582 | 1.1431 | 0.0088173 | 129.6468
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VIN | FUSE | 20 | 103 | 12331 | 0.0081218 | 6.7841e-05 | 119.7184
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | CUTOUT | 11 | 876 | 138516 | 0.091745 | 0.00058021 | 158.1233
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 12 | 5651 | 679470 | 0.45004 | 0.0037429 | 120.2389
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CE | CUTOUT | 1 | 1 | 298 | 0.00019738 | 6.6234e-07 | 298
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 55 | 9154 | 1183899 | 0.78956 | 0.0061049 | 129.3313
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CE | CONN/CLAMP | 5 | 8 | 990 | 0.00065572 | 5.2987e-06 | 123.75
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 9 | 405 | 0.00026675 | 5.9278e-06 | 45
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | INSULATOR | 9 | 2483 | 333624 | 0.21974 | 0.0016354 | 134.3633
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | REGULATOR | 8 | 2453 | 85530 | 0.05665 | 0.0016247 | 34.8675
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 4 | 491 | 106314 | 0.070023 | 0.0003234 | 216.5255
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | O | METERING | 2 | 2 | 82 | 5.4312e-05 | 1.3247e-06 | 41
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | CROSSARM | 57 | 20454 | 5444859 | 3.5862 | 0.013472 | 266.2002
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | POLE | 606 | 156162 | 25879704 | 17.1412 | 0.10343 | 165.7234
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | FUSE | 22 | 53 | 6257 | 0.0041211 | 3.4908e-05 | 118.0566
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | NONE | 288 | 7303 | 973386 | 0.64112 | 0.0048101 | 133.2858
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 116 | 1887 | 589909 | 0.39072 | 0.0012498 | 312.6174
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 1667 | 17460 | 1744953 | 1.1558 | 0.011564 | 99.94
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | NONE | 163 | 22992 | 2947654 | 1.9524 | 0.015229 | 128.2035
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | CROSSARM | 100 | 35907 | 4425609 | 2.9149 | 0.02365 | 123.252
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 410 | 2054 | 214990 | 0.14105 | 0.0013475 | 104.6689
AEP-OH | 2021 | 1509795 | PARTIAL POWER | OL | FUSE | 1 | 36 | 7308 | 0.0048404 | 2.3844e-05 | 203
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 10 | 1366 | 183202 | 0.12134 | 0.00090476 | 134.1157
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 20 | 2086 | 150323 | 0.10025 | 0.0013912 | 72.0628
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 265 | 1246 | 188728 | 0.12587 | 0.00083097 | 151.4671
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 3 | 611 | 0.00040748 | 2.0007e-06 | 203.6667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 948 | 6041 | 1420236 | 0.94717 | 0.0040288 | 235.0995
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | METERING | 24 | 93 | 5645 | 0.0037647 | 6.2023e-05 | 60.6989
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | FUSE | 11 | 111 | 15550 | 0.010299 | 7.352e-05 | 140.0901
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | PEDESTAL | 24 | 303 | 44875 | 0.029723 | 0.00020069 | 148.1023
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | POLE HARDWARE | 2 | 1326 | 29172 | 0.019214 | 0.00087336 | 22
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | ARRESTER | 75 | 623 | 75996 | 0.050335 | 0.00041264 | 121.9839
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 147 | 14831 | 2298111 | 1.5221 | 0.0098232 | 154.9532
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | CUTOUT | 38 | 1429 | 453902 | 0.29896 | 0.0009412 | 317.6361
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | ERF | NONE | 3 | 2974 | 109776 | 0.072303 | 0.0019588 | 36.9119
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | POLE | 148 | 18218 | 3457857 | 2.2775 | 0.011999 | 189.8044
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 18 | 16424 | 1605103 | 1.0572 | 0.010818 | 97.7291
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 309 | 3104 | 213914 | 0.14089 | 0.0020444 | 68.9156
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | CUTOUT | 64 | 893 | 93355 | 0.061246 | 0.00058586 | 104.5409
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | CROSSARM | 3 | 3611 | 516976 | 0.3405 | 0.0023784 | 143.167
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | CAPACITOR | 11 | 6422 | 525819 | 0.34827 | 0.0042536 | 81.8778
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 26 | 31 | 4661 | 0.0031085 | 2.0674e-05 | 150.3548
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | POLE | 9 | 771 | 221902 | 0.14615 | 0.00050782 | 287.8106
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | NONE | 3419 | 63278 | 4428570 | 2.9535 | 0.042201 | 69.9859
AEP-OH | 2021 | 1509795 | PARTIAL POWER | A | NONE | 121 | 751 | 69418 | 0.045978 | 0.00049742 | 92.4341
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | CUTOUT | 6 | 36 | 8389 | 0.0055254 | 2.3711e-05 | 233.0278
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | POLE | 7 | 155 | 110797 | 0.072976 | 0.00010209 | 714.8194
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | ARRESTER | 45 | 2455 | 372151 | 0.24512 | 0.001617 | 151.589
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 18 | 186 | 29299 | 0.019298 | 0.00012251 | 157.5215
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | REGULATOR | 11 | 2683 | 222759 | 0.14754 | 0.0017771 | 83.0261
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | REGULATOR | 8 | 8095 | 451113 | 0.29879 | 0.0053617 | 55.7274
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 34 | 456 | 53599 | 0.035164 | 0.00029916 | 117.5417
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | SWITCH, OH | 6 | 2931 | 314365 | 0.20822 | 0.0019413 | 107.2552
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TIR | ARRESTER | 1 | 6 | 1986 | 0.0013154 | 3.974e-06 | 331
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 6 | 882 | 0.00058419 | 3.974e-06 | 147
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | V | TRANSFORMER, GROUNDING | 2 | 2 | 224 | 0.00014754 | 1.3173e-06 | 112
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | SPLICE, OH | 18 | 45 | 8110 | 0.0054087 | 3.0011e-05 | 180.2222
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 13 | 2759 | 969911 | 0.64685 | 0.00184 | 351.5444
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VIN | ARRESTER | 2 | 3 | 363 | 0.00023909 | 1.9759e-06 | 121
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | NONE | 3212 | 116095 | 11385509 | 7.4154 | 0.075613 | 98.0706
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | CROSSARM | 65 | 14585 | 4345786 | 2.8511 | 0.0095686 | 297.9627
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | NONE | 108 | 19025 | 720798 | 0.47289 | 0.012482 | 37.8869
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | UG | SPLICE, UG | 3 | 23 | 4568 | 0.0029969 | 1.5089e-05 | 198.6087
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | POLE | 4 | 346 | 27962 | 0.01852 | 0.00022917 | 80.815
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | NONE | 17 | 35 | 7050 | 0.0046252 | 2.2962e-05 | 201.4286
AEP-OH | 2022 | 1518267 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 68 | 4.4788e-05 | 6.5865e-07 | 68
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 193 | 3314 | 650333 | 0.42356 | 0.0021584 | 196.2381
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | METERING | 67 | 1430 | 150776 | 0.0982 | 0.00093136 | 105.4378
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 13 | 937 | 311597 | 0.20443 | 0.00061473 | 332.5475
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | CONN/CLAMP | 5 | 1631 | 54006 | 0.035431 | 0.00107 | 33.1122
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 10 | 6010 | 0.0039429 | 6.5606e-06 | 601
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | CONDUCTOR UG | 10 | 160 | 57187 | 0.037246 | 0.00010421 | 357.4187
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | F | POLE | 9 | 1472 | 289094 | 0.18829 | 0.00095871 | 196.3954
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | POLE | 2 | 3 | 403 | 0.00026439 | 1.9682e-06 | 134.3333
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 41 | 1862 | 605668 | 0.39447 | 0.0012127 | 325.2782
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | BE | CONDUCTOR OVERHEAD | 1 | 6 | 1686 | 0.0011167 | 3.974e-06 | 281
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | CIRCUIT SWITCHER | 1 | 1 | 102 | 6.8025e-05 | 6.6691e-07 | 102
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | REGULATOR | 1 | 1138 | 199544 | 0.12996 | 0.00074118 | 175.3462
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | NONE | 611 | 27780 | 2727364 | 1.7763 | 0.018093 | 98.1772
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | POLE | 193 | 35280 | 6836461 | 4.4526 | 0.022978 | 193.7772
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | CONN/CLAMP | 6 | 148 | 14755 | 0.0096099 | 9.6392e-05 | 99.6959
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VA | OTHER EQUIPMENT | 1 | 1 | 210 | 0.00013777 | 6.5606e-07 | 210
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | CONN/CLAMP | 5 | 35 | 1691 | 0.0011094 | 2.2962e-05 | 48.3143
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | CE | TRANSFORMER, UG | 1 | 3 | 1050 | 0.00068386 | 1.9539e-06 | 350
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ABI | CUTOUT | 4 | 12 | 1293 | 0.00086232 | 8.003e-06 | 107.75
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WFS | CONDUCTOR UG | 1 | 1 | 383 | 0.00025543 | 6.6691e-07 | 383
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | CUTOUT | 8 | 116 | 13943 | 0.0092988 | 7.7362e-05 | 120.1983
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UG | FUSE | 1 | 3 | 408 | 0.00027024 | 1.987e-06 | 136
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 15 | 3464 | 900823 | 0.60077 | 0.0023102 | 260.0528
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 174 | 16356 | 0.010653 | 0.00011333 | 94
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 2 | 9 | 9014 | 0.0058708 | 5.8617e-06 | 1001.5556
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | CUTOUT | 1 | 2 | 230 | 0.00015234 | 1.3247e-06 | 115
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 18 | 4538 | 0.0030057 | 1.1922e-05 | 252.1111
AEP-OH | 2021 | 1509795 | PARTIAL POWER | UG | SPLICE, UG | 1 | 49 | 14847 | 0.0098338 | 3.2455e-05 | 303
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | JUMPER/RISER | 1 | 449 | 2694 | 0.0017674 | 0.00029457 | 6
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 382 | 27270 | 0.018187 | 0.00025476 | 71.3874
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 53 | 6254 | 0.0040732 | 3.4519e-05 | 118
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 89 | 38804 | 0.025273 | 5.7966e-05 | 436
AEP-OH | 2025 | 1535393 | PARTIAL POWER | A | FUSE | 1 | 1 | 64 | 4.1683e-05 | 6.513e-07 | 64
AEP-OH | 2025 | 1535393 | DISTRIBUTION SOURCE | WU | NONE | 1 | 3 | 870 | 0.00056663 | 1.9539e-06 | 290
AEP-OH | 2024 | 1535393 | PARTIAL POWER | U | CONN/CLAMP | 3 | 10 | 590 | 0.00038427 | 6.513e-06 | 59
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 8 | 8131 | 1130944 | 0.75424 | 0.0054227 | 139.0904
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 2 | 226 | 0.00015072 | 1.3338e-06 | 113
AEP-OH | 2021 | 1509795 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 72 | 4.7689e-05 | 6.6234e-07 | 72
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WFS | POLE | 3 | 703 | 155311 | 0.10287 | 0.00046563 | 220.926
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | CUTOUT | 1 | 3 | 396 | 0.0002641 | 2.0007e-06 | 132
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 64 | 4.1988e-05 | 6.5606e-07 | 64
AEP-OH | 2023 | 1524255 | PARTIAL POWER | OU | NONE | 1 | 1 | 115 | 7.5447e-05 | 6.5606e-07 | 115
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 269 | 0.0001794 | 6.6691e-07 | 269
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 15 | 416 | 0.00027094 | 9.7695e-06 | 27.7333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 191 | 53237 | 0.035504 | 0.00012738 | 278.7277
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | BREAKER | 4 | 3830 | 46978 | 0.030597 | 0.0024945 | 12.2658
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 22 | 1914 | 0.0012557 | 1.4433e-05 | 87
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 4 | 604 | 0.00039338 | 2.6052e-06 | 151
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | V | SWITCH, UG | 1 | 1159 | 158783 | 0.10342 | 0.00075486 | 137
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | NONE | 3319 | 188038 | 15725983 | 10.416 | 0.12455 | 83.6319
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 7 | 611 | 66560 | 0.043839 | 0.00040243 | 108.9362
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | CUTOUT | 56 | 143 | 20875 | 0.013749 | 9.4186e-05 | 145.979
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | TRANSFORMER, OH | 31 | 111 | 39910 | 0.026287 | 7.311e-05 | 359.5495
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | CONN/CLAMP | 32 | 270 | 43655 | 0.028915 | 0.00017883 | 161.6852
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FO | FUSE | 3 | 14 | 1450 | 0.00095504 | 9.221e-06 | 103.5714
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | POLE | 124 | 22535 | 4027788 | 2.6862 | 0.015029 | 178.7348
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VIN | POLE | 3 | 10 | 1602 | 0.0010611 | 6.6234e-06 | 160.2
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | SCO | REGULATOR | 4 | 2620 | 950995 | 0.63423 | 0.0017473 | 362.9752
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | CUTOUT | 8 | 310 | 75341 | 0.050246 | 0.00020674 | 243.0355
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | SWITCH, UG | 4 | 980 | 110087 | 0.073418 | 0.00065357 | 112.3337
AEP-OH | 2020 | 1499447 | DISTRIBUTION SOURCE | WU | NONE | 2 | 882 | 257544 | 0.17176 | 0.00058822 | 292
AEP-OH | 2023 | 1524255 | PARTIAL POWER | A | NONE | 129 | 854 | 80341 | 0.052708 | 0.00056027 | 94.0761
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WI | NONE | 43 | 4017 | 1328031 | 0.87961 | 0.0026606 | 330.6027
AEP-OH | 2022 | 1518267 | PARTIAL POWER | A | FUSE | 5 | 11 | 1666 | 0.0010973 | 7.2451e-06 | 151.4545
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | JUMPER/RISER | 2 | 3 | 911 | 0.00060003 | 1.9759e-06 | 303.6667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | NONE | 46 | 4766 | 136938 | 0.091326 | 0.0031785 | 28.7323
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 3 | 258 | 0.00017088 | 1.987e-06 | 86
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | POLE | 2 | 1880 | 98040 | 0.064936 | 0.0012452 | 52.1489
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 2 | 20 | 1.3173e-05 | 1.3173e-06 | 10
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 4 | 3972 | 0.002649 | 2.6677e-06 | 993
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 367 | 0.00024476 | 6.6691e-07 | 367
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 23 | 931 | 0.00061079 | 1.5089e-05 | 40.4783
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 13 | 930 | 122631 | 0.080453 | 0.00061013 | 131.8613
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 4 | 2904 | 1883867 | 1.2408 | 0.0019127 | 648.7145
AEP-OH | 2023 | 1524255 | DISTRIBUTION SOURCE | SCO | POLE | 2 | 22 | 3245 | 0.0021289 | 1.4433e-05 | 147.5
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 1 | 321 | 0.00021059 | 6.5606e-07 | 321
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | TRANSFORMER, GROUNDING | 4 | 5046 | 458813 | 0.30599 | 0.0033652 | 90.9261
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | REGULATOR | 10 | 3532 | 90728 | 0.059523 | 0.0023172 | 25.6874
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | REGULATOR | 11 | 13794 | 953338 | 0.63579 | 0.0091994 | 69.1125
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | ARRESTER | 1 | 2 | 150 | 9.8797e-05 | 1.3173e-06 | 75
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | PEDESTAL | 1 | 26 | 2470 | 0.0016269 | 1.7125e-05 | 95
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | SPLICE, UG | 2 | 3 | 437 | 0.00029144 | 2.0007e-06 | 145.6667
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 92 | 6.1356e-05 | 6.6691e-07 | 92
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 54 | 3240 | 0.002134 | 3.5567e-05 | 60
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | NETWORK PROTECTOR | 1 | 95 | 42105 | 0.027623 | 6.2326e-05 | 443.2105
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | FUSE | 61 | 1233 | 805523 | 0.52464 | 0.00080305 | 653.3033
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | FUSE | 4 | 9 | 819 | 0.00053341 | 5.8617e-06 | 91
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 190 | 126347 | 0.082891 | 0.00012465 | 664.9842
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | FUSE | 7 | 59 | 41065 | 0.026746 | 3.8427e-05 | 696.0169
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | CUTOUT | 2 | 1496 | 23936 | 0.015765 | 0.00098533 | 16
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 28 | 3308 | 0.0022061 | 1.8674e-05 | 118.1429
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | METERING | 1 | 1 | 343 | 0.0002234 | 6.513e-07 | 343
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 5 | 600 | 0.00039519 | 3.2932e-06 | 120
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | CROSSARM | 4 | 4160 | 1717649 | 1.1269 | 0.0027292 | 412.8964
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VA | CUTOUT | 1 | 1 | 192 | 0.00012596 | 6.5606e-07 | 192
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | TRANSFORMER, UG | 5 | 17 | 4579 | 0.0029823 | 1.1072e-05 | 269.3529
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 4 | 308 | 0.00020207 | 2.6242e-06 | 77
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 18 | 2034 | 0.0013344 | 1.1809e-05 | 113
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | V | TRANSFORMER, POWER - NON LTC | 2 | 1748 | 176216 | 0.11606 | 0.0011513 | 100.8101
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 2 | 2 | 753 | 0.00049874 | 1.3247e-06 | 376.5
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 37 | 1464 | 539106 | 0.35112 | 0.0009535 | 368.2418
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 1 | 489 | 0.00032081 | 6.5606e-07 | 489
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 6 | 1430 | 0.00095368 | 4.0015e-06 | 238.3333
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 2 | 1935 | 104781 | 0.069401 | 0.0012816 | 54.1504
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 4 | 896 | 0.00059346 | 2.6494e-06 | 224
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | FUSE | 4 | 30 | 691 | 0.00045005 | 1.9539e-05 | 23.0333
AEP-OH | 2024 | 1535393 | PARTIAL POWER | FW | CONDUCTOR UG | 1 | 1 | 73 | 4.7545e-05 | 6.513e-07 | 73
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 72 | 4.7236e-05 | 6.5606e-07 | 72
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 17 | 1309 | 0.00085255 | 1.1072e-05 | 77
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 33 | 4704 | 0.0031157 | 2.1857e-05 | 142.5455
AEP-OH | 2021 | 1509795 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 56 | 3.7091e-05 | 6.6234e-07 | 56
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 8 | 1560 | 0.0010275 | 5.2692e-06 | 195
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 6 | 522 | 0.00034246 | 3.9363e-06 | 87
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WFS | CONDUCTOR OVERHEAD | 1 | 1 | 119 | 7.9363e-05 | 6.6691e-07 | 119
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | BREAKER | 6 | 7572 | 755386 | 0.49558 | 0.0049677 | 99.7604
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TOR | CUTOUT | 1 | 2 | 180 | 0.00011809 | 1.3121e-06 | 90
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WH | OTHER EQUIPMENT | 1 | 1 | 279 | 0.00018171 | 6.513e-07 | 279
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 140 | 9.3368e-05 | 6.6691e-07 | 140
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 2 | 182 | 0.0001194 | 1.3121e-06 | 91
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ERO | FUSE | 1 | 96 | 11136 | 0.0072529 | 6.2525e-05 | 116
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 2 | 2 | 851 | 0.00055426 | 1.3026e-06 | 425.5
AEP-OH | 2025 | 1535393 | PARTIAL POWER | WU | CUTOUT | 1 | 1 | 224 | 0.00014589 | 6.513e-07 | 224
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | NONE | 3754 | 65599 | 4856093 | 3.1859 | 0.043037 | 74.0269
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | FUSE | 214 | 7457 | 493150 | 0.32481 | 0.0049115 | 66.1325
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | METERING | 32 | 41 | 7066 | 0.004654 | 2.7004e-05 | 172.3415
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | CONN/CLAMP | 35 | 590 | 72772 | 0.047931 | 0.0003886 | 123.3424
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 1067 | 44814 | 0.029517 | 0.00070277 | 42
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | NONE | 2532 | 98463 | 9835583 | 6.4527 | 0.064597 | 99.8912
AEP-OH | 2022 | 1518267 | PARTIAL POWER | UG | CONDUCTOR UG | 69 | 188 | 30646 | 0.020185 | 0.00012383 | 163.0106
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 51 | 2093 | 291683 | 0.19319 | 0.0013863 | 139.3612
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 94 | 16699 | 0.010999 | 6.1913e-05 | 177.6489
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 21 | 93 | 23066 | 0.015192 | 6.1254e-05 | 248.0215
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 2 | 224 | 0.00014754 | 1.3173e-06 | 112
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 22 | 135 | 56017 | 0.037102 | 8.9416e-05 | 414.9407
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WL | NONE | 7 | 10 | 2534 | 0.001669 | 6.5865e-06 | 253.4
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | FUSE | 68 | 1748 | 141284 | 0.093578 | 0.0011578 | 80.8261
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 324 | 3029 | 464512 | 0.30979 | 0.0020201 | 153.3549
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 244 | 390 | 96125 | 0.064107 | 0.0002601 | 246.4744
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 1 | 279 | 0.00018376 | 6.5865e-07 | 279
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 4 | 113 | 20391 | 0.013506 | 7.4845e-05 | 180.4513
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | POLE | 3 | 35 | 3280 | 0.0021725 | 2.3182e-05 | 93.7143
AEP-OH | 2021 | 1509795 | PARTIAL POWER | F | CONDUCTOR OVERHEAD | 1 | 1 | 88 | 5.8286e-05 | 6.6234e-07 | 88
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OU | JUMPER/RISER | 1 | 580 | 114840 | 0.074795 | 0.00037775 | 198
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | ARRESTER | 153 | 12592 | 1238497 | 0.81573 | 0.0082937 | 98.3559
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | NONE | 1775 | 27092 | 2432058 | 1.6019 | 0.017844 | 89.7703
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | POLE | 11 | 2680 | 162378 | 0.10695 | 0.0017652 | 60.5888
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 96 | 16636 | 1591318 | 1.0481 | 0.010957 | 95.6551
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 37 | 410 | 65963 | 0.04369 | 0.00027156 | 160.8854
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | CUTOUT | 12 | 1471 | 186252 | 0.12267 | 0.00096887 | 126.6159
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | SPLICE, UG | 1 | 1 | 15 | 9.8797e-06 | 6.5865e-07 | 15
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | FUSE | 35 | 797 | 71411 | 0.047298 | 0.00052789 | 89.5997
AEP-OH | 2021 | 1509795 | PARTIAL POWER | UG | NONE | 8 | 8 | 1393 | 0.00092264 | 5.2987e-06 | 174.125
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | PEDESTAL | 2 | 2 | 4187 | 0.0027577 | 1.3173e-06 | 2093.5
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | ARRESTER | 8 | 39 | 3917 | 0.0025944 | 2.5831e-05 | 100.4359
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | INSULATOR | 122 | 31497 | 3819331 | 2.5297 | 0.020862 | 121.2602
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 103 | 2938 | 790920 | 0.52747 | 0.0019594 | 269.2035
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | O | NONE | 26 | 388 | 72216 | 0.047832 | 0.00025699 | 186.1237
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 9 | 4060 | 318912 | 0.21123 | 0.0026891 | 78.5498
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | PEDESTAL | 1 | 1 | 1737 | 0.0011441 | 6.5865e-07 | 1737
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 363 | 2751 | 275061 | 0.18344 | 0.0018347 | 99.9858
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 794 | 35003 | 3673162 | 2.4497 | 0.023344 | 104.9385
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | POLE | 206 | 18825 | 5745755 | 3.8319 | 0.012555 | 305.2194
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | NONE | 228 | 45087 | 4500446 | 3.0014 | 0.030069 | 99.8169
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 6 | 5139 | 203183 | 0.13458 | 0.0034038 | 39.5375
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | NONE | 25 | 1054 | 159146 | 0.10541 | 0.00069811 | 150.9924
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | CAPACITOR | 5 | 16 | 1179 | 0.00078629 | 1.0671e-05 | 73.6875
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 8 | 6712 | 1493622 | 0.98929 | 0.0044456 | 222.5301
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | CUTOUT | 25 | 472 | 50664 | 0.03337 | 0.00031088 | 107.339
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 677 | 6770 | 0.0044841 | 0.00044841 | 10
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | NONE | 205 | 3238 | 623784 | 0.40924 | 0.0021243 | 192.6448
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 90 | 5.9278e-05 | 6.5865e-07 | 90
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | POLE | 4 | 66 | 14785 | 0.0097381 | 4.3471e-05 | 224.0152
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 4 | 156 | 20030 | 0.013267 | 0.00010333 | 128.3974
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 29 | 2871 | 0.0019016 | 1.9208e-05 | 99
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 2 | 166 | 0.00011071 | 1.3338e-06 | 83
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | SPLICE, OH | 7 | 12 | 1932 | 0.0012725 | 7.9037e-06 | 161
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 13 | 328 | 58848 | 0.038977 | 0.00021725 | 179.4146
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 23 | 212 | 92419 | 0.061635 | 0.00014139 | 435.9387
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | POLE | 7 | 1442 | 679412 | 0.45 | 0.0009551 | 471.1595
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | SWITCH, OH | 3 | 943 | 157426 | 0.10499 | 0.0006289 | 166.9417
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TR | NONE | 3 | 3 | 309 | 0.00020466 | 1.987e-06 | 103
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | CROSSARM | 5 | 2636 | 388943 | 0.25939 | 0.001758 | 147.5505
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 19 | 520 | 93075 | 0.061063 | 0.00034115 | 178.9904
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | UG | NONE | 67 | 1922 | 183610 | 0.12046 | 0.0012609 | 95.5307
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TIR | NONE | 15 | 60 | 11901 | 0.0078077 | 3.9363e-05 | 198.35
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 1924 | 21164 | 0.01394 | 0.0012672 | 11
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 777 | 34960 | 5542727 | 3.61 | 0.022769 | 158.5448
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WI | OTHER EQUIPMENT | 2 | 84 | 27401 | 0.018048 | 5.5326e-05 | 326.2024
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | NONE | 1007 | 14908 | 923569 | 0.60152 | 0.0097096 | 61.9512
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WI | NONE | 1 | 1 | 103 | 6.7841e-05 | 6.5865e-07 | 103
AEP-OH | 2020 | 1499447 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 345 | 0.00023008 | 1.3338e-06 | 172.5
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 2 | 306 | 0.00020408 | 1.3338e-06 | 153
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 74 | 6803 | 750914 | 0.48907 | 0.0044308 | 110.3798
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 4 | 5 | 6072 | 0.0039993 | 3.2932e-06 | 1214.4
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | TRANSFORMER, OH | 27 | 79 | 23881 | 0.015667 | 5.1829e-05 | 302.2911
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | FUSE | 1 | 37 | 5205 | 0.0034283 | 2.437e-05 | 140.6757
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 28 | 7899 | 1259719 | 0.82045 | 0.0051446 | 159.4783
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 29 | 10306 | 0.0067613 | 1.9026e-05 | 355.3793
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | FUSE | 4 | 55 | 7244 | 0.004798 | 3.6429e-05 | 131.7091
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | METERING | 2 | 2 | 158 | 0.00010366 | 1.3121e-06 | 79
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 14 | 9573 | 0.0062349 | 9.1182e-06 | 683.7857
AEP-OH | 2023 | 1524255 | PARTIAL POWER | OL | CONN/CLAMP | 4 | 14 | 1474 | 0.00096703 | 9.1848e-06 | 105.2857
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | CUTOUT | 1 | 309 | 14523 | 0.0096192 | 0.00020466 | 47
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | BREAKER | 1 | 1106 | 27650 | 0.018314 | 0.00073255 | 25
AEP-OH | 2024 | 1535393 | PARTIAL POWER | V | CONDUCTOR UG | 2 | 6 | 901 | 0.00058682 | 3.9078e-06 | 150.1667
AEP-OH | 2024 | 1535393 | PARTIAL POWER | A | CUTOUT | 1 | 1 | 93 | 6.0571e-05 | 6.513e-07 | 93
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WT | POLE | 1 | 188 | 226164 | 0.14838 | 0.00012334 | 1203
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TR | POLE | 6 | 38 | 18673 | 0.012251 | 2.493e-05 | 491.3947
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | O | NONE | 32 | 2693 | 160065 | 0.10425 | 0.0017539 | 59.4374
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | POLE | 2 | 97 | 24531 | 0.016157 | 6.3889e-05 | 252.8969
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TR | POLE | 3 | 74 | 15803 | 0.010539 | 4.9352e-05 | 213.5541
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | CONN/CLAMP | 4 | 39 | 3457 | 0.0023055 | 2.601e-05 | 88.641
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 3 | 1092 | 0.00071122 | 1.9539e-06 | 364
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 12 | 3709 | 0.0024333 | 7.8727e-06 | 309.0833
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 10 | 594 | 32636 | 0.021256 | 0.00038687 | 54.9428
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | POLE | 92 | 10001 | 3042849 | 1.9818 | 0.0065136 | 304.2545
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | METERING | 8 | 8 | 675 | 0.00043963 | 5.2104e-06 | 84.375
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | SCO | REGULATOR | 1 | 1173 | 7038 | 0.0046616 | 0.00077693 | 6
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 43 | 5504 | 0.0035847 | 2.8006e-05 | 128
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | CUTOUT | 1700 | 61724 | 6725346 | 4.4296 | 0.040654 | 108.9584
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 581 | 7381 | 788178 | 0.51709 | 0.0048424 | 106.7847
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | NONE | 1957 | 93951 | 15779365 | 10.4513 | 0.062228 | 167.9531
AEP-OH | 2022 | 1518267 | PARTIAL POWER | U | NONE | 138 | 513 | 53272 | 0.035087 | 0.00033789 | 103.8441
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | PEDESTAL | 18 | 95 | 8634 | 0.0056867 | 6.2571e-05 | 90.8842
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | INSULATOR | 14 | 2029 | 159149 | 0.10541 | 0.0013439 | 78.4372
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | POLE | 124 | 23280 | 4447968 | 2.9461 | 0.015419 | 191.0639
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 42 | 481 | 123625 | 0.081425 | 0.00031681 | 257.0166
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | NONE | 23 | 300 | 65721 | 0.04353 | 0.0001987 | 219.07
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 10 | 3014 | 86608 | 0.057364 | 0.0019963 | 28.7352
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VIN | NONE | 4 | 10 | 3092 | 0.0020365 | 6.5865e-06 | 309.2
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 4 | 9 | 1056 | 0.00069553 | 5.9278e-06 | 117.3333
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | METERING | 19 | 20 | 2393 | 0.001585 | 1.3247e-05 | 119.65
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 9 | 27 | 5111 | 0.0033663 | 1.7783e-05 | 189.2963
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | FUSE | 526 | 4140 | 411521 | 0.27445 | 0.002761 | 99.4012
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | INSULATOR | 15 | 164 | 7625 | 0.0050852 | 0.00010937 | 46.4939
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 3 | 24 | 4841 | 0.0032064 | 1.5896e-05 | 201.7083
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | FUSE | 10 | 2645 | 79265 | 0.052501 | 0.0017519 | 29.9679
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 18 | 1487 | 623313 | 0.41285 | 0.0009849 | 419.1748
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | SWITCH, OH | 12 | 900 | 31253 | 0.020843 | 0.00060022 | 34.7256
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 5 | 416 | 0.00027553 | 3.3117e-06 | 83.2
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | CUTOUT | 1395 | 49667 | 5715032 | 3.7494 | 0.032584 | 115.067
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | FUSE | 31 | 317 | 16750 | 0.011094 | 0.00020996 | 52.8391
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 26 | 3323 | 0.0022162 | 1.734e-05 | 127.8077
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | CUTOUT | 7 | 16 | 4061 | 0.0026643 | 1.0497e-05 | 253.8125
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 244 | 69607 | 0.045666 | 0.00016008 | 285.2746
AEP-OH | 2023 | 1524255 | PARTIAL POWER | UG | CONDUCTOR UG | 71 | 125 | 18029 | 0.011828 | 8.2007e-05 | 144.232
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 10 | 44 | 6308 | 0.0041547 | 2.898e-05 | 143.3636
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERO | METERING | 5 | 5 | 420 | 0.00027663 | 3.2932e-06 | 84
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WL | NONE | 6 | 20 | 3459 | 0.0022693 | 1.3121e-05 | 172.95
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 186 | 354 | 65284 | 0.042519 | 0.00023056 | 184.4181
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 3 | 2424 | 267879 | 0.17743 | 0.0016055 | 110.5111
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | SPLICE, OH | 1 | 314 | 28260 | 0.018613 | 0.00020681 | 90
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 13 | 387 | 50581 | 0.033733 | 0.0002581 | 130.7003
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | F | CUTOUT | 4 | 31 | 4720 | 0.0031478 | 2.0674e-05 | 152.2581
AEP-OH | 2023 | 1524255 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 3 | 636 | 0.00041725 | 1.9682e-06 | 212
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | CROSSARM | 27 | 13474 | 1849814 | 1.2337 | 0.008986 | 137.2877
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TOR | CONN/CLAMP | 9 | 10 | 2323 | 0.0015492 | 6.6691e-06 | 232.3
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | METERING | 4 | 10 | 1453 | 0.00096902 | 6.6691e-06 | 145.3
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 3 | 1023 | 60971 | 0.040662 | 0.00068225 | 59.6002
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 4 | 7 | 1579 | 0.0010531 | 4.6684e-06 | 225.5714
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | ARRESTER | 20 | 331 | 3124 | 0.0020347 | 0.00021558 | 9.4381
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 3 | 185 | 0.00012185 | 1.9759e-06 | 61.6667
AEP-OH | 2022 | 1518267 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 6 | 23 | 4636 | 0.0030535 | 1.5149e-05 | 201.5652
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | FO | NONE | 4 | 3696 | 2071972 | 1.3495 | 0.0024072 | 560.5985
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 4 | 4 | 295 | 0.00019674 | 2.6677e-06 | 73.75
AEP-OH | 2024 | 1535393 | PARTIAL POWER | UG | NONE | 14 | 35 | 5659 | 0.0036857 | 2.2795e-05 | 161.6857
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 52 | 24804 | 0.016273 | 3.4115e-05 | 477
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VA | TRANSFORMER, UG | 1 | 1 | 396 | 0.00026082 | 6.5865e-07 | 396
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | OL | TRANSFORMER, STATION SERVICE | 7 | 9858 | 740522 | 0.48774 | 0.0064929 | 75.1189
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 18 | 1162 | 0.00076234 | 1.1809e-05 | 64.5556
AEP-OH | 2023 | 1524255 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 3 | 165 | 0.00010825 | 1.9682e-06 | 55
AEP-OH | 2023 | 1524255 | PARTIAL POWER | FO | NONE | 2 | 3 | 653 | 0.00042841 | 1.9682e-06 | 217.6667
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | FUSE | 145 | 2024 | 147800 | 0.096262 | 0.0013182 | 73.0237
AEP-OH | 2025 | 1535393 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 44 | 53 | 8183 | 0.0053296 | 3.4519e-05 | 154.3962
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 12 | 2713 | 0.001767 | 7.8156e-06 | 226.0833
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 4 | 79 | 20337 | 0.013245 | 5.1453e-05 | 257.4304
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | O | NONE | 10 | 3169 | 154695 | 0.10075 | 0.002064 | 48.8151
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 8 | 2405 | 447451 | 0.29142 | 0.0015664 | 186.0503
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | RELAY | 1 | 186 | 42036 | 0.028034 | 0.00012405 | 226
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | CROSSARM | 3 | 3729 | 688520 | 0.44843 | 0.0024287 | 184.6393
AEP-OH | 2024 | 1535393 | PARTIAL POWER | FW | NONE | 1 | 1 | 57 | 3.7124e-05 | 6.513e-07 | 57
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 16 | 1731 | 851731 | 0.55473 | 0.0011274 | 492.0456
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 1 | 71 | 4.6242e-05 | 6.513e-07 | 71
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 17 | 23153 | 0.01519 | 1.1153e-05 | 1361.9412
AEP-OH | 2020 | 1499447 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 98 | 6.5357e-05 | 6.6691e-07 | 98
AEP-OH | 2022 | 1518267 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 485 | 0.00031944 | 6.5865e-07 | 485
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 2 | 392 | 0.00025717 | 1.3121e-06 | 196
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 895 | 275710 | 0.17957 | 0.00058291 | 308.0559
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 1 | 4 | 2560 | 0.0016861 | 2.6346e-06 | 640
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 14 | 5157 | 758650 | 0.49772 | 0.0033833 | 147.1107
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | FUSE | 21 | 53 | 10887 | 0.0071425 | 3.4771e-05 | 205.4151
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 19 | 1074 | 126864 | 0.084607 | 0.00071626 | 118.1229
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 15 | 476 | 88077 | 0.057784 | 0.00031228 | 185.0357
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 372 | 2012 | 184091 | 0.1199 | 0.0013104 | 91.4965
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VIN | NONE | 202 | 3298 | 406387 | 0.26468 | 0.002148 | 123.2223
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 1 | 308 | 0.00020207 | 6.5606e-07 | 308
AEP-OH | 2023 | 1524255 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 2 | 2 | 275 | 0.00018042 | 1.3121e-06 | 137.5
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 9 | 143 | 36930 | 0.024052 | 9.3136e-05 | 258.2517
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | WU | NONE | 9 | 12190 | 1658182 | 1.0879 | 0.0079973 | 136.0281
AEP-OH | 2021 | 1509795 | PARTIAL POWER | U | FUSE | 1 | 5 | 185 | 0.00012253 | 3.3117e-06 | 37
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | CUTOUT | 36 | 1495 | 493310 | 0.32129 | 0.00097369 | 329.9732
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | CE | NONE | 26 | 252 | 39037 | 0.025425 | 0.00016413 | 154.9087
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 4 | 235 | 40532 | 0.026398 | 0.00015306 | 172.4766
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 6 | 5845 | 3803444 | 2.4953 | 0.0038347 | 650.7175
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 1 | 59 | 3.886e-05 | 6.5865e-07 | 59
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | CUTOUT | 5 | 1145 | 199572 | 0.13093 | 0.00075119 | 174.2987
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 1 | 64 | 4.2682e-05 | 6.6691e-07 | 64
AEP-OH | 2023 | 1524255 | PARTIAL POWER | UG | SPLICE, UG | 1 | 1 | 60 | 3.9363e-05 | 6.5606e-07 | 60
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OU | SPLICE, UG | 1 | 10 | 3430 | 0.0022503 | 6.5606e-06 | 343
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | SCO | SWITCH, OH | 1 | 1 | 425 | 0.0002768 | 6.513e-07 | 425
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | ARRESTER | 8 | 6994 | 818126 | 0.53284 | 0.0045552 | 116.9754
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 58 | 9971 | 0.0066498 | 3.8681e-05 | 171.9138
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 2 | 28 | 4004 | 0.0026703 | 1.8674e-05 | 143
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 38 | 8546 | 0.0056994 | 2.5343e-05 | 224.8947
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 3 | 931 | 0.0006209 | 2.0007e-06 | 310.3333
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | JUMPER/RISER | 4 | 29 | 3303 | 0.0021512 | 1.8888e-05 | 113.8966
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | POLE | 76 | 4843 | 1371557 | 0.89329 | 0.0031542 | 283.204
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 9 | 3951 | 444986 | 0.28982 | 0.0025733 | 112.6262
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OU | CUTOUT | 1 | 1 | 60 | 3.9078e-05 | 6.513e-07 | 60
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | V | NONE | 8 | 9843 | 935153 | 0.60906 | 0.0064107 | 95.0069
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 31 | 2393 | 0.0015586 | 2.019e-05 | 77.1935
AEP-OH | 2021 | 1509795 | PARTIAL POWER | VA | TRANSFORMER, UG | 1 | 5 | 2105 | 0.0013942 | 3.3117e-06 | 421
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 1 | 1 | 240 | 0.00015745 | 6.5606e-07 | 240
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 3 | 1773 | 0.0011632 | 1.9682e-06 | 591
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | CROSSARM | 3 | 7 | 406 | 0.00026443 | 4.5591e-06 | 58
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 1 | 5 | 385 | 0.00025075 | 3.2565e-06 | 77
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 86 | 4872 | 0.0031731 | 5.6012e-05 | 56.6512
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 10 | 965 | 0.00064357 | 6.6691e-06 | 96.5
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UG | METERING | 1 | 1 | 388 | 0.00025699 | 6.6234e-07 | 388
AEP-OH | 2023 | 1524255 | PARTIAL POWER | U | CUTOUT | 2 | 3 | 204 | 0.00013384 | 1.9682e-06 | 68
AEP-OH | 2023 | 1524255 | DISTRIBUTION SOURCE | UG | NONE | 1 | 7 | 1092 | 0.00071642 | 4.5924e-06 | 156
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 93 | 6.2023e-05 | 6.6691e-07 | 93
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | SCO | NONE | 23 | 19140 | 849078 | 0.55924 | 0.012606 | 44.3614
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 709 | 53175 | 0.035023 | 0.00046698 | 75
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 5 | 211 | 38364 | 0.025268 | 0.00013897 | 181.8199
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | METERING | 9 | 14 | 954 | 0.00062835 | 9.221e-06 | 68.1429
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | INSULATOR | 7 | 351 | 82486 | 0.054634 | 0.00023248 | 235.0028
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | FUSE | 8 | 23 | 14367 | 0.0094628 | 1.5149e-05 | 624.6522
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 6 | 272 | 46242 | 0.030628 | 0.00018016 | 170.0074
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 6 | 4940 | 513530 | 0.34013 | 0.003272 | 103.9534
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 93 | 6384 | 773175 | 0.50725 | 0.0041883 | 121.1114
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 5 | 1124 | 201134 | 0.13248 | 0.00074032 | 178.9448
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | BREAKER | 1 | 1 | 91 | 5.9937e-05 | 6.5865e-07 | 91
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 37 | 8351 | 0.0055004 | 2.437e-05 | 225.7027
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VA | CUTOUT | 1 | 4 | 364 | 0.00024276 | 2.6677e-06 | 91
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CE | METERING | 4 | 7 | 1096 | 0.00072188 | 4.6105e-06 | 156.5714
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AO | NONE | 18 | 18399 | 1731838 | 1.155 | 0.012271 | 94.1267
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | ARRESTER | 8 | 3682 | 635094 | 0.4183 | 0.0024251 | 172.4861
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SO | NONE | 4 | 23 | 1288 | 0.000845 | 1.5089e-05 | 56
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | ARRESTER | 14 | 2755 | 496798 | 0.32593 | 0.0018074 | 180.326
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | CUTOUT | 42 | 400 | 30753 | 0.02051 | 0.00026677 | 76.8825
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | ARRESTER | 5 | 134 | 12016 | 0.0079587 | 8.8754e-05 | 89.6716
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VA | NONE | 5 | 175 | 12741 | 0.0084971 | 0.00011671 | 72.8057
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 2 | 1796 | 371392 | 0.24769 | 0.0011978 | 206.7884
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AF | INSULATOR | 3 | 2075 | 292217 | 0.19171 | 0.0013613 | 140.8275
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | INSULATOR | 14 | 1315 | 401139 | 0.26126 | 0.00085646 | 305.0487
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 6 | 529 | 0.00035038 | 3.974e-06 | 88.1667
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 2 | 179 | 0.00011743 | 1.3121e-06 | 89.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 16 | 2629 | 0.0017316 | 1.0538e-05 | 164.3125
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 35 | 19950 | 1802458 | 1.2021 | 0.013305 | 90.3488
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | METERING | 2 | 2 | 338 | 0.00022387 | 1.3247e-06 | 169
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 7 | 1591 | 0.0010479 | 4.6105e-06 | 227.2857
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 2 | 42 | 7465 | 0.0049785 | 2.801e-05 | 177.7381
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WW | NONE | 5 | 30 | 5443 | 0.0036051 | 1.987e-05 | 181.4333
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 1112 | 49727 | 0.032936 | 0.00073652 | 44.7185
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 2 | 184 | 0.00012187 | 1.3247e-06 | 92
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | R | POLE | 1 | 782 | 4692 | 0.0031077 | 0.00051795 | 6
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | SWITCH, OH | 1 | 506 | 71122 | 0.047107 | 0.00033514 | 140.5573
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | AF | NONE | 4 | 4299 | 354162 | 0.23458 | 0.0028474 | 82.3824
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 597 | 86188 | 0.057086 | 0.00039542 | 144.3685
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | NONE | 291 | 12372 | 2062190 | 1.3529 | 0.0081168 | 166.682
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CE | NONE | 35 | 932 | 79184 | 0.051949 | 0.00061145 | 84.9614
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TR | SPLICE, OH | 1 | 1 | 81 | 5.3141e-05 | 6.5606e-07 | 81
AEP-OH | 2020 | 1499447 | PARTIAL POWER | UB | TRANSFORMER, OH | 1 | 1 | 105 | 7.0026e-05 | 6.6691e-07 | 105
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 777 | 11215 | 1827562 | 1.1903 | 0.0073043 | 162.9569
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 10 | 321 | 17781 | 0.011858 | 0.00021408 | 55.3925
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | SPLICE, OH | 3 | 6 | 838 | 0.00055887 | 4.0015e-06 | 139.6667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | ARRESTER | 41 | 3538 | 281385 | 0.18766 | 0.0023595 | 79.5322
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 26 | 709 | 448701 | 0.29437 | 0.00046515 | 632.8646
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | WL | TRANSFORMER, STATION SERVICE | 2 | 1795 | 911855 | 0.60059 | 0.0011823 | 507.9972
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WU | SPLICE, OH | 1 | 2 | 314 | 0.00020681 | 1.3173e-06 | 157
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | FUSE | 20 | 217 | 7266 | 0.0048458 | 0.00014472 | 33.4839
AEP-OH | 2020 | 1499447 | DISTRIBUTION SOURCE | OU | NONE | 1 | 672 | 50400 | 0.033612 | 0.00044817 | 75
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | METERING | 33 | 49 | 4979 | 0.0032428 | 3.1914e-05 | 101.6122
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | BREAKER | 1 | 2 | 148 | 9.7097e-05 | 1.3121e-06 | 74
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OL | FUSE | 7 | 200 | 39708 | 0.026051 | 0.00013121 | 198.54
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | FUSE | 23 | 69 | 5360 | 0.0035165 | 4.5268e-05 | 77.6812
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 6 | 10 | 7098 | 0.0046567 | 6.5606e-06 | 709.8
AEP-OH | 2023 | 1524255 | PARTIAL POWER | ERF | NONE | 6 | 34 | 2204 | 0.001446 | 2.2306e-05 | 64.8235
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TR | CONDUCTOR UG | 1 | 11 | 4378 | 0.0028722 | 7.2166e-06 | 398
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | TRANSFORMER, GROUNDING | 1 | 3 | 4077 | 0.0027004 | 1.987e-06 | 1359
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | FUSE | 3 | 318 | 17232 | 0.011413 | 0.00021062 | 54.1887
AEP-OH | 2023 | 1524255 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 74 | 4.8548e-05 | 6.5606e-07 | 74
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 3 | 4939 | 482757 | 0.31975 | 0.0032713 | 97.7439
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | V | OTHER EQUIPMENT | 10 | 8971 | 1209814 | 0.78795 | 0.0058428 | 134.8583
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | POLE | 9 | 920 | 430622 | 0.28719 | 0.00061356 | 468.0674
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WU | CONDUCTOR UG | 2 | 43 | 4838 | 0.0031865 | 2.8322e-05 | 112.5116
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | POLE | 3 | 298 | 98348 | 0.06559 | 0.00019874 | 330.0268
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 4 | 16 | 2679 | 0.0017576 | 1.0497e-05 | 167.4375
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 2 | 90 | 14270 | 0.009294 | 5.8617e-05 | 158.5556
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 556 | 48824 | 0.031799 | 0.00036212 | 87.8129
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 118 | 1079 | 131972 | 0.085953 | 0.00070275 | 122.3095
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 27 | 563 | 78350 | 0.051029 | 0.00036668 | 139.1652
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 110 | 19111 | 0.012447 | 7.1643e-05 | 173.7364
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 1 | 1 | 123 | 8.1468e-05 | 6.6234e-07 | 123
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERO | FUSE | 1 | 58 | 4176 | 0.0027397 | 3.8051e-05 | 72
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | SPLICE, OH | 5 | 14 | 10111 | 0.0065853 | 9.1182e-06 | 722.2143
AEP-OH | 2025 | 1535393 | DISTRIBUTION SOURCE | VA | POLE | 1 | 9 | 5112 | 0.0033294 | 5.8617e-06 | 568
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | TRANSFORMER, UG | 1 | 1 | 198 | 0.00012896 | 6.513e-07 | 198
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 4 | 436 | 0.00028397 | 2.6052e-06 | 109
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WT | NONE | 1 | 13 | 936 | 0.00061407 | 8.5288e-06 | 72
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 1 | 5 | 5870 | 0.0038231 | 3.2565e-06 | 1174
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 165 | 57807 | 0.03765 | 0.00010746 | 350.3455
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 64 | 6336 | 0.0041266 | 4.1683e-05 | 99
AEP-OH | 2024 | 1535393 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 463 | 57875 | 0.037694 | 0.00030155 | 125
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 6 | 612 | 0.00040815 | 4.0015e-06 | 102
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WFS | PEDESTAL | 1 | 1 | 47 | 3.1345e-05 | 6.6691e-07 | 47
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AB | BREAKER | 1 | 905 | 199100 | 0.13114 | 0.00059607 | 220
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | FUSE | 1 | 1 | 67 | 4.3956e-05 | 6.5606e-07 | 67
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 979 | 7832 | 0.0051875 | 0.00064843 | 8
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 354 | 97470 | 0.065004 | 0.00023609 | 275.339
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 11 | 1485 | 0.00097809 | 7.2451e-06 | 135
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | POLE | 1 | 4 | 1696 | 0.0011127 | 2.6242e-06 | 424
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | NONE | 1032 | 19924 | 1749370 | 1.1587 | 0.013196 | 87.8021
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VIN | NONE | 149 | 1230 | 228798 | 0.1507 | 0.00081013 | 186.0146
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TR | NONE | 45 | 1498 | 167514 | 0.11033 | 0.00098665 | 111.8251
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | CROSSARM | 335 | 11334 | 798335 | 0.52877 | 0.007507 | 70.4372
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | CUTOUT | 48 | 149 | 13855 | 0.0091767 | 9.8689e-05 | 92.9866
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | SPLICE, OH | 39 | 3495 | 482098 | 0.31753 | 0.002302 | 137.9393
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 43 | 791 | 119763 | 0.078881 | 0.00052099 | 151.4071
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 30 | 75 | 20098 | 0.013312 | 4.9676e-05 | 267.9733
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 22 | 2084 | 71891 | 0.047616 | 0.0013803 | 34.4966
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERO | NONE | 11 | 1916 | 192887 | 0.12704 | 0.001262 | 100.6717
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AB | SWITCH, OH | 1 | 946 | 232338 | 0.15495 | 0.0006309 | 245.6004
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 16 | 24880 | 0.016204 | 1.0421e-05 | 1555
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | FUSE | 11 | 79 | 10139 | 0.0066035 | 5.1453e-05 | 128.3418
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | GUY/ANCHOR | 2 | 152 | 11831 | 0.0078362 | 0.00010068 | 77.8355
AEP-OH | 2022 | 1518267 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 2 | 572 | 0.00037675 | 1.3173e-06 | 286
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | O | POLE | 1 | 12 | 16848 | 0.010973 | 7.8156e-06 | 1404
AEP-OH | 2023 | 1524255 | PARTIAL POWER | AF | REGULATOR | 1 | 1 | 264 | 0.0001732 | 6.5606e-07 | 264
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | POLE | 3 | 48 | 2677 | 0.0017853 | 3.2012e-05 | 55.7708
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | AF | BREAKER | 1 | 715 | 50050 | 0.032598 | 0.00046568 | 70
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 8 | 84 | 35495 | 0.023118 | 5.4709e-05 | 422.5595
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | POLE | 1 | 1 | 150 | 9.7695e-05 | 6.513e-07 | 150
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 16 | 5131 | 0.0033662 | 1.0497e-05 | 320.6875
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | F | POLE HARDWARE | 2 | 17 | 6163 | 0.0041102 | 1.1338e-05 | 362.5294
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 1 | 57 | 3.7543e-05 | 6.5865e-07 | 57
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 6 | 72 | 12149 | 0.0079126 | 4.6894e-05 | 168.7361
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | CUTOUT | 3 | 1730 | 115626 | 0.075307 | 0.0011267 | 66.8358
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | GUY/ANCHOR | 1 | 328 | 116112 | 0.076176 | 0.00021519 | 354
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 3 | 486 | 0.0003201 | 1.9759e-06 | 162
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 146 | 9.509e-05 | 6.513e-07 | 146
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 1 | 1020 | 0.00066918 | 6.5606e-07 | 1020
AEP-OH | 2024 | 1535393 | PARTIAL POWER | VIN | FUSE | 1 | 3 | 558 | 0.00036342 | 1.9539e-06 | 186
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TOR | SWITCH, OH | 1 | 1 | 191 | 0.0001244 | 6.513e-07 | 191
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AF | NONE | 3 | 1441 | 141218 | 0.09418 | 0.00096102 | 98
AEP-OH | 2024 | 1535393 | PARTIAL POWER | V | METERING | 2 | 5 | 428 | 0.00027876 | 3.2565e-06 | 85.6
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CO | CONN/CLAMP | 57 | 148 | 20485 | 0.013492 | 9.748e-05 | 138.4122
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | CONDUCTOR UG | 584 | 1283 | 316537 | 0.20966 | 0.00084978 | 246.7163
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | CONN/CLAMP | 718 | 2033 | 262107 | 0.1736 | 0.0013465 | 128.9262
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERO | NONE | 910 | 37951 | 1920488 | 1.272 | 0.025137 | 50.6044
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | CABLE TERMINATOR | 10 | 23 | 3811 | 0.0025101 | 1.5149e-05 | 165.6957
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 27 | 5916 | 814835 | 0.53669 | 0.0038965 | 137.7341
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OL | NONE | 61 | 8270 | 492434 | 0.32616 | 0.0054776 | 59.5446
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | BREAKER | 1 | 3 | 321 | 0.00021143 | 1.9759e-06 | 107
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | CROSSARM | 1 | 293 | 70661 | 0.046541 | 0.00019298 | 241.1638
AEP-OH | 2022 | 1518267 | PARTIAL POWER | UG | NONE | 10 | 21 | 7517 | 0.004951 | 1.3832e-05 | 357.9524
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 150 | 8289 | 2165284 | 1.4441 | 0.005528 | 261.2238
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | REGULATOR | 16 | 10048 | 664599 | 0.44323 | 0.0067011 | 66.1424
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 10 | 32 | 4093 | 0.0027297 | 2.1341e-05 | 127.9062
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | SCO | SWITCH, OH | 2 | 22 | 5483 | 0.0036316 | 1.4572e-05 | 249.2273
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 2 | 12 | 7.9481e-06 | 1.3247e-06 | 6
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | POLE HARDWARE | 2 | 216 | 33397 | 0.02212 | 0.00014307 | 154.6157
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 13 | 6623 | 1844216 | 1.2147 | 0.0043622 | 278.4563
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | NONE | 5 | 656 | 61315 | 0.040385 | 0.00043207 | 93.468
AEP-OH | 2021 | 1509795 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 2 | 308 | 0.000204 | 1.3247e-06 | 154
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 350 | 77445 | 0.051009 | 0.00023053 | 221.2714
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 5 | 934 | 154345 | 0.10126 | 0.00061276 | 165.2516
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | CROSSARM | 3 | 4976 | 517584 | 0.3409 | 0.0032774 | 104.0161
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 207 | 1666 | 132497 | 0.086926 | 0.001093 | 79.53
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WU | NONE | 12 | 91 | 20943 | 0.013967 | 6.0689e-05 | 230.1429
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | SPLICE, OH | 20 | 21 | 2695 | 0.001785 | 1.3909e-05 | 128.3333
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | ARRESTER | 9 | 77 | 12866 | 0.0085217 | 5.1e-05 | 167.0909
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 4 | 74 | 12225 | 0.0080519 | 4.874e-05 | 165.2027
AEP-OH | 2020 | 1499447 | PARTIAL POWER | OL | NONE | 10 | 86 | 3007 | 0.0020054 | 5.7354e-05 | 34.9651
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 25 | 71 | 26324 | 0.017556 | 4.7351e-05 | 370.7606
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 86 | 2222 | 0.0014819 | 5.7354e-05 | 25.8372
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | POLE | 4 | 216 | 324603 | 0.21648 | 0.00014405 | 1502.7917
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 7 | 1895 | 0.0012481 | 4.6105e-06 | 270.7143
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 3 | 1113 | 120923 | 0.079645 | 0.00073307 | 108.646
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | SWITCH, OH | 3 | 3581 | 96785 | 0.063747 | 0.0023586 | 27.0274
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | RELAY | 1 | 631 | 77613 | 0.051119 | 0.00041561 | 123
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 11 | 319 | 0.00021011 | 7.2451e-06 | 29
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 697 | 43653 | 5940537 | 3.8691 | 0.028431 | 136.0854
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | POLE HARDWARE | 5 | 1042 | 42007 | 0.027823 | 0.00069016 | 40.3138
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 2 | 47 | 1214 | 0.00080408 | 3.113e-05 | 25.8298
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 19 | 163 | 6167 | 0.0041128 | 0.00010871 | 37.8344
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UB | TRANSFORMER, GROUNDING | 1 | 153 | 1071 | 0.00071426 | 0.00010204 | 7
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | NETWORK TRANSFORMER | 3 | 18 | 1192 | 0.00078511 | 1.1856e-05 | 66.2222
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | POLE | 6 | 239 | 81710 | 0.054493 | 0.00015939 | 341.8828
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 12 | 1329 | 86047 | 0.056452 | 0.0008719 | 64.7457
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | SCO | REGULATOR | 5 | 3353 | 261904 | 0.17182 | 0.0021998 | 78.1103
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | POLE | 1 | 1 | 65 | 4.2812e-05 | 6.5865e-07 | 65
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 234 | 25974 | 0.017204 | 0.00015499 | 111
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | SPLICE, UG | 16 | 44 | 10697 | 0.0069669 | 2.8657e-05 | 243.1136
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VA | NONE | 6 | 35 | 3641 | 0.0023887 | 2.2962e-05 | 104.0286
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 3 | 5 | 1093 | 0.00071707 | 3.2803e-06 | 218.6
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 2551 | 157652 | 0.10514 | 0.0017013 | 61.8001
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 753 | 18072 | 0.011856 | 0.00049401 | 24
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | NONE | 63 | 1189 | 77290 | 0.050339 | 0.00077439 | 65.0042
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | CROSSARM | 2 | 164 | 14113 | 0.0092589 | 0.00010759 | 86.0549
AEP-OH | 2024 | 1535393 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 6 | 6 | 652 | 0.00042465 | 3.9078e-06 | 108.6667
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | POLE HARDWARE | 2 | 2 | 430 | 0.00028481 | 1.3247e-06 | 215
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 1 | 35 | 2.3182e-05 | 6.6234e-07 | 35
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WI | CAPACITOR | 1 | 9 | 2655 | 0.0017707 | 6.0022e-06 | 295
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | METERING | 1 | 2 | 290 | 0.00019101 | 1.3173e-06 | 145
AEP-OH | 2020 | 1499447 | PARTIAL POWER | V | CIRCUIT SWITCHER | 1 | 1 | 114 | 7.6028e-05 | 6.6691e-07 | 114
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | INSULATOR | 3 | 421 | 98812 | 0.064356 | 0.0002742 | 234.7078
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | V | METERING | 7 | 8 | 825 | 0.00053732 | 5.2104e-06 | 103.125
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | SPLICE, OH | 2 | 2 | 213 | 0.00013873 | 1.3026e-06 | 106.5
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 2 | 62 | 4.0381e-05 | 1.3026e-06 | 31
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 25 | 1.6282e-05 | 6.513e-07 | 25
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 25 | 7175 | 0.0046731 | 1.6282e-05 | 287
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 9 | 657 | 0.0004279 | 5.8617e-06 | 73
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 199 | 0.00012961 | 6.513e-07 | 199
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SO | TRANSFORMER, OH | 1 | 6 | 900 | 0.00059045 | 3.9363e-06 | 150
AEP-OH | 2020 | 1499447 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 14 | 854 | 0.00056954 | 9.3368e-06 | 61
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | NONE | 3682 | 72725 | 5482082 | 3.631 | 0.048169 | 75.381
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 11 | 1582 | 401995 | 0.26477 | 0.001042 | 254.1056
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | NONE | 172 | 10167 | 1053267 | 0.69373 | 0.0066965 | 103.5966
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 288 | 1934 | 212234 | 0.14057 | 0.001281 | 109.7384
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 764 | 3668 | 334021 | 0.22124 | 0.0024295 | 91.0635
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FO | NONE | 42 | 3935 | 340673 | 0.22438 | 0.0025918 | 86.5751
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 7 | 8567 | 1037957 | 0.68365 | 0.0056426 | 121.1576
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | FUSE | 22 | 515 | 84791 | 0.055847 | 0.0003392 | 164.6427
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | FUSE | 4 | 22 | 2856 | 0.0018811 | 1.449e-05 | 129.8182
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CO | CONDUCTOR UG | 22 | 41 | 7365 | 0.0048509 | 2.7004e-05 | 179.6341
AEP-OH | 2021 | 1509795 | PARTIAL POWER | ERF | CONDUCTOR UG | 2 | 2 | 417 | 0.0002762 | 1.3247e-06 | 208.5
AEP-OH | 2021 | 1509795 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 11 | 19 | 2805 | 0.0018579 | 1.2584e-05 | 147.6316
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | FUSE | 2 | 16 | 2015 | 0.0013346 | 1.0597e-05 | 125.9375
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | NETWORK PROTECTOR | 1 | 4 | 1644 | 0.0010889 | 2.6494e-06 | 411
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | ARRESTER | 9 | 539 | 118186 | 0.07882 | 0.00035947 | 219.269
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | INSULATOR | 10 | 791 | 116349 | 0.077063 | 0.00052391 | 147.091
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | POLE | 3 | 1278 | 118814 | 0.078695 | 0.00084647 | 92.9687
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | PEDESTAL | 1 | 1 | 98 | 6.4547e-05 | 6.5865e-07 | 98
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1410 | 52110 | 15044526 | 9.8701 | 0.034187 | 288.7071
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 1761 | 417219 | 0.27634 | 0.0011664 | 236.9216
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | NONE | 54 | 4462 | 639988 | 0.42682 | 0.0029758 | 143.4307
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 25 | 3078 | 0.0020273 | 1.6466e-05 | 123.12
AEP-OH | 2022 | 1518267 | PARTIAL POWER | O | NONE | 5 | 37 | 4752 | 0.0031299 | 2.437e-05 | 128.4324
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 4 | 889 | 359742 | 0.23694 | 0.00058554 | 404.6592
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WI | POLE | 5 | 82 | 133836 | 0.088151 | 5.4009e-05 | 1632.1463
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 3 | 48 | 5321 | 0.0035243 | 3.1792e-05 | 110.8542
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OU | NONE | 9 | 40 | 2733 | 0.0018001 | 2.6346e-05 | 68.325
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FO | CUTOUT | 2 | 69 | 3849 | 0.0025494 | 4.5702e-05 | 55.7826
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | CUTOUT | 3 | 36 | 3284 | 0.0021751 | 2.3844e-05 | 91.2222
AEP-OH | 2021 | 1509795 | PARTIAL POWER | V | NONE | 1 | 1 | 57 | 3.7753e-05 | 6.6234e-07 | 57
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | CONN/CLAMP | 8 | 1002 | 36901 | 0.024441 | 0.00066367 | 36.8273
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VA | CONN/CLAMP | 2 | 2 | 207 | 0.00013634 | 1.3173e-06 | 103.5
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 10 | 1330 | 0.00087256 | 6.5606e-06 | 133
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | CONN/CLAMP | 4 | 30 | 2751 | 0.0018347 | 2.0007e-05 | 91.7
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 2 | 3 | 230 | 0.00015339 | 2.0007e-06 | 76.6667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | FUSE | 1 | 14 | 784 | 0.00052286 | 9.3368e-06 | 56
AEP-OH | 2023 | 1524255 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 5 | 9 | 743 | 0.00048745 | 5.9045e-06 | 82.5556
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 59 | 9381 | 0.0061788 | 3.886e-05 | 159
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | SPLICE, OH | 4 | 7 | 602 | 0.00039873 | 4.6364e-06 | 86
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 17 | 11905 | 801103 | 0.52176 | 0.0077537 | 67.2913
AEP-OH | 2024 | 1535393 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 82 | 5.3407e-05 | 6.513e-07 | 82
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 19 | 203 | 32903 | 0.02143 | 0.00013221 | 162.0837
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 266 | 0.00017325 | 6.513e-07 | 266
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | V | CONN/CLAMP | 1 | 4 | 32 | 2.0842e-05 | 2.6052e-06 | 8
AEP-OH | 2024 | 1535393 | PARTIAL POWER | ERF | CONN/CLAMP | 7 | 20 | 5822 | 0.0037919 | 1.3026e-05 | 291.1
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 4 | 1508 | 0.00098216 | 2.6052e-06 | 377
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | CONDUCTOR UG | 6 | 29 | 4608 | 0.0030012 | 1.8888e-05 | 158.8966
AEP-OH | 2023 | 1524255 | PARTIAL POWER | V | CONN/CLAMP | 2 | 2 | 176 | 0.00011547 | 1.3121e-06 | 88
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 4 | 426 | 41866 | 0.027267 | 0.00027745 | 98.277
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 2 | 2622 | 78226 | 0.05217 | 0.0017486 | 29.8345
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 18 | 1099 | 115914 | 0.075495 | 0.00071578 | 105.4722
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | OU | NONE | 8 | 159 | 17899 | 0.011658 | 0.00010356 | 112.5723
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | METERING | 25 | 38 | 4187 | 0.002727 | 2.4749e-05 | 110.1842
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 22 | 4620 | 0.0030811 | 1.4672e-05 | 210
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 37 | 2.4098e-05 | 6.513e-07 | 37
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 3 | 3475 | 0.0022633 | 1.9539e-06 | 1158.3333
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | FUSE | 9 | 25 | 1590 | 0.0010356 | 1.6282e-05 | 63.6
AEP-OH | 2022 | 1518267 | PARTIAL POWER | U | CONN/CLAMP | 2 | 2 | 154 | 0.00010143 | 1.3173e-06 | 77
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 1 | 10 | 6.5606e-06 | 6.5606e-07 | 10
AEP-OH | 2023 | 1524255 | PARTIAL POWER | O | FUSE | 2 | 2 | 877 | 0.00057536 | 1.3121e-06 | 438.5
AEP-OH | 2025 | 1535393 | PARTIAL POWER | UG | NONE | 2 | 5 | 441 | 0.00028722 | 3.2565e-06 | 88.2
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 2 | 226 | 0.00015072 | 1.3338e-06 | 113
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 96 | 6.323e-05 | 6.5865e-07 | 96
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 735 | 171255 | 0.11421 | 0.00049018 | 233
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | METERING | 2 | 2 | 218 | 0.00014302 | 1.3121e-06 | 109
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | CUTOUT | 480 | 19903 | 2122541 | 1.3824 | 0.012963 | 106.6443
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FW | POLE | 5 | 519 | 35071 | 0.022842 | 0.00033802 | 67.5742
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | METERING | 33 | 71 | 2503 | 0.0016302 | 4.6242e-05 | 35.2535
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | CUTOUT | 3 | 13 | 696 | 0.0004533 | 8.4669e-06 | 53.5385
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | NONE | 74 | 1274 | 230160 | 0.1499 | 0.00082975 | 180.6593
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 3 | 3712 | 1028410 | 0.6698 | 0.0024176 | 277.0501
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 8 | 41 | 7790 | 0.0050736 | 2.6703e-05 | 190
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 930 | 147111 | 0.095813 | 0.00060571 | 158.1839
AEP-OH | 2025 | 1535393 | PARTIAL POWER | U | NONE | 24 | 87 | 11449 | 0.0074567 | 5.6663e-05 | 131.5977
AEP-OH | 2025 | 1535393 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 3 | 180 | 0.00011723 | 1.9539e-06 | 60
AEP-OH | 2025 | 1535393 | PARTIAL POWER | U | FUSE | 2 | 3 | 348 | 0.00022665 | 1.9539e-06 | 116
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | SCO | SWITCH, OH | 3 | 1011 | 7077 | 0.0046092 | 0.00065846 | 7
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 5 | 610 | 0.00040177 | 3.2932e-06 | 122
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | SWITCH, OH | 5 | 324 | 52331 | 0.034332 | 0.00021256 | 161.5154
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | POLE | 1 | 30 | 1050 | 0.00069546 | 1.987e-05 | 35
AEP-OH | 2020 | 1499447 | PARTIAL POWER | OL | METERING | 1 | 1 | 71 | 4.7351e-05 | 6.6691e-07 | 71
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 1882 | 707632 | 0.46869 | 0.0012465 | 376
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | FUSE | 2 | 49 | 5509 | 0.0036142 | 3.2147e-05 | 112.4286
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | INSULATOR | 9 | 4266 | 210631 | 0.13951 | 0.0028255 | 49.3744
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | CUTOUT | 4 | 2259 | 130033 | 0.086721 | 0.0015066 | 57.5622
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | CONN/CLAMP | 5 | 76 | 17273 | 0.01125 | 4.9499e-05 | 227.2763
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | SWITCH, OH | 4 | 291 | 41028 | 0.026721 | 0.00018953 | 140.9897
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | SWITCH, OH | 2 | 2278 | 609226 | 0.39969 | 0.0014945 | 267.439
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ERF | FUSE | 2 | 29 | 6474 | 0.0042165 | 1.8888e-05 | 223.2414
AEP-OH | 2023 | 1524255 | PARTIAL POWER | A | CUTOUT | 2 | 3 | 312 | 0.00020469 | 1.9682e-06 | 104
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TOR | POLE | 3 | 9 | 3159 | 0.0020575 | 5.8617e-06 | 351
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 484 | 0.00031753 | 6.5606e-07 | 484
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | FUSE | 2 | 5 | 4334 | 0.0028227 | 3.2565e-06 | 866.8
AEP-OH | 2024 | 1535393 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 7 | 3505 | 0.0022828 | 4.5591e-06 | 500.7143
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 2 | 112 | 2375 | 0.0015468 | 7.2945e-05 | 21.2054
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | SPLICE, OH | 2 | 4 | 88 | 5.7733e-05 | 2.6242e-06 | 22
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WI | NONE | 3 | 11 | 14209 | 0.0094112 | 7.2858e-06 | 1291.7273
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 3 | 858 | 0.00056512 | 1.9759e-06 | 286
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 1 | 321 | 65484 | 0.042961 | 0.00021059 | 204
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 3 | 4680 | 767730 | 0.51201 | 0.0031212 | 164.0449
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 136 | 5660 | 1189333 | 0.78335 | 0.0037279 | 210.1295
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | NONE | 1846 | 35031 | 2953785 | 1.9564 | 0.023202 | 84.3192
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CE | CONN/CLAMP | 4 | 5 | 525 | 0.00034579 | 3.2932e-06 | 105
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | CUTOUT | 7 | 232 | 22860 | 0.015057 | 0.00015281 | 98.5345
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | NONE | 55 | 2680 | 247736 | 0.16317 | 0.0017652 | 92.4388
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | METERING | 56 | 74 | 6537 | 0.0043297 | 4.9013e-05 | 88.3378
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | SPLICE, OH | 26 | 33 | 4646 | 0.0030601 | 2.1735e-05 | 140.7879
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | POLE | 4 | 4072 | 622757 | 0.41018 | 0.002682 | 152.9364
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | REGULATOR | 2 | 711 | 25994 | 0.017121 | 0.0004683 | 36.5598
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 34 | 7582 | 0.0049939 | 2.2394e-05 | 223
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | NONE | 6 | 99 | 18158 | 0.01196 | 6.5206e-05 | 183.4141
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 900 | 81999 | 0.054311 | 0.00059611 | 91.11
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2749 | 118817 | 28969148 | 19.3199 | 0.079241 | 243.8132
AEP-OH | 2020 | 1499447 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 36 | 2.4009e-05 | 6.6691e-07 | 36
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | POLE | 6 | 142 | 30978 | 0.020518 | 9.4053e-05 | 218.1549
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | CAPACITOR | 2 | 2442 | 271294 | 0.17969 | 0.0016174 | 111.095
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FW | CONDUCTOR UG | 1 | 1 | 218 | 0.00014439 | 6.6234e-07 | 218
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 27 | 13893 | 0.0092019 | 1.7883e-05 | 514.5556
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | SWITCH, OH | 23 | 15803 | 1326500 | 0.8786 | 0.010467 | 83.9398
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 699 | 15467 | 1958613 | 1.285 | 0.010147 | 126.6317
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 16 | 1664 | 0.0011021 | 1.0597e-05 | 104
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | POLE | 426 | 96761 | 16845496 | 11.0516 | 0.063481 | 174.0939
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 5 | 219 | 46670 | 0.030739 | 0.00014424 | 213.105
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 7 | 17 | 1644 | 0.0010786 | 1.1153e-05 | 96.7059
AEP-OH | 2021 | 1509795 | PARTIAL POWER | VIN | NONE | 2 | 4 | 522 | 0.00034574 | 2.6494e-06 | 130.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 6 | 59 | 13687 | 0.0090149 | 3.886e-05 | 231.9831
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 12 | 159 | 83716 | 0.055831 | 0.00010604 | 526.5157
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 21 | 2480 | 0.0016334 | 1.3832e-05 | 118.0952
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | NONE | 82 | 6873 | 449214 | 0.29959 | 0.0045837 | 65.3592
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | FUSE | 233 | 4135 | 343415 | 0.2253 | 0.0027128 | 83.0508
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 20 | 1045 | 196360 | 0.12882 | 0.00068558 | 187.9043
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OU | NONE | 9 | 563 | 122849 | 0.080596 | 0.00036936 | 218.2043
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1691 | 67109 | 19714920 | 12.8403 | 0.043708 | 293.7746
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 53 | 7381 | 0.0048615 | 3.4908e-05 | 139.2642
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 2 | 147 | 9.8036e-05 | 1.3338e-06 | 73.5
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CO | METERING | 1 | 1 | 64 | 4.239e-05 | 6.6234e-07 | 64
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | FUSE | 32 | 85 | 8104 | 0.0052781 | 5.536e-05 | 95.3412
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | ARRESTER | 24 | 548 | 60457 | 0.039376 | 0.00035691 | 110.323
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | TRANSFORMER, OH | 40 | 182 | 53569 | 0.034889 | 0.00011854 | 294.3352
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 223 | 22831 | 0.014978 | 0.0001463 | 102.3812
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CE | TRANSFORMER, UG | 1 | 2 | 1140 | 0.00074791 | 1.3121e-06 | 570
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VIN | CABLE TERMINATOR | 1 | 42 | 4494 | 0.0029483 | 2.7554e-05 | 107
AEP-OH | 2023 | 1524255 | PARTIAL POWER | O | NONE | 10 | 12 | 2089 | 0.0013705 | 7.8727e-06 | 174.0833
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 1623 | 31838 | 0.020888 | 0.0010648 | 19.6168
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AF | NONE | 5 | 1076 | 43160 | 0.028315 | 0.00070592 | 40.1115
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | CROSSARM | 3 | 340 | 273718 | 0.18129 | 0.0002252 | 805.0529
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 2 | 16 | 1.0497e-05 | 1.3121e-06 | 8
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 1 | 203 | 0.00013318 | 6.5606e-07 | 203
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TOR | FUSE | 1 | 5 | 450 | 0.00029805 | 3.3117e-06 | 90
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WU | FUSE | 1 | 1 | 12 | 7.9037e-06 | 6.5865e-07 | 12
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | V | METERING | 18 | 28 | 5592 | 0.0036421 | 1.8236e-05 | 199.7143
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 30 | 1742 | 0.0011429 | 1.9682e-05 | 58.0667
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 7 | 2914 | 769956 | 0.50147 | 0.0018979 | 264.2265
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | POLE | 3 | 2544 | 97574 | 0.064014 | 0.001669 | 38.3546
AEP-OH | 2022 | 1518267 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 67 | 4.4129e-05 | 6.5865e-07 | 67
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | ARRESTER | 2 | 38 | 7646 | 0.0049798 | 2.4749e-05 | 201.2105
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WW | NONE | 6 | 35 | 6136 | 0.0040256 | 2.2962e-05 | 175.3143
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WT | NONE | 1 | 1 | 97 | 6.4247e-05 | 6.6234e-07 | 97
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | ARRESTER | 43 | 196 | 4886 | 0.0031822 | 0.00012765 | 24.9286
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | CUTOUT | 9 | 51 | 13467 | 0.008771 | 3.3216e-05 | 264.0588
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 9 | 147 | 5206 | 0.0033907 | 9.5741e-05 | 35.415
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TOR | CONDUCTOR UG | 2 | 2 | 489 | 0.00032389 | 1.3247e-06 | 244.5
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 437 | 119907 | 0.079967 | 0.00029144 | 274.3867
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 80 | 4880 | 0.0031783 | 5.2104e-05 | 61
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 33 | 6471 | 0.004286 | 2.1857e-05 | 196.0909
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 1 | 1 | 193 | 0.00012783 | 6.6234e-07 | 193
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | CROSSARM | 1 | 7 | 1288 | 0.0008531 | 4.6364e-06 | 184
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 3 | 11 | 1688 | 0.0011074 | 7.2166e-06 | 153.4545
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WFS | SPLICE, OH | 1 | 1 | 133 | 8.76e-05 | 6.5865e-07 | 133
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | TRANSFORMER, GROUNDING | 1 | 2 | 102 | 6.6918e-05 | 1.3121e-06 | 51
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | INSULATOR | 2 | 165 | 5608 | 0.00374 | 0.00011004 | 33.9879
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | CUTOUT | 2 | 388 | 58497 | 0.038099 | 0.0002527 | 150.7655
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | SPLICE, UG | 1 | 4 | 143 | 9.3136e-05 | 2.6052e-06 | 35.75
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | SWITCH, OH | 6 | 5353 | 305260 | 0.19882 | 0.0034864 | 57.026
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | CROSSARM | 1 | 13 | 1914 | 0.0012466 | 8.4669e-06 | 147.2308
AEP-OH | 2023 | 1524255 | PARTIAL POWER | OL | FUSE | 1 | 1 | 68 | 4.4612e-05 | 6.5606e-07 | 68
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | POLE HARDWARE | 2 | 16 | 1399 | 0.00091117 | 1.0421e-05 | 87.4375
AEP-OH | 2025 | 1535393 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 496 | 0.00032304 | 1.3026e-06 | 248
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SO | NONE | 1 | 6 | 738 | 0.00048066 | 3.9078e-06 | 123
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 2 | 734 | 0.00048155 | 1.3121e-06 | 367
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | UG | CONN/CLAMP | 2 | 18 | 4553 | 0.0029654 | 1.1723e-05 | 252.9444
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 9 | 270 | 0.00017714 | 5.9045e-06 | 30
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 5 | 550 | 0.0003668 | 3.3346e-06 | 110
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 6 | 546 | 0.00036413 | 4.0015e-06 | 91
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | CONN/CLAMP | 765 | 1909 | 238235 | 0.15691 | 0.0012574 | 124.7957
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 733 | 63345 | 8580708 | 5.6834 | 0.041956 | 135.4599
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 701 | 41321 | 7737003 | 5.1245 | 0.027369 | 187.2414
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | TRANSFORMER, OH | 33 | 132 | 25982 | 0.017209 | 8.7429e-05 | 196.8333
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | NONE | 159 | 22332 | 3126867 | 2.0595 | 0.014709 | 140.0173
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | NONE | 63 | 798 | 94444 | 0.062205 | 0.0005256 | 118.3509
AEP-OH | 2022 | 1518267 | PARTIAL POWER | OU | CONDUCTOR UG | 2 | 3 | 1162 | 0.00076535 | 1.9759e-06 | 387.3333
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 49 | 201 | 55779 | 0.036945 | 0.00013313 | 277.5075
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | FUSE | 57 | 1556 | 384036 | 0.25294 | 0.0010249 | 246.8098
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 24 | 9271 | 465896 | 0.30858 | 0.0061406 | 50.253
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TR | FUSE | 2 | 19 | 1374 | 0.00090498 | 1.2514e-05 | 72.3158
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | POLE | 10 | 294 | 118750 | 0.078653 | 0.00019473 | 403.9116
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 5 | 15 | 4264 | 0.0028085 | 9.8797e-06 | 284.2667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 825 | 60326 | 9908170 | 6.6079 | 0.040232 | 164.2438
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 5 | 4976 | 287177 | 0.19021 | 0.0032958 | 57.7124
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 1 | 29 | 1.9101e-05 | 6.5865e-07 | 29
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | INSULATOR | 173 | 49328 | 5861912 | 3.9094 | 0.032897 | 118.8354
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UG | NONE | 39 | 2338 | 386470 | 0.25598 | 0.0015486 | 165.2994
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 32 | 11766 | 554220 | 0.36708 | 0.0077931 | 47.1035
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 4 | 297 | 176126 | 0.11666 | 0.00019672 | 593.0168
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | INSULATOR | 4 | 55 | 10125 | 0.0067062 | 3.6429e-05 | 184.0909
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CF | NONE | 2 | 47 | 4782 | 0.0031673 | 3.113e-05 | 101.7447
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 33 | 6167 | 1362030 | 0.89357 | 0.0040459 | 220.8578
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CE | NONE | 5 | 16 | 968 | 0.00064115 | 1.0597e-05 | 60.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 167 | 0.00010999 | 6.5865e-07 | 167
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | POLE | 23 | 1472 | 624065 | 0.4162 | 0.0009817 | 423.9572
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 448 | 28672 | 0.018991 | 0.00029673 | 64
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 12 | 255 | 0.0001689 | 7.9481e-06 | 21.25
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | CABLE TERMINATOR | 9 | 58 | 17258 | 0.01151 | 3.8681e-05 | 297.5517
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | NONE | 273 | 25950 | 2136404 | 1.4016 | 0.017025 | 82.3277
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 6 | 267 | 15838 | 0.010432 | 0.00017586 | 59.3184
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OL | FUSE | 20 | 516 | 52759 | 0.034749 | 0.00033986 | 102.2461
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 836 | 4878 | 459776 | 0.30663 | 0.0032532 | 94.255
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | TRANSFORMER, OH | 40 | 191 | 52617 | 0.035091 | 0.00012738 | 275.4817
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AF | REGULATOR | 3 | 2281 | 36561 | 0.024383 | 0.0015212 | 16.0285
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 7 | 262 | 107261 | 0.071534 | 0.00017473 | 409.3931
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 303 | 1440 | 184605 | 0.12111 | 0.00094472 | 128.1979
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | CROSSARM | 4 | 42 | 6697 | 0.0044357 | 2.7818e-05 | 159.4524
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | CONDUCTOR UG | 23 | 48 | 9069 | 0.0059498 | 3.1491e-05 | 188.9375
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | POLE HARDWARE | 2 | 1174 | 137340 | 0.090458 | 0.00077325 | 116.9847
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TOR | TRANSFORMER, OH | 1 | 3 | 345 | 0.00022851 | 1.987e-06 | 115
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 24 | 5472 | 0.0036041 | 1.5807e-05 | 228
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OL | NONE | 34 | 733 | 58242 | 0.03821 | 0.00048089 | 79.457
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | INSULATOR | 3 | 1509 | 379492 | 0.25309 | 0.0010064 | 251.4858
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | CUTOUT | 11 | 213 | 31576 | 0.021058 | 0.00014205 | 148.2441
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 43 | 2189 | 258282 | 0.16945 | 0.0014361 | 117.9909
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 5 | 3566 | 0.0023487 | 3.2932e-06 | 713.2
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WI | FUSE | 3 | 7 | 5292 | 0.0034856 | 4.6105e-06 | 756
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 2 | 218 | 0.00014358 | 1.3173e-06 | 109
AEP-OH | 2020 | 1499447 | PARTIAL POWER | A | CONDUCTOR UG | 3 | 7 | 873 | 0.00058221 | 4.6684e-06 | 124.7143
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 25 | 442 | 11401 | 0.0076035 | 0.00029478 | 25.7941
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | POLE | 8 | 438 | 67522 | 0.044298 | 0.00028735 | 154.1598
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 237 | 780 | 120581 | 0.078534 | 0.00050801 | 154.591
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | POLE | 6 | 337 | 88955 | 0.057936 | 0.00021949 | 263.9614
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | V | FUSE | 1 | 2 | 368 | 0.00024143 | 1.3121e-06 | 184
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 7 | 1064 | 0.00070959 | 4.6684e-06 | 152
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | CUTOUT | 9 | 105 | 8680 | 0.0056946 | 6.8886e-05 | 82.6667
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | RELAY | 15 | 6135 | 311139 | 0.20413 | 0.0040249 | 50.7154
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | METERING | 2 | 1376 | 107376 | 0.070445 | 0.00090274 | 78.0349
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 63 | 1049 | 511594 | 0.3332 | 0.00068321 | 487.6969
AEP-OH | 2024 | 1535393 | PARTIAL POWER | VIN | NONE | 5 | 6 | 1140 | 0.00074248 | 3.9078e-06 | 190
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | PEDESTAL | 1 | 4 | 836 | 0.00055372 | 2.6494e-06 | 209
AEP-OH | 2024 | 1535393 | PARTIAL POWER | VA | CONDUCTOR UG | 4 | 6 | 571 | 0.00037189 | 3.9078e-06 | 95.1667
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 753 | 166479 | 0.10843 | 0.00049043 | 221.0876
AEP-OH | 2023 | 1524255 | PARTIAL POWER | OL | CIRCUIT SWITCHER | 1 | 4 | 512 | 0.0003359 | 2.6242e-06 | 128
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VIN | NONE | 5 | 84 | 10761 | 0.0071766 | 5.6021e-05 | 128.1071
AEP-OH | 2025 | 1535393 | PARTIAL POWER | A | NONE | 12 | 30 | 2655 | 0.0017292 | 1.9539e-05 | 88.5
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 6 | 140 | 339330 | 0.22101 | 9.1182e-05 | 2423.7857
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WH | CUTOUT | 1 | 5 | 15120 | 0.0098476 | 3.2565e-06 | 3024
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 1 | 125 | 8.1412e-05 | 6.513e-07 | 125
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OU | CONN/CLAMP | 1 | 22 | 1870 | 0.0012268 | 1.4433e-05 | 85
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | SPLICE, OH | 2 | 2 | 323 | 0.00021037 | 1.3026e-06 | 161.5
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 118 | 7.6853e-05 | 1.3026e-06 | 59
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | FUSE | 14 | 98 | 40100 | 0.026117 | 6.3827e-05 | 409.1837
AEP-OH | 2021 | 1509795 | PARTIAL POWER | VA | CONN/CLAMP | 1 | 1 | 88 | 5.8286e-05 | 6.6234e-07 | 88
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | POLE HARDWARE | 2 | 60 | 1932 | 0.0012796 | 3.974e-05 | 32.2
AEP-OH | 2021 | 1509795 | PARTIAL POWER | UB | NONE | 1 | 1 | 2380 | 0.0015764 | 6.6234e-07 | 2380
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 18 | 3078 | 0.0020528 | 1.2004e-05 | 171
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | ARRESTER | 7 | 35 | 3980 | 0.0025922 | 2.2795e-05 | 113.7143
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 5 | 995 | 0.00064804 | 3.2565e-06 | 199
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 140 | 18620 | 0.012127 | 9.1182e-05 | 133
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | O | NONE | 2 | 2289 | 319034 | 0.2093 | 0.0015017 | 139.377
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | REGULATOR | 3 | 892 | 17424 | 0.011348 | 0.00058096 | 19.5336
AEP-OH | 2023 | 1524255 | PARTIAL POWER | O | CONDUCTOR UG | 1 | 2 | 1130 | 0.00074135 | 1.3121e-06 | 565
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1 | 111 | 7.2294e-05 | 6.513e-07 | 111
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VA | POLE | 1 | 1 | 192 | 0.00012646 | 6.5865e-07 | 192
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | CABLE TERMINATOR | 1 | 1 | 156 | 0.00010235 | 6.5606e-07 | 156
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | NETWORK LIMITER | 1 | 3 | 2244 | 0.0014722 | 1.9682e-06 | 748
AEP-OH | 2024 | 1535393 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 92 | 5.992e-05 | 6.513e-07 | 92
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 33 | 547 | 0.00035626 | 2.1493e-05 | 16.5758
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 59 | 3.8427e-05 | 6.513e-07 | 59
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CE | CONDUCTOR UG | 3 | 7 | 1131 | 0.00074911 | 4.6364e-06 | 161.5714
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | POLE HARDWARE | 1 | 101 | 29492 | 0.019425 | 6.6523e-05 | 292
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 1 | 112 | 7.2945e-05 | 6.513e-07 | 112
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 57 | 47475 | 0.031662 | 3.8014e-05 | 832.8947
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 164 | 0.00010759 | 6.5606e-07 | 164
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 2 | 194 | 0.00012938 | 1.3338e-06 | 97
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SO | POLE | 1 | 1 | 178 | 0.0001179 | 6.6234e-07 | 178
AEP-OH | 2020 | 1499447 | PARTIAL POWER | A | ARRESTER | 1 | 1 | 85 | 5.6688e-05 | 6.6691e-07 | 85
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 4 | 468 | 0.00030825 | 2.6346e-06 | 117
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CE | ARRESTER | 1 | 2 | 436 | 0.00028878 | 1.3247e-06 | 218
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 13 | 3932 | 0.0026223 | 8.6699e-06 | 302.4615
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | SWITCH, UG | 1 | 12 | 3156 | 0.0021048 | 8.003e-06 | 263
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | NETWORK TRANSFORMER | 1 | 4 | 344 | 0.00022942 | 2.6677e-06 | 86
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 1 | 93 | 6.1013e-05 | 6.5606e-07 | 93
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2606 | 115212 | 29911665 | 19.8117 | 0.07631 | 259.6228
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 338 | 71656 | 0.047196 | 0.00022262 | 212
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 1 | 188 | 0.00012452 | 6.6234e-07 | 188
AEP-OH | 2025 | 1535393 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 57 | 3.7124e-05 | 6.513e-07 | 57
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 15 | 5205 | 0.00339 | 9.7695e-06 | 347
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VA | CONN/CLAMP | 2 | 2 | 209 | 0.00013712 | 1.3121e-06 | 104.5
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 1177 | 15675 | 0.010454 | 0.00078496 | 13.3178
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 75 | 4.8847e-05 | 6.513e-07 | 75
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 2 | 149 | 9.7044e-05 | 1.3026e-06 | 74.5
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 1 | 774 | 0.00050411 | 6.513e-07 | 774
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 280 | 29446 | 0.019503 | 0.00018546 | 105.1643
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TOR | POLE | 1 | 1 | 103 | 6.8221e-05 | 6.6234e-07 | 103
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | CE | POLE | 1 | 149 | 21456 | 0.013974 | 9.7044e-05 | 144
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 151 | 44092 | 0.029406 | 0.0001007 | 292
AEP-OH | 2023 | 1524255 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 186 | 0.00012203 | 6.5606e-07 | 186
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | CABLE TERMINATOR | 1 | 1 | 114 | 7.4248e-05 | 6.513e-07 | 114
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 227 | 69008 | 0.046022 | 0.00015139 | 304
AEP-OH | 2024 | 1535393 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 129 | 8.4018e-05 | 6.513e-07 | 129
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CE | INSULATOR | 1 | 132 | 17688 | 0.011604 | 8.66e-05 | 134
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | INSULATOR | 117 | 27610 | 3657820 | 2.4092 | 0.018185 | 132.4817
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 10 | 155 | 35911 | 0.023785 | 0.00010266 | 231.6839
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | ARRESTER | 172 | 9875 | 1029969 | 0.68219 | 0.0065406 | 104.3007
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 71 | 18350 | 0.012154 | 4.7026e-05 | 258.4507
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | NONE | 51 | 5387 | 599736 | 0.39723 | 0.003568 | 111.3302
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 47 | 3437 | 823143 | 0.5452 | 0.0022765 | 239.4946
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 2922 | 516102 | 0.34184 | 0.0019354 | 176.6263
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 23 | 554 | 95386 | 0.062826 | 0.00036489 | 172.1769
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | SPLICE, OH | 33 | 5870 | 728412 | 0.48246 | 0.0038879 | 124.0906
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 18 | 3655 | 185192 | 0.12198 | 0.0024073 | 50.6681
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | CUTOUT | 1686 | 74695 | 7645510 | 5.0989 | 0.049815 | 102.3564
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 4 | 13 | 4409 | 0.0029203 | 8.6104e-06 | 339.1538
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | WL | OTHER EQUIPMENT | 1 | 582 | 155290 | 0.10228 | 0.00038333 | 266.8213
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | CROSSARM | 246 | 9004 | 766544 | 0.51122 | 0.0060049 | 85.1337
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | POLE | 14 | 2557 | 856701 | 0.56426 | 0.0016842 | 335.0415
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TOR | NONE | 77 | 739 | 82532 | 0.055042 | 0.00049285 | 111.6806
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 2 | 196 | 0.00012982 | 1.3247e-06 | 98
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | SWITCH, OH | 3 | 1761 | 137122 | 0.090822 | 0.0011664 | 77.866
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | CONDUCTOR UG | 499 | 828 | 161246 | 0.10579 | 0.00054322 | 194.7415
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 19 | 308 | 34250 | 0.022842 | 0.00020541 | 111.2013
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 161 | 4724 | 1491624 | 0.97859 | 0.0030992 | 315.7544
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | O | FUSE | 2 | 4 | 244 | 0.00016161 | 2.6494e-06 | 61
AEP-OH | 2022 | 1518267 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 2 | 2 | 238 | 0.00015676 | 1.3173e-06 | 119
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | SCO | NONE | 16 | 9994 | 804183 | 0.53632 | 0.0066651 | 80.4666
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CE | BREAKER | 1 | 1 | 93 | 6.1254e-05 | 6.5865e-07 | 93
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 41 | 2591 | 0.0017066 | 2.7004e-05 | 63.1951
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | FUSE | 48 | 876 | 174842 | 0.11471 | 0.00057471 | 199.5913
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | POLE | 16 | 1018 | 341330 | 0.22393 | 0.00066787 | 335.2947
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | SPLICE, OH | 46 | 7467 | 716204 | 0.46987 | 0.0048988 | 95.9159
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 17 | 91 | 19334 | 0.012684 | 5.9701e-05 | 212.4615
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | FUSE | 11 | 100 | 25527 | 0.016747 | 6.5606e-05 | 255.27
AEP-OH | 2023 | 1524255 | PARTIAL POWER | A | FUSE | 11 | 48 | 3303 | 0.002167 | 3.1491e-05 | 68.8125
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | CUTOUT | 8 | 91 | 7274 | 0.0048511 | 6.0689e-05 | 79.9341
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ABI | ARRESTER | 1 | 2 | 138 | 9.2034e-05 | 1.3338e-06 | 69
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | FUSE | 53 | 481 | 54244 | 0.035329 | 0.00031327 | 112.7734
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TR | CONN/CLAMP | 2 | 2 | 266 | 0.00017451 | 1.3121e-06 | 133
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | ARRESTER | 6 | 410 | 103726 | 0.06805 | 0.00026898 | 252.9902
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 4 | 20 | 3032 | 0.0019892 | 1.3121e-05 | 151.6
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | SWITCH, UG | 6 | 1290 | 182602 | 0.12094 | 0.00085442 | 141.5519
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | NONE | 139 | 5847 | 1315648 | 0.85688 | 0.0038081 | 225.0125
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | POLE | 21 | 1683 | 1384175 | 0.90151 | 0.0010961 | 822.445
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 5 | 14500 | 0.0095128 | 3.2803e-06 | 2900
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WU | SPLICE, OH | 1 | 0 | 0 | 0 | 0
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | POLE HARDWARE | 9 | 737 | 157045 | 0.10303 | 0.00048351 | 213.0868
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | SPLICE, OH | 4 | 27 | 2078 | 0.0013633 | 1.7714e-05 | 76.963
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 49 | 2009 | 0.001318 | 3.2147e-05 | 41
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WT | INSULATOR | 1 | 501 | 171843 | 0.11274 | 0.00032869 | 343
AEP-OH | 2021 | 1509795 | PARTIAL POWER | OL | CONN/CLAMP | 3 | 6 | 4895 | 0.0032422 | 3.974e-06 | 815.8333
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | FUSE | 2 | 2 | 104 | 6.823e-05 | 1.3121e-06 | 52
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | ARRESTER | 2 | 13 | 1573 | 0.001032 | 8.5288e-06 | 121
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 5 | 27 | 4262 | 0.0027758 | 1.7585e-05 | 157.8519
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 1 | 36 | 2.3447e-05 | 6.513e-07 | 36
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 1 | 41 | 2.6703e-05 | 6.513e-07 | 41
AEP-OH | 2021 | 1509795 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 2 | 546 | 0.00036164 | 1.3247e-06 | 273
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 47 | 3.113e-05 | 6.6234e-07 | 47
AEP-OH | 2021 | 1509795 | PARTIAL POWER | OU | SPLICE, OH | 1 | 4 | 224 | 0.00014836 | 2.6494e-06 | 56
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WL | METERING | 1 | 1 | 53 | 3.5104e-05 | 6.6234e-07 | 53
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 3 | 485 | 0.00032345 | 2.0007e-06 | 161.6667
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | REGULATOR | 3 | 288 | 17881 | 0.011646 | 0.00018757 | 62.0868
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | U | NONE | 1 | 15 | 1110 | 0.00072294 | 9.7695e-06 | 74
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | FUSE | 1 | 9 | 684 | 0.00044549 | 5.8617e-06 | 76
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | SCO | REGULATOR | 2 | 2418 | 31434 | 0.020473 | 0.0015748 | 13
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 3 | 2295 | 0.0014947 | 1.9539e-06 | 765
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 66 | 5280 | 0.0035213 | 4.4016e-05 | 80
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 20 | 5475 | 0.0035659 | 1.3026e-05 | 273.75
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 1 | 36 | 2.3447e-05 | 6.513e-07 | 36
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | ABI | NONE | 1 | 1300 | 61100 | 0.039794 | 0.00084669 | 47
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 794 | 222320 | 0.1448 | 0.00051713 | 280
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WFS | GUY/ANCHOR | 1 | 450 | 46220 | 0.030103 | 0.00029308 | 102.7111
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 36 | 1224 | 0.00079719 | 2.3447e-05 | 34
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VIN | NONE | 172 | 1772 | 236186 | 0.15495 | 0.0011625 | 133.2878
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 38 | 259 | 79264 | 0.052002 | 0.00016992 | 306.0386
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AO | NONE | 5 | 4846 | 723097 | 0.47439 | 0.0031793 | 149.2152
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | ARRESTER | 19 | 16025 | 1821450 | 1.2147 | 0.010687 | 113.663
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WW | NONE | 1 | 3 | 414 | 0.00027268 | 1.9759e-06 | 138
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 7 | 1255 | 0.0008266 | 4.6105e-06 | 179.2857
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TOR | JUMPER/RISER | 1 | 5 | 1200 | 0.00079037 | 3.2932e-06 | 240
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | FUSE | 2 | 15 | 1570 | 0.00103 | 9.8409e-06 | 104.6667
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 7 | 1121 | 0.00073011 | 4.5591e-06 | 160.1429
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | SPLICE, OH | 73 | 3059 | 386164 | 0.25151 | 0.0019923 | 126.2386
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CF | FUSE | 2 | 3 | 285 | 0.00018877 | 1.987e-06 | 95
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 4 | 15 | 2493 | 0.0016512 | 9.9351e-06 | 166.2
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 35 | 1017 | 188842 | 0.12389 | 0.00066721 | 185.6853
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | METERING | 1 | 1 | 282 | 0.00018807 | 6.6691e-07 | 282
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | CAPACITOR | 5 | 3443 | 481683 | 0.31601 | 0.0022588 | 139.9021
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 5 | 18 | 2862 | 0.0018776 | 1.1809e-05 | 159
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CE | JUMPER/RISER | 1 | 3 | 462 | 0.0003031 | 1.9682e-06 | 154
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | CUTOUT | 7 | 242 | 43909 | 0.028598 | 0.00015761 | 181.4421
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CE | NONE | 6 | 26 | 10005 | 0.0065639 | 1.7058e-05 | 384.8077
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SO | POLE | 2 | 7 | 1289 | 0.00084566 | 4.5924e-06 | 184.1429
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 19 | 121 | 10724 | 0.0069845 | 7.8807e-05 | 88.6281
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AF | OTHER EQUIPMENT | 1 | 53 | 30793 | 0.020202 | 3.4771e-05 | 581
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | FUSE | 15 | 385 | 61452 | 0.040024 | 0.00025075 | 159.6156
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 38 | 155 | 36069 | 0.023492 | 0.00010095 | 232.7032
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | UB | NONE | 1 | 310 | 25572 | 0.016777 | 0.00020338 | 82.4903
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 4 | 396 | 60864 | 0.039641 | 0.00025791 | 153.697
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 3 | 3 | 1191 | 0.0007757 | 1.9539e-06 | 397
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 20 | 16083 | 1271197 | 0.82793 | 0.010475 | 79.0398
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WFS | POLE | 5 | 488 | 121401 | 0.080964 | 0.00032545 | 248.7725
AEP-OH | 2021 | 1509795 | PARTIAL POWER | ERO | NONE | 1 | 1 | 318 | 0.00021062 | 6.6234e-07 | 318
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | CUTOUT | 11 | 214 | 20081 | 0.013079 | 0.00013938 | 93.8364
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WU | SPLICE, OH | 2 | 2 | 1216 | 0.00079198 | 1.3026e-06 | 608
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 11 | 91 | 1365 | 0.00088902 | 5.9268e-05 | 15
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | CONN/CLAMP | 8 | 63 | 5867 | 0.0038212 | 4.1032e-05 | 93.127
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 3101 | 0.0020197 | 6.513e-07 | 3101
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OU | POLE | 4 | 125 | 29985 | 0.019997 | 8.3364e-05 | 239.88
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FO | CUTOUT | 1 | 9 | 909 | 0.00060207 | 5.9611e-06 | 101
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 24 | 936 | 0.00061649 | 1.5807e-05 | 39
AEP-OH | 2025 | 1535393 | PARTIAL POWER | UG | CONDUCTOR UG | 10 | 12 | 4203 | 0.0027374 | 7.8156e-06 | 350.25
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 1 | 131 | 8.532e-05 | 6.513e-07 | 131
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | CABLE TERMINATOR | 1 | 1 | 1374 | 0.00090142 | 6.5606e-07 | 1374
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WT | NONE | 9 | 3324 | 1822763 | 1.1872 | 0.0021649 | 548.3643
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OU | ARRESTER | 1 | 1 | 32 | 2.0842e-05 | 6.513e-07 | 32
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | INSULATOR | 2 | 1056 | 205644 | 0.13715 | 0.00070426 | 194.7386
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WI | NONE | 2 | 15 | 4960 | 0.0033079 | 1.0004e-05 | 330.6667
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | CROSSARM | 4 | 1151 | 154747 | 0.10079 | 0.00074965 | 134.4457
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | CAPACITOR | 1 | 741 | 54834 | 0.035713 | 0.00048261 | 74
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SO | JUMPER/RISER | 1 | 1 | 120 | 8.003e-05 | 6.6691e-07 | 120
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WI | NONE | 1 | 1464 | 642346 | 0.41836 | 0.0009535 | 438.7609
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 108 | 7.034e-05 | 6.513e-07 | 108
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 96 | 40314 | 0.026256 | 6.2525e-05 | 419.9375
AEP-OH | 2025 | 1535393 | PARTIAL POWER | VA | POLE | 1 | 15 | 1425 | 0.0009281 | 9.7695e-06 | 95
AEP-OH | 2025 | 1535393 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 557 | 0.00036277 | 6.513e-07 | 557
AEP-OH | 2025 | 1535393 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 1 | 8 | 1104 | 0.00071903 | 5.2104e-06 | 138
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | R | NONE | 2 | 478 | 79635 | 0.051866 | 0.00031132 | 166.6004
AEP-OH | 2020 | 1499447 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 4 | 592 | 0.00039481 | 2.6677e-06 | 148
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | ABX | BREAKER | 1 | 2443 | 254072 | 0.16734 | 0.0016091 | 104
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 75 | 2850 | 0.0019007 | 5.0018e-05 | 38
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 4 | 104 | 6.8884e-05 | 2.6494e-06 | 26
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 103 | 5974 | 0.0038909 | 6.7084e-05 | 58
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | CONDUCTOR UG | 568 | 1003 | 214380 | 0.1412 | 0.00066062 | 213.7388
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 417 | 3287 | 426075 | 0.28221 | 0.0021771 | 129.6243
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | CONN/CLAMP | 41 | 633 | 72969 | 0.047872 | 0.00041528 | 115.2749
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 7 | 155 | 23013 | 0.015157 | 0.00010209 | 148.471
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | CROSSARM | 2 | 3 | 536 | 0.00035303 | 1.9759e-06 | 178.6667
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 20 | 483 | 15394 | 0.010139 | 0.00031813 | 31.8716
AEP-OH | 2022 | 1518267 | PARTIAL POWER | U | FUSE | 15 | 64 | 5862 | 0.003861 | 4.2153e-05 | 91.5938
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | F | NONE | 26 | 1079 | 23881 | 0.015927 | 0.0007196 | 22.1325
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CE | NONE | 30 | 3137 | 227435 | 0.15064 | 0.0020778 | 72.5008
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 35 | 336 | 16495 | 0.010925 | 0.00022255 | 49.0923
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | POLE | 5 | 1155 | 57333 | 0.037614 | 0.00075775 | 49.639
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 2626 | 123587 | 0.08108 | 0.0017228 | 47.0628
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 3 | 3 | 1297 | 0.00085091 | 1.9682e-06 | 432.3333
AEP-OH | 2023 | 1524255 | PARTIAL POWER | OL | NONE | 5 | 6 | 881 | 0.00057799 | 3.9363e-06 | 146.8333
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 11 | 41 | 3683 | 0.0024562 | 2.7343e-05 | 89.8293
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SO | CUTOUT | 1 | 7 | 140 | 9.221e-05 | 4.6105e-06 | 20
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 9 | 32 | 3302 | 0.0021506 | 2.0842e-05 | 103.1875
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OU | NONE | 20 | 2893 | 721300 | 0.46978 | 0.0018842 | 249.326
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | FW | NONE | 1 | 1863 | 11178 | 0.0073334 | 0.0012222 | 6
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | POLE | 1 | 261 | 54810 | 0.035698 | 0.00016999 | 210
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | FUSE | 7 | 119 | 13577 | 0.0088427 | 7.7505e-05 | 114.0924
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 615 | 20376 | 6664014 | 4.3403 | 0.013271 | 327.0521
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | SPLICE, OH | 3 | 7 | 682 | 0.00044743 | 4.5924e-06 | 97.4286
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 4 | 11 | 441 | 0.00028722 | 7.1643e-06 | 40.0909
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | SWITCH, UG | 7 | 4401 | 427449 | 0.2784 | 0.0028664 | 97.1254
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 2 | 258 | 0.00017088 | 1.3247e-06 | 129
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | POLE | 35 | 4010 | 1381464 | 0.89975 | 0.0026117 | 344.5047
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 108 | 7.034e-05 | 6.513e-07 | 108
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 2 | 329 | 0.00021941 | 1.3338e-06 | 164.5
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 1 | 9 | 3123 | 0.0020685 | 5.9611e-06 | 347
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 3 | 2459 | 199483 | 0.12992 | 0.0016015 | 81.1236
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 44 | 6424 | 0.0041839 | 2.8657e-05 | 146
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | CABLE TERMINATOR | 1 | 35 | 2240 | 0.0014589 | 2.2795e-05 | 64
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | CUTOUT | 2 | 100 | 10095 | 0.0065749 | 6.513e-05 | 100.95
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 6 | 1693 | 0.0011026 | 3.9078e-06 | 282.1667
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TR | SPLICE, OH | 1 | 1 | 60 | 3.9078e-05 | 6.513e-07 | 60
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | SCO | TRANSFORMER, POWER - NON LTC | 3 | 1014 | 167310 | 0.10977 | 0.00066524 | 165
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 228 | 0.0001485 | 6.513e-07 | 228
AEP-OH | 2022 | 1518267 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 4 | 777 | 0.00051177 | 2.6346e-06 | 194.25
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | POLE | 2 | 29 | 8704 | 0.0057103 | 1.9026e-05 | 300.1379
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | PEDESTAL | 1 | 5 | 880 | 0.00057733 | 3.2803e-06 | 176
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 111 | 7.352e-05 | 6.6234e-07 | 111
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WFS | NONE | 3 | 40 | 4790 | 0.0031425 | 2.6242e-05 | 119.75
AEP-OH | 2024 | 1535393 | PARTIAL POWER | OL | FUSE | 2 | 2 | 212 | 0.00013808 | 1.3026e-06 | 106
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | TRANSFORMER, STATION SERVICE | 1 | 1 | 193 | 0.0001257 | 6.513e-07 | 193
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 3 | 996 | 0.00066424 | 2.0007e-06 | 332
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 5 | 1940 | 0.0012635 | 3.2565e-06 | 388
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | SWITCH, UG | 1 | 2 | 250 | 0.00016466 | 1.3173e-06 | 125
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 90 | 5.9611e-05 | 6.6234e-07 | 90
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 867 | 201874 | 0.13244 | 0.0005688 | 232.842
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 833 | 165376 | 0.10954 | 0.00055173 | 198.5306
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 10 | 3040 | 0.0020274 | 6.6691e-06 | 304
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TOR | CUTOUT | 1 | 1 | 206 | 0.00013417 | 6.513e-07 | 206
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | FUSE | 3 | 1179 | 70740 | 0.04641 | 0.00077349 | 60
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OU | CONN/CLAMP | 1 | 1 | 118 | 7.6853e-05 | 6.513e-07 | 118
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | NONE | 738 | 10630 | 729194 | 0.48028 | 0.0070014 | 68.5977
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | CONN/CLAMP | 52 | 148 | 20569 | 0.013494 | 9.7097e-05 | 138.9797
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 266 | 385 | 84314 | 0.055845 | 0.000255 | 218.9974
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 1773 | 19947 | 2180606 | 1.4362 | 0.013138 | 109.32
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | CUTOUT | 1189 | 7621 | 235453 | 0.15508 | 0.0050195 | 30.8953
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | FUSE | 568 | 9210 | 693786 | 0.45696 | 0.0060661 | 75.3296
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | CUTOUT | 831 | 6887 | 322080 | 0.2113 | 0.0045183 | 46.7664
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 27 | 56 | 9513 | 0.0062657 | 3.6884e-05 | 169.875
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | NONE | 148 | 6637 | 1132110 | 0.74984 | 0.004396 | 170.5756
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | POLE | 3 | 14 | 3704 | 0.0024396 | 9.221e-06 | 264.5714
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VIN | POLE | 1 | 3 | 792 | 0.00052165 | 1.9759e-06 | 264
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 467 | 91301 | 0.060135 | 0.00030759 | 195.5054
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | NONE | 42 | 2017 | 66319 | 0.043926 | 0.0013359 | 32.88
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 5 | 5 | 608 | 0.00040046 | 3.2932e-06 | 121.6
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 23 | 630 | 93211 | 0.061393 | 0.00041495 | 147.954
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 43 | 2184 | 313398 | 0.20758 | 0.0014466 | 143.4973
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 4 | 1364 | 0.00090343 | 2.6494e-06 | 341
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | NONE | 24 | 14322 | 1335282 | 0.88441 | 0.0094861 | 93.2329
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TR | NONE | 81 | 4831 | 412606 | 0.27517 | 0.0032219 | 85.408
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 2 | 6 | 96 | 6.3585e-05 | 3.974e-06 | 16
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | CUTOUT | 14 | 94 | 19930 | 0.013127 | 6.1913e-05 | 212.0213
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | METERING | 3 | 7 | 489 | 0.00032389 | 4.6364e-06 | 69.8571
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 79 | 16128 | 0.010756 | 5.2686e-05 | 204.1519
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 526 | 33478 | 0.022327 | 0.0003508 | 63.6464
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | CUTOUT | 3 | 14 | 13080 | 0.0086151 | 9.221e-06 | 934.2857
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | TRANSFORMER, UG | 7 | 11 | 3528 | 0.0023529 | 7.336e-06 | 320.7273
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | CAPACITOR | 2 | 299 | 44512 | 0.029482 | 0.00019804 | 148.8696
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | FUSE | 26 | 94 | 8673 | 0.00569 | 6.1669e-05 | 92.266
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 6 | 2686 | 0.0017691 | 3.9519e-06 | 447.6667
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WU | CUTOUT | 2 | 3 | 2299 | 0.0015083 | 1.9682e-06 | 766.3333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FO | CAPACITOR | 1 | 30 | 1800 | 0.0012004 | 2.0007e-05 | 60
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | NONE | 60 | 5231 | 387891 | 0.25263 | 0.0034069 | 74.1524
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | METERING | 39 | 72 | 5625 | 0.0036903 | 4.7236e-05 | 78.125
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 2 | 3 | 1388 | 0.00091933 | 1.987e-06 | 462.6667
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | NONE | 2346 | 132221 | 24602941 | 16.2046 | 0.087087 | 186.0744
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | POLE | 2903 | 24428 | 3480290 | 2.2833 | 0.016026 | 142.4713
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | NONE | 2886 | 47635 | 4671920 | 3.0651 | 0.031251 | 98.0775
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2463 | 115554 | 28744089 | 18.9322 | 0.076109 | 248.7503
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 171 | 31077 | 3376973 | 2.2242 | 0.020469 | 108.6647
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 640 | 40884 | 8009430 | 5.2754 | 0.026928 | 195.9062
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TR | POLE | 10 | 318 | 105013 | 0.069166 | 0.00020945 | 330.2296
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TOR | NONE | 88 | 364 | 51478 | 0.033906 | 0.00023975 | 141.4231
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 12 | 2976 | 0.0019601 | 7.9037e-06 | 248
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | POLE | 5 | 5868 | 1211849 | 0.79818 | 0.0038649 | 206.5182
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FO | NONE | 60 | 5524 | 454613 | 0.30111 | 0.0036588 | 82.2978
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 138 | 15276 | 0.010118 | 9.1403e-05 | 110.6957
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | REGULATOR | 14 | 6382 | 197131 | 0.12984 | 0.0042035 | 30.8886
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | JUMPER/RISER | 3 | 22 | 2618 | 0.0017243 | 1.449e-05 | 119
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | SWITCH, OH | 16 | 9492 | 1336734 | 0.88043 | 0.0062519 | 140.8274
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 16 | 90 | 11963 | 0.0079783 | 6.0022e-05 | 132.9222
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 1 | 402 | 0.00026478 | 6.5865e-07 | 402
AEP-OH | 2020 | 1499447 | PARTIAL POWER | U | NONE | 171 | 943 | 114838 | 0.076587 | 0.0006289 | 121.7794
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FO | NONE | 79 | 10557 | 858729 | 0.5727 | 0.0070406 | 81.3421
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | FUSE | 35 | 87 | 11519 | 0.0076822 | 5.8021e-05 | 132.4023
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | BREAKER | 13 | 12884 | 1593239 | 1.0553 | 0.0085336 | 123.6603
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | ARRESTER | 4 | 250 | 18281 | 0.012108 | 0.00016559 | 73.124
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | CONN/CLAMP | 1 | 1 | 33 | 2.1857e-05 | 6.6234e-07 | 33
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | V | NONE | 32 | 939 | 51994 | 0.034675 | 0.00062623 | 55.3717
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 615 | 84605 | 0.056424 | 0.00041015 | 137.5691
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | OTHER EQUIPMENT | 1 | 4 | 1492 | 0.0009827 | 2.6346e-06 | 373
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | CONN/CLAMP | 28 | 548 | 44622 | 0.029759 | 0.00036547 | 81.427
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 12 | 1087 | 0.00071314 | 7.8727e-06 | 90.5833
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 7 | 14 | 2438 | 0.0016148 | 9.2728e-06 | 174.1429
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 4 | 12 | 682 | 0.00045172 | 7.9481e-06 | 56.8333
AEP-OH | 2022 | 1518267 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 9 | 1591 | 0.0010479 | 5.9278e-06 | 176.7778
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 4 | 67 | 20083 | 0.013176 | 4.3956e-05 | 299.7463
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | ARRESTER | 16 | 2133 | 255098 | 0.17013 | 0.0014225 | 119.5959
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 40 | 1045 | 448115 | 0.29515 | 0.00068828 | 428.8182
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | O | CUTOUT | 2 | 6 | 1448 | 0.00095907 | 3.974e-06 | 241.3333
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | V | NONE | 27 | 843 | 37920 | 0.024878 | 0.00055306 | 44.9822
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | CROSSARM | 85 | 26879 | 8026214 | 5.2275 | 0.017506 | 298.6054
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 12 | 2364 | 286109 | 0.19081 | 0.0015766 | 121.0275
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | JUMPER/RISER | 2 | 345 | 4165 | 0.0027433 | 0.00022723 | 12.0725
AEP-OH | 2023 | 1524255 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 5 | 7 | 739 | 0.00048483 | 4.5924e-06 | 105.5714
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | INSULATOR | 2 | 116 | 8508 | 0.0056038 | 7.6403e-05 | 73.3448
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERO | METERING | 3 | 4 | 217 | 0.00014472 | 2.6677e-06 | 54.25
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 6 | 909 | 0.00059636 | 3.9363e-06 | 151.5
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | CONN/CLAMP | 4 | 58 | 6571 | 0.0042797 | 3.7775e-05 | 113.2931
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 27 | 6827 | 839238 | 0.54659 | 0.0044464 | 122.9293
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 1 | 120 | 7.9481e-05 | 6.6234e-07 | 120
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 4 | 39 | 8742 | 0.0056937 | 2.5401e-05 | 224.1538
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 1 | 132 | 8.5971e-05 | 6.513e-07 | 132
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 18 | 234 | 0.00015352 | 1.1809e-05 | 13
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 4 | 349 | 0.00023275 | 2.6677e-06 | 87.25
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SO | NONE | 11 | 52 | 1853 | 0.0012358 | 3.4679e-05 | 35.6346
AEP-OH | 2024 | 1535393 | PARTIAL POWER | ERF | NONE | 6 | 6 | 1706 | 0.0011111 | 3.9078e-06 | 284.3333
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | OL | NONE | 9 | 16096 | 2589727 | 1.6867 | 0.010483 | 160.8926
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | ERF | NONE | 9 | 7208 | 1123578 | 0.73713 | 0.0047289 | 155.8793
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | WU | NONE | 8 | 8640 | 582825 | 0.37959 | 0.0056272 | 67.4566
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AF | TRANSFORMER, GROUNDING | 1 | 316 | 15800 | 0.010407 | 0.00020813 | 50
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | INSULATOR | 2 | 49 | 5579 | 0.0036952 | 3.2455e-05 | 113.8571
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 4 | 57 | 3618 | 0.0024129 | 3.8014e-05 | 63.4737
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | CE | METERING | 1 | 1271 | 234676 | 0.15284 | 0.0008278 | 184.6389
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | U | NONE | 4 | 2667 | 308717 | 0.20589 | 0.0017787 | 115.7544
AEP-OH | 2023 | 1524255 | PARTIAL POWER | UG | CONN/CLAMP | 3 | 3 | 361 | 0.00023684 | 1.9682e-06 | 120.3333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 2 | 36 | 15575 | 0.010387 | 2.4009e-05 | 432.6389
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 5 | 2101 | 348348 | 0.22688 | 0.0013684 | 165.801
AEP-OH | 2024 | 1535393 | PARTIAL POWER | CE | OTHER EQUIPMENT | 1 | 1 | 1370 | 0.00089228 | 6.513e-07 | 1370
AEP-OH | 2023 | 1524255 | PARTIAL POWER | V | METERING | 1 | 1 | 53 | 3.4771e-05 | 6.5606e-07 | 53
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | INSULATOR | 7 | 466 | 89166 | 0.058074 | 0.00030351 | 191.3433
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 2 | 134 | 8.7912e-05 | 1.3121e-06 | 67
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 11 | 1848 | 0.0012124 | 7.2166e-06 | 168
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | F | POLE | 1 | 200 | 7896 | 0.0051427 | 0.00013026 | 39.48
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 155 | 8370 | 0.0055129 | 0.00010209 | 54
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | JUMPER/RISER | 1 | 105 | 66390 | 0.043556 | 6.8886e-05 | 632.2857
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | BE | CONDUCTOR UG | 1 | 1 | 191 | 0.00012651 | 6.6234e-07 | 191
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | SPLICE, OH | 3 | 5 | 549 | 0.00036018 | 3.2803e-06 | 109.8
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 5 | 3737 | 604156 | 0.39636 | 0.0024517 | 161.6687
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 225 | 199309 | 0.12981 | 0.00014654 | 885.8178
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 9 | 3978 | 0.0025909 | 5.8617e-06 | 442
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 1 | 452 | 0.00029439 | 6.513e-07 | 452
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 7 | 938 | 0.00061092 | 4.5591e-06 | 134
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 6 | 1458 | 0.00096031 | 3.9519e-06 | 243
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 10 | 1257 | 0.00081868 | 6.513e-06 | 125.7
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | PEDESTAL | 1 | 1 | 104 | 6.7735e-05 | 6.513e-07 | 104
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | NETWORK LIMITER | 1 | 1 | 99 | 6.4479e-05 | 6.513e-07 | 99
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | AB | INSULATOR | 1 | 1793 | 272528 | 0.18051 | 0.0011876 | 151.9955
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 13 | 1131 | 0.00075428 | 8.6699e-06 | 87
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CF | NONE | 1 | 21 | 5103 | 0.0034033 | 1.4005e-05 | 243
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 3113 | 662245 | 0.43618 | 0.0020504 | 212.7353
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | SWITCH, UG | 2 | 1605 | 275726 | 0.18089 | 0.001053 | 171.7919
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WU | METERING | 1 | 1 | 192 | 0.00012805 | 6.6691e-07 | 192
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 1 | 120 | 7.9037e-05 | 6.5865e-07 | 120
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 28 | 1470 | 141331 | 0.093087 | 0.00096821 | 96.1435
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | CROSSARM | 281 | 7047 | 446283 | 0.29394 | 0.0046415 | 63.3295
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CE | NONE | 10 | 15 | 2105 | 0.0013864 | 9.8797e-06 | 140.3333
AEP-OH | 2022 | 1518267 | PARTIAL POWER | OL | NONE | 7 | 119 | 11041 | 0.0072721 | 7.8379e-05 | 92.7815
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | NONE | 3264 | 163181 | 12029056 | 8.0223 | 0.10883 | 73.716
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CE | NONE | 16 | 91 | 9460 | 0.006309 | 6.0689e-05 | 103.956
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 49 | 1101 | 237362 | 0.1583 | 0.00073427 | 215.5876
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 8 | 1430 | 0.00094715 | 5.2987e-06 | 178.75
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 1452 | 86412 | 0.057234 | 0.00096172 | 59.5124
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | ARRESTER | 7 | 4109 | 489674 | 0.32433 | 0.0027216 | 119.1711
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | SCO | OTHER EQUIPMENT | 1 | 1369 | 157435 | 0.10369 | 0.00090169 | 115
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | SWITCH, OH | 8 | 162 | 5070 | 0.0033393 | 0.0001067 | 31.2963
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WU | NONE | 16 | 34 | 8900 | 0.0058619 | 2.2394e-05 | 261.7647
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | METERING | 35 | 45 | 6120 | 0.0040815 | 3.0011e-05 | 136
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | SPLICE, UG | 2 | 4 | 818 | 0.00053877 | 2.6346e-06 | 204.5
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | METERING | 52 | 319 | 26222 | 0.017488 | 0.00021275 | 82.2006
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 11 | 140 | 22890 | 0.015076 | 9.221e-05 | 163.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | NETWORK TRANSFORMER | 1 | 75 | 7875 | 0.0051868 | 4.9398e-05 | 105
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 90 | 34905 | 3940359 | 2.6279 | 0.023279 | 112.8881
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 153 | 77509 | 0.051337 | 0.00010134 | 506.5948
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 3 | 105 | 6.9158e-05 | 1.9759e-06 | 35
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VA | POLE | 3 | 7 | 2570 | 0.001714 | 4.6684e-06 | 367.1429
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | ARRESTER | 39 | 890 | 176524 | 0.11581 | 0.00058389 | 198.3416
AEP-OH | 2021 | 1509795 | PARTIAL POWER | OU | CUTOUT | 1 | 3 | 186 | 0.0001232 | 1.987e-06 | 62
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | NONE | 3405 | 156302 | 32957009 | 21.4649 | 0.1018 | 210.8547
AEP-OH | 2023 | 1524255 | PARTIAL POWER | ABI | NONE | 44 | 87 | 7004 | 0.004595 | 5.7077e-05 | 80.5057
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 9 | 24 | 3172 | 0.0021154 | 1.6006e-05 | 132.1667
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 14 | 7934 | 930352 | 0.61037 | 0.0052052 | 117.2614
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | CONN/CLAMP | 674 | 1999 | 244989 | 0.15956 | 0.0013019 | 122.5558
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 4 | 21 | 5521 | 0.0036364 | 1.3832e-05 | 262.9048
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 4 | 404 | 0.00026609 | 2.6346e-06 | 101
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | POLE | 484 | 75491 | 14740408 | 9.6004 | 0.049167 | 195.2605
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UB | NONE | 2 | 58 | 9353 | 0.0061603 | 3.8201e-05 | 161.2586
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 5 | 549 | 356688 | 0.23401 | 0.00036018 | 649.7049
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | PEDESTAL | 1 | 5 | 475 | 0.00031678 | 3.3346e-06 | 95
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 17 | 164 | 2169 | 0.0014127 | 0.00010681 | 13.2256
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | POLE HARDWARE | 2 | 22 | 4706 | 0.003065 | 1.4329e-05 | 213.9091
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ERF | FUSE | 9 | 647 | 94702 | 0.061679 | 0.00042139 | 146.3709
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | CUTOUT | 4 | 47 | 28631 | 0.018858 | 3.0956e-05 | 609.1702
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | CUTOUT | 7 | 424 | 10402 | 0.0069372 | 0.00028277 | 24.533
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | SWITCH, UG | 1 | 199 | 61690 | 0.040472 | 0.00013056 | 310
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 12 | 251 | 15183 | 0.0098887 | 0.00016348 | 60.49
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 6 | 399 | 61505 | 0.040351 | 0.00026177 | 154.1479
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | REGULATOR | 1 | 412 | 4120 | 0.002703 | 0.0002703 | 10
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | SWITCH, OH | 2 | 955 | 72170 | 0.047004 | 0.00062199 | 75.5707
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | NONE | 28 | 969 | 92950 | 0.060538 | 0.00063111 | 95.9236
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | FUSE | 14 | 27 | 2139 | 0.0013931 | 1.7585e-05 | 79.2222
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | SPLICE, OH | 6 | 17 | 16831 | 0.010962 | 1.1072e-05 | 990.0588
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SO | CROSSARM | 2 | 72 | 2400 | 0.0015807 | 4.7422e-05 | 33.3333
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 36 | 218 | 36602 | 0.023839 | 0.00014198 | 167.8991
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | CABLE TERMINATOR | 1 | 3 | 594 | 0.0003897 | 1.9682e-06 | 198
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 1 | 79 | 5.1829e-05 | 6.5606e-07 | 79
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | POLE | 16 | 493 | 318430 | 0.20739 | 0.00032109 | 645.9026
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 6 | 136 | 51233 | 0.033368 | 8.8577e-05 | 376.7132
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | TRANSFORMER, GROUNDING | 1 | 9 | 63 | 4.1332e-05 | 5.9045e-06 | 7
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | METERING | 1 | 1 | 64 | 4.1988e-05 | 6.5606e-07 | 64
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | SWITCH, OH | 6 | 3365 | 339088 | 0.22085 | 0.0021916 | 100.7691
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 8 | 3610 | 0.0023512 | 5.2104e-06 | 451.25
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | INSULATOR | 6 | 102 | 11576 | 0.0075394 | 6.6433e-05 | 113.4902
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | CUTOUT | 10 | 671 | 53668 | 0.035792 | 0.0004475 | 79.9821
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | V | METERING | 27 | 37 | 2660 | 0.001774 | 2.4676e-05 | 71.8919
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 5 | 11 | 2461 | 0.00163 | 7.2858e-06 | 223.7273
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 577 | 91646 | 0.060701 | 0.00038217 | 158.8319
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | CUTOUT | 1 | 1 | 118 | 7.772e-05 | 6.5865e-07 | 118
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 3 | 25 | 2959 | 0.0019489 | 1.6466e-05 | 118.36
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 27 | 2390 | 274140 | 0.18283 | 0.0015939 | 114.7029
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | JUMPER/RISER | 9 | 56 | 5070 | 0.0033812 | 3.7347e-05 | 90.5357
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 2857 | 523762 | 0.3493 | 0.0019054 | 183.3259
AEP-OH | 2023 | 1524255 | PARTIAL POWER | UG | NONE | 26 | 59 | 11434 | 0.0075014 | 3.8707e-05 | 193.7966
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 6990 | 150838 | 0.1006 | 0.0046617 | 21.5791
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WI | NONE | 39 | 600 | 333654 | 0.21976 | 0.00039519 | 556.09
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ABI | NONE | 46 | 111 | 10653 | 0.0071046 | 7.4027e-05 | 95.973
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WU | CONN/CLAMP | 4 | 4 | 413 | 0.00027202 | 2.6346e-06 | 103.25
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | WL | INSULATOR | 4 | 1723 | 850096 | 0.56694 | 0.0011491 | 493.3813
AEP-OH | 2024 | 1535393 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 3 | 703 | 0.00045786 | 1.9539e-06 | 234.3333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 13 | 323 | 46847 | 0.031243 | 0.00021541 | 145.0372
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | INSULATOR | 7 | 8028 | 1643758 | 1.0784 | 0.0052668 | 204.7531
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | FUSE | 9 | 32 | 10354 | 0.0067436 | 2.0842e-05 | 323.5625
AEP-OH | 2020 | 1499447 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 5 | 6 | 600 | 0.00040015 | 4.0015e-06 | 100
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 16 | 4614 | 0.0030271 | 1.0497e-05 | 288.375
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | ABI | NONE | 7 | 3047 | 614162 | 0.40293 | 0.001999 | 201.5628
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TR | NONE | 4 | 5 | 401 | 0.00026308 | 3.2803e-06 | 80.2
AEP-OH | 2021 | 1509795 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 5 | 21 | 889 | 0.00058882 | 1.3909e-05 | 42.3333
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 338 | 0.00022387 | 6.6234e-07 | 338
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 4 | 102 | 6.6433e-05 | 2.6052e-06 | 25.5
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | NONE | 451 | 8376 | 589030 | 0.38363 | 0.0054553 | 70.3235
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | SPLICE, OH | 17 | 31 | 5404 | 0.0035196 | 2.019e-05 | 174.3226
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 5 | 182 | 58574 | 0.038149 | 0.00011854 | 321.8352
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | ARRESTER | 51 | 4887 | 697922 | 0.45456 | 0.0031829 | 142.812
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 4 | 28 | 5285 | 0.0034421 | 1.8236e-05 | 188.75
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TR | NONE | 13 | 833 | 39159 | 0.025504 | 0.00054253 | 47.0096
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ABI | NONE | 55 | 6197 | 766883 | 0.49947 | 0.0040361 | 123.7507
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | V | NONE | 6 | 10 | 1343 | 0.00087469 | 6.513e-06 | 134.3
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 95 | 6.1873e-05 | 6.513e-07 | 95
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 6 | 27 | 8625 | 0.0056175 | 1.7585e-05 | 319.4444
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | CONN/CLAMP | 3 | 23 | 2001 | 0.0013345 | 1.5339e-05 | 87
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | CROSSARM | 2 | 572 | 74876 | 0.049593 | 0.00037886 | 130.9021
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | NONE | 32 | 1829 | 295216 | 0.19227 | 0.0011912 | 161.4084
AEP-OH | 2021 | 1509795 | PARTIAL POWER | ERF | NONE | 1 | 1 | 94 | 6.226e-05 | 6.6234e-07 | 94
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 1 | 162 | 0.00010804 | 6.6691e-07 | 162
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WI | METERING | 2 | 2 | 93 | 6.0571e-05 | 1.3026e-06 | 46.5
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | ARRESTER | 1 | 7 | 105 | 6.9546e-05 | 4.6364e-06 | 15
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WI | POLE | 5 | 1136 | 1205449 | 0.79842 | 0.00075242 | 1061.1347
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | POLE | 1 | 4 | 424 | 0.00027927 | 2.6346e-06 | 106
AEP-OH | 2021 | 1509795 | PARTIAL POWER | VA | NONE | 2 | 136 | 18662 | 0.012361 | 9.0078e-05 | 137.2206
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | SPLICE, UG | 4 | 5 | 958 | 0.0006285 | 3.2803e-06 | 191.6
AEP-OH | 2020 | 1499447 | PARTIAL POWER | OL | FUSE | 1 | 1 | 104 | 6.9359e-05 | 6.6691e-07 | 104
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | SPLICE, OH | 4 | 5 | 578 | 0.00038548 | 3.3346e-06 | 115.6
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 3 | 6 | 5418 | 0.0036133 | 4.0015e-06 | 903
AEP-OH | 2021 | 1509795 | PARTIAL POWER | ERO | CONDUCTOR UG | 1 | 1 | 132 | 8.7429e-05 | 6.6234e-07 | 132
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OU | POLE | 2 | 179 | 49985 | 0.032793 | 0.00011743 | 279.2458
AEP-OH | 2025 | 1535393 | DISTRIBUTION SOURCE | EQF | ARRESTER | 2 | 2 | 958 | 0.00062394 | 1.3026e-06 | 479
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 405 | 109404 | 0.071255 | 0.00026378 | 270.1333
AEP-OH | 2025 | 1535393 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 27 | 1.7585e-05 | 6.513e-07 | 27
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | REGULATOR | 1 | 51 | 3774 | 0.002458 | 3.3216e-05 | 74
AEP-OH | 2022 | 1518267 | DISTRIBUTION SOURCE | VA | POLE | 2 | 463 | 6945 | 0.0045743 | 0.00030495 | 15
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TR | NONE | 1 | 1 | 142 | 9.3528e-05 | 6.5865e-07 | 142
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 2 | 3709 | 314618 | 0.20641 | 0.0024333 | 84.8256
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 2 | 228 | 0.00015017 | 1.3173e-06 | 114
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 159 | 0.00010431 | 6.5606e-07 | 159
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AB | ARRESTER | 1 | 1403 | 106628 | 0.071112 | 0.00093568 | 76
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | TRANSFORMER, UG | 1 | 4 | 1432 | 0.00093948 | 2.6242e-06 | 358
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | FUSE | 1 | 3 | 429 | 0.00028414 | 1.987e-06 | 143
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 3 | 20 | 47697 | 0.031592 | 1.3247e-05 | 2384.85
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FO | ARRESTER | 2 | 3 | 364 | 0.00023881 | 1.9682e-06 | 121.3333
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FO | POLE | 1 | 82 | 7708 | 0.0051053 | 5.4312e-05 | 94
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | INSULATOR | 1 | 1 | 226 | 0.00015072 | 6.6691e-07 | 226
AEP-OH | 2023 | 1524255 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 61 | 4.002e-05 | 6.5606e-07 | 61
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | BREAKER | 1 | 1 | 469 | 0.00030769 | 6.5606e-07 | 469
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AO | CONDUCTOR UG | 3 | 3484 | 1232461 | 0.82194 | 0.0023235 | 353.7489
AEP-OH | 2024 | 1535393 | PARTIAL POWER | U | METERING | 1 | 1 | 141 | 9.1833e-05 | 6.513e-07 | 141
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 205 | 9250 | 1659862 | 1.0933 | 0.0060925 | 179.4445
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CF | CONN/CLAMP | 5 | 17 | 1782 | 0.0011737 | 1.1197e-05 | 104.8235
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 12 | 1365 | 138158 | 0.090997 | 0.00089905 | 101.2147
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | FUSE | 5 | 23 | 3296 | 0.0021709 | 1.5149e-05 | 143.3043
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | JUMPER/RISER | 5 | 5 | 665 | 0.000438 | 3.2932e-06 | 133
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | POLE | 510 | 113897 | 17473355 | 11.6532 | 0.075959 | 153.4137
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 13 | 7735 | 0.0050378 | 8.4669e-06 | 595
AEP-OH | 2021 | 1509795 | PARTIAL POWER | A | CONN/CLAMP | 1 | 10 | 1040 | 0.00068884 | 6.6234e-06 | 104
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 1 | 25 | 1.6559e-05 | 6.6234e-07 | 25
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 3 | 435 | 0.00028651 | 1.9759e-06 | 145
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | CUTOUT | 4 | 3440 | 633620 | 0.41733 | 0.0022657 | 184.1919
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 1 | 173 | 0.0001135 | 6.5606e-07 | 173
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 290 | 0.00018888 | 6.513e-07 | 290
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 263 | 0.00017254 | 6.5606e-07 | 263
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 5 | 1285 | 0.00085698 | 3.3346e-06 | 257
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 24 | 4512 | 0.0029718 | 1.5807e-05 | 188
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | SWITCH, OH | 2 | 3454 | 209044 | 0.13941 | 0.0023035 | 60.5223
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 2 | 4 | 1978 | 0.0013192 | 2.6677e-06 | 494.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 1697 | 130669 | 0.086065 | 0.0011177 | 77
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | FUSE | 1 | 25 | 2000 | 0.0013338 | 1.6673e-05 | 80
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | CUTOUT | 1432 | 10636 | 291379 | 0.19299 | 0.0070447 | 27.3955
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 14 | 665 | 99417 | 0.065481 | 0.000438 | 149.4992
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | METERING | 23 | 93 | 10620 | 0.0069948 | 6.1254e-05 | 114.1935
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AB | NONE | 7 | 7190 | 778231 | 0.51258 | 0.0047357 | 108.238
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 268 | 1101 | 212996 | 0.14108 | 0.00072924 | 193.4569
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | FUSE | 4 | 13 | 1702 | 0.001121 | 8.5624e-06 | 130.9231
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 5 | 67 | 8123 | 0.0053502 | 4.4129e-05 | 121.2388
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 2097 | 18549 | 1850011 | 1.2338 | 0.012371 | 99.7364
AEP-OH | 2022 | 1518267 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 7 | 2033 | 0.001339 | 4.6105e-06 | 290.4286
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 24 | 726 | 120578 | 0.079864 | 0.00048086 | 166.0854
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 23 | 40 | 6077 | 0.004025 | 2.6494e-05 | 151.925
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | R | NONE | 9 | 13721 | 1115636 | 0.73893 | 0.009088 | 81.3087
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | NONE | 2923 | 138032 | 28034018 | 18.3919 | 0.090557 | 203.098
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AF | NONE | 3 | 7993 | 849797 | 0.55972 | 0.0052646 | 106.3177
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 14 | 161 | 40508 | 0.026576 | 0.00010563 | 251.6025
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | WU | CONDUCTOR OVERHEAD | 1 | 210 | 24360 | 0.016045 | 0.00013832 | 116
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 580 | 88160 | 0.058392 | 0.00038416 | 152
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WW | POLE | 3 | 41 | 4837 | 0.0032037 | 2.7156e-05 | 117.9756
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WFS | SWITCH, UG | 1 | 342 | 77648 | 0.051429 | 0.00022652 | 227.0409
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | POLE | 1 | 2 | 524 | 0.00034707 | 1.3247e-06 | 262
AEP-OH | 2021 | 1509795 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 95 | 6.2922e-05 | 6.6234e-07 | 95
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 125 | 12318 | 1354424 | 0.88858 | 0.0080813 | 109.9549
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | CUTOUT | 43 | 126 | 17176 | 0.011268 | 8.2663e-05 | 136.3175
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERO | NONE | 15 | 2323 | 221022 | 0.145 | 0.001524 | 95.1451
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WFS | NONE | 12 | 3461 | 760045 | 0.50688 | 0.0023082 | 219.6027
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OU | JUMPER/RISER | 1 | 670 | 41540 | 0.02736 | 0.00044129 | 62
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1184 | 105304 | 0.069086 | 0.00077677 | 88.9392
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 9 | 156 | 8543 | 0.0056974 | 0.00010404 | 54.7628
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | INSULATOR | 2 | 969 | 115255 | 0.075912 | 0.00063823 | 118.9422
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 129 | 26621 | 3204655 | 2.0872 | 0.017338 | 120.3807
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 4 | 19 | 4380 | 0.0028735 | 1.2465e-05 | 230.5263
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 11 | 27 | 2785 | 0.0018271 | 1.7714e-05 | 103.1481
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | POLE | 1 | 9 | 3150 | 0.0021008 | 6.0022e-06 | 350
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | CUTOUT | 315 | 13010 | 205717 | 0.13398 | 0.0084734 | 15.8122
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | NONE | 56 | 2722 | 1081110 | 0.70413 | 0.0017728 | 397.1749
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | PEDESTAL | 22 | 104 | 8055 | 0.0052462 | 6.7735e-05 | 77.4519
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 4 | 13 | 968 | 0.00063506 | 8.5288e-06 | 74.4615
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 8 | 2256 | 0.0014859 | 5.2692e-06 | 282
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 1 | 231 | 0.000153 | 6.6234e-07 | 231
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERO | SWITCH, OH | 2 | 3970 | 369210 | 0.24318 | 0.0026148 | 93
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VIN | CUTOUT | 4 | 6 | 1682 | 0.0011141 | 3.974e-06 | 280.3333
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 7 | 462 | 0.0003031 | 4.5924e-06 | 66
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | AB | NONE | 20 | 14003 | 1505753 | 0.9807 | 0.0091201 | 107.5307
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | CUTOUT | 10 | 108 | 12924 | 0.0084174 | 7.034e-05 | 119.6667
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | INSULATOR | 4 | 212 | 52760 | 0.034363 | 0.00013808 | 248.8679
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UB | NONE | 3 | 147 | 12480 | 0.008266 | 9.7364e-05 | 84.898
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TOR | ARRESTER | 1 | 1 | 142 | 9.3528e-05 | 6.5865e-07 | 142
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | SPLICE, OH | 30 | 61 | 7721 | 0.0050287 | 3.9729e-05 | 126.5738
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | FUSE | 1 | 11 | 1386 | 0.00091801 | 7.2858e-06 | 126
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 1643 | 0.0010701 | 6.513e-07 | 1643
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | FUSE | 14 | 666 | 12478 | 0.0081269 | 0.00043377 | 18.7357
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 1807 | 137794 | 0.089745 | 0.0011769 | 76.2557
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 13 | 1244 | 0.00081022 | 8.4669e-06 | 95.6923
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VIN | CUTOUT | 4 | 13 | 1645 | 0.0010714 | 8.4669e-06 | 126.5385
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | PEDESTAL | 4 | 1680 | 184461 | 0.12014 | 0.0010942 | 109.7982
AEP-OH | 2021 | 1509795 | PARTIAL POWER | ABI | CUTOUT | 2 | 13 | 1726 | 0.0011432 | 8.6104e-06 | 132.7692
AEP-OH | 2024 | 1535393 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 14 | 812 | 0.00052885 | 9.1182e-06 | 58
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 20 | 9781 | 0.0065231 | 1.3338e-05 | 489.05
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 2 | 211 | 167769 | 0.1105 | 0.00013897 | 795.1137
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 30 | 5340 | 0.0035034 | 1.9682e-05 | 178
AEP-OH | 2024 | 1535393 | PARTIAL POWER | ABI | FUSE | 2 | 4 | 368 | 0.00023968 | 2.6052e-06 | 92
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | CUTOUT | 1 | 1 | 31 | 2.0533e-05 | 6.6234e-07 | 31
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WU | FUSE | 2 | 2 | 183 | 0.00011919 | 1.3026e-06 | 91.5
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | INSULATOR | 3 | 501 | 110533 | 0.07199 | 0.0003263 | 220.6248
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 1 | 1 | 81 | 5.3141e-05 | 6.5606e-07 | 81
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 10 | 940 | 0.0006226 | 6.6234e-06 | 94
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | ARRESTER | 1 | 979 | 39160 | 0.025937 | 0.00064843 | 40
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 5 | 23 | 2705 | 0.0017746 | 1.5089e-05 | 117.6087
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TR | NONE | 43 | 2180 | 261616 | 0.17039 | 0.0014198 | 120.0073
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | CONDUCTOR UG | 3 | 28 | 3416 | 0.0022782 | 1.8674e-05 | 122
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 5 | 115 | 31277 | 0.02052 | 7.5447e-05 | 271.9739
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | ARRESTER | 7 | 51 | 9900 | 0.006495 | 3.3459e-05 | 194.1176
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 2 | 6 | 200 | 0.00013247 | 3.974e-06 | 33.3333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FO | CUTOUT | 3 | 7 | 442 | 0.00029478 | 4.6684e-06 | 63.1429
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 93 | 6.0571e-05 | 6.513e-07 | 93
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | SCO | REGULATOR | 1 | 1900 | 62700 | 0.040836 | 0.0012375 | 33
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 19 | 1043 | 218014 | 0.14199 | 0.0006793 | 209.0259
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FO | NONE | 19 | 1205 | 55200 | 0.035952 | 0.00078482 | 45.8091
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | SWITCH, UG | 2 | 2 | 432 | 0.00028613 | 1.3247e-06 | 216
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 5 | 38 | 6908 | 0.0044992 | 2.4749e-05 | 181.7895
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 2 | 25 | 489 | 0.00031849 | 1.6282e-05 | 19.56
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | ARRESTER | 5 | 23 | 2866 | 0.0018666 | 1.498e-05 | 124.6087
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WL | FUSE | 1 | 1 | 121 | 7.9383e-05 | 6.5606e-07 | 121
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WT | POLE | 3 | 547 | 256281 | 0.16692 | 0.00035626 | 468.521
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 1 | 240 | 0.00016006 | 6.6691e-07 | 240
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WH | FUSE | 4 | 71 | 13809 | 0.0089938 | 4.6242e-05 | 194.493
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WH | SPLICE, OH | 1 | 8 | 15688 | 0.010218 | 5.2104e-06 | 1961
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TOR | SPLICE, UG | 1 | 1 | 399 | 0.0002661 | 6.6691e-07 | 399
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | ARRESTER | 1 | 1 | 218 | 0.00014302 | 6.5606e-07 | 218
AEP-OH | 2023 | 1524255 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 307 | 0.00020141 | 6.5606e-07 | 307
AEP-OH | 2023 | 1524255 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 1 | 121 | 7.9383e-05 | 6.5606e-07 | 121
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | SWITCH, UG | 7 | 217 | 29256 | 0.019054 | 0.00014133 | 134.8203
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AB | NONE | 3 | 2422 | 280753 | 0.18419 | 0.001589 | 115.9178
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AF | SPLICE, UG | 1 | 46 | 7724 | 0.0050874 | 3.0298e-05 | 167.913
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | SECTIONALIZER | 2 | 23 | 345 | 0.00022634 | 1.5089e-05 | 15
AEP-OH | 2025 | 1535393 | PARTIAL POWER | TOR | OTHER EQUIPMENT | 1 | 5 | 615 | 0.00040055 | 3.2565e-06 | 123
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 1 | 1 | 56 | 3.6473e-05 | 6.513e-07 | 56
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 1 | 14 | 1582 | 0.001042 | 9.221e-06 | 113
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | FW | NONE | 2 | 1732 | 137493 | 0.089549 | 0.001128 | 79.3839
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WL | ARRESTER | 2 | 3 | 687 | 0.00044744 | 1.9539e-06 | 229
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 1 | 260 | 0.00016934 | 6.513e-07 | 260
AEP-OH | 2024 | 1535393 | PARTIAL POWER | FO | CUTOUT | 1 | 4 | 396 | 0.00025791 | 2.6052e-06 | 99
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 1 | 241 | 0.00015962 | 6.6234e-07 | 241
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | METERING | 1 | 12 | 1536 | 0.0010244 | 8.003e-06 | 128
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 2 | 14 | 1126 | 0.00075094 | 9.3368e-06 | 80.4286
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 689 | 64638 | 0.042574 | 0.00045381 | 93.8142
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | CAPACITOR | 1 | 1 | 511 | 0.00033657 | 6.5865e-07 | 511
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 3 | 669 | 0.00044063 | 1.9759e-06 | 223
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 2 | 30 | 5804 | 0.0038442 | 1.987e-05 | 193.4667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 23 | 1863 | 0.0012425 | 1.5339e-05 | 81
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | SPLICE, OH | 1 | 794 | 135774 | 0.089076 | 0.00052091 | 171
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 4 | 240 | 19608 | 0.013077 | 0.00016006 | 81.7
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 1 | 2 | 150 | 9.8409e-05 | 1.3121e-06 | 75
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | SCO | SWITCH, OH | 2 | 1854 | 111322 | 0.073322 | 0.0012211 | 60.0442
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 3 | 3719 | 507163 | 0.33823 | 0.0024802 | 136.3708
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 1 | 8 | 5.2104e-06 | 6.513e-07 | 8
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 439 | 3386 | 377580 | 0.24869 | 0.0022302 | 111.5121
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | NONE | 82 | 19683 | 923111 | 0.608 | 0.012964 | 46.8989
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | CUTOUT | 1748 | 72502 | 7172660 | 4.7508 | 0.048021 | 98.9305
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 17 | 1200 | 303972 | 0.20021 | 0.00079037 | 253.31
AEP-OH | 2021 | 1509795 | PARTIAL POWER | ABI | NONE | 42 | 86 | 8718 | 0.0057743 | 5.6961e-05 | 101.3721
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | TRANSFORMER, UG | 13 | 54 | 19321 | 0.012726 | 3.5567e-05 | 357.7963
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WL | NONE | 8 | 20 | 5026 | 0.0033289 | 1.3247e-05 | 251.3
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 17 | 3559 | 379712 | 0.2501 | 0.0023441 | 106.6906
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 29 | 4084 | 383146 | 0.25552 | 0.0027237 | 93.8164
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | AB | NONE | 9 | 9377 | 1162023 | 0.76966 | 0.0062108 | 123.9227
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 3 | 11 | 1273 | 0.00084316 | 7.2858e-06 | 115.7273
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | CONN/CLAMP | 88 | 188 | 19706 | 0.013142 | 0.00012538 | 104.8191
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | NONE | 459 | 23867 | 3706435 | 2.4316 | 0.015658 | 155.2954
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 225 | 507 | 88197 | 0.057862 | 0.00033262 | 173.9586
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | CONN/CLAMP | 4 | 41 | 5670 | 0.0037555 | 2.7156e-05 | 138.2927
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 9 | 1242 | 0.00081804 | 5.9278e-06 | 138
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 8 | 2140 | 182886 | 0.12046 | 0.0014095 | 85.4607
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CE | OTHER EQUIPMENT | 1 | 10 | 350 | 0.00023182 | 6.6234e-06 | 35
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 38 | 1298 | 1231864 | 0.81591 | 0.00085972 | 949.0478
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | O | NONE | 5 | 1281 | 11637 | 0.0077609 | 0.00085431 | 9.0843
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | REGULATOR | 2 | 230 | 2034 | 0.0013565 | 0.00015339 | 8.8435
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FO | NONE | 54 | 8550 | 615406 | 0.40374 | 0.0056093 | 71.9773
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 238 | 615 | 96749 | 0.063473 | 0.00040348 | 157.3154
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | FO | NONE | 1 | 952 | 59024 | 0.039364 | 0.0006349 | 62
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | INSULATOR | 9 | 4140 | 642038 | 0.42818 | 0.002761 | 155.0816
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 51 | 440 | 34935 | 0.023299 | 0.00029344 | 79.3977
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | NONE | 53 | 4274 | 303631 | 0.20111 | 0.0028308 | 71.0414
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | CUTOUT | 12 | 67 | 8837 | 0.0058531 | 4.4377e-05 | 131.8955
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | SCO | NONE | 26 | 16221 | 496392 | 0.32878 | 0.010744 | 30.6018
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1201 | 69702 | 0.046167 | 0.00079547 | 58.0366
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 29 | 23646 | 0.015662 | 1.9208e-05 | 815.3793
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | CABLE TERMINATOR | 3 | 1933 | 202965 | 0.13368 | 0.0012732 | 105
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 6 | 9 | 4804 | 0.0031819 | 5.9611e-06 | 533.7778
AEP-OH | 2021 | 1509795 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 15 | 390 | 0.00025831 | 9.9351e-06 | 26
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 232 | 6032 | 0.003973 | 0.00015281 | 26
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 2 | 58 | 3.8201e-05 | 1.3173e-06 | 29
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | V | METERING | 17 | 24 | 1892 | 0.0012413 | 1.5745e-05 | 78.8333
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | PEDESTAL | 21 | 123 | 10448 | 0.0068545 | 8.0695e-05 | 84.9431
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | CUTOUT | 1372 | 50907 | 5357361 | 3.4892 | 0.033156 | 105.2382
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | JUMPER/RISER | 7 | 9 | 1305 | 0.00085616 | 5.9045e-06 | 145
AEP-OH | 2020 | 1499447 | PARTIAL POWER | FW | CONN/CLAMP | 1 | 5 | 200 | 0.00013338 | 3.3346e-06 | 40
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | REGULATOR | 6 | 1097 | 218165 | 0.14313 | 0.0007197 | 198.8742
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | NONE | 13 | 8521 | 532300 | 0.355 | 0.0056828 | 62.4692
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | POLE | 1 | 1 | 155 | 0.00010337 | 6.6691e-07 | 155
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CE | OTHER EQUIPMENT | 1 | 3 | 2544 | 0.0016756 | 1.9759e-06 | 848
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | WI | NONE | 2 | 506 | 149008 | 0.098143 | 0.00033327 | 294.4822
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 3 | 70 | 48204 | 0.032148 | 4.6684e-05 | 688.6286
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 2342 | 221710 | 0.14603 | 0.0015425 | 94.667
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | METERING | 5 | 9 | 1063 | 0.00069739 | 5.9045e-06 | 118.1111
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | REGULATOR | 11 | 4942 | 191560 | 0.12775 | 0.0032959 | 38.7616
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | SCO | NONE | 28 | 9844 | 953867 | 0.62579 | 0.0064582 | 96.8983
AEP-OH | 2024 | 1535393 | PARTIAL POWER | ABI | NONE | 36 | 70 | 5635 | 0.0036701 | 4.5591e-05 | 80.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | METERING | 4 | 256 | 19223 | 0.012661 | 0.00016861 | 75.0898
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CF | CABLE TERMINATOR | 2 | 2 | 390 | 0.00025687 | 1.3173e-06 | 195
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WT | ARRESTER | 1 | 1 | 19 | 1.2465e-05 | 6.5606e-07 | 19
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 67 | 4.3637e-05 | 6.513e-07 | 67
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 2 | 760 | 0.00050338 | 1.3247e-06 | 380
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 1945 | 529830 | 0.34508 | 0.0012668 | 272.4062
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 8 | 465 | 40885 | 0.026628 | 0.00030285 | 87.9247
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 6 | 291 | 11039 | 0.0071897 | 0.00018953 | 37.9347
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 11 | 74 | 7240 | 0.0047154 | 4.8196e-05 | 97.8378
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | CROSSARM | 41 | 13556 | 1799148 | 1.1718 | 0.008829 | 132.7197
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 116 | 1187 | 209554 | 0.13648 | 0.00077309 | 176.5409
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | FUSE | 2 | 920 | 276025 | 0.17977 | 0.0005992 | 300.0272
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 6 | 23 | 866 | 0.00056402 | 1.498e-05 | 37.6522
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | TRANSFORMER, GROUNDING | 1 | 265 | 50155 | 0.032666 | 0.00017259 | 189.2642
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | CUTOUT | 6 | 15 | 8854 | 0.0057666 | 9.7695e-06 | 590.2667
AEP-OH | 2021 | 1509795 | PARTIAL POWER | VIN | CONN/CLAMP | 2 | 6 | 590 | 0.00039078 | 3.974e-06 | 98.3333
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 49 | 3973 | 0.0025876 | 3.1914e-05 | 81.0816
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 4 | 2612 | 130044 | 0.084698 | 0.0017012 | 49.7871
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 1 | 509 | 140484 | 0.091497 | 0.00033151 | 276
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SO | TRANSFORMER, UG | 1 | 20 | 580 | 0.00038416 | 1.3247e-05 | 29
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | SWITCH, UG | 5 | 16 | 4572 | 0.0029995 | 1.0497e-05 | 285.75
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 1 | 150 | 9.8409e-05 | 6.5606e-07 | 150
AEP-OH | 2023 | 1524255 | PARTIAL POWER | O | CROSSARM | 1 | 1 | 237 | 0.00015549 | 6.5606e-07 | 237
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | O | ARRESTER | 1 | 1 | 15 | 9.7695e-06 | 6.513e-07 | 15
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | BE | OTHER EQUIPMENT | 1 | 26 | 20748 | 0.013742 | 1.7221e-05 | 798
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | METERING | 1 | 2 | 124 | 8.213e-05 | 1.3247e-06 | 62
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | POLE | 1 | 61 | 7808 | 0.0050853 | 3.9729e-05 | 128
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 266 | 49476 | 0.032224 | 0.00017325 | 186
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 78 | 4836 | 0.0031497 | 5.0801e-05 | 62
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | NONE | 40 | 2645 | 503948 | 0.32822 | 0.0017227 | 190.5285
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | ERF | NONE | 2 | 1490 | 116220 | 0.075694 | 0.00097044 | 78
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | FUSE | 1 | 8 | 1232 | 0.0008024 | 5.2104e-06 | 154
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 3 | 756 | 101686 | 0.066228 | 0.00049238 | 134.5053
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 2 | 14 | 2336 | 0.0015214 | 9.1182e-06 | 166.8571
AEP-OH | 2024 | 1535393 | DISTRIBUTION SOURCE | V | OTHER EQUIPMENT | 1 | 100 | 900 | 0.00058617 | 6.513e-05 | 9
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 805 | 0.0005243 | 1.3026e-06 | 402.5
AEP-OH | 2025 | 1535393 | PARTIAL POWER | WW | NONE | 1 | 2 | 290 | 0.00018888 | 1.3026e-06 | 145
AEP-OH | 2023 | 1524255 | PARTIAL POWER | FW | NONE | 1 | 10 | 2870 | 0.0018829 | 6.5606e-06 | 287
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | SPLICE, UG | 1 | 1707 | 287247 | 0.18919 | 0.0011243 | 168.2759
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | WL | BREAKER | 1 | 1527 | 241266 | 0.15714 | 0.00099453 | 158
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 241 | 36391 | 0.023701 | 0.00015696 | 151
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | NONE | 3660 | 66883 | 5597111 | 3.6865 | 0.044052 | 83.6851
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 15 | 318 | 74807 | 0.049271 | 0.00020945 | 235.2421
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 25 | 130 | 30315 | 0.019967 | 8.5624e-05 | 233.1923
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | FUSE | 76 | 1456 | 150621 | 0.099763 | 0.00096437 | 103.4485
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | NONE | 48 | 2087 | 160715 | 0.10585 | 0.0013746 | 77.0077
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ERF | SPLICE, OH | 1 | 1 | 50 | 3.3346e-05 | 6.6691e-07 | 50
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | PEDESTAL | 1 | 9 | 342 | 0.00022274 | 5.8617e-06 | 38
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 6 | 1824 | 0.0011967 | 3.9363e-06 | 304
AEP-OH | 2024 | 1535393 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 22 | 1547 | 0.0010076 | 1.4329e-05 | 70.3182
AEP-OH | 2025 | 1535393 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 2 | 6 | 2452 | 0.001597 | 3.9078e-06 | 408.6667
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 1 | 129 | 8.4018e-05 | 6.513e-07 | 129
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | ARRESTER | 3 | 1467 | 116740 | 0.076033 | 0.00095546 | 79.5774
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | CABLE TERMINATOR | 2 | 164 | 18345 | 0.011948 | 0.00010681 | 111.8598
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OU | POLE | 1 | 19 | 3135 | 0.0020418 | 1.2375e-05 | 165
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 98 | 6.5357e-05 | 6.6691e-07 | 98
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 986 | 122264 | 0.081539 | 0.00065758 | 124
AEP-OH | 2021 | 1509795 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 266 | 0.00017618 | 6.6234e-07 | 266
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 1074 | 82698 | 0.055152 | 0.00071626 | 77
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 3 | 3273 | 0.0021828 | 2.0007e-06 | 1091
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | SWITCH, UG | 2 | 1987 | 429054 | 0.28614 | 0.0013252 | 215.9305
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | SWITCH, UG | 2 | 49 | 4512 | 0.0030091 | 3.2679e-05 | 92.0816
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 178 | 0.0001179 | 6.6234e-07 | 178
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | UG | CROSSARM | 1 | 56 | 2533 | 0.0016497 | 3.6473e-05 | 45.2321
AEP-OH | 2023 | 1524255 | PARTIAL POWER | UB | METERING | 1 | 1 | 67 | 4.3956e-05 | 6.5606e-07 | 67
AEP-OH | 2023 | 1524255 | PARTIAL POWER | AF | CONDUCTOR UG | 1 | 2 | 402 | 0.00026374 | 1.3121e-06 | 201
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 5 | 1150 | 0.00076695 | 3.3346e-06 | 230
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | NONE | 541 | 26917 | 4835405 | 3.1848 | 0.017729 | 179.6413
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 52 | 538 | 37829 | 0.024916 | 0.00035435 | 70.3141
AEP-OH | 2022 | 1518267 | PARTIAL POWER | ERF | NONE | 4 | 22 | 503 | 0.0003313 | 1.449e-05 | 22.8636
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | FUSE | 52 | 2723 | 251353 | 0.16555 | 0.0017935 | 92.3074
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 37 | 19272 | 2652490 | 1.7569 | 0.012765 | 137.6344
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TOR | NONE | 61 | 145 | 25411 | 0.016831 | 9.604e-05 | 175.2483
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 12 | 7367 | 1174569 | 0.77362 | 0.0048522 | 159.4365
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | FUSE | 7 | 537 | 42340 | 0.028044 | 0.00035568 | 78.8454
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | CUTOUT | 22 | 380 | 90197 | 0.059741 | 0.00025169 | 237.3605
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 5 | 380 | 17318 | 0.011406 | 0.00025029 | 45.5737
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TIR | NONE | 2 | 8 | 1096 | 0.00072593 | 5.2987e-06 | 137
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | ARRESTER | 172 | 24910 | 2712286 | 1.8089 | 0.016613 | 108.8834
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UG | NONE | 51 | 592 | 103009 | 0.068698 | 0.00039481 | 174.0017
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 145 | 14135 | 1806335 | 1.2047 | 0.0094268 | 127.7917
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WU | NONE | 7 | 13 | 2543 | 0.0016843 | 8.6104e-06 | 195.6154
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | CIRCUIT SWITCHER | 2 | 2 | 275 | 0.00018214 | 1.3247e-06 | 137.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 454 | 81534 | 0.053702 | 0.00029903 | 179.5903
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 3 | 13 | 8279 | 0.0054529 | 8.5624e-06 | 636.8462
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 63 | 4.1728e-05 | 6.6234e-07 | 63
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | SWITCH, OH | 1 | 2 | 566 | 0.00037279 | 1.3173e-06 | 283
AEP-OH | 2022 | 1518267 | PARTIAL POWER | UG | SPLICE, UG | 2 | 2 | 252 | 0.00016598 | 1.3173e-06 | 126
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | POLE | 7 | 1480 | 456306 | 0.29936 | 0.00097097 | 308.3149
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 11 | 43 | 4387 | 0.0028781 | 2.8211e-05 | 102.0233
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 19 | 1582 | 0.001042 | 1.2514e-05 | 83.2632
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 10 | 497 | 51653 | 0.034448 | 0.00033146 | 103.9296
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 8 | 577 | 109854 | 0.072071 | 0.00037855 | 190.3882
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 7 | 1223 | 0.00080552 | 4.6105e-06 | 174.7143
AEP-OH | 2023 | 1524255 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 2 | 318 | 0.00020863 | 1.3121e-06 | 159
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 2438 | 241220 | 0.15888 | 0.0016058 | 98.9418
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VIN | FUSE | 11 | 62 | 13007 | 0.0085333 | 4.0676e-05 | 209.7903
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | NONE | 4506 | 58762 | 4689039 | 3.054 | 0.038272 | 79.7971
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | CONDUCTOR UG | 541 | 1053 | 183065 | 0.11923 | 0.00068582 | 173.8509
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 273 | 3330 | 276326 | 0.17997 | 0.0021688 | 82.9808
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | NONE | 571 | 44069 | 7105247 | 4.6276 | 0.028702 | 161.23
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 1 | 76 | 5.0057e-05 | 6.5865e-07 | 76
AEP-OH | 2023 | 1524255 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 26 | 85 | 18114 | 0.011884 | 5.5765e-05 | 213.1059
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 7 | 14 | 1175 | 0.00078362 | 9.3368e-06 | 83.9286
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 4 | 48 | 10305 | 0.0067116 | 3.1262e-05 | 214.6875
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | NONE | 211 | 5900 | 1031121 | 0.67157 | 0.0038427 | 174.7663
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | INSULATOR | 101 | 24528 | 3358147 | 2.1872 | 0.015975 | 136.9108
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | FUSE | 9 | 175 | 57309 | 0.037598 | 0.00011481 | 327.48
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 5 | 18 | 8254 | 0.0053758 | 1.1723e-05 | 458.5556
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | SWITCH, UG | 3 | 145 | 24393 | 0.016268 | 9.6702e-05 | 168.2276
AEP-OH | 2023 | 1524255 | PARTIAL POWER | A | CABLE TERMINATOR | 1 | 2 | 138 | 9.0536e-05 | 1.3121e-06 | 69
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 2521 | 249159 | 0.16228 | 0.0016419 | 98.8334
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 5 | 1250 | 0.00081412 | 3.2565e-06 | 250
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 7 | 651 | 0.00043118 | 4.6364e-06 | 93
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | ARRESTER | 6 | 6 | 178 | 0.00011593 | 3.9078e-06 | 29.6667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 78 | 4914 | 0.0032772 | 5.2019e-05 | 63
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | CROSSARM | 4 | 370 | 93263 | 0.062198 | 0.00024676 | 252.0622
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CF | JUMPER/RISER | 1 | 1 | 139 | 9.2065e-05 | 6.6234e-07 | 139
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 6 | 1146 | 0.00074639 | 3.9078e-06 | 191
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 16 | 2472 | 0.00161 | 1.0421e-05 | 154.5
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 4 | 102 | 13927 | 0.0091369 | 6.6918e-05 | 136.5392
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | ABX | BREAKER | 1 | 902 | 83886 | 0.055034 | 0.00059176 | 93
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 14 | 692 | 0.0004507 | 9.1182e-06 | 49.4286
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 34 | 7140 | 0.0046503 | 2.2144e-05 | 210
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 4 | 19 | 4974 | 0.0032396 | 1.2375e-05 | 261.7895
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 4 | 640 | 0.00041683 | 2.6052e-06 | 160
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | POLE | 1 | 23 | 16606 | 0.010815 | 1.498e-05 | 722
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 2 | 1978 | 0.0012883 | 1.3026e-06 | 989
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 5 | 2075 | 0.0013514 | 3.2565e-06 | 415
AEP-OH | 2024 | 1535393 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 10 | 970 | 0.00063176 | 6.513e-06 | 97
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 8 | 7232 | 0.0047446 | 5.2485e-06 | 904
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | AB | BREAKER | 5 | 9598 | 1137509 | 0.75342 | 0.0063572 | 118.5152
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 3 | 51 | 3.3459e-05 | 1.9682e-06 | 17
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 71 | 55664 | 0.036254 | 4.6242e-05 | 784
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ABI | CONN/CLAMP | 1 | 2 | 162 | 0.00010804 | 1.3338e-06 | 81
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 6 | 1110 | 0.00072294 | 3.9078e-06 | 185
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 1 | 106 | 7.0693e-05 | 6.6691e-07 | 106
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 826 | 6805 | 1661008 | 1.094 | 0.0044821 | 244.0864
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | POLE | 4111 | 31918 | 4404847 | 2.9175 | 0.021141 | 138.0051
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | V | METERING | 23 | 33 | 2858 | 0.0018824 | 2.1735e-05 | 86.6061
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | SPLICE, OH | 11 | 42 | 1889 | 0.0012442 | 2.7663e-05 | 44.9762
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TOR | NONE | 135 | 275 | 68425 | 0.044891 | 0.00018042 | 248.8182
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TIR | NONE | 10 | 17 | 2018 | 0.0013291 | 1.1197e-05 | 118.7059
AEP-OH | 2022 | 1518267 | PARTIAL POWER | ABI | NONE | 40 | 219 | 22817 | 0.015028 | 0.00014424 | 104.1872
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 16 | 391 | 72704 | 0.047886 | 0.00025753 | 185.9437
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 164 | 12521 | 1234146 | 0.81743 | 0.0082932 | 98.5661
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | NONE | 46 | 324 | 27542 | 0.01814 | 0.0002134 | 85.0062
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 13 | 3674 | 1013404 | 0.66747 | 0.0024199 | 275.8312
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | SPLICE, OH | 3 | 16 | 8116 | 0.0053456 | 1.0538e-05 | 507.25
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | CUTOUT | 36 | 542 | 200385 | 0.13272 | 0.00035899 | 369.714
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TOR | CONN/CLAMP | 11 | 25 | 4168 | 0.0027452 | 1.6466e-05 | 166.72
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 54 | 3078 | 0.0020273 | 3.5567e-05 | 57
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 74 | 23464 | 2190251 | 1.4507 | 0.015541 | 93.3452
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 1 | 190 | 0.00012514 | 6.5865e-07 | 190
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 657 | 31496 | 5946962 | 3.9661 | 0.021005 | 188.8164
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | CONDUCTOR UG | 532 | 922 | 204034 | 0.13607 | 0.00061489 | 221.295
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 129 | 8.6032e-05 | 1.3338e-06 | 64.5
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | PEDESTAL | 39 | 208 | 16142 | 0.010765 | 0.00013872 | 77.6058
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 23 | 1601 | 147050 | 0.098069 | 0.0010677 | 91.8488
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | NONE | 352 | 8970 | 1247386 | 0.8319 | 0.0059822 | 139.062
AEP-OH | 2021 | 1509795 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 7 | 7 | 1036 | 0.00068619 | 4.6364e-06 | 148
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 17 | 1993 | 595193 | 0.39202 | 0.0013127 | 298.6417
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VA | TRANSFORMER, OH | 2 | 3 | 541 | 0.00035633 | 1.9759e-06 | 180.3333
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | CUTOUT | 7 | 319 | 78541 | 0.051731 | 0.00021011 | 246.21
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 22 | 3238 | 0.0021327 | 1.449e-05 | 147.1818
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CO | ARRESTER | 1 | 1 | 288 | 0.00019075 | 6.6234e-07 | 288
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 248 | 18519 | 0.012266 | 0.00016426 | 74.6734
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SO | FUSE | 1 | 4 | 452 | 0.00029938 | 2.6494e-06 | 113
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WL | SPLICE, OH | 1 | 1 | 174 | 0.0001146 | 6.5865e-07 | 174
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | INSULATOR | 10 | 1121 | 18305 | 0.012057 | 0.00073834 | 16.3292
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | NONE | 754 | 12425 | 980449 | 0.64323 | 0.0081515 | 78.9094
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 29 | 515 | 210049 | 0.1378 | 0.00033787 | 407.8621
AEP-OH | 2023 | 1524255 | PARTIAL POWER | A | OTHER EQUIPMENT | 1 | 1 | 95 | 6.2326e-05 | 6.5606e-07 | 95
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 5 | 43 | 4815 | 0.0031589 | 2.8211e-05 | 111.9767
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 4 | 668 | 0.0004455 | 2.6677e-06 | 167
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | INSULATOR | 5 | 191 | 4161 | 0.0027101 | 0.0001244 | 21.7853
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | CUTOUT | 10 | 63 | 3683 | 0.0024163 | 4.1332e-05 | 58.4603
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 7 | 4872 | 0.0032089 | 4.6105e-06 | 696
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 3 | 8 | 2046 | 0.0013552 | 5.2987e-06 | 255.75
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | ARRESTER | 150 | 6496 | 800344 | 0.52126 | 0.0042308 | 123.2057
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WL | NONE | 9 | 46 | 20394 | 0.013601 | 3.0678e-05 | 443.3478
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 11 | 116 | 17712 | 0.01162 | 7.6103e-05 | 152.6897
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 5 | 300 | 0.00019682 | 3.2803e-06 | 60
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | TRANSFORMER, UG | 6 | 10 | 3190 | 0.0020928 | 6.5606e-06 | 319
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 3860 | 546855 | 0.35617 | 0.002514 | 141.6723
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 3 | 13 | 590 | 0.00038427 | 8.4669e-06 | 45.3846
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | INSULATOR | 15 | 13564 | 1895281 | 1.264 | 0.009046 | 139.7288
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | INSULATOR | 1 | 3 | 717 | 0.0004749 | 1.987e-06 | 239
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | ARRESTER | 10 | 386 | 145917 | 0.096108 | 0.00025424 | 378.0233
AEP-OH | 2022 | 1518267 | PARTIAL POWER | U | CONDUCTOR UG | 6 | 6 | 1812 | 0.0011935 | 3.9519e-06 | 302
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | POLE | 9 | 1272 | 197663 | 0.13019 | 0.0008378 | 155.3954
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 2 | 2364 | 242682 | 0.16074 | 0.0015658 | 102.6574
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | JUMPER/RISER | 1 | 235 | 10105 | 0.006693 | 0.00015565 | 43
AEP-OH | 2022 | 1518267 | PARTIAL POWER | A | CUTOUT | 1 | 1 | 72 | 4.7422e-05 | 6.5865e-07 | 72
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | FUSE | 11 | 146 | 30716 | 0.020231 | 9.6162e-05 | 210.3836
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | SWITCH, OH | 5 | 8398 | 448874 | 0.29565 | 0.0055313 | 53.4501
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | U | NONE | 17 | 16990 | 2480438 | 1.6337 | 0.01119 | 145.994
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | NONE | 123 | 15759 | 749559 | 0.49989 | 0.01051 | 47.5639
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 863 | 25300 | 0.016873 | 0.00057555 | 29.3163
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 10 | 2237 | 208855 | 0.13833 | 0.0014817 | 93.3639
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 22 | 4110 | 0.0027222 | 1.4572e-05 | 186.8182
AEP-OH | 2021 | 1509795 | PARTIAL POWER | TOR | CONN/CLAMP | 15 | 18 | 2416 | 0.0016002 | 1.1922e-05 | 134.2222
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 4 | 48 | 3.1792e-05 | 2.6494e-06 | 12
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WI | METERING | 3 | 3 | 1234 | 0.00081733 | 1.987e-06 | 411.3333
AEP-OH | 2022 | 1518267 | PARTIAL POWER | V | NONE | 1 | 1 | 28 | 1.8442e-05 | 6.5865e-07 | 28
AEP-OH | 2021 | 1509795 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 15 | 9.9351e-06 | 6.6234e-07 | 15
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AO | INSULATOR | 2 | 787 | 163187 | 0.10748 | 0.00051835 | 207.3532
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | R | NONE | 3 | 1429 | 192718 | 0.12693 | 0.0009412 | 134.8621
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SO | NONE | 6 | 65 | 1838 | 0.0012106 | 4.2812e-05 | 28.2769
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 67 | 19162 | 0.012621 | 4.4129e-05 | 286
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | NONE | 68 | 2917 | 573360 | 0.37616 | 0.0019137 | 196.5581
AEP-OH | 2022 | 1518267 | PARTIAL POWER | OU | NONE | 1 | 1 | 143 | 9.4186e-05 | 6.5865e-07 | 143
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 14 | 1062 | 51035 | 0.033482 | 0.00069673 | 48.0556
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WL | ARRESTER | 1 | 19 | 1501 | 0.00098474 | 1.2465e-05 | 79
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | NONE | 93 | 2104 | 191206 | 0.12544 | 0.0013803 | 90.8774
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 1074 | 115713 | 0.075914 | 0.00070461 | 107.7402
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | POLE | 3602 | 24533 | 3050880 | 1.987 | 0.015978 | 124.3582
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 4 | 906 | 0.00059673 | 2.6346e-06 | 226.5
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OL | CONN/CLAMP | 4 | 16 | 1348 | 0.00089284 | 1.0597e-05 | 84.25
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WL | ARRESTER | 3 | 12 | 2065 | 0.0013772 | 8.003e-06 | 172.0833
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 33 | 470 | 31025 | 0.020691 | 0.00031345 | 66.0106
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WFS | NONE | 3 | 31 | 13652 | 0.0090423 | 2.0533e-05 | 440.3871
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ERF | NONE | 85 | 13216 | 685510 | 0.44647 | 0.0086076 | 51.8697
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WU | NONE | 14 | 28 | 4981 | 0.0032441 | 1.8236e-05 | 177.8929
AEP-OH | 2024 | 1535393 | PARTIAL POWER | U | TRANSFORMER, OH | 2 | 3 | 584 | 0.00038036 | 1.9539e-06 | 194.6667
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | METERING | 16 | 81 | 6610 | 0.0043365 | 5.3141e-05 | 81.6049
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 2 | 72 | 104719 | 0.069838 | 4.8018e-05 | 1454.4306
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | CROSSARM | 26 | 12071 | 1312012 | 0.86076 | 0.0079193 | 108.6912
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | METERING | 1 | 81 | 6318 | 0.004145 | 5.3141e-05 | 78
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | NONE | 10 | 80 | 11008 | 0.0073414 | 5.3353e-05 | 137.6
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AO | INSULATOR | 1 | 941 | 251545 | 0.16776 | 0.00062756 | 267.3167
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 200 | 0.00013173 | 6.5865e-07 | 200
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 1 | 2 | 2480 | 0.0016426 | 1.3247e-06 | 1240
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | POLE | 1 | 6 | 1578 | 0.0010353 | 3.9363e-06 | 263
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | POLE | 7 | 3360 | 1102754 | 0.71822 | 0.0021884 | 328.2006
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | FUSE | 3 | 18 | 2338 | 0.0015592 | 1.2004e-05 | 129.8889
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 4 | 12 | 392 | 0.00025531 | 7.8156e-06 | 32.6667
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 255 | 15698 | 1726833 | 1.1247 | 0.010224 | 110.0034
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 182 | 729 | 69095 | 0.045002 | 0.0004748 | 94.7805
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 52 | 339 | 55309 | 0.036023 | 0.00022079 | 163.1534
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | CONN/CLAMP | 9 | 21 | 4835 | 0.003149 | 1.3677e-05 | 230.2381
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 11 | 219 | 26783 | 0.017444 | 0.00014263 | 122.2968
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 342 | 2722 | 322980 | 0.21036 | 0.0017728 | 118.6554
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | FUSE | 16 | 212 | 108190 | 0.070464 | 0.00013808 | 510.3302
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | FUSE | 14 | 51 | 3963 | 0.0025811 | 3.3216e-05 | 77.7059
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | CE | NONE | 13 | 836 | 140283 | 0.091366 | 0.00054449 | 167.8026
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | CUTOUT | 13 | 127 | 16361 | 0.010656 | 8.2715e-05 | 128.8268
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 589 | 0.00038362 | 6.513e-07 | 589
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 6 | 876 | 0.00058021 | 3.974e-06 | 146
AEP-OH | 2020 | 1499447 | PARTIAL POWER | UB | CONDUCTOR UG | 3 | 4 | 2866 | 0.0019114 | 2.6677e-06 | 716.5
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AO | REGULATOR | 1 | 112 | 9408 | 0.0061722 | 7.3479e-05 | 84
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 6 | 67 | 6627 | 0.0043162 | 4.3637e-05 | 98.9104
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 6116 | 1139405 | 0.74209 | 0.0039833 | 186.2991
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | OL | NONE | 1 | 1104 | 141312 | 0.092036 | 0.00071903 | 128
AEP-OH | 2024 | 1535393 | PARTIAL POWER | U | FUSE | 3 | 4 | 291 | 0.00018953 | 2.6052e-06 | 72.75
AEP-OH | 2023 | 1524255 | DISTRIBUTION SOURCE | EQF | CUTOUT | 1 | 5 | 5960 | 0.0039101 | 3.2803e-06 | 1192
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 4 | 705 | 0.00045917 | 2.6052e-06 | 176.25
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | INSULATOR | 1 | 6 | 432 | 0.00028136 | 3.9078e-06 | 72
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | POLE HARDWARE | 2 | 37 | 8698 | 0.005665 | 2.4098e-05 | 235.0811
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1 | 40 | 2.6052e-05 | 6.513e-07 | 40
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TIR | NONE | 9 | 40 | 9311 | 0.0062096 | 2.6677e-05 | 232.775
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 831 | 34018 | 3260866 | 2.1238 | 0.022156 | 95.8571
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 146 | 800 | 69594 | 0.045327 | 0.00052104 | 86.9925
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | NONE | 261 | 27707 | 3466290 | 2.2576 | 0.018046 | 125.1052
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | METERING | 10 | 15 | 1171 | 0.00078095 | 1.0004e-05 | 78.0667
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 3 | 10 | 2259 | 0.0015066 | 6.6691e-06 | 225.9
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 2 | 4 | 412 | 0.00026834 | 2.6052e-06 | 103
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | FUSE | 27 | 1122 | 151423 | 0.099342 | 0.0007361 | 134.9581
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | SWITCH, OH | 1 | 711 | 21330 | 0.014049 | 0.0004683 | 30
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 5 | 26 | 3783 | 0.0025229 | 1.734e-05 | 145.5
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 6 | 3445 | 772123 | 0.50656 | 0.0022601 | 224.1286
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 3 | 43 | 984 | 0.00064556 | 2.8211e-05 | 22.8837
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 2 | 216 | 0.00014307 | 1.3247e-06 | 108
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WU | FUSE | 2 | 3 | 655 | 0.00043383 | 1.987e-06 | 218.3333
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | CROSSARM | 5 | 4355 | 1006603 | 0.66672 | 0.0028845 | 231.1373
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CF | CUTOUT | 4 | 24 | 1045 | 0.00069215 | 1.5896e-05 | 43.5417
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 60 | 1795 | 223511 | 0.14557 | 0.0011691 | 124.5187
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 10 | 344 | 29288 | 0.019075 | 0.00022405 | 85.1395
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | CUTOUT | 10 | 59 | 52829 | 0.034407 | 3.8427e-05 | 895.4068
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | INSULATOR | 47 | 7157 | 1165939 | 0.75937 | 0.0046613 | 162.9089
AEP-OH | 2025 | 1535393 | DISTRIBUTION SOURCE | O | NONE | 1 | 282 | 42018 | 0.027366 | 0.00018367 | 149
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | JUMPER/RISER | 3 | 16 | 3251 | 0.0021174 | 1.0421e-05 | 203.1875
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 9 | 2070 | 0.0013634 | 5.9278e-06 | 230
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 6 | 4875 | 956425 | 0.63785 | 0.0032512 | 196.1897
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 1 | 368 | 0.00024542 | 6.6691e-07 | 368
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 36 | 7289 | 0.0048611 | 2.4009e-05 | 202.4722
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | U | NONE | 4 | 4599 | 416347 | 0.27576 | 0.0030461 | 90.5299
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 718 | 9991 | 0.0065071 | 0.00046763 | 13.915
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | FUSE | 5 | 98 | 24800 | 0.016152 | 6.3827e-05 | 253.0612
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | ARRESTER | 1 | 4 | 96 | 6.2525e-05 | 2.6052e-06 | 24
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | OL | FUSE | 1 | 102 | 2040 | 0.0013287 | 6.6433e-05 | 20
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SO | CUTOUT | 2 | 11 | 2480 | 0.0016539 | 7.336e-06 | 225.4545
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | POLE | 5 | 245 | 313096 | 0.20392 | 0.00015957 | 1277.9429
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FW | CROSSARM | 1 | 300 | 19500 | 0.0127 | 0.00019539 | 65
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | POLE HARDWARE | 1 | 100 | 25419 | 0.016555 | 6.513e-05 | 254.19
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 2500 | 430000 | 0.28006 | 0.0016282 | 172
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 99 | 6.5206e-05 | 6.5865e-07 | 99
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 3 | 9 | 559 | 0.00036674 | 5.9045e-06 | 62.1111
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 1448 | 0.00096569 | 6.6691e-07 | 1448
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 89 | 8291 | 0.0053999 | 5.7966e-05 | 93.1573
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | SWITCH, UG | 1 | 5 | 475 | 0.00030937 | 3.2565e-06 | 95
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VIN | CONDUCTOR UG | 1 | 5 | 540 | 0.00035766 | 3.3117e-06 | 108
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 355 | 0.00023382 | 6.5865e-07 | 355
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1201 | 174544 | 0.11641 | 0.00080096 | 145.3322
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | POLE | 502 | 91853 | 16569099 | 10.9132 | 0.060499 | 180.3871
AEP-OH | 2023 | 1524255 | PARTIAL POWER | U | NONE | 139 | 362 | 42549 | 0.027915 | 0.00023749 | 117.5387
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | NONE | 45 | 478 | 88964 | 0.058596 | 0.00031483 | 186.1172
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 264 | 795 | 148206 | 0.097615 | 0.00052362 | 186.4226
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 677 | 3978 | 1032320 | 0.67726 | 0.0026098 | 259.5073
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | METERING | 47 | 291 | 49949 | 0.032899 | 0.00019167 | 171.646
AEP-OH | 2021 | 1509795 | PARTIAL POWER | U | NONE | 124 | 446 | 54031 | 0.035787 | 0.0002954 | 121.1457
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | ARRESTER | 10 | 760 | 58965 | 0.038837 | 0.00050057 | 77.5855
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | FUSE | 44 | 383 | 29915 | 0.019703 | 0.00025226 | 78.107
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 121 | 2638 | 695773 | 0.45827 | 0.0017375 | 263.7502
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 258 | 61146 | 0.040274 | 0.00016993 | 237
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | NONE | 368 | 23931 | 3511374 | 2.3257 | 0.01585 | 146.7291
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | WU | NONE | 2 | 1573 | 429810 | 0.28309 | 0.001036 | 273.2422
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 7 | 21 | 9124 | 0.0060095 | 1.3832e-05 | 434.4762
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | POLE | 11 | 855 | 332197 | 0.22003 | 0.0005663 | 388.5345
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | CROSSARM | 34 | 22257 | 2298097 | 1.5221 | 0.014742 | 103.2528
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | NONE | 1449 | 35311 | 2739307 | 1.8269 | 0.023549 | 77.5766
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | ABI | NONE | 1 | 556 | 120940 | 0.079657 | 0.00036621 | 217.518
AEP-OH | 2020 | 1499447 | PARTIAL POWER | EQF | CONN/CLAMP | 813 | 2202 | 270970 | 0.18071 | 0.0014685 | 123.0563
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OU | NONE | 13 | 7436 | 505356 | 0.33703 | 0.0049592 | 67.9607
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | NONE | 158 | 6552 | 1476621 | 0.98478 | 0.0043696 | 225.3695
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 4 | 752 | 0.00049808 | 2.6494e-06 | 188
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 18 | 312 | 23102 | 0.015301 | 0.00020665 | 74.0449
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | FUSE | 4 | 56 | 8792 | 0.0058233 | 3.7091e-05 | 157
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | FUSE | 457 | 4847 | 501706 | 0.32915 | 0.0031799 | 103.5086
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VA | NONE | 2 | 5 | 348 | 0.00022921 | 3.2932e-06 | 69.6
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | INSULATOR | 135 | 33803 | 3831340 | 2.5136 | 0.022177 | 113.3432
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | ARRESTER | 82 | 424 | 11639 | 0.0077622 | 0.00028277 | 27.4505
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 47 | 169 | 55221 | 0.036828 | 0.00011271 | 326.7515
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 3 | 476 | 412714 | 0.27076 | 0.00031228 | 867.0462
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | CROSSARM | 4 | 1436 | 396106 | 0.26236 | 0.00095112 | 275.8398
AEP-OH | 2020 | 1499447 | PARTIAL POWER | U | METERING | 1 | 1 | 150 | 0.00010004 | 6.6691e-07 | 150
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | UG | NONE | 9 | 666 | 209565 | 0.13649 | 0.00043377 | 314.6622
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ERF | POLE | 2 | 912 | 245532 | 0.15991 | 0.00059398 | 269.2237
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CE | NONE | 1 | 2 | 274 | 0.00018273 | 1.3338e-06 | 137
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | CE | POLE | 1 | 3 | 1176 | 0.00076593 | 1.9539e-06 | 392
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | O | FUSE | 2 | 91 | 16561 | 0.010786 | 5.9268e-05 | 181.989
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | CUTOUT | 5 | 14 | 4547 | 0.0029615 | 9.1182e-06 | 324.7857
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | F | CUTOUT | 2 | 73 | 20005 | 0.013029 | 4.7545e-05 | 274.0411
AEP-OH | 2025 | 1535393 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 2 | 142 | 9.2484e-05 | 1.3026e-06 | 71
AEP-OH | 2023 | 1524255 | DISTRIBUTION SOURCE | SCO | ARRESTER | 1 | 10 | 170 | 0.00011153 | 6.5606e-06 | 17
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WI | CONN/CLAMP | 1 | 3 | 90 | 5.9278e-05 | 1.9759e-06 | 30
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | AF | NONE | 3 | 297 | 43092 | 0.028066 | 0.00019344 | 145.0909
AEP-OH | 2025 | 1535393 | PARTIAL POWER | WU | FUSE | 1 | 1 | 26 | 1.6934e-05 | 6.513e-07 | 26
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 18 | 1134 | 0.00073857 | 1.1723e-05 | 63
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 8 | 480 | 0.00031491 | 5.2485e-06 | 60
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | V | REGULATOR | 1 | 412 | 16068 | 0.010542 | 0.0002703 | 39
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | SPLICE, OH | 1 | 6 | 642 | 0.00041813 | 3.9078e-06 | 107
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | POLE | 11 | 4431 | 1204189 | 0.78429 | 0.0028859 | 271.7646
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | WU | NONE | 2 | 4639 | 652567 | 0.42502 | 0.0030214 | 140.6698
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 213 | 75330 | 0.049062 | 0.00013873 | 353.662
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | BREAKER | 4 | 2858 | 661091 | 0.44089 | 0.001906 | 231.3125
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 346 | 0.00023075 | 6.6691e-07 | 346
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 24 | 1901 | 0.0012591 | 1.5896e-05 | 79.2083
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 4 | 4 | 793 | 0.00052524 | 2.6494e-06 | 198.25
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | POLE HARDWARE | 1 | 1 | 248 | 0.00016426 | 6.6234e-07 | 248
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 2 | 74 | 4.8548e-05 | 1.3121e-06 | 37
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CF | CROSSARM | 1 | 26 | 2080 | 0.0013777 | 1.7221e-05 | 80
AEP-OH | 2021 | 1509795 | DISTRIBUTION SOURCE | TOR | CONDUCTOR OVERHEAD | 1 | 1277 | 739383 | 0.48972 | 0.00084581 | 579
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 655 | 24848 | 3312528 | 2.1818 | 0.016366 | 133.3117
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 269 | 526 | 125163 | 0.082438 | 0.00034645 | 237.9525
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | FUSE | 67 | 1288 | 74778 | 0.049252 | 0.00084834 | 58.0575
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 9 | 4936 | 162172 | 0.10681 | 0.0032511 | 32.8549
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 58 | 2174 | 400968 | 0.2641 | 0.0014319 | 184.4379
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | FUSE | 5 | 749 | 44987 | 0.02963 | 0.00049333 | 60.0628
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | JUMPER/RISER | 8 | 5932 | 790784 | 0.52085 | 0.0039071 | 133.3082
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | REGULATOR | 12 | 18367 | 981966 | 0.64677 | 0.012097 | 53.4636
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | NONE | 362 | 12016 | 1510090 | 1.0002 | 0.0079587 | 125.6733
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 28 | 3824 | 293434 | 0.19569 | 0.0025503 | 76.7348
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | CUTOUT | 1226 | 8019 | 286686 | 0.19119 | 0.005348 | 35.7508
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | CUTOUT | 7 | 64 | 11355 | 0.0075209 | 4.239e-05 | 177.4219
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CO | CONDUCTOR UG | 36 | 121 | 43884 | 0.029066 | 8.0143e-05 | 362.6777
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | METERING | 4 | 115 | 122339 | 0.080578 | 7.5744e-05 | 1063.8174
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 653 | 46997 | 6167711 | 4.0464 | 0.030833 | 131.2363
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 51 | 1249 | 284452 | 0.1897 | 0.00083297 | 227.7438
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | ERF | NONE | 11 | 7470 | 543676 | 0.3601 | 0.0049477 | 72.7813
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 4 | 3572 | 0.0023659 | 2.6494e-06 | 893
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 1 | 91 | 6.0273e-05 | 6.6234e-07 | 91
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CO | NONE | 10 | 32 | 3867 | 0.002547 | 2.1077e-05 | 120.8438
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | POLE | 7 | 149 | 78112 | 0.051246 | 9.7753e-05 | 524.2416
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 7 | 126 | 7501 | 0.0049211 | 8.2663e-05 | 59.5317
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 10 | 1026 | 71224 | 0.046727 | 0.00067312 | 69.4191
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | JUMPER/RISER | 10 | 5264 | 508661 | 0.33691 | 0.0034866 | 96.6301
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 167 | 5931 | 1405060 | 0.91511 | 0.0038629 | 236.901
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | METERING | 29 | 37 | 3407 | 0.0022352 | 2.4274e-05 | 92.0811
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | CUTOUT | 2 | 40 | 11620 | 0.0076234 | 2.6242e-05 | 290.5
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 109 | 29321 | 0.019555 | 7.2693e-05 | 269
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | INSULATOR | 4 | 2778 | 258519 | 0.1696 | 0.0018225 | 93.0594
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | CF | NONE | 6 | 1175 | 157315 | 0.10492 | 0.00078362 | 133.8851
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 13 | 3874 | 0.0025416 | 8.5288e-06 | 298
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TR | SPLICE, OH | 1 | 1 | 94 | 6.269e-05 | 6.6691e-07 | 94
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CO | CABLE TERMINATOR | 4 | 6 | 794 | 0.0005259 | 3.974e-06 | 132.3333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 86 | 8256 | 0.005506 | 5.7354e-05 | 96
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 3880 | 35690 | 0.023415 | 0.0025455 | 9.1985
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TR | NONE | 3 | 19 | 2271 | 0.0015146 | 1.2671e-05 | 119.5263
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 3 | 63 | 4.1332e-05 | 1.9682e-06 | 21
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 4 | 4104 | 56276 | 0.03692 | 0.0026925 | 13.7125
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AB | INSULATOR | 2 | 2674 | 281238 | 0.18756 | 0.0017833 | 105.175
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 1 | 147 | 9.5741e-05 | 6.513e-07 | 147
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | CUTOUT | 415 | 3154 | 74087 | 0.048253 | 0.0020542 | 23.4899
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ERF | NONE | 26 | 3163 | 97696 | 0.063629 | 0.0020601 | 30.8871
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 5 | 12 | 869 | 0.00056598 | 7.8156e-06 | 72.4167
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | GUY/ANCHOR | 3 | 2922 | 322944 | 0.21033 | 0.0019031 | 110.5216
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 589 | 267406 | 0.17416 | 0.00038362 | 454
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TR | POLE | 6 | 150 | 47972 | 0.031244 | 9.7695e-05 | 319.8133
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | RELAY | 20 | 7686 | 1117963 | 0.74047 | 0.0050908 | 145.4545
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | ERF | INSULATOR | 2 | 201 | 42161 | 0.027925 | 0.00013313 | 209.7562
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | JUMPER/RISER | 3 | 46 | 7458 | 0.0048574 | 2.996e-05 | 162.1304
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 19 | 9994 | 0.0066651 | 1.2671e-05 | 526
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | F | CUTOUT | 3 | 96 | 2032 | 0.0013234 | 6.2525e-05 | 21.1667
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | FUSE | 20 | 272 | 44338 | 0.028877 | 0.00017715 | 163.0074
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 17 | 482 | 240407 | 0.15658 | 0.00031393 | 498.7697
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OU | POLE | 3 | 184 | 162278 | 0.10748 | 0.00012187 | 881.9457
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | R | NONE | 2 | 4461 | 729939 | 0.47541 | 0.0029054 | 163.6268
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | CAPACITOR | 1 | 4 | 784 | 0.00052286 | 2.6677e-06 | 196
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 936 | 0.00061995 | 6.6234e-07 | 936
AEP-OH | 2021 | 1509795 | PARTIAL POWER | SCO | CONDUCTOR OVERHEAD | 1 | 1 | 490 | 0.00032455 | 6.6234e-07 | 490
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 193 | 45350 | 0.029752 | 0.00012662 | 234.9741
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 1 | 125 | 8.2793e-05 | 6.6234e-07 | 125
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | AB | INSULATOR | 9 | 14704 | 967314 | 0.63001 | 0.0095767 | 65.7858
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 10 | 38 | 896 | 0.00059755 | 2.5343e-05 | 23.5789
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 11 | 6408 | 0.0042736 | 7.336e-06 | 582.5455
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | O | POLE | 1 | 33 | 1290 | 0.00086032 | 2.2008e-05 | 39.0909
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SO | TRANSFORMER, OH | 1 | 3 | 360 | 0.00023844 | 1.987e-06 | 120
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | FUSE | 1 | 58 | 5452 | 0.003636 | 3.8681e-05 | 94
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | U | NONE | 12 | 7049 | 870320 | 0.57098 | 0.0046246 | 123.4672
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WH | POLE | 1 | 4 | 11344 | 0.0073883 | 2.6052e-06 | 2836
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | EQF | RELAY | 1 | 1345 | 182593 | 0.11892 | 0.000876 | 135.7569
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | AO | NONE | 7 | 5404 | 206070 | 0.13421 | 0.0035196 | 38.1329
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | POLE | 5 | 906 | 59612 | 0.039756 | 0.00060422 | 65.7969
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | SWITCH, OH | 2 | 11 | 583 | 0.00037971 | 7.1643e-06 | 53
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | V | CONDUCTOR UG | 3 | 7182 | 473783 | 0.30857 | 0.0046776 | 65.9681
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 1 | 103 | 145745 | 0.094924 | 6.7084e-05 | 1415
AEP-OH | 2025 | 1535393 | PARTIAL POWER | ERF | CROSSARM | 1 | 1 | 30 | 1.9539e-05 | 6.513e-07 | 30
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | SPLICE, UG | 2 | 1705 | 28985 | 0.018878 | 0.0011105 | 17
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TIR | FUSE | 1 | 6 | 2208 | 0.0014486 | 3.9363e-06 | 368
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 1382 | 235133 | 0.15314 | 0.0009001 | 170.1397
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WFS | TRANSFORMER, UG | 1 | 1 | 697 | 0.00046484 | 6.6691e-07 | 697
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | FUSE | 3 | 2206 | 246363 | 0.1643 | 0.0014712 | 111.6786
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 1 | 49 | 3.2455e-05 | 6.6234e-07 | 49
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 4 | 1256 | 0.00083764 | 2.6677e-06 | 314
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 444 | 70170 | 0.045702 | 0.00028918 | 158.0405
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 972 | 0.00063306 | 1.3026e-06 | 486
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 902 | 15858 | 2313759 | 1.5325 | 0.010503 | 145.9048
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 118 | 2987 | 831433 | 0.55069 | 0.0019784 | 278.3505
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | POLE | 3333 | 25788 | 3907378 | 2.5736 | 0.016985 | 151.5192
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 750 | 3851 | 412806 | 0.27189 | 0.0025364 | 107.1945
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | REGULATOR | 7 | 4680 | 972609 | 0.6406 | 0.0030825 | 207.8224
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | FUSE | 579 | 6997 | 759977 | 0.50336 | 0.0046344 | 108.6147
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | OL | NONE | 9 | 8817 | 635607 | 0.41864 | 0.0058073 | 72.0888
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | ARRESTER | 86 | 281 | 6462 | 0.0042562 | 0.00018508 | 22.9964
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WL | ARRESTER | 46 | 1357 | 178515 | 0.11824 | 0.0008988 | 131.5512
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | SPLICE, OH | 7 | 24 | 4719 | 0.0031256 | 1.5896e-05 | 196.625
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 41 | 1875 | 580263 | 0.38433 | 0.0012419 | 309.4736
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 3 | 7194 | 0.0047383 | 1.9759e-06 | 2398
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FW | METERING | 1 | 1 | 25 | 1.6559e-05 | 6.6234e-07 | 25
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 12 | 36 | 11897 | 0.0079343 | 2.4009e-05 | 330.4722
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | CUTOUT | 35 | 2096 | 144443 | 0.096331 | 0.0013978 | 68.9136
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | CROSSARM | 57 | 12064 | 3693728 | 2.4634 | 0.0080456 | 306.1777
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | ABI | NONE | 1 | 885 | 245097 | 0.16234 | 0.00058617 | 276.9458
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERF | METERING | 9 | 9 | 807 | 0.00053451 | 5.9611e-06 | 89.6667
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | ARRESTER | 132 | 13100 | 1048672 | 0.68799 | 0.0085944 | 80.0513
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | POLE | 220 | 27148 | 11290437 | 7.4072 | 0.017811 | 415.8847
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | CABLE TERMINATOR | 8 | 10 | 1046 | 0.00069281 | 6.6234e-06 | 104.6
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CO | NONE | 7 | 19 | 1368 | 0.00090608 | 1.2584e-05 | 72
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | CUTOUT | 13 | 162 | 21146 | 0.013928 | 0.0001067 | 130.5309
AEP-OH | 2020 | 1499447 | PARTIAL POWER | WW | NONE | 4 | 38 | 17519 | 0.011684 | 2.5343e-05 | 461.0263
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | JUMPER/RISER | 2 | 76 | 13946 | 0.0091855 | 5.0057e-05 | 183.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | METERING | 1 | 1 | 100 | 6.5865e-05 | 6.5865e-07 | 100
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | SPLICE, OH | 8 | 15 | 2050 | 0.0013449 | 9.8409e-06 | 136.6667
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | F | NONE | 56 | 1217 | 81415 | 0.053413 | 0.00079842 | 66.8981
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | POLE | 135 | 16818 | 2790950 | 1.831 | 0.011034 | 165.9502
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | FUSE | 78 | 428 | 36885 | 0.024023 | 0.00027876 | 86.1799
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 2 | 1078 | 0.0007021 | 1.3026e-06 | 539
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1711 | 183077 | 0.11924 | 0.0011144 | 107
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TR | SPLICE, OH | 1 | 1 | 61 | 3.9729e-05 | 6.513e-07 | 61
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TR | ARRESTER | 1 | 10 | 5072 | 0.0033034 | 6.513e-06 | 507.2
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | ERF | NONE | 2 | 3657 | 259229 | 0.16884 | 0.0023818 | 70.8857
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 149 | 9.8138e-05 | 6.5865e-07 | 149
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AF | OTHER EQUIPMENT | 3 | 3341 | 779052 | 0.51312 | 0.0022005 | 233.1793
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 1 | 269 | 0.0001794 | 6.6691e-07 | 269
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 1 | 100 | 6.6234e-05 | 6.6234e-07 | 100
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | AO | BREAKER | 2 | 2348 | 164954 | 0.10743 | 0.0015293 | 70.253
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | TRANSFORMER, GROUNDING | 1 | 27 | 1026 | 0.00067577 | 1.7783e-05 | 38
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OU | CROSSARM | 1 | 674 | 217826 | 0.14527 | 0.0004495 | 323.184
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VA | TRANSFORMER, UG | 1 | 5 | 375 | 0.00025009 | 3.3346e-06 | 75
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | CROSSARM | 1 | 211 | 14457 | 0.0096416 | 0.00014072 | 68.5166
AEP-OH | 2020 | 1499447 | PARTIAL POWER | F | CONDUCTOR OVERHEAD | 1 | 8 | 1232 | 0.00082164 | 5.3353e-06 | 154
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | ABI | ARRESTER | 1 | 1210 | 224405 | 0.14863 | 0.00080143 | 185.4587
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | WU | BREAKER | 1 | 3148 | 199416 | 0.12988 | 0.0020503 | 63.3469
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 802 | 66337 | 9535206 | 6.2803 | 0.043693 | 143.7389
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | CUTOUT | 72 | 1290 | 168871 | 0.11123 | 0.00084965 | 130.9078
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | ARRESTER | 2 | 15 | 1076 | 0.0007087 | 9.8797e-06 | 71.7333
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AO | NONE | 13 | 12982 | 1190850 | 0.78435 | 0.0085505 | 91.7309
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 54 | 4103 | 1626826 | 1.0715 | 0.0027024 | 396.4967
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CO | CONN/CLAMP | 40 | 118 | 10903 | 0.0072215 | 7.8156e-05 | 92.3983
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CO | SPLICE, OH | 10 | 19 | 1929 | 0.0012705 | 1.2514e-05 | 101.5263
AEP-OH | 2022 | 1518267 | DISTRIBUTION SOURCE | ABI | NONE | 1 | 892 | 243516 | 0.16039 | 0.00058751 | 273
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 144 | 8205 | 999158 | 0.66635 | 0.005472 | 121.7743
AEP-OH | 2020 | 1499447 | PARTIAL POWER | A | NONE | 108 | 409 | 35596 | 0.023739 | 0.00027277 | 87.0318
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | CROSSARM | 101 | 37540 | 3766233 | 2.5117 | 0.025036 | 100.3259
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 4 | 937 | 0.00062061 | 2.6494e-06 | 234.25
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 6 | 55 | 4720 | 0.0031263 | 3.6429e-05 | 85.8182
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 18 | 787 | 88489 | 0.05861 | 0.00052126 | 112.4384
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 2 | 282 | 0.00018678 | 1.3247e-06 | 141
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 150 | 3043 | 0.0020043 | 9.8797e-05 | 20.2867
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 8 | 91 | 11773 | 0.0077977 | 6.0273e-05 | 129.3736
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 103 | 19434 | 2441629 | 1.6019 | 0.01275 | 125.637
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | A | ARRESTER | 13 | 1400 | 116508 | 0.077701 | 0.00093368 | 83.22
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | ARRESTER | 3 | 343 | 33937 | 0.022478 | 0.00022718 | 98.9417
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 9 | 3574 | 0.002354 | 5.9278e-06 | 397.1111
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 8 | 339 | 25672 | 0.016909 | 0.00022328 | 75.7286
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 5 | 354 | 111645 | 0.073246 | 0.00023224 | 315.3814
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 9 | 26 | 3659 | 0.0024402 | 1.734e-05 | 140.7308
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TR | NONE | 83 | 3526 | 368060 | 0.24147 | 0.0023133 | 104.3846
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | CONN/CLAMP | 2 | 18 | 954 | 0.00062835 | 1.1856e-05 | 53
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | CROSSARM | 1 | 64 | 3904 | 0.0025714 | 4.2153e-05 | 61
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | PEDESTAL | 4 | 19 | 1483 | 0.00097677 | 1.2514e-05 | 78.0526
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | SPLICE, UG | 7 | 12 | 2500 | 0.0016466 | 7.9037e-06 | 208.3333
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | CONN/CLAMP | 4 | 33 | 3655 | 0.0023979 | 2.165e-05 | 110.7576
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | NONE | 78 | 5969 | 328803 | 0.21571 | 0.003916 | 55.0851
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 6 | 44 | 2636 | 0.0017362 | 2.898e-05 | 59.9091
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | SPLICE, UG | 7 | 14 | 3555 | 0.0023323 | 9.1848e-06 | 253.9286
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | POLE | 251 | 20971 | 10138167 | 6.603 | 0.013658 | 483.4375
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | R | NONE | 6 | 1507 | 244091 | 0.16279 | 0.001005 | 161.9715
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 3 | 321 | 0.00021261 | 1.987e-06 | 107
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 22 | 734 | 187089 | 0.12185 | 0.00047805 | 254.8896
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | CUTOUT | 70 | 1512 | 177558 | 0.11564 | 0.00098476 | 117.4325
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UG | SPLICE, UG | 3 | 3 | 1183 | 0.00078896 | 2.0007e-06 | 394.3333
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ERO | METERING | 5 | 5 | 351 | 0.00023028 | 3.2803e-06 | 70.2
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | JUMPER/RISER | 4 | 368 | 50888 | 0.033385 | 0.00024143 | 138.2826
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 8 | 39 | 3024 | 0.0020029 | 2.5831e-05 | 77.5385
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 3 | 172 | 13843 | 0.0090818 | 0.00011284 | 80.4826
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 3 | 7 | 426 | 0.00027745 | 4.5591e-06 | 60.8571
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | PEDESTAL | 3 | 64 | 12106 | 0.0080183 | 4.239e-05 | 189.1562
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TIR | NONE | 13 | 53 | 11071 | 0.0072105 | 3.4519e-05 | 208.8868
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 4 | 256 | 0.00016673 | 2.6052e-06 | 64
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 2 | 2 | 1377 | 0.00089684 | 1.3026e-06 | 688.5
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 2 | 352 | 0.00023093 | 1.3121e-06 | 176
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 2 | 508 | 95780 | 0.062381 | 0.00033086 | 188.5433
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 298 | 9305 | 1609165 | 1.048 | 0.0060603 | 172.9355
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | NONE | 41 | 1725 | 247684 | 0.16132 | 0.0011235 | 143.5849
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | CROSSARM | 38 | 13486 | 4278103 | 2.7863 | 0.0087834 | 317.2255
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 10 | 2123 | 239117 | 0.15574 | 0.0013827 | 112.6317
AEP-OH | 2020 | 1499447 | PARTIAL POWER | FO | NONE | 2 | 7 | 600 | 0.00040015 | 4.6684e-06 | 85.7143
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FO | NONE | 1 | 6 | 540 | 0.00035766 | 3.974e-06 | 90
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | JUMPER/RISER | 3 | 6264 | 1401965 | 0.93499 | 0.0041775 | 223.8131
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CO | NONE | 15 | 66 | 18624 | 0.012421 | 4.4016e-05 | 282.1818
AEP-OH | 2024 | 1535393 | PARTIAL POWER | UG | CONDUCTOR UG | 68 | 141 | 22659 | 0.014758 | 9.1833e-05 | 160.7021
AEP-OH | 2023 | 1524255 | PARTIAL POWER | U | CONDUCTOR UG | 13 | 28 | 4606 | 0.0030218 | 1.837e-05 | 164.5
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | FUSE | 423 | 6177 | 602098 | 0.39215 | 0.0040231 | 97.4742
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TOR | NONE | 122 | 244 | 46665 | 0.030393 | 0.00015892 | 191.25
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WU | NONE | 11 | 63 | 10667 | 0.0069982 | 4.1332e-05 | 169.3175
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | JUMPER/RISER | 3 | 2660 | 495041 | 0.32478 | 0.0017451 | 186.1056
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 2 | 5 | 453 | 0.00029719 | 3.2803e-06 | 90.6
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 176 | 13751 | 0.0091707 | 0.00011738 | 78.1307
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | CROSSARM | 136 | 4916 | 304340 | 0.19822 | 0.0032018 | 61.9081
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 6 | 552 | 0.00036214 | 3.9363e-06 | 92
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | SCO | TRANSFORMER, POWER - LTC | 3 | 1027 | 7688 | 0.0050921 | 0.00068022 | 7.4859
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | CIRCUIT SWITCHER | 1 | 11 | 1232 | 0.000816 | 7.2858e-06 | 112
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VIN | FUSE | 8 | 31 | 5926 | 0.0038596 | 2.019e-05 | 191.1613
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | FUSE | 34 | 421 | 100645 | 0.06555 | 0.0002742 | 239.0618
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | U | NONE | 10 | 5331 | 826183 | 0.53809 | 0.0034721 | 154.9771
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WFS | PEDESTAL | 1 | 14 | 1246 | 0.00081745 | 9.1848e-06 | 89
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ABI | CUTOUT | 9 | 2234 | 212292 | 0.13827 | 0.001455 | 95.0278
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | POLE | 5 | 595 | 67113 | 0.043711 | 0.00038752 | 112.795
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | BE | CABLE TERMINATOR | 1 | 5 | 3230 | 0.0021394 | 3.3117e-06 | 646
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | V | NONE | 26 | 297 | 7325 | 0.0047708 | 0.00019344 | 24.6633
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 2140 | 427386 | 0.27836 | 0.0013938 | 199.7131
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | SWITCH, UG | 1 | 1355 | 860719 | 0.56059 | 0.00088251 | 635.217
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FW | NONE | 18 | 631 | 32695 | 0.021294 | 0.00041097 | 51.8146
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WFS | REGULATOR | 1 | 106 | 2968 | 0.0019331 | 6.9038e-05 | 28
AEP-OH | 2023 | 1524255 | PARTIAL POWER | FW | PEDESTAL | 1 | 3 | 807 | 0.00052944 | 1.9682e-06 | 269
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 601 | 328350 | 0.21748 | 0.00039807 | 546.3394
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 2 | 9 | 1260 | 0.00084031 | 6.0022e-06 | 140
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 1 | 514 | 0.00034279 | 6.6691e-07 | 514
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VIN | POLE | 2 | 16 | 3076 | 0.0020514 | 1.0671e-05 | 192.25
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | CAPACITOR | 2 | 1375 | 79482 | 0.052644 | 0.00091072 | 57.8051
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 9 | 9850 | 2861631 | 1.9085 | 0.0065691 | 290.5209
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | V | POLE | 1 | 2 | 478 | 0.00031132 | 1.3026e-06 | 239
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | NETWORK TRANSFORMER | 1 | 2 | 169 | 0.00011007 | 1.3026e-06 | 84.5
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | ERF | TRANSFORMER, GROUNDING | 3 | 2501 | 323376 | 0.21061 | 0.0016289 | 129.2987
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WU | CUTOUT | 1 | 3 | 576 | 0.00037515 | 1.9539e-06 | 192
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 3 | 20 | 1755 | 0.0011514 | 1.3121e-05 | 87.75
AEP-OH | 2025 | 1535393 | PARTIAL POWER | WU | NONE | 2 | 2 | 100 | 6.513e-05 | 1.3026e-06 | 50
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | POLE | 5 | 318 | 39778 | 0.025907 | 0.00020711 | 125.0881
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | BE | NONE | 1 | 2 | 108 | 7.034e-05 | 1.3026e-06 | 54
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 45 | 11295 | 0.0073564 | 2.9308e-05 | 251
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 31 | 837 | 0.00054514 | 2.019e-05 | 27
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TOR | FUSE | 1 | 1 | 113 | 7.4135e-05 | 6.5606e-07 | 113
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 1 | 646 | 0.00042074 | 6.513e-07 | 646
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 66 | 6996 | 0.0045565 | 4.2986e-05 | 106
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | CONDUCTOR UG | 1 | 1 | 129 | 8.4965e-05 | 6.5865e-07 | 129
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 1 | 36 | 2.3711e-05 | 6.5865e-07 | 36
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VIN | POLE HARDWARE | 1 | 12 | 350 | 0.00022962 | 7.8727e-06 | 29.1667
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | SPLICE, UG | 1 | 3 | 394 | 0.00025661 | 1.9539e-06 | 131.3333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UB | NONE | 2 | 9 | 889 | 0.00059289 | 6.0022e-06 | 98.7778
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TOR | TRANSFORMER, OH | 1 | 1 | 312 | 0.00020469 | 6.5606e-07 | 312
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 1 | 75 | 4.9676e-05 | 6.6234e-07 | 75
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 4 | 436 | 0.00029077 | 2.6677e-06 | 109
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 25 | 2575 | 0.0017055 | 1.6559e-05 | 103
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | AF | CUTOUT | 3 | 3249 | 287711 | 0.19188 | 0.0021668 | 88.5537
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 38 | 13298 | 0.0088686 | 2.5343e-05 | 349.9474
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | AO | INSULATOR | 3 | 2861 | 710643 | 0.47069 | 0.001895 | 248.3897
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | R | JUMPER/RISER | 1 | 1432 | 351056 | 0.22864 | 0.00093266 | 245.1508
AEP-OH | 2021 | 1509795 | DISTRIBUTION SOURCE | VA | CROSSARM | 3 | 2027 | 227024 | 0.15037 | 0.0013426 | 112
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | UB | CONN/CLAMP | 1 | 1 | 104 | 6.8884e-05 | 6.6234e-07 | 104
AEP-OH | 2022 | 1518267 | PARTIAL POWER | ERO | CONDUCTOR UG | 1 | 4 | 536 | 0.00035303 | 2.6346e-06 | 134
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | SECTIONALIZER | 1 | 1 | 138 | 9.0893e-05 | 6.5865e-07 | 138
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 713 | 65596 | 0.043205 | 0.00046961 | 92
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 3 | 6 | 1160 | 0.00075551 | 3.9078e-06 | 193.3333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 1 | 203 | 0.00013538 | 6.6691e-07 | 203
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | CF | ARRESTER | 1 | 2180 | 303536 | 0.19992 | 0.0014358 | 139.2367
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | POLE | 237 | 18740 | 6045243 | 4.004 | 0.012412 | 322.585
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WFS | POLE | 3 | 117 | 43007 | 0.028326 | 7.7062e-05 | 367.5812
AEP-OH | 2022 | 1518267 | PARTIAL POWER | ABI | FUSE | 3 | 4 | 441 | 0.00029046 | 2.6346e-06 | 110.25
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 29 | 739 | 162853 | 0.10786 | 0.00048947 | 220.3694
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | NONE | 2117 | 110119 | 17671849 | 11.7856 | 0.07344 | 160.4796
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 92 | 6.0595e-05 | 1.3173e-06 | 46
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 13 | 6433 | 368351 | 0.24397 | 0.0042608 | 57.2596
AEP-OH | 2021 | 1509795 | PARTIAL POWER | UG | CONDUCTOR UG | 50 | 88 | 15271 | 0.010115 | 5.8286e-05 | 173.5341
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | FW | NONE | 2 | 848 | 5093 | 0.0033545 | 0.00055853 | 6.0059
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | AF | POLE | 3 | 788 | 16460 | 0.01072 | 0.00051322 | 20.8883
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | METERING | 1 | 1 | 51 | 3.3216e-05 | 6.513e-07 | 51
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 450 | 0.00029523 | 6.5606e-07 | 450
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 9 | 657 | 0.00043816 | 6.0022e-06 | 73
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AF | TRANSFORMER, POWER - NON LTC | 1 | 41 | 13419 | 0.0088384 | 2.7004e-05 | 327.2927
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 1 | 155 | 0.00010266 | 6.6234e-07 | 155
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 63 | 5670 | 0.0037814 | 4.2015e-05 | 90
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 17 | 16998 | 0.011071 | 1.1072e-05 | 999.8824
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1345 | 181501 | 0.11821 | 0.000876 | 134.945
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 7 | 43 | 2924 | 0.0019044 | 2.8006e-05 | 68
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 136 | 8.8577e-05 | 1.3026e-06 | 68
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 49 | 99225 | 0.065097 | 3.2147e-05 | 2025
AEP-OH | 2023 | 1524255 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 90 | 5.9045e-05 | 6.5606e-07 | 90
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 1111 | 76337 | 0.049718 | 0.00072359 | 68.7102
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 1 | 94 | 6.1222e-05 | 6.513e-07 | 94
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 37 | 6179 | 0.0040244 | 2.4098e-05 | 167
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FO | CONN/CLAMP | 2 | 4 | 2555 | 0.0016923 | 2.6494e-06 | 638.75
AEP-OH | 2022 | 1518267 | PARTIAL POWER | EQF | ARRESTER | 5 | 50 | 6313 | 0.004158 | 3.2932e-05 | 126.26
AEP-OH | 2023 | 1524255 | PARTIAL POWER | U | CONN/CLAMP | 1 | 2 | 252 | 0.00016533 | 1.3121e-06 | 126
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OU | POLE | 4 | 443 | 51753 | 0.034087 | 0.00029178 | 116.8239
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ABI | CAPACITOR | 1 | 1970 | 120170 | 0.080143 | 0.0013138 | 61
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 2 | 2438 | 0.0016259 | 1.3338e-06 | 1219
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OL | POLE | 1 | 6 | 378 | 0.00024799 | 3.9363e-06 | 63
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 102 | 11824 | 0.0078856 | 6.8025e-05 | 115.9216
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 1 | 14 | 19390 | 0.012931 | 9.3368e-06 | 1385
AEP-OH | 2021 | 1509795 | PARTIAL POWER | CO | SPLICE, OH | 1 | 1 | 149 | 9.8689e-05 | 6.6234e-07 | 149
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 11 | 893 | 0.00058586 | 7.2166e-06 | 81.1818
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WL | ARRESTER | 2 | 2 | 201 | 0.00013239 | 1.3173e-06 | 100.5
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AF | BREAKER | 4 | 2166 | 221561 | 0.14536 | 0.001421 | 102.2904
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 2542 | 91512 | 0.060274 | 0.0016743 | 36
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | ERF | TRANSFORMER, POWER - NON LTC | 2 | 2634 | 322415 | 0.21502 | 0.0017566 | 122.4051
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WU | TRANSFORMER, UG | 1 | 8 | 752 | 0.00048978 | 5.2104e-06 | 94
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WT | POLE | 2 | 794 | 459488 | 0.30434 | 0.0005259 | 578.7003
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 7 | 2232 | 317230 | 0.20812 | 0.0014643 | 142.1281
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 95 | 11115 | 0.0073208 | 6.2571e-05 | 117
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | CUTOUT | 25 | 44 | 6615 | 0.0043083 | 2.8657e-05 | 150.3409
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 2 | 162 | 0.00010551 | 1.3026e-06 | 81
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | POLE HARDWARE | 7 | 1657 | 477356 | 0.3109 | 0.0010792 | 288.0845
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | NONE | 228 | 14283 | 3130315 | 2.0388 | 0.0093025 | 219.1637
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | EQF | INSULATOR | 4 | 2371 | 837786 | 0.54565 | 0.0015442 | 353.3471
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 51 | 26268 | 0.017108 | 3.3216e-05 | 515.0588
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 1 | 232 | 0.00015221 | 6.5606e-07 | 232
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 14 | 2688 | 0.0017927 | 9.3368e-06 | 192
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 61 | 4.0682e-05 | 6.6691e-07 | 61
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 92 | 4886 | 0.0031822 | 5.992e-05 | 53.1087
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 6 | 45 | 5672 | 0.0036942 | 2.9308e-05 | 126.0444
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 2 | 142 | 9.2484e-05 | 1.3026e-06 | 71
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 2 | 3 | 1444 | 0.00096302 | 2.0007e-06 | 481.3333
AEP-OH | 2025 | 1535393 | PARTIAL POWER | TOR | POLE | 1 | 1 | 27 | 1.7585e-05 | 6.513e-07 | 27
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 4 | 30 | 2838 | 0.0018927 | 2.0007e-05 | 94.6
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TR | NONE | 1 | 1 | 58 | 3.7775e-05 | 6.513e-07 | 58
AEP-OH | 2023 | 1524255 | PARTIAL POWER | SCO | CONDUCTOR UG | 1 | 8 | 560 | 0.00036739 | 5.2485e-06 | 70
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 305 | 31110 | 0.020262 | 0.00019865 | 102
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 42 | 17752 | 0.011692 | 2.7663e-05 | 422.6667
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | WL | INSULATOR | 1 | 1558 | 267976 | 0.17581 | 0.0010221 | 172
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 1 | 151 | 9.9065e-05 | 6.5606e-07 | 151
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 1 | 126 | 8.2663e-05 | 6.5606e-07 | 126
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VA | CUTOUT | 1 | 1 | 79 | 5.2033e-05 | 6.5865e-07 | 79
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | FUSE | 1 | 1 | 143 | 9.5368e-05 | 6.6691e-07 | 143
AEP-OH | 2022 | 1518267 | PARTIAL POWER | OL | FUSE | 2 | 26 | 1800 | 0.0011856 | 1.7125e-05 | 69.2308
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 927 | 75602 | 0.05042 | 0.00061823 | 81.5556
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | SPLICE, UG | 1 | 1 | 463 | 0.00030878 | 6.6691e-07 | 463
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 767 | 24920 | 0.016506 | 0.00050802 | 32.4902
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FW | NONE | 1 | 1 | 71 | 4.7026e-05 | 6.6234e-07 | 71
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 28 | 1.8546e-05 | 6.6234e-07 | 28
AEP-OH | 2020 | 1499447 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 22 | 1156 | 0.00077095 | 1.4672e-05 | 52.5455
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 882 | 123480 | 0.08133 | 0.00058093 | 140
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 1 | 381 | 0.00024996 | 6.5606e-07 | 381
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | NONE | 50 | 26219 | 2986293 | 1.9669 | 0.017269 | 113.8981
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 677 | 14125 | 1392144 | 0.92207 | 0.0093556 | 98.5589
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TOR | POLE | 187 | 18720 | 6857647 | 4.5168 | 0.01233 | 366.3273
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | FUSE | 129 | 1165 | 138482 | 0.091211 | 0.00076732 | 118.8687
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | NONE | 68 | 2378 | 1553229 | 1.023 | 0.0015663 | 653.1661
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | POLE | 7 | 4100 | 239190 | 0.15754 | 0.0027004 | 58.339
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CF | INSULATOR | 3 | 663 | 129758 | 0.085465 | 0.00043668 | 195.7134
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 21 | 289 | 60824 | 0.040286 | 0.00019142 | 210.4637
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | EQF | CROSSARM | 90 | 39132 | 4761174 | 3.1535 | 0.025919 | 121.6696
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 7 | 768 | 0.00050584 | 4.6105e-06 | 109.7143
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ABI | NONE | 767 | 9991 | 760365 | 0.5071 | 0.0066631 | 76.105
AEP-OH | 2020 | 1499447 | PARTIAL POWER | VA | CONDUCTOR UG | 3 | 31 | 916 | 0.00061089 | 2.0674e-05 | 29.5484
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AB | NONE | 31 | 34716 | 3837099 | 2.559 | 0.023153 | 110.5283
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | METERING | 17 | 134 | 14207 | 0.0094099 | 8.8754e-05 | 106.0224
AEP-OH | 2020 | 1499447 | PARTIAL POWER | CO | CONDUCTOR UG | 20 | 30 | 5129 | 0.0034206 | 2.0007e-05 | 170.9667
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 913 | 228250 | 0.15118 | 0.00060472 | 250
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ERO | METERING | 4 | 4 | 262 | 0.00017353 | 2.6494e-06 | 65.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FO | POLE | 1 | 29 | 3799 | 0.0025022 | 1.9101e-05 | 131
AEP-OH | 2022 | 1518267 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 2 | 20 | 1723 | 0.0011348 | 1.3173e-05 | 86.15
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | ABI | GUY/ANCHOR | 1 | 1 | 93 | 6.1598e-05 | 6.6234e-07 | 93
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 11 | 605 | 0.00040072 | 7.2858e-06 | 55
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OL | POLE | 2 | 3 | 394 | 0.00026096 | 1.987e-06 | 131.3333
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 5 | 6295 | 1593286 | 1.0494 | 0.0041462 | 253.1034
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | CROSSARM | 71 | 25697 | 3626127 | 2.379 | 0.016859 | 141.1109
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | INSULATOR | 11 | 134 | 4637 | 0.0030421 | 8.7912e-05 | 34.6045
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | CONN/CLAMP | 9 | 45 | 1665 | 0.0010966 | 2.9639e-05 | 37
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 6 | 1027 | 0.00068492 | 4.0015e-06 | 171.1667
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | CROSSARM | 103 | 28789 | 4079833 | 2.6572 | 0.01875 | 141.715
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FO | FUSE | 2 | 24 | 2497 | 0.0016382 | 1.5745e-05 | 104.0417
AEP-OH | 2020 | 1499447 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 3 | 180 | 0.00012004 | 2.0007e-06 | 60
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | UG | NONE | 54 | 817 | 98856 | 0.064385 | 0.00053211 | 120.9988
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WW | CONN/CLAMP | 5 | 68 | 96753 | 0.063476 | 4.4612e-05 | 1422.8382
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 1 | 571 | 0.0003782 | 6.6234e-07 | 571
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | OL | FUSE | 7 | 145 | 13966 | 0.0092503 | 9.604e-05 | 96.3172
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 6 | 1510 | 0.00099455 | 3.9519e-06 | 251.6667
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 27 | 112 | 36541 | 0.023973 | 7.3479e-05 | 326.2589
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | FUSE | 16 | 216 | 36478 | 0.023932 | 0.00014171 | 168.8796
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 47 | 5209 | 0.0034174 | 3.0835e-05 | 110.8298
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 61 | 5700 | 1786054 | 1.1633 | 0.0037124 | 313.3428
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 120 | 21048 | 0.013863 | 7.9037e-05 | 175.4
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 10 | 85 | 15987 | 0.010662 | 5.6688e-05 | 188.0824
AEP-OH | 2024 | 1535393 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 5 | 6 | 499 | 0.000325 | 3.9078e-06 | 83.1667
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 4 | 8 | 529 | 0.00034454 | 5.2104e-06 | 66.125
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | JUMPER/RISER | 3 | 3291 | 246902 | 0.16198 | 0.0021591 | 75.0234
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 31 | 2.0533e-05 | 6.6234e-07 | 31
AEP-OH | 2022 | 1518267 | PARTIAL POWER | WI | CONDUCTOR UG | 1 | 1 | 176 | 0.00011592 | 6.5865e-07 | 176
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ERO | NONE | 12 | 176 | 19600 | 0.012765 | 0.00011463 | 111.3636
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | NETWORK PROTECTOR | 1 | 3 | 150 | 9.7695e-05 | 1.9539e-06 | 50
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 20 | 3010 | 339397 | 0.22105 | 0.0019604 | 112.7565
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | UG | SPLICE, UG | 4 | 31 | 6512 | 0.0042413 | 2.019e-05 | 210.0645
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WW | POLE | 19 | 3854 | 1945454 | 1.2671 | 0.0025101 | 504.7883
AEP-OH | 2023 | 1524255 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 4 | 20 | 2044 | 0.001341 | 1.3121e-05 | 102.2
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | U | GUY/ANCHOR | 3 | 51 | 5764 | 0.0037815 | 3.3459e-05 | 113.0196
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 120 | 14352 | 0.0095715 | 8.003e-05 | 119.6
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | O | POLE | 2 | 1570 | 307800 | 0.20387 | 0.0010399 | 196.051
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 34 | 3430 | 0.002234 | 2.2144e-05 | 100.8824
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | CROSSARM | 4 | 3334 | 364092 | 0.24115 | 0.0022082 | 109.2058
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WH | NONE | 10 | 615 | 157333 | 0.10247 | 0.00040055 | 255.826
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | SCO | NONE | 6 | 4645 | 66471 | 0.043292 | 0.0030253 | 14.3102
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 8 | 1274 | 129150 | 0.084115 | 0.00082975 | 101.3736
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 17 | 2210 | 0.0014638 | 1.126e-05 | 130
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 2 | 421 | 0.0002762 | 1.3121e-06 | 210.5
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | CAPACITOR | 6 | 5367 | 189174 | 0.12616 | 0.0035793 | 35.2476
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | FW | CUTOUT | 2 | 740 | 20061 | 0.013287 | 0.00049013 | 27.1095
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | CROSSARM | 8 | 7323 | 805885 | 0.52487 | 0.0047695 | 110.0485
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | VA | CROSSARM | 13 | 6559 | 507533 | 0.33056 | 0.0042719 | 77.3796
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | TRANSFORMER, UG | 2 | 208 | 23920 | 0.015579 | 0.00013547 | 115
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 20 | 3540 | 0.0023224 | 1.3121e-05 | 177
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 247 | 51376 | 0.033461 | 0.00016087 | 208
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 6 | 39 | 2138 | 0.0013925 | 2.5401e-05 | 54.8205
AEP-OH | 2025 | 1535393 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 3 | 12 | 4679 | 0.0030474 | 7.8156e-06 | 389.9167
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 2 | 314 | 0.00020451 | 1.3026e-06 | 157
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | INSULATOR | 2 | 1006 | 100153 | 0.06523 | 0.00065521 | 99.5557
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | SCO | OTHER EQUIPMENT | 2 | 1678 | 115782 | 0.077216 | 0.0011191 | 69
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 3 | 780 | 0.00050801 | 1.9539e-06 | 260
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ERO | NONE | 2 | 774 | 13147 | 0.0085626 | 0.00050411 | 16.9858
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 2 | 316 | 11540 | 0.007516 | 0.00020581 | 36.519
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | OU | OTHER EQUIPMENT | 1 | 104 | 39936 | 0.02601 | 6.7735e-05 | 384
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 1 | 244 | 0.00015892 | 6.513e-07 | 244
AEP-OH | 2024 | 1535393 | PARTIAL POWER | CE | NONE | 1 | 2 | 84 | 5.4709e-05 | 1.3026e-06 | 42
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | CUTOUT | 1 | 3 | 126 | 8.2989e-05 | 1.9759e-06 | 42
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 610 | 0.0004002 | 6.5606e-07 | 610
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | CE | METERING | 1 | 2 | 143 | 9.3136e-05 | 1.3026e-06 | 71.5
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | FO | NONE | 2 | 200 | 63200 | 0.04186 | 0.00013247 | 316
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | SCO | SPLICE, UG | 2 | 5 | 63 | 4.1495e-05 | 3.2932e-06 | 12.6
AEP-OH | 2022 | 1518267 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 65 | 4.2812e-05 | 6.5865e-07 | 65
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AF | CUTOUT | 1 | 602 | 101738 | 0.067009 | 0.0003965 | 169
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 1 | 731 | 0.00048751 | 6.6691e-07 | 731
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 40 | 4600 | 0.0030468 | 2.6494e-05 | 115
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 109 | 31937 | 0.021035 | 7.1792e-05 | 293
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 5 | 275 | 0.0001834 | 3.3346e-06 | 55
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 22 | 7892 | 0.0052633 | 1.4672e-05 | 358.7273
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AF | FUSE | 1 | 93 | 5580 | 0.0036608 | 6.1013e-05 | 60
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | POLE | 1 | 876 | 299904 | 0.19533 | 0.00057054 | 342.3562
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | NONE | 2928 | 156438 | 14531546 | 9.5711 | 0.10304 | 92.8901
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 29 | 1536 | 213120 | 0.14037 | 0.0010117 | 138.75
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | V | NONE | 17 | 62 | 11612 | 0.0076482 | 4.0836e-05 | 187.2903
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 16 | 396 | 99362 | 0.065444 | 0.00026082 | 250.9141
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | CROSSARM | 18 | 7962 | 697766 | 0.45958 | 0.0052441 | 87.637
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 1 | 64 | 4.2153e-05 | 6.5865e-07 | 64
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 7 | 52 | 18563 | 0.012226 | 3.425e-05 | 356.9808
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | CUTOUT | 46 | 1663 | 137529 | 0.091091 | 0.0011015 | 82.6993
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | U | CUTOUT | 13 | 279 | 42169 | 0.02793 | 0.00018479 | 151.1434
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 11 | 307 | 78662 | 0.052101 | 0.00020334 | 256.228
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VIN | NONE | 129 | 932 | 111718 | 0.074506 | 0.00062156 | 119.8691
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | WU | NONE | 494 | 43225 | 5401031 | 3.602 | 0.028827 | 124.9516
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 7 | 3423 | 577557 | 0.38254 | 0.0022672 | 168.7283
AEP-OH | 2023 | 1524255 | PARTIAL POWER | EQF | CONN/CLAMP | 675 | 2045 | 248578 | 0.16308 | 0.0013416 | 121.554
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | CROSSARM | 243 | 9928 | 348947 | 0.22893 | 0.0065133 | 35.1478
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 624 | 27141 | 5177949 | 3.397 | 0.017806 | 190.7796
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 14 | 231 | 15264 | 0.01011 | 0.000153 | 66.0779
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CE | METERING | 3 | 22 | 2127 | 0.0014088 | 1.4572e-05 | 96.6818
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 1740 | 700544 | 0.46141 | 0.001146 | 402.6115
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 1 | 13 | 8.5624e-06 | 6.5865e-07 | 13
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | U | ARRESTER | 5 | 20 | 1831 | 0.001206 | 1.3173e-05 | 91.55
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 2080 | 147680 | 0.097269 | 0.00137 | 71
AEP-OH | 2022 | 1518267 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 101 | 6.6523e-05 | 6.5865e-07 | 101
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | SPLICE, UG | 2 | 3 | 1200 | 0.00078727 | 1.9682e-06 | 400
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 33 | 244 | 59808 | 0.039238 | 0.00016008 | 245.1148
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 33 | 1406 | 161541 | 0.10521 | 0.00091573 | 114.894
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | U | CUTOUT | 23 | 310 | 44967 | 0.029287 | 0.0002019 | 145.0548
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 19 | 52 | 7112 | 0.004632 | 3.3868e-05 | 136.7692
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 4 | 455 | 64797 | 0.043214 | 0.00030345 | 142.411
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | CUTOUT | 20 | 87 | 64423 | 0.041959 | 5.6663e-05 | 740.4943
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | POLE | 1733 | 11818 | 1546315 | 1.0071 | 0.0076971 | 130.8441
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | NONE | 954 | 47550 | 8775136 | 5.7152 | 0.030969 | 184.5454
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 40 | 989 | 108874 | 0.07091 | 0.00064413 | 110.0849
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | CROSSARM | 174 | 3310 | 298326 | 0.1943 | 0.0021558 | 90.1287
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 69 | 179 | 32958 | 0.021466 | 0.00011658 | 184.1229
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WL | NONE | 7 | 13 | 952 | 0.00062004 | 8.4669e-06 | 73.2308
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | AF | INSULATOR | 1 | 6 | 1170 | 0.00076202 | 3.9078e-06 | 195
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 46 | 4942 | 432836 | 0.28191 | 0.0032187 | 87.5832
AEP-OH | 2024 | 1535393 | PARTIAL POWER | VA | NONE | 7 | 46 | 4377 | 0.0028507 | 2.996e-05 | 95.1522
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | A | ARRESTER | 13 | 5217 | 451749 | 0.29422 | 0.0033978 | 86.5917
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CO | ARRESTER | 1 | 2 | 188 | 0.00012452 | 1.3247e-06 | 94
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | TOR | SPLICE, OH | 13 | 177 | 106328 | 0.069251 | 0.00011528 | 600.7232
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | AO | ARRESTER | 3 | 2082 | 282143 | 0.18688 | 0.001379 | 135.5154
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | METERING | 2 | 12 | 942 | 0.00062823 | 8.003e-06 | 78.5
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | REGULATOR | 6 | 3518 | 350166 | 0.22806 | 0.0022913 | 99.5355
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 12 | 3396 | 0.0022493 | 7.9481e-06 | 283
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ABI | POLE | 2 | 1299 | 109362 | 0.072935 | 0.00086632 | 84.1894
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 7 | 105 | 6.9546e-05 | 4.6364e-06 | 15
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | CROSSARM | 2 | 66 | 5496 | 0.0035795 | 4.2986e-05 | 83.2727
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 47 | 8022 | 0.0052247 | 3.0611e-05 | 170.6809
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 92 | 2576 | 0.0016777 | 5.992e-05 | 28
AEP-OH | 2025 | 1535393 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 68 | 7574 | 0.0049329 | 4.4288e-05 | 111.3824
AEP-OH | 2025 | 1535393 | PARTIAL POWER | VA | NONE | 1 | 2 | 52 | 3.3868e-05 | 1.3026e-06 | 26
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 5 | 1420 | 0.00092484 | 3.2565e-06 | 284
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | CE | FUSE | 1 | 5 | 535 | 0.00034844 | 3.2565e-06 | 107
AEP-OH | 2020 | 1499447 | PARTIAL POWER | UG | NONE | 3 | 3 | 798 | 0.0005322 | 2.0007e-06 | 266
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 29 | 5220 | 0.0033998 | 1.8888e-05 | 180
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 1 | 84 | 5.4709e-05 | 6.513e-07 | 84
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | OU | CUTOUT | 1 | 28 | 5264 | 0.0034671 | 1.8442e-05 | 188
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | F | REGULATOR | 1 | 1 | 93 | 6.0571e-05 | 6.513e-07 | 93
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | SECTIONALIZER | 1 | 1 | 103 | 6.7574e-05 | 6.5606e-07 | 103
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 126 | 40194 | 0.02637 | 8.2663e-05 | 319
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | METERING | 2 | 12 | 1964 | 0.0012936 | 7.9037e-06 | 163.6667
AEP-OH | 2020 | 1499447 | PARTIAL POWER | UB | NONE | 1 | 1 | 204 | 0.00013605 | 6.6691e-07 | 204
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 2 | 2186 | 0.0014479 | 1.3247e-06 | 1093
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | CUTOUT | 1 | 2 | 146 | 9.6162e-05 | 1.3173e-06 | 73
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 1 | 3 | 843 | 0.00055524 | 1.9759e-06 | 281
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 3 | 420 | 0.00027554 | 1.9682e-06 | 140
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CF | POLE | 2 | 304 | 75765 | 0.050182 | 0.00020135 | 249.227
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WFS | NONE | 1 | 35 | 5040 | 0.0032825 | 2.2795e-05 | 144
AEP-OH | 2024 | 1535393 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 75 | 4.8847e-05 | 6.513e-07 | 75
AEP-OH | 2021 | 1509795 | PARTIAL POWER | FW | CONN/CLAMP | 1 | 12 | 228 | 0.00015101 | 7.9481e-06 | 19
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | R | RELAY | 5 | 4888 | 419209 | 0.27766 | 0.0032375 | 85.7629
AEP-OH | 2021 | 1509795 | PARTIAL POWER | A | JUMPER/RISER | 1 | 2 | 1052 | 0.00069678 | 1.3247e-06 | 526
AEP-OH | 2023 | 1524255 | PARTIAL POWER | AF | CONN/CLAMP | 1 | 1 | 79 | 5.1829e-05 | 6.5606e-07 | 79
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 1 | 1 | 354 | 0.00023316 | 6.5865e-07 | 354
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 1 | 47 | 3.0956e-05 | 6.5865e-07 | 47
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | FW | FUSE | 1 | 1 | 52 | 3.425e-05 | 6.5865e-07 | 52
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | NONE | 2222 | 32402 | 3116125 | 2.0295 | 0.021103 | 96.1708
AEP-OH | 2022 | 1518267 | PARTIAL POWER | ERF | CONN/CLAMP | 5 | 16 | 903 | 0.00059476 | 1.0538e-05 | 56.4375
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 4 | 137 | 40375 | 0.026593 | 9.0234e-05 | 294.708
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 1 | 1 | 225 | 0.00015006 | 6.6691e-07 | 225
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ERF | METERING | 3 | 3 | 164 | 0.00010937 | 2.0007e-06 | 54.6667
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VIN | CUTOUT | 6 | 1583 | 175730 | 0.11529 | 0.0010385 | 111.0107
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 3730 | 289258 | 0.18977 | 0.0024471 | 77.5491
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 82 | 5.3797e-05 | 6.5606e-07 | 82
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | ARRESTER | 6 | 9019 | 1181222 | 0.77495 | 0.005917 | 130.9704
AEP-OH | 2024 | 1535393 | PARTIAL POWER | TOR | SPLICE, OH | 10 | 22 | 3401 | 0.0022151 | 1.4329e-05 | 154.5909
AEP-OH | 2023 | 1524255 | PARTIAL POWER | U | FUSE | 9 | 32 | 3261 | 0.0021394 | 2.0994e-05 | 101.9062
AEP-OH | 2023 | 1524255 | PARTIAL POWER | AF | CONDUCTOR OVERHEAD | 1 | 1 | 1872 | 0.0012281 | 6.5606e-07 | 1872
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | CUTOUT | 9 | 45 | 46764 | 0.03068 | 2.9523e-05 | 1039.2
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 4605 | 2055304 | 1.3484 | 0.0030211 | 446.3201
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TOR | ARRESTER | 8 | 134 | 29865 | 0.019451 | 8.7274e-05 | 222.8731
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 6 | 16 | 6227 | 0.0040556 | 1.0421e-05 | 389.1875
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 7 | 209 | 32587 | 0.021224 | 0.00013612 | 155.9187
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | CONDUCTOR UG | 274 | 439 | 77041 | 0.050177 | 0.00028592 | 175.492
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 3 | 3 | 738 | 0.00048066 | 1.9539e-06 | 246
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | FW | METERING | 1 | 1 | 41 | 2.6898e-05 | 6.5606e-07 | 41
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 2927 | 571087 | 0.37195 | 0.0019064 | 195.11
AEP-OH | 2025 | 1535393 | PARTIAL POWER | TOR | NONE | 25 | 74 | 17875 | 0.011642 | 4.8196e-05 | 241.5541
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 245 | 1960 | 0.0012982 | 0.00016227 | 8
AEP-OH | 2025 | 1535393 | PARTIAL POWER | ERF | CONN/CLAMP | 3 | 29 | 2651 | 0.0017266 | 1.8888e-05 | 91.4138
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 3 | 239 | 62015 | 0.04039 | 0.00015566 | 259.477
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 1472 | 217417 | 0.1416 | 0.00095871 | 147.7018
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SCO | TRANSFORMER, STATION SERVICE | 1 | 1 | 65 | 4.3052e-05 | 6.6234e-07 | 65
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WW | NONE | 2 | 5 | 639 | 0.00041618 | 3.2565e-06 | 127.8
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ERF | NONE | 2 | 2 | 156 | 0.00010404 | 1.3338e-06 | 78
AEP-OH | 2020 | 1499447 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 2 | 2 | 203 | 0.00013538 | 1.3338e-06 | 101.5
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 33 | 16498 | 0.011003 | 2.2008e-05 | 499.9394
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TOR | POLE | 2 | 2 | 994 | 0.00065212 | 1.3121e-06 | 497
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 313 | 114177 | 0.074363 | 0.00020386 | 364.7827
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | ABI | FUSE | 3 | 6 | 679 | 0.00044223 | 3.9078e-06 | 113.1667
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 1232 | 141202 | 0.091965 | 0.0008024 | 114.612
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 57 | 57342 | 0.037347 | 3.7124e-05 | 1006
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 2906 | 241198 | 0.15709 | 0.0018927 | 83
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | WFS | POLE | 4 | 60 | 45470 | 0.029615 | 3.9078e-05 | 757.8333
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | POLE | 1 | 18 | 9738 | 0.0064139 | 1.1856e-05 | 541
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 2 | 9 | 1542 | 0.0010116 | 5.9045e-06 | 171.3333
AEP-OH | 2020 | 1499447 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 135 | 9.0033e-05 | 6.6691e-07 | 135
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 2 | 22 | 275 | 0.0001834 | 1.4672e-05 | 12.5
AEP-OH | 2024 | 1535393 | PARTIAL POWER | FO | SPLICE, OH | 1 | 1 | 1001 | 0.00065195 | 6.513e-07 | 1001
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | A | SPLICE, OH | 1 | 1 | 117 | 7.7062e-05 | 6.5865e-07 | 117
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | FUSE | 2 | 3 | 339 | 0.00022328 | 1.9759e-06 | 113
AEP-OH | 2023 | 1524255 | DISTRIBUTION STATION | AO | INSULATOR | 1 | 727 | 26899 | 0.017647 | 0.00047695 | 37
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | U | POLE | 1 | 12 | 9384 | 0.0062583 | 8.003e-06 | 782
AEP-OH | 2021 | 1509795 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 852 | 0.00056432 | 6.6234e-07 | 852
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 1 | 607 | 0.00040204 | 6.6234e-07 | 607
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 1 | 59 | 43719 | 0.029157 | 3.9348e-05 | 741
AEP-OH | 2020 | 1499447 | PARTIAL POWER | OL | CONN/CLAMP | 5 | 44 | 4839 | 0.0032272 | 2.9344e-05 | 109.9773
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | AF | SWITCH, OH | 2 | 273 | 34761 | 0.023024 | 0.00018082 | 127.3297
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 354 | 30447 | 0.020166 | 0.00023447 | 86.0085
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 5143 | 241546 | 0.15909 | 0.0033874 | 46.966
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 2 | 184 | 0.00012187 | 1.3247e-06 | 92
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TOR | CUTOUT | 42 | 1461 | 395956 | 0.25977 | 0.0009585 | 271.0171
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | SO | NONE | 11 | 700 | 28697 | 0.019007 | 0.00046364 | 40.9957
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CO | CUTOUT | 10 | 31 | 3420 | 0.0022526 | 2.0418e-05 | 110.3226
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 13 | 59 | 14329 | 0.0094907 | 3.9078e-05 | 242.8644
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | FUSE | 24 | 493 | 44429 | 0.029148 | 0.00032344 | 90.1197
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | EQF | BREAKER | 6 | 5113 | 703070 | 0.46307 | 0.0033677 | 137.5064
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | UG | METERING | 2 | 643 | 129215 | 0.085107 | 0.00042351 | 200.9565
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | V | NONE | 5 | 2268 | 723340 | 0.47642 | 0.0014938 | 318.933
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TOR | SPLICE, OH | 4 | 4 | 379 | 0.00024963 | 2.6346e-06 | 94.75
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | VA | POLE HARDWARE | 7 | 758 | 70238 | 0.046843 | 0.00050552 | 92.6623
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | ARRESTER | 54 | 211 | 5636 | 0.0036975 | 0.00013843 | 26.7109
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | V | BREAKER | 3 | 993 | 12909 | 0.0085502 | 0.00065771 | 13
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | AF | NONE | 33 | 13466 | 902128 | 0.59185 | 0.0088345 | 66.993
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | POLE | 7 | 123 | 75849 | 0.049761 | 8.0695e-05 | 616.6585
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | TIR | CUTOUT | 5 | 2589 | 365052 | 0.2395 | 0.0016985 | 141.0012
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | CUTOUT | 9 | 26 | 2508 | 0.0016454 | 1.7058e-05 | 96.4615
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | POLE | 162 | 17526 | 3159365 | 2.0577 | 0.011415 | 180.2673
AEP-OH | 2023 | 1524255 | PARTIAL POWER | TOR | CONN/CLAMP | 8 | 8 | 3056 | 0.0020049 | 5.2485e-06 | 382
AEP-OH | 2024 | 1535393 | PARTIAL POWER | U | NONE | 149 | 377 | 45086 | 0.029364 | 0.00024554 | 119.5915
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 25 | 1748 | 175390 | 0.11507 | 0.0011468 | 100.3375
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | CE | METERING | 4 | 9 | 831 | 0.00054733 | 5.9278e-06 | 92.3333
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 18 | 3168 | 0.0021128 | 1.2004e-05 | 176
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 151 | 1288 | 100373 | 0.065373 | 0.00083887 | 77.9293
AEP-OH | 2022 | 1518267 | PARTIAL POWER | TOR | POLE | 4 | 4 | 1642 | 0.0010815 | 2.6346e-06 | 410.5
AEP-OH | 2022 | 1518267 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 2 | 4808 | 263000 | 0.17322 | 0.0031668 | 54.7005
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ERF | POLE | 2 | 909 | 172606 | 0.11511 | 0.00060622 | 189.8856
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 4 | 368 | 0.00023968 | 2.6052e-06 | 92
AEP-OH | 2024 | 1535393 | PARTIAL POWER | A | NONE | 135 | 502 | 40020 | 0.026065 | 0.00032695 | 79.7211
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | F | NONE | 45 | 3255 | 113093 | 0.073657 | 0.00212 | 34.7444
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | UG | CUTOUT | 3 | 86 | 9542 | 0.0062601 | 5.6421e-05 | 110.9535
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | EQF | SWITCH, UG | 6 | 3551 | 307397 | 0.20167 | 0.0023297 | 86.5663
AEP-OH | 2023 | 1524255 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 80 | 5.2485e-05 | 6.5606e-07 | 80
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | EQF | SWITCH, OH | 6 | 4067 | 867649 | 0.57468 | 0.0026937 | 213.3388
AEP-OH | 2023 | 1524255 | DISTRIBUTION SOURCE | VA | POLE | 1 | 896 | 90496 | 0.059371 | 0.00058783 | 101
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 14 | 255 | 56536 | 0.036822 | 0.00016608 | 221.7098
AEP-OH | 2024 | 1535393 | DISTRIBUTION STATION | EQF | REGULATOR | 8 | 10715 | 635972 | 0.41421 | 0.0069787 | 59.3534
AEP-OH | 2023 | 1524255 | PARTIAL POWER | VIN | NONE | 5 | 23 | 2207 | 0.0014479 | 1.5089e-05 | 95.9565
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | NETWORK LIMITER | 1 | 6 | 516 | 0.00033607 | 3.9078e-06 | 86
AEP-OH | 2020 | 1499447 | DISTRIBUTION STATION | AF | INSULATOR | 2 | 694 | 38910 | 0.02595 | 0.00046284 | 56.0663
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 326 | 4313 | 428184 | 0.27888 | 0.0028091 | 99.2775
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | SCO | NONE | 835 | 11699 | 837869 | 0.5457 | 0.0076195 | 71.6189
AEP-OH | 2025 | 1535393 | PARTIAL POWER | EQF | CONN/CLAMP | 269 | 594 | 62351 | 0.040609 | 0.00038687 | 104.968
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | EQF | SPLICE, UG | 9 | 357 | 13809 | 0.0089938 | 0.00023251 | 38.6807
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | VIN | NONE | 14 | 221 | 19928 | 0.012979 | 0.00014394 | 90.1719
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | WL | ARRESTER | 15 | 94 | 16871 | 0.010988 | 6.1222e-05 | 179.4787
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 185 | 20350 | 0.013479 | 0.00012253 | 110
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | EQF | PEDESTAL | 5 | 540 | 44305 | 0.029548 | 0.00036013 | 82.0463
AEP-OH | 2021 | 1509795 | DISTRIBUTION STATION | AO | NONE | 6 | 6554 | 834586 | 0.55278 | 0.004341 | 127.3399
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | NONE | 22 | 13429 | 1116755 | 0.72734 | 0.0087463 | 83.16
AEP-OH | 2024 | 1535393 | PARTIAL POWER | ERF | CUTOUT | 1 | 15 | 15525 | 0.010111 | 9.7695e-06 | 1035
AEP-OH | 2024 | 1535393 | PARTIAL POWER | WT | CONN/CLAMP | 1 | 1 | 130 | 8.4669e-05 | 6.513e-07 | 130
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 4 | 27 | 3303 | 0.0022028 | 1.8007e-05 | 122.3333
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 117 | 7.7062e-05 | 6.5865e-07 | 117
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 4 | 284 | 0.00018632 | 2.6242e-06 | 71
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | AF | TRANSFORMER, OH | 1 | 3859 | 1134349 | 0.7388 | 0.0025134 | 293.949
AEP-OH | 2025 | 1535393 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 5 | 3020 | 423022 | 0.27551 | 0.0019669 | 140.0735
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | ARRESTER | 2 | 3 | 772 | 0.00050648 | 1.9682e-06 | 257.3333
AEP-OH | 2025 | 1535393 | DISTRIBUTION LINE | A | INSULATOR | 1 | 32 | 8576 | 0.0055855 | 2.0842e-05 | 268
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 13 | 912 | 0.00059833 | 8.5288e-06 | 70.1538
AEP-OH | 2025 | 1535393 | PARTIAL POWER | U | BREAKER | 1 | 1 | 52 | 3.3868e-05 | 6.513e-07 | 52
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | CE | POLE | 1 | 2 | 20 | 1.3121e-05 | 1.3121e-06 | 10
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | ABI | CAPACITOR | 1 | 2510 | 238450 | 0.15644 | 0.0016467 | 95
AEP-OH | 2022 | 1518267 | DISTRIBUTION LINE | AF | FUSE | 2 | 514 | 28784 | 0.018958 | 0.00033854 | 56
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | SCO | BREAKER | 1 | 6 | 1872 | 0.0012281 | 3.9363e-06 | 312
AEP-OH | 2024 | 1535393 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 96 | 15360 | 0.010004 | 6.2525e-05 | 160
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | O | POLE | 2 | 7 | 104 | 6.823e-05 | 4.5924e-06 | 14.8571
AEP-OH | 2021 | 1509795 | DISTRIBUTION LINE | F | ARRESTER | 1 | 82 | 9102 | 0.0060286 | 5.4312e-05 | 111
AEP-OH | 2021 | 1509795 | PARTIAL POWER | EQF | NETWORK LIMITER | 1 | 9 | 1521 | 0.0010074 | 5.9611e-06 | 169
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WFS | POLE | 2 | 119 | 19509 | 0.012799 | 7.8071e-05 | 163.9412
AEP-OH | 2021 | 1509795 | PARTIAL POWER | WU | METERING | 1 | 1 | 55 | 3.6429e-05 | 6.6234e-07 | 55
AEP-OH | 2023 | 1524255 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 2 | 74 | 12084 | 0.0079278 | 4.8548e-05 | 163.2973
AEP-OH | 2022 | 1518267 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 2 | 328 | 0.00021604 | 1.3173e-06 | 164
AEP-OH | 2020 | 1499447 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 40 | 4400 | 0.0029344 | 2.6677e-05 | 110
AEP-OH | 2024 | 1535393 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 3 | 231 | 0.00015045 | 1.9539e-06 | 77
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 225 | 13624 | 1374802 | 2.4098 | 0.023881 | 100.9103
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 104 | 226 | 29458 | 0.052622 | 0.00040371 | 130.3451
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | NONE | 281 | 10362 | 1094377 | 1.9549 | 0.01851 | 105.6145
AEP-PSO | 2022 | 570502 | PARTIAL POWER | U | CONN/CLAMP | 2 | 2 | 238 | 0.00041718 | 3.5057e-06 | 119
AEP-PSO | 2022 | 570502 | TRANSMISSION STATION | R | NONE | 2 | 3078 | 36936 | 0.064743 | 0.0053952 | 12
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | WW | NONE | 5 | 883 | 157776 | 0.27656 | 0.0015478 | 178.6818
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | JUMPER/RISER | 9 | 125 | 44136 | 0.077363 | 0.00021911 | 353.088
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | FW | TRANSFORMER, OH | 1 | 6 | 1572 | 0.0027555 | 1.0517e-05 | 262
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 45 | 69 | 5039 | 0.0088326 | 0.00012095 | 73.029
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 54 | 3085 | 314316 | 0.55095 | 0.0054075 | 101.8853
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ABI | NONE | 284 | 2963 | 265431 | 0.46327 | 0.0051714 | 89.5818
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 68 | 346 | 34762 | 0.060932 | 0.00060648 | 100.4682
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CO | NONE | 7 | 7 | 906 | 0.0016019 | 1.2377e-05 | 129.4286
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 3 | 1150 | 50615 | 0.090416 | 0.0020543 | 44.013
AEP-PSO | 2020 | 559804 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 1 | 278 | 12510 | 0.022347 | 0.0004966 | 45
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CO | CONDUCTOR UG | 36 | 95 | 14425 | 0.025768 | 0.0001697 | 151.8421
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TIR | NONE | 4 | 5 | 544 | 0.00095355 | 8.7642e-06 | 108.8
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OU | NONE | 7 | 192 | 35430 | 0.062103 | 0.00033655 | 184.5312
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | V | METERING | 12 | 24 | 1363 | 0.0023891 | 4.2068e-05 | 56.7917
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | POLE | 22 | 1071 | 255339 | 0.44757 | 0.0018773 | 238.4118
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | FUSE | 205 | 2135 | 148804 | 0.26311 | 0.003775 | 69.6974
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 7 | 806 | 7913 | 0.01387 | 0.0014128 | 9.8176
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | NONE | 245 | 10076 | 2726079 | 4.8201 | 0.017816 | 270.5517
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | NONE | 384 | 30556 | 2792253 | 4.8944 | 0.05356 | 91.3815
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | NONE | 324 | 11595 | 1129570 | 1.98 | 0.020324 | 97.4187
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 46 | 50 | 5425 | 0.0096909 | 8.9317e-05 | 108.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | CONDUCTOR UG | 7 | 122 | 21443 | 0.038304 | 0.00021793 | 175.7623
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | NONE | 46 | 1349 | 165882 | 0.29632 | 0.0024098 | 122.9666
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 142 | 3428 | 334553 | 0.59763 | 0.0061236 | 97.5942
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | FUSE | 2 | 54 | 2619 | 0.0046784 | 9.6462e-05 | 48.5
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 2 | 114 | 0.00019982 | 3.5057e-06 | 57
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | METERING | 10 | 10 | 2229 | 0.0039071 | 1.7528e-05 | 222.9
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | BREAKER | 6 | 3147 | 39328 | 0.068936 | 0.0055162 | 12.497
AEP-PSO | 2021 | 565565 | PARTIAL POWER | UB | NONE | 2 | 4 | 180 | 0.00031827 | 7.0726e-06 | 45
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | PEDESTAL | 10 | 38 | 2685 | 0.0047064 | 6.6608e-05 | 70.6579
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ABI | NONE | 231 | 3316 | 291159 | 0.51481 | 0.0058632 | 87.8043
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | ABI | NONE | 5 | 2434 | 144366 | 0.25305 | 0.0042664 | 59.3122
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | NETWORK PROTECTOR | 1 | 2 | 60 | 0.00010517 | 3.5057e-06 | 30
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | CROSSARM | 1 | 6 | 90 | 0.00016077 | 1.0718e-05 | 15
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | FUSE | 4 | 7 | 693 | 0.0012253 | 1.2377e-05 | 99
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | FUSE | 100 | 1593 | 114344 | 0.20426 | 0.0028456 | 71.779
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | POLE | 111 | 7160 | 1063674 | 1.9001 | 0.01279 | 148.5578
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | EQF | CROSSARM | 3 | 1720 | 230561 | 0.40414 | 0.0030149 | 134.0471
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | WU | NONE | 13 | 9405 | 507522 | 0.88961 | 0.016485 | 53.963
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WT | NONE | 5 | 2718 | 695009 | 1.2289 | 0.0048058 | 255.706
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | POLE | 104 | 7994 | 1581986 | 2.7972 | 0.014135 | 197.8967
AEP-PSO | 2022 | 570502 | PARTIAL POWER | A | NONE | 103 | 273 | 23761 | 0.041649 | 0.00047853 | 87.0366
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | NONE | 312 | 10838 | 555953 | 0.9745 | 0.018997 | 51.2966
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 62 | 4721 | 519130 | 0.90995 | 0.0082752 | 109.9619
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | O | NONE | 71 | 555 | 62590 | 0.10971 | 0.00097283 | 112.7748
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 7 | 657 | 0.0011617 | 1.2377e-05 | 93.8571
AEP-PSO | 2021 | 565565 | PARTIAL POWER | OL | NONE | 7 | 15 | 903 | 0.0015966 | 2.6522e-05 | 60.2
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | ERF | CONDUCTOR OVERHEAD | 2 | 700 | 117382 | 0.20755 | 0.0012377 | 167.6886
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OU | POLE | 1 | 14 | 1708 | 0.0029939 | 2.454e-05 | 122
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | O | NONE | 5 | 6405 | 366667 | 0.64832 | 0.011325 | 57.247
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WT | CONDUCTOR UG | 1 | 4 | 484 | 0.00084838 | 7.0114e-06 | 121
AEP-PSO | 2023 | 572956 | PARTIAL POWER | U | NONE | 112 | 245 | 17848 | 0.031151 | 0.00042761 | 72.849
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 3 | 114 | 0.00019982 | 5.2585e-06 | 38
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | ARRESTER | 14 | 20 | 2325 | 0.0040579 | 3.4907e-05 | 116.25
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 9 | 1314 | 0.0023233 | 1.5913e-05 | 146
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 8 | 283 | 37826 | 0.06757 | 0.00050553 | 133.6608
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 1941 | 214279 | 0.37399 | 0.0033877 | 110.3962
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | FUSE | 22 | 250 | 42457 | 0.074102 | 0.00043633 | 169.828
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 10 | 10 | 1021 | 0.0018239 | 1.7863e-05 | 102.1
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | FUSE | 24 | 74 | 5195 | 0.00928 | 0.00013219 | 70.2027
AEP-PSO | 2024 | 579031 | PARTIAL POWER | A | NONE | 96 | 444 | 36945 | 0.063805 | 0.0007668 | 83.2095
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WT | POLE | 9 | 1609 | 1042949 | 1.8012 | 0.0027788 | 648.197
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | POLE | 4 | 1812 | 703063 | 1.2559 | 0.0032368 | 388.0039
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | SPLICE, UG | 9 | 1823 | 99237 | 0.1732 | 0.0031817 | 54.4361
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 72 | 0.00012566 | 1.7453e-06 | 72
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | V | NONE | 3 | 4609 | 153208 | 0.26459 | 0.0079599 | 33.2411
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 1 | 100 | 0.00017453 | 1.7453e-06 | 100
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 21 | 2730 | 0.0047148 | 3.6267e-05 | 130
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 14 | 2325 | 0.0040153 | 2.4178e-05 | 166.0714
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | NONE | 521 | 2955 | 175619 | 0.3033 | 0.0051034 | 59.4311
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | CONDUCTOR UG | 90 | 120 | 16741 | 0.028912 | 0.00020724 | 139.5083
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 3 | 143 | 0.00024696 | 5.1811e-06 | 47.6667
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 48 | 690 | 143678 | 0.24814 | 0.0011916 | 208.229
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | FUSE | 50 | 470 | 77567 | 0.13396 | 0.0008117 | 165.0362
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CF | NONE | 2 | 11 | 907 | 0.001583 | 1.9199e-05 | 82.4545
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | O | FUSE | 2 | 9 | 985 | 0.0017192 | 1.5708e-05 | 109.4444
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | ARRESTER | 4 | 154 | 12278 | 0.021521 | 0.00026994 | 79.7273
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 5 | 689 | 321448 | 0.56103 | 0.0012025 | 466.5428
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | V | PEDESTAL | 1 | 7 | 1512 | 0.0026389 | 1.2217e-05 | 216
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | AO | OTHER EQUIPMENT | 1 | 409 | 184459 | 0.32194 | 0.00071384 | 451
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 371 | 32298 | 0.056371 | 0.00064752 | 87.0566
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | INSULATOR | 5 | 388 | 41162 | 0.071088 | 0.00067009 | 106.0876
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | SPLICE, OH | 12 | 980 | 33209 | 0.057353 | 0.0016925 | 33.8867
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 14 | 4823 | 0.0083294 | 2.4178e-05 | 344.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 7 | 29 | 3758 | 0.0064902 | 5.0084e-05 | 129.5862
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERF | FUSE | 3 | 33 | 1422 | 0.0024558 | 5.6992e-05 | 43.0909
AEP-PSO | 2021 | 565565 | PARTIAL POWER | ERF | NONE | 1 | 1 | 104 | 0.00018389 | 1.7681e-06 | 104
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | WU | NONE | 2 | 29 | 4466 | 0.0079778 | 5.1804e-05 | 154
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 69 | 10163 | 0.017552 | 0.00011916 | 147.2899
AEP-PSO | 2022 | 570502 | PARTIAL POWER | OU | METERING | 1 | 1 | 109 | 0.00019106 | 1.7528e-06 | 109
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | CUTOUT | 3 | 140 | 28792 | 0.050908 | 0.00024754 | 205.6571
AEP-PSO | 2024 | 579031 | PARTIAL POWER | U | CONDUCTOR UG | 3 | 3 | 293 | 0.00050602 | 5.1811e-06 | 97.6667
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | VIN | CROSSARM | 1 | 17 | 4216 | 0.0072811 | 2.9359e-05 | 248
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 4 | 583 | 0.0010069 | 6.9081e-06 | 145.75
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OU | FUSE | 2 | 35 | 1960 | 0.003385 | 6.0446e-05 | 56
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 34 | 4862 | 0.0086852 | 6.0736e-05 | 143
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | UB | NONE | 2 | 31 | 317 | 0.00055327 | 5.4105e-05 | 10.2258
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | A | NONE | 1 | 1274 | 21658 | 0.037404 | 0.0022002 | 17
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | POLE | 1 | 159 | 10010 | 0.017699 | 0.00028113 | 62.956
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CE | CONDUCTOR UG | 1 | 1 | 97 | 0.00017003 | 1.7528e-06 | 97
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 3 | 2025 | 0.0034972 | 5.1811e-06 | 675
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 1 | 1 | 58 | 0.00010017 | 1.727e-06 | 58
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 390 | 0.00067354 | 1.727e-06 | 390
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | BREAKER | 1 | 140 | 10362 | 0.017895 | 0.00024178 | 74.0143
AEP-PSO | 2024 | 579031 | PARTIAL POWER | CO | CONN/CLAMP | 1 | 1 | 87 | 0.00015025 | 1.727e-06 | 87
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 440 | 64575 | 0.11152 | 0.00075989 | 146.7614
AEP-PSO | 2022 | 570502 | PARTIAL POWER | U | NONE | 113 | 237 | 13747 | 0.024096 | 0.00041542 | 58.0042
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 558 | 18388 | 1996345 | 3.5298 | 0.032513 | 108.5678
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | NONE | 1556 | 26451 | 4062969 | 7.1839 | 0.046769 | 153.6036
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OL | NONE | 57 | 14007 | 771042 | 1.3515 | 0.024552 | 55.0469
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 2 | 282 | 0.0004943 | 3.5057e-06 | 141
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | FUSE | 2 | 7 | 537 | 0.00094949 | 1.2377e-05 | 76.7143
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | AB | NONE | 7 | 4850 | 259747 | 0.45927 | 0.0085755 | 53.5561
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | FUSE | 23 | 157 | 9877 | 0.017644 | 0.00028046 | 62.9108
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | ARRESTER | 2 | 1818 | 182878 | 0.32335 | 0.0032145 | 100.593
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | POLE | 2 | 616 | 83905 | 0.14836 | 0.0010892 | 136.2094
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 1 | 97 | 0.00017003 | 1.7528e-06 | 97
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 162 | 16668 | 0.029775 | 0.00028939 | 102.8889
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | F | NONE | 31 | 239 | 18136 | 0.031653 | 0.00041713 | 75.8828
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | POLE | 12 | 459 | 72730 | 0.12992 | 0.00081993 | 158.4532
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | REGULATOR | 2 | 781 | 15158 | 0.026456 | 0.0013631 | 19.4085
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 24 | 1268 | 0.0022226 | 4.2068e-05 | 52.8333
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | ARRESTER | 8 | 6253 | 1138103 | 2.033 | 0.01117 | 182.0091
AEP-PSO | 2023 | 572956 | PARTIAL POWER | VIN | NONE | 1 | 2 | 84 | 0.00014661 | 3.4907e-06 | 42
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | SPLICE, OH | 9 | 156 | 9997 | 0.017523 | 0.00027344 | 64.0833
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | NONE | 45 | 7702 | 392189 | 0.67732 | 0.013302 | 50.9204
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | SWITCH, OH | 1 | 1 | 219 | 0.00037822 | 1.727e-06 | 219
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CE | ARRESTER | 1 | 44 | 3124 | 0.0054524 | 7.6795e-05 | 71
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | EQF | TRANSFORMER, POWER - LTC | 4 | 2637 | 124420 | 0.22226 | 0.0047106 | 47.1824
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WL | FUSE | 12 | 39 | 3514 | 0.0061331 | 6.8068e-05 | 90.1026
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 10 | 900 | 0.0015913 | 1.7681e-05 | 90
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 3 | 3 | 453 | 0.00079064 | 5.236e-06 | 151
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | U | NONE | 10 | 9769 | 450990 | 0.79741 | 0.017273 | 46.1654
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | POLE | 15 | 2447 | 850201 | 1.4683 | 0.004226 | 347.4463
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 103 | 29896 | 0.052179 | 0.00017977 | 290.2524
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 139 | 20989 | 0.036248 | 0.00024006 | 151
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 209 | 91989 | 0.16432 | 0.00037334 | 440.1388
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 4 | 276 | 0.00048801 | 7.0726e-06 | 69
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 3 | 761 | 117214 | 0.20546 | 0.0013339 | 154.0263
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | WU | NONE | 5 | 1873 | 211776 | 0.36574 | 0.0032347 | 113.0678
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 3 | 1020 | 0.0017802 | 5.236e-06 | 340
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 9 | 11 | 985 | 0.0017011 | 1.8997e-05 | 89.5455
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | POLE | 16 | 1337 | 166497 | 0.28754 | 0.002309 | 124.5303
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 10 | 1889 | 0.0032623 | 1.727e-05 | 188.9
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 933 | 10263 | 0.017724 | 0.0016113 | 11
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 5 | 165 | 0.00028496 | 8.6351e-06 | 33
AEP-PSO | 2020 | 559804 | PARTIAL POWER | O | CONN/CLAMP | 3 | 23 | 2536 | 0.0045302 | 4.1086e-05 | 110.2609
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | O | SPLICE, OH | 1 | 1 | 107 | 0.00019114 | 1.7863e-06 | 107
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 3 | 4 | 717 | 0.0012383 | 6.9081e-06 | 179.25
AEP-PSO | 2025 | 579031 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 3 | 355 | 0.00061309 | 5.1811e-06 | 118.3333
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERO | NONE | 2 | 2 | 165 | 0.00029475 | 3.5727e-06 | 82.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 2 | 365 | 5110 | 0.0091282 | 0.00065201 | 14
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | CONN/CLAMP | 4 | 6 | 551 | 0.00095159 | 1.0362e-05 | 91.8333
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | F | METERING | 1 | 1 | 53 | 9.3712e-05 | 1.7681e-06 | 53
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 2 | 42 | 9149 | 0.016177 | 7.4262e-05 | 217.8333
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WL | OTHER EQUIPMENT | 1 | 1 | 82 | 0.00014373 | 1.7528e-06 | 82
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | SWITCH, OH | 1 | 799 | 10387 | 0.018555 | 0.0014273 | 13
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 8 | 264 | 0.00046679 | 1.4145e-05 | 33
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 36 | 10431 | 0.018015 | 6.2173e-05 | 289.75
AEP-PSO | 2021 | 565565 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 4 | 676 | 0.0011953 | 7.0726e-06 | 169
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 68 | 7276 | 0.012865 | 0.00012023 | 107
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | AF | NONE | 4 | 17 | 2214 | 0.0038236 | 2.9359e-05 | 130.2353
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | INSULATOR | 1 | 33 | 5181 | 0.0090815 | 5.7844e-05 | 157
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 2 | 28 | 4.908e-05 | 3.5057e-06 | 14
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 16 | 1382 | 0.0023867 | 2.7632e-05 | 86.375
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WL | INSULATOR | 1 | 6 | 876 | 0.0015129 | 1.0362e-05 | 146
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 16 | 1648 | 0.0028461 | 2.7632e-05 | 103
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 36 | 10422 | 0.01819 | 6.2832e-05 | 289.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | EQF | RELAY | 1 | 772 | 15440 | 0.026665 | 0.0013333 | 20
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 2 | 94 | 0.00016234 | 3.454e-06 | 47
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 13 | 1092 | 0.0018859 | 2.2451e-05 | 84
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | AO | NONE | 24 | 19464 | 1389271 | 2.4352 | 0.034117 | 71.3764
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 56 | 6274 | 0.010997 | 9.8159e-05 | 112.0357
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | SWITCH, UG | 4 | 1480 | 99474 | 0.17436 | 0.0025942 | 67.2122
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | CONN/CLAMP | 344 | 658 | 43857 | 0.077545 | 0.0011634 | 66.652
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 12 | 1398 | 0.0024719 | 2.1218e-05 | 116.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | ARRESTER | 2 | 5 | 388 | 0.0006801 | 8.7642e-06 | 77.6
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | WL | NONE | 12 | 66 | 7628 | 0.013487 | 0.0001167 | 115.5758
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | CUTOUT | 26 | 870 | 120327 | 0.21276 | 0.0015383 | 138.3069
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | CROSSARM | 7 | 187 | 36816 | 0.065096 | 0.00033064 | 196.877
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | FUSE | 23 | 171 | 13647 | 0.02413 | 0.00030235 | 79.807
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | POLE | 7 | 48 | 7762 | 0.013606 | 8.4136e-05 | 161.7083
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 4 | 484 | 0.00085578 | 7.0726e-06 | 121
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 6 | 30 | 1248 | 0.0021875 | 5.2585e-05 | 41.6
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CE | ARRESTER | 1 | 2 | 128 | 0.00022632 | 3.5363e-06 | 64
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | FUSE | 222 | 2470 | 354881 | 0.61939 | 0.004311 | 143.6765
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CE | NONE | 17 | 717 | 12714 | 0.02219 | 0.0012514 | 17.7322
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | CONN/CLAMP | 3 | 5 | 1746 | 0.0031189 | 8.9317e-06 | 349.2
AEP-PSO | 2022 | 570502 | PARTIAL POWER | A | SPLICE, OH | 1 | 1 | 16 | 2.8045e-05 | 1.7528e-06 | 16
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | V | NONE | 38 | 98 | 6160 | 0.010751 | 0.00017104 | 62.8571
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 1 | 100 | 0.00017528 | 1.7528e-06 | 100
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | JUMPER/RISER | 10 | 13 | 2233 | 0.0038973 | 2.2689e-05 | 171.7692
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | METERING | 2 | 2 | 102 | 0.00018221 | 3.5727e-06 | 51
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | FUSE | 13 | 79 | 22633 | 0.039502 | 0.00013788 | 286.4937
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | CAPACITOR | 2 | 184 | 8104 | 0.014144 | 0.00032114 | 44.0435
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | CONN/CLAMP | 320 | 629 | 54661 | 0.094401 | 0.0010863 | 86.9014
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 1 | 219 | 0.00038223 | 1.7453e-06 | 219
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | FUSE | 79 | 1112 | 107419 | 0.18748 | 0.0019408 | 96.5998
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | CUTOUT | 14 | 465 | 66403 | 0.11862 | 0.00083065 | 142.8022
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | ERF | NONE | 1 | 299 | 9568 | 0.016771 | 0.0005241 | 32
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 6 | 206 | 20574 | 0.036063 | 0.00036109 | 99.8738
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | FUSE | 11 | 103 | 12140 | 0.021465 | 0.00018212 | 117.8641
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 10 | 1334 | 0.0023587 | 1.7681e-05 | 133.4
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WW | NONE | 6 | 10 | 739 | 0.0013067 | 1.7681e-05 | 73.9
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 41 | 1834 | 278283 | 0.4806 | 0.0031674 | 151.7356
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | U | NONE | 18 | 14750 | 1321851 | 2.3071 | 0.025744 | 89.617
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 1 | 117 | 0.00020206 | 1.727e-06 | 117
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 3 | 3665 | 101709 | 0.18169 | 0.0065469 | 27.7514
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 1 | 118 | 0.00020595 | 1.7453e-06 | 118
AEP-PSO | 2024 | 579031 | PARTIAL POWER | A | FUSE | 18 | 31 | 1362 | 0.0023522 | 5.3538e-05 | 43.9355
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | FUSE | 57 | 796 | 51039 | 0.088146 | 0.0013747 | 64.1193
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | JUMPER/RISER | 5 | 29 | 1708 | 0.0029498 | 5.0084e-05 | 58.8966
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 2 | 21 | 1829 | 0.0032339 | 3.7131e-05 | 87.0952
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 1 | 43 | 7.5049e-05 | 1.7453e-06 | 43
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WW | CONN/CLAMP | 3 | 3 | 211 | 0.0003644 | 5.1811e-06 | 70.3333
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 15 | 3390 | 0.0059167 | 2.618e-05 | 226
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | OU | POLE | 2 | 605 | 443976 | 0.77489 | 0.0010559 | 733.8446
AEP-PSO | 2023 | 572956 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 1 | 108 | 0.0001885 | 1.7453e-06 | 108
AEP-PSO | 2023 | 572956 | PARTIAL POWER | CO | NONE | 1 | 1 | 69 | 0.00012043 | 1.7453e-06 | 69
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WI | FUSE | 3 | 21 | 1408 | 0.0024316 | 3.6267e-05 | 67.0476
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WT | POLE | 5 | 95 | 30829 | 0.053242 | 0.00016407 | 324.5158
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 8 | 318 | 0.00054919 | 1.3816e-05 | 39.75
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 3 | 692 | 14052 | 0.024268 | 0.0011951 | 20.3064
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | CONN/CLAMP | 9 | 10 | 1424 | 0.0024593 | 1.727e-05 | 142.4
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | UB | NONE | 3 | 106 | 3542 | 0.0062628 | 0.00018742 | 33.4151
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | V | POLE | 2 | 4 | 1210 | 0.0020897 | 6.9081e-06 | 302.5
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WW | FUSE | 5 | 27 | 4446 | 0.0076783 | 4.663e-05 | 164.6667
AEP-PSO | 2025 | 579031 | PARTIAL POWER | A | FUSE | 1 | 1 | 33 | 5.6992e-05 | 1.727e-06 | 33
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | EQF | INSULATOR | 2 | 791 | 158602 | 0.28332 | 0.001413 | 200.5082
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | CABLE TERMINATOR | 1 | 1 | 344 | 0.0006145 | 1.7863e-06 | 344
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 4 | 311 | 0.00054989 | 7.0726e-06 | 77.75
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | INSULATOR | 6 | 715 | 78835 | 0.13615 | 0.0012348 | 110.2587
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 43 | 7.603e-05 | 1.7681e-06 | 43
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 1 | 312 | 0.00055734 | 1.7863e-06 | 312
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WL | CUTOUT | 1 | 2 | 152 | 0.00026876 | 3.5363e-06 | 76
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | WW | POLE | 1 | 615 | 153135 | 0.26447 | 0.0010621 | 249
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | BREAKER | 1 | 587 | 90504 | 0.16002 | 0.0010379 | 154.1806
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 2 | 220 | 0.00038397 | 3.4907e-06 | 110
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 927 | 108466 | 0.18931 | 0.0016179 | 117.0076
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | ABI | JUMPER/RISER | 1 | 881 | 54622 | 0.097573 | 0.0015738 | 62
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 7 | 2096 | 0.0036582 | 1.2217e-05 | 299.4286
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | F | NONE | 3 | 1074 | 74106 | 0.12798 | 0.0018548 | 69
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 53 | 12561 | 0.021923 | 9.2503e-05 | 237
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 2 | 3186 | 957405 | 1.6535 | 0.0055023 | 300.5038
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 1 | 51 | 8.8078e-05 | 1.727e-06 | 51
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 1 | 104 | 0.00017961 | 1.727e-06 | 104
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | TRANSFORMER, GROUNDING | 1 | 1 | 206 | 0.00035577 | 1.727e-06 | 206
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | CUTOUT | 319 | 7907 | 914366 | 1.6027 | 0.01386 | 115.6401
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | FUSE | 249 | 2169 | 161381 | 0.28288 | 0.0038019 | 74.4034
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | R | NONE | 5 | 3879 | 158452 | 0.28017 | 0.0068586 | 40.8487
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 2 | 3 | 179 | 0.00031975 | 5.359e-06 | 59.6667
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 152 | 3001 | 618861 | 1.0801 | 0.0052377 | 206.2183
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 8 | 8705 | 373774 | 0.65517 | 0.015258 | 42.9379
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 32 | 1159 | 0.0020315 | 5.6091e-05 | 36.2188
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | JUMPER/RISER | 15 | 64 | 11356 | 0.020079 | 0.00011316 | 177.4375
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 87 | 1914 | 0.0033842 | 0.00015383 | 22
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | CUTOUT | 285 | 8212 | 805955 | 1.3919 | 0.014182 | 98.1436
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | CROSSARM | 19 | 252 | 12546 | 0.021897 | 0.00043982 | 49.7857
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | NONE | 182 | 3975 | 152918 | 0.26409 | 0.0068649 | 38.4699
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | NONE | 350 | 3539 | 228132 | 0.39399 | 0.0061119 | 64.4623
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 2 | 2 | 180 | 0.00031827 | 3.5363e-06 | 90
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | POLE | 2 | 6 | 648 | 0.0011458 | 1.0609e-05 | 108
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 11 | 40 | 3370 | 0.00602 | 7.1454e-05 | 84.25
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 159 | 6768 | 740037 | 1.2781 | 0.011688 | 109.3435
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 35 | 3239 | 396440 | 0.68466 | 0.0055938 | 122.3958
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 16 | 2627 | 0.0046927 | 2.8581e-05 | 164.1875
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 8 | 1593 | 0.0028167 | 1.4145e-05 | 199.125
AEP-PSO | 2022 | 570502 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 2 | 21 | 2586 | 0.0045329 | 3.681e-05 | 123.1429
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OL | SWITCH, OH | 1 | 2 | 564 | 0.00098437 | 3.4907e-06 | 282
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | F | NONE | 26 | 26616 | 12675312 | 22.1227 | 0.046454 | 476.229
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 2 | 2 | 255 | 0.00044039 | 3.454e-06 | 127.5
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | ARRESTER | 2 | 10 | 404 | 0.00070512 | 1.7453e-05 | 40.4
AEP-PSO | 2023 | 572956 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 4 | 24 | 2541 | 0.0044349 | 4.1888e-05 | 105.875
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 7 | 2590 | 0.0045204 | 1.2217e-05 | 370
AEP-PSO | 2023 | 572956 | PARTIAL POWER | A | METERING | 1 | 2 | 58 | 0.00010123 | 3.4907e-06 | 29
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 5 | 151 | 0.00026699 | 8.8407e-06 | 30.2
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | SPLICE, OH | 1 | 4 | 160 | 0.00028581 | 7.1454e-06 | 40
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | WL | NONE | 8 | 4210 | 332431 | 0.59383 | 0.0075205 | 78.9622
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | WL | NONE | 2 | 2 | 103 | 0.00018054 | 3.5057e-06 | 51.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 115 | 0.00020158 | 3.5057e-06 | 57.5
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | JUMPER/RISER | 3 | 138 | 3331 | 0.0058137 | 0.00024086 | 24.1377
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | POLE | 10 | 580 | 33682 | 0.05817 | 0.0010017 | 58.0724
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | V | METERING | 4 | 14 | 922 | 0.0015923 | 2.4178e-05 | 65.8571
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 8 | 4680 | 0.0080825 | 1.3816e-05 | 585
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | TRANSFORMER, STATION SERVICE | 2 | 7 | 277 | 0.00047839 | 1.2089e-05 | 39.5714
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 1 | 68 | 0.00011744 | 1.727e-06 | 68
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | FW | CROSSARM | 2 | 525 | 8925 | 0.015943 | 0.00093783 | 17
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | U | RECLOSER, LINE/OCR/BR | 1 | 182 | 3640 | 0.006436 | 0.0003218 | 20
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 403 | 0.00071989 | 1.7863e-06 | 403
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 181 | 0.00032003 | 1.7681e-06 | 181
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 4 | 23 | 3171 | 0.0054764 | 3.9722e-05 | 137.8696
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | FW | NONE | 4 | 1446 | 52546 | 0.092909 | 0.0025567 | 36.3389
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 16 | 2336 | 0.0040771 | 2.7925e-05 | 146
AEP-PSO | 2021 | 565565 | PARTIAL POWER | UB | CONN/CLAMP | 1 | 1 | 34 | 6.0117e-05 | 1.7681e-06 | 34
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 4 | 8772 | 0.01531 | 6.9813e-06 | 2193
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | WI | NONE | 4 | 3248 | 25984 | 0.045351 | 0.0056688 | 8
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WU | JUMPER/RISER | 1 | 1 | 12 | 2.1218e-05 | 1.7681e-06 | 12
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | WL | POLE | 1 | 279 | 96534 | 0.17069 | 0.00049331 | 346
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 12 | 492 | 0.00086993 | 2.1218e-05 | 41
AEP-PSO | 2024 | 579031 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 79 | 0.00013643 | 1.727e-06 | 79
AEP-PSO | 2022 | 570502 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 1 | 70 | 0.0001227 | 1.7528e-06 | 70
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | SWITCH, OH | 1 | 9 | 549 | 0.00094814 | 1.5543e-05 | 61
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 302 | 0.00052156 | 1.727e-06 | 302
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 6 | 63 | 5146 | 0.0088873 | 0.0001088 | 81.6825
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | EQF | CONN/CLAMP | 1 | 182 | 24388 | 0.042119 | 0.00031432 | 134
AEP-PSO | 2024 | 579031 | PARTIAL POWER | VIN | SPLICE, OH | 1 | 1 | 113 | 0.00019515 | 1.727e-06 | 113
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 3 | 579 | 0.00099995 | 5.1811e-06 | 193
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 4 | 424 | 0.00073226 | 6.9081e-06 | 106
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WL | CUTOUT | 2 | 3 | 190 | 0.00033304 | 5.2585e-06 | 63.3333
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | NONE | 1778 | 36456 | 3347470 | 5.8676 | 0.063902 | 91.8222
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | FUSE | 15 | 230 | 14828 | 0.026218 | 0.00040667 | 64.4696
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | METERING | 5 | 100 | 8018 | 0.014177 | 0.00017681 | 80.18
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 1 | 10 | 1150 | 0.0020158 | 1.7528e-05 | 115
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TOR | NONE | 16 | 31 | 2923 | 0.0051236 | 5.4338e-05 | 94.2903
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | AO | NONE | 7 | 2792 | 99460 | 0.17586 | 0.0049367 | 35.6232
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 197 | 1528 | 399944 | 0.71444 | 0.0027295 | 261.7435
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 36 | 4959 | 468396 | 0.82102 | 0.0086923 | 94.4537
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 200 | 15218 | 0.026908 | 0.00035363 | 76.09
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | JUMPER/RISER | 4 | 310 | 13129 | 0.023013 | 0.00054338 | 42.3516
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 282 | 3847 | 276706 | 0.49429 | 0.006872 | 71.9277
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | FUSE | 113 | 1638 | 102724 | 0.1835 | 0.002926 | 62.7131
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | SPLICE, OH | 2 | 28 | 2408 | 0.0042577 | 4.9508e-05 | 86
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | ABX | NONE | 3 | 4 | 301 | 0.00053221 | 7.0726e-06 | 75.25
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | WU | POLE | 1 | 2 | 430 | 0.0007603 | 3.5363e-06 | 215
AEP-PSO | 2022 | 570502 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 2 | 152 | 0.00026643 | 3.5057e-06 | 76
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | JUMPER/RISER | 13 | 103 | 14268 | 0.025228 | 0.00018212 | 138.5243
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 1 | 39 | 6.8361e-05 | 1.7528e-06 | 39
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WT | METERING | 1 | 1 | 207 | 0.00036284 | 1.7528e-06 | 207
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TR | FUSE | 1 | 3 | 219 | 0.00038387 | 5.2585e-06 | 73
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | V | CIRCUIT SWITCHER | 5 | 6545 | 92960 | 0.16437 | 0.011572 | 14.2032
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 4 | 56 | 9701 | 0.017329 | 0.00010004 | 173.2321
AEP-PSO | 2021 | 565565 | PARTIAL POWER | O | CONN/CLAMP | 1 | 1 | 28 | 4.9508e-05 | 1.7681e-06 | 28
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CF | POLE | 2 | 68 | 7704 | 0.013622 | 0.00012023 | 113.2941
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | EQF | POLE | 3 | 1079 | 65815 | 0.11536 | 0.0018913 | 60.9963
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | TRANSFORMER, OH | 27 | 94 | 20536 | 0.036684 | 0.00016792 | 218.4681
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 771 | 43947 | 0.077032 | 0.0013514 | 57
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 25 | 54 | 4182 | 0.0074705 | 9.6462e-05 | 77.4444
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | CUTOUT | 3 | 633 | 141516 | 0.24806 | 0.0011095 | 223.564
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | NONE | 431 | 16085 | 1861320 | 3.2145 | 0.027779 | 115.7177
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 23 | 1200 | 166340 | 0.29032 | 0.0020944 | 138.6167
AEP-PSO | 2020 | 559804 | PARTIAL POWER | A | FUSE | 5 | 6 | 726 | 0.0012969 | 1.0718e-05 | 121
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | ABI | NONE | 5 | 2723 | 254144 | 0.44357 | 0.0047525 | 93.3324
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 7 | 415 | 40681 | 0.071002 | 0.00072431 | 98.0265
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | CUTOUT | 27 | 463 | 34813 | 0.060123 | 0.00079961 | 75.1901
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 5 | 700 | 220292 | 0.38951 | 0.0012377 | 314.7029
AEP-PSO | 2022 | 570502 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 2 | 2 | 109 | 0.00019106 | 3.5057e-06 | 54.5
AEP-PSO | 2021 | 565565 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 17 | 2089 | 0.0036937 | 3.0058e-05 | 122.8824
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | FUSE | 10 | 707 | 38515 | 0.066516 | 0.001221 | 54.4767
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 1322 | 64961 | 0.11387 | 0.0023173 | 49.1384
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | R | NONE | 13 | 2971 | 238909 | 0.41698 | 0.0051854 | 80.4137
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 4 | 1831 | 13302 | 0.023216 | 0.0031957 | 7.2649
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | INSULATOR | 1 | 3 | 162 | 0.00028644 | 5.3044e-06 | 54
AEP-PSO | 2024 | 579031 | PARTIAL POWER | ERF | CONN/CLAMP | 4 | 4 | 381 | 0.000658 | 6.9081e-06 | 95.25
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OU | NONE | 7 | 2211 | 464458 | 0.82968 | 0.0039496 | 210.0669
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 6 | 24 | 2642 | 0.0047195 | 4.2872e-05 | 110.0833
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | WW | NONE | 5 | 1296 | 91983 | 0.15886 | 0.0022382 | 70.9745
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WFS | CONDUCTOR UG | 1 | 1 | 76 | 0.00013576 | 1.7863e-06 | 76
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 2 | 139 | 0.0002483 | 3.5727e-06 | 69.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 2 | 66 | 0.0001179 | 3.5727e-06 | 33
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | NONE | 456 | 9514 | 915178 | 1.5805 | 0.016431 | 96.1928
AEP-PSO | 2024 | 579031 | PARTIAL POWER | FO | NONE | 4 | 290 | 29635 | 0.05118 | 0.00050084 | 102.1897
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 2 | 1224 | 0.0021865 | 3.5727e-06 | 612
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | ARRESTER | 1 | 1 | 36 | 6.2173e-05 | 1.727e-06 | 36
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CO | CUTOUT | 1 | 2 | 182 | 0.00031432 | 3.454e-06 | 91
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 9 | 76 | 11765 | 0.020318 | 0.00013125 | 154.8026
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 7 | 132 | 25129 | 0.043398 | 0.00022797 | 190.3712
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERO | NONE | 1 | 1 | 56 | 9.6713e-05 | 1.727e-06 | 56
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 5 | 28 | 3605 | 0.0062259 | 4.8357e-05 | 128.75
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 2 | 376 | 0.00066482 | 3.5363e-06 | 188
AEP-PSO | 2020 | 559804 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 2 | 134 | 0.00023937 | 3.5727e-06 | 67
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WT | JUMPER/RISER | 1 | 1 | 192 | 0.00034298 | 1.7863e-06 | 192
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 40 | 6630 | 0.011843 | 7.1454e-05 | 165.75
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TR | POLE | 1 | 1 | 279 | 0.00049839 | 1.7863e-06 | 279
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WT | NONE | 1 | 1 | 123 | 0.00021242 | 1.727e-06 | 123
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 2 | 132 | 0.00023339 | 3.5363e-06 | 66
AEP-PSO | 2021 | 565565 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 38 | 6.7189e-05 | 1.7681e-06 | 38
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | U | BREAKER | 1 | 552 | 56304 | 0.099554 | 0.00097602 | 102
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 561 | 0.00096886 | 3.454e-06 | 280.5
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | TRANSFORMER, STATION SERVICE | 1 | 1 | 61 | 0.00010535 | 1.727e-06 | 61
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 6 | 546 | 0.00097534 | 1.0718e-05 | 91
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 124 | 26846 | 0.046364 | 0.00021415 | 216.5
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | PEDESTAL | 1 | 7 | 441 | 0.00076162 | 1.2089e-05 | 63
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 1 | 55 | 9.5993e-05 | 1.7453e-06 | 55
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | EQF | JUMPER/RISER | 1 | 441 | 26901 | 0.048054 | 0.00078778 | 61
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 10 | 1340 | 0.0023693 | 1.7681e-05 | 134
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | EQF | CROSSARM | 5 | 1170 | 192905 | 0.33668 | 0.002042 | 164.8761
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | BE | NONE | 1 | 44 | 1540 | 0.0027229 | 7.7798e-05 | 35
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 1795 | 315078 | 0.56284 | 0.0032065 | 175.5309
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | EQF | CROSSARM | 4 | 1143 | 144544 | 0.24963 | 0.001974 | 126.4602
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | PEDESTAL | 1 | 31 | 2666 | 0.0046531 | 5.4105e-05 | 86
AEP-PSO | 2024 | 579031 | GENERATION | G | NONE | 15 | 9275 | 814031 | 1.4059 | 0.016018 | 87.7661
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WI | POLE HARDWARE | 1 | 2 | 158 | 0.00027287 | 3.454e-06 | 79
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 651 | 23259 | 3072157 | 5.385 | 0.040769 | 132.0847
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CO | CONN/CLAMP | 101 | 191 | 11953 | 0.021135 | 0.00033772 | 62.5812
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | CROSSARM | 153 | 19094 | 2537491 | 4.4866 | 0.033761 | 132.8947
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | F | NONE | 38 | 1683 | 84172 | 0.14883 | 0.0029758 | 50.0131
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | INSULATOR | 43 | 5550 | 485477 | 0.85839 | 0.0098132 | 87.4733
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | CONN/CLAMP | 334 | 542 | 44088 | 0.078756 | 0.0009682 | 81.3432
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | CONN/CLAMP | 109 | 409 | 20159 | 0.036011 | 0.00073061 | 49.2885
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 4 | 27 | 4045 | 0.0072257 | 4.8231e-05 | 149.8148
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 38 | 187 | 24070 | 0.042559 | 0.00033064 | 128.7166
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | POLE | 9 | 3401 | 575207 | 1.017 | 0.0060135 | 169.1288
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | POLE | 2 | 12 | 2042 | 0.0035793 | 2.1034e-05 | 170.1667
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | O | FUSE | 6 | 32 | 1699 | 0.0029781 | 5.6091e-05 | 53.0938
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 11 | 191 | 11251 | 0.019721 | 0.00033479 | 58.9058
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | CROSSARM | 10 | 1496 | 171257 | 0.30019 | 0.0026223 | 114.4766
AEP-PSO | 2022 | 570502 | PARTIAL POWER | U | FUSE | 9 | 17 | 1158 | 0.0020298 | 2.9798e-05 | 68.1176
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 15 | 1312 | 0.0023198 | 2.6522e-05 | 87.4667
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | REGULATOR | 9 | 3876 | 327794 | 0.57457 | 0.006794 | 84.5702
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CO | JUMPER/RISER | 2 | 2 | 155 | 0.00027406 | 3.5363e-06 | 77.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | POLE | 4 | 22 | 1300 | 0.0022986 | 3.8899e-05 | 59.0909
AEP-PSO | 2023 | 572956 | PARTIAL POWER | ABI | NONE | 28 | 52 | 3012 | 0.0052569 | 9.0757e-05 | 57.9231
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 2 | 86 | 0.00015074 | 3.5057e-06 | 43
AEP-PSO | 2023 | 572956 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 45 | 87 | 14827 | 0.025878 | 0.00015184 | 170.4253
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 4 | 15 | 641 | 0.0011236 | 2.6293e-05 | 42.7333
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 1 | 1 | 79 | 0.00013788 | 1.7453e-06 | 79
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | NONE | 1721 | 89016 | 3548114 | 6.1277 | 0.15373 | 39.8593
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 1085 | 54250 | 0.095092 | 0.0019018 | 50
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 30 | 174 | 6732 | 0.01175 | 0.00030369 | 38.6897
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | U | NONE | 9 | 2877 | 92921 | 0.16599 | 0.0051393 | 32.2979
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 2 | 5735 | 91760 | 0.16224 | 0.01014 | 16
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 1 | 107 | 0.00018919 | 1.7681e-06 | 107
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | UB | NONE | 1 | 1 | 136 | 0.00024294 | 1.7863e-06 | 136
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CO | NONE | 4 | 4 | 391 | 0.00069846 | 7.1454e-06 | 97.75
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | INSULATOR | 12 | 1818 | 234743 | 0.40971 | 0.003173 | 129.1216
AEP-PSO | 2023 | 572956 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 1 | 13 | 609 | 0.0010629 | 2.2689e-05 | 46.8462
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 3 | 357 | 0.00062308 | 5.236e-06 | 119
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | WW | NONE | 10 | 2274 | 351970 | 0.61431 | 0.0039689 | 154.7801
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | WW | POLE | 5 | 1894 | 951872 | 1.6613 | 0.0033057 | 502.5723
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | TRANSFORMER, STATION SERVICE | 1 | 42 | 8232 | 0.014555 | 7.4262e-05 | 196
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 1 | 71 | 0.00012554 | 1.7681e-06 | 71
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | FO | NONE | 4 | 538 | 69106 | 0.12219 | 0.00095126 | 128.4498
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | CABLE TERMINATOR | 1 | 1 | 239 | 0.00042259 | 1.7681e-06 | 239
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | V | OTHER EQUIPMENT | 4 | 4836 | 618921 | 1.0849 | 0.0084767 | 127.982
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | METERING | 2 | 2 | 176 | 0.0003144 | 3.5727e-06 | 88
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | INSULATOR | 1 | 1 | 34 | 6.0736e-05 | 1.7863e-06 | 34
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 4 | 260 | 0.00045379 | 6.9813e-06 | 65
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | CONN/CLAMP | 7 | 32 | 7354 | 0.012701 | 5.5265e-05 | 229.8125
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | V | CIRCUIT SWITCHER | 2 | 1500 | 34320 | 0.060683 | 0.0026522 | 22.88
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WFS | NONE | 2 | 52 | 4167 | 0.0074437 | 9.289e-05 | 80.1346
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WW | NONE | 4 | 24 | 5123 | 0.0088475 | 4.1449e-05 | 213.4583
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERF | NONE | 19 | 3960 | 111196 | 0.19204 | 0.006839 | 28.0798
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 5 | 1636 | 147035 | 0.25393 | 0.0028254 | 89.8747
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WU | NONE | 6 | 8 | 2138 | 0.0036924 | 1.3816e-05 | 267.25
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | AF | NONE | 7 | 1481 | 95742 | 0.16535 | 0.0025577 | 64.6469
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 9 | 101 | 5876 | 0.010148 | 0.00017443 | 58.1782
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | CONN/CLAMP | 3 | 18 | 508 | 0.00087733 | 3.1086e-05 | 28.2222
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CO | SPLICE, OH | 2 | 5 | 279 | 0.00049331 | 8.8407e-06 | 55.8
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | STATIC WIRE | 7 | 2528 | 158758 | 0.2836 | 0.0045159 | 62.7998
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WW | CONN/CLAMP | 3 | 4 | 515 | 0.00088942 | 6.9081e-06 | 128.75
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WW | NONE | 6 | 54 | 6179 | 0.011038 | 9.6462e-05 | 114.4259
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 2 | 5 | 857 | 0.0014801 | 8.6351e-06 | 171.4
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | PEDESTAL | 6 | 21 | 3950 | 0.0068217 | 3.6267e-05 | 188.0952
AEP-PSO | 2020 | 559804 | PARTIAL POWER | OL | NONE | 1 | 1 | 91 | 0.00016256 | 1.7863e-06 | 91
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | TOR | NONE | 1 | 1026 | 42066 | 0.075144 | 0.0018328 | 41
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | SPLICE, OH | 1 | 8 | 1687 | 0.0030136 | 1.4291e-05 | 210.875
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 11 | 1043 | 0.0018204 | 1.9199e-05 | 94.8182
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | CABLE TERMINATOR | 3 | 3 | 575 | 0.0010271 | 5.359e-06 | 191.6667
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | ERF | NONE | 3 | 1802 | 16218 | 0.028971 | 0.003219 | 9
AEP-PSO | 2021 | 565565 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 114 | 0.00020157 | 1.7681e-06 | 114
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CE | FUSE | 1 | 7 | 336 | 0.00058028 | 1.2089e-05 | 48
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | R | BREAKER | 5 | 5897 | 218763 | 0.37781 | 0.010184 | 37.0973
AEP-PSO | 2025 | 579031 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 2 | 98 | 0.00016925 | 3.454e-06 | 49
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 4 | 1251 | 109305 | 0.18877 | 0.0021605 | 87.3741
AEP-PSO | 2024 | 579031 | PARTIAL POWER | U | SPLICE, UG | 1 | 1 | 119 | 0.00020552 | 1.727e-06 | 119
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 1 | 24 | 4.2872e-05 | 1.7863e-06 | 24
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 34 | 2235 | 0.0038599 | 5.8719e-05 | 65.7353
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WI | ARRESTER | 1 | 3 | 345 | 0.00059582 | 5.1811e-06 | 115
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | F | POLE | 1 | 240 | 47040 | 0.083173 | 0.00042435 | 196
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 4 | 141 | 0.00024715 | 7.0114e-06 | 35.25
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | SWITCH, OH | 14 | 4952 | 497245 | 0.87159 | 0.0086801 | 100.413
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | CUTOUT | 20 | 62 | 4736 | 0.0084601 | 0.00011075 | 76.3871
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | WW | NONE | 1 | 248 | 99696 | 0.17809 | 0.00044301 | 402
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 2 | 84 | 0.00014852 | 3.5363e-06 | 42
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 145 | 20445 | 0.03615 | 0.00025638 | 141
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | WL | FUSE | 2 | 2 | 479 | 0.00084694 | 3.5363e-06 | 239.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WH | NONE | 1 | 2 | 70 | 0.00012377 | 3.5363e-06 | 35
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | FUSE | 3 | 71 | 10490 | 0.018548 | 0.00012554 | 147.7465
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 369 | 2160 | 355181 | 0.61991 | 0.0037699 | 164.4356
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WT | METERING | 1 | 1 | 217 | 0.00038369 | 1.7681e-06 | 217
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 8 | 2432 | 0.0043001 | 1.4145e-05 | 304
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | INSULATOR | 57 | 8608 | 799551 | 1.4283 | 0.015377 | 92.8846
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 1 | 58 | 0.00010255 | 1.7681e-06 | 58
AEP-PSO | 2021 | 565565 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 1 | 33 | 5.8349e-05 | 1.7681e-06 | 33
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 39 | 6.8361e-05 | 1.7528e-06 | 39
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | CUTOUT | 4 | 44 | 5642 | 0.010079 | 7.8599e-05 | 128.2273
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | FUSE | 20 | 33 | 2645 | 0.0047249 | 5.8949e-05 | 80.1515
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 30 | 2870 | 302735 | 0.52837 | 0.0050091 | 105.4826
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 29 | 463 | 0.00080809 | 5.0615e-05 | 15.9655
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | POLE | 43 | 811 | 150006 | 0.26181 | 0.0014155 | 184.9642
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | CROSSARM | 1 | 1 | 366 | 0.00064154 | 1.7528e-06 | 366
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | POLE | 16 | 1409 | 218015 | 0.38051 | 0.0024592 | 154.7303
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 5 | 13 | 2405 | 0.0041975 | 2.2689e-05 | 185
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 21 | 3422 | 0.0060506 | 3.7131e-05 | 162.9524
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | FUSE | 62 | 220 | 12589 | 0.021741 | 0.00037995 | 57.2227
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | FW | NONE | 6 | 1820 | 36941 | 0.065317 | 0.003218 | 20.2973
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 8 | 1194 | 36709 | 0.064069 | 0.0020839 | 30.7446
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | POLE | 1 | 2 | 30 | 5.236e-05 | 3.4907e-06 | 15
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 9 | 1540 | 0.0026878 | 1.5708e-05 | 171.1111
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 3 | 19 | 6131 | 0.010701 | 3.3161e-05 | 322.6842
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 5 | 12 | 3341 | 0.00577 | 2.0724e-05 | 278.4167
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | PEDESTAL | 1 | 3 | 465 | 0.00083065 | 5.359e-06 | 155
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | PEDESTAL | 11 | 86 | 3321 | 0.0059324 | 0.00015363 | 38.6163
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | CUTOUT | 1 | 30 | 990 | 0.0017685 | 5.359e-05 | 33
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 1 | 761 | 0.0013143 | 1.727e-06 | 761
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 188 | 5284 | 546691 | 0.94415 | 0.0091256 | 103.4616
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | EQF | BREAKER | 1 | 558 | 81468 | 0.14219 | 0.0009739 | 146
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | NONE | 145 | 9469 | 788571 | 1.3619 | 0.016353 | 83.2792
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WT | POLE HARDWARE | 1 | 28 | 7756 | 0.013395 | 4.8357e-05 | 277
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 229 | 0.00039549 | 3.454e-06 | 114.5
AEP-PSO | 2024 | 579031 | PARTIAL POWER | FW | CONN/CLAMP | 1 | 1 | 43 | 7.4262e-05 | 1.727e-06 | 43
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 1 | 38 | 6.7881e-05 | 1.7863e-06 | 38
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 5 | 18 | 3444 | 0.0061522 | 3.2154e-05 | 191.3333
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | EQF | MOAB | 2 | 692 | 90652 | 0.16029 | 0.0012236 | 131
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TR | NONE | 1 | 1 | 53 | 9.4676e-05 | 1.7863e-06 | 53
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | EQF | RELAY | 4 | 1596 | 22198 | 0.038336 | 0.0027563 | 13.9085
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | ABI | MOAB | 4 | 1533 | 22995 | 0.040658 | 0.0027106 | 15
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WFS | POLE | 1 | 2 | 420 | 0.00074262 | 3.5363e-06 | 210
AEP-PSO | 2022 | 570502 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 35 | 6.1349e-05 | 1.7528e-06 | 35
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 366 | 40352 | 0.070731 | 0.00064154 | 110.2514
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 2 | 140 | 0.0002454 | 3.5057e-06 | 70
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 33 | 5709 | 0.010094 | 5.8349e-05 | 173
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | CABLE TERMINATOR | 3 | 958 | 68038 | 0.1203 | 0.0016939 | 71.0209
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 1 | 1 | 72 | 0.00012731 | 1.7681e-06 | 72
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 290 | 15080 | 0.026938 | 0.00051804 | 52
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 77 | 0.00013755 | 1.7863e-06 | 77
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 52 | 2804 | 0.0050089 | 9.289e-05 | 53.9231
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 5 | 2429 | 0.0041949 | 8.6351e-06 | 485.8
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 8 | 72 | 0.00012862 | 1.4291e-05 | 9
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | WI | NONE | 2 | 1080 | 104760 | 0.18092 | 0.0018652 | 97
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | SPLICE, OH | 1 | 1 | 126 | 0.00022508 | 1.7863e-06 | 126
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | CROSSARM | 1 | 12 | 558 | 0.00096368 | 2.0724e-05 | 46.5
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 7 | 517 | 0.00089287 | 1.2089e-05 | 73.8571
AEP-PSO | 2024 | 579031 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 1 | 185 | 0.0003195 | 1.727e-06 | 185
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | EQF | BREAKER | 4 | 1702 | 529658 | 0.91473 | 0.0029394 | 311.1974
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 15 | 2775 | 0.0048433 | 2.618e-05 | 185
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 10 | 60 | 0.00010362 | 1.727e-05 | 6
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TIR | POLE | 1 | 57 | 4748 | 0.0081999 | 9.844e-05 | 83.2982
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | CONN/CLAMP | 7 | 10 | 1130 | 0.0019807 | 1.7528e-05 | 113
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | CUTOUT | 32 | 2302 | 301836 | 0.52907 | 0.004035 | 131.119
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | ARRESTER | 149 | 11324 | 1329085 | 2.35 | 0.020022 | 117.3689
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 22 | 4221 | 117495 | 0.20595 | 0.0073987 | 27.8358
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | JUMPER/RISER | 19 | 47 | 7497 | 0.013392 | 8.3958e-05 | 159.5106
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | ARRESTER | 2 | 3 | 227 | 0.00040137 | 5.3044e-06 | 75.6667
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | NONE | 51 | 13498 | 582249 | 1.0295 | 0.023866 | 43.1359
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 28 | 4646 | 505123 | 0.89313 | 0.0082148 | 108.7221
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 3 | 183 | 0.00032077 | 5.2585e-06 | 61
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | POLE | 23 | 461 | 178960 | 0.31235 | 0.0008046 | 388.1996
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | CROSSARM | 160 | 28044 | 2834518 | 4.8953 | 0.048433 | 101.074
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | NONE | 3690 | 34910 | 2055911 | 3.5506 | 0.06029 | 58.8918
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | POLE HARDWARE | 4 | 124 | 13767 | 0.023776 | 0.00021415 | 111.0242
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | WU | NONE | 37 | 6147 | 511273 | 0.89234 | 0.010729 | 83.1744
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 29 | 2594 | 212023 | 0.37875 | 0.0046338 | 81.7359
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 3 | 614 | 0.0010762 | 5.2585e-06 | 204.6667
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CF | CROSSARM | 1 | 469 | 21574 | 0.038146 | 0.00082926 | 46
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WFS | NONE | 1 | 1 | 394 | 0.00069665 | 1.7681e-06 | 394
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 3 | 525 | 0.00093783 | 5.359e-06 | 175
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CE | METERING | 2 | 6 | 346 | 0.00061178 | 1.0609e-05 | 57.6667
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | METERING | 4 | 4 | 783 | 0.0013666 | 6.9813e-06 | 195.75
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 824 | 97145 | 0.16955 | 0.0014382 | 117.8944
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | INSULATOR | 39 | 5927 | 525816 | 0.9081 | 0.010236 | 88.7154
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | ERF | GUY/ANCHOR | 1 | 213 | 159111 | 0.28133 | 0.00037661 | 747
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 4 | 844 | 0.0014731 | 6.9813e-06 | 211
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | U | NONE | 5 | 1151 | 88843 | 0.15506 | 0.0020089 | 77.1877
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | CROSSARM | 8 | 71 | 2646 | 0.0047267 | 0.00012683 | 37.2676
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | POLE | 23 | 205 | 28088 | 0.048509 | 0.00035404 | 137.0146
AEP-PSO | 2023 | 572956 | PARTIAL POWER | OL | CUTOUT | 1 | 1 | 212 | 0.00037001 | 1.7453e-06 | 212
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 1982 | 151356 | 0.27037 | 0.0035405 | 76.3653
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | V | NONE | 1 | 795 | 27825 | 0.049705 | 0.0014201 | 35
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | ARRESTER | 3 | 4 | 49 | 8.5521e-05 | 6.9813e-06 | 12.25
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | INSULATOR | 2 | 191 | 25441 | 0.044403 | 0.00033336 | 133.199
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 3161 | 342212 | 0.59727 | 0.005517 | 108.2607
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 1 | 147 | 0.00025656 | 1.7453e-06 | 147
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 1 | 156 | 0.00027583 | 1.7681e-06 | 156
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 46 | 9108 | 0.01627 | 8.2172e-05 | 198
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 2674 | 236176 | 0.42189 | 0.0047767 | 88.3231
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | ARRESTER | 2 | 37 | 1930 | 0.0034125 | 6.5421e-05 | 52.1622
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ABI | NONE | 21 | 180 | 10416 | 0.017989 | 0.00031086 | 57.8667
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | CONN/CLAMP | 10 | 27 | 1711 | 0.0029549 | 4.663e-05 | 63.3704
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | CAPACITOR | 1 | 360 | 42120 | 0.072742 | 0.00062173 | 117
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | POLE | 2 | 8 | 315 | 0.0005627 | 1.4291e-05 | 39.375
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 1 | 76 | 0.00013125 | 1.727e-06 | 76
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | INSULATOR | 7 | 1202 | 162726 | 0.28103 | 0.0020759 | 135.3794
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | V | NONE | 7 | 14 | 1376 | 0.0023764 | 2.4178e-05 | 98.2857
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1302 | 114021 | 0.20368 | 0.0023258 | 87.5737
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CF | NONE | 1 | 2 | 52 | 9.1943e-05 | 3.5363e-06 | 26
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 2 | 117 | 12010 | 0.021454 | 0.000209 | 102.6496
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | WU | CONDUCTOR OVERHEAD | 2 | 284 | 63808 | 0.11185 | 0.00049781 | 224.6761
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | BREAKER | 1 | 504 | 31248 | 0.05582 | 0.00090032 | 62
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | F | POLE | 1 | 46 | 14966 | 0.026462 | 8.1335e-05 | 325.3478
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 8 | 651 | 0.0011243 | 1.3816e-05 | 81.375
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | JUMPER/RISER | 5 | 72 | 9128 | 0.015764 | 0.00012435 | 126.7778
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OU | POLE | 1 | 3 | 132 | 0.0002358 | 5.359e-06 | 44
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CF | NONE | 2 | 29 | 2807 | 0.0048478 | 5.0084e-05 | 96.7931
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | CROSSARM | 1 | 6 | 1536 | 0.0026924 | 1.0517e-05 | 256
AEP-PSO | 2023 | 572956 | PARTIAL POWER | A | CONN/CLAMP | 1 | 1 | 34 | 5.9341e-05 | 1.7453e-06 | 34
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WT | POLE | 2 | 2601 | 1183546 | 2.1142 | 0.0046463 | 455.035
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 35 | 4270 | 0.0076277 | 6.2522e-05 | 122
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | CROSSARM | 1 | 2 | 178 | 0.00030741 | 3.454e-06 | 89
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | CO | NONE | 1 | 408 | 7344 | 0.013119 | 0.00072883 | 18
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 17 | 465 | 0.00080307 | 2.9359e-05 | 27.3529
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TR | POLE HARDWARE | 1 | 180 | 35504 | 0.062776 | 0.00031827 | 197.2444
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 176 | 10544 | 0.01821 | 0.00030396 | 59.9091
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TR | FUSE | 2 | 7 | 580 | 0.0010017 | 1.2089e-05 | 82.8571
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 4 | 4 | 889 | 0.0015516 | 6.9813e-06 | 222.25
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 2 | 862 | 0.0014887 | 3.454e-06 | 431
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 6 | 150 | 0.00026795 | 1.0718e-05 | 25
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | FO | NONE | 9 | 3401 | 144657 | 0.24983 | 0.0058736 | 42.5337
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 74 | 5402 | 0.0093294 | 0.0001278 | 73
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | EQF | RELAY | 1 | 377 | 3393 | 0.0059219 | 0.00065799 | 9
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 1 | 1 | 65 | 0.00011226 | 1.727e-06 | 65
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | OL | NONE | 4 | 518 | 61642 | 0.11011 | 0.00092532 | 119
AEP-PSO | 2021 | 565565 | PARTIAL POWER | U | NONE | 150 | 328 | 31706 | 0.056061 | 0.00057995 | 96.6646
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | FUSE | 106 | 1231 | 102793 | 0.18018 | 0.0021577 | 83.5037
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 70 | 239 | 43991 | 0.078583 | 0.00042694 | 184.0628
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | CONDUCTOR UG | 293 | 434 | 66626 | 0.11902 | 0.00077527 | 153.5161
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | METERING | 66 | 142 | 14385 | 0.025696 | 0.00025366 | 101.3028
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | CUTOUT | 268 | 5457 | 635141 | 1.1346 | 0.0097481 | 116.3901
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WI | NONE | 6 | 24 | 1529 | 0.0026801 | 4.2068e-05 | 63.7083
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | TRANSFORMER, OH | 20 | 38 | 7847 | 0.013875 | 6.7189e-05 | 206.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ABI | FUSE | 11 | 157 | 18891 | 0.033113 | 0.0002752 | 120.3248
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 1241 | 165282 | 0.28971 | 0.0021753 | 133.1845
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FO | NONE | 31 | 3377 | 279950 | 0.49071 | 0.0059193 | 82.899
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | ARRESTER | 1 | 1113 | 170289 | 0.30419 | 0.0019882 | 153
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | NONE | 82 | 9466 | 1043045 | 1.8632 | 0.016909 | 110.1886
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | CUTOUT | 3 | 12 | 1163 | 0.0020564 | 2.1218e-05 | 96.9167
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 28 | 64 | 6123 | 0.010826 | 0.00011316 | 95.6719
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | ARRESTER | 145 | 6095 | 506737 | 0.88443 | 0.010638 | 83.1398
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | SPLICE, UG | 9 | 214 | 20733 | 0.036659 | 0.00037838 | 96.8832
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | INSULATOR | 4 | 19 | 297 | 0.00052059 | 3.3304e-05 | 15.6316
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 1 | 133 | 0.00023313 | 1.7528e-06 | 133
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | JUMPER/RISER | 2 | 36 | 1782 | 0.0031236 | 6.3102e-05 | 49.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | V | NONE | 3 | 2272 | 199318 | 0.34937 | 0.0039825 | 87.728
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 2 | 15 | 3042 | 0.0053787 | 2.6522e-05 | 202.8
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | TIR | NONE | 2 | 607 | 159570 | 0.2797 | 0.001064 | 262.883
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 2213 | 480585 | 0.84974 | 0.0039129 | 217.1645
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 1 | 546 | 0.00096541 | 1.7681e-06 | 546
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | POLE HARDWARE | 2 | 4 | 282 | 0.0004943 | 7.0114e-06 | 70.5
AEP-PSO | 2020 | 559804 | PARTIAL POWER | VIN | SPLICE, OH | 1 | 1 | 104 | 0.00018578 | 1.7863e-06 | 104
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 591 | 25853 | 0.045122 | 0.0010315 | 43.7445
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | JUMPER/RISER | 6 | 51 | 13696 | 0.024466 | 9.1103e-05 | 268.549
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | CUTOUT | 5 | 88 | 15476 | 0.027011 | 0.00015359 | 175.8636
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 3 | 22 | 795 | 0.0013875 | 3.8397e-05 | 36.1364
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WU | FUSE | 4 | 9 | 493 | 0.00086045 | 1.5708e-05 | 54.7778
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 131 | 265 | 27951 | 0.048272 | 0.00045766 | 105.4755
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TR | NONE | 3 | 3 | 135 | 0.00023663 | 5.2585e-06 | 45
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | RECLOSER, LINE/OCR/BR | 4 | 1501 | 193941 | 0.34644 | 0.0026813 | 129.2079
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FO | FUSE | 8 | 111 | 8198 | 0.014158 | 0.0001917 | 73.8559
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | R | BREAKER | 1 | 341 | 65472 | 0.11696 | 0.00060914 | 192
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | WL | NONE | 26 | 5351 | 389507 | 0.67982 | 0.0093393 | 72.7914
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 29 | 1587 | 50136 | 0.086586 | 0.0027408 | 31.5917
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 4 | 43 | 7063 | 0.012327 | 7.5049e-05 | 164.2558
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CE | POLE | 1 | 5 | 965 | 0.0017063 | 8.8407e-06 | 193
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 2 | 163 | 0.00028449 | 3.4907e-06 | 81.5
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 31 | 3360 | 783187 | 1.3669 | 0.0058643 | 233.0914
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 17 | 2221 | 0.0038357 | 2.9359e-05 | 130.6471
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | AB | NONE | 11 | 11119 | 523211 | 0.93463 | 0.019862 | 47.0556
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 2 | 148 | 0.00026438 | 3.5727e-06 | 74
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | FUSE | 38 | 883 | 196342 | 0.33909 | 0.001525 | 222.3579
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 18 | 212 | 71143 | 0.12287 | 0.00036613 | 335.5802
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WL | SPLICE, UG | 1 | 1 | 40 | 6.9081e-05 | 1.727e-06 | 40
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CE | NONE | 5 | 16 | 682 | 0.0011778 | 2.7632e-05 | 42.625
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 72 | 0.00012435 | 1.727e-06 | 72
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | MOAB | 1 | 180 | 10800 | 0.019096 | 0.00031827 | 60
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | ARRESTER | 6 | 1795 | 432878 | 0.74759 | 0.0031 | 241.1577
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 15 | 935 | 0.0016532 | 2.6522e-05 | 62.3333
AEP-PSO | 2020 | 559804 | PARTIAL POWER | V | NONE | 1 | 1 | 57 | 0.00010182 | 1.7863e-06 | 57
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | AF | CROSSARM | 1 | 257 | 15163 | 0.026578 | 0.00045048 | 59
AEP-PSO | 2024 | 579031 | PARTIAL POWER | U | ARRESTER | 1 | 1 | 126 | 0.0002176 | 1.727e-06 | 126
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 4 | 19 | 1508 | 0.0026044 | 3.2813e-05 | 79.3684
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 3 | 380 | 0.00065627 | 5.1811e-06 | 126.6667
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 266 | 21014 | 0.036292 | 0.00045939 | 79
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | O | FUSE | 1 | 7 | 322 | 0.0005561 | 1.2089e-05 | 46
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | ERF | NONE | 10 | 3960 | 245113 | 0.43786 | 0.0070739 | 61.8972
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 3 | 71 | 2571 | 0.0044402 | 0.00012262 | 36.2113
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | CABLE TERMINATOR | 1 | 1 | 9 | 1.5776e-05 | 1.7528e-06 | 9
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 3 | 51 | 1342 | 0.0023177 | 8.8078e-05 | 26.3137
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 3 | 8 | 515 | 0.00091059 | 1.4145e-05 | 64.375
AEP-PSO | 2020 | 559804 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 4 | 40 | 7.1454e-05 | 7.1454e-06 | 10
AEP-PSO | 2020 | 559804 | PARTIAL POWER | ABI | FUSE | 2 | 3 | 97 | 0.00017327 | 5.359e-06 | 32.3333
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | BREAKER | 1 | 581 | 8134 | 0.01453 | 0.0010379 | 14
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | FUSE | 2 | 4 | 256 | 0.0004573 | 7.1454e-06 | 64
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WI | NONE | 2 | 4 | 563 | 0.0010057 | 7.1454e-06 | 140.75
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 85 | 0.0001468 | 1.727e-06 | 85
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 643 | 48947 | 0.084533 | 0.0011105 | 76.1229
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1 | 26 | 4.4903e-05 | 1.727e-06 | 26
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | WL | SWITCH, OH | 1 | 5 | 2020 | 0.0036084 | 8.9317e-06 | 404
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | WU | ARRESTER | 1 | 122 | 2318 | 0.0040986 | 0.00021571 | 19
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 8 | 1664 | 0.0028738 | 1.3816e-05 | 208
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | EQF | SWITCH, OH | 5 | 1212 | 474274 | 0.81908 | 0.0020932 | 391.3152
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 28 | 4.8869e-05 | 1.7453e-06 | 28
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | CONDUCTOR UG | 316 | 463 | 59586 | 0.10444 | 0.00081157 | 128.6955
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | JUMPER/RISER | 28 | 193 | 12772 | 0.022387 | 0.0003383 | 66.1762
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | POLE | 31 | 5396 | 1040086 | 1.8231 | 0.0094583 | 192.7513
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | FUSE | 170 | 1003 | 57370 | 0.10144 | 0.0017734 | 57.1984
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | CE | ARRESTER | 4 | 2771 | 189509 | 0.33218 | 0.0048571 | 68.3901
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 1 | 20 | 3.5057e-05 | 1.7528e-06 | 20
AEP-PSO | 2022 | 570502 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 3 | 312 | 0.00054689 | 5.2585e-06 | 104
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | FUSE | 5 | 59 | 3398 | 0.00607 | 0.00010539 | 57.5932
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | POLE | 7 | 263 | 134871 | 0.24093 | 0.00046981 | 512.8175
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 2 | 8 | 1636 | 0.0028927 | 1.4145e-05 | 204.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | CROSSARM | 3 | 55 | 36299 | 0.064182 | 9.7248e-05 | 659.9818
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 19 | 312 | 8233 | 0.014557 | 0.00055166 | 26.3878
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | POLE | 5 | 1796 | 101102 | 0.1806 | 0.0032083 | 56.2929
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 8 | 19 | 1880 | 0.0033241 | 3.3595e-05 | 98.9474
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CE | CABLE TERMINATOR | 1 | 42 | 8148 | 0.014282 | 7.3619e-05 | 194
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 2 | 2512 | 203472 | 0.36347 | 0.0044873 | 81
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OL | NONE | 18 | 2952 | 333672 | 0.59605 | 0.0052733 | 113.0325
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | V | NONE | 11 | 13023 | 253082 | 0.44749 | 0.023027 | 19.4335
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | NONE | 1971 | 43108 | 6281655 | 10.9636 | 0.075238 | 145.719
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 2 | 5 | 455 | 0.00079413 | 8.7267e-06 | 91
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | POLE | 3 | 79 | 16830 | 0.029374 | 0.00013788 | 213.038
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 3 | 203 | 0.00035583 | 5.2585e-06 | 67.6667
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | CF | NONE | 7 | 45 | 3094 | 0.0054706 | 7.9566e-05 | 68.7556
AEP-PSO | 2020 | 559804 | PARTIAL POWER | FO | NONE | 5 | 27 | 947 | 0.0016917 | 4.8231e-05 | 35.0741
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | POLE | 29 | 5668 | 1467552 | 2.5345 | 0.0097888 | 258.9188
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 76 | 5456 | 1364968 | 2.3573 | 0.0094226 | 250.1774
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | NONE | 131 | 15476 | 3127450 | 5.4012 | 0.026727 | 202.0839
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | SWITCH, UG | 5 | 2027 | 345476 | 0.59665 | 0.0035007 | 170.4371
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 5 | 59 | 5455 | 0.0097445 | 0.00010539 | 92.4576
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 91 | 0.00016256 | 1.7863e-06 | 91
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 1 | 52 | 9.0757e-05 | 1.7453e-06 | 52
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | CUTOUT | 88 | 3616 | 395894 | 0.68372 | 0.0062449 | 109.484
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | NONE | 56 | 1216 | 71706 | 0.12384 | 0.0021001 | 58.9688
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | JUMPER/RISER | 44 | 424 | 85030 | 0.14685 | 0.00073226 | 200.5425
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | FUSE | 81 | 972 | 76400 | 0.13194 | 0.0016787 | 78.6008
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | POLE | 5 | 251 | 47656 | 0.082303 | 0.00043348 | 189.8645
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 6 | 60 | 12241 | 0.02114 | 0.00010362 | 204.0167
AEP-PSO | 2025 | 579031 | PARTIAL POWER | OL | NONE | 1 | 1 | 166 | 0.00028669 | 1.727e-06 | 166
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | FUSE | 3 | 5 | 393 | 0.00067872 | 8.6351e-06 | 78.6
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 1 | 186 | 0.00032123 | 1.727e-06 | 186
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | TRANSFORMER, GROUNDING | 1 | 1 | 36 | 6.3102e-05 | 1.7528e-06 | 36
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | ERF | NONE | 3 | 626 | 4530 | 0.0079064 | 0.0010926 | 7.2364
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 38 | 2888 | 0.0051589 | 6.7881e-05 | 76
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | WL | NONE | 2 | 401 | 54268 | 0.096941 | 0.00071632 | 135.3317
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 146 | 0.00026081 | 1.7863e-06 | 146
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 2 | 51 | 13890 | 0.02456 | 9.0175e-05 | 272.3529
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | GC | NONE | 7 | 1201 | 404947 | 0.69935 | 0.0020742 | 337.1749
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 18 | 1166 | 0.0020137 | 3.1086e-05 | 64.7778
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 6 | 1430 | 0.0025545 | 1.0718e-05 | 238.3333
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 6 | 253 | 44378 | 0.076642 | 0.00043694 | 175.4071
AEP-PSO | 2025 | 579031 | TRANSMISSION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 1171 | 47719 | 0.082412 | 0.0020223 | 40.7506
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CF | NONE | 1 | 1 | 72 | 0.00012862 | 1.7863e-06 | 72
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 50 | 5850 | 0.010103 | 8.6351e-05 | 117
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 4 | 29 | 1886 | 0.0033347 | 5.1276e-05 | 65.0345
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | METERING | 3 | 3 | 176 | 0.00031119 | 5.3044e-06 | 58.6667
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CE | NONE | 7 | 52 | 2662 | 0.0047552 | 9.289e-05 | 51.1923
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 44 | 3502 | 635240 | 1.1348 | 0.0062558 | 181.3935
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | POLE | 35 | 6051 | 1565674 | 2.7683 | 0.010699 | 258.7463
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 31 | 5558 | 0.0098273 | 5.4812e-05 | 179.2903
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | FUSE | 4 | 22 | 1258 | 0.0022051 | 3.8563e-05 | 57.1818
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | WL | FUSE | 1 | 211 | 47686 | 0.083586 | 0.00036985 | 226
AEP-PSO | 2021 | 565565 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 1 | 91 | 0.0001609 | 1.7681e-06 | 91
AEP-PSO | 2022 | 570502 | PARTIAL POWER | A | METERING | 1 | 1 | 148 | 0.00025942 | 1.7528e-06 | 148
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WL | ARRESTER | 2 | 2 | 101 | 0.00017704 | 3.5057e-06 | 50.5
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WL | NONE | 86 | 265 | 43654 | 0.076191 | 0.00046251 | 164.7321
AEP-PSO | 2020 | 559804 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 2 | 6 | 1181 | 0.0021097 | 1.0718e-05 | 196.8333
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 6 | 662 | 14823 | 0.025982 | 0.0011604 | 22.3912
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TR | POLE | 1 | 3 | 1020 | 0.0017879 | 5.2585e-06 | 340
AEP-PSO | 2023 | 572956 | PARTIAL POWER | A | NONE | 85 | 180 | 10488 | 0.018305 | 0.00031416 | 58.2667
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | R | BREAKER | 1 | 587 | 75723 | 0.13273 | 0.0010289 | 129
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FO | NONE | 33 | 1382 | 123337 | 0.21526 | 0.0024121 | 89.2453
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 171 | 12312 | 0.021581 | 0.00029974 | 72
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 509 | 21422 | 2950362 | 5.0953 | 0.036996 | 137.7258
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | METERING | 25 | 26 | 3066 | 0.0053512 | 4.5379e-05 | 117.9231
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 18 | 340 | 74470 | 0.12861 | 0.00058719 | 219.0294
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | FUSE | 248 | 1824 | 107815 | 0.1862 | 0.0031501 | 59.1091
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | FUSE | 767 | 4670 | 314945 | 0.54392 | 0.0080652 | 67.44
AEP-PSO | 2020 | 559804 | PARTIAL POWER | U | FUSE | 2 | 2 | 215 | 0.00038406 | 3.5727e-06 | 107.5
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | PEDESTAL | 1 | 2 | 140 | 0.00025009 | 3.5727e-06 | 70
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | CONN/CLAMP | 10 | 43 | 1450 | 0.0025307 | 7.5049e-05 | 33.7209
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 1 | 20 | 3.5363e-05 | 1.7681e-06 | 20
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 7 | 1756 | 63819 | 0.11022 | 0.0030327 | 36.3434
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | ARRESTER | 1 | 389 | 8491 | 0.014664 | 0.00067181 | 21.8278
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 41 | 105 | 7128 | 0.012733 | 0.00018757 | 67.8857
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 1103 | 103916 | 0.18137 | 0.0019251 | 94.2121
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 10 | 1472 | 152579 | 0.2663 | 0.0025691 | 103.6542
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 6 | 6 | 537 | 0.00093724 | 1.0472e-05 | 89.5
AEP-PSO | 2022 | 570502 | PARTIAL POWER | O | TRANSFORMER, OH | 1 | 2 | 174 | 0.00030499 | 3.5057e-06 | 87
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | POLE | 1 | 2 | 70 | 0.0001227 | 3.5057e-06 | 35
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | WI | NONE | 4 | 5780 | 1161780 | 2.0364 | 0.010131 | 201
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WI | FUSE | 1 | 1 | 245 | 0.00042761 | 1.7453e-06 | 245
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 13 | 559 | 0.00098839 | 2.2986e-05 | 43
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 2 | 22 | 3984 | 0.0070443 | 3.8899e-05 | 181.0909
AEP-PSO | 2020 | 559804 | PARTIAL POWER | FO | CUTOUT | 1 | 2 | 30 | 5.359e-05 | 3.5727e-06 | 15
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WL | TRANSFORMER, UG | 1 | 2 | 536 | 0.00095748 | 3.5727e-06 | 268
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 240 | 5492 | 731874 | 1.264 | 0.0094848 | 133.2618
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 125 | 1045 | 193689 | 0.33451 | 0.0018047 | 185.3483
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | CONN/CLAMP | 5 | 19 | 802 | 0.0013851 | 3.2813e-05 | 42.2105
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 20 | 715 | 0.0012348 | 3.454e-05 | 35.75
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | JUMPER/RISER | 5 | 42 | 4099 | 0.0070791 | 7.2535e-05 | 97.5952
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 963 | 88608 | 0.15303 | 0.0016631 | 92.0125
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 13 | 955 | 0.001706 | 2.3222e-05 | 73.4615
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | CROSSARM | 4 | 63 | 12314 | 0.021267 | 0.0001088 | 195.4603
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 73 | 7041 | 0.01216 | 0.00012607 | 96.4521
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 6 | 28 | 1362 | 0.0023522 | 4.8357e-05 | 48.6429
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | ERF | NONE | 3 | 2881 | 386237 | 0.68995 | 0.0051464 | 134.0635
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 8 | 872 | 0.0015577 | 1.4291e-05 | 109
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | AB | NONE | 5 | 2676 | 332897 | 0.57492 | 0.0046215 | 124.401
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 1 | 59 | 0.00010432 | 1.7681e-06 | 59
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | CABLE TERMINATOR | 1 | 2 | 198 | 0.0003537 | 3.5727e-06 | 99
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WL | CUTOUT | 3 | 5 | 771 | 0.0013773 | 8.9317e-06 | 154.2
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 1 | 67 | 2479 | 0.0043832 | 0.00011847 | 37
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | CUTOUT | 1 | 4 | 88 | 0.0001556 | 7.0726e-06 | 22
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1918 | 157276 | 0.27162 | 0.0033124 | 82
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 33 | 33330 | 0.057562 | 5.6992e-05 | 1010
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 5 | 730 | 0.0012607 | 8.6351e-06 | 146
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OU | POLE | 2 | 17 | 1153 | 0.0020124 | 2.9671e-05 | 67.8235
AEP-PSO | 2025 | 579031 | DISTRIBUTION STATION | U | NONE | 6 | 5740 | 253855 | 0.43841 | 0.0099131 | 44.2256
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | AB | NONE | 4 | 3852 | 200550 | 0.35003 | 0.006723 | 52.0639
AEP-PSO | 2024 | 579031 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 220 | 0.00037995 | 1.727e-06 | 220
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 2 | 3 | 341 | 0.00058891 | 5.1811e-06 | 113.6667
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WL | CONDUCTOR UG | 1 | 1 | 285 | 0.0004922 | 1.727e-06 | 285
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | VIN | TRANSFORMER, UG | 1 | 1 | 331 | 0.00058019 | 1.7528e-06 | 331
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FO | NONE | 32 | 2563 | 117298 | 0.20953 | 0.0045784 | 45.7659
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 43 | 51 | 12865 | 0.022747 | 9.0175e-05 | 252.2549
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 3 | 68 | 0.00012147 | 5.359e-06 | 22.6667
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | CONN/CLAMP | 4 | 12 | 4384 | 0.0078313 | 2.1436e-05 | 365.3333
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | WU | FUSE | 1 | 246 | 21156 | 0.037083 | 0.0004312 | 86
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | V | ARRESTER | 1 | 2 | 92 | 0.00016126 | 3.5057e-06 | 46
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 25 | 12565 | 0.022024 | 4.3821e-05 | 502.6
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | WU | NONE | 7 | 2787 | 172444 | 0.30491 | 0.0049278 | 61.8744
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | NONE | 334 | 12252 | 1704470 | 2.9749 | 0.021384 | 139.1177
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | NONE | 409 | 21401 | 2094026 | 3.6548 | 0.037352 | 97.8471
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | JUMPER/RISER | 4 | 41 | 11029 | 0.019332 | 7.1867e-05 | 269
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | WI | POLE | 9 | 1588 | 154146 | 0.27019 | 0.0027835 | 97.0693
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ABI | FUSE | 9 | 27 | 2165 | 0.0037786 | 4.7124e-05 | 80.1852
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | ARRESTER | 124 | 7589 | 585877 | 1.0118 | 0.013106 | 77.2008
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 2 | 163 | 0.00028821 | 3.5363e-06 | 81.5
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 13 | 822 | 31224 | 0.054496 | 0.0014347 | 37.9854
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | VIN | FUSE | 2 | 3 | 245 | 0.00043765 | 5.359e-06 | 81.6667
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 4 | 12 | 435 | 0.00075922 | 2.0944e-05 | 36.25
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | F | NONE | 1 | 19 | 1178 | 0.002056 | 3.3161e-05 | 62
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 114 | 0.00019897 | 1.7453e-06 | 114
AEP-PSO | 2022 | 570502 | PARTIAL POWER | ERF | CONN/CLAMP | 3 | 13 | 1066 | 0.0018685 | 2.2787e-05 | 82
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | V | NONE | 39 | 1278 | 179953 | 0.31078 | 0.0022071 | 140.8083
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 35 | 814 | 176970 | 0.30563 | 0.0014058 | 217.4079
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 7 | 873 | 133590 | 0.23071 | 0.0015077 | 153.0241
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | SPLICE, OH | 14 | 25 | 2884 | 0.0049807 | 4.3176e-05 | 115.36
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | POLE | 3 | 395 | 202166 | 0.35285 | 0.00068941 | 511.8127
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WI | FUSE | 1 | 14 | 1190 | 0.0020769 | 2.4435e-05 | 85
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 8 | 58 | 16952 | 0.029587 | 0.00010123 | 292.2759
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | NONE | 171 | 13324 | 1415203 | 2.4441 | 0.023011 | 106.2146
AEP-PSO | 2025 | 579031 | PARTIAL POWER | U | NONE | 14 | 19 | 2145 | 0.0037045 | 3.2813e-05 | 112.8947
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | CUTOUT | 3 | 37 | 2107 | 0.0036388 | 6.39e-05 | 56.9459
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ABI | TRANSFORMER, GROUNDING | 1 | 9 | 333 | 0.0005812 | 1.5708e-05 | 37
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 12 | 3684 | 0.0063624 | 2.0724e-05 | 307
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 19 | 2755 | 0.0047579 | 3.2813e-05 | 145
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | WL | NONE | 4 | 785 | 128308 | 0.2292 | 0.0014023 | 163.4497
AEP-PSO | 2021 | 565565 | PARTIAL POWER | OL | FUSE | 3 | 3 | 255 | 0.00045088 | 5.3044e-06 | 85
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WL | CUTOUT | 5 | 15 | 2694 | 0.0046526 | 2.5905e-05 | 179.6
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | WU | NONE | 13 | 2664 | 418402 | 0.74741 | 0.0047588 | 157.0578
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | EQF | INSULATOR | 1 | 252 | 26964 | 0.047061 | 0.00043982 | 107
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 6 | 2428 | 189134 | 0.33786 | 0.0043372 | 77.897
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | CROSSARM | 6 | 54 | 2062 | 0.0035611 | 9.3259e-05 | 38.1852
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 35 | 5635 | 0.009835 | 6.1087e-05 | 161
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | PEDESTAL | 4 | 15 | 442 | 0.00076334 | 2.5905e-05 | 29.4667
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 23 | 2484 | 0.0043921 | 4.0667e-05 | 108
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | POLE HARDWARE | 2 | 724 | 120761 | 0.20856 | 0.0012504 | 166.797
AEP-PSO | 2024 | 579031 | PARTIAL POWER | TOR | CONN/CLAMP | 4 | 4 | 733 | 0.0012659 | 6.9081e-06 | 183.25
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | POLE | 2 | 2 | 719 | 0.0012417 | 3.454e-06 | 359.5
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | SPLICE, OH | 4 | 130 | 11888 | 0.020531 | 0.00022451 | 91.4462
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | CUTOUT | 7 | 31 | 4262 | 0.0073606 | 5.3538e-05 | 137.4839
AEP-PSO | 2024 | 579031 | PARTIAL POWER | VIN | NONE | 1 | 1 | 39 | 6.7354e-05 | 1.727e-06 | 39
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 2 | 5 | 220 | 0.00039299 | 8.9317e-06 | 44
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | WL | NONE | 1 | 871 | 215137 | 0.37155 | 0.0015042 | 247
AEP-PSO | 2021 | 565565 | TRANSMISSION STATION | WI | NONE | 4 | 2136 | 646094 | 1.1424 | 0.0037768 | 302.4785
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | BREAKER | 1 | 1147 | 25234 | 0.045076 | 0.0020489 | 22
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | AF | NONE | 1 | 32 | 352 | 0.00062879 | 5.7163e-05 | 11
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | EQF | INSULATOR | 1 | 611 | 116701 | 0.20456 | 0.001071 | 191
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TOR | SPLICE, UG | 1 | 1 | 452 | 0.00080743 | 1.7863e-06 | 452
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 43 | 8208 | 0.014387 | 7.5372e-05 | 190.8837
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 2 | 14 | 2.4178e-05 | 3.454e-06 | 7
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | FUSE | 23 | 393 | 27381 | 0.047995 | 0.00068887 | 69.6718
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | CONDUCTOR UG | 293 | 477 | 77900 | 0.13774 | 0.0008434 | 163.3124
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | SWITCH, UG | 6 | 1286 | 182571 | 0.32281 | 0.0022738 | 141.9681
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | INSULATOR | 12 | 1760 | 160995 | 0.2822 | 0.003085 | 91.4744
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | FUSE | 28 | 59 | 5209 | 0.0091306 | 0.00010342 | 88.2881
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | F | POLE HARDWARE | 2 | 1218 | 112901 | 0.19963 | 0.0021536 | 92.6938
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | WW | NONE | 4 | 679 | 99731 | 0.17634 | 0.0012006 | 146.8792
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | SPLICE, OH | 14 | 52 | 5170 | 0.0090622 | 9.1148e-05 | 99.4231
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | FUSE | 2 | 2 | 135 | 0.00023663 | 3.5057e-06 | 67.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 97 | 12020 | 0.021253 | 0.00017151 | 123.9175
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 26 | 2636 | 299322 | 0.52924 | 0.0046608 | 113.5516
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 1 | 2 | 94 | 0.00016234 | 3.454e-06 | 47
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 12 | 3609 | 0.0062328 | 2.0724e-05 | 300.75
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 2 | 4 | 1470 | 0.0025387 | 6.9081e-06 | 367.5
AEP-PSO | 2020 | 559804 | PARTIAL POWER | U | TRANSFORMER, OH | 2 | 2 | 133 | 0.00023758 | 3.5727e-06 | 66.5
AEP-PSO | 2025 | 579031 | PARTIAL POWER | CO | METERING | 1 | 1 | 25 | 4.3176e-05 | 1.727e-06 | 25
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | CROSSARM | 2 | 1218 | 127708 | 0.22055 | 0.0021035 | 104.8506
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CE | FUSE | 1 | 2 | 118 | 0.00020379 | 3.454e-06 | 59
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 14 | 1231 | 0.002126 | 2.4178e-05 | 87.9286
AEP-PSO | 2021 | 565565 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 83 | 0.00014676 | 1.7681e-06 | 83
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | V | NONE | 3 | 3104 | 181974 | 0.31897 | 0.0054408 | 58.6256
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | WL | FUSE | 1 | 563 | 156783 | 0.27077 | 0.00097231 | 278.4778
AEP-PSO | 2021 | 565565 | PARTIAL POWER | ABI | NONE | 25 | 226 | 15486 | 0.027381 | 0.0003996 | 68.5221
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | POLE | 17 | 1037 | 245842 | 0.43468 | 0.0018336 | 237.0704
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | ARRESTER | 181 | 7599 | 715854 | 1.2548 | 0.01332 | 94.2037
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TR | NONE | 23 | 239 | 25572 | 0.044824 | 0.00041893 | 106.9958
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 9 | 435 | 0.00076249 | 1.5776e-05 | 48.3333
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 12 | 2761 | 345005 | 0.60474 | 0.0048396 | 124.9565
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | FW | CUTOUT | 1 | 6 | 1254 | 0.0021981 | 1.0517e-05 | 209
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | ABX | NONE | 4 | 13 | 826 | 0.0014478 | 2.2787e-05 | 63.5385
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | NONE | 42 | 2661 | 213980 | 0.37835 | 0.004705 | 80.4134
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | NONE | 54 | 8939 | 231917 | 0.41428 | 0.015968 | 25.9444
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | U | NONE | 8 | 3794 | 95840 | 0.1712 | 0.0067774 | 25.2609
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | U | NONE | 8 | 1766 | 86779 | 0.15344 | 0.0031225 | 49.1387
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | REGULATOR | 10 | 6555 | 348182 | 0.61564 | 0.01159 | 53.117
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 9 | 339 | 118048 | 0.20873 | 0.0005994 | 348.2242
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | SWITCH, OH | 1 | 1 | 106 | 0.0001858 | 1.7528e-06 | 106
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | F | PEDESTAL | 1 | 1 | 264 | 0.00046679 | 1.7681e-06 | 264
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | ARRESTER | 4 | 18 | 955 | 0.0016886 | 3.1827e-05 | 53.0556
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | PEDESTAL | 1 | 4 | 1216 | 0.0021315 | 7.0114e-06 | 304
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 4 | 2052 | 0.0036282 | 7.0726e-06 | 513
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 6 | 17 | 749 | 0.0013129 | 2.9798e-05 | 44.0588
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CF | FUSE | 1 | 1 | 64 | 0.00011218 | 1.7528e-06 | 64
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 37 | 199 | 34105 | 0.060923 | 0.00035548 | 171.3819
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | OU | NONE | 9 | 5726 | 274637 | 0.47933 | 0.0099938 | 47.9632
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | SPLICE, UG | 1 | 9 | 237 | 0.00041542 | 1.5776e-05 | 26.3333
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 4 | 5 | 439 | 0.0007695 | 8.7642e-06 | 87.8
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 13 | 1963 | 0.0035066 | 2.3222e-05 | 151
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | CUTOUT | 3 | 4 | 187 | 0.00033405 | 7.1454e-06 | 46.75
AEP-PSO | 2024 | 579031 | PARTIAL POWER | U | NONE | 85 | 240 | 17391 | 0.030035 | 0.00041449 | 72.4625
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | JUMPER/RISER | 20 | 33 | 3137 | 0.0054177 | 5.6992e-05 | 95.0606
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | REGULATOR | 3 | 1353 | 99222 | 0.17136 | 0.0023367 | 73.3348
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 40 | 13316 | 0.022997 | 6.9081e-05 | 332.9
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CE | POLE | 2 | 54 | 4476 | 0.0078121 | 9.4248e-05 | 82.8889
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | EQF | ARRESTER | 3 | 2332 | 216744 | 0.37992 | 0.0040876 | 92.9434
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WW | NONE | 7 | 30 | 5743 | 0.010023 | 5.236e-05 | 191.4333
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OU | ARRESTER | 1 | 1 | 47 | 8.2031e-05 | 1.7453e-06 | 47
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | WL | CROSSARM | 2 | 596 | 48766 | 0.085479 | 0.0010447 | 81.8221
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 53 | 11872 | 0.020721 | 9.2503e-05 | 224
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | POLE | 52 | 4638 | 544801 | 0.94088 | 0.0080099 | 117.4646
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 198 | 2955 | 245428 | 0.42386 | 0.0051034 | 83.0552
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | CROSSARM | 56 | 5223 | 452209 | 0.78098 | 0.0090202 | 86.5803
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | PEDESTAL | 2 | 2 | 115 | 0.00020071 | 3.4907e-06 | 57.5
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | POLE | 13 | 150 | 36468 | 0.062981 | 0.00025905 | 243.12
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 36 | 6.2173e-05 | 1.727e-06 | 36
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | EQF | INSULATOR | 6 | 3334 | 289983 | 0.50081 | 0.0057579 | 86.9775
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | F | NONE | 4 | 11 | 896 | 0.0015474 | 1.8997e-05 | 81.4545
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | CROSSARM | 4 | 78 | 11722 | 0.020244 | 0.00013471 | 150.2821
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 101 | 12928 | 0.022859 | 0.00017858 | 128
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 29 | 5858 | 0.010224 | 5.0615e-05 | 202
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 1 | 179 | 0.00031975 | 1.7863e-06 | 179
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | EQF | CONDUCTOR UG | 1 | 458 | 20610 | 0.036816 | 0.00081814 | 45
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 6 | 22 | 941 | 0.0016251 | 3.7995e-05 | 42.7727
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | EQF | POLE | 1 | 725 | 30450 | 0.053145 | 0.0012654 | 42
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | WU | NONE | 4 | 3102 | 118554 | 0.20475 | 0.0053572 | 38.2186
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 2 | 9 | 1278 | 0.0022071 | 1.5543e-05 | 142
AEP-PSO | 2025 | 579031 | DISTRIBUTION STATION | EQF | CIRCUIT SWITCHER | 1 | 408 | 28152 | 0.048619 | 0.00070463 | 69
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 158 | 30020 | 0.051845 | 0.00027287 | 190
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WL | FUSE | 3 | 10 | 419 | 0.00072362 | 1.727e-05 | 41.9
AEP-PSO | 2025 | 579031 | PARTIAL POWER | TOR | NONE | 1 | 1 | 146 | 0.00025215 | 1.727e-06 | 146
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | AO | RELAY | 1 | 1945 | 33065 | 0.057104 | 0.0033591 | 17
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 1 | 30 | 5.3044e-05 | 1.7681e-06 | 30
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 1 | 48 | 3552 | 0.0062804 | 8.4871e-05 | 74
AEP-PSO | 2021 | 565565 | TRANSMISSION STATION | OL | NONE | 2 | 1789 | 375347 | 0.66367 | 0.0031632 | 209.8083
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 1 | 229 | 0.00040907 | 1.7863e-06 | 229
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | BREAKER | 2 | 9 | 1330 | 0.0023516 | 1.5913e-05 | 147.7778
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | U | RELAY | 13 | 7134 | 56467 | 0.09752 | 0.012321 | 7.9152
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 265 | 40952 | 0.071782 | 0.0004645 | 154.5358
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 2 | 306 | 0.00054105 | 3.5363e-06 | 153
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | TRANSFORMER, OH | 1 | 1 | 62 | 0.00010962 | 1.7681e-06 | 62
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WT | OTHER EQUIPMENT | 1 | 3 | 186 | 0.00032123 | 5.1811e-06 | 62
AEP-PSO | 2023 | 572956 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 122 | 0.00021293 | 1.7453e-06 | 122
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 2 | 220 | 0.00037995 | 3.454e-06 | 110
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TR | NONE | 24 | 159 | 13786 | 0.024061 | 0.00027751 | 86.7044
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | CONN/CLAMP | 295 | 515 | 37499 | 0.06573 | 0.00090271 | 72.8136
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | ARRESTER | 50 | 5177 | 561879 | 0.98489 | 0.0090745 | 108.5337
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | FUSE | 11 | 155 | 9188 | 0.016105 | 0.00027169 | 59.2774
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | NONE | 112 | 6932 | 1203074 | 2.1272 | 0.012257 | 173.5537
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | CONN/CLAMP | 71 | 212 | 17258 | 0.030515 | 0.00037485 | 81.4057
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | FUSE | 3 | 53 | 3306 | 0.0057949 | 9.2901e-05 | 62.3774
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | CROSSARM | 17 | 2704 | 161987 | 0.28642 | 0.0047811 | 59.9064
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | NONE | 11 | 41 | 4749 | 0.0083969 | 7.2494e-05 | 115.8293
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 8 | 408 | 0.00072883 | 1.4291e-05 | 51
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WL | NONE | 75 | 143 | 11753 | 0.020995 | 0.00025545 | 82.1888
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 38 | 6319 | 0.011173 | 6.7189e-05 | 166.2895
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | JUMPER/RISER | 7 | 182 | 16821 | 0.029742 | 0.0003218 | 92.4231
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 419 | 3371 | 337951 | 0.58984 | 0.0058835 | 100.2524
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 12 | 61 | 8273 | 0.014628 | 0.00010786 | 135.623
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 6 | 166 | 14409 | 0.025477 | 0.00029351 | 86.8012
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | NONE | 285 | 19222 | 4523004 | 7.8942 | 0.033549 | 235.3035
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | CONN/CLAMP | 366 | 646 | 53834 | 0.093958 | 0.0011275 | 83.3344
AEP-PSO | 2020 | 559804 | PARTIAL POWER | ERF | NONE | 2 | 2 | 262 | 0.00046802 | 3.5727e-06 | 131
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | SPLICE, UG | 1 | 1 | 240 | 0.00042872 | 1.7863e-06 | 240
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | AB | FUSE | 2 | 556 | 48892 | 0.086448 | 0.00098309 | 87.9353
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | CUTOUT | 3 | 81 | 11926 | 0.021087 | 0.00014322 | 147.2346
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | INSULATOR | 1 | 5 | 755 | 0.0013234 | 8.7642e-06 | 151
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WL | CUTOUT | 3 | 3 | 378 | 0.00065974 | 5.236e-06 | 126
AEP-PSO | 2021 | 565565 | PARTIAL POWER | O | CONDUCTOR UG | 1 | 1 | 103 | 0.00018212 | 1.7681e-06 | 103
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | FO | CROSSARM | 1 | 211 | 42608 | 0.074685 | 0.00036985 | 201.9336
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | SPLICE, UG | 1 | 19 | 1254 | 0.0022173 | 3.3595e-05 | 66
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | NONE | 601 | 38874 | 4157988 | 7.1809 | 0.067136 | 106.9606
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | SPLICE, OH | 13 | 69 | 8143 | 0.014546 | 0.00012326 | 118.0145
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WW | FUSE | 1 | 1 | 218 | 0.00038942 | 1.7863e-06 | 218
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | EQF | SWITCH, OH | 5 | 1187 | 35802 | 0.061831 | 0.00205 | 30.1618
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | EQF | ARRESTER | 9 | 6978 | 610323 | 1.054 | 0.012051 | 87.4639
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | TRANSFORMER, OH | 24 | 78 | 17100 | 0.029845 | 0.00013614 | 219.2308
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 10 | 6568 | 947403 | 1.6535 | 0.011463 | 144.2453
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 6 | 327 | 0.00058413 | 1.0718e-05 | 54.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | FO | NONE | 1 | 246 | 34932 | 0.0624 | 0.00043944 | 142
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | ARRESTER | 6 | 131 | 7871 | 0.01406 | 0.00023401 | 60.084
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | REGULATOR | 1 | 213 | 38979 | 0.068031 | 0.00037176 | 183
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | SPLICE, OH | 6 | 6 | 423 | 0.00073828 | 1.0472e-05 | 70.5
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 4 | 1309 | 0.0022846 | 6.9813e-06 | 327.25
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | INSULATOR | 4 | 2120 | 209394 | 0.36163 | 0.0036613 | 98.7708
AEP-PSO | 2022 | 570502 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 14 | 13898 | 925484 | 1.6222 | 0.024361 | 66.5912
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | V | METERING | 9 | 10 | 624 | 0.0010777 | 1.727e-05 | 62.4
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | FUSE | 32 | 241 | 29635 | 0.05118 | 0.00041621 | 122.9668
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | GUY/ANCHOR | 2 | 73 | 5402 | 0.0094283 | 0.00012741 | 74
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FO | FUSE | 4 | 54 | 6114 | 0.010559 | 9.3259e-05 | 113.2222
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | V | NONE | 10 | 7013 | 266115 | 0.46446 | 0.01224 | 37.946
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | ARRESTER | 44 | 1127 | 77372 | 0.13362 | 0.0019464 | 68.6531
AEP-PSO | 2021 | 565565 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 5 | 641 | 0.0011334 | 8.8407e-06 | 128.2
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | CF | INSULATOR | 1 | 204 | 25500 | 0.045552 | 0.00036441 | 125
AEP-PSO | 2022 | 570502 | PARTIAL POWER | ERF | NONE | 1 | 2 | 150 | 0.00026293 | 3.5057e-06 | 75
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | AO | FUSE | 1 | 1 | 75 | 0.00013146 | 1.7528e-06 | 75
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | FUSE | 1 | 28 | 3080 | 0.0054459 | 4.9508e-05 | 110
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 31 | 29450 | 0.050861 | 5.3538e-05 | 950
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | CABLE TERMINATOR | 1 | 1 | 60 | 0.00010718 | 1.7863e-06 | 60
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1 | 49 | 8.4624e-05 | 1.727e-06 | 49
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 48 | 3888 | 0.0067859 | 8.3776e-05 | 81
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | NONE | 1923 | 66216 | 3639030 | 6.3786 | 0.11607 | 54.957
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | NONE | 2348 | 22419 | 1543063 | 2.6932 | 0.039129 | 68.8284
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | NONE | 43 | 599 | 32496 | 0.05696 | 0.00105 | 54.2504
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 67 | 452 | 75880 | 0.13301 | 0.00079228 | 167.8761
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 32 | 3568 | 0.0063087 | 5.6581e-05 | 111.5
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WL | FUSE | 7 | 23 | 3206 | 0.0056196 | 4.0315e-05 | 139.3913
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 9 | 1246 | 0.002184 | 1.5776e-05 | 138.4444
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | WL | NONE | 21 | 19756 | 1513256 | 2.6525 | 0.034629 | 76.5973
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | OL | BREAKER | 1 | 287 | 25543 | 0.044773 | 0.00050307 | 89
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 10 | 17 | 1110 | 0.0019626 | 3.0058e-05 | 65.2941
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | FUSE | 180 | 989 | 50480 | 0.090174 | 0.0017667 | 51.0415
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 28 | 3878 | 0.0069274 | 5.0018e-05 | 138.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 1 | 58 | 0.00010255 | 1.7681e-06 | 58
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | WU | NONE | 11 | 2747 | 325506 | 0.57554 | 0.0048571 | 118.4951
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | METERING | 59 | 87 | 7083 | 0.012362 | 0.00015184 | 81.4138
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 8 | 1040 | 0.001823 | 1.4023e-05 | 130
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | RELAY | 2 | 834 | 5004 | 0.0088478 | 0.0014746 | 6
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 8 | 449 | 66864 | 0.11823 | 0.0007939 | 148.9176
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | NONE | 39 | 885 | 43820 | 0.078277 | 0.0015809 | 49.5141
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | NONE | 49 | 7204 | 137875 | 0.24064 | 0.012573 | 19.1387
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 6 | 13 | 2676 | 0.0047316 | 2.2986e-05 | 205.8462
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WT | POLE | 3 | 2697 | 490338 | 0.8558 | 0.0047072 | 181.8087
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | ARRESTER | 45 | 1294 | 161270 | 0.28147 | 0.0022585 | 124.6291
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | POLE | 12 | 956 | 176332 | 0.30776 | 0.0016685 | 184.4477
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | CROSSARM | 6 | 71 | 11825 | 0.021123 | 0.00012683 | 166.5493
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 2 | 1748 | 0.003064 | 3.5057e-06 | 874
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | AF | NONE | 2 | 1963 | 62816 | 0.10963 | 0.0034261 | 32
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | ARRESTER | 18 | 23 | 1472 | 0.0025422 | 3.9722e-05 | 64
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 129 | 2679 | 602241 | 1.0401 | 0.0046267 | 224.8007
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | POLE HARDWARE | 2 | 57 | 4322 | 0.0077206 | 0.00010182 | 75.8246
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 2 | 5 | 465 | 0.00082219 | 8.8407e-06 | 93
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 2 | 44 | 8249 | 0.014246 | 7.5989e-05 | 187.4773
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | FUSE | 23 | 48 | 4173 | 0.0072069 | 8.2897e-05 | 86.9375
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 3 | 13 | 1049 | 0.0018309 | 2.2689e-05 | 80.6923
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | SPLICE, UG | 1 | 107 | 4988 | 0.0087432 | 0.00018755 | 46.6168
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 52 | 10026 | 0.01791 | 9.289e-05 | 192.8077
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | EQF | CONDUCTOR UG | 4 | 618 | 119224 | 0.20898 | 0.0010833 | 192.9191
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CE | METERING | 3 | 4 | 278 | 0.0004966 | 7.1454e-06 | 69.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | NONE | 14 | 38 | 2282 | 0.0040764 | 6.7881e-05 | 60.0526
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | CUTOUT | 11 | 261 | 80656 | 0.13929 | 0.00045075 | 309.0268
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WU | NONE | 23 | 283 | 33113 | 0.057187 | 0.00048875 | 117.0071
AEP-PSO | 2025 | 579031 | TRANSMISSION STATION | U | NONE | 4 | 4836 | 100466 | 0.17351 | 0.0083519 | 20.7746
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | JUMPER/RISER | 6 | 74 | 9848 | 0.017008 | 0.0001278 | 133.0811
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | F | POLE | 5 | 156 | 18741 | 0.032366 | 0.00026942 | 120.1346
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 3 | 562 | 49897 | 0.086173 | 0.00097059 | 88.7847
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TIR | NONE | 23 | 1737 | 163331 | 0.28208 | 0.0029998 | 94.0305
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | SPLICE, OH | 6 | 6 | 440 | 0.00075989 | 1.0362e-05 | 73.3333
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | U | NONE | 13 | 2155 | 453364 | 0.78297 | 0.0037217 | 210.3777
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | ERF | CONDUCTOR OVERHEAD | 1 | 460 | 8740 | 0.015613 | 0.00082172 | 19
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | CROSSARM | 1 | 8 | 1976 | 0.0035298 | 1.4291e-05 | 247
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | NONE | 63 | 2690 | 303944 | 0.53742 | 0.0047563 | 112.9903
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | VIN | FUSE | 4 | 27 | 1844 | 0.0031846 | 4.663e-05 | 68.2963
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 72 | 28368 | 0.050159 | 0.00012731 | 394
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | AB | TRANSFORMER, OH | 1 | 359 | 75390 | 0.13215 | 0.00062927 | 210
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 49 | 40229 | 0.070213 | 8.5521e-05 | 821
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 9 | 43 | 6151 | 0.010782 | 7.5372e-05 | 143.0465
AEP-PSO | 2021 | 565565 | PARTIAL POWER | A | FUSE | 8 | 14 | 991 | 0.0017522 | 2.4754e-05 | 70.7857
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | FUSE | 11 | 227 | 27923 | 0.049372 | 0.00040137 | 123.0088
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | POLE | 1 | 408 | 95072 | 0.1681 | 0.0007214 | 233.0196
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | METERING | 19 | 21 | 1466 | 0.0025921 | 3.7131e-05 | 69.8095
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | METERING | 4 | 5 | 396 | 0.00069413 | 8.7642e-06 | 79.2
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 1 | 80 | 0.00014023 | 1.7528e-06 | 80
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | CUTOUT | 4 | 18 | 355 | 0.00062226 | 3.1551e-05 | 19.7222
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | POLE | 4 | 18 | 6349 | 0.011341 | 3.2154e-05 | 352.7222
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 8 | 26 | 2086 | 0.0036883 | 4.5972e-05 | 80.2308
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 3 | 390 | 0.00068958 | 5.3044e-06 | 130
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 340 | 131580 | 0.23265 | 0.00060117 | 387
AEP-PSO | 2020 | 559804 | PARTIAL POWER | O | CONDUCTOR UG | 3 | 3 | 286 | 0.00051089 | 5.359e-06 | 95.3333
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | U | NONE | 30 | 20352 | 2086852 | 3.6579 | 0.035674 | 102.5379
AEP-PSO | 2023 | 572956 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 2 | 254 | 0.00044332 | 3.4907e-06 | 127
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | JUMPER/RISER | 8 | 119 | 22507 | 0.039451 | 0.00020859 | 189.1345
AEP-PSO | 2023 | 572956 | PARTIAL POWER | U | FUSE | 9 | 24 | 1642 | 0.0028658 | 4.1888e-05 | 68.4167
AEP-PSO | 2023 | 572956 | PARTIAL POWER | A | FUSE | 20 | 36 | 3837 | 0.0066968 | 6.2832e-05 | 106.5833
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TOR | OTHER EQUIPMENT | 1 | 1 | 77 | 0.00013615 | 1.7681e-06 | 77
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 17 | 817 | 15061 | 0.026904 | 0.0014594 | 18.4345
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 156 | 17334 | 0.030649 | 0.00027583 | 111.1154
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | TRANSFORMER, OH | 15 | 63 | 7483 | 0.012923 | 0.0001088 | 118.7778
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 6 | 306 | 0.00053637 | 1.0517e-05 | 51
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | EQF | ARRESTER | 2 | 386 | 97274 | 0.16799 | 0.00066663 | 252.0052
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 23 | 113 | 9016 | 0.016106 | 0.00020186 | 79.7876
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | JUMPER/RISER | 15 | 219 | 31986 | 0.055826 | 0.00038223 | 146.0548
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | U | NONE | 3 | 3004 | 161825 | 0.28907 | 0.0053662 | 53.8698
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 1 | 141 | 0.00025187 | 1.7863e-06 | 141
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 5 | 17 | 502 | 0.00087616 | 2.9671e-05 | 29.5294
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CE | FUSE | 2 | 12 | 1869 | 0.003262 | 2.0944e-05 | 155.75
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | O | NONE | 1 | 1 | 84 | 0.00015005 | 1.7863e-06 | 84
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | CROSSARM | 4 | 1954 | 293941 | 0.51303 | 0.0034104 | 150.4304
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 12 | 201 | 12873 | 0.022232 | 0.00034713 | 64.0448
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WT | NONE | 3 | 1416 | 82173 | 0.14342 | 0.0024714 | 58.0318
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | POLE | 2 | 3 | 90 | 0.00015708 | 5.236e-06 | 30
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | FUSE | 3 | 12 | 996 | 0.0017201 | 2.0724e-05 | 83
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | TRANSFORMER, GROUNDING | 1 | 4 | 192 | 0.00033159 | 6.9081e-06 | 48
AEP-PSO | 2023 | 572956 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 5 | 290 | 0.00050615 | 8.7267e-06 | 58
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | INSULATOR | 26 | 3540 | 275290 | 0.47543 | 0.0061137 | 77.7655
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | FUSE | 95 | 1017 | 82081 | 0.14176 | 0.0017564 | 80.7089
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | POLE | 49 | 5781 | 1080416 | 1.8659 | 0.0099839 | 186.8908
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | CUTOUT | 7 | 146 | 11701 | 0.020208 | 0.00025215 | 80.1438
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 4 | 303 | 0.00052329 | 6.9081e-06 | 75.75
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | INSULATOR | 3 | 1108 | 103117 | 0.17809 | 0.0019135 | 93.0659
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | ERF | NONE | 1 | 937 | 91826 | 0.15859 | 0.0016182 | 98
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 913 | 21346 | 0.038131 | 0.0016309 | 23.3801
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 29 | 406 | 0.00070117 | 5.0084e-05 | 14
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | PEDESTAL | 1 | 3 | 75 | 0.00013398 | 5.359e-06 | 25
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 2 | 8 | 967 | 0.00167 | 1.3816e-05 | 120.875
AEP-PSO | 2025 | 579031 | PARTIAL POWER | U | PEDESTAL | 1 | 1 | 50 | 8.6351e-05 | 1.727e-06 | 50
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 1620 | 167990 | 0.30009 | 0.0028939 | 103.6975
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | RELAY | 7 | 9679 | 269819 | 0.47295 | 0.016966 | 27.8767
AEP-PSO | 2024 | 579031 | PARTIAL POWER | TIR | NONE | 1 | 1 | 50 | 8.6351e-05 | 1.727e-06 | 50
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 2098 | 98951 | 0.17089 | 0.0036233 | 47.1644
AEP-PSO | 2025 | 579031 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 1 | 423 | 62528 | 0.10799 | 0.00073053 | 147.8203
AEP-PSO | 2025 | 579031 | TRANSMISSION STATION | ABI | NONE | 2 | 1512 | 89606 | 0.15475 | 0.0026113 | 59.2632
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 163 | 12877 | 0.022239 | 0.0002815 | 79
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 249 | 48651 | 0.084021 | 0.00043003 | 195.3855
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | EQF | SWITCH, UG | 1 | 457 | 61633 | 0.1101 | 0.00081636 | 134.8643
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | WW | NONE | 2 | 381 | 192717 | 0.33283 | 0.000658 | 505.8189
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 43 | 12206 | 0.021804 | 7.6813e-05 | 283.8605
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WI | FUSE | 1 | 13 | 975 | 0.0016838 | 2.2451e-05 | 75
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | EQF | CUTOUT | 5 | 2221 | 275679 | 0.4761 | 0.0038357 | 124.1238
AEP-PSO | 2025 | 579031 | PARTIAL POWER | CO | CONN/CLAMP | 1 | 1 | 58 | 0.00010017 | 1.727e-06 | 58
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 369 | 0.00063727 | 5.1811e-06 | 123
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | FO | NONE | 1 | 770 | 25410 | 0.043884 | 0.0013298 | 33
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | WL | NONE | 4 | 1734 | 50517 | 0.087244 | 0.0029947 | 29.1332
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | CAPACITOR | 2 | 2432 | 194374 | 0.33569 | 0.0042001 | 79.9235
AEP-PSO | 2023 | 572956 | PARTIAL POWER | FW | NONE | 1 | 1 | 229 | 0.00039968 | 1.7453e-06 | 229
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 1 | 88 | 0.0001572 | 1.7863e-06 | 88
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | V | CIRCUIT SWITCHER | 1 | 1344 | 33600 | 0.05941 | 0.0023764 | 25
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 97 | 0.00017003 | 1.7528e-06 | 97
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 48 | 8.4871e-05 | 1.7681e-06 | 48
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 373 | 135026 | 0.23875 | 0.00065952 | 362
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | POLE | 17 | 259 | 71168 | 0.12475 | 0.00045399 | 274.7799
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | TRANSFORMER, OH | 13 | 24 | 5390 | 0.0094478 | 4.2068e-05 | 224.5833
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 528 | 35070 | 3423416 | 6.0007 | 0.061472 | 97.6167
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | O | CUTOUT | 1 | 2 | 162 | 0.00028396 | 3.5057e-06 | 81
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | CUTOUT | 276 | 10156 | 680953 | 1.204 | 0.017957 | 67.0493
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ABI | ARRESTER | 4 | 282 | 32550 | 0.057055 | 0.0004943 | 115.4255
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | ARRESTER | 17 | 29 | 2401 | 0.0042086 | 5.0832e-05 | 82.7931
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | CUTOUT | 11 | 90 | 8023 | 0.014063 | 0.00015776 | 89.1444
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 3 | 3 | 167 | 0.00029272 | 5.2585e-06 | 55.6667
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 2 | 86 | 0.00015074 | 3.5057e-06 | 43
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 5 | 6 | 522 | 0.00091498 | 1.0517e-05 | 87
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 149 | 5326 | 738747 | 1.3062 | 0.0094171 | 138.7058
AEP-PSO | 2021 | 565565 | PARTIAL POWER | U | FUSE | 3 | 4 | 278 | 0.00049154 | 7.0726e-06 | 69.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | FUSE | 2 | 34 | 1871 | 0.0033082 | 6.0117e-05 | 55.0294
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | A | NONE | 8 | 909 | 88568 | 0.15821 | 0.0016238 | 97.4345
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | NONE | 256 | 927 | 59968 | 0.10712 | 0.0016559 | 64.6904
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | POLE | 12 | 431 | 266074 | 0.4753 | 0.00076991 | 617.3411
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | ARRESTER | 24 | 204 | 12573 | 0.022231 | 0.0003607 | 61.6324
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | CUTOUT | 9 | 220 | 14966 | 0.026462 | 0.00038899 | 68.0273
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 134 | 2677 | 519523 | 0.92804 | 0.004782 | 194.0691
AEP-PSO | 2022 | 570502 | PARTIAL POWER | U | CONDUCTOR UG | 4 | 4 | 576 | 0.0010096 | 7.0114e-06 | 144
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 5886 | 536744 | 0.94904 | 0.010407 | 91.1899
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 687 | 18824 | 2564095 | 4.4752 | 0.032854 | 136.2141
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | CROSSARM | 132 | 11679 | 1228218 | 2.194 | 0.020863 | 105.1647
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OU | NONE | 7 | 1823 | 226630 | 0.40071 | 0.0032233 | 124.3171
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 1 | 522 | 8352 | 0.01464 | 0.00091498 | 16
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 1 | 87 | 0.00015383 | 1.7681e-06 | 87
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 19 | 884 | 145334 | 0.25697 | 0.001563 | 164.405
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | POLE | 61 | 10333 | 2143916 | 3.7419 | 0.018035 | 207.4824
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | JUMPER/RISER | 4 | 170 | 15048 | 0.026264 | 0.00029671 | 88.5176
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 445 | 4171 | 413352 | 0.71387 | 0.0072034 | 99.1014
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 3 | 14 | 1403 | 0.0025062 | 2.5009e-05 | 100.2143
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | V | NONE | 2 | 1769 | 86681 | 0.15129 | 0.0030875 | 49
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | CONN/CLAMP | 3 | 329 | 43536 | 0.075985 | 0.00057422 | 132.3283
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | V | METERING | 7 | 9 | 859 | 0.0014992 | 1.5708e-05 | 95.4444
AEP-PSO | 2020 | 559804 | TRANSMISSION STATION | WL | NONE | 1 | 499 | 52395 | 0.093595 | 0.00089138 | 105
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | SWITCH, OH | 1 | 180 | 6048 | 0.010601 | 0.00031551 | 33.6
AEP-PSO | 2024 | 579031 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 6 | 6 | 555 | 0.0009585 | 1.0362e-05 | 92.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 141 | 0.00024715 | 3.5057e-06 | 70.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | INSULATOR | 4 | 1389 | 118074 | 0.20877 | 0.002456 | 85.0065
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 9 | 5999 | 878528 | 1.5693 | 0.010716 | 146.4457
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 6 | 2037 | 272305 | 0.48643 | 0.0036388 | 133.6794
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | F | FUSE | 3 | 14 | 799 | 0.0013945 | 2.4435e-05 | 57.0714
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | CUTOUT | 61 | 1381 | 176851 | 0.30543 | 0.002385 | 128.0601
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 6 | 624 | 0.0010777 | 1.0362e-05 | 104
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OU | NONE | 15 | 848 | 208841 | 0.3645 | 0.00148 | 246.2748
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | VIN | FUSE | 16 | 63 | 5577 | 0.0096316 | 0.0001088 | 88.5238
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | NONE | 5 | 20 | 1446 | 0.002583 | 3.5727e-05 | 72.3
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CE | NONE | 24 | 144 | 9455 | 0.016329 | 0.00024869 | 65.6597
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WU | TRANSFORMER, STATION SERVICE | 1 | 5 | 225 | 0.00038858 | 8.6351e-06 | 45
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 11 | 2542 | 309543 | 0.53459 | 0.0043901 | 121.7714
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | LS | NONE | 38 | 41727 | 4996627 | 8.7208 | 0.072828 | 119.7457
AEP-PSO | 2023 | 572956 | PARTIAL POWER | CE | NONE | 1 | 2 | 442 | 0.00077144 | 3.4907e-06 | 221
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WFS | NONE | 1 | 1 | 60 | 0.00010472 | 1.7453e-06 | 60
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | JUMPER/RISER | 1 | 1 | 92 | 0.00016267 | 1.7681e-06 | 92
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OU | NONE | 4 | 28 | 1835 | 0.0031691 | 4.8357e-05 | 65.5357
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 39 | 3931 | 0.0068609 | 6.8068e-05 | 100.7949
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | JUMPER/RISER | 7 | 477 | 95889 | 0.1656 | 0.00082379 | 201.0252
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 29 | 4067 | 290435 | 0.50159 | 0.0070238 | 71.4126
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | POLE | 3 | 24 | 7463 | 0.012889 | 4.1449e-05 | 310.9583
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 12 | 1160 | 0.0020722 | 2.1436e-05 | 96.6667
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 3 | 19 | 11606 | 0.020044 | 3.2813e-05 | 610.8421
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WW | NONE | 2 | 24 | 5175 | 0.0089373 | 4.1449e-05 | 215.625
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 1 | 822 | 0.0014347 | 1.7453e-06 | 822
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 223 | 0.00038513 | 1.727e-06 | 223
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | WL | POLE | 1 | 568 | 57368 | 0.10056 | 0.00099561 | 101
AEP-PSO | 2024 | 579031 | PARTIAL POWER | ERF | NONE | 4 | 5 | 293 | 0.00050602 | 8.6351e-06 | 58.6
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 31 | 6415 | 0.011079 | 5.3538e-05 | 206.9355
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | TRANSFORMER, POWER - LTC | 1 | 1 | 78 | 0.00013471 | 1.727e-06 | 78
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CO | CONN/CLAMP | 2 | 2 | 131 | 0.00022624 | 3.454e-06 | 65.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | PEDESTAL | 1 | 3 | 768 | 0.0013264 | 5.1811e-06 | 256
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 847 | 71939 | 0.12424 | 0.0014628 | 84.9339
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | FUSE | 1 | 1 | 120 | 0.00021436 | 1.7863e-06 | 120
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | RECLOSER, LINE/OCR/BR | 1 | 1206 | 207832 | 0.36748 | 0.0021324 | 172.3317
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WL | JUMPER/RISER | 1 | 1 | 188 | 0.00032953 | 1.7528e-06 | 188
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 8 | 1344 | 0.0023457 | 1.3963e-05 | 168
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | METERING | 1 | 2 | 112 | 0.00020007 | 3.5727e-06 | 56
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 14 | 116 | 10259 | 0.018139 | 0.0002051 | 88.4397
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 444 | 29234 | 3403313 | 6.0175 | 0.05169 | 116.4163
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 17 | 118 | 18042 | 0.031625 | 0.00020684 | 152.8983
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 2 | 7 | 985 | 0.0017265 | 1.227e-05 | 140.7143
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 29 | 5786 | 379120 | 0.66454 | 0.010142 | 65.5237
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | CUTOUT | 19 | 39 | 5309 | 0.0093871 | 6.8958e-05 | 136.1282
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | NONE | 41 | 8639 | 653275 | 1.1551 | 0.015275 | 75.6193
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 2 | 172 | 0.00030149 | 3.5057e-06 | 86
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | F | POLE | 7 | 167 | 28164 | 0.049798 | 0.00029528 | 168.6467
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 5 | 15 | 1774 | 0.0031367 | 2.6522e-05 | 118.2667
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TIR | NONE | 4 | 4 | 268 | 0.00047386 | 7.0726e-06 | 67
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 3 | 69 | 0.00012095 | 5.2585e-06 | 23
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | FUSE | 188 | 2550 | 226432 | 0.3952 | 0.0044506 | 88.7969
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 7 | 1971 | 0.0034549 | 1.227e-05 | 281.5714
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 1465 | 42525 | 0.075964 | 0.002617 | 29.0273
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | SPLICE, OH | 2 | 36 | 869 | 0.0015523 | 6.4308e-05 | 24.1389
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | PEDESTAL | 3 | 7 | 333 | 0.00058879 | 1.2377e-05 | 47.5714
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | FUSE | 188 | 2346 | 169688 | 0.29616 | 0.0040946 | 72.3308
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | FUSE | 5 | 452 | 59348 | 0.10602 | 0.00080743 | 131.3009
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | JUMPER/RISER | 6 | 56 | 6082 | 0.010865 | 0.00010004 | 108.6071
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | POLE | 171 | 10884 | 2212190 | 3.861 | 0.018996 | 203.2516
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 3 | 35 | 1382 | 0.0024224 | 6.1349e-05 | 39.4857
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 88 | 745 | 132778 | 0.23174 | 0.0013003 | 178.2255
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | CUTOUT | 33 | 1484 | 312618 | 0.54562 | 0.0025901 | 210.659
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WU | NONE | 17 | 34 | 4513 | 0.0078767 | 5.9341e-05 | 132.7353
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 35 | 196 | 32718 | 0.058445 | 0.00035012 | 166.9286
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | PEDESTAL | 4 | 22 | 516 | 0.00091236 | 3.8899e-05 | 23.4545
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 1 | 27 | 4.8231e-05 | 1.7863e-06 | 27
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | POLE | 1 | 7 | 686 | 0.0012254 | 1.2504e-05 | 98
AEP-PSO | 2022 | 570502 | PARTIAL POWER | A | CABLE TERMINATOR | 1 | 1 | 138 | 0.00024189 | 1.7528e-06 | 138
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 5 | 685 | 0.0012236 | 8.9317e-06 | 137
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | FUSE | 112 | 1648 | 132345 | 0.22856 | 0.0028461 | 80.3064
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | ARRESTER | 40 | 2267 | 574674 | 0.99248 | 0.0039152 | 253.4954
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | U | NONE | 6 | 2009 | 173675 | 0.29994 | 0.0034696 | 86.4485
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 12 | 23 | 932 | 0.0016649 | 4.1086e-05 | 40.5217
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | V | NONE | 14 | 15848 | 559888 | 1.0002 | 0.02831 | 35.3286
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | FUSE | 2 | 8 | 350 | 0.00061087 | 1.3963e-05 | 43.75
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 3 | 16 | 6910 | 0.011934 | 2.7632e-05 | 431.875
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 3 | 138 | 0.00024651 | 5.359e-06 | 46
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | POLE HARDWARE | 2 | 3 | 1040 | 0.0018389 | 5.3044e-06 | 346.6667
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OL | FUSE | 2 | 417 | 82364 | 0.14375 | 0.0007278 | 197.5156
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CO | JUMPER/RISER | 1 | 1 | 116 | 0.00020722 | 1.7863e-06 | 116
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | V | TRANSFORMER, GROUNDING | 4 | 5212 | 181139 | 0.31751 | 0.0091358 | 34.7542
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TR | NONE | 3 | 52 | 1878 | 0.0032433 | 8.9805e-05 | 36.1154
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | ARRESTER | 9 | 58 | 5665 | 0.0097836 | 0.00010017 | 97.6724
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 744 | 9672 | 0.016881 | 0.0012985 | 13
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | POLE HARDWARE | 3 | 688 | 155383 | 0.26835 | 0.0011882 | 225.8474
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | A | NONE | 5 | 1770 | 149337 | 0.25791 | 0.0030568 | 84.3712
AEP-PSO | 2025 | 579031 | PARTIAL POWER | U | FUSE | 3 | 5 | 355 | 0.00061309 | 8.6351e-06 | 71
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | POLE | 10 | 886 | 92704 | 0.1601 | 0.0015301 | 104.6321
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 3 | 66 | 0.00011569 | 5.2585e-06 | 22
AEP-PSO | 2024 | 579031 | PARTIAL POWER | O | NONE | 2 | 89 | 3861 | 0.006668 | 0.00015371 | 43.382
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 1 | 23 | 1495 | 0.0026205 | 4.0315e-05 | 65
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | WL | CONDUCTOR UG | 1 | 90 | 53460 | 0.093306 | 0.00015708 | 594
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | FO | NONE | 1 | 1663 | 84769 | 0.1464 | 0.002872 | 50.9735
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERO | NONE | 5 | 1051 | 11610 | 0.020051 | 0.0018151 | 11.0466
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 140 | 0.00024178 | 3.454e-06 | 70
AEP-PSO | 2025 | 579031 | TRANSMISSION STATION | ERF | NONE | 2 | 331 | 5958 | 0.01029 | 0.00057164 | 18
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | EQF | POLE | 6 | 1629 | 1043578 | 1.8023 | 0.0028133 | 640.6249
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | BE | CONDUCTOR UG | 1 | 14 | 882 | 0.0015595 | 2.4754e-05 | 63
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 60 | 0.00010609 | 1.7681e-06 | 60
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 845 | 5123 | 0.0091514 | 0.0015095 | 6.0627
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 87 | 1479 | 0.0025925 | 0.0001525 | 17
AEP-PSO | 2023 | 572956 | PARTIAL POWER | FO | CUTOUT | 1 | 1 | 78 | 0.00013614 | 1.7453e-06 | 78
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 3 | 10 | 554 | 0.00097955 | 1.7681e-05 | 55.4
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 1 | 17 | 3.0058e-05 | 1.7681e-06 | 17
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 2 | 1143 | 21965 | 0.038336 | 0.0019949 | 19.217
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | OL | JUMPER/RISER | 1 | 1910 | 91580 | 0.16359 | 0.0034119 | 47.9476
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 7 | 308 | 0.00053988 | 1.227e-05 | 44
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 48 | 2160 | 0.0037861 | 8.4136e-05 | 45
AEP-PSO | 2023 | 572956 | PARTIAL POWER | ABI | ARRESTER | 1 | 9 | 1377 | 0.0024033 | 1.5708e-05 | 153
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | METERING | 1 | 1 | 50 | 8.6351e-05 | 1.727e-06 | 50
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | INSULATOR | 1 | 5 | 745 | 0.0012866 | 8.6351e-06 | 149
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | NETWORK TRANSFORMER | 1 | 1 | 71 | 0.00012683 | 1.7863e-06 | 71
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | NONE | 2965 | 27922 | 1588263 | 2.8083 | 0.04937 | 56.8821
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | POLE | 161 | 14086 | 1882867 | 3.3004 | 0.024691 | 133.6694
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | NONE | 226 | 3220 | 117446 | 0.20766 | 0.0056934 | 36.4739
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ABI | NONE | 366 | 6412 | 393276 | 0.68935 | 0.011239 | 61.3344
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | NONE | 155 | 5800 | 853356 | 1.4958 | 0.010166 | 147.1303
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 30 | 3610 | 599446 | 1.0599 | 0.006383 | 166.0515
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 9 | 2730 | 0.0047853 | 1.5776e-05 | 303.3333
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 10 | 54 | 13061 | 0.022894 | 9.4653e-05 | 241.8704
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 819 | 55427 | 0.097155 | 0.0014356 | 67.6764
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | WU | NONE | 5 | 2922 | 297061 | 0.5207 | 0.0051218 | 101.6636
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 82 | 1768 | 238584 | 0.42185 | 0.0031261 | 134.9457
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | ARRESTER | 12 | 1818 | 145851 | 0.26054 | 0.0032476 | 80.2261
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | POLE | 31 | 789 | 75059 | 0.13272 | 0.0013951 | 95.1318
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 15 | 1860 | 0.0033226 | 2.6795e-05 | 124
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 10 | 1.7528e-05 | 1.7528e-06 | 10
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | GUY/ANCHOR | 2 | 6 | 610 | 0.0010786 | 1.0609e-05 | 101.6667
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 1299 | 87762 | 0.15518 | 0.0022968 | 67.5612
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 4 | 356 | 0.00062946 | 7.0726e-06 | 89
AEP-PSO | 2022 | 570502 | PARTIAL POWER | FO | CUTOUT | 1 | 2 | 108 | 0.00018931 | 3.5057e-06 | 54
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 10 | 18 | 3399 | 0.0060718 | 3.2154e-05 | 188.8333
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 8 | 2241 | 0.0039624 | 1.4145e-05 | 280.125
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 11 | 1045 | 0.0018317 | 1.9281e-05 | 95
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | ERF | NONE | 1 | 43 | 11051 | 0.019288 | 7.5049e-05 | 257
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 2 | 594 | 0.0010259 | 3.454e-06 | 297
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | OU | NONE | 8 | 3440 | 489343 | 0.87413 | 0.006145 | 142.2509
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 1 | 1110 | 83250 | 0.1453 | 0.0019373 | 75
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | EQF | CONN/CLAMP | 1 | 182 | 27482 | 0.047965 | 0.00031765 | 151
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | POLE HARDWARE | 3 | 1428 | 32536 | 0.056786 | 0.0024923 | 22.7843
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 831 | 138350 | 0.24251 | 0.0014566 | 166.4862
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FO | FUSE | 1 | 1 | 11 | 1.9281e-05 | 1.7528e-06 | 11
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | CONN/CLAMP | 3 | 4 | 274 | 0.00048946 | 7.1454e-06 | 68.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 7 | 145 | 64138 | 0.11077 | 0.00025042 | 442.331
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | METERING | 3 | 3 | 165 | 0.00028496 | 5.1811e-06 | 55
AEP-PSO | 2025 | 579031 | PARTIAL POWER | A | NONE | 12 | 14 | 2355 | 0.0040671 | 2.4178e-05 | 168.2143
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 1 | 100 | 0.0001727 | 1.727e-06 | 100
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | R | NONE | 1 | 1 | 65 | 0.00011611 | 1.7863e-06 | 65
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | ERF | NONE | 3 | 893 | 102946 | 0.17779 | 0.0015422 | 115.2811
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 2 | 682 | 23452 | 0.041466 | 0.0012059 | 34.3871
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 3 | 8 | 770 | 0.0013615 | 1.4145e-05 | 96.25
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | WU | POLE | 1 | 114 | 7068 | 0.012389 | 0.00019982 | 62
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 57 | 0.00010078 | 1.7681e-06 | 57
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 150 | 13870 | 0.023954 | 0.00025905 | 92.4667
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 88 | 10317 | 0.018242 | 0.0001556 | 117.2386
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WI | NONE | 9 | 127 | 8205 | 0.01432 | 0.00022166 | 64.6063
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WT | FUSE | 3 | 87 | 73410 | 0.12678 | 0.00015025 | 843.7931
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | VIN | NONE | 7 | 29 | 3136 | 0.0054159 | 5.0084e-05 | 108.1379
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | V | FUSE | 2 | 2 | 155 | 0.00026769 | 3.454e-06 | 77.5
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | CUTOUT | 2 | 2 | 522 | 0.00091106 | 3.4907e-06 | 261
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERO | NONE | 2 | 2 | 51 | 9.0175e-05 | 3.5363e-06 | 25.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | METERING | 1 | 1 | 60 | 0.00010517 | 1.7528e-06 | 60
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 3 | 234 | 0.000418 | 5.359e-06 | 78
AEP-PSO | 2022 | 570502 | PARTIAL POWER | OL | NONE | 2 | 2 | 333 | 0.0005837 | 3.5057e-06 | 166.5
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | OU | NONE | 5 | 1303 | 66453 | 0.11477 | 0.0022503 | 51
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OL | NETWORK TRANSFORMER | 1 | 6 | 780 | 0.0013672 | 1.0517e-05 | 130
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | CROSSARM | 4 | 122 | 6168 | 0.011018 | 0.00021793 | 50.5574
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 2 | 351 | 0.00062062 | 3.5363e-06 | 175.5
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WI | NONE | 2 | 5 | 327 | 0.00057818 | 8.8407e-06 | 65.4
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 81 | 0.00014322 | 1.7681e-06 | 81
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 1 | 1 | 65 | 0.00011611 | 1.7863e-06 | 65
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 2413 | 116106 | 0.20052 | 0.0041673 | 48.1169
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | FUSE | 101 | 1058 | 66391 | 0.11637 | 0.0018545 | 62.7514
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 169 | 6326 | 559022 | 0.97568 | 0.011041 | 88.369
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | SPLICE, OH | 17 | 1233 | 138695 | 0.24523 | 0.0021801 | 112.4858
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | VIN | NONE | 76 | 593 | 57139 | 0.10016 | 0.0010394 | 96.3558
AEP-PSO | 2021 | 565565 | PARTIAL POWER | VIN | NONE | 2 | 3 | 271 | 0.00047917 | 5.3044e-06 | 90.3333
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 4 | 556 | 0.00097458 | 7.0114e-06 | 139
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | CROSSARM | 8 | 918 | 187341 | 0.32838 | 0.0016091 | 204.0752
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | EQF | RELAY | 3 | 2147 | 47234 | 0.082794 | 0.0037634 | 22
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 24 | 3024 | 532038 | 0.93258 | 0.0053006 | 175.9385
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 482 | 12632 | 1405688 | 2.511 | 0.022565 | 111.2799
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 4 | 116 | 16048 | 0.028375 | 0.0002051 | 138.3448
AEP-PSO | 2022 | 570502 | PARTIAL POWER | O | CONN/CLAMP | 2 | 10 | 235 | 0.00041192 | 1.7528e-05 | 23.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | NONE | 1893 | 75322 | 2970099 | 5.3056 | 0.13455 | 39.432
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | NONE | 255 | 9918 | 993806 | 1.7753 | 0.017717 | 100.2023
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | WL | NONE | 5 | 15 | 2194 | 0.0038793 | 2.6522e-05 | 146.2667
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | CROSSARM | 7 | 791 | 86512 | 0.15297 | 0.0013986 | 109.3704
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | U | NONE | 40 | 20874 | 2800662 | 4.952 | 0.036908 | 134.1699
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | CONDUCTOR UG | 398 | 623 | 81886 | 0.14292 | 0.0010873 | 131.4382
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 5 | 42 | 5964 | 0.010545 | 7.4262e-05 | 142
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | METERING | 8 | 8 | 576 | 0.0010185 | 1.4145e-05 | 72
AEP-PSO | 2022 | 570502 | PARTIAL POWER | ABI | NONE | 20 | 27 | 1709 | 0.0029956 | 4.7327e-05 | 63.2963
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | TRANSFORMER, UG | 4 | 56 | 4275 | 0.0076366 | 0.00010004 | 76.3393
AEP-PSO | 2022 | 570502 | PARTIAL POWER | O | NONE | 6 | 12 | 826 | 0.0014478 | 2.1034e-05 | 68.8333
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | POLE | 2 | 11 | 1894 | 0.0033489 | 1.945e-05 | 172.1818
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | EQF | POLE | 2 | 1311 | 67801 | 0.11884 | 0.002298 | 51.717
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | FUSE | 23 | 162 | 11337 | 0.019787 | 0.00028274 | 69.9815
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WL | NONE | 57 | 83 | 9526 | 0.016452 | 0.00014334 | 114.7711
AEP-PSO | 2023 | 572956 | PARTIAL POWER | TIR | NONE | 1 | 1 | 120 | 0.00020944 | 1.7453e-06 | 120
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | WL | NONE | 24 | 14823 | 726613 | 1.2549 | 0.0256 | 49.0193
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | CONN/CLAMP | 1 | 3 | 57 | 0.00010078 | 5.3044e-06 | 19
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | GUY/ANCHOR | 2 | 10 | 316 | 0.00054574 | 1.727e-05 | 31.6
AEP-PSO | 2021 | 565565 | PARTIAL POWER | FO | NONE | 2 | 8 | 280 | 0.00049508 | 1.4145e-05 | 35
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 5 | 912 | 58055 | 0.10026 | 0.001575 | 63.6568
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | VIN | CROSSARM | 1 | 22 | 2772 | 0.0048381 | 3.8397e-05 | 126
AEP-PSO | 2020 | 559804 | PARTIAL POWER | FO | CONDUCTOR UG | 4 | 4 | 424 | 0.00075741 | 7.1454e-06 | 106
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | CROSSARM | 12 | 1037 | 23779 | 0.041067 | 0.0017909 | 22.9306
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERO | TRANSFORMER, OH | 1 | 1 | 218 | 0.00038212 | 1.7528e-06 | 218
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | ERF | NONE | 1 | 832 | 16640 | 0.028738 | 0.0014369 | 20
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 88 | 2177 | 545496 | 0.94208 | 0.0037597 | 250.5723
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | ARRESTER | 9 | 263 | 24704 | 0.042664 | 0.00045421 | 93.9316
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | CROSSARM | 2 | 10 | 704 | 0.0012158 | 1.727e-05 | 70.4
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 1 | 88 | 0.0001556 | 1.7681e-06 | 88
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | CROSSARM | 9 | 1977 | 54687 | 0.094446 | 0.0034143 | 27.6616
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | METERING | 5 | 7 | 914 | 0.0016161 | 1.2377e-05 | 130.5714
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 2 | 8 | 357 | 0.00061655 | 1.3816e-05 | 44.625
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WW | CUTOUT | 1 | 1 | 161 | 0.00027805 | 1.727e-06 | 161
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 12 | 1863 | 0.003328 | 2.1436e-05 | 155.25
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | CONN/CLAMP | 2 | 673 | 38398 | 0.068592 | 0.0012022 | 57.055
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FO | POLE | 1 | 51 | 7065 | 0.012331 | 8.9012e-05 | 138.5294
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | FUSE | 4 | 69 | 1921 | 0.0034316 | 0.00012326 | 27.8406
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 43 | 8716 | 0.015053 | 7.4262e-05 | 202.6977
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | VIN | FUSE | 2 | 4 | 320 | 0.00056581 | 7.0726e-06 | 80
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 2 | 33 | 3818 | 0.0065938 | 5.6992e-05 | 115.697
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | CONN/CLAMP | 3 | 13 | 1915 | 0.0033072 | 2.2451e-05 | 147.3077
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | CROSSARM | 1 | 2 | 84 | 0.00014724 | 3.5057e-06 | 42
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 417 | 56955 | 0.099833 | 0.00073094 | 136.5827
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 19 | 209 | 0.00036095 | 3.2813e-05 | 11
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 275 | 0.00047493 | 1.727e-06 | 275
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 7 | 210 | 0.00037131 | 1.2377e-05 | 30
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 1 | 8 | 1.4291e-05 | 1.7863e-06 | 8
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 1 | 16 | 5889 | 0.010278 | 2.7925e-05 | 368.0625
AEP-PSO | 2024 | 579031 | PARTIAL POWER | TOR | CONDUCTOR UG | 2 | 2 | 502 | 0.00086697 | 3.454e-06 | 251
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 1 | 1235 | 0.0022061 | 1.7863e-06 | 1235
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 16 | 3562 | 0.0061517 | 2.7632e-05 | 222.625
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 728 | 184184 | 0.31809 | 0.0012573 | 253
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | OU | NONE | 1 | 181 | 15396 | 0.027502 | 0.00032333 | 85.0608
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 2 | 15 | 2718 | 0.004694 | 2.5905e-05 | 181.2
AEP-PSO | 2025 | 579031 | PARTIAL POWER | OL | FUSE | 1 | 1 | 97 | 0.00016752 | 1.727e-06 | 97
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | EQF | JUMPER/RISER | 4 | 3006 | 1029477 | 1.7779 | 0.0051914 | 342.4741
AEP-PSO | 2023 | 572956 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 3 | 222 | 0.00038746 | 5.236e-06 | 74
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 2 | 272 | 0.00048588 | 3.5727e-06 | 136
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 10 | 4100 | 0.0071867 | 1.7528e-05 | 410
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | ARRESTER | 1 | 1 | 149 | 0.00026117 | 1.7528e-06 | 149
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | FW | NONE | 4 | 963 | 131974 | 0.22792 | 0.0016631 | 137.0447
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 237 | 14301 | 0.025546 | 0.00042336 | 60.3418
AEP-PSO | 2020 | 559804 | PARTIAL POWER | O | FUSE | 1 | 1 | 48 | 8.5744e-05 | 1.7863e-06 | 48
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | EQF | CONN/CLAMP | 1 | 30 | 2940 | 0.0051534 | 5.2585e-05 | 98
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 133 | 13832 | 0.024245 | 0.00023313 | 104
AEP-PSO | 2021 | 565565 | TRANSMISSION STATION | ERF | NONE | 8 | 6369 | 140118 | 0.24775 | 0.011261 | 22
AEP-PSO | 2022 | 570502 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 150 | 0.00026293 | 1.7528e-06 | 150
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | TIR | FUSE | 1 | 6 | 870 | 0.001525 | 1.0517e-05 | 145
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WFS | TRANSFORMER, UG | 1 | 2 | 130 | 0.00023222 | 3.5727e-06 | 65
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | PEDESTAL | 1 | 3 | 552 | 0.00096757 | 5.2585e-06 | 184
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | POLE | 25 | 375 | 18312 | 0.032098 | 0.00065732 | 48.832
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | V | NONE | 34 | 168 | 12887 | 0.022589 | 0.00029448 | 76.7083
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 30 | 2329 | 565151 | 0.99062 | 0.0040824 | 242.6582
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CE | NONE | 13 | 472 | 44555 | 0.078098 | 0.00082734 | 94.3962
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 2 | 401 | 0.00070289 | 3.5057e-06 | 200.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | CROSSARM | 4 | 29 | 5362 | 0.0093987 | 5.0832e-05 | 184.8966
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | NONE | 262 | 19572 | 1251155 | 2.2122 | 0.034606 | 63.9258
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 77 | 317 | 59656 | 0.10457 | 0.00055565 | 188.1893
AEP-PSO | 2022 | 570502 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 109 | 0.00019106 | 1.7528e-06 | 109
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | PEDESTAL | 6 | 23 | 895 | 0.0015688 | 4.0315e-05 | 38.913
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 71 | 819 | 186979 | 0.33401 | 0.001463 | 228.3016
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | POLE | 38 | 264 | 38353 | 0.068511 | 0.00047159 | 145.2765
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WT | NONE | 1 | 1 | 31 | 5.5377e-05 | 1.7863e-06 | 31
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 8 | 193 | 35605 | 0.062955 | 0.00034125 | 184.4819
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 2 | 8 | 539 | 0.00094478 | 1.4023e-05 | 67.375
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | R | ARRESTER | 2 | 560 | 67564 | 0.12069 | 0.0010004 | 120.65
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CE | FUSE | 1 | 2 | 120 | 0.00021034 | 3.5057e-06 | 60
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 168 | 399 | 30508 | 0.053247 | 0.00069639 | 76.4612
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 5 | 1350 | 0.002387 | 8.8407e-06 | 270
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | CUTOUT | 2 | 5 | 828 | 0.0014514 | 8.7642e-06 | 165.6
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 289 | 11560 | 0.020263 | 0.00050657 | 40
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | FUSE | 4 | 191 | 21161 | 0.037092 | 0.00033479 | 110.7906
AEP-PSO | 2023 | 572956 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 4 | 5 | 456 | 0.00079587 | 8.7267e-06 | 91.2
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 16 | 17 | 1404 | 0.0024504 | 2.9671e-05 | 82.5882
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | V | NONE | 34 | 6210 | 133473 | 0.23843 | 0.011093 | 21.4932
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | INSULATOR | 3 | 2053 | 411764 | 0.71113 | 0.0035456 | 200.567
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WT | NONE | 22 | 1385 | 607268 | 1.0488 | 0.0023919 | 438.4606
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 100 | 672 | 158419 | 0.27359 | 0.0011606 | 235.7426
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | F | POLE | 10 | 1015 | 108966 | 0.19018 | 0.0017715 | 107.3557
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CO | METERING | 4 | 4 | 192 | 0.00034298 | 7.1454e-06 | 48
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 6 | 7 | 601 | 0.0010489 | 1.2217e-05 | 85.8571
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | U | NONE | 33 | 33612 | 1392927 | 2.4311 | 0.058664 | 41.4414
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | CUTOUT | 13 | 203 | 22495 | 0.039261 | 0.0003543 | 110.8128
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 3 | 25 | 1627 | 0.0029064 | 4.4658e-05 | 65.08
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | CROSSARM | 9 | 1570 | 191220 | 0.33374 | 0.0027402 | 121.7962
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 3 | 452 | 41769 | 0.072136 | 0.00078061 | 92.4093
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | FW | NONE | 1 | 146 | 2774 | 0.0049048 | 0.00025815 | 19
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 6 | 975 | 125100 | 0.21605 | 0.0016838 | 128.3077
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | PEDESTAL | 2 | 5 | 248 | 0.0004385 | 8.8407e-06 | 49.6
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 7 | 89 | 10085 | 0.017417 | 0.00015371 | 113.3146
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OU | NONE | 20 | 229 | 15329 | 0.026474 | 0.00039549 | 66.9389
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | CROSSARM | 3 | 35 | 10883 | 0.018994 | 6.1087e-05 | 310.9429
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 10 | 43 | 2838 | 0.0049013 | 7.4262e-05 | 66
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 80 | 7168 | 550603 | 0.9509 | 0.012379 | 76.814
AEP-PSO | 2024 | 579031 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 6 | 5826 | 0.010062 | 1.0362e-05 | 971
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERO | SWITCH, OH | 2 | 1227 | 14724 | 0.025429 | 0.0021191 | 12
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | CROSSARM | 10 | 2562 | 337115 | 0.58221 | 0.0044246 | 131.5827
AEP-PSO | 2025 | 579031 | PARTIAL POWER | ERF | CONDUCTOR UG | 2 | 3 | 290 | 0.00050084 | 5.1811e-06 | 96.6667
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 2 | 35 | 10502 | 0.018569 | 6.1885e-05 | 300.0571
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | FUSE | 6 | 118 | 8966 | 0.015484 | 0.00020379 | 75.9831
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 2 | 232 | 0.00041443 | 3.5727e-06 | 116
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OU | FUSE | 2 | 11 | 560 | 0.00096713 | 1.8997e-05 | 50.9091
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | BREAKER | 7 | 1623 | 137231 | 0.237 | 0.002803 | 84.5539
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 19 | 1254 | 0.0021657 | 3.2813e-05 | 66
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 8 | 10 | 1574 | 0.0027183 | 1.727e-05 | 157.4
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 1 | 1 | 104 | 0.00017961 | 1.727e-06 | 104
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 36 | 14180 | 0.024489 | 6.2173e-05 | 393.8889
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 104 | 0.0001823 | 3.5057e-06 | 52
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | WW | REGULATOR | 3 | 710 | 93010 | 0.16063 | 0.0012262 | 131
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 2 | 3 | 212 | 0.00037001 | 5.236e-06 | 70.6667
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 2 | 2 | 80 | 0.00013816 | 3.454e-06 | 40
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | CROSSARM | 1 | 1 | 377 | 0.00065109 | 1.727e-06 | 377
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 111 | 0.0001917 | 1.727e-06 | 111
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 2 | 484 | 0.00083588 | 3.454e-06 | 242
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | PEDESTAL | 5 | 6 | 917 | 0.0015837 | 1.0362e-05 | 152.8333
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | POLE HARDWARE | 1 | 1115 | 91430 | 0.16166 | 0.0019715 | 82
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 1 | 3 | 507 | 0.00089645 | 5.3044e-06 | 169
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 2 | 17 | 1575 | 0.0028135 | 3.0368e-05 | 92.6471
AEP-PSO | 2020 | 559804 | PARTIAL POWER | VIN | ARRESTER | 1 | 3 | 141 | 0.00025187 | 5.359e-06 | 47
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | U | CIRCUIT SWITCHER | 1 | 1007 | 7049 | 0.012592 | 0.0017988 | 7
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | OL | FUSE | 2 | 519 | 51729 | 0.092406 | 0.00092711 | 99.6705
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WI | CROSSARM | 3 | 27 | 6693 | 0.011559 | 4.663e-05 | 247.8889
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | NONE | 109 | 8892 | 1481583 | 2.6197 | 0.015722 | 166.6198
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | R | RELAY | 4 | 3909 | 141296 | 0.24983 | 0.0069117 | 36.1463
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | METERING | 17 | 18 | 1417 | 0.0024838 | 3.1551e-05 | 78.7222
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 332 | 4591 | 336309 | 0.59464 | 0.0081175 | 73.254
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WFS | NONE | 3 | 4 | 294 | 0.00051534 | 7.0114e-06 | 73.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 67 | 4748 | 713889 | 1.2623 | 0.0083951 | 150.3557
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 11 | 23 | 1896 | 0.0033869 | 4.1086e-05 | 82.4348
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | POLE | 11 | 646 | 187793 | 0.33204 | 0.0011422 | 290.7012
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 22 | 128 | 22103 | 0.038577 | 0.0002234 | 172.6797
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | SWITCH, OH | 4 | 4340 | 284330 | 0.49839 | 0.0076073 | 65.5138
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | CUTOUT | 9 | 320 | 27629 | 0.048429 | 0.00056091 | 86.3406
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | POLE HARDWARE | 2 | 312 | 96492 | 0.16914 | 0.00054689 | 309.2692
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 2 | 12 | 2.1218e-05 | 3.5363e-06 | 6
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WL | ARRESTER | 3 | 3 | 131 | 0.00023401 | 5.359e-06 | 43.6667
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 6 | 408 | 0.00072883 | 1.0718e-05 | 68
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | U | NONE | 15 | 13506 | 661690 | 1.1598 | 0.023674 | 48.9923
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 62 | 0.00010868 | 1.7528e-06 | 62
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | CONDUCTOR UG | 12 | 52 | 7024 | 0.012259 | 9.0757e-05 | 135.0769
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | AO | NONE | 2 | 306 | 18336 | 0.032002 | 0.00053407 | 59.9216
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | SWITCH, OH | 9 | 5592 | 225487 | 0.39355 | 0.0097599 | 40.3231
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | SPLICE, OH | 38 | 992 | 26935 | 0.046517 | 0.0017132 | 27.1522
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | POLE | 11 | 82 | 16739 | 0.028909 | 0.00014162 | 204.1341
AEP-PSO | 2020 | 559804 | PARTIAL POWER | ABI | NONE | 25 | 35 | 2348 | 0.0041943 | 6.2522e-05 | 67.0857
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WL | FUSE | 14 | 22 | 2274 | 0.0039273 | 3.7995e-05 | 103.3636
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 25 | 3546 | 0.006189 | 4.3633e-05 | 141.84
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 1506 | 82351 | 0.14373 | 0.0026285 | 54.6819
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | WU | NONE | 7 | 4628 | 487889 | 0.85153 | 0.0080774 | 105.4211
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WU | FUSE | 3 | 35 | 12963 | 0.022387 | 6.0446e-05 | 370.3714
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | WL | NONE | 4 | 3492 | 58147 | 0.10149 | 0.0060947 | 16.6515
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | ERF | NONE | 1 | 205 | 10660 | 0.018848 | 0.00036247 | 52
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | SWITCH, UG | 2 | 881 | 110356 | 0.19513 | 0.0015577 | 125.2622
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | METERING | 21 | 23 | 1940 | 0.0033504 | 3.9722e-05 | 84.3478
AEP-PSO | 2023 | 572956 | PARTIAL POWER | FO | FUSE | 1 | 1 | 60 | 0.00010472 | 1.7453e-06 | 60
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TR | SPLICE, OH | 1 | 1 | 20 | 3.454e-05 | 1.727e-06 | 20
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | PEDESTAL | 4 | 5 | 550 | 0.00095993 | 8.7267e-06 | 110
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 124 | 25930 | 0.044782 | 0.00021415 | 209.1129
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | WU | CROSSARM | 2 | 521 | 34924 | 0.062386 | 0.00093068 | 67.0326
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WL | CONDUCTOR UG | 1 | 20 | 18440 | 0.032184 | 3.4907e-05 | 922
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | AO | NONE | 6 | 5726 | 724887 | 1.2519 | 0.0098889 | 126.5957
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 25 | 4.3176e-05 | 1.727e-06 | 25
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 22 | 260 | 43299 | 0.074778 | 0.00044903 | 166.5346
AEP-PSO | 2020 | 559804 | PARTIAL POWER | O | NONE | 5 | 822 | 39000 | 0.069667 | 0.0014684 | 47.4453
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | INSULATOR | 3 | 161 | 60267 | 0.10766 | 0.0002876 | 374.3292
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CO | TRANSFORMER, UG | 1 | 8 | 848 | 0.0015148 | 1.4291e-05 | 106
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | JUMPER/RISER | 18 | 19670 | 2678562 | 4.7848 | 0.035137 | 136.175
AEP-PSO | 2024 | 579031 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 127 | 0.00021933 | 1.727e-06 | 127
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 829 | 283551 | 0.4897 | 0.0014317 | 342.0398
AEP-PSO | 2025 | 579031 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 49 | 8.4624e-05 | 1.727e-06 | 49
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | WL | CUTOUT | 1 | 1 | 33 | 5.7844e-05 | 1.7528e-06 | 33
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 45 | 16484 | 0.028894 | 7.8878e-05 | 366.3111
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 3 | 21 | 2152 | 0.003805 | 3.7131e-05 | 102.4762
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WH | NONE | 1 | 1 | 42 | 7.3304e-05 | 1.7453e-06 | 42
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | WL | ARRESTER | 1 | 800 | 89485 | 0.15618 | 0.0013963 | 111.8563
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 89 | 6675 | 0.011802 | 0.00015736 | 75
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 3 | 4 | 947 | 0.0016599 | 7.0114e-06 | 236.75
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 11 | 897 | 0.0015723 | 1.9281e-05 | 81.5455
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | EQF | CROSSARM | 4 | 1099 | 74220 | 0.1301 | 0.0019264 | 67.5341
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | CUTOUT | 11 | 18 | 2343 | 0.0041069 | 3.1551e-05 | 130.1667
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | POLE | 9 | 1730 | 239672 | 0.42011 | 0.0030324 | 138.5387
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERF | NONE | 55 | 17924 | 417323 | 0.7315 | 0.031418 | 23.2829
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | WT | NONE | 5 | 3422 | 402206 | 0.705 | 0.0059982 | 117.5354
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | INSULATOR | 1 | 133 | 11451 | 0.020455 | 0.00023758 | 86.0977
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | WW | NONE | 15 | 3323 | 381753 | 0.66915 | 0.0058247 | 114.882
AEP-PSO | 2021 | 565565 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 230 | 0.00040667 | 3.5363e-06 | 115
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | CONDUCTOR UG | 2 | 467 | 4673 | 0.0082625 | 0.00082572 | 10.0064
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 9 | 46 | 2204 | 0.0038633 | 8.0631e-05 | 47.913
AEP-PSO | 2022 | 570502 | PARTIAL POWER | OU | CONDUCTOR UG | 6 | 6 | 1082 | 0.0018966 | 1.0517e-05 | 180.3333
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERO | METERING | 2 | 2 | 75 | 0.00013261 | 3.5363e-06 | 37.5
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | V | METERING | 11 | 11 | 1089 | 0.0019255 | 1.945e-05 | 99
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 263 | 0.00046502 | 1.7681e-06 | 263
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | AB | RELAY | 15 | 4436 | 390698 | 0.69081 | 0.0078435 | 88.0744
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | CUTOUT | 11 | 44 | 3507 | 0.0061209 | 7.6795e-05 | 79.7045
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TOR | NONE | 28 | 39 | 2827 | 0.00505 | 6.9667e-05 | 72.4872
AEP-PSO | 2022 | 570502 | PARTIAL POWER | FO | NONE | 3 | 156 | 13968 | 0.024484 | 0.00027344 | 89.5385
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | VIN | NONE | 53 | 331 | 39564 | 0.069052 | 0.00057771 | 119.5287
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 740 | 17609 | 2721046 | 4.6993 | 0.030411 | 154.5259
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 3 | 1326 | 0.0023243 | 5.2585e-06 | 442
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 2 | 22 | 3.8563e-05 | 3.5057e-06 | 11
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 12 | 150 | 12792 | 0.022326 | 0.0002618 | 85.28
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | FUSE | 7 | 153 | 18679 | 0.033367 | 0.00027331 | 122.085
AEP-PSO | 2022 | 570502 | PARTIAL POWER | FW | CONDUCTOR UG | 1 | 1 | 71 | 0.00012445 | 1.7528e-06 | 71
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 3 | 12 | 135 | 0.00023663 | 2.1034e-05 | 11.25
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 279 | 29450 | 0.0514 | 0.00048695 | 105.5556
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 23 | 41 | 3038 | 0.0052467 | 7.0808e-05 | 74.0976
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | CUTOUT | 8 | 28 | 5842 | 0.010196 | 4.8869e-05 | 208.6429
AEP-PSO | 2023 | 572956 | PARTIAL POWER | OL | NONE | 7 | 7 | 445 | 0.00077667 | 1.2217e-05 | 63.5714
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 3 | 67 | 16190 | 0.028257 | 0.00011694 | 241.6418
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | POLE HARDWARE | 2 | 2 | 208 | 0.00036777 | 3.5363e-06 | 104
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | V | NONE | 1 | 827 | 16540 | 0.028565 | 0.0014282 | 20
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | FUSE | 16 | 239 | 28873 | 0.049864 | 0.00041276 | 120.8075
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | CROSSARM | 7 | 705 | 180740 | 0.32286 | 0.0012594 | 256.3688
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | FUSE | 4 | 40 | 1397 | 0.0024955 | 7.1454e-05 | 34.925
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | CUTOUT | 10 | 42 | 2471 | 0.0042675 | 7.2535e-05 | 58.8333
AEP-PSO | 2024 | 579031 | PARTIAL POWER | UB | NONE | 1 | 1 | 353 | 0.00060964 | 1.727e-06 | 353
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | METERING | 19 | 41 | 2996 | 0.0051742 | 7.0808e-05 | 73.0732
AEP-PSO | 2024 | 579031 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 69 | 0.00011916 | 1.727e-06 | 69
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | O | NONE | 4 | 1292 | 84248 | 0.1505 | 0.002308 | 65.2074
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OL | FUSE | 2 | 6 | 244 | 0.00043587 | 1.0718e-05 | 40.6667
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 2 | 2 | 133 | 0.00022969 | 3.454e-06 | 66.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | CONDUCTOR UG | 15 | 219 | 20859 | 0.036024 | 0.00037822 | 95.2466
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 170 | 22181 | 0.038713 | 0.00029671 | 130.4765
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 2 | 2 | 140 | 0.00024754 | 3.5363e-06 | 70
AEP-PSO | 2025 | 579031 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 232 | 0.00040067 | 1.727e-06 | 232
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 1 | 148 | 0.0002556 | 1.727e-06 | 148
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WU | CONN/CLAMP | 3 | 3 | 289 | 0.00049911 | 5.1811e-06 | 96.3333
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | OU | NONE | 5 | 8859 | 371439 | 0.64148 | 0.0153 | 41.9279
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | AF | OTHER EQUIPMENT | 1 | 31 | 2263 | 0.0039083 | 5.3538e-05 | 73
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 1 | 1 | 188 | 0.00032468 | 1.727e-06 | 188
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 5 | 635 | 0.0011131 | 8.7642e-06 | 127
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | F | FUSE | 1 | 3 | 264 | 0.00045593 | 5.1811e-06 | 88
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | OU | NONE | 5 | 1990 | 194063 | 0.33515 | 0.0034368 | 97.5191
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 811 | 50282 | 0.087759 | 0.0014155 | 62
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WW | METERING | 1 | 1 | 91 | 0.00015716 | 1.727e-06 | 91
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 106 | 0.00018935 | 1.7863e-06 | 106
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CO | CONN/CLAMP | 4 | 4 | 319 | 0.00055676 | 6.9813e-06 | 79.75
AEP-PSO | 2023 | 572956 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 29 | 5.0615e-05 | 1.7453e-06 | 29
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OL | POLE | 1 | 1 | 125 | 0.00022329 | 1.7863e-06 | 125
AEP-PSO | 2022 | 570502 | PARTIAL POWER | OL | FUSE | 2 | 3 | 166 | 0.00029097 | 5.2585e-06 | 55.3333
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | ABI | ARRESTER | 2 | 2744 | 268912 | 0.46442 | 0.004739 | 98
AEP-PSO | 2023 | 572956 | PARTIAL POWER | ERF | SPLICE, OH | 1 | 1 | 73 | 0.00012741 | 1.7453e-06 | 73
AEP-PSO | 2024 | 579031 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 3 | 189 | 0.00032641 | 5.1811e-06 | 63
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 1 | 11 | 2948 | 0.0051674 | 1.9281e-05 | 268
AEP-PSO | 2022 | 570502 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 6 | 564 | 0.0009886 | 1.0517e-05 | 94
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | A | CUTOUT | 1 | 5 | 690 | 0.0012095 | 8.7642e-06 | 138
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | V | NONE | 33 | 1394 | 132289 | 0.23391 | 0.0024648 | 94.8989
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WW | NONE | 9 | 57 | 17381 | 0.030466 | 9.9912e-05 | 304.9298
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 569 | 75108 | 0.13165 | 0.00099737 | 132
AEP-PSO | 2021 | 565565 | PARTIAL POWER | O | OTHER EQUIPMENT | 2 | 2 | 66 | 0.0001167 | 3.5363e-06 | 33
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | ERF | RELAY | 2 | 2736 | 49248 | 0.086324 | 0.0047958 | 18
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | POLE | 6 | 288 | 58019 | 0.10364 | 0.00051447 | 201.4549
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | POLE | 5 | 117 | 18486 | 0.032403 | 0.00020508 | 158
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 5 | 228 | 0.00039965 | 8.7642e-06 | 45.6
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | CUTOUT | 24 | 2313 | 354754 | 0.63371 | 0.0041318 | 153.374
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | BREAKER | 2 | 2161 | 103593 | 0.18317 | 0.003821 | 47.9375
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ERO | NONE | 7 | 609 | 6219 | 0.010901 | 0.0010675 | 10.2118
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | AF | NONE | 1 | 6 | 180 | 0.00031551 | 1.0517e-05 | 30
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 3 | 295 | 0.00051709 | 5.2585e-06 | 98.3333
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 3011 | 310553 | 0.54202 | 0.0052552 | 103.1395
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 17 | 3995 | 0.0070026 | 2.9798e-05 | 235
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | POLE | 114 | 6533 | 969767 | 1.6748 | 0.011283 | 148.4413
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | INSULATOR | 2 | 408 | 26724 | 0.047738 | 0.00072883 | 65.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | RELAY | 4 | 3631 | 114733 | 0.20495 | 0.0064862 | 31.5982
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | FUSE | 8 | 50 | 2780 | 0.004852 | 8.7267e-05 | 55.6
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | JUMPER/RISER | 17 | 135 | 17294 | 0.029867 | 0.00023315 | 128.1037
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 9 | 12 | 3071 | 0.0053599 | 2.0944e-05 | 255.9167
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 75 | 0.0001309 | 1.7453e-06 | 75
AEP-PSO | 2023 | 572956 | PARTIAL POWER | V | CONN/CLAMP | 1 | 1 | 34 | 5.9341e-05 | 1.7453e-06 | 34
AEP-PSO | 2024 | 579031 | PARTIAL POWER | ABI | FUSE | 8 | 9 | 451 | 0.00077889 | 1.5543e-05 | 50.1111
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | EQF | OTHER EQUIPMENT | 1 | 558 | 96839 | 0.16902 | 0.0009739 | 173.5466
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TR | POLE | 1 | 4 | 228 | 0.00039794 | 6.9813e-06 | 57
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 31 | 8109 | 0.014153 | 5.4105e-05 | 261.5806
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | CUTOUT | 5 | 52 | 9135 | 0.015776 | 8.9805e-05 | 175.6731
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 540 | 127604 | 0.22038 | 0.00093259 | 236.3037
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OL | NONE | 4 | 1190 | 103504 | 0.17875 | 0.0020552 | 86.9782
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | F | CUTOUT | 1 | 1 | 56 | 9.6713e-05 | 1.727e-06 | 56
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 2 | 362 | 0.00064007 | 3.5363e-06 | 181
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 8 | 606 | 101982 | 0.17613 | 0.0010466 | 168.2871
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 3 | 2562 | 160154 | 0.27659 | 0.0044246 | 62.5113
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | CROSSARM | 14 | 1203 | 253963 | 0.4386 | 0.0020776 | 211.1081
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | SPLICE, UG | 2 | 2 | 384 | 0.00066318 | 3.454e-06 | 192
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 1 | 1312 | 76096 | 0.13142 | 0.0022659 | 58
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 116 | 0.00020333 | 3.5057e-06 | 58
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | POLE HARDWARE | 1 | 1 | 115 | 0.00020158 | 1.7528e-06 | 115
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 55 | 9.4986e-05 | 1.727e-06 | 55
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 1 | 43 | 7.5372e-05 | 1.7528e-06 | 43
AEP-PSO | 2023 | 572956 | PARTIAL POWER | CE | TRANSFORMER, OH | 2 | 13 | 1418 | 0.0024749 | 2.2689e-05 | 109.0769
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ABI | FUSE | 4 | 61 | 3177 | 0.0054868 | 0.00010535 | 52.082
AEP-PSO | 2024 | 579031 | PARTIAL POWER | FW | CONDUCTOR UG | 1 | 11 | 1254 | 0.0021657 | 1.8997e-05 | 114
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 54 | 5346 | 0.0092327 | 9.3259e-05 | 99
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 2 | 2 | 505 | 0.00087215 | 3.454e-06 | 252.5
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FO | FUSE | 2 | 37 | 1396 | 0.0024365 | 6.4577e-05 | 37.7297
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 2 | 172 | 0.0003002 | 3.4907e-06 | 86
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | EQF | RELAY | 1 | 339 | 6780 | 0.011709 | 0.00058546 | 20
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | V | POLE | 1 | 12 | 1812 | 0.0031294 | 2.0724e-05 | 151
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WFS | NONE | 2 | 1379 | 341951 | 0.59056 | 0.0023816 | 247.9703
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | TRANSFORMER, POWER - LTC | 1 | 4 | 652 | 0.001126 | 6.9081e-06 | 163
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OU | TRANSFORMER, OH | 1 | 5 | 535 | 0.00092396 | 8.6351e-06 | 107
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 14 | 144 | 11866 | 0.020493 | 0.00024869 | 82.4028
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 64 | 16930 | 0.029239 | 0.00011053 | 264.5312
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 11 | 2151 | 0.0037542 | 1.9199e-05 | 195.5455
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | CUTOUT | 12 | 226 | 21157 | 0.036539 | 0.00039031 | 93.615
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | METERING | 1 | 1 | 43 | 7.6813e-05 | 1.7863e-06 | 43
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 5741 | 300074 | 0.53057 | 0.010151 | 52.2686
AEP-PSO | 2020 | 559804 | PARTIAL POWER | OL | TRANSFORMER, OH | 1 | 2 | 128 | 0.00022865 | 3.5727e-06 | 64
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 1907 | 74672 | 0.13203 | 0.0033718 | 39.1568
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | U | POLE | 1 | 1128 | 203040 | 0.3627 | 0.002015 | 180
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | NETWORK TRANSFORMER | 1 | 7 | 826 | 0.0014605 | 1.2377e-05 | 118
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | EQF | BREAKER | 2 | 288 | 45216 | 0.078089 | 0.00049738 | 157
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | V | REGULATOR | 1 | 314 | 4082 | 0.0070497 | 0.00054229 | 13
AEP-PSO | 2025 | 579031 | DISTRIBUTION STATION | AO | NONE | 2 | 563 | 30812 | 0.053213 | 0.00097231 | 54.7282
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | EQF | BREAKER | 2 | 2587 | 345683 | 0.597 | 0.0044678 | 133.6231
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TIR | FUSE | 1 | 39 | 1053 | 0.0018186 | 6.7354e-05 | 27
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 2 | 273 | 11537 | 0.020223 | 0.00047853 | 42.2601
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 5 | 6537 | 839659 | 1.4501 | 0.01129 | 128.4471
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 2 | 216 | 0.00037304 | 3.454e-06 | 108
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 12 | 821 | 0.0014666 | 2.1436e-05 | 68.4167
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 1 | 354 | 0.00063236 | 1.7863e-06 | 354
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | TRANSFORMER, POWER - LTC | 1 | 3 | 33 | 5.8349e-05 | 5.3044e-06 | 11
AEP-PSO | 2020 | 559804 | PARTIAL POWER | O | CABLE TERMINATOR | 1 | 2 | 152 | 0.00027152 | 3.5727e-06 | 76
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 26 | 988 | 0.0017063 | 4.4903e-05 | 38
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 1 | 24 | 4.1888e-05 | 1.7453e-06 | 24
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 3 | 1097 | 13164 | 0.023074 | 0.0019229 | 12
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | O | TRANSFORMER, POWER - NON LTC | 1 | 256 | 122624 | 0.21177 | 0.00044212 | 479
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | FUSE | 203 | 2319 | 211311 | 0.37039 | 0.0040648 | 91.1216
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WU | NONE | 11 | 24 | 1107 | 0.0019404 | 4.2068e-05 | 46.125
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | INSULATOR | 70 | 8978 | 1308331 | 2.2933 | 0.015737 | 145.7263
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 36 | 2119 | 333493 | 0.58456 | 0.0037143 | 157.3823
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | CROSSARM | 34 | 4218 | 240676 | 0.42187 | 0.0073935 | 57.0593
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 365 | 2169 | 298997 | 0.52867 | 0.0038351 | 137.8502
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | CONDUCTOR UG | 41 | 48 | 4840 | 0.0084838 | 8.4136e-05 | 100.8333
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 10 | 58 | 6358 | 0.011145 | 0.00010166 | 109.6207
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OL | FUSE | 14 | 1188 | 70427 | 0.12345 | 0.0020824 | 59.282
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 178 | 8108 | 523286 | 0.92524 | 0.014336 | 64.5395
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | NONE | 48 | 438 | 56793 | 0.099549 | 0.00076774 | 129.6644
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 72 | 461 | 74131 | 0.13107 | 0.00081511 | 160.8048
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | ARRESTER | 35 | 2762 | 227656 | 0.40253 | 0.0048836 | 82.4243
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TR | FUSE | 2 | 2 | 245 | 0.00042945 | 3.5057e-06 | 122.5
AEP-PSO | 2020 | 559804 | PARTIAL POWER | U | NONE | 116 | 263 | 16945 | 0.03027 | 0.00046981 | 64.4297
AEP-PSO | 2022 | 570502 | TRANSMISSION LINE | OU | NONE | 3 | 1540 | 148088 | 0.25957 | 0.0026994 | 96.161
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | NONE | 63 | 2632 | 137746 | 0.24355 | 0.0046538 | 52.3351
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WU | FUSE | 3 | 3 | 225 | 0.00039783 | 5.3044e-06 | 75
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | NONE | 1608 | 68910 | 2684190 | 4.6848 | 0.12027 | 38.9521
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 22 | 2207 | 483207 | 0.86317 | 0.0039425 | 218.9429
AEP-PSO | 2022 | 570502 | PARTIAL POWER | A | FUSE | 7 | 8 | 572 | 0.0010026 | 1.4023e-05 | 71.5
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 1 | 45 | 8.0385e-05 | 1.7863e-06 | 45
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | JUMPER/RISER | 4 | 4 | 464 | 0.00081332 | 7.0114e-06 | 116
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 116 | 54644 | 0.096618 | 0.0002051 | 471.069
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | EQF | JUMPER/RISER | 4 | 578 | 45664 | 0.080042 | 0.0010131 | 79.0035
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 139 | 0.00024365 | 1.7528e-06 | 139
AEP-PSO | 2022 | 570502 | PARTIAL POWER | O | FUSE | 1 | 1 | 100 | 0.00017528 | 1.7528e-06 | 100
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | POLE | 2 | 10 | 3143 | 0.0056145 | 1.7863e-05 | 314.3
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WU | NONE | 15 | 19 | 1712 | 0.0030582 | 3.394e-05 | 90.1053
AEP-PSO | 2023 | 572956 | PARTIAL POWER | CE | OTHER EQUIPMENT | 1 | 2 | 130 | 0.00022689 | 3.4907e-06 | 65
AEP-PSO | 2023 | 572956 | PARTIAL POWER | ERF | CONN/CLAMP | 5 | 8 | 775 | 0.0013526 | 1.3963e-05 | 96.875
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 14 | 206 | 43919 | 0.075849 | 0.00035577 | 213.199
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TR | NONE | 10 | 824 | 58823 | 0.10159 | 0.0014231 | 71.3871
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | FUSE | 3 | 23 | 1768 | 0.0031582 | 4.1086e-05 | 76.8696
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | ABI | NONE | 2 | 270 | 20815 | 0.036329 | 0.00047124 | 77.0926
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | F | CROSSARM | 3 | 208 | 31971 | 0.0558 | 0.00036303 | 153.7067
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WI | CONDUCTOR UG | 1 | 1 | 131 | 0.00023401 | 1.7863e-06 | 131
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | FUSE | 251 | 1951 | 125193 | 0.21621 | 0.0033694 | 64.1686
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 280 | 24634 | 0.042543 | 0.00048357 | 87.9786
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | EQF | ARRESTER | 2 | 510 | 67681 | 0.11689 | 0.00088078 | 132.7078
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | AB | ARRESTER | 1 | 1177 | 40018 | 0.069112 | 0.0020327 | 34
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WI | NONE | 3 | 46 | 2156 | 0.0037235 | 7.9443e-05 | 46.8696
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | WU | NONE | 1 | 255 | 14806 | 0.02557 | 0.00044039 | 58.0627
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | WW | NONE | 11 | 3149 | 994187 | 1.717 | 0.0054384 | 315.7151
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 4 | 85 | 20190 | 0.035699 | 0.00015029 | 237.5294
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | TRANSFORMER, OH | 2 | 4 | 322 | 0.0005561 | 6.9081e-06 | 80.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 5 | 890 | 0.0015898 | 8.9317e-06 | 178
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | CUTOUT | 4 | 13 | 329 | 0.00056819 | 2.2451e-05 | 25.3077
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 7 | 42 | 7.5026e-05 | 1.2504e-05 | 6
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | FW | BREAKER | 1 | 1625 | 149500 | 0.26706 | 0.0029028 | 92
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WL | TRANSFORMER, OH | 3 | 4 | 783 | 0.0013987 | 7.1454e-06 | 195.75
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | METERING | 2 | 2 | 155 | 0.00026769 | 3.454e-06 | 77.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | TRANSFORMER, GROUNDING | 1 | 1 | 20 | 3.5727e-05 | 1.7863e-06 | 20
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WU | FUSE | 3 | 4 | 281 | 0.00048529 | 6.9081e-06 | 70.25
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 2 | 2 | 160 | 0.00027632 | 3.454e-06 | 80
AEP-PSO | 2025 | 579031 | PARTIAL POWER | ABI | NONE | 1 | 1 | 53 | 9.1532e-05 | 1.727e-06 | 53
AEP-PSO | 2025 | 579031 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 1 | 1 | 75 | 0.00012953 | 1.727e-06 | 75
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | ARRESTER | 1 | 3 | 117 | 0.00020206 | 5.1811e-06 | 39
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CE | CONN/CLAMP | 2 | 6 | 90 | 0.00016077 | 1.0718e-05 | 15
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 36 | 3868 | 0.006751 | 6.2832e-05 | 107.4444
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | EQF | CROSSARM | 3 | 1398 | 41940 | 0.074919 | 0.0024973 | 30
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 9 | 2742 | 0.0048063 | 1.5776e-05 | 304.6667
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | FW | POLE | 3 | 528 | 110398 | 0.1952 | 0.00093358 | 209.0871
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | TRANSFORMER, UG | 1 | 10 | 4680 | 0.0082749 | 1.7681e-05 | 468
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CE | CUTOUT | 1 | 1 | 97 | 0.00017151 | 1.7681e-06 | 97
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WL | ARRESTER | 2 | 2 | 209 | 0.00036954 | 3.5363e-06 | 104.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 77 | 3542 | 0.0063272 | 0.00013755 | 46
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 854 | 36724 | 0.064371 | 0.0014969 | 43.0023
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | CROSSARM | 1 | 126 | 41832 | 0.073965 | 0.00022279 | 332
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | ERF | NONE | 2 | 324 | 2592 | 0.0044764 | 0.00055956 | 8
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 18 | 514 | 98453 | 0.17183 | 0.0008971 | 191.5428
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 131 | 399 | 39765 | 0.069702 | 0.00069938 | 99.6617
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | JUMPER/RISER | 26 | 2196 | 142549 | 0.24987 | 0.0038492 | 64.913
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CF | NONE | 5 | 19 | 786 | 0.0013777 | 3.3304e-05 | 41.3684
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 12 | 660 | 0.0011569 | 2.1034e-05 | 55
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | NONE | 8 | 16 | 723 | 0.0012673 | 2.8045e-05 | 45.1875
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CE | NONE | 31 | 109 | 11248 | 0.019888 | 0.00019273 | 103.1927
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | METERING | 52 | 57 | 4952 | 0.0087558 | 0.00010078 | 86.8772
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | ARRESTER | 143 | 6803 | 485012 | 0.8664 | 0.012152 | 71.2938
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 3 | 271 | 0.0004841 | 5.359e-06 | 90.3333
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TOR | NONE | 14 | 84 | 16440 | 0.029068 | 0.00014852 | 195.7143
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | METERING | 5 | 17 | 1523 | 0.0027206 | 3.0368e-05 | 89.5882
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 38 | 292 | 42328 | 0.074842 | 0.0005163 | 144.9589
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 6 | 1255 | 0.0022419 | 1.0718e-05 | 209.1667
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | AO | FUSE | 1 | 63 | 6139 | 0.010855 | 0.00011139 | 97.4444
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | WI | NONE | 9 | 8189 | 1633280 | 2.8879 | 0.014479 | 199.448
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | NONE | 37 | 203 | 11607 | 0.020734 | 0.00036263 | 57.1773
AEP-PSO | 2022 | 570502 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 99 | 0.00017353 | 1.7528e-06 | 99
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | F | INSULATOR | 1 | 3 | 183 | 0.00032357 | 5.3044e-06 | 61
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | POLE HARDWARE | 2 | 302 | 79611 | 0.13955 | 0.00052936 | 263.6126
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 16 | 123 | 14409 | 0.025739 | 0.00021972 | 117.1463
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WL | FUSE | 5 | 9 | 901 | 0.0015931 | 1.5913e-05 | 100.1111
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | CAPACITOR | 1 | 1147 | 10323 | 0.018253 | 0.0020281 | 9
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TR | NONE | 22 | 203 | 16169 | 0.028883 | 0.00036263 | 79.6502
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | TOR | NONE | 1 | 102 | 11424 | 0.020024 | 0.00017879 | 112
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 295 | 6577 | 1260855 | 2.2006 | 0.011479 | 191.7067
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 9 | 54 | 9.4653e-05 | 1.5776e-05 | 6
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | FUSE | 17 | 303 | 54912 | 0.09584 | 0.00052884 | 181.2277
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 5 | 5 | 1296 | 0.002262 | 8.7267e-06 | 259.2
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | R | NONE | 3 | 2287 | 130294 | 0.22838 | 0.0040088 | 56.9716
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 1779 | 153696 | 0.2694 | 0.0031183 | 86.3946
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | WW | NONE | 20 | 16272 | 761523 | 1.3152 | 0.028102 | 46.7996
AEP-PSO | 2020 | 559804 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 2 | 250 | 0.00044658 | 3.5727e-06 | 125
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | VIN | FUSE | 7 | 43 | 6722 | 0.011732 | 7.5049e-05 | 156.3256
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 374 | 7887 | 1415615 | 2.4448 | 0.013621 | 179.4871
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | CAPACITOR | 2 | 242 | 6411 | 0.011452 | 0.00043229 | 26.4917
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ABI | SWITCH, UG | 1 | 1 | 372 | 0.00064245 | 1.727e-06 | 372
AEP-PSO | 2023 | 572956 | PARTIAL POWER | TOR | CONN/CLAMP | 5 | 5 | 879 | 0.0015341 | 8.7267e-06 | 175.8
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | INSULATOR | 3 | 20 | 2911 | 0.0052 | 3.5727e-05 | 145.55
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | INSULATOR | 2 | 956 | 81724 | 0.14599 | 0.0017077 | 85.4854
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | CONDUCTOR UG | 6 | 7 | 1237 | 0.0021872 | 1.2377e-05 | 176.7143
AEP-PSO | 2023 | 572956 | PARTIAL POWER | TOR | NONE | 8 | 18 | 1933 | 0.0033737 | 3.1416e-05 | 107.3889
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | CROSSARM | 3 | 332 | 23029 | 0.041138 | 0.00059306 | 69.3645
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | EQF | POLE | 5 | 3591 | 53496 | 0.093368 | 0.0062675 | 14.8972
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 12 | 2916 | 0.0050894 | 2.0944e-05 | 243
AEP-PSO | 2023 | 572956 | PARTIAL POWER | FO | NONE | 1 | 1 | 80 | 0.00013963 | 1.7453e-06 | 80
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | WI | NONE | 1 | 246 | 10578 | 0.018896 | 0.00043944 | 43
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | WU | BREAKER | 2 | 649 | 97283 | 0.17201 | 0.0011475 | 149.8968
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 121 | 0.00021119 | 1.7453e-06 | 121
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 1 | 1 | 98 | 0.00016925 | 1.727e-06 | 98
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | POLE | 2 | 8 | 1478 | 0.0026402 | 1.4291e-05 | 184.75
AEP-PSO | 2022 | 570502 | PARTIAL POWER | FW | NONE | 1 | 5 | 1040 | 0.001823 | 8.7642e-06 | 208
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WL | METERING | 1 | 1 | 154 | 0.00027229 | 1.7681e-06 | 154
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 65 | 0.00011611 | 1.7863e-06 | 65
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 28 | 5036 | 0.0086973 | 4.8357e-05 | 179.8571
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 119 | 0.00021257 | 1.7863e-06 | 119
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | NONE | 1742 | 65969 | 2901650 | 5.1305 | 0.11664 | 43.9851
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | CROSSARM | 19 | 3486 | 560875 | 0.98313 | 0.0061104 | 160.8936
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | METERING | 51 | 655 | 70357 | 0.12332 | 0.0011481 | 107.4153
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | CIRCUIT SWITCHER | 5 | 4178 | 183260 | 0.32123 | 0.0073234 | 43.8631
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | POLE | 28 | 3431 | 1074733 | 1.9198 | 0.0061289 | 313.2419
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 51 | 2945 | 375396 | 0.67058 | 0.0052608 | 127.4689
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 3 | 313 | 0.00055343 | 5.3044e-06 | 104.3333
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | FUSE | 13 | 168 | 47234 | 0.083516 | 0.00029705 | 281.1548
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | POLE | 9 | 3039 | 662624 | 1.1615 | 0.0053269 | 218.0401
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 9 | 44 | 6842 | 0.011993 | 7.7125e-05 | 155.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | VIN | FUSE | 4 | 30 | 1785 | 0.0031288 | 5.2585e-05 | 59.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 28 | 1707 | 127463 | 0.22769 | 0.0030493 | 74.6708
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | FW | NONE | 1 | 2 | 102 | 0.00017879 | 3.5057e-06 | 51
AEP-PSO | 2020 | 559804 | PARTIAL POWER | A | NONE | 93 | 295 | 22750 | 0.040639 | 0.00052697 | 77.1186
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | NONE | 45 | 992 | 137992 | 0.2465 | 0.001772 | 139.1048
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | BREAKER | 5 | 3167 | 380160 | 0.67909 | 0.0056573 | 120.0379
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 4 | 252 | 0.00045016 | 7.1454e-06 | 63
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OL | NONE | 22 | 4356 | 385366 | 0.67259 | 0.0076027 | 88.4679
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 3 | 2571 | 394679 | 0.70503 | 0.0045927 | 153.5119
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | ARRESTER | 14 | 25 | 1890 | 0.0033762 | 4.4658e-05 | 75.6
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | FUSE | 269 | 3288 | 457197 | 0.78959 | 0.0056785 | 139.0502
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | NONE | 207 | 23177 | 2960190 | 5.1123 | 0.040027 | 127.721
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | SWITCH, OH | 5 | 1334 | 62087 | 0.11091 | 0.002383 | 46.542
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 3 | 44 | 4931 | 0.0086062 | 7.6795e-05 | 112.0682
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | BREAKER | 1 | 276 | 61795 | 0.11039 | 0.00049303 | 223.8949
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | ARRESTER | 4 | 271 | 23725 | 0.041408 | 0.00047299 | 87.5461
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OU | FUSE | 1 | 12 | 288 | 0.00050266 | 2.0944e-05 | 24
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 5 | 685 | 0.0011956 | 8.7267e-06 | 137
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | CONDUCTOR UG | 7 | 13 | 793 | 0.0013695 | 2.2451e-05 | 61
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | EQF | BREAKER | 7 | 5893 | 557332 | 0.97273 | 0.010285 | 94.5753
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | WW | NONE | 2 | 2922 | 49348 | 0.087254 | 0.0051665 | 16.8884
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | FW | NONE | 14 | 4259 | 185079 | 0.31964 | 0.0073554 | 43.456
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 9 | 1099 | 0.0019432 | 1.5913e-05 | 122.1111
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 253 | 0.00044734 | 1.7681e-06 | 253
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | ABI | ARRESTER | 3 | 1809 | 164316 | 0.28679 | 0.0031573 | 90.8325
AEP-PSO | 2024 | 579031 | PARTIAL POWER | ABI | NONE | 20 | 32 | 1942 | 0.0033539 | 5.5265e-05 | 60.6875
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | TRANSFORMER, GROUNDING | 2 | 6 | 742 | 0.0012815 | 1.0362e-05 | 123.6667
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | BREAKER | 5 | 3758 | 151577 | 0.27077 | 0.0067131 | 40.3345
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | NONE | 233 | 15304 | 719187 | 1.2421 | 0.02643 | 46.9934
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | FUSE | 19 | 200 | 24491 | 0.042297 | 0.0003454 | 122.455
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 1 | 70 | 0.00012089 | 1.727e-06 | 70
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 2 | 152 | 0.00026251 | 3.454e-06 | 76
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | AB | NONE | 16 | 15373 | 869687 | 1.502 | 0.02655 | 56.5724
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 3 | 14 | 2287 | 0.0039497 | 2.4178e-05 | 163.3571
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 63 | 8644 | 0.015284 | 0.00011139 | 137.2063
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 99 | 0.00017505 | 1.7681e-06 | 99
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 2 | 10 | 2612 | 0.004511 | 1.727e-05 | 261.2
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | A | CROSSARM | 3 | 6 | 690 | 0.0011916 | 1.0362e-05 | 115
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | ABI | OTHER EQUIPMENT | 3 | 3162 | 146864 | 0.25364 | 0.0054608 | 46.4466
AEP-PSO | 2020 | 559804 | TRANSMISSION STATION | FW | BREAKER | 1 | 671 | 61732 | 0.11027 | 0.0011986 | 92
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 18 | 810 | 0.0014469 | 3.2154e-05 | 45
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | V | NONE | 2 | 1589 | 26232 | 0.046382 | 0.0028096 | 16.5085
AEP-PSO | 2020 | 559804 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 74 | 0.00013219 | 1.7863e-06 | 74
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 3 | 24 | 4712 | 0.0081377 | 4.1449e-05 | 196.3333
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 4 | 257 | 0.00044855 | 6.9813e-06 | 64.25
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | CABLE TERMINATOR | 2 | 28 | 3107 | 0.0054228 | 4.8869e-05 | 110.9643
AEP-PSO | 2024 | 579031 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 2 | 7 | 611 | 0.0010552 | 1.2089e-05 | 87.2857
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CO | NONE | 2 | 3 | 142 | 0.00024524 | 5.1811e-06 | 47.3333
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | SWITCH, UG | 1 | 775 | 62415 | 0.1094 | 0.0013585 | 80.5355
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 1 | 10 | 4930 | 0.0085142 | 1.727e-05 | 493
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 7 | 638 | 0.0011018 | 1.2089e-05 | 91.1429
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 41 | 189 | 29649 | 0.051205 | 0.00032641 | 156.873
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 3654 | 245294 | 0.42363 | 0.0063105 | 67.1303
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | AO | NONE | 3 | 2423 | 103597 | 0.17891 | 0.0041846 | 42.7557
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | WU | NONE | 4 | 693 | 45721 | 0.078961 | 0.0011968 | 65.9755
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WT | CUTOUT | 1 | 30 | 7560 | 0.013056 | 5.1811e-05 | 252
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CE | NONE | 1 | 3 | 138 | 0.00024189 | 5.2585e-06 | 46
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | WL | NONE | 18 | 8128 | 759801 | 1.3434 | 0.014371 | 93.4795
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 16 | 1667 | 0.0029475 | 2.829e-05 | 104.1875
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 2 | 193 | 0.00034125 | 3.5363e-06 | 96.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 2 | 16 | 5052 | 0.0087249 | 2.7632e-05 | 315.75
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | SPLICE, UG | 4 | 8 | 3371 | 0.0058218 | 1.3816e-05 | 421.375
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WL | TRANSFORMER, OH | 3 | 15 | 1760 | 0.0030396 | 2.5905e-05 | 117.3333
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 1 | 508 | 0.00090746 | 1.7863e-06 | 508
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | JUMPER/RISER | 1 | 746 | 8206 | 0.014172 | 0.0012884 | 11
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CF | CONN/CLAMP | 1 | 9 | 837 | 0.0014455 | 1.5543e-05 | 93
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OU | METERING | 1 | 1 | 39 | 6.7354e-05 | 1.727e-06 | 39
AEP-PSO | 2024 | 579031 | PARTIAL POWER | OL | NONE | 3 | 6 | 1107 | 0.0019118 | 1.0362e-05 | 184.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 2 | 40 | 6.9081e-05 | 3.454e-06 | 20
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | TRANSFORMER, STATION SERVICE | 2 | 3 | 115 | 0.00019861 | 5.1811e-06 | 38.3333
AEP-PSO | 2023 | 572956 | PARTIAL POWER | CO | CONDUCTOR UG | 1 | 1 | 83 | 0.00014486 | 1.7453e-06 | 83
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 12 | 3132 | 0.0054664 | 2.0944e-05 | 261
AEP-PSO | 2021 | 565565 | GENERATION | G | NONE | 9 | 11637 | 675443 | 1.1943 | 0.020576 | 58.0427
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 19 | 1265 | 0.0022078 | 3.3161e-05 | 66.5789
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 14 | 1008 | 0.0017669 | 2.454e-05 | 72
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WW | POLE | 1 | 1 | 140 | 0.0002454 | 1.7528e-06 | 140
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | EQF | BREAKER | 3 | 595 | 54460 | 0.09546 | 0.0010429 | 91.5294
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WT | JUMPER/RISER | 1 | 1 | 17 | 2.9359e-05 | 1.727e-06 | 17
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | U | NONE | 7 | 2477 | 165417 | 0.28995 | 0.0043418 | 66.7812
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WW | JUMPER/RISER | 4 | 5 | 386 | 0.0006766 | 8.7642e-06 | 77.2
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 3 | 639 | 0.0011201 | 5.2585e-06 | 213
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 10 | 37 | 3405 | 0.0059684 | 6.4855e-05 | 92.027
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 55 | 16667 | 0.029215 | 9.6406e-05 | 303.0364
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | JUMPER/RISER | 6 | 28 | 4972 | 0.0087912 | 4.9508e-05 | 177.5714
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | POLE HARDWARE | 4 | 1540 | 98587 | 0.17281 | 0.0026994 | 64.0175
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CO | CONDUCTOR UG | 49 | 69 | 10762 | 0.019029 | 0.000122 | 155.971
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WL | FUSE | 13 | 21 | 1273 | 0.002274 | 3.7513e-05 | 60.619
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | FUSE | 74 | 1380 | 194485 | 0.34388 | 0.00244 | 140.9312
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | CROSSARM | 12 | 269 | 11726 | 0.020733 | 0.00047563 | 43.5911
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WU | NONE | 18 | 84 | 10630 | 0.018795 | 0.00014852 | 126.5476
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | ABX | FUSE | 3 | 22 | 1028 | 0.0018019 | 3.8563e-05 | 46.7273
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | WU | NONE | 3 | 36 | 360 | 0.00063653 | 6.3653e-05 | 10
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | A | NONE | 9 | 1683 | 76422 | 0.13513 | 0.0029758 | 45.4082
AEP-PSO | 2021 | 565565 | TRANSMISSION STATION | AB | NONE | 3 | 39 | 2714 | 0.0047987 | 6.8958e-05 | 69.5897
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 7 | 4841 | 1044399 | 1.8466 | 0.0085596 | 215.7403
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | V | METERING | 8 | 8 | 736 | 0.0013147 | 1.4291e-05 | 92
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | FUSE | 5 | 45 | 2767 | 0.0048501 | 7.8878e-05 | 61.4889
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERO | NONE | 4 | 127 | 16614 | 0.028997 | 0.00022166 | 130.8189
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | PEDESTAL | 15 | 64 | 4783 | 0.0083479 | 0.0001117 | 74.7344
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 7 | 967 | 65360 | 0.11676 | 0.0017274 | 67.5905
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WI | CONN/CLAMP | 3 | 6 | 1220 | 0.0021793 | 1.0718e-05 | 203.3333
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | JUMPER/RISER | 8 | 154 | 21993 | 0.038385 | 0.00026878 | 142.8117
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 2 | 7 | 438 | 0.00075644 | 1.2089e-05 | 62.5714
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 9 | 13 | 881 | 0.0015738 | 2.3222e-05 | 67.7692
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 3 | 2414 | 101388 | 0.17927 | 0.0042683 | 42
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | SWITCH, UG | 1 | 345 | 5175 | 0.0091501 | 0.00061001 | 15
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | BREAKER | 1 | 23 | 4531 | 0.0080115 | 4.0667e-05 | 197
AEP-PSO | 2021 | 565565 | PARTIAL POWER | A | ARRESTER | 1 | 5 | 315 | 0.00055697 | 8.8407e-06 | 63
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 1 | 63 | 0.00011139 | 1.7681e-06 | 63
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 2 | 24 | 4.1888e-05 | 3.4907e-06 | 12
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 1 | 1 | 133 | 0.00023213 | 1.7453e-06 | 133
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 3 | 1398 | 143179 | 0.2499 | 0.00244 | 102.417
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | A | OTHER EQUIPMENT | 1 | 7 | 441 | 0.00076162 | 1.2089e-05 | 63
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 8 | 1952 | 0.0034869 | 1.4291e-05 | 244
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | CONN/CLAMP | 76 | 208 | 16908 | 0.029637 | 0.00036459 | 81.2885
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | FUSE | 80 | 835 | 55050 | 0.097336 | 0.0014764 | 65.9281
AEP-PSO | 2022 | 570502 | PARTIAL POWER | EQF | CROSSARM | 3 | 4 | 363 | 0.00063628 | 7.0114e-06 | 90.75
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 31 | 817 | 94053 | 0.1663 | 0.0014446 | 115.12
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WT | NONE | 5 | 75 | 9691 | 0.016987 | 0.00013146 | 129.2133
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | WW | CONDUCTOR OVERHEAD | 3 | 382 | 35080 | 0.06149 | 0.00066959 | 91.8325
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | NONE | 1666 | 31523 | 3335117 | 5.9577 | 0.056311 | 105.7995
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 397 | 5413 | 815222 | 1.4563 | 0.0096695 | 150.6045
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 55 | 254 | 16229 | 0.028991 | 0.00045373 | 63.8937
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 34 | 3072 | 261540 | 0.4672 | 0.0054876 | 85.1367
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | ARRESTER | 46 | 789 | 84122 | 0.15027 | 0.0014094 | 106.6185
AEP-PSO | 2020 | 559804 | PARTIAL POWER | CO | CONN/CLAMP | 90 | 159 | 12317 | 0.022002 | 0.00028403 | 77.4654
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | POLE | 1 | 1 | 126 | 0.00022508 | 1.7863e-06 | 126
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | BREAKER | 1 | 858 | 6864 | 0.012137 | 0.0015171 | 8
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CF | NONE | 10 | 2534 | 71717 | 0.12681 | 0.0044805 | 28.3019
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 8 | 126 | 13373 | 0.023441 | 0.00022086 | 106.1349
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 11 | 30 | 2923 | 0.0051683 | 5.3044e-05 | 97.4333
AEP-PSO | 2021 | 565565 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 12 | 520 | 0.00091943 | 2.1218e-05 | 43.3333
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | INSULATOR | 10 | 2301 | 225020 | 0.39787 | 0.0040685 | 97.7923
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 1 | 18 | 3.1416e-05 | 1.7453e-06 | 18
AEP-PSO | 2024 | 579031 | PARTIAL POWER | EQF | CONDUCTOR UG | 439 | 666 | 96992 | 0.16751 | 0.0011502 | 145.6336
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 34 | 671 | 117524 | 0.20512 | 0.0011711 | 175.1475
AEP-PSO | 2023 | 572956 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 238 | 0.00041539 | 3.4907e-06 | 119
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 67 | 1570 | 307056 | 0.53029 | 0.0027114 | 195.5771
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 10 | 3420 | 0.005969 | 1.7453e-05 | 342
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 71 | 0.00012683 | 1.7863e-06 | 71
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 6 | 1554 | 0.0027123 | 1.0472e-05 | 259
AEP-PSO | 2023 | 572956 | TRANSMISSION LINE | WU | NONE | 4 | 1925 | 78926 | 0.13775 | 0.0033598 | 41.0005
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 3 | 3897 | 77756 | 0.13571 | 0.0068016 | 19.9528
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | ERF | NONE | 6 | 7503 | 61257 | 0.10737 | 0.013152 | 8.1643
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | FW | CUTOUT | 1 | 3 | 165 | 0.00028922 | 5.2585e-06 | 55
AEP-PSO | 2024 | 579031 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 4 | 7 | 1556 | 0.0026872 | 1.2089e-05 | 222.2857
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | NETWORK TRANSFORMER | 1 | 4 | 116 | 0.0002051 | 7.0726e-06 | 29
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | WU | NONE | 2 | 1604 | 235660 | 0.40699 | 0.0027701 | 146.9202
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 4 | 296 | 0.00051884 | 7.0114e-06 | 74
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | LS | NONE | 11 | 10962 | 792234 | 1.3682 | 0.018932 | 72.2709
AEP-PSO | 2021 | 565565 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 4 | 4 | 210 | 0.00037131 | 7.0726e-06 | 52.5
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | SPLICE, OH | 6 | 7 | 1440 | 0.0025133 | 1.2217e-05 | 205.7143
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TOR | NONE | 98 | 5418 | 478670 | 0.82667 | 0.009357 | 88.3481
AEP-PSO | 2024 | 579031 | PARTIAL POWER | TOR | NONE | 20 | 21 | 1909 | 0.0032969 | 3.6267e-05 | 90.9048
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 31 | 61 | 6508 | 0.011239 | 0.00010535 | 106.6885
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | O | CONDUCTOR OVERHEAD | 1 | 11 | 352 | 0.00062239 | 1.945e-05 | 32
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | JUMPER/RISER | 3 | 10 | 1405 | 0.0024265 | 1.727e-05 | 140.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 6 | 24 | 1030 | 0.0018054 | 4.2068e-05 | 42.9167
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 165 | 0.00029475 | 3.5727e-06 | 82.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 2 | 14 | 1669 | 0.0029255 | 2.454e-05 | 119.2143
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | EQF | CROSSARM | 9 | 9995 | 678865 | 1.2127 | 0.017854 | 67.9205
AEP-PSO | 2024 | 579031 | PARTIAL POWER | A | ARRESTER | 1 | 20 | 1200 | 0.0020724 | 3.454e-05 | 60
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WW | JUMPER/RISER | 4 | 4 | 354 | 0.00061137 | 6.9081e-06 | 88.5
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | METERING | 4 | 4 | 238 | 0.00041103 | 6.9081e-06 | 59.5
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | U | NONE | 7 | 2555 | 31170 | 0.053831 | 0.0044125 | 12.1996
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 29 | 3043 | 0.0054358 | 5.1804e-05 | 104.931
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 2 | 262 | 0.00045924 | 3.5057e-06 | 131
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | ABI | NONE | 4 | 6460 | 54241 | 0.093675 | 0.011157 | 8.3964
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 14 | 1106 | 0.0019101 | 2.4178e-05 | 79
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 9 | 1495 | 0.0026205 | 1.5776e-05 | 166.1111
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | AB | NONE | 2 | 4804 | 337124 | 0.59093 | 0.0084207 | 70.1757
AEP-PSO | 2022 | 570502 | PARTIAL POWER | VIN | NONE | 1 | 4 | 440 | 0.00077125 | 7.0114e-06 | 110
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 3 | 252 | 0.00044172 | 5.2585e-06 | 84
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CE | NONE | 3 | 3 | 215 | 0.00038015 | 5.3044e-06 | 71.6667
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | WI | CONDUCTOR OVERHEAD | 3 | 809 | 140482 | 0.25095 | 0.0014451 | 173.6489
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | CUTOUT | 5 | 15 | 1648 | 0.0028763 | 2.618e-05 | 109.8667
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CE | METERING | 6 | 66 | 3778 | 0.0065247 | 0.00011398 | 57.2424
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 3 | 6 | 451 | 0.00077889 | 1.0362e-05 | 75.1667
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 4 | 35 | 3656 | 0.006314 | 6.0446e-05 | 104.4571
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | EQF | RECLOSER, LINE/OCR/BR | 1 | 832 | 49088 | 0.084776 | 0.0014369 | 59
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | SWITCH, OH | 7 | 1332 | 79814 | 0.13784 | 0.0023004 | 59.9204
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 4 | 19 | 1554 | 0.0026838 | 3.2813e-05 | 81.7895
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | JUMPER/RISER | 5 | 65 | 11358 | 0.020289 | 0.00011611 | 174.7385
AEP-PSO | 2023 | 572956 | PARTIAL POWER | ERF | SPLICE, UG | 1 | 1 | 126 | 0.00021991 | 1.7453e-06 | 126
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 51 | 4437 | 0.0076628 | 8.8078e-05 | 87
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | CROSSARM | 10 | 247 | 41705 | 0.072026 | 0.00042657 | 168.8462
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 6 | 90 | 0.00015776 | 1.0517e-05 | 15
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | INSULATOR | 8 | 451 | 53260 | 0.09514 | 0.00080564 | 118.0931
AEP-PSO | 2020 | 559804 | TRANSMISSION STATION | EQF | BREAKER | 5 | 2803 | 57805 | 0.10326 | 0.0050071 | 20.6225
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | O | POLE | 1 | 16 | 4025 | 0.0071168 | 2.829e-05 | 251.5625
AEP-PSO | 2025 | 579031 | PARTIAL POWER | VIN | FUSE | 1 | 1 | 93 | 0.00016061 | 1.727e-06 | 93
AEP-PSO | 2023 | 572956 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 4 | 249 | 0.00043459 | 6.9813e-06 | 62.25
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WW | JUMPER/RISER | 2 | 2 | 344 | 0.0005941 | 3.454e-06 | 172
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 458 | 0.00081814 | 1.7863e-06 | 458
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | EQF | INSULATOR | 3 | 396 | 41580 | 0.07181 | 0.0006839 | 105
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 2 | 2 | 138 | 0.00023833 | 3.454e-06 | 69
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 3 | 231 | 0.00039894 | 5.1811e-06 | 77
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | CABLE TERMINATOR | 1 | 24 | 22968 | 0.039666 | 4.1449e-05 | 957
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 77 | 0.00013298 | 1.727e-06 | 77
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | ABI | NONE | 1 | 1916 | 30656 | 0.053735 | 0.0033584 | 16
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 2 | 56 | 0.00010004 | 3.5727e-06 | 28
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | PEDESTAL | 2 | 10 | 564 | 0.0010075 | 1.7863e-05 | 56.4
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 1 | 457 | 0.00080804 | 1.7681e-06 | 457
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 1 | 1 | 8 | 1.4023e-05 | 1.7528e-06 | 8
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | SPLICE, OH | 1 | 1 | 14 | 2.5009e-05 | 1.7863e-06 | 14
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 3 | 864 | 0.0014921 | 5.1811e-06 | 288
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WT | CONDUCTOR OVERHEAD | 1 | 1 | 156 | 0.00026942 | 1.727e-06 | 156
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 259 | 0.00045204 | 1.7453e-06 | 259
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | BREAKER | 1 | 306 | 26928 | 0.048103 | 0.00054662 | 88
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 3 | 535 | 0.00092396 | 5.1811e-06 | 178.3333
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | WL | BREAKER | 1 | 200 | 26600 | 0.047517 | 0.00035727 | 133
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 43 | 10392 | 0.017947 | 7.4262e-05 | 241.6744
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | CROSSARM | 180 | 18425 | 1875784 | 3.288 | 0.032296 | 101.8065
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 162 | 2669 | 458182 | 0.80312 | 0.0046783 | 171.668
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WL | NONE | 72 | 163 | 16425 | 0.02879 | 0.00028571 | 100.7669
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FW | CONN/CLAMP | 9 | 40 | 1145 | 0.002007 | 7.0114e-05 | 28.625
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 236 | 5212 | 867718 | 1.5342 | 0.0092156 | 166.4847
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | VIN | NONE | 89 | 935 | 88974 | 0.15732 | 0.0016532 | 95.1594
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 362 | 20872 | 2603293 | 4.6504 | 0.037284 | 124.7266
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | METERING | 30 | 34 | 3731 | 0.0066648 | 6.0736e-05 | 109.7353
AEP-PSO | 2021 | 565565 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 124 | 325 | 36444 | 0.064438 | 0.00057465 | 112.1354
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 2 | 88 | 11030 | 0.019503 | 0.0001556 | 125.3409
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TR | NONE | 26 | 1707 | 88572 | 0.15661 | 0.0030182 | 51.8875
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1 | 73 | 0.00012907 | 1.7681e-06 | 73
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | ARRESTER | 5 | 1493 | 136039 | 0.24054 | 0.0026398 | 91.1179
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CF | CUTOUT | 2 | 5 | 257 | 0.00045441 | 8.8407e-06 | 51.4
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | CONDUCTOR UG | 3 | 46 | 2798 | 0.0049045 | 8.0631e-05 | 60.8261
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | CONN/CLAMP | 5 | 274 | 54323 | 0.09522 | 0.00048028 | 198.2591
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 361 | 93909 | 0.16461 | 0.00063278 | 260.1357
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 477 | 16096 | 2048462 | 3.5753 | 0.028093 | 127.2653
AEP-PSO | 2021 | 565565 | PARTIAL POWER | O | NONE | 8 | 18 | 1111 | 0.0019644 | 3.1827e-05 | 61.7222
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 6 | 883 | 0.0015773 | 1.0718e-05 | 147.1667
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 3 | 731 | 21428 | 0.038278 | 0.0013058 | 29.3133
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | CROSSARM | 4 | 1047 | 92983 | 0.16441 | 0.0018512 | 88.809
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | CROSSARM | 4 | 459 | 141154 | 0.25215 | 0.00081993 | 307.5251
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | EQF | ARRESTER | 5 | 1377 | 273587 | 0.48374 | 0.0024347 | 198.6834
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 61 | 5622 | 0.0099405 | 0.00010786 | 92.1639
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CE | METERING | 2 | 5 | 487 | 0.00085363 | 8.7642e-06 | 97.4
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TIR | NONE | 80 | 5047 | 849596 | 1.4828 | 0.0088087 | 168.3368
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | WU | FUSE | 1 | 14 | 3136 | 0.005602 | 2.5009e-05 | 224
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 92 | 7645 | 1699821 | 2.9668 | 0.013343 | 222.3441
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | WU | NONE | 5 | 1539 | 130936 | 0.22951 | 0.0026976 | 85.0786
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 2 | 224 | 0.00040014 | 3.5727e-06 | 112
AEP-PSO | 2020 | 559804 | PARTIAL POWER | TIR | NONE | 6 | 17 | 3519 | 0.0062861 | 3.0368e-05 | 207
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 11 | 24 | 2087 | 0.0036901 | 4.2435e-05 | 86.9583
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 13 | 151 | 58713 | 0.1014 | 0.00026078 | 388.8278
AEP-PSO | 2020 | 559804 | PARTIAL POWER | V | CONN/CLAMP | 1 | 1 | 36 | 6.4308e-05 | 1.7863e-06 | 36
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | CONN/CLAMP | 4 | 24 | 8390 | 0.014643 | 4.1888e-05 | 349.5833
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WI | POLE | 5 | 15 | 2242 | 0.004005 | 2.6795e-05 | 149.4667
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 11 | 8539 | 1076526 | 1.8789 | 0.014903 | 126.0717
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 281 | 55937 | 0.096604 | 0.00048529 | 199.0641
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 2 | 8 | 900 | 0.0015543 | 1.3816e-05 | 112.5
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 106 | 397 | 62952 | 0.10872 | 0.00068563 | 158.5693
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CF | FUSE | 1 | 2 | 42 | 7.2535e-05 | 3.454e-06 | 21
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | PEDESTAL | 2 | 27 | 694 | 0.0011986 | 4.663e-05 | 25.7037
AEP-PSO | 2025 | 579031 | TRANSMISSION LINE | EQF | RELAY | 1 | 576 | 51248 | 0.088506 | 0.00099477 | 88.9722
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | EQF | RECLOSER, LINE/OCR/BR | 4 | 826 | 114493 | 0.19773 | 0.0014265 | 138.6114
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | F | POLE | 1 | 185 | 50320 | 0.089889 | 0.00033047 | 272
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | FO | NONE | 1 | 28 | 3948 | 0.0070525 | 5.0018e-05 | 141
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 6 | 456 | 0.00080627 | 1.0609e-05 | 76
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WW | JUMPER/RISER | 4 | 4 | 241 | 0.00043051 | 7.1454e-06 | 60.25
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 1 | 181 | 0.00031726 | 1.7528e-06 | 181
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ABI | FUSE | 4 | 21 | 954 | 0.0016868 | 3.7131e-05 | 45.4286
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FO | CABLE TERMINATOR | 1 | 32 | 2624 | 0.0046396 | 5.6581e-05 | 82
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | ARRESTER | 2 | 7 | 651 | 0.0011511 | 1.2377e-05 | 93
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | PEDESTAL | 1 | 4 | 152 | 0.00026876 | 7.0726e-06 | 38
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 305 | 0.00053928 | 1.7681e-06 | 305
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WL | TRANSFORMER, OH | 2 | 4 | 160 | 0.00027925 | 6.9813e-06 | 40
AEP-PSO | 2025 | 579031 | DISTRIBUTION STATION | R | NONE | 5 | 5859 | 52867 | 0.091303 | 0.010119 | 9.0232
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | POLE | 2 | 3 | 391 | 0.00068243 | 5.236e-06 | 130.3333
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 1 | 65 | 0.00011226 | 1.727e-06 | 65
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | V | NONE | 1 | 58 | 2692 | 0.0046984 | 0.00010123 | 46.4138
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 51 | 41055 | 0.070903 | 8.8078e-05 | 805
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 5 | 545 | 0.00095121 | 8.7267e-06 | 109
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | INSULATOR | 1 | 37 | 2109 | 0.0036809 | 6.4577e-05 | 57
AEP-PSO | 2024 | 579031 | PARTIAL POWER | A | CONN/CLAMP | 2 | 2 | 119 | 0.00020552 | 3.454e-06 | 59.5
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 551 | 77231 | 0.13796 | 0.00098427 | 140.1652
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 1 | 88 | 0.00015198 | 1.727e-06 | 88
AEP-PSO | 2020 | 559804 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 1 | 2 | 246 | 0.00043944 | 3.5727e-06 | 123
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | SPLICE, OH | 2 | 2 | 183 | 0.00031605 | 3.454e-06 | 91.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CO | CONN/CLAMP | 3 | 3 | 242 | 0.00041794 | 5.1811e-06 | 80.6667
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | FW | NONE | 2 | 1716 | 72072 | 0.12447 | 0.0029636 | 42
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | EQF | BREAKER | 2 | 51 | 17442 | 0.030123 | 8.8078e-05 | 342
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 57 | 17556 | 0.03032 | 9.844e-05 | 308
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 16 | 752 | 0.0013181 | 2.8045e-05 | 47
AEP-PSO | 2021 | 565565 | PARTIAL POWER | AF | CONDUCTOR UG | 1 | 1 | 76 | 0.00013438 | 1.7681e-06 | 76
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | EQF | TRANSFORMER, STATION SERVICE | 3 | 479 | 37841 | 0.065352 | 0.00082724 | 79
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | F | FUSE | 1 | 6 | 894 | 0.001567 | 1.0517e-05 | 149
AEP-PSO | 2024 | 579031 | PARTIAL POWER | OL | FUSE | 1 | 49 | 6174 | 0.010663 | 8.4624e-05 | 126
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | WL | NONE | 3 | 1009 | 91419 | 0.15788 | 0.0017426 | 90.6036
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 1 | 21 | 3.6267e-05 | 1.727e-06 | 21
AEP-PSO | 2024 | 579031 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 1 | 57 | 9.844e-05 | 1.727e-06 | 57
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 3 | 1378 | 290008 | 0.50085 | 0.0023798 | 210.4557
AEP-PSO | 2025 | 579031 | PARTIAL POWER | WL | NONE | 6 | 10 | 1118 | 0.0019308 | 1.727e-05 | 111.8
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 1 | 21 | 3.6267e-05 | 1.727e-06 | 21
AEP-PSO | 2025 | 579031 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 8 | 1800 | 0.0031086 | 1.3816e-05 | 225
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 13 | 1838 | 0.0031743 | 2.2451e-05 | 141.3846
AEP-PSO | 2024 | 579031 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 63 | 0.0001088 | 1.727e-06 | 63
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 14 | 1224 | 0.0021363 | 2.4435e-05 | 87.4286
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | A | CONDUCTOR OVERHEAD | 1 | 99 | 10593 | 0.018923 | 0.00017685 | 107
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 2 | 421 | 68765 | 0.11876 | 0.00072708 | 163.3373
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WI | TRANSFORMER, POWER - LTC | 1 | 5 | 3285 | 0.0058084 | 8.8407e-06 | 657
AEP-PSO | 2020 | 559804 | PARTIAL POWER | U | CONN/CLAMP | 1 | 2 | 246 | 0.00043944 | 3.5727e-06 | 123
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 3 | 72 | 0.00012862 | 5.359e-06 | 24
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 846 | 201657 | 0.36023 | 0.0015112 | 238.3652
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | AO | NONE | 6 | 3254 | 181542 | 0.3243 | 0.0058127 | 55.7904
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | AF | TRANSFORMER, STATION SERVICE | 2 | 510 | 25500 | 0.045552 | 0.00091103 | 50
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 3 | 1302 | 0.0023021 | 5.3044e-06 | 434
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 1 | 35 | 6.0446e-05 | 1.727e-06 | 35
AEP-PSO | 2023 | 572956 | PARTIAL POWER | EQF | CROSSARM | 1 | 24 | 4992 | 0.0087127 | 4.1888e-05 | 208
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | FO | NONE | 3 | 2331 | 144522 | 0.25817 | 0.004164 | 62
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | U | BREAKER | 1 | 43 | 4644 | 0.0080203 | 7.4262e-05 | 108
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TIR | NONE | 117 | 5028 | 656760 | 1.1512 | 0.0088133 | 130.6205
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | NONE | 152 | 6590 | 288775 | 0.50401 | 0.011502 | 43.8202
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 377 | 5213 | 368532 | 0.64598 | 0.0091376 | 70.6948
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | CONN/CLAMP | 92 | 170 | 10097 | 0.017698 | 0.00029798 | 59.3941
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WL | NONE | 62 | 99 | 8920 | 0.015772 | 0.00017505 | 90.101
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 4 | 388 | 0.00068604 | 7.0726e-06 | 97
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | CUTOUT | 4 | 88 | 6028 | 0.010566 | 0.00015425 | 68.5
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 53 | 13313 | 0.023336 | 9.2901e-05 | 251.1887
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WU | CROSSARM | 8 | 607 | 243007 | 0.42595 | 0.001064 | 400.341
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | NONE | 210 | 2496 | 118426 | 0.21155 | 0.0044587 | 47.4463
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | A | NONE | 2991 | 23863 | 1408432 | 2.5159 | 0.042627 | 59.0216
AEP-PSO | 2022 | 570502 | DISTRIBUTION SOURCE | A | NONE | 3 | 1286 | 81695 | 0.1432 | 0.0022542 | 63.5264
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | CONDUCTOR UG | 3 | 10 | 1424 | 0.0025437 | 1.7863e-05 | 142.4
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | EQF | FUSE | 4 | 527 | 6093 | 0.01068 | 0.00092375 | 11.5617
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 3099 | 257991 | 0.45617 | 0.0054795 | 83.2498
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TOR | CONN/CLAMP | 5 | 5 | 594 | 0.0010503 | 8.8407e-06 | 118.8
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | WL | CIRCUIT SWITCHER | 4 | 1545 | 23123 | 0.041306 | 0.0027599 | 14.9663
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 87 | 609 | 0.0010768 | 0.00015383 | 7
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | JUMPER/RISER | 2 | 201 | 4146 | 0.0073307 | 0.0003554 | 20.6269
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | CROSSARM | 179 | 18321 | 1920333 | 3.3516 | 0.031976 | 104.8159
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 5 | 202 | 7642 | 0.013338 | 0.00035256 | 37.8317
AEP-PSO | 2023 | 572956 | PARTIAL POWER | CO | CONN/CLAMP | 2 | 10 | 742 | 0.001295 | 1.7453e-05 | 74.2
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | INSULATOR | 57 | 10012 | 943028 | 1.6459 | 0.017474 | 94.1898
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | POLE | 24 | 1879 | 367197 | 0.63416 | 0.0032451 | 195.4215
AEP-PSO | 2024 | 579031 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 47 | 64 | 6877 | 0.011877 | 0.00011053 | 107.4531
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | METERING | 56 | 78 | 9035 | 0.015604 | 0.00013471 | 115.8333
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 8 | 21 | 1112 | 0.0019864 | 3.7513e-05 | 52.9524
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 372 | 0.00066452 | 5.359e-06 | 124
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | V | CONDUCTOR UG | 5 | 6 | 667 | 0.0011641 | 1.0472e-05 | 111.1667
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 3073 | 216875 | 0.38741 | 0.0054894 | 70.5744
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 9 | 903 | 111330 | 0.19431 | 0.001576 | 123.289
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WW | FUSE | 1 | 3 | 183 | 0.0003194 | 5.236e-06 | 61
AEP-PSO | 2024 | 579031 | DISTRIBUTION SOURCE | EQF | CROSSARM | 9 | 1557 | 120954 | 0.20889 | 0.002689 | 77.684
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 3 | 104 | 0.00018389 | 5.3044e-06 | 34.6667
AEP-PSO | 2021 | 565565 | PARTIAL POWER | CE | METERING | 1 | 1 | 58 | 0.00010255 | 1.7681e-06 | 58
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | ERF | NONE | 49 | 9335 | 321553 | 0.55533 | 0.016122 | 34.446
AEP-PSO | 2024 | 579031 | TRANSMISSION STATION | EQF | CONDUCTOR UG | 2 | 2460 | 20369 | 0.035178 | 0.0042485 | 8.2801
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | VIN | NONE | 37 | 238 | 20186 | 0.034862 | 0.00041103 | 84.8151
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 74 | 6068 | 0.010729 | 0.00013084 | 82
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 473 | 47420 | 0.082764 | 0.00082554 | 100.2537
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 5 | 3229 | 571138 | 0.99683 | 0.0056357 | 176.8777
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | JUMPER/RISER | 3 | 1774 | 145717 | 0.2603 | 0.003169 | 82.1404
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FO | NONE | 43 | 4109 | 233550 | 0.40335 | 0.0070963 | 56.8386
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 84 | 7392 | 0.013205 | 0.00015005 | 88
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | CUTOUT | 4 | 4 | 504 | 0.00087042 | 6.9081e-06 | 126
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 2 | 31 | 6310 | 0.010898 | 5.3538e-05 | 203.5484
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | O | NONE | 9 | 615 | 54435 | 0.094011 | 0.0010621 | 88.5122
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 732 | 90228 | 0.15583 | 0.0012642 | 123.2623
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 6 | 636 | 0.0011361 | 1.0718e-05 | 106
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 1 | 29 | 4958 | 0.0088567 | 5.1804e-05 | 170.9655
AEP-PSO | 2024 | 579031 | TRANSMISSION LINE | EQF | JUMPER/RISER | 16 | 15561 | 1833942 | 3.1673 | 0.026874 | 117.855
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | EQF | SWITCH, OH | 3 | 2166 | 1647389 | 2.9128 | 0.0038298 | 760.5674
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 2 | 82 | 46704 | 0.081514 | 0.00014312 | 569.561
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | INSULATOR | 1 | 46 | 15180 | 0.02684 | 8.1335e-05 | 330
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 180 | 0.00031086 | 5.1811e-06 | 60
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | NONE | 2956 | 23167 | 1382955 | 2.4241 | 0.040608 | 59.695
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 448 | 2058 | 314494 | 0.55126 | 0.0036073 | 152.8154
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 261 | 2319 | 458293 | 0.80332 | 0.0040648 | 197.6253
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 6 | 800 | 0.0014023 | 1.0517e-05 | 133.3333
AEP-PSO | 2021 | 565565 | PARTIAL POWER | A | NONE | 127 | 435 | 23242 | 0.041095 | 0.00076914 | 53.4299
AEP-PSO | 2022 | 570502 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 19 | 32 | 2212 | 0.0038773 | 5.6091e-05 | 69.125
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | FUSE | 7 | 18 | 1385 | 0.0024277 | 3.1551e-05 | 76.9444
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 7 | 35 | 7725 | 0.013541 | 6.1349e-05 | 220.7143
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | ARRESTER | 8 | 367 | 65922 | 0.11555 | 0.00064329 | 179.624
AEP-PSO | 2021 | 565565 | TRANSMISSION LINE | WT | NONE | 11 | 7338 | 1157520 | 2.0467 | 0.012975 | 157.7433
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 38 | 9362 | 1164435 | 2.0589 | 0.016553 | 124.3789
AEP-PSO | 2022 | 570502 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 4 | 312 | 0.00054689 | 7.0114e-06 | 78
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 15 | 6778 | 0.011881 | 2.6293e-05 | 451.8667
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | FUSE | 183 | 2271 | 106658 | 0.19053 | 0.0040568 | 46.9652
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | TIR | NONE | 164 | 8855 | 1236452 | 2.2087 | 0.015818 | 139.6332
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | VIN | NONE | 55 | 539 | 52756 | 0.09424 | 0.00096284 | 97.8776
AEP-PSO | 2021 | 565565 | DISTRIBUTION STATION | EQF | CUTOUT | 1 | 1 | 31 | 5.4812e-05 | 1.7681e-06 | 31
AEP-PSO | 2021 | 565565 | PARTIAL POWER | VIN | FUSE | 1 | 1 | 62 | 0.00010962 | 1.7681e-06 | 62
AEP-PSO | 2020 | 559804 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 868 | 64787 | 0.11573 | 0.0015505 | 74.6394
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | FUSE | 7 | 24 | 1522 | 0.0026911 | 4.2435e-05 | 63.4167
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WFS | NONE | 6 | 28 | 7057 | 0.01237 | 4.908e-05 | 252.0357
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | A | CUTOUT | 16 | 272 | 20811 | 0.036797 | 0.00048093 | 76.511
AEP-PSO | 2022 | 570502 | DISTRIBUTION STATION | WL | NONE | 6 | 254 | 70090 | 0.12286 | 0.00044522 | 275.9449
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | ARRESTER | 2 | 704 | 212272 | 0.37533 | 0.0012448 | 301.5227
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | V | BREAKER | 1 | 802 | 5614 | 0.0099264 | 0.0014181 | 7
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 14 | 42 | 7664 | 0.013551 | 7.4262e-05 | 182.4762
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | EQF | CUTOUT | 284 | 6019 | 615701 | 1.0746 | 0.010505 | 102.2929
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | A | FUSE | 397 | 2585 | 157034 | 0.27408 | 0.0045117 | 60.7482
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 441 | 34839 | 0.0616 | 0.00077975 | 79
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 3 | 183 | 0.00032077 | 5.2585e-06 | 61
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WW | JUMPER/RISER | 2 | 2 | 212 | 0.00037001 | 3.4907e-06 | 106
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OL | GUY/ANCHOR | 1 | 1 | 168 | 0.00029448 | 1.7528e-06 | 168
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | CROSSARM | 11 | 2855 | 709220 | 1.2378 | 0.0049829 | 248.4133
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | CROSSARM | 9 | 676 | 202893 | 0.35412 | 0.0011798 | 300.1376
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | O | NONE | 7 | 219 | 12579 | 0.021955 | 0.00038223 | 57.4384
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WT | FUSE | 1 | 1 | 80 | 0.00014023 | 1.7528e-06 | 80
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 3 | 703 | 54191 | 0.094581 | 0.001227 | 77.0853
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | NONE | 1633 | 38520 | 4561230 | 7.8774 | 0.066525 | 118.412
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 4 | 4628 | 0.0080774 | 6.9813e-06 | 1157
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | JUMPER/RISER | 5 | 89 | 6244 | 0.011154 | 0.00015898 | 70.1573
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 321 | 1645 | 244303 | 0.42192 | 0.002841 | 148.5125
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 7 | 560 | 0.0010004 | 1.2504e-05 | 80
AEP-PSO | 2020 | 559804 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 3 | 4 | 451 | 0.00080564 | 7.1454e-06 | 112.75
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | R | CABLE TERMINATOR | 1 | 2093 | 210327 | 0.36709 | 0.003653 | 100.4907
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | CROSSARM | 13 | 731 | 163567 | 0.28248 | 0.0012625 | 223.7579
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | POLE | 1 | 8 | 288 | 0.00051447 | 1.4291e-05 | 36
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FO | SPLICE, OH | 1 | 1 | 57 | 9.9484e-05 | 1.7453e-06 | 57
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WW | CONN/CLAMP | 8 | 240 | 34811 | 0.061551 | 0.00042435 | 145.0458
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 5 | 25 | 2089 | 0.003646 | 4.3633e-05 | 83.56
AEP-PSO | 2023 | 572956 | DISTRIBUTION SOURCE | A | NONE | 5 | 575 | 32435 | 0.05661 | 0.0010036 | 56.4087
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WU | ARRESTER | 2 | 20 | 2989 | 0.0052168 | 3.4907e-05 | 149.45
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | NONE | 44 | 3438 | 93270 | 0.16108 | 0.0059375 | 27.1291
AEP-PSO | 2023 | 572956 | PARTIAL POWER | WW | CUTOUT | 1 | 1 | 311 | 0.0005428 | 1.7453e-06 | 311
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | FUSE | 153 | 846 | 45212 | 0.078082 | 0.0014611 | 53.4421
AEP-PSO | 2025 | 579031 | PARTIAL POWER | EQF | CONN/CLAMP | 95 | 158 | 11703 | 0.020211 | 0.00027287 | 74.0696
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 9 | 328 | 0.00058592 | 1.6077e-05 | 36.4444
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 4 | 723 | 0.0012486 | 6.9081e-06 | 180.75
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 531 | 63159 | 0.10908 | 0.00091705 | 118.9435
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 33 | 5982 | 0.010441 | 5.7596e-05 | 181.2727
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | METERING | 4 | 4 | 477 | 0.00085208 | 7.1454e-06 | 119.25
AEP-PSO | 2024 | 579031 | PARTIAL POWER | U | FUSE | 11 | 17 | 1003 | 0.0017322 | 2.9359e-05 | 59
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 3 | 730 | 130568 | 0.22549 | 0.0012607 | 178.8603
AEP-PSO | 2020 | 559804 | TRANSMISSION STATION | WU | NONE | 2 | 2533 | 443275 | 0.79184 | 0.0045248 | 175
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 2360 | 103256 | 0.18445 | 0.0042158 | 43.7525
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 11 | 677 | 0.0012094 | 1.965e-05 | 61.5455
AEP-PSO | 2020 | 559804 | PARTIAL POWER | FW | TRANSFORMER, OH | 1 | 6 | 198 | 0.0003537 | 1.0718e-05 | 33
AEP-PSO | 2024 | 579031 | PARTIAL POWER | U | CUTOUT | 1 | 2 | 108 | 0.00018652 | 3.454e-06 | 54
AEP-PSO | 2023 | 572956 | PARTIAL POWER | TOR | FUSE | 1 | 2 | 182 | 0.00031765 | 3.4907e-06 | 91
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TOR | FUSE | 30 | 650 | 102423 | 0.17689 | 0.0011226 | 157.5738
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | U | NONE | 17 | 16327 | 748886 | 1.2933 | 0.028197 | 45.8679
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | CUTOUT | 4 | 107 | 15083 | 0.026049 | 0.00018479 | 140.9626
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 1 | 246 | 0.00042935 | 1.7453e-06 | 246
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WI | NONE | 6 | 437 | 191079 | 0.33 | 0.00075471 | 437.2517
AEP-PSO | 2021 | 565565 | PARTIAL POWER | TOR | POLE | 1 | 8 | 344 | 0.00060824 | 1.4145e-05 | 43
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WW | BREAKER | 1 | 362 | 39096 | 0.06752 | 0.00062518 | 108
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | FW | FUSE | 2 | 18 | 1833 | 0.0031656 | 3.1086e-05 | 101.8333
AEP-PSO | 2025 | 579031 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 12 | 21 | 1497 | 0.0025854 | 3.6267e-05 | 71.2857
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | JUMPER/RISER | 5 | 70 | 16097 | 0.0278 | 0.00012089 | 229.9571
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | TIR | FUSE | 3 | 36 | 5788 | 0.010234 | 6.3653e-05 | 160.7778
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OL | FUSE | 1 | 15 | 2025 | 0.0034972 | 2.5905e-05 | 135
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | CABLE TERMINATOR | 1 | 3 | 60 | 0.00010609 | 5.3044e-06 | 20
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 1 | 62 | 0.00010708 | 1.727e-06 | 62
AEP-PSO | 2024 | 579031 | PARTIAL POWER | ERF | OTHER EQUIPMENT | 1 | 1 | 52 | 8.9805e-05 | 1.727e-06 | 52
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | BREAKER | 1 | 1 | 233 | 0.0004024 | 1.727e-06 | 233
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | WU | NONE | 9 | 4215 | 498928 | 0.89125 | 0.0075294 | 118.3696
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 57 | 2565 | 0.0044768 | 9.9484e-05 | 45
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | WT | POLE | 1 | 20 | 8520 | 0.014934 | 3.5057e-05 | 426
AEP-PSO | 2020 | 559804 | PARTIAL POWER | A | TRANSFORMER, OH | 1 | 1 | 78 | 0.00013933 | 1.7863e-06 | 78
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | VIN | SPLICE, OH | 1 | 2 | 208 | 0.00036777 | 3.5363e-06 | 104
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 10 | 2064 | 0.0036024 | 1.7453e-05 | 206.4
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WFS | SWITCH, UG | 1 | 2 | 428 | 0.00075677 | 3.5363e-06 | 214
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 1 | 49 | 8.5521e-05 | 1.7453e-06 | 49
AEP-PSO | 2020 | 559804 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 166 | 0.00029653 | 1.7863e-06 | 166
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CO | PEDESTAL | 1 | 8 | 328 | 0.00058592 | 1.4291e-05 | 41
AEP-PSO | 2022 | 570502 | PARTIAL POWER | ERF | METERING | 1 | 1 | 86 | 0.00015074 | 1.7528e-06 | 86
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WW | REGULATOR | 1 | 296 | 28712 | 0.050112 | 0.00051662 | 97
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | ERF | FUSE | 1 | 1 | 98 | 0.00017328 | 1.7681e-06 | 98
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | F | METERING | 1 | 20 | 1920 | 0.0033159 | 3.454e-05 | 96
AEP-PSO | 2025 | 579031 | DISTRIBUTION SOURCE | WL | POLE | 1 | 168 | 8400 | 0.014507 | 0.00029014 | 50
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 6 | 696 | 0.001202 | 1.0362e-05 | 116
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 253 | 69575 | 0.12016 | 0.00043694 | 275
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | ABI | NONE | 1 | 1396 | 15356 | 0.02652 | 0.0024109 | 11
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | POLE | 1 | 2 | 44 | 7.5989e-05 | 3.454e-06 | 22
AEP-PSO | 2020 | 559804 | TRANSMISSION LINE | WW | NONE | 8 | 7922 | 440431 | 0.78676 | 0.014151 | 55.5959
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 624 | 88008 | 0.15199 | 0.0010777 | 141.0385
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 1 | 3 | 1293 | 0.002233 | 5.1811e-06 | 431
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | BREAKER | 1 | 145 | 12325 | 0.021286 | 0.00025042 | 85
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | R | NONE | 2 | 1921 | 21194 | 0.036603 | 0.0033176 | 11.0328
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 1 | 255 | 0.00044506 | 1.7453e-06 | 255
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 1 | 225 | 0.00039439 | 1.7528e-06 | 225
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CE | TRANSFORMER, UG | 1 | 5 | 1990 | 0.0034882 | 8.7642e-06 | 398
AEP-PSO | 2024 | 579031 | PARTIAL POWER | CE | NONE | 1 | 2 | 288 | 0.00049738 | 3.454e-06 | 144
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 1 | 583 | 81037 | 0.14205 | 0.0010219 | 139
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | U | ARRESTER | 1 | 3 | 66 | 0.00011569 | 5.2585e-06 | 22
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | BE | ARRESTER | 1 | 1 | 101 | 0.00017858 | 1.7681e-06 | 101
AEP-PSO | 2021 | 565565 | PARTIAL POWER | WI | CONN/CLAMP | 1 | 3 | 249 | 0.00044027 | 5.3044e-06 | 83
AEP-PSO | 2022 | 570502 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 22 | 3.8563e-05 | 1.7528e-06 | 22
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | CO | SWITCH, UG | 1 | 111 | 19827 | 0.035057 | 0.00019626 | 178.6216
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | A | INSULATOR | 1 | 5 | 370 | 0.00064855 | 8.7642e-06 | 74
AEP-PSO | 2022 | 570502 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 1 | 57 | 9.9912e-05 | 1.7528e-06 | 57
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 29 | 5.0084e-05 | 1.727e-06 | 29
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 5 | 545 | 0.00097356 | 8.9317e-06 | 109
AEP-PSO | 2025 | 579031 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 2 | 103 | 0.00017788 | 3.454e-06 | 51.5
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | FO | NONE | 9 | 2080 | 90200 | 0.15578 | 0.0035922 | 43.3654
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WL | SWITCH, OH | 1 | 30 | 7020 | 0.012412 | 5.3044e-05 | 234
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | WT | FUSE | 1 | 15 | 4875 | 0.0086197 | 2.6522e-05 | 325
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WL | POLE | 10 | 592 | 86832 | 0.14996 | 0.0010224 | 146.6757
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 5 | 11 | 632 | 0.001129 | 1.965e-05 | 57.4545
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 4 | 40 | 9280 | 0.016027 | 6.9081e-05 | 232
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 383 | 45194 | 0.078051 | 0.00066145 | 118
AEP-PSO | 2025 | 579031 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 71 | 11519 | 0.019894 | 0.00012262 | 162.2394
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | TR | TRANSFORMER, UG | 1 | 12 | 228 | 0.00039794 | 2.0944e-05 | 19
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | FW | METERING | 2 | 2 | 185 | 0.00032289 | 3.4907e-06 | 92.5
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 1 | 89 | 0.00015371 | 1.727e-06 | 89
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | CE | JUMPER/RISER | 1 | 13 | 2470 | 0.0044123 | 2.3222e-05 | 190
AEP-PSO | 2023 | 572956 | DISTRIBUTION LINE | WL | SWITCH, OH | 3 | 960 | 29974 | 0.052315 | 0.0016755 | 31.2229
AEP-PSO | 2020 | 559804 | DISTRIBUTION SOURCE | OU | NONE | 1 | 205 | 9840 | 0.017578 | 0.0003662 | 48
AEP-PSO | 2024 | 579031 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 1 | 8 | 1.3816e-05 | 1.727e-06 | 8
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 9 | 900 | 0.0016077 | 1.6077e-05 | 100
AEP-PSO | 2021 | 565565 | DISTRIBUTION SOURCE | FO | RECLOSER, LINE/OCR/BR | 1 | 445 | 72535 | 0.12825 | 0.00078682 | 163
AEP-PSO | 2024 | 579031 | DISTRIBUTION STATION | ABX | BREAKER | 1 | 1 | 151 | 0.00026078 | 1.727e-06 | 151
AEP-PSO | 2020 | 559804 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 4 | 773 | 38560 | 0.068881 | 0.0013808 | 49.8836
AEP-PSO | 2021 | 565565 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 3 | 30 | 5.3044e-05 | 5.3044e-06 | 10
AEP-PSO | 2023 | 572956 | DISTRIBUTION STATION | ABX | NONE | 1 | 726 | 42834 | 0.07476 | 0.0012671 | 59
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERO | METERING | 1 | 4 | 420 | 0.00075772 | 7.2163e-06 | 105
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 1 | 1017 | 0.0018348 | 1.8041e-06 | 1017
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WI | ARRESTER | 1 | 4 | 1156 | 0.0020855 | 7.2163e-06 | 289
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 1 | 67 | 0.00012087 | 1.8041e-06 | 67
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | FO | POLE | 1 | 1 | 380 | 0.00068555 | 1.8041e-06 | 380
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | SWITCH, OH | 2 | 24 | 2005 | 0.0036172 | 4.3298e-05 | 83.5417
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ERO | NONE | 1 | 2 | 206 | 0.00037164 | 3.6082e-06 | 103
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | PEDESTAL | 1 | 1 | 60 | 0.00010825 | 1.8041e-06 | 60
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 41 | 24436 | 0.044703 | 7.5004e-05 | 596
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WL | TRANSFORMER, POWER - LTC | 1 | 8 | 1224 | 0.0022252 | 1.4544e-05 | 153
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | TRANSFORMER, OH | 1 | 7 | 1687 | 0.0030611 | 1.2702e-05 | 241
AEP-SEP | 2021 | 546634 | PARTIAL POWER | FO | NONE | 1 | 1 | 68 | 0.0001244 | 1.8294e-06 | 68
AEP-SEP | 2020 | 543859 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 5 | 3208 | 407546 | 0.74936 | 0.0058986 | 127.0405
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | U | POLE | 1 | 12 | 3336 | 0.0061339 | 2.2065e-05 | 278
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 174 | 19662 | 0.035969 | 0.00031831 | 113
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 1 | 158 | 0.00028724 | 1.8179e-06 | 158
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 1 | 40 | 7.2718e-05 | 1.8179e-06 | 40
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WI | CROSSARM | 2 | 168 | 160251 | 0.29466 | 0.0003089 | 953.875
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 16 | 1168 | 0.0021193 | 2.9032e-05 | 73
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | CROSSARM | 3 | 545 | 59493 | 0.10795 | 0.00098891 | 109.1615
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VA | POLE | 77 | 14997 | 2784760 | 5.0239 | 0.027056 | 185.6878
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | POLE | 1 | 1 | 161 | 0.00029453 | 1.8294e-06 | 161
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | AF | ARRESTER | 1 | 40 | 960 | 0.0017562 | 7.3175e-05 | 24
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | CABLE TERMINATOR | 9 | 13 | 2708 | 0.0048855 | 2.3453e-05 | 208.3077
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | SPLICE, OH | 4 | 63 | 5671 | 0.010374 | 0.00011525 | 90.0159
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 2 | 106 | 0.00019391 | 3.6588e-06 | 53
AEP-SEP | 2024 | 554297 | PARTIAL POWER | FO | CONDUCTOR UG | 2 | 7 | 2623 | 0.0047321 | 1.2629e-05 | 374.7143
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | FUSE | 31 | 561 | 43199 | 0.077935 | 0.0010121 | 77.0036
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | CROSSARM | 9 | 1990 | 368023 | 0.66395 | 0.0035901 | 184.9362
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1 | 2 | 102 | 0.00018402 | 3.6082e-06 | 51
AEP-SEP | 2025 | 554297 | PARTIAL POWER | WL | NONE | 7 | 13 | 625 | 0.0011276 | 2.3453e-05 | 48.0769
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 36 | 6084 | 0.010976 | 6.4947e-05 | 169
AEP-SEP | 2025 | 554297 | PARTIAL POWER | WU | NONE | 3 | 32 | 4088 | 0.0073751 | 5.7731e-05 | 127.75
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 5 | 159 | 88202 | 0.15912 | 0.00028685 | 554.7296
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | POLE | 1 | 76 | 18240 | 0.033538 | 0.00013974 | 240
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 1 | 22 | 3960 | 0.0072813 | 4.0452e-05 | 180
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | PEDESTAL | 7 | 78 | 21325 | 0.038472 | 0.00014072 | 273.3974
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 207 | 37342 | 0.067368 | 0.00037345 | 180.3961
AEP-SEP | 2024 | 554297 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 8 | 1046 | 0.0018871 | 1.4433e-05 | 130.75
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 28 | 4536 | 0.0081833 | 5.0514e-05 | 162
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 270 | 0.0004871 | 1.8041e-06 | 270
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 3 | 956 | 563612 | 1.0168 | 0.0017247 | 589.5523
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 2 | 1170 | 0.0021513 | 3.6774e-06 | 585
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 12 | 3501 | 0.0063161 | 2.1649e-05 | 291.75
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TR | POLE | 2 | 61 | 24093 | 0.043466 | 0.00011005 | 394.9672
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 4 | 561 | 0.0010121 | 7.2163e-06 | 140.25
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TIR | CONN/CLAMP | 2 | 7 | 962 | 0.0017355 | 1.2629e-05 | 137.4286
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | POLE HARDWARE | 1 | 7 | 1036 | 0.0018834 | 1.2726e-05 | 148
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | POLE | 1 | 5 | 1180 | 0.0021411 | 9.0725e-06 | 236
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | METERING | 1 | 1 | 122 | 0.00022137 | 1.8145e-06 | 122
AEP-SEP | 2024 | 554297 | DISTRIBUTION SOURCE | U | NONE | 1 | 912 | 9537 | 0.017206 | 0.0016453 | 10.4572
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | CUTOUT | 1 | 8 | 1560 | 0.0028144 | 1.4433e-05 | 195
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CF | TRANSFORMER, OH | 1 | 1 | 42 | 7.6834e-05 | 1.8294e-06 | 42
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | INSULATOR | 1 | 5 | 2105 | 0.0038195 | 9.0725e-06 | 421
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 1 | 17 | 6970 | 0.012671 | 3.0905e-05 | 410
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 42 | 9198 | 0.01669 | 7.6209e-05 | 219
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 1 | 142 | 0.00025815 | 1.8179e-06 | 142
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 5 | 290 | 0.00053323 | 9.1936e-06 | 58
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 96 | 0.00017562 | 1.8294e-06 | 96
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 119 | 15103 | 0.027404 | 0.00021593 | 126.916
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | SWITCH, OH | 2 | 1484 | 437170 | 0.78869 | 0.0026773 | 294.5889
AEP-SEP | 2023 | 551114 | PARTIAL POWER | OL | ARRESTER | 1 | 4 | 336 | 0.00060967 | 7.258e-06 | 84
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 5 | 2154 | 0.0039084 | 9.0725e-06 | 430.8
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | REGULATOR | 1 | 323 | 23902 | 0.043121 | 0.00058272 | 74
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 1 | 117 | 0.0002127 | 1.8179e-06 | 117
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | SPLICE, OH | 2 | 22 | 11474 | 0.02082 | 3.9919e-05 | 521.5455
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 2 | 114 | 0.00020725 | 3.6359e-06 | 57
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | AB | NONE | 14 | 7430 | 1051894 | 1.9341 | 0.013662 | 141.5739
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TR | POLE HARDWARE | 1 | 38 | 6612 | 0.012158 | 6.9871e-05 | 174
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | JUMPER/RISER | 1 | 93 | 18042 | 0.033006 | 0.00017013 | 194
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 80 | 5280 | 0.0096591 | 0.00014635 | 66
AEP-SEP | 2022 | 550071 | PARTIAL POWER | A | CUTOUT | 1 | 7 | 301 | 0.0005472 | 1.2726e-05 | 43
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | SPLICE, OH | 1 | 4 | 372 | 0.00067112 | 7.2163e-06 | 93
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | AF | NONE | 6 | 1959 | 27510 | 0.04963 | 0.0035342 | 14.0429
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 55 | 9.9798e-05 | 1.8145e-06 | 55
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | SPLICE, OH | 2 | 2 | 74 | 0.00013606 | 3.6774e-06 | 37
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 3 | 7 | 2449 | 0.0044437 | 1.2702e-05 | 349.8571
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | POLE | 1 | 10 | 4300 | 0.0078663 | 1.8294e-05 | 430
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | REGULATOR | 3 | 934 | 97656 | 0.17956 | 0.0017174 | 104.5567
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | METERING | 1 | 1 | 269 | 0.0004853 | 1.8041e-06 | 269
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | NONE | 163 | 6223 | 773578 | 1.3956 | 0.011227 | 124.3095
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 154 | 11242 | 0.020671 | 0.00028316 | 73
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 2 | 76 | 0.0001379 | 3.629e-06 | 38
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 19 | 5523 | 0.010022 | 3.4476e-05 | 290.6842
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | SWITCH, UG | 4 | 361 | 91297 | 0.16471 | 0.00065128 | 252.9003
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | FO | TRANSFORMER, UG | 1 | 1 | 303 | 0.00055084 | 1.8179e-06 | 303
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 3 | 740 | 0.0013427 | 5.4435e-06 | 246.6667
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 7 | 1001 | 0.0018406 | 1.2871e-05 | 143
AEP-SEP | 2021 | 546634 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 3 | 234 | 0.00042807 | 5.4881e-06 | 78
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 9 | 79 | 13477 | 0.02478 | 0.00014526 | 170.5949
AEP-SEP | 2024 | 554297 | DISTRIBUTION STATION | U | NONE | 3 | 3267 | 476982 | 0.86052 | 0.005894 | 146
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VA | NONE | 48 | 8410 | 689553 | 1.244 | 0.015172 | 81.992
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 111 | 9324 | 0.016918 | 0.00020141 | 84
AEP-SEP | 2025 | 554297 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 3 | 441 | 0.0007956 | 5.4123e-06 | 147
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ERF | POLE | 2 | 418 | 30457 | 0.054947 | 0.00075411 | 72.8636
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | BREAKER | 1 | 1 | 165 | 0.00029939 | 1.8145e-06 | 165
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | WU | NONE | 1 | 52 | 2600 | 0.0047267 | 9.4533e-05 | 50
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 22 | 2530 | 0.0045643 | 3.969e-05 | 115
AEP-SEP | 2020 | 543859 | DISTRIBUTION SOURCE | AF | NONE | 1 | 965 | 158260 | 0.29099 | 0.0017744 | 164
AEP-SEP | 2020 | 543859 | PARTIAL POWER | VA | NONE | 1 | 1 | 281 | 0.00051668 | 1.8387e-06 | 281
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | CUTOUT | 1 | 1 | 117 | 0.00021404 | 1.8294e-06 | 117
AEP-SEP | 2020 | 543859 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 11 | 2024 | 0.0037216 | 2.0226e-05 | 184
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 525 | 108675 | 0.19881 | 0.00096042 | 207
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 8 | 1208 | 0.0021793 | 1.4433e-05 | 151
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 148 | 2354 | 455733 | 0.8285 | 0.0042794 | 193.5994
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 123 | 549 | 86283 | 0.15656 | 0.00099616 | 157.1639
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | OL | NONE | 165 | 9191 | 2556977 | 4.6484 | 0.016709 | 278.2044
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 24 | 2751 | 309866 | 0.56686 | 0.0050326 | 112.6376
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WL | TRANSFORMER, OH | 8 | 36 | 6902 | 0.012626 | 6.5858e-05 | 191.7222
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 285 | 11399 | 2820138 | 5.1591 | 0.020853 | 247.4022
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 64 | 10513 | 0.019112 | 0.00011635 | 164.2656
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | FO | POLE | 1 | 1 | 1301 | 0.0023651 | 1.8179e-06 | 1301
AEP-SEP | 2020 | 543859 | PARTIAL POWER | U | FUSE | 2 | 4 | 141 | 0.00025926 | 7.3548e-06 | 35.25
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TOR | NONE | 17 | 49 | 8213 | 0.015101 | 9.0097e-05 | 167.6122
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | NONE | 139 | 21298 | 2474559 | 4.55 | 0.039161 | 116.1874
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | ARRESTER | 22 | 282 | 58457 | 0.10749 | 0.00051852 | 207.2943
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | CONDUCTOR UG | 9 | 51 | 7741 | 0.014233 | 9.3774e-05 | 151.7843
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 2 | 174 | 0.00031831 | 3.6588e-06 | 87
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | NONE | 27 | 4510 | 515769 | 0.94354 | 0.0082505 | 114.3612
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | JUMPER/RISER | 7 | 22 | 1737 | 0.0031578 | 3.9995e-05 | 78.9545
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | BREAKER | 7 | 2535 | 105488 | 0.19298 | 0.0046375 | 41.6126
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | METERING | 2 | 2 | 165 | 0.00030339 | 3.6774e-06 | 82.5
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CF | NONE | 1 | 4 | 152 | 0.00027633 | 7.2718e-06 | 38
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 3 | 63 | 52206 | 0.094728 | 0.00011431 | 828.6667
AEP-SEP | 2023 | 551114 | PARTIAL POWER | WL | NONE | 52 | 201 | 25770 | 0.04676 | 0.00036472 | 128.209
AEP-SEP | 2020 | 543859 | PARTIAL POWER | O | NONE | 23 | 52 | 5402 | 0.0099327 | 9.5613e-05 | 103.8846
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WL | CUTOUT | 1 | 2 | 66 | 0.00012074 | 3.6588e-06 | 33
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | SWITCH, OH | 2 | 115 | 13748 | 0.02515 | 0.00021038 | 119.5478
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | JUMPER/RISER | 6 | 296 | 15216 | 0.027978 | 0.00054426 | 51.4054
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 84 | 18414 | 0.033412 | 0.00015242 | 219.2143
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 51 | 7753 | 858191 | 1.5483 | 0.013987 | 110.6915
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | TRANSFORMER, UG | 4 | 29 | 8853 | 0.016064 | 5.2621e-05 | 305.2759
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 1 | 175 | 0.00031572 | 1.8041e-06 | 175
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | BREAKER | 10 | 6358 | 563420 | 1.0165 | 0.01147 | 88.6159
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 98 | 10808 | 0.019499 | 0.0001768 | 110.2857
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 33 | 101 | 36980 | 0.066715 | 0.00018221 | 366.1386
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | METERING | 11 | 24 | 2633 | 0.0047502 | 4.3298e-05 | 109.7083
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | FUSE | 53 | 303 | 23822 | 0.042977 | 0.00054664 | 78.6205
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 18 | 1944 | 0.0035071 | 3.2474e-05 | 108
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 2 | 6 | 1342 | 0.002455 | 1.0976e-05 | 223.6667
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | STATIC WIRE | 4 | 132 | 6060 | 0.010933 | 0.00023814 | 45.9091
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WT | NONE | 2 | 539 | 61113 | 0.11025 | 0.0009724 | 113.3822
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 2 | 826 | 209193 | 0.3774 | 0.0014902 | 253.2603
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 1704 | 182328 | 0.33525 | 0.0031332 | 107
AEP-SEP | 2025 | 554297 | PARTIAL POWER | U | NONE | 7 | 41 | 8830 | 0.01593 | 7.3968e-05 | 215.3659
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WL | ARRESTER | 5 | 12 | 829 | 0.0014956 | 2.1649e-05 | 69.0833
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 802 | 0.0014552 | 1.8145e-06 | 802
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 32 | 5384 | 0.0098494 | 5.854e-05 | 168.25
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 4 | 13 | 1778 | 0.0032077 | 2.3453e-05 | 136.7692
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | AF | BREAKER | 1 | 26 | 2210 | 0.0040636 | 4.7807e-05 | 85
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 3 | 5 | 354 | 0.0006476 | 9.1469e-06 | 70.8
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 519 | 34429 | 0.062113 | 0.00093632 | 66.3372
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | ARRESTER | 10 | 32 | 2744 | 0.0049504 | 5.7731e-05 | 85.75
AEP-SEP | 2024 | 554297 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 12 | 838 | 0.0015118 | 2.1649e-05 | 69.8333
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | ARRESTER | 2 | 385 | 32782 | 0.059142 | 0.00069457 | 85.1481
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 173 | 107952 | 0.19475 | 0.00031211 | 624
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 785 | 131880 | 0.23792 | 0.0014162 | 168
AEP-SEP | 2025 | 554297 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 238 | 0.00042937 | 3.6082e-06 | 119
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 697 | 36244 | 0.066304 | 0.0012751 | 52
AEP-SEP | 2024 | 554297 | PARTIAL POWER | FO | NONE | 2 | 14 | 2752 | 0.0049648 | 2.5257e-05 | 196.5714
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | REGULATOR | 1 | 473 | 9460 | 0.017198 | 0.00085989 | 20
AEP-SEP | 2022 | 550071 | PARTIAL POWER | U | FUSE | 1 | 2 | 74 | 0.00013453 | 3.6359e-06 | 37
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | POLE | 1 | 1 | 112 | 0.00020206 | 1.8041e-06 | 112
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | SPLICE, OH | 1 | 2 | 432 | 0.00078535 | 3.6359e-06 | 216
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 2 | 263 | 0.00047447 | 3.6082e-06 | 131.5
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | AF | TRANSFORMER, POWER - LTC | 1 | 1 | 188 | 0.00034177 | 1.8179e-06 | 188
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 44 | 10498 | 0.018939 | 7.938e-05 | 238.5909
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 4 | 736 | 0.0013464 | 7.3175e-06 | 184
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | FUSE | 1 | 2 | 308 | 0.00055993 | 3.6359e-06 | 154
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 1 | 135 | 0.00024496 | 1.8145e-06 | 135
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 1802 | 147764 | 0.2717 | 0.0033134 | 82
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 82 | 0.00015077 | 1.8387e-06 | 82
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WH | CONN/CLAMP | 1 | 1 | 76 | 0.00013974 | 1.8387e-06 | 76
AEP-SEP | 2025 | 554297 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 4 | 2663 | 42608 | 0.076869 | 0.0048043 | 16
AEP-SEP | 2025 | 554297 | DISTRIBUTION SOURCE | AF | SWITCH, OH | 1 | 29 | 1160 | 0.0020927 | 5.2319e-05 | 40
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 1 | 42 | 7.5772e-05 | 1.8041e-06 | 42
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | POLE | 1 | 122 | 18666 | 0.033934 | 0.00022179 | 153
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WI | CIRCUIT SWITCHER | 1 | 42 | 62496 | 0.11433 | 7.6834e-05 | 1488
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 267 | 2937 | 0.0054003 | 0.00049094 | 11
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 1 | 351 | 0.00064211 | 1.8294e-06 | 351
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 18 | 450 | 0.00081653 | 3.2661e-05 | 25
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | FUSE | 1 | 1 | 234 | 0.00042216 | 1.8041e-06 | 234
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 357 | 14457 | 5505792 | 10.0092 | 0.026282 | 380.8392
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TR | NONE | 99 | 3900 | 577559 | 1.05 | 0.00709 | 148.0921
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | CONDUCTOR UG | 9 | 25 | 6565 | 0.011935 | 4.5449e-05 | 262.6
AEP-SEP | 2021 | 546634 | PARTIAL POWER | VIN | NONE | 25 | 92 | 9116 | 0.016677 | 0.0001683 | 99.087
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 5 | 1658 | 0.0030142 | 9.0897e-06 | 331.6
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 4 | 151 | 23061 | 0.042403 | 0.00027765 | 152.7219
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 285 | 17345 | 4388003 | 8.0683 | 0.031892 | 252.9837
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | ARRESTER | 5 | 157 | 17772 | 0.032512 | 0.00028721 | 113.1975
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 3 | 113 | 47493 | 0.086883 | 0.00020672 | 420.292
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | FUSE | 19 | 268 | 21932 | 0.040122 | 0.00049027 | 81.8358
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | NONE | 79 | 3979 | 407907 | 0.75002 | 0.0073162 | 102.515
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | NONE | 1782 | 18506 | 1433797 | 2.6016 | 0.033579 | 77.4774
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 0 | 0 | 0 | 0
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 11 | 1156 | 105765 | 0.19348 | 0.0021148 | 91.4922
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | AF | NONE | 39 | 19960 | 1556348 | 2.8617 | 0.036701 | 77.9733
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | SWITCH, OH | 3 | 207 | 47667 | 0.087201 | 0.00037868 | 230.2754
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | NONE | 121 | 9948 | 1038062 | 1.8836 | 0.018051 | 104.3488
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 1079 | 336854 | 0.61238 | 0.0019616 | 312.1909
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | POLE | 44 | 3076 | 740617 | 1.3439 | 0.0055814 | 240.7728
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 204 | 3868 | 979352 | 1.7668 | 0.0069782 | 253.1934
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CO | SPLICE, OH | 3 | 13 | 8917 | 0.016087 | 2.3453e-05 | 685.9231
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | CAPACITOR | 8 | 1713 | 120588 | 0.21881 | 0.0031082 | 70.3958
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WH | NONE | 15 | 1749 | 243287 | 0.44733 | 0.0032159 | 139.1006
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 301 | 47515 | 0.087366 | 0.00055345 | 157.8571
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 4 | 48 | 13885 | 0.025531 | 8.8258e-05 | 289.2708
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | CONDUCTOR UG | 4 | 16 | 3185 | 0.0058563 | 2.9419e-05 | 199.0625
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 1 | 262 | 0.00047267 | 1.8041e-06 | 262
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | AF | NONE | 3 | 984 | 25749 | 0.046453 | 0.0017752 | 26.1677
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 4 | 164 | 0.00029587 | 7.2163e-06 | 41
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | CO | NONE | 1 | 2 | 488 | 0.00088039 | 3.6082e-06 | 244
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 318 | 0.00057701 | 1.8145e-06 | 318
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | FO | POLE | 2 | 49 | 10544 | 0.019022 | 8.84e-05 | 215.1837
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | NONE | 905 | 46486 | 6245578 | 11.2676 | 0.083865 | 134.354
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 13 | 429 | 0.00077395 | 2.3453e-05 | 33
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | CONDUCTOR UG | 7 | 16 | 4732 | 0.0085369 | 2.8865e-05 | 295.75
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ABI | FUSE | 4 | 5 | 417 | 0.00076674 | 9.1936e-06 | 83.4
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 5 | 57 | 16982 | 0.031066 | 0.00010427 | 297.9298
AEP-SEP | 2020 | 543859 | PARTIAL POWER | O | JUMPER/RISER | 1 | 1 | 54 | 9.929e-05 | 1.8387e-06 | 54
AEP-SEP | 2024 | 554297 | PARTIAL POWER | ERO | NONE | 1 | 1 | 67 | 0.00012087 | 1.8041e-06 | 67
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | CONN/CLAMP | 3 | 8 | 465 | 0.0008389 | 1.4433e-05 | 58.125
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | CUTOUT | 4 | 30 | 3422 | 0.0061736 | 5.4123e-05 | 114.0667
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 1 | 65 | 0.00011727 | 1.8041e-06 | 65
AEP-SEP | 2024 | 554297 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 2 | 162 | 0.00029226 | 3.6082e-06 | 81
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | CAPACITOR | 1 | 68 | 5712 | 0.010364 | 0.00012339 | 84
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 4 | 796 | 0.0014471 | 7.2718e-06 | 199
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 41 | 5330 | 0.0098003 | 7.5387e-05 | 130
AEP-SEP | 2020 | 543859 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 2 | 286 | 0.00052587 | 3.6774e-06 | 143
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 1 | 108 | 0.00019858 | 1.8387e-06 | 108
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 17 | 799 | 0.0014617 | 3.1099e-05 | 47
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WFS | NONE | 1 | 12 | 1008 | 0.0018325 | 2.1815e-05 | 84
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 1 | 166 | 0.00030178 | 1.8179e-06 | 166
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 33 | 142 | 30651 | 0.055722 | 0.00025815 | 215.8521
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | POLE | 8 | 1164 | 785332 | 1.4277 | 0.0021161 | 674.6838
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | FUSE | 10 | 93 | 22629 | 0.041138 | 0.00016907 | 243.3226
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | CROSSARM | 39 | 9074 | 770068 | 1.4087 | 0.0166 | 84.8653
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 2 | 242 | 0.00044271 | 3.6588e-06 | 121
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 154 | 13090 | 0.024069 | 0.00028316 | 85
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 15 | 965 | 164281 | 0.30053 | 0.0017653 | 170.2394
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 40 | 8640 | 0.015806 | 7.3175e-05 | 216
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | CONDUCTOR UG | 74 | 250 | 72490 | 0.13153 | 0.00045363 | 289.96
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 2 | 47 | 21472 | 0.03928 | 8.5981e-05 | 456.8511
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 4 | 568 | 0.0010391 | 7.3175e-06 | 142
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | AO | NONE | 10 | 10222 | 1467674 | 2.6849 | 0.0187 | 143.5799
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 8 | 2519 | 0.0046082 | 1.4635e-05 | 314.875
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 6 | 1311 | 0.0023833 | 1.0908e-05 | 218.5
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 2 | 290 | 0.00053323 | 3.6774e-06 | 145
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | CONN/CLAMP | 146 | 423 | 51062 | 0.09212 | 0.00076313 | 120.7139
AEP-SEP | 2023 | 551114 | PARTIAL POWER | FO | NONE | 3 | 12 | 1015 | 0.0018417 | 2.1774e-05 | 84.5833
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | FUSE | 63 | 1166 | 479580 | 0.8652 | 0.0021036 | 411.3036
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | CUTOUT | 2 | 239 | 25685 | 0.046988 | 0.00043722 | 107.4686
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 1 | 289 | 0.00052869 | 1.8294e-06 | 289
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | AF | TRANSFORMER, OH | 1 | 21 | 5586 | 0.010271 | 3.8613e-05 | 266
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | CROSSARM | 23 | 4387 | 1060238 | 1.9238 | 0.0079602 | 241.6772
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 27 | 1322 | 208367 | 0.37808 | 0.0023988 | 157.615
AEP-SEP | 2020 | 543859 | PARTIAL POWER | FO | NONE | 5 | 19 | 1997 | 0.0036719 | 3.4936e-05 | 105.1053
AEP-SEP | 2020 | 543859 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 5 | 25 | 3579 | 0.0065807 | 4.5968e-05 | 143.16
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | TRANSFORMER, OH | 9 | 23 | 3531 | 0.0064925 | 4.229e-05 | 153.5217
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | FUSE | 18 | 82 | 10590 | 0.019216 | 0.00014879 | 129.1463
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | SWITCH, UG | 1 | 354 | 73632 | 0.13539 | 0.0006509 | 208
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TIR | CUTOUT | 1 | 3 | 687 | 0.0012466 | 5.4435e-06 | 229
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | POLE | 11 | 983 | 99524 | 0.18059 | 0.0017837 | 101.2452
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 7 | 771 | 0.0014105 | 1.2806e-05 | 110.1429
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | CUTOUT | 12 | 194 | 60200 | 0.10861 | 0.00034999 | 310.3093
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 12 | 2357 | 183667 | 0.33135 | 0.0042522 | 77.9241
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 25 | 486 | 53665 | 0.096816 | 0.00087679 | 110.4218
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 7 | 476 | 0.00087523 | 1.2871e-05 | 68
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | POLE | 1 | 38 | 8930 | 0.01611 | 6.8555e-05 | 235
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TR | POLE | 8 | 1209 | 113536 | 0.20483 | 0.0021811 | 93.909
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1109 | 32534 | 0.058694 | 0.0020007 | 29.3363
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 6 | 115 | 56643 | 0.10219 | 0.00020747 | 492.5478
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | ARRESTER | 5 | 9 | 788 | 0.0014489 | 1.6548e-05 | 87.5556
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 4 | 1496 | 0.0027196 | 7.2718e-06 | 374
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | BREAKER | 10 | 5455 | 523750 | 0.95035 | 0.0098981 | 96.0128
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 1700 | 222700 | 0.40409 | 0.0030847 | 131
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | NONE | 667 | 9205 | 1368312 | 2.4686 | 0.016607 | 148.6488
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 139 | 934 | 238491 | 0.43026 | 0.001685 | 255.3437
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | BREAKER | 1 | 81 | 2592 | 0.0047121 | 0.00014725 | 32
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WFS | NETWORK TRANSFORMER | 1 | 1 | 118 | 0.00021587 | 1.8294e-06 | 118
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | INSULATOR | 5 | 409 | 86961 | 0.15779 | 0.00074213 | 212.6186
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | CUTOUT | 6 | 88 | 5231 | 0.0094917 | 0.00015968 | 59.4432
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | TRANSFORMER, OH | 16 | 31 | 11125 | 0.020456 | 5.7e-05 | 358.871
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | FUSE | 14 | 46 | 4179 | 0.0075828 | 8.3467e-05 | 90.8478
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | TRANSFORMER, UG | 2 | 21 | 12585 | 0.022879 | 3.8177e-05 | 599.2857
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | CUTOUT | 4 | 10 | 632 | 0.0011402 | 1.8041e-05 | 63.2
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 3 | 10 | 2196 | 0.0040378 | 1.8387e-05 | 219.6
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | CONN/CLAMP | 5 | 107 | 27986 | 0.050781 | 0.00019415 | 261.5514
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 4 | 304 | 0.00054844 | 7.2163e-06 | 76
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 2 | 882 | 0.0015912 | 3.6082e-06 | 441
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | CROSSARM | 4 | 1387 | 186660 | 0.3387 | 0.0025167 | 134.5782
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 16 | 1680 | 0.003089 | 2.9419e-05 | 105
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 2 | 132 | 0.00023997 | 3.6359e-06 | 66
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 316 | 74576 | 0.13643 | 0.00057808 | 236
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | CF | CROSSARM | 1 | 29 | 5452 | 0.0098927 | 5.2621e-05 | 188
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 3 | 1356 | 0.0024933 | 5.5161e-06 | 452
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | CONN/CLAMP | 1 | 5 | 340 | 0.00062516 | 9.1936e-06 | 68
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | AF | POLE HARDWARE | 1 | 24 | 2952 | 0.0054003 | 4.3905e-05 | 123
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WW | NONE | 2 | 8 | 3809 | 0.0068718 | 1.4433e-05 | 476.125
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 4 | 376 | 0.00067834 | 7.2163e-06 | 94
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | POLE | 136 | 11452 | 1925337 | 3.5002 | 0.020819 | 168.1223
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | FUSE | 97 | 1268 | 245509 | 0.44632 | 0.0023052 | 193.6191
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 9 | 85 | 15573 | 0.028311 | 0.00015453 | 183.2118
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | FUSE | 31 | 288 | 24984 | 0.045705 | 0.00052686 | 86.75
AEP-SEP | 2022 | 550071 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 2 | 192 | 0.00034905 | 3.6359e-06 | 96
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 11 | 73 | 18859 | 0.0345 | 0.00013354 | 258.3425
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 26 | 133 | 28555 | 0.052238 | 0.00024331 | 214.6992
AEP-SEP | 2021 | 546634 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 40 | 7.3175e-05 | 1.8294e-06 | 40
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 12 | 312 | 54604 | 0.099891 | 0.00057077 | 175.0128
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | ARRESTER | 20 | 891 | 145469 | 0.26612 | 0.00163 | 163.2649
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 1371 | 158726 | 0.28856 | 0.0024924 | 115.7739
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | INSULATOR | 3 | 234 | 36793 | 0.066888 | 0.0004254 | 157.235
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | NONE | 31 | 2251 | 93586 | 0.16981 | 0.0040845 | 41.5753
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 7 | 1589 | 0.0029069 | 1.2806e-05 | 227
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 7 | 860 | 402316 | 0.73974 | 0.0015813 | 467.8093
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 20 | 85 | 12157 | 0.022353 | 0.00015629 | 143.0235
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 2 | 1493 | 340273 | 0.61743 | 0.0027091 | 227.9123
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | SWITCH, OH | 5 | 8 | 1554 | 0.0028036 | 1.4433e-05 | 194.25
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 18 | 1799 | 149015 | 0.27039 | 0.0032643 | 82.8321
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | ARRESTER | 2 | 106 | 11514 | 0.020892 | 0.00019234 | 108.6226
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 1 | 1 | 59 | 0.00010848 | 1.8387e-06 | 59
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 2 | 180 | 0.00033097 | 3.6774e-06 | 90
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | NONE | 237 | 24128 | 1907852 | 3.4419 | 0.043529 | 79.0721
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | SPLICE, OH | 3 | 138 | 12999 | 0.023901 | 0.00025374 | 94.1957
AEP-SEP | 2023 | 551114 | DISTRIBUTION SOURCE | EQF | RECLOSER, LINE/OCR/BR | 1 | 303 | 226938 | 0.41178 | 0.0005498 | 748.9703
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 11 | 21 | 2212 | 0.0039906 | 3.7886e-05 | 105.3333
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 1046 | 138676 | 0.25018 | 0.0018871 | 132.5774
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | SWITCH, OH | 5 | 388 | 50466 | 0.092792 | 0.00071342 | 130.067
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | SPLICE, OH | 2 | 2 | 261 | 0.00047747 | 3.6588e-06 | 130.5
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 12 | 2173 | 531612 | 0.95907 | 0.0039203 | 244.6443
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 3 | 258 | 0.00046545 | 5.4123e-06 | 86
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 3 | 108 | 0.00019858 | 5.5161e-06 | 36
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 8 | 1112 | 0.0020343 | 1.4635e-05 | 139
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 542 | 35530 | 0.064469 | 0.00098346 | 65.5535
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 8 | 3316 | 0.0059824 | 1.4433e-05 | 414.5
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | CUTOUT | 1 | 4 | 3440 | 0.0062061 | 7.2163e-06 | 860
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | NONE | 148 | 7854 | 1196210 | 2.1581 | 0.014169 | 152.3058
AEP-SEP | 2023 | 551114 | PARTIAL POWER | WL | TRANSFORMER, UG | 2 | 3 | 969 | 0.0017583 | 5.4435e-06 | 323
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | CROSSARM | 3 | 100 | 6934 | 0.01251 | 0.00018041 | 69.34
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | JUMPER/RISER | 4 | 208 | 78378 | 0.1414 | 0.00037525 | 376.8173
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WI | SPLICE, OH | 1 | 3 | 468 | 0.0008508 | 5.4538e-06 | 156
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WW | NONE | 1 | 1 | 436 | 0.00080168 | 1.8387e-06 | 436
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 4 | 524 | 0.00094534 | 7.2163e-06 | 131
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 3 | 1125 | 0.0020296 | 5.4123e-06 | 375
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | ABI | NONE | 2 | 1899 | 153819 | 0.28283 | 0.0034917 | 81
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 100 | 19559 | 0.035286 | 0.00018041 | 195.59
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 7 | 12 | 1904 | 0.003435 | 2.1649e-05 | 158.6667
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | SWITCH, OH | 42 | 6031 | 256992 | 0.46364 | 0.01088 | 42.6118
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 78 | 5004 | 858410 | 1.5486 | 0.0090277 | 171.5448
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VIN | NONE | 125 | 2126 | 288016 | 0.51961 | 0.0038355 | 135.4732
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | CONN/CLAMP | 65 | 151 | 17014 | 0.030695 | 0.00027242 | 112.6755
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 2 | 140 | 0.00025257 | 3.6082e-06 | 70
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 251 | 0.00046152 | 1.8387e-06 | 251
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 3 | 198 | 38140 | 0.068808 | 0.00035721 | 192.6263
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 5 | 14 | 4692 | 0.0085834 | 2.5611e-05 | 335.1429
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 4 | 300 | 0.00054123 | 7.2163e-06 | 75
AEP-SEP | 2020 | 543859 | PARTIAL POWER | O | FUSE | 1 | 7 | 637 | 0.0011713 | 1.2871e-05 | 91
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 22 | 10144 | 0.018301 | 3.969e-05 | 461.0909
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 124 | 21232 | 0.038304 | 0.00022371 | 171.2258
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 16 | 2128 | 0.0038391 | 2.8865e-05 | 133
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 49 | 2744 | 0.0049504 | 8.84e-05 | 56
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TIR | FUSE | 3 | 13 | 1363 | 0.0025062 | 2.3903e-05 | 104.8462
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | SWITCH, OH | 4 | 1369 | 127037 | 0.22919 | 0.0024698 | 92.7955
AEP-SEP | 2024 | 554297 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 1 | 281 | 0.00050695 | 1.8041e-06 | 281
AEP-SEP | 2022 | 550071 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 2 | 244 | 0.00044358 | 3.6359e-06 | 122
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | RECLOSER, LINE/OCR/BR | 1 | 52 | 3692 | 0.0067119 | 9.4533e-05 | 71
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | INSULATOR | 1 | 461 | 22880 | 0.041278 | 0.00083168 | 49.6312
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 29 | 2436 | 0.0044285 | 5.272e-05 | 84
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 3 | 165 | 0.00030185 | 5.4881e-06 | 55
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 2 | 300 | 0.00054435 | 3.629e-06 | 150
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | BREAKER | 1 | 2 | 290 | 0.00053323 | 3.6774e-06 | 145
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TIR | POLE | 1 | 5 | 1195 | 0.0021861 | 9.1469e-06 | 239
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 1 | 119 | 0.0002177 | 1.8294e-06 | 119
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 6 | 318 | 0.00057701 | 1.0887e-05 | 53
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | AO | NONE | 5 | 1317 | 207428 | 0.3814 | 0.0024216 | 157.5004
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | NONE | 839 | 77615 | 10109218 | 18.378 | 0.1411 | 130.2483
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | NONE | 2127 | 58849 | 9610193 | 17.4708 | 0.10698 | 163.3026
AEP-SEP | 2022 | 550071 | PARTIAL POWER | U | NONE | 28 | 113 | 10486 | 0.019063 | 0.00020543 | 92.7965
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 11 | 1081 | 0.0019652 | 1.9997e-05 | 98.2727
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | CONN/CLAMP | 42 | 91 | 13339 | 0.024402 | 0.00016647 | 146.5824
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | CONN/CLAMP | 72 | 308 | 52663 | 0.095739 | 0.00055993 | 170.9838
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TIR | NONE | 78 | 637 | 126882 | 0.23066 | 0.001158 | 199.1868
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | ARRESTER | 109 | 9483 | 651459 | 1.1918 | 0.017348 | 68.6976
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VIN | FUSE | 29 | 285 | 71008 | 0.12909 | 0.00051811 | 249.1509
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | FUSE | 3 | 85 | 4142 | 0.0075773 | 0.0001555 | 48.7294
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 6 | 1577 | 0.0028669 | 1.0908e-05 | 262.8333
AEP-SEP | 2021 | 546634 | PARTIAL POWER | OL | NONE | 10 | 24 | 1651 | 0.0030203 | 4.3905e-05 | 68.7917
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 175 | 1505 | 409625 | 0.75318 | 0.0027673 | 272.1761
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TIR | NONE | 48 | 128 | 16266 | 0.029908 | 0.00023536 | 127.0781
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | FUSE | 49 | 483 | 48466 | 0.089115 | 0.0008881 | 100.3437
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 3 | 5 | 1005 | 0.0018479 | 9.1936e-06 | 201
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | SWITCH, OH | 50 | 4091 | 516842 | 0.9455 | 0.007484 | 126.3363
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 20 | 2981 | 400470 | 0.72803 | 0.0054193 | 134.3408
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 51 | 32487 | 0.059734 | 9.3774e-05 | 637
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 4 | 142 | 13206 | 0.024008 | 0.00025815 | 93
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | FUSE | 8 | 116 | 22595 | 0.041077 | 0.00021088 | 194.7845
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | AB | BREAKER | 1 | 824 | 159032 | 0.29093 | 0.0015074 | 193
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | FUSE | 8 | 756 | 126606 | 0.23161 | 0.001383 | 167.4683
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | METERING | 2 | 4 | 418 | 0.0007599 | 7.2718e-06 | 104.5
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | PEDESTAL | 3 | 12 | 3527 | 0.0064119 | 2.1815e-05 | 293.9167
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TR | TRANSFORMER, UG | 1 | 8 | 3416 | 0.0062101 | 1.4544e-05 | 427
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | POLE | 1 | 12 | 3336 | 0.0060647 | 2.1815e-05 | 278
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 33 | 96 | 11636 | 0.021287 | 0.00017562 | 121.2083
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | NONE | 142 | 19204 | 2393481 | 4.343 | 0.034846 | 124.6345
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | SWITCH, OH | 2 | 3 | 275 | 0.00049994 | 5.4538e-06 | 91.6667
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 24 | 1752 | 0.003185 | 4.3631e-05 | 73
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 13 | 820 | 128992 | 0.23406 | 0.0014879 | 157.3073
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | ARRESTER | 63 | 3429 | 662016 | 1.1943 | 0.0061862 | 193.0639
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 264 | 9633 | 1731740 | 3.1242 | 0.017379 | 179.7716
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WFS | NONE | 2 | 10 | 1472 | 0.0027066 | 1.8387e-05 | 147.2
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 4 | 533 | 0.00098003 | 7.3548e-06 | 133.25
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 58 | 3564 | 0.0065532 | 0.00010665 | 61.4483
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 7 | 2538 | 0.0046667 | 1.2871e-05 | 362.5714
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TR | NONE | 1 | 1 | 50 | 9.1936e-05 | 1.8387e-06 | 50
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | METERING | 22 | 735 | 40158 | 0.072449 | 0.001326 | 54.6367
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 5 | 15 | 2936 | 0.0053274 | 2.7218e-05 | 195.7333
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | FO | NONE | 52 | 3241 | 110869 | 0.20002 | 0.005847 | 34.2083
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 78 | 280 | 51109 | 0.092205 | 0.00050514 | 182.5321
AEP-SEP | 2025 | 554297 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 4 | 494 | 0.00089122 | 7.2163e-06 | 123.5
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | CUTOUT | 3 | 12 | 978 | 0.001778 | 2.1815e-05 | 81.5
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 2003 | 128192 | 0.23571 | 0.0036829 | 64
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WL | CONDUCTOR UG | 1 | 2 | 608 | 0.0011123 | 3.6588e-06 | 304
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | BREAKER | 1 | 1 | 117 | 0.00021404 | 1.8294e-06 | 117
AEP-SEP | 2020 | 543859 | PARTIAL POWER | OL | TRANSFORMER, GROUNDING | 1 | 2 | 470 | 0.00086419 | 3.6774e-06 | 235
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | ARRESTER | 1 | 4 | 568 | 0.0010444 | 7.3548e-06 | 142
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | AF | NONE | 1 | 1062 | 145494 | 0.26752 | 0.0019527 | 137
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | EQF | SWITCH, OH | 5 | 3678 | 305274 | 0.56131 | 0.0067628 | 83
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 8 | 400 | 0.00072163 | 1.4433e-05 | 50
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 9 | 963 | 0.0017373 | 1.6237e-05 | 107
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | INSULATOR | 28 | 4733 | 1212260 | 2.2038 | 0.0086043 | 256.1293
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | ARRESTER | 28 | 654 | 132797 | 0.24142 | 0.0011889 | 203.0535
AEP-SEP | 2023 | 551114 | PARTIAL POWER | WU | NONE | 13 | 35 | 4923 | 0.0089328 | 6.3508e-05 | 140.6571
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | ARRESTER | 7 | 626 | 66629 | 0.12189 | 0.0011452 | 106.4361
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | CONN/CLAMP | 4 | 16 | 2758 | 0.0050454 | 2.927e-05 | 172.375
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 7 | 33 | 12447 | 0.022628 | 5.9992e-05 | 377.1818
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | FUSE | 18 | 97 | 9271 | 0.016854 | 0.00017634 | 95.5773
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 3 | 11 | 1943 | 0.0035726 | 2.0226e-05 | 176.6364
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | FUSE | 33 | 304 | 50879 | 0.093552 | 0.00055897 | 167.3651
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 38 | 1765 | 525099 | 0.96551 | 0.0032453 | 297.5065
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 7 | 608 | 331501 | 0.60953 | 0.0011179 | 545.2319
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 121 | 980 | 223704 | 0.41133 | 0.0018019 | 228.2694
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WL | FUSE | 5 | 13 | 1329 | 0.0024312 | 2.3782e-05 | 102.2308
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | CIRCUIT SWITCHER | 3 | 14 | 2700 | 0.0049393 | 2.5611e-05 | 192.8571
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 15 | 78 | 19110 | 0.034959 | 0.00014269 | 245
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERF | NONE | 32 | 16385 | 574128 | 1.0557 | 0.030127 | 35.0399
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TOR | NONE | 16 | 50 | 7466 | 0.013573 | 9.0897e-05 | 149.32
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 5 | 2260 | 0.0041086 | 9.0897e-06 | 452
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TIR | NONE | 73 | 364 | 61041 | 0.11076 | 0.00066048 | 167.6951
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | U | FUSE | 16 | 378 | 31748 | 0.058375 | 0.00069503 | 83.9894
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | AO | REGULATOR | 1 | 1043 | 185654 | 0.33963 | 0.001908 | 178
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | ARRESTER | 129 | 3851 | 551950 | 1.0015 | 0.0069877 | 143.3264
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | ARRESTER | 63 | 2060 | 351786 | 0.63832 | 0.0037379 | 170.7699
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | NONE | 3613 | 170705 | 21863562 | 39.4438 | 0.30797 | 128.078
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | NONE | 654 | 35392 | 3836770 | 6.9219 | 0.06385 | 108.4078
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | CONDUCTOR UG | 3 | 256 | 112805 | 0.20636 | 0.00046832 | 440.6445
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | CONN/CLAMP | 24 | 48 | 3747 | 0.0068897 | 8.8258e-05 | 78.0625
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | ARRESTER | 1 | 2 | 80 | 0.00014635 | 3.6588e-06 | 40
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | RELAY | 3 | 4843 | 295779 | 0.54385 | 0.0089049 | 61.0735
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 3 | 286 | 62345 | 0.11313 | 0.00051895 | 217.9895
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TIR | FUSE | 1 | 1 | 56 | 0.00010161 | 1.8145e-06 | 56
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | FUSE | 3 | 40 | 3054 | 0.0055415 | 7.258e-05 | 76.35
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 105 | 0.00019306 | 1.8387e-06 | 105
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | FUSE | 4 | 11 | 684 | 0.001234 | 1.9845e-05 | 62.1818
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | U | NONE | 1 | 1741 | 41784 | 0.075817 | 0.0031591 | 24
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | CONN/CLAMP | 36 | 128 | 10015 | 0.018321 | 0.00023416 | 78.2422
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | ABI | NONE | 3 | 2894 | 343269 | 0.62404 | 0.0052611 | 118.614
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | ARRESTER | 70 | 2812 | 244779 | 0.45008 | 0.0051705 | 87.048
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 10 | 105 | 42604 | 0.078336 | 0.00019306 | 405.7524
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | FUSE | 79 | 1157 | 117954 | 0.21578 | 0.0021166 | 101.9481
AEP-SEP | 2021 | 546634 | PARTIAL POWER | ABI | NONE | 5 | 13 | 1053 | 0.0019263 | 2.3782e-05 | 81
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 21 | 193 | 30239 | 0.055319 | 0.00035307 | 156.6788
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WW | POLE | 5 | 1643 | 255176 | 0.46681 | 0.0030057 | 155.311
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | REGULATOR | 2 | 127 | 97184 | 0.17869 | 0.00023352 | 765.2283
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 3 | 155 | 79108 | 0.14381 | 0.00028178 | 510.3742
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | FO | FUSE | 3 | 9 | 958 | 0.0017525 | 1.6464e-05 | 106.4444
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | U | NONE | 764 | 38458 | 3324613 | 6.0325 | 0.069782 | 86.4479
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WW | POLE | 8 | 978 | 1056703 | 1.943 | 0.0017983 | 1080.4734
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 4 | 532 | 0.00096715 | 7.2718e-06 | 133
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | ARRESTER | 7 | 31 | 2581 | 0.0046921 | 5.6356e-05 | 83.2581
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 31 | 2232 | 0.0040832 | 5.6711e-05 | 72
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 9 | 3291 | 0.0060205 | 1.6464e-05 | 365.6667
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | EQF | REGULATOR | 3 | 1550 | 170284 | 0.3131 | 0.00285 | 109.8606
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | REGULATOR | 2 | 137 | 19049 | 0.03463 | 0.00024906 | 139.0438
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TR | NONE | 5 | 11 | 1305 | 0.0023724 | 1.9997e-05 | 118.6364
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | INSULATOR | 15 | 471 | 106847 | 0.19546 | 0.00086164 | 226.8514
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | POLE | 179 | 9892 | 1882402 | 3.396 | 0.017846 | 190.2954
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | CABLE TERMINATOR | 6 | 13 | 4272 | 0.0077516 | 2.3589e-05 | 328.6154
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 63 | 2051 | 0.0037521 | 0.00011525 | 32.5556
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERO | NONE | 7 | 15 | 1391 | 0.002524 | 2.7218e-05 | 92.7333
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 443 | 27349 | 5425222 | 9.7876 | 0.04934 | 198.37
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 27 | 2510 | 509164 | 0.91858 | 0.0045283 | 202.8542
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | CUTOUT | 187 | 5566 | 567768 | 1.0243 | 0.010042 | 102.0065
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | FO | FUSE | 4 | 11 | 1511 | 0.0027783 | 2.0226e-05 | 137.3636
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | JUMPER/RISER | 3 | 3 | 901 | 0.0016483 | 5.4881e-06 | 300.3333
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 13 | 2050 | 90941 | 0.16501 | 0.0037197 | 44.3615
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | FUSE | 307 | 3411 | 331784 | 0.59857 | 0.0061537 | 97.2688
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 2 | 52 | 9.5128e-05 | 3.6588e-06 | 26
AEP-SEP | 2023 | 551114 | PARTIAL POWER | VA | NONE | 4 | 11 | 780 | 0.0014153 | 1.996e-05 | 70.9091
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | SWITCH, OH | 1 | 44 | 2640 | 0.0048542 | 8.0903e-05 | 60
AEP-SEP | 2024 | 554297 | PARTIAL POWER | OL | FUSE | 4 | 7 | 600 | 0.0010825 | 1.2629e-05 | 85.7143
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | SPLICE, OH | 2 | 3 | 218 | 0.00039329 | 5.4123e-06 | 72.6667
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WH | NONE | 1 | 3 | 1830 | 0.0033648 | 5.5161e-06 | 610
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | FUSE | 2 | 11 | 1458 | 0.0026808 | 2.0226e-05 | 132.5455
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 2 | 303 | 0.00054664 | 3.6082e-06 | 151.5
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | SPLICE, UG | 1 | 1 | 110 | 0.00019845 | 1.8041e-06 | 110
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 495 | 38325 | 0.069142 | 0.00089302 | 77.4242
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 17 | 952 | 0.0017175 | 3.0669e-05 | 56
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 37 | 12173 | 0.022383 | 6.8032e-05 | 329
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | ARRESTER | 1 | 4 | 558 | 0.0010208 | 7.3175e-06 | 139.5
AEP-SEP | 2022 | 550071 | PARTIAL POWER | A | CONN/CLAMP | 1 | 1 | 89 | 0.0001618 | 1.8179e-06 | 89
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 73 | 0.00013271 | 1.8179e-06 | 73
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WH | FUSE | 1 | 71 | 3905 | 0.0071802 | 0.00013055 | 55
AEP-SEP | 2024 | 554297 | PARTIAL POWER | A | POLE HARDWARE | 1 | 4 | 412 | 0.00074328 | 7.2163e-06 | 103
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VIN | NONE | 549 | 8564 | 1236846 | 2.2485 | 0.015569 | 144.4239
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 147 | 6260 | 886417 | 1.6115 | 0.01138 | 141.6002
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | NONE | 549 | 24562 | 3775320 | 6.8633 | 0.044652 | 153.7057
AEP-SEP | 2021 | 546634 | PARTIAL POWER | U | NONE | 18 | 26 | 1955 | 0.0035764 | 4.7564e-05 | 75.1923
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | POLE | 88 | 21265 | 3314887 | 6.0642 | 0.038902 | 155.8846
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 121 | 8272 | 1677667 | 3.0691 | 0.015133 | 202.8127
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 28 | 976 | 102832 | 0.18812 | 0.0017855 | 105.3607
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 11 | 86 | 29429 | 0.053837 | 0.00015733 | 342.1977
AEP-SEP | 2022 | 550071 | PARTIAL POWER | FO | CONN/CLAMP | 3 | 10 | 890 | 0.001618 | 1.8179e-05 | 89
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | CUTOUT | 27 | 1596 | 127408 | 0.23308 | 0.0029197 | 79.8296
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | NONE | 4223 | 163514 | 24773603 | 45.5515 | 0.30066 | 151.5075
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | FUSE | 60 | 713 | 49115 | 0.090308 | 0.001311 | 68.885
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 18 | 340 | 52262 | 0.095607 | 0.00062199 | 153.7118
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | FUSE | 2 | 7 | 610 | 0.0011159 | 1.2806e-05 | 87.1429
AEP-SEP | 2022 | 550071 | PARTIAL POWER | O | FUSE | 1 | 1 | 64 | 0.00011635 | 1.8179e-06 | 64
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 19 | 4693 | 0.0086291 | 3.4936e-05 | 247
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | CROSSARM | 12 | 5894 | 599466 | 1.0898 | 0.010715 | 101.7078
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 33 | 5.9992e-05 | 1.8179e-06 | 33
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TOR | NONE | 30 | 90 | 17899 | 0.032478 | 0.00016331 | 198.8778
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 10 | 47 | 5068 | 0.0092134 | 8.5444e-05 | 107.8298
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 6 | 57 | 45302 | 0.083297 | 0.00010481 | 794.7719
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 63 | 53739 | 0.098811 | 0.00011584 | 853
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TIR | SPLICE, OH | 2 | 9 | 2439 | 0.004434 | 1.6362e-05 | 271
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | TRANSFORMER, POWER - NON LTC | 1 | 10 | 2040 | 0.0037086 | 1.8179e-05 | 204
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | WL | JUMPER/RISER | 1 | 993 | 296907 | 0.53976 | 0.0018052 | 299
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | CONDUCTOR UG | 19 | 58 | 14518 | 0.026694 | 0.00010665 | 250.3103
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | AO | METERING | 1 | 530 | 95400 | 0.17343 | 0.00096351 | 180
AEP-SEP | 2022 | 550071 | DISTRIBUTION SOURCE | WL | NONE | 1 | 351 | 47736 | 0.086782 | 0.0006381 | 136
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WI | NONE | 15 | 402 | 354186 | 0.65125 | 0.00073916 | 881.0597
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 3 | 4 | 976 | 0.0017946 | 7.3548e-06 | 244
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | FUSE | 9 | 53 | 10330 | 0.018994 | 9.7452e-05 | 194.9057
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | CUTOUT | 3 | 942 | 65953 | 0.12065 | 0.0017233 | 70.0138
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 5 | 680 | 0.0012339 | 9.0725e-06 | 136
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ABI | FUSE | 3 | 220 | 33408 | 0.060619 | 0.00039919 | 151.8545
AEP-SEP | 2022 | 550071 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 205 | 0.00037268 | 1.8179e-06 | 205
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 3 | 237 | 0.00043085 | 5.4538e-06 | 79
AEP-SEP | 2024 | 554297 | DISTRIBUTION SOURCE | TIR | NONE | 1 | 49 | 21731 | 0.039205 | 8.84e-05 | 443.4898
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 1 | 342 | 0.00062565 | 1.8294e-06 | 342
AEP-SEP | 2021 | 546634 | PARTIAL POWER | VA | PEDESTAL | 1 | 1 | 191 | 0.00034941 | 1.8294e-06 | 191
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 18 | 2509 | 0.0045526 | 3.2661e-05 | 139.3889
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | CROSSARM | 23 | 7807 | 819929 | 1.4792 | 0.014085 | 105.0248
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 15 | 8239 | 0.01495 | 2.7218e-05 | 549.2667
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 3 | 62 | 10472 | 0.018892 | 0.00011185 | 168.9032
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | BREAKER | 1 | 1468 | 45508 | 0.083251 | 0.0026855 | 31
AEP-SEP | 2020 | 543859 | PARTIAL POWER | OL | PEDESTAL | 1 | 1 | 676 | 0.001243 | 1.8387e-06 | 676
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 4 | 93 | 20549 | 0.037072 | 0.00016778 | 220.957
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 13 | 209 | 0.00037705 | 2.3453e-05 | 16.0769
AEP-SEP | 2021 | 546634 | DISTRIBUTION SOURCE | AF | NONE | 1 | 53 | 3869 | 0.0070779 | 9.6957e-05 | 73
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | CROSSARM | 2 | 37 | 2747 | 0.0050253 | 6.7687e-05 | 74.2432
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 7 | 636 | 0.0011694 | 1.2871e-05 | 90.8571
AEP-SEP | 2020 | 543859 | PARTIAL POWER | ABI | NONE | 2 | 2 | 162 | 0.00029787 | 3.6774e-06 | 81
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | INSULATOR | 1 | 17 | 697 | 0.0012751 | 3.1099e-05 | 41
AEP-SEP | 2025 | 554297 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 4 | 284 | 0.00051236 | 7.2163e-06 | 71
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ABI | FUSE | 7 | 10 | 490 | 0.000884 | 1.8041e-05 | 49
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | ARRESTER | 1 | 3 | 162 | 0.00029226 | 5.4123e-06 | 54
AEP-SEP | 2025 | 554297 | PARTIAL POWER | VIN | TRANSFORMER, OH | 1 | 5 | 250 | 0.00045102 | 9.0204e-06 | 50
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 45 | 4320 | 0.0079029 | 8.2322e-05 | 96
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 2 | 27 | 3039 | 0.0054826 | 4.871e-05 | 112.5556
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | ARRESTER | 3 | 70 | 10193 | 0.018389 | 0.00012629 | 145.6143
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 4 | 16 | 1029 | 0.0018564 | 2.8865e-05 | 64.3125
AEP-SEP | 2025 | 554297 | PARTIAL POWER | TOR | NONE | 8 | 19 | 2053 | 0.0037038 | 3.4278e-05 | 108.0526
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 3 | 864 | 0.0015886 | 5.5161e-06 | 288
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 3 | 738 | 0.001357 | 5.5161e-06 | 246
AEP-SEP | 2023 | 551114 | PARTIAL POWER | VA | OTHER EQUIPMENT | 1 | 1 | 227 | 0.00041189 | 1.8145e-06 | 227
AEP-SEP | 2024 | 554297 | PARTIAL POWER | A | ARRESTER | 1 | 1 | 30 | 5.4123e-05 | 1.8041e-06 | 30
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | JUMPER/RISER | 10 | 497 | 48660 | 0.087787 | 0.00089663 | 97.9074
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WT | NONE | 1 | 9 | 1035 | 0.0018672 | 1.6237e-05 | 115
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 23 | 2536 | 0.0045752 | 4.1494e-05 | 110.2609
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 5 | 2875 | 0.0051868 | 9.0204e-06 | 575
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 58 | 8642 | 0.015681 | 0.00010524 | 149
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | NETWORK TRANSFORMER | 1 | 1 | 50 | 9.1469e-05 | 1.8294e-06 | 50
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | TRANSFORMER, GROUNDING | 1 | 1 | 7 | 1.2629e-05 | 1.8041e-06 | 7
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 30 | 7170 | 0.013035 | 5.4538e-05 | 239
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | CUTOUT | 1 | 75 | 5625 | 0.010226 | 0.00013635 | 75
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | ARRESTER | 1 | 5 | 295 | 0.00053629 | 9.0897e-06 | 59
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 220 | 8170 | 1769585 | 3.2109 | 0.014825 | 216.5955
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | OL | NONE | 105 | 4415 | 370331 | 0.67748 | 0.0080767 | 83.8802
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | NONE | 57 | 175 | 25647 | 0.046918 | 0.00032014 | 146.5543
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 169 | 76082 | 0.13831 | 0.00030723 | 450.1893
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | POLE | 78 | 5288 | 1085520 | 1.9858 | 0.0096737 | 205.2799
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 38 | 2207 | 121034 | 0.22003 | 0.0040122 | 54.841
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | SPLICE, OH | 6 | 34 | 3500 | 0.0063628 | 6.181e-05 | 102.9412
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | BREAKER | 5 | 1624 | 83611 | 0.15296 | 0.0029709 | 51.4846
AEP-SEP | 2021 | 546634 | PARTIAL POWER | ERF | NONE | 3 | 14 | 1168 | 0.0021367 | 2.5611e-05 | 83.4286
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 1 | 108 | 0.00019757 | 1.8294e-06 | 108
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | POLE | 47 | 8727 | 2270391 | 4.1746 | 0.016046 | 260.1571
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | CONN/CLAMP | 8 | 82 | 14521 | 0.026564 | 0.00015001 | 177.0854
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | CUTOUT | 172 | 2920 | 351126 | 0.63712 | 0.0052984 | 120.2486
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 82 | 18040 | 0.032796 | 0.00014907 | 220
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 1327 | 97470 | 0.1772 | 0.0024124 | 73.4514
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 19 | 4571 | 0.0083098 | 3.4541e-05 | 240.5789
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 121 | 6905 | 1370684 | 2.4871 | 0.012529 | 198.506
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | INSULATOR | 38 | 5172 | 458445 | 0.83185 | 0.0093846 | 88.6398
AEP-SEP | 2022 | 550071 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 2 | 134 | 0.0002436 | 3.6359e-06 | 67
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | METERING | 1 | 1 | 133 | 0.00024331 | 1.8294e-06 | 133
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | ARRESTER | 10 | 175 | 39053 | 0.071807 | 0.00032177 | 223.16
AEP-SEP | 2023 | 551114 | PARTIAL POWER | O | NONE | 3 | 3 | 339 | 0.00061512 | 5.4435e-06 | 113
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | NONE | 104 | 5300 | 569073 | 1.0267 | 0.0095617 | 107.3723
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 39 | 2431 | 0.0044472 | 7.1346e-05 | 62.3333
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | JUMPER/RISER | 3 | 10 | 11215 | 0.020516 | 1.8294e-05 | 1121.5
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 5 | 2123 | 0.0038522 | 9.0725e-06 | 424.6
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 2 | 5 | 1055 | 0.0019033 | 9.0204e-06 | 211
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 1 | 21 | 3.8417e-05 | 1.8294e-06 | 21
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | CUTOUT | 1 | 1 | 137 | 0.00025062 | 1.8294e-06 | 137
AEP-SEP | 2023 | 551114 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 210 | 0.00038105 | 1.8145e-06 | 210
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 3 | 16 | 1050 | 0.0018943 | 2.8865e-05 | 65.625
AEP-SEP | 2024 | 554297 | PARTIAL POWER | ERF | NONE | 3 | 13 | 2168 | 0.0039113 | 2.3453e-05 | 166.7692
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 3 | 6 | 1065 | 0.0019324 | 1.0887e-05 | 177.5
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | U | ARRESTER | 4 | 11 | 1362 | 0.0024714 | 1.996e-05 | 123.8182
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 7 | 877 | 85809 | 0.15481 | 0.0015822 | 97.8438
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WI | NONE | 1 | 1 | 47 | 8.6419e-05 | 1.8387e-06 | 47
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | FUSE | 12 | 166 | 13852 | 0.02499 | 0.00029948 | 83.4458
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 2 | 2 | 99 | 0.0001786 | 3.6082e-06 | 49.5
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 142 | 0.00025977 | 1.8294e-06 | 142
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 2 | 5 | 2832 | 0.0051387 | 9.0725e-06 | 566.4
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | CAPACITOR | 1 | 908 | 36320 | 0.066782 | 0.0016696 | 40
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TIR | ARRESTER | 1 | 5 | 485 | 0.00087498 | 9.0204e-06 | 97
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 3850 | 308134 | 0.56657 | 0.007079 | 80.0348
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1 | 7 | 553 | 0.0010034 | 1.2702e-05 | 79
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 66 | 0.00011907 | 1.8041e-06 | 66
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 35 | 10220 | 0.018438 | 6.3143e-05 | 292
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | SPLICE, OH | 1 | 1 | 80 | 0.00014433 | 1.8041e-06 | 80
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 4 | 200 | 0.00036082 | 7.2163e-06 | 50
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 2 | 49 | 10960 | 0.019773 | 8.84e-05 | 223.6735
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | INSULATOR | 3 | 700 | 58538 | 0.10561 | 0.0012629 | 83.6257
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 2 | 614 | 0.0011077 | 3.6082e-06 | 307
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1761 | 10566 | 0.019329 | 0.0032215 | 6
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | POLE HARDWARE | 1 | 20 | 1600 | 0.002927 | 3.6588e-05 | 80
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 6 | 2754 | 410743 | 0.7514 | 0.0050381 | 149.1442
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | POLE | 47 | 2931 | 1803965 | 3.3001 | 0.0053619 | 615.4777
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | CROSSARM | 42 | 5799 | 747319 | 1.3586 | 0.010542 | 128.8703
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WL | TRANSFORMER, OH | 7 | 35 | 8413 | 0.015294 | 6.3628e-05 | 240.3714
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | CUTOUT | 8 | 64 | 13015 | 0.023661 | 0.00011635 | 203.3594
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | ARRESTER | 63 | 1131 | 163808 | 0.29779 | 0.0020561 | 144.8347
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 1 | 69 | 0.00012544 | 1.8179e-06 | 69
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | SWITCH, OH | 9 | 212 | 64805 | 0.11781 | 0.0003854 | 305.684
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | WL | NONE | 4 | 5541 | 621124 | 1.1363 | 0.010137 | 112.096
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 9 | 20 | 2326 | 0.0042768 | 3.6774e-05 | 116.3
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 14 | 69 | 27766 | 0.050794 | 0.00012623 | 402.4058
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | FUSE | 60 | 601 | 48201 | 0.088178 | 0.0010995 | 80.2013
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | CROSSARM | 4 | 534 | 262455 | 0.48013 | 0.00097689 | 491.4888
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | CUTOUT | 7 | 35 | 7151 | 0.013082 | 6.4028e-05 | 204.3143
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | CONDUCTOR UG | 18 | 61 | 15091 | 0.027607 | 0.00011159 | 247.3934
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 5 | 52 | 15075 | 0.027197 | 9.3813e-05 | 289.9038
AEP-SEP | 2025 | 554297 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 54 | 9.7421e-05 | 1.8041e-06 | 54
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | CUTOUT | 1 | 1 | 282 | 0.00051852 | 1.8387e-06 | 282
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | SPLICE, UG | 3 | 7 | 1416 | 0.0025546 | 1.2629e-05 | 202.2857
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 5 | 1985 | 0.0036018 | 9.0725e-06 | 397
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 3 | 435 | 0.00078931 | 5.4435e-06 | 145
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CF | CUTOUT | 1 | 1 | 172 | 0.0003103 | 1.8041e-06 | 172
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1308 | 86328 | 0.15574 | 0.0023597 | 66
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 7 | 3213 | 0.0057965 | 1.2629e-05 | 459
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 458 | 108818 | 0.19632 | 0.00082627 | 237.5939
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 818 | 15542 | 0.028577 | 0.0015041 | 19
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 6 | 3936 | 0.0071419 | 1.0887e-05 | 656
AEP-SEP | 2023 | 551114 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 5 | 420 | 0.00076209 | 9.0725e-06 | 84
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 8 | 552 | 0.00099586 | 1.4433e-05 | 69
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | JUMPER/RISER | 5 | 42 | 6967 | 0.012666 | 7.6354e-05 | 165.881
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | JUMPER/RISER | 15 | 296 | 46252 | 0.084084 | 0.00053811 | 156.2568
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 1 | 23 | 4.1813e-05 | 1.8179e-06 | 23
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 6 | 397 | 69761 | 0.12762 | 0.00072626 | 175.7204
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 13 | 1639 | 0.0029796 | 2.3633e-05 | 126.0769
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WU | NONE | 9 | 34 | 2361 | 0.0043192 | 6.2199e-05 | 69.4412
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | CONN/CLAMP | 18 | 533 | 78039 | 0.14276 | 0.00097506 | 146.4146
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | NONE | 2390 | 58999 | 7960501 | 14.6371 | 0.10848 | 134.926
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 5 | 845 | 0.0015362 | 9.0897e-06 | 169
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | ABX | NONE | 1 | 179 | 92543 | 0.16824 | 0.00032541 | 517
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | FUSE | 81 | 816 | 181270 | 0.3333 | 0.0015004 | 222.1446
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 2 | 300 | 0.00054881 | 3.6588e-06 | 150
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | JUMPER/RISER | 2 | 158 | 12405 | 0.022693 | 0.00028904 | 78.5127
AEP-SEP | 2022 | 550071 | PARTIAL POWER | VIN | FUSE | 1 | 1 | 37 | 6.7264e-05 | 1.8179e-06 | 37
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | SWITCH, OH | 1 | 18 | 3618 | 0.0066187 | 3.2929e-05 | 201
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 15 | 756 | 89411 | 0.16254 | 0.0013744 | 118.2685
AEP-SEP | 2022 | 550071 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 242 | 0.00043994 | 1.8179e-06 | 242
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 5 | 1590 | 0.0029236 | 9.1936e-06 | 318
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | POLE | 2 | 8 | 1704 | 0.0030978 | 1.4544e-05 | 213
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | ARRESTER | 14 | 543 | 97486 | 0.17689 | 0.00098528 | 179.5322
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | JUMPER/RISER | 1 | 1 | 28 | 5.0903e-05 | 1.8179e-06 | 28
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 5 | 30 | 4378 | 0.0079439 | 5.4435e-05 | 145.9333
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | SPLICE, OH | 2 | 2 | 225 | 0.00041371 | 3.6774e-06 | 112.5
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | BREAKER | 6 | 4307 | 297154 | 0.54638 | 0.0079193 | 68.9933
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | OL | FUSE | 9 | 232 | 16885 | 0.030638 | 0.00042097 | 72.7802
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | FUSE | 27 | 376 | 36497 | 0.065844 | 0.00067834 | 97.0665
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 26 | 113 | 26534 | 0.048146 | 0.00020504 | 234.8142
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 6 | 534 | 0.00098187 | 1.1032e-05 | 89
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 6 | 68 | 10433 | 0.018931 | 0.00012339 | 153.4265
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 6 | 1428 | 0.0026124 | 1.0976e-05 | 238
AEP-SEP | 2021 | 546634 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 4 | 8 | 987 | 0.0018056 | 1.4635e-05 | 123.375
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | EQF | RELAY | 2 | 2847 | 45552 | 0.083757 | 0.0052348 | 16
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | POLE | 8 | 1717 | 322862 | 0.59365 | 0.0031571 | 188.0384
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 36 | 90 | 10421 | 0.0188 | 0.00016237 | 115.7889
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CO | NONE | 14 | 55 | 8689 | 0.015676 | 9.9225e-05 | 157.9818
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 9 | 68 | 19274 | 0.034772 | 0.00012268 | 283.4412
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | CONN/CLAMP | 8 | 60 | 4139 | 0.0074671 | 0.00010825 | 68.9833
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 13 | 7306 | 0.013181 | 2.3453e-05 | 562
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 120 | 39360 | 0.071009 | 0.00021649 | 328
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | ARRESTER | 4 | 377 | 83293 | 0.15027 | 0.00068014 | 220.9363
AEP-SEP | 2024 | 554297 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 5 | 2920 | 0.0052679 | 9.0204e-06 | 584
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | BREAKER | 2 | 62 | 1283 | 0.0023146 | 0.00011185 | 20.6935
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | FO | PEDESTAL | 1 | 2 | 486 | 0.00088185 | 3.629e-06 | 243
AEP-SEP | 2021 | 546634 | PARTIAL POWER | ABI | FUSE | 1 | 8 | 968 | 0.0017708 | 1.4635e-05 | 121
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 27 | 4401 | 0.0079856 | 4.8992e-05 | 163
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 5 | 875 | 0.0015877 | 9.0725e-06 | 175
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 1 | 109 | 0.00020042 | 1.8387e-06 | 109
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 2 | 268 | 0.00048629 | 3.629e-06 | 134
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | ARRESTER | 8 | 28 | 2531 | 0.0046302 | 5.1223e-05 | 90.3929
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | TRANSFORMER, OH | 13 | 38 | 15152 | 0.027719 | 6.9516e-05 | 398.7368
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 2 | 12 | 2669 | 0.0049075 | 2.2065e-05 | 222.4167
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 2 | 134 | 0.0002436 | 3.6359e-06 | 67
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 10 | 1454 | 0.0026383 | 1.8145e-05 | 145.4
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 45 | 9558 | 0.017243 | 8.1184e-05 | 212.4
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TIR | CONN/CLAMP | 3 | 8 | 1646 | 0.0030112 | 1.4635e-05 | 205.75
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 3 | 88 | 13386 | 0.02415 | 0.00015876 | 152.1136
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 2507 | 618752 | 1.1163 | 0.0045228 | 246.8097
AEP-SEP | 2023 | 551114 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 4 | 4 | 540 | 0.00097983 | 7.258e-06 | 135
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TR | FUSE | 6 | 149 | 14993 | 0.027049 | 0.00026881 | 100.6242
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | POLE | 9 | 94 | 35185 | 0.063477 | 0.00016958 | 374.3085
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | SPLICE, UG | 4 | 19 | 3830 | 0.0069097 | 3.4278e-05 | 201.5789
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 1299 | 59754 | 0.1078 | 0.0023435 | 46
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WL | TRANSFORMER, OH | 4 | 18 | 3236 | 0.005838 | 3.2474e-05 | 179.7778
AEP-SEP | 2025 | 554297 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 2 | 19 | 1849 | 0.0033358 | 3.4278e-05 | 97.3158
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | POLE | 2 | 7 | 1526 | 0.002753 | 1.2629e-05 | 218
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | CUTOUT | 2 | 3 | 150 | 0.00027061 | 5.4123e-06 | 50
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 1 | 5 | 195 | 0.0003518 | 9.0204e-06 | 39
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WT | CONDUCTOR UG | 2 | 81 | 14742 | 0.026596 | 0.00014613 | 182
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | BREAKER | 1 | 2 | 482 | 0.00087625 | 3.6359e-06 | 241
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WT | FUSE | 1 | 15 | 2160 | 0.0039193 | 2.7218e-05 | 144
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WL | METERING | 1 | 2 | 322 | 0.00058538 | 3.6359e-06 | 161
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 1 | 71 | 0.00012989 | 1.8294e-06 | 71
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | SPLICE, OH | 1 | 1 | 56 | 0.00010245 | 1.8294e-06 | 56
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 250 | 22764 | 0.041305 | 0.00045363 | 91.056
AEP-SEP | 2024 | 554297 | PARTIAL POWER | VA | NONE | 1 | 1 | 42 | 7.5772e-05 | 1.8041e-06 | 42
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WFS | PEDESTAL | 1 | 1 | 174 | 0.00031391 | 1.8041e-06 | 174
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 1 | 3 | 213 | 0.00038427 | 5.4123e-06 | 71
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | FO | NONE | 66 | 4107 | 527123 | 0.95828 | 0.0074663 | 128.3475
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | NONE | 1488 | 24331 | 1845740 | 3.3555 | 0.044232 | 75.8596
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | NONE | 1195 | 19826 | 1858419 | 3.3998 | 0.036269 | 93.7365
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | CUTOUT | 26 | 275 | 74054 | 0.13463 | 0.00049994 | 269.2873
AEP-SEP | 2022 | 550071 | PARTIAL POWER | O | NONE | 11 | 42 | 5245 | 0.0095351 | 7.6354e-05 | 124.881
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | FUSE | 22 | 352 | 48250 | 0.088267 | 0.00064394 | 137.0739
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WL | NONE | 87 | 474 | 50608 | 0.092581 | 0.00086712 | 106.7679
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | FUSE | 1 | 2 | 90 | 0.00016362 | 3.6359e-06 | 45
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 104 | 5821 | 1064263 | 1.9469 | 0.010649 | 182.8316
AEP-SEP | 2022 | 550071 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 741 | 43657 | 0.079366 | 0.0013471 | 58.9163
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 5 | 33 | 4498 | 0.0081771 | 5.9992e-05 | 136.303
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 14 | 110 | 16448 | 0.030243 | 0.00020226 | 149.5273
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 2039 | 338549 | 0.61933 | 0.0037301 | 166.0368
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | JUMPER/RISER | 1 | 8 | 696 | 0.0012653 | 1.4544e-05 | 87
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 270 | 0.00049393 | 1.8294e-06 | 270
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | POLE | 6 | 252 | 52815 | 0.096619 | 0.000461 | 209.5833
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WU | NONE | 5 | 32 | 16241 | 0.029863 | 5.8839e-05 | 507.5312
AEP-SEP | 2023 | 551114 | PARTIAL POWER | OL | NONE | 17 | 53 | 4106 | 0.0074504 | 9.6169e-05 | 77.4717
AEP-SEP | 2022 | 550071 | DISTRIBUTION SOURCE | WL | CROSSARM | 1 | 2 | 532 | 0.00096715 | 3.6359e-06 | 266
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TR | NONE | 83 | 6406 | 538167 | 0.9709 | 0.011557 | 84.0098
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 587 | 21132 | 0.038658 | 0.0010738 | 36
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | CO | NONE | 4 | 9 | 814 | 0.001477 | 1.6331e-05 | 90.4444
AEP-SEP | 2023 | 551114 | PARTIAL POWER | CO | NONE | 1 | 2 | 140 | 0.00025403 | 3.629e-06 | 70
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 2 | 142 | 0.00025977 | 3.6588e-06 | 71
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | CUTOUT | 14 | 159 | 12285 | 0.022163 | 0.00028685 | 77.2642
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | CUTOUT | 8 | 82 | 6100 | 0.011216 | 0.00015077 | 74.3902
AEP-SEP | 2023 | 551114 | PARTIAL POWER | WU | TRANSFORMER, OH | 2 | 2 | 541 | 0.00098165 | 3.629e-06 | 270.5
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WU | NONE | 17 | 33 | 15061 | 0.027171 | 5.9535e-05 | 456.3939
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 7 | 64 | 15912 | 0.028872 | 0.00011613 | 248.625
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | FUSE | 92 | 1205 | 217526 | 0.39244 | 0.0021739 | 180.5195
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 12 | 520 | 50501 | 0.091108 | 0.00093813 | 97.1173
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 181 | 2998 | 399995 | 0.72163 | 0.0054087 | 133.4206
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | OL | NONE | 33 | 5569 | 780237 | 1.4076 | 0.010047 | 140.1036
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 3 | 624 | 0.0011344 | 5.4538e-06 | 208
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TIR | CABLE TERMINATOR | 1 | 1 | 25 | 4.5968e-05 | 1.8387e-06 | 25
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | TRANSFORMER, OH | 2 | 10 | 1420 | 0.0025815 | 1.8179e-05 | 142
AEP-SEP | 2024 | 554297 | PARTIAL POWER | O | CONN/CLAMP | 1 | 3 | 432 | 0.00077937 | 5.4123e-06 | 144
AEP-SEP | 2023 | 551114 | PARTIAL POWER | ERF | FUSE | 2 | 20 | 2440 | 0.0044274 | 3.629e-05 | 122
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | SWITCH, OH | 3 | 35 | 6060 | 0.010996 | 6.3508e-05 | 173.1429
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 23 | 2523 | 186431 | 0.33634 | 0.0045517 | 73.8926
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 4 | 16 | 2438 | 0.0044828 | 2.9419e-05 | 152.375
AEP-SEP | 2024 | 554297 | PARTIAL POWER | A | FUSE | 1 | 1 | 138 | 0.00024896 | 1.8041e-06 | 138
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 1 | 322 | 0.00059207 | 1.8387e-06 | 322
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | INSULATOR | 4 | 10 | 5041 | 0.0090944 | 1.8041e-05 | 504.1
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | SWITCH, OH | 4 | 15 | 2913 | 0.0052553 | 2.7061e-05 | 194.2
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | AF | POLE | 3 | 46 | 2722 | 0.0049796 | 8.4151e-05 | 59.1739
AEP-SEP | 2021 | 546634 | PARTIAL POWER | A | FUSE | 1 | 4 | 288 | 0.00052686 | 7.3175e-06 | 72
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 26 | 3094 | 0.0056247 | 4.7267e-05 | 119
AEP-SEP | 2020 | 543859 | PARTIAL POWER | OL | NONE | 5 | 5 | 855 | 0.0015721 | 9.1936e-06 | 171
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 9 | 585 | 0.0010702 | 1.6464e-05 | 65
AEP-SEP | 2024 | 554297 | PARTIAL POWER | OL | TRANSFORMER, OH | 2 | 11 | 2215 | 0.0039961 | 1.9845e-05 | 201.3636
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 52 | 4471 | 0.0080661 | 9.3813e-05 | 85.9808
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 3 | 321 | 0.00058356 | 5.4538e-06 | 107
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | TRANSFORMER, POWER - LTC | 1 | 2 | 424 | 0.00076935 | 3.629e-06 | 212
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 953 | 79367 | 0.14429 | 0.0017325 | 83.2812
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 612 | 0.0011041 | 1.8041e-06 | 612
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 1 | 47 | 8.6419e-05 | 1.8387e-06 | 47
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | ARRESTER | 3 | 427 | 126329 | 0.22922 | 0.00077479 | 295.8525
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | U | NONE | 3 | 1921 | 330816 | 0.60828 | 0.0035322 | 172.2103
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 54 | 9.7983e-05 | 1.8145e-06 | 54
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | CONDUCTOR UG | 6 | 73 | 23892 | 0.043434 | 0.00013271 | 327.2877
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 44 | 113 | 16202 | 0.02964 | 0.00020672 | 143.3805
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | SWITCH, OH | 7 | 40 | 4176 | 0.0075917 | 7.2718e-05 | 104.4
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | FUSE | 9 | 13 | 883 | 0.0016052 | 2.3633e-05 | 67.9231
AEP-SEP | 2022 | 550071 | PARTIAL POWER | OL | NONE | 20 | 94 | 9287 | 0.016883 | 0.00017089 | 98.7979
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | NONE | 511 | 12401 | 1212703 | 2.2298 | 0.022802 | 97.7907
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | FUSE | 101 | 1701 | 297105 | 0.54629 | 0.0031276 | 174.6649
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | CONDUCTOR UG | 9 | 41 | 11720 | 0.021306 | 7.4536e-05 | 285.8537
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | SWITCH, OH | 19 | 1646 | 220755 | 0.4059 | 0.0030265 | 134.116
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WT | POLE | 1 | 109 | 322858 | 0.59063 | 0.0001994 | 2962
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 439 | 2609 | 703601 | 1.2767 | 0.004734 | 269.6823
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 906 | 151438 | 0.27531 | 0.0016471 | 167.1501
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WT | NONE | 11 | 1214 | 503526 | 0.92114 | 0.0022209 | 414.7661
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | SPLICE, UG | 1 | 1 | 483 | 0.00088359 | 1.8294e-06 | 483
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WL | CONN/CLAMP | 2 | 19 | 2497 | 0.004568 | 3.4758e-05 | 131.4211
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WT | TRANSFORMER, OH | 1 | 1 | 413 | 0.00075081 | 1.8179e-06 | 413
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | JUMPER/RISER | 14 | 51 | 5195 | 0.0094264 | 9.254e-05 | 101.8627
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 1 | 98 | 0.00017816 | 1.8179e-06 | 98
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | NONE | 776 | 33137 | 1997396 | 3.6035 | 0.059782 | 60.2769
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 454 | 3464 | 722476 | 1.3034 | 0.0062494 | 208.567
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 3 | 53 | 10500 | 0.019208 | 9.6957e-05 | 198.1132
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 7 | 2386 | 0.0043872 | 1.2871e-05 | 340.8571
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | CONN/CLAMP | 10 | 147 | 10958 | 0.020149 | 0.00027029 | 74.5442
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | NONE | 47 | 6799 | 1349136 | 2.434 | 0.012266 | 198.4315
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | CROSSARM | 6 | 538 | 165026 | 0.29944 | 0.0009762 | 306.7398
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | CUTOUT | 24 | 1343 | 165297 | 0.29993 | 0.0024369 | 123.0804
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | FUSE | 171 | 2067 | 355222 | 0.64085 | 0.003729 | 171.8539
AEP-SEP | 2023 | 551114 | PARTIAL POWER | WL | FUSE | 1 | 1 | 75 | 0.00013609 | 1.8145e-06 | 75
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | METERING | 9 | 23 | 2178 | 0.0039293 | 4.1494e-05 | 94.6957
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | CUTOUT | 67 | 2921 | 215697 | 0.38914 | 0.0052697 | 73.8435
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | NONE | 252 | 20167 | 1456615 | 2.6279 | 0.036383 | 72.2276
AEP-SEP | 2024 | 554297 | PARTIAL POWER | ABI | NONE | 7 | 8 | 574 | 0.0010355 | 1.4433e-05 | 71.75
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 2 | 6 | 714 | 0.0012881 | 1.0825e-05 | 119
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 63 | 13370 | 0.024121 | 0.00011366 | 212.2222
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | INSULATOR | 22 | 2524 | 282381 | 0.50944 | 0.0045535 | 111.8784
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 4 | 603 | 45137 | 0.081431 | 0.0010879 | 74.8541
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 3 | 1159 | 0.0021311 | 5.5161e-06 | 386.3333
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | FUSE | 2 | 16 | 1930 | 0.0035307 | 2.927e-05 | 120.625
AEP-SEP | 2025 | 554297 | PARTIAL POWER | A | NONE | 10 | 20 | 2651 | 0.0047826 | 3.6082e-05 | 132.55
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 1 | 226 | 42712 | 0.078535 | 0.00041555 | 188.9912
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 48 | 10733 | 0.019363 | 8.6596e-05 | 223.6042
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | AF | NONE | 3 | 812 | 13905 | 0.025279 | 0.0014762 | 17.1244
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WT | NONE | 16 | 1277 | 1392309 | 2.5311 | 0.0023215 | 1090.2968
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | SWITCH, UG | 1 | 17 | 2295 | 0.0042198 | 3.1258e-05 | 135
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 47 | 13160 | 0.023924 | 8.5444e-05 | 280
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 4 | 282 | 0.00051266 | 7.2718e-06 | 70.5
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 18 | 3186 | 0.0058284 | 3.2929e-05 | 177
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | ARRESTER | 4 | 6 | 664 | 0.0012071 | 1.0908e-05 | 110.6667
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 4 | 131 | 13313 | 0.024479 | 0.00024087 | 101.626
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | POLE | 50 | 1196 | 287577 | 0.51881 | 0.0021577 | 240.449
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 8 | 5600 | 0.010181 | 1.4544e-05 | 700
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 238 | 88536 | 0.16279 | 0.00043761 | 372
AEP-SEP | 2022 | 550071 | PARTIAL POWER | O | TRANSFORMER, OH | 1 | 1 | 754 | 0.0013707 | 1.8179e-06 | 754
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | U | CUTOUT | 3 | 9 | 381 | 0.00069133 | 1.6331e-05 | 42.3333
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 2 | 26 | 5343 | 0.0096949 | 4.7177e-05 | 205.5
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 2 | 48 | 12240 | 0.022392 | 8.781e-05 | 255
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 2 | 684 | 0.0012513 | 3.6588e-06 | 342
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | CONDUCTOR UG | 66 | 170 | 43241 | 0.078011 | 0.00030669 | 254.3588
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CF | NONE | 1 | 12 | 792 | 0.0014288 | 2.1649e-05 | 66
AEP-SEP | 2024 | 554297 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 9 | 492 | 0.00088761 | 1.6237e-05 | 54.6667
AEP-SEP | 2024 | 554297 | PARTIAL POWER | O | NONE | 6 | 34 | 2165 | 0.0039058 | 6.1339e-05 | 63.6765
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 6 | 70 | 9618 | 0.017352 | 0.00012629 | 137.4
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 10 | 62 | 5968 | 0.010767 | 0.00011185 | 96.2581
AEP-SEP | 2025 | 554297 | PARTIAL POWER | WL | METERING | 1 | 2 | 230 | 0.00041494 | 3.6082e-06 | 115
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 1 | 124 | 0.00022543 | 1.8179e-06 | 124
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 74 | 0.00013453 | 1.8179e-06 | 74
AEP-SEP | 2022 | 550071 | PARTIAL POWER | VIN | TRANSFORMER, OH | 1 | 2 | 296 | 0.00053811 | 3.6359e-06 | 148
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WH | TRANSFORMER, OH | 1 | 7 | 2457 | 0.0045177 | 1.2871e-05 | 351
AEP-SEP | 2020 | 543859 | PARTIAL POWER | FO | METERING | 1 | 1 | 97 | 0.00017836 | 1.8387e-06 | 97
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | BREAKER | 1 | 8 | 1856 | 0.0033484 | 1.4433e-05 | 232
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 111 | 9879 | 0.017823 | 0.00020025 | 89
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WT | SWITCH, OH | 1 | 1 | 203 | 0.00036834 | 1.8145e-06 | 203
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | POLE | 1 | 12 | 11184 | 0.020564 | 2.2065e-05 | 932
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 1 | 352 | 66176 | 0.1203 | 0.00063992 | 188
AEP-SEP | 2022 | 550071 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 9 | 2259 | 0.0041067 | 1.6362e-05 | 251
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 231 | 79695 | 0.14654 | 0.00042474 | 345
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1 | 160 | 0.00029087 | 1.8179e-06 | 160
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 8 | 8188 | 0.014857 | 1.4516e-05 | 1023.5
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | NONE | 4823 | 221264 | 35308218 | 64.1885 | 0.40225 | 159.5751
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 13 | 492 | 68421 | 0.12439 | 0.00089443 | 139.0671
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | NONE | 55 | 239 | 38515 | 0.070018 | 0.00043449 | 161.1506
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | FUSE | 155 | 2985 | 459456 | 0.84052 | 0.0054607 | 153.9216
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 42 | 1185 | 153589 | 0.27922 | 0.0021543 | 129.611
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | FUSE | 81 | 1872 | 121997 | 0.22318 | 0.0034246 | 65.1693
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 19 | 3021 | 0.005492 | 3.4541e-05 | 159
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WW | NONE | 38 | 2435 | 614800 | 1.1304 | 0.0044773 | 252.4846
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | NONE | 650 | 11778 | 1461257 | 2.6868 | 0.021656 | 124.0666
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 28 | 126 | 20806 | 0.038256 | 0.00023168 | 165.127
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 28 | 1051 | 238474 | 0.43626 | 0.0019227 | 226.902
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | JUMPER/RISER | 9 | 1950 | 191186 | 0.35154 | 0.0035855 | 98.0441
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 1 | 53 | 10983 | 0.020092 | 9.6957e-05 | 207.2264
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 7 | 211 | 86242 | 0.15678 | 0.00038359 | 408.7299
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | SS | NONE | 2 | 1109 | 38674 | 0.070307 | 0.0020161 | 34.8729
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | SWITCH, OH | 4 | 81 | 11223 | 0.020531 | 0.00014818 | 138.5556
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | NONE | 551 | 6835 | 1230506 | 2.2328 | 0.012402 | 180.0301
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 39 | 3144 | 536272 | 0.97307 | 0.0057048 | 170.57
AEP-SEP | 2023 | 551114 | PARTIAL POWER | U | NONE | 23 | 58 | 7073 | 0.012834 | 0.00010524 | 121.9483
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 4 | 14 | 3173 | 0.0058342 | 2.5742e-05 | 226.6429
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | CROSSARM | 4 | 1498 | 278436 | 0.50936 | 0.0027404 | 185.8718
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | FUSE | 268 | 4943 | 1021809 | 1.8434 | 0.0089176 | 206.7184
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | CROSSARM | 32 | 3617 | 899967 | 1.6236 | 0.0065254 | 248.8159
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | NONE | 12 | 127 | 23645 | 0.043476 | 0.00023352 | 186.1811
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 26 | 2298 | 458223 | 0.82667 | 0.0041458 | 199.4008
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | FUSE | 216 | 2992 | 361125 | 0.6515 | 0.0053978 | 120.6969
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 28 | 1265 | 203950 | 0.37007 | 0.0022954 | 161.2253
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | TRANSFORMER, OH | 2 | 4 | 1062 | 0.0019428 | 7.3175e-06 | 265.5
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | POLE | 4 | 534 | 46097 | 0.083802 | 0.00097078 | 86.324
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 48 | 11376 | 0.020811 | 8.781e-05 | 237
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 19 | 2375 | 0.0043176 | 3.4541e-05 | 125
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 3 | 54 | 47324 | 0.087015 | 9.929e-05 | 876.3704
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | CROSSARM | 11 | 1867 | 380841 | 0.70026 | 0.0034329 | 203.9855
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | SWITCH, OH | 3 | 64 | 12495 | 0.022975 | 0.00011768 | 195.2344
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 43 | 3703 | 0.0067319 | 7.8172e-05 | 86.1163
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | CO | SWITCH, OH | 4 | 4055 | 621383 | 1.1367 | 0.0074181 | 153.2387
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WW | NONE | 84 | 5564 | 1057079 | 1.9181 | 0.010096 | 189.9854
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WI | POLE | 3 | 92 | 82406 | 0.15152 | 0.00016916 | 895.7174
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 13 | 1592 | 102969 | 0.18933 | 0.0029272 | 64.679
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | NONE | 1555 | 32437 | 3747927 | 6.7616 | 0.058519 | 115.5448
AEP-SEP | 2021 | 546634 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 5 | 1380 | 0.0025245 | 9.1469e-06 | 276
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 15 | 1275 | 0.0023179 | 2.7269e-05 | 85
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 2 | 7 | 1162 | 0.0021257 | 1.2806e-05 | 166
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 10 | 29 | 3214 | 0.0057983 | 5.2319e-05 | 110.8276
AEP-SEP | 2024 | 554297 | PARTIAL POWER | U | NONE | 15 | 59 | 6051 | 0.010917 | 0.00010644 | 102.5593
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 9 | 738 | 0.0013501 | 1.6464e-05 | 82
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | INSULATOR | 4 | 45 | 15643 | 0.028384 | 8.1653e-05 | 347.6222
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 139 | 0.00025428 | 1.8294e-06 | 139
AEP-SEP | 2023 | 551114 | PARTIAL POWER | ABI | FUSE | 2 | 6 | 519 | 0.00094173 | 1.0887e-05 | 86.5
AEP-SEP | 2023 | 551114 | PARTIAL POWER | OL | TRANSFORMER, OH | 1 | 2 | 912 | 0.0016548 | 3.629e-06 | 456
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | NONE | 16 | 1076 | 130718 | 0.23583 | 0.0019412 | 121.4851
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | CONDUCTOR UG | 26 | 100 | 20082 | 0.03623 | 0.00018041 | 200.82
AEP-SEP | 2025 | 554297 | PARTIAL POWER | ERF | NONE | 2 | 2 | 178 | 0.00032113 | 3.6082e-06 | 89
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | FUSE | 12 | 74 | 5154 | 0.0092983 | 0.0001335 | 69.6486
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ABI | BREAKER | 1 | 1 | 28 | 5.0514e-05 | 1.8041e-06 | 28
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | JUMPER/RISER | 4 | 6 | 700 | 0.0012629 | 1.0825e-05 | 116.6667
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | FUSE | 4 | 42 | 2589 | 0.0047604 | 7.7226e-05 | 61.6429
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 2 | 287 | 0.00052771 | 3.6774e-06 | 143.5
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WW | JUMPER/RISER | 3 | 6 | 650 | 0.0011727 | 1.0825e-05 | 108.3333
AEP-SEP | 2021 | 546634 | PARTIAL POWER | U | CIRCUIT SWITCHER | 1 | 6 | 972 | 0.0017782 | 1.0976e-05 | 162
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 21 | 4686 | 0.0086162 | 3.8613e-05 | 223.1429
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | SWITCH, OH | 2 | 92 | 18064 | 0.033214 | 0.00016916 | 196.3478
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | OL | CAPACITOR | 1 | 1 | 90 | 0.00016548 | 1.8387e-06 | 90
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | REGULATOR | 2 | 210 | 6340 | 0.011598 | 0.00038417 | 30.1905
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 2 | 1482 | 0.0026737 | 3.6082e-06 | 741
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 20 | 1415 | 0.0025528 | 3.6082e-05 | 70.75
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 2 | 122 | 0.0002201 | 3.6082e-06 | 61
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 3 | 29 | 6453 | 0.011642 | 5.2319e-05 | 222.5172
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | SPLICE, OH | 1 | 2 | 498 | 0.00090534 | 3.6359e-06 | 249
AEP-SEP | 2022 | 550071 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 75 | 0.00013635 | 1.8179e-06 | 75
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 1 | 2 | 230 | 0.00041494 | 3.6082e-06 | 115
AEP-SEP | 2021 | 546634 | PARTIAL POWER | OL | CUTOUT | 1 | 1 | 79 | 0.00014452 | 1.8294e-06 | 79
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 16 | 1280 | 0.0023536 | 2.9419e-05 | 80
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | SWITCH, UG | 1 | 29 | 1740 | 0.0031831 | 5.3052e-05 | 60
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WU | TRANSFORMER, OH | 1 | 4 | 1696 | 0.0031026 | 7.3175e-06 | 424
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 13 | 2782 | 0.005048 | 2.3589e-05 | 214
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | POLE | 10 | 161 | 52089 | 0.094695 | 0.00029269 | 323.5342
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | NONE | 4617 | 211528 | 30835958 | 55.952 | 0.38382 | 145.7772
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CF | NONE | 5 | 25 | 3937 | 0.0072023 | 4.5734e-05 | 157.48
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | NONE | 424 | 6201 | 573110 | 1.0484 | 0.011344 | 92.4222
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 7 | 545 | 128022 | 0.23274 | 0.00099078 | 234.9028
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 32 | 110 | 10728 | 0.019503 | 0.00019997 | 97.5273
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 11 | 1571 | 0.002874 | 2.0123e-05 | 142.8182
AEP-SEP | 2022 | 550071 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 4 | 824 | 0.001498 | 7.2718e-06 | 206
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | CABLE TERMINATOR | 7 | 17 | 3105 | 0.0056447 | 3.0905e-05 | 182.6471
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 1 | 112 | 0.00020361 | 1.8179e-06 | 112
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | SWITCH, OH | 66 | 4505 | 477838 | 0.87861 | 0.0082834 | 106.0684
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | FO | NONE | 50 | 2868 | 237517 | 0.43673 | 0.0052734 | 82.8162
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | FUSE | 27 | 294 | 51421 | 0.093481 | 0.00053448 | 174.9014
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 3 | 71 | 21361 | 0.038833 | 0.00012907 | 300.8592
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 13 | 1011 | 143566 | 0.26398 | 0.0018589 | 142.004
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 155 | 22952 | 0.041726 | 0.00028178 | 148.0774
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WH | NONE | 1 | 1 | 40 | 7.2718e-05 | 1.8179e-06 | 40
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 4 | 764 | 37386 | 0.068742 | 0.0014048 | 48.9346
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 36 | 120 | 19527 | 0.035228 | 0.00021649 | 162.725
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 1 | 178 | 0.00032563 | 1.8294e-06 | 178
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 2 | 184 | 0.00033387 | 3.629e-06 | 92
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 81 | 7954 | 956179 | 1.725 | 0.01435 | 120.2136
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERO | NONE | 5 | 14 | 776 | 0.0014268 | 2.5742e-05 | 55.4286
AEP-SEP | 2022 | 550071 | PARTIAL POWER | ERF | NONE | 5 | 9 | 1045 | 0.0018998 | 1.6362e-05 | 116.1111
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | ABX | NONE | 2 | 522 | 103356 | 0.18754 | 0.00094717 | 198
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 5 | 72 | 35096 | 0.063682 | 0.00013064 | 487.4444
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | CROSSARM | 1 | 64 | 9420 | 0.017233 | 0.00011708 | 147.1875
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 11 | 137 | 14796 | 0.026693 | 0.00024716 | 108
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 22 | 2082 | 338334 | 0.61038 | 0.0037561 | 162.5043
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | EQF | BREAKER | 5 | 2113 | 335967 | 0.60961 | 0.0038341 | 159
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | SWITCH, OH | 4 | 178 | 21803 | 0.039562 | 0.00032298 | 122.4888
AEP-SEP | 2024 | 554297 | DISTRIBUTION SOURCE | A | NONE | 4 | 2537 | 466873 | 0.84228 | 0.004577 | 184.0256
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | BREAKER | 2 | 12 | 1000 | 0.0018145 | 2.1774e-05 | 83.3333
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | TRANSFORMER, OH | 3 | 19 | 6106 | 0.01117 | 3.4758e-05 | 321.3684
AEP-SEP | 2024 | 554297 | DISTRIBUTION STATION | ABI | NONE | 2 | 2053 | 227883 | 0.41112 | 0.0037038 | 111
AEP-SEP | 2023 | 551114 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 10 | 1780 | 0.0032298 | 1.8145e-05 | 178
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | ARRESTER | 8 | 440 | 48775 | 0.087994 | 0.0007938 | 110.8523
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 113 | 631 | 127927 | 0.23079 | 0.0011384 | 202.7369
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 5 | 97 | 16050 | 0.028956 | 0.000175 | 165.4639
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | METERING | 3 | 15 | 4294 | 0.0077467 | 2.7061e-05 | 286.2667
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 4 | 398 | 0.00071803 | 7.2163e-06 | 99.5
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 53 | 9.5617e-05 | 1.8041e-06 | 53
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VIN | FUSE | 4 | 10 | 5013 | 0.0090439 | 1.8041e-05 | 501.3
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | PEDESTAL | 1 | 6 | 384 | 0.00069277 | 1.0825e-05 | 64
AEP-SEP | 2021 | 546634 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 4 | 6 | 868 | 0.0015879 | 1.0976e-05 | 144.6667
AEP-SEP | 2025 | 554297 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 13 | 1123 | 0.002026 | 2.3453e-05 | 86.3846
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | REGULATOR | 1 | 2 | 162 | 0.00029787 | 3.6774e-06 | 81
AEP-SEP | 2020 | 543859 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 9 | 1067 | 0.0019619 | 1.6548e-05 | 118.5556
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 23 | 4922 | 0.0089479 | 4.1813e-05 | 214
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 10 | 1000 | 130663 | 0.23573 | 0.0018041 | 130.663
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WL | JUMPER/RISER | 1 | 4 | 124 | 0.00022371 | 7.2163e-06 | 31
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | METERING | 1 | 6 | 1086 | 0.0019592 | 1.0825e-05 | 181
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 26 | 3138 | 0.0056612 | 4.6906e-05 | 120.6923
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 8 | 1872 | 0.0033773 | 1.4433e-05 | 234
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 4 | 38 | 5632 | 0.010161 | 6.8555e-05 | 148.2105
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 3 | 9 | 859 | 0.0015616 | 1.6362e-05 | 95.4444
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 70 | 0.00012726 | 1.8179e-06 | 70
AEP-SEP | 2024 | 554297 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 8 | 2064 | 0.0037236 | 1.4433e-05 | 258
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 102 | 0.00018402 | 1.8041e-06 | 102
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 1 | 9 | 729 | 0.0013152 | 1.6237e-05 | 81
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TOR | ARRESTER | 1 | 6 | 792 | 0.0014398 | 1.0908e-05 | 132
AEP-SEP | 2021 | 546634 | PARTIAL POWER | OL | CABLE TERMINATOR | 1 | 1 | 165 | 0.00030185 | 1.8294e-06 | 165
AEP-SEP | 2023 | 551114 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 6 | 1278 | 0.0023189 | 1.0887e-05 | 213
AEP-SEP | 2021 | 546634 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 3 | 642 | 0.0011745 | 5.4881e-06 | 214
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | CAPACITOR | 1 | 51 | 62016 | 0.11345 | 9.3298e-05 | 1216
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WT | CROSSARM | 2 | 232 | 187784 | 0.34353 | 0.00042442 | 809.4138
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 44 | 151 | 25939 | 0.047156 | 0.00027451 | 171.7815
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | CONDUCTOR UG | 42 | 199 | 49120 | 0.089298 | 0.00036177 | 246.8342
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | ARRESTER | 128 | 5980 | 793567 | 1.4427 | 0.010871 | 132.7035
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | CROSSARM | 16 | 1451 | 365679 | 0.66479 | 0.0026378 | 252.0186
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | NONE | 513 | 34918 | 4374391 | 8.0024 | 0.063878 | 125.2761
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 112 | 2933 | 335555 | 0.61002 | 0.005332 | 114.4068
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | NONE | 124 | 1989 | 348875 | 0.63822 | 0.0036386 | 175.4022
AEP-SEP | 2022 | 550071 | PARTIAL POWER | OL | FUSE | 1 | 1 | 95 | 0.0001727 | 1.8179e-06 | 95
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 104 | 7964 | 1305838 | 2.4011 | 0.014644 | 163.9676
AEP-SEP | 2020 | 543859 | PARTIAL POWER | O | CONN/CLAMP | 4 | 7 | 2026 | 0.0037252 | 1.2871e-05 | 289.4286
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | FUSE | 33 | 280 | 30176 | 0.055485 | 0.00051484 | 107.7714
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | FO | NONE | 46 | 3930 | 335315 | 0.61342 | 0.0071895 | 85.3219
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 40 | 1979 | 0.0036203 | 7.3175e-05 | 49.475
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 5 | 9 | 971 | 0.0017652 | 1.6362e-05 | 107.8889
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | WU | CONDUCTOR OVERHEAD | 1 | 14 | 4704 | 0.0085516 | 2.5451e-05 | 336
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 17 | 1293 | 398054 | 0.73191 | 0.0023775 | 307.8531
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | CROSSARM | 13 | 879 | 244645 | 0.44983 | 0.0016162 | 278.322
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | CUTOUT | 29 | 733 | 89082 | 0.1638 | 0.0013478 | 121.5307
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | CONDUCTOR UG | 6 | 19 | 3283 | 0.0060365 | 3.4936e-05 | 172.7895
AEP-SEP | 2021 | 546634 | PARTIAL POWER | U | FUSE | 2 | 4 | 122 | 0.00022318 | 7.3175e-06 | 30.5
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | FUSE | 3 | 29 | 3460 | 0.0063296 | 5.3052e-05 | 119.3103
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | CONDUCTOR UG | 9 | 26 | 6247 | 0.011428 | 4.7564e-05 | 240.2692
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERO | NONE | 2 | 6 | 1351 | 0.0024715 | 1.0976e-05 | 225.1667
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | ARRESTER | 9 | 323 | 25609 | 0.046556 | 0.0005872 | 79.2848
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | ARRESTER | 18 | 386 | 38676 | 0.071114 | 0.00070974 | 100.1969
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | SWITCH, OH | 63 | 6813 | 803356 | 1.4577 | 0.012362 | 117.9152
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | ARRESTER | 3 | 11 | 1919 | 0.0035106 | 2.0123e-05 | 174.4545
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | CONN/CLAMP | 159 | 453 | 50095 | 0.090898 | 0.00082197 | 110.585
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | CUTOUT | 12 | 13 | 1186 | 0.002152 | 2.3589e-05 | 91.2308
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1 | 49 | 8.9079e-05 | 1.8179e-06 | 49
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | ARRESTER | 19 | 283 | 66820 | 0.12125 | 0.00051351 | 236.1131
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | OL | NONE | 109 | 5843 | 458034 | 0.83111 | 0.010602 | 78.3902
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | SWITCH, OH | 1 | 2 | 230 | 0.00041813 | 3.6359e-06 | 115
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | WU | NONE | 3 | 1435 | 175016 | 0.3218 | 0.0026386 | 121.9624
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | TRANSFORMER, STATION SERVICE | 1 | 1 | 50 | 9.0204e-05 | 1.8041e-06 | 50
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | CROSSARM | 67 | 10642 | 1773301 | 3.1992 | 0.019199 | 166.6323
AEP-SEP | 2020 | 543859 | DISTRIBUTION SOURCE | TIR | NONE | 1 | 729 | 26244 | 0.048255 | 0.0013404 | 36
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | CUTOUT | 7 | 37 | 20195 | 0.037133 | 6.8032e-05 | 545.8108
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | AB | NONE | 10 | 8820 | 1167459 | 2.1184 | 0.016004 | 132.365
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | SPLICE, OH | 17 | 668 | 81017 | 0.14616 | 0.0012051 | 121.2829
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | JUMPER/RISER | 8 | 250 | 17936 | 0.032545 | 0.00045363 | 71.744
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 18 | 80 | 10463 | 0.019238 | 0.0001471 | 130.7875
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | FO | FUSE | 4 | 372 | 32884 | 0.059326 | 0.00067112 | 88.3978
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | TRANSFORMER, OH | 25 | 398 | 117724 | 0.21238 | 0.00071803 | 295.7889
AEP-SEP | 2023 | 551114 | PARTIAL POWER | WL | TRANSFORMER, OH | 6 | 13 | 2841 | 0.005155 | 2.3589e-05 | 218.5385
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1 | 164 | 0.00029587 | 1.8041e-06 | 164
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 6 | 480 | 0.00088258 | 1.1032e-05 | 80
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | NONE | 395 | 5292 | 288028 | 0.51963 | 0.0095472 | 54.4271
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 31 | 2301 | 293904 | 0.53023 | 0.0041512 | 127.7288
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 2 | 7 | 3003 | 0.0054177 | 1.2629e-05 | 429
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | FUSE | 7 | 156 | 31629 | 0.057061 | 0.00028144 | 202.75
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 11 | 2521 | 257680 | 0.46488 | 0.0045481 | 102.2134
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 4 | 6 | 795 | 0.0014342 | 1.0825e-05 | 132.5
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 1 | 105 | 0.00019306 | 1.8387e-06 | 105
AEP-SEP | 2025 | 554297 | PARTIAL POWER | ERF | FUSE | 1 | 1 | 67 | 0.00012087 | 1.8041e-06 | 67
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | FUSE | 1 | 3 | 21 | 3.8613e-05 | 5.5161e-06 | 7
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | OL | FUSE | 2 | 210 | 42860 | 0.077323 | 0.00037886 | 204.0952
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 2 | 316 | 0.00057009 | 3.6082e-06 | 158
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | AF | NONE | 54 | 22929 | 2645313 | 4.8393 | 0.041946 | 115.3698
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 14 | 271 | 24161 | 0.044425 | 0.00049829 | 89.155
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TIR | FUSE | 3 | 4 | 347 | 0.00063479 | 7.3175e-06 | 86.75
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 4 | 118 | 118068 | 0.21599 | 0.00021587 | 1000.5763
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | CONN/CLAMP | 7 | 64 | 9884 | 0.018082 | 0.00011708 | 154.4375
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 15 | 217 | 55765 | 0.10202 | 0.00039697 | 256.9816
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | CUTOUT | 85 | 2253 | 277260 | 0.5098 | 0.0041426 | 123.0626
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WL | CUTOUT | 1 | 0 | 0 | 0 | 0
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | INSULATOR | 2 | 28 | 1587 | 0.0029032 | 5.1223e-05 | 56.6786
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | AB | NONE | 1 | 101 | 13231 | 0.024053 | 0.00018361 | 131
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TR | FUSE | 6 | 130 | 12837 | 0.023484 | 0.00023782 | 98.7462
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | JUMPER/RISER | 1 | 6 | 408 | 0.00074639 | 1.0976e-05 | 68
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | METERING | 2 | 5 | 1158 | 0.0021184 | 9.1469e-06 | 231.6
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 3 | 712 | 17481 | 0.031979 | 0.0013025 | 24.552
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 1 | 91 | 36309 | 0.066423 | 0.00016647 | 399
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 62 | 7582 | 0.013784 | 0.00011271 | 122.2903
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 2 | 332 | 0.00060356 | 3.6359e-06 | 166
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 5 | 226 | 19397 | 0.035196 | 0.00041008 | 85.8274
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | R | NONE | 3 | 2282 | 192309 | 0.34961 | 0.0041486 | 84.2721
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 15 | 2.7061e-05 | 1.8041e-06 | 15
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | NONE | 110 | 2466 | 429785 | 0.78133 | 0.0044831 | 174.2843
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TIR | CONN/CLAMP | 4 | 22 | 4009 | 0.0072882 | 3.9995e-05 | 182.2273
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 35 | 4441 | 794192 | 1.4438 | 0.0080735 | 178.8318
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | METERING | 7 | 15 | 1106 | 0.0020106 | 2.7269e-05 | 73.7333
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 5 | 2320 | 0.0042176 | 9.0897e-06 | 464
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ERF | NONE | 26 | 6768 | 954551 | 1.7353 | 0.012304 | 141.0389
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TOR | NONE | 20 | 59 | 5832 | 0.010669 | 0.00010793 | 98.8475
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | AB | NONE | 11 | 956 | 170370 | 0.31167 | 0.0017489 | 178.2113
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 9 | 2003 | 332248 | 0.60781 | 0.0036642 | 165.8752
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | POLE | 71 | 20245 | 3135061 | 5.7645 | 0.037225 | 154.8561
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 49 | 5045 | 476401 | 0.87596 | 0.0092763 | 94.4303
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 307 | 34833 | 0.063723 | 0.00056162 | 113.4625
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | POLE HARDWARE | 1 | 120 | 41400 | 0.075736 | 0.00021953 | 345
AEP-SEP | 2022 | 550071 | PARTIAL POWER | U | CAPACITOR | 1 | 2 | 28 | 5.0903e-05 | 3.6359e-06 | 14
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | ARRESTER | 6 | 83 | 14399 | 0.026476 | 0.00015261 | 173.4819
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 297 | 15671 | 2373548 | 4.3068 | 0.028435 | 151.4612
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | REGULATOR | 2 | 270 | 46691 | 0.085415 | 0.00049393 | 172.9296
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ABI | NONE | 81 | 1466 | 228596 | 0.41479 | 0.0026601 | 155.9318
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | SWITCH, OH | 25 | 369 | 60925 | 0.11055 | 0.00066955 | 165.1084
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 20 | 69 | 7215 | 0.013116 | 0.00012544 | 104.5652
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 3 | 630 | 0.0011453 | 5.4538e-06 | 210
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | CONN/CLAMP | 4 | 20 | 5366 | 0.0098665 | 3.6774e-05 | 268.3
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | SWITCH, OH | 5 | 32 | 2761 | 0.0050509 | 5.854e-05 | 86.2812
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 6 | 1200 | 0.0021815 | 1.0908e-05 | 200
AEP-SEP | 2020 | 543859 | PARTIAL POWER | OL | TRANSFORMER, OH | 3 | 8 | 1115 | 0.0020502 | 1.471e-05 | 139.375
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | CONN/CLAMP | 28 | 114 | 11703 | 0.021518 | 0.00020961 | 102.6579
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 68 | 1730 | 505665 | 0.91753 | 0.0031391 | 292.2919
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | POLE | 43 | 3033 | 533390 | 0.96228 | 0.0054718 | 175.8622
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 1824 | 224368 | 0.40712 | 0.0033097 | 123.0088
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | BREAKER | 1 | 3 | 153 | 0.00028132 | 5.5161e-06 | 51
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 8 | 102 | 7748 | 0.014059 | 0.00018508 | 75.9608
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | POLE | 2 | 36 | 8202 | 0.015081 | 6.6194e-05 | 227.8333
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 46 | 8.3467e-05 | 1.8145e-06 | 46
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 1045 | 125400 | 0.22754 | 0.0018962 | 120
AEP-SEP | 2021 | 546634 | PARTIAL POWER | VA | NONE | 2 | 6 | 1486 | 0.0027185 | 1.0976e-05 | 247.6667
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 15 | 65 | 15693 | 0.028312 | 0.00011727 | 241.4308
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 2 | 280 | 0.00050806 | 3.629e-06 | 140
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 7 | 1897 | 0.0034224 | 1.2629e-05 | 271
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 8 | 1404 | 0.0025329 | 1.4433e-05 | 175.5
AEP-SEP | 2025 | 554297 | PARTIAL POWER | TIR | NONE | 15 | 62 | 7773 | 0.014023 | 0.00011185 | 125.371
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | POLE | 4 | 87 | 25834 | 0.046607 | 0.00015696 | 296.9425
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 447 | 123757 | 0.2264 | 0.00081773 | 276.8613
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | SPLICE, OH | 11 | 501 | 58434 | 0.10542 | 0.00090385 | 116.6347
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 186 | 21762 | 0.039261 | 0.00033556 | 117
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | ABI | NONE | 8 | 7225 | 790625 | 1.4464 | 0.013217 | 109.4291
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 12 | 5742 | 0.010359 | 2.1649e-05 | 478.5
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | SWITCH, OH | 1 | 5 | 875 | 0.0015786 | 9.0204e-06 | 175
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 4 | 752 | 0.0013757 | 7.3175e-06 | 188
AEP-SEP | 2023 | 551114 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 4 | 428 | 0.00077661 | 7.258e-06 | 107
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 4 | 556 | 0.0010089 | 7.258e-06 | 139
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 1 | 365 | 0.00066229 | 1.8145e-06 | 365
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | CUTOUT | 1 | 2 | 292 | 0.0005369 | 3.6774e-06 | 146
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 4 | 392 | 0.00072078 | 7.3548e-06 | 98
AEP-SEP | 2020 | 543859 | PARTIAL POWER | OL | FUSE | 1 | 1 | 120 | 0.00022065 | 1.8387e-06 | 120
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 273 | 19383 | 0.03564 | 0.00050197 | 71
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | NONE | 602 | 33632 | 2782914 | 5.0592 | 0.061141 | 82.746
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | NONE | 2084 | 48817 | 5093741 | 9.3184 | 0.089305 | 104.3436
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 60 | 2749 | 494745 | 0.89942 | 0.0049975 | 179.9727
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 21 | 1727 | 236989 | 0.43083 | 0.0031396 | 137.2258
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 12 | 47 | 13436 | 0.024426 | 8.5444e-05 | 285.8723
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | SPLICE, OH | 14 | 2924 | 378861 | 0.68875 | 0.0053157 | 129.5694
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 27 | 3483 | 0.0063319 | 4.9085e-05 | 129
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WT | FUSE | 1 | 2 | 62 | 0.00011271 | 3.6359e-06 | 31
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 1 | 263 | 0.00048113 | 1.8294e-06 | 263
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 4 | 204 | 0.00037086 | 7.2718e-06 | 51
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 3 | 816 | 0.0014806 | 5.4435e-06 | 272
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 6 | 228 | 0.00041371 | 1.0887e-05 | 38
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 32 | 3232 | 0.0059427 | 5.8839e-05 | 101
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 4 | 1912 | 0.0035156 | 7.3548e-06 | 478
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 2 | 328 | 0.0006031 | 3.6774e-06 | 164
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 13 | 2067 | 0.003729 | 2.3453e-05 | 159
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 6 | 829 | 0.0015071 | 1.0908e-05 | 138.1667
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | CUTOUT | 173 | 6712 | 699046 | 1.2708 | 0.012202 | 104.1487
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 16 | 151 | 57176 | 0.10394 | 0.00027451 | 378.649
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 6 | 1079 | 0.0019739 | 1.0976e-05 | 179.8333
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | NONE | 36 | 148 | 21031 | 0.03867 | 0.00027213 | 142.1014
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | CUTOUT | 5 | 85 | 19494 | 0.035662 | 0.0001555 | 229.3412
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 4 | 682 | 529154 | 0.97296 | 0.001254 | 775.8856
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | AF | POLE | 1 | 57 | 43377 | 0.079758 | 0.00010481 | 761
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | CROSSARM | 22 | 4497 | 743374 | 1.3669 | 0.0082687 | 165.3044
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 3 | 2003 | 0.0036642 | 5.4881e-06 | 667.6667
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WI | NONE | 12 | 2587 | 543806 | 0.98861 | 0.004703 | 210.2072
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 12 | 939 | 0.0017178 | 2.1953e-05 | 78.25
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 65 | 11180 | 0.020452 | 0.00011891 | 172
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TIR | CONDUCTOR UG | 2 | 8 | 1868 | 0.0034173 | 1.4635e-05 | 233.5
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 20 | 60 | 14635 | 0.026555 | 0.00010887 | 243.9167
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 12 | 148 | 60090 | 0.10903 | 0.00026855 | 406.0135
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | INSULATOR | 2 | 29 | 3841 | 0.0070625 | 5.3323e-05 | 132.4483
AEP-SEP | 2024 | 554297 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 5 | 9 | 507 | 0.00091467 | 1.6237e-05 | 56.3333
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 9 | 4612 | 0.0083204 | 1.6237e-05 | 512.4444
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | SWITCH, OH | 3 | 144 | 32708 | 0.060141 | 0.00026477 | 227.1389
AEP-SEP | 2020 | 543859 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 12 | 780 | 0.0014342 | 2.2065e-05 | 65
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | CROSSARM | 6 | 1092 | 765383 | 1.3808 | 0.0019701 | 700.9002
AEP-SEP | 2021 | 546634 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 13 | 1233 | 0.0022556 | 2.3782e-05 | 94.8462
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 11 | 1472 | 146232 | 0.26534 | 0.002671 | 99.3424
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | POLE | 9 | 1674 | 265231 | 0.48126 | 0.0030375 | 158.4415
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 3 | 402 | 0.00072943 | 5.4435e-06 | 134
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 1 | 26 | 3536 | 0.0064283 | 4.7267e-05 | 136
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | FUSE | 2 | 9 | 401 | 0.00073358 | 1.6464e-05 | 44.5556
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 1209 | 179079 | 0.3276 | 0.0022117 | 148.1216
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | ARRESTER | 20 | 209 | 24385 | 0.043993 | 0.00037705 | 116.6746
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 7 | 1449 | 0.0026292 | 1.2702e-05 | 207
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | FUSE | 22 | 165 | 17388 | 0.031369 | 0.00029767 | 105.3818
AEP-SEP | 2020 | 543859 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 3 | 793 | 0.0014581 | 5.5161e-06 | 264.3333
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 7 | 14 | 2256 | 0.00407 | 2.5257e-05 | 161.1429
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 38 | 3990 | 0.0073365 | 6.9871e-05 | 105
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 1915 | 78515 | 0.14165 | 0.0034548 | 41
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 7 | 6433 | 0.011768 | 1.2806e-05 | 919
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CF | CONN/CLAMP | 3 | 13 | 1875 | 0.0034301 | 2.3782e-05 | 144.2308
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | FUSE | 5 | 29 | 1943 | 0.0035726 | 5.3323e-05 | 67
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 1 | 73 | 0.0001317 | 1.8041e-06 | 73
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | SWITCH, OH | 2 | 316 | 16255 | 0.029325 | 0.00057009 | 51.4399
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CO | CONDUCTOR UG | 2 | 5 | 355 | 0.00064045 | 9.0204e-06 | 71
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 2 | 4 | 2396 | 0.0043226 | 7.2163e-06 | 599
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VA | CUTOUT | 2 | 11 | 992 | 0.0017897 | 1.9845e-05 | 90.1818
AEP-SEP | 2025 | 554297 | PARTIAL POWER | ABI | NONE | 1 | 2 | 56 | 0.00010103 | 3.6082e-06 | 28
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 5 | 582 | 83527 | 0.15069 | 0.00105 | 143.5172
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 2 | 152 | 0.00027422 | 3.6082e-06 | 76
AEP-SEP | 2024 | 554297 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 3 | 16 | 1849 | 0.0033358 | 2.8865e-05 | 115.5625
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 1 | 137 | 0.00025062 | 1.8294e-06 | 137
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 121 | 15620 | 0.028721 | 0.00022248 | 129.0909
AEP-SEP | 2024 | 554297 | DISTRIBUTION STATION | AO | NONE | 2 | 1423 | 751017 | 1.3549 | 0.0025672 | 527.7702
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 1 | 26 | 3578 | 0.0065789 | 4.7807e-05 | 137.6154
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 243 | 50745 | 0.092252 | 0.00044176 | 208.8272
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | OL | TRANSFORMER, POWER - LTC | 1 | 2 | 408 | 0.00074639 | 3.6588e-06 | 204
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 2 | 186 | 0.00033814 | 3.6359e-06 | 93
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | METERING | 1 | 1 | 185 | 0.00033568 | 1.8145e-06 | 185
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ABI | FUSE | 2 | 21 | 906 | 0.0016345 | 3.7886e-05 | 43.1429
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 36 | 1854 | 0.0033448 | 6.4947e-05 | 51.5
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 1 | 14 | 980 | 0.001768 | 2.5257e-05 | 70
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | SWITCH, OH | 1 | 749 | 6741 | 0.012161 | 0.0013513 | 9
AEP-SEP | 2024 | 554297 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 1835 | 121110 | 0.21849 | 0.0033105 | 66
AEP-SEP | 2022 | 550071 | PARTIAL POWER | VA | NONE | 4 | 20 | 1375 | 0.0024997 | 3.6359e-05 | 68.75
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | CONN/CLAMP | 10 | 69 | 8600 | 0.015813 | 0.00012687 | 124.6377
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | POLE | 7 | 959 | 60213 | 0.11071 | 0.0017633 | 62.7873
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 46 | 957 | 295050 | 0.53976 | 0.0017507 | 308.3072
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WU | NONE | 19 | 70 | 10076 | 0.018318 | 0.00012726 | 143.9429
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 52 | 4732 | 0.0086025 | 9.4533e-05 | 91
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 31 | 6089 | 851703 | 1.5454 | 0.011049 | 139.8757
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 4 | 30 | 10432 | 0.018965 | 5.4538e-05 | 347.7333
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | FUSE | 83 | 714 | 66850 | 0.1213 | 0.0012956 | 93.6275
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 23 | 78 | 10006 | 0.018398 | 0.00014342 | 128.2821
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 413 | 49147 | 0.089908 | 0.00075553 | 119
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | POLE | 9 | 1143 | 193631 | 0.35603 | 0.0021016 | 169.4059
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | FO | FUSE | 2 | 19 | 10723 | 0.019494 | 3.4541e-05 | 564.3684
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 286 | 21201 | 0.038983 | 0.00052587 | 74.1294
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | NONE | 716 | 42170 | 5272696 | 9.5124 | 0.076078 | 125.0343
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERF | POLE | 1 | 2 | 662 | 0.0012172 | 3.6774e-06 | 331
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | ARRESTER | 7 | 7 | 388 | 0.00071342 | 1.2871e-05 | 55.4286
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | SPLICE, OH | 15 | 665 | 59942 | 0.10877 | 0.0012066 | 90.1383
AEP-SEP | 2023 | 551114 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 16 | 2509 | 0.0045526 | 2.9032e-05 | 156.8125
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | ARRESTER | 10 | 16 | 1885 | 0.0034007 | 2.8865e-05 | 117.8125
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | BREAKER | 1 | 1 | 49 | 8.8911e-05 | 1.8145e-06 | 49
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | TRANSFORMER, OH | 1 | 8 | 1432 | 0.002633 | 1.471e-05 | 179
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | ARRESTER | 6 | 489 | 49218 | 0.090038 | 0.00089457 | 100.6503
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 4 | 9 | 1064 | 0.0019195 | 1.6237e-05 | 118.2222
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 143 | 24116 | 0.044342 | 0.00026294 | 168.6434
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 464 | 14848 | 0.026787 | 0.0008371 | 32
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 7 | 1401 | 35480 | 0.064009 | 0.0025275 | 25.3248
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 2 | 11 | 3439 | 0.0062043 | 1.9845e-05 | 312.6364
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TIR | ARRESTER | 1 | 2 | 142 | 0.0002611 | 3.6774e-06 | 71
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 2 | 19 | 9728 | 0.017685 | 3.4541e-05 | 512
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WT | CONDUCTOR UG | 1 | 1 | 227 | 0.00040953 | 1.8041e-06 | 227
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | JUMPER/RISER | 2 | 6 | 652 | 0.0011763 | 1.0825e-05 | 108.6667
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 5 | 87 | 28375 | 0.052173 | 0.00015997 | 326.1494
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 1661 | 44847 | 0.080908 | 0.0029966 | 27
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | GUY/ANCHOR | 1 | 6 | 660 | 0.0011976 | 1.0887e-05 | 110
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 3 | 200 | 23453 | 0.042311 | 0.00036082 | 117.265
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 225 | 109350 | 0.20106 | 0.00041371 | 486
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | FO | CUTOUT | 2 | 125 | 18960 | 0.034862 | 0.00022984 | 151.68
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 4 | 652 | 0.0011928 | 7.3175e-06 | 163
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 2 | 1107 | 29889 | 0.053922 | 0.0019971 | 27
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 4 | 399 | 0.00071983 | 7.2163e-06 | 99.75
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 34 | 5018 | 0.0090529 | 6.1339e-05 | 147.5882
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WFS | NONE | 1 | 6 | 1080 | 0.0019484 | 1.0825e-05 | 180
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 4 | 380 | 0.00068555 | 7.2163e-06 | 95
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 2 | 542 | 0.00099658 | 3.6774e-06 | 271
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 1 | 90 | 0.00016331 | 1.8145e-06 | 90
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | R | NONE | 2 | 916 | 114503 | 0.21054 | 0.0016843 | 125.0033
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WU | ARRESTER | 1 | 1 | 34 | 6.2199e-05 | 1.8294e-06 | 34
AEP-SEP | 2023 | 551114 | DISTRIBUTION SOURCE | TOR | NONE | 1 | 469 | 62846 | 0.11403 | 0.000851 | 134
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | SWITCH, OH | 1 | 2 | 482 | 0.00088626 | 3.6774e-06 | 241
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | FUSE | 136 | 3542 | 569328 | 1.035 | 0.0064392 | 160.7363
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WL | NONE | 60 | 139 | 16150 | 0.02936 | 0.00025269 | 116.1871
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | NONE | 649 | 11604 | 1397746 | 2.557 | 0.021228 | 120.4538
AEP-SEP | 2022 | 550071 | PARTIAL POWER | FO | NONE | 5 | 41 | 6668 | 0.012122 | 7.4536e-05 | 162.6341
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | CUTOUT | 104 | 3602 | 532360 | 0.97389 | 0.0065894 | 147.7957
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | JUMPER/RISER | 18 | 582 | 102989 | 0.18723 | 0.001058 | 176.957
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | AF | ARRESTER | 1 | 8 | 432 | 0.00077937 | 1.4433e-05 | 54
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | SWITCH, UG | 1 | 39 | 1716 | 0.0030958 | 7.0359e-05 | 44
AEP-SEP | 2025 | 554297 | PARTIAL POWER | ERF | PEDESTAL | 1 | 7 | 154 | 0.00027783 | 1.2629e-05 | 22
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 1 | 264 | 0.00047994 | 1.8179e-06 | 264
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 5 | 27 | 1865 | 0.0033646 | 4.871e-05 | 69.0741
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 557 | 60547 | 0.10986 | 0.0010107 | 108.702
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 1514 | 151400 | 0.27472 | 0.0027472 | 100
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 5 | 14 | 2581 | 0.0046832 | 2.5403e-05 | 184.3571
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WU | ARRESTER | 1 | 1 | 456 | 0.00083845 | 1.8387e-06 | 456
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 3 | 4 | 390 | 0.00070359 | 7.2163e-06 | 97.5
AEP-SEP | 2022 | 550071 | PARTIAL POWER | U | CABLE TERMINATOR | 1 | 4 | 388 | 0.00070536 | 7.2718e-06 | 97
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 2 | 149 | 0.00027258 | 3.6588e-06 | 74.5
AEP-SEP | 2021 | 546634 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 47 | 8.5981e-05 | 1.8294e-06 | 47
AEP-SEP | 2025 | 554297 | DISTRIBUTION SOURCE | TOR | NONE | 3 | 76 | 6806 | 0.012279 | 0.00013711 | 89.5526
AEP-SEP | 2025 | 554297 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 2 | 302 | 0.00054483 | 3.6082e-06 | 151
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 57 | 10449 | 0.018851 | 0.00010283 | 183.3158
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 67 | 15007 | 0.027074 | 0.00012087 | 223.9851
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 95 | 19520 | 0.035216 | 0.00017139 | 205.4737
AEP-SEP | 2025 | 554297 | PARTIAL POWER | WW | NONE | 1 | 6 | 4452 | 0.0080318 | 1.0825e-05 | 742
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 120 | 78411 | 0.14255 | 0.00021815 | 653.425
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | ARRESTER | 56 | 985 | 102820 | 0.1881 | 0.0018019 | 104.3858
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 15 | 178 | 39247 | 0.071349 | 0.00032359 | 220.4888
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1 | 116 | 0.00021088 | 1.8179e-06 | 116
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 5 | 12 | 2121 | 0.0038999 | 2.2065e-05 | 176.75
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | SWITCH, OH | 24 | 2620 | 268740 | 0.49163 | 0.004793 | 102.5725
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WU | FUSE | 3 | 21 | 7241 | 0.013164 | 3.8177e-05 | 344.8095
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | POLE | 69 | 10450 | 1400911 | 2.542 | 0.018962 | 134.0585
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | SWITCH, OH | 10 | 1399 | 121904 | 0.22162 | 0.0025433 | 87.1365
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | FUSE | 145 | 1306 | 191912 | 0.34823 | 0.0023697 | 146.9464
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | CONDUCTOR UG | 4 | 84 | 15627 | 0.028588 | 0.00015367 | 186.0357
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WT | POLE | 4 | 984 | 625891 | 1.1378 | 0.0017889 | 636.0681
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | FUSE | 5 | 91 | 25175 | 0.04629 | 0.00016732 | 276.6484
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | TRANSFORMER, STATION SERVICE | 1 | 4 | 376 | 0.00068785 | 7.3175e-06 | 94
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | NONE | 34 | 136 | 11533 | 0.020927 | 0.00024677 | 84.8015
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | CUTOUT | 3 | 61 | 15756 | 0.028971 | 0.00011216 | 258.2951
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 6 | 336 | 0.00061467 | 1.0976e-05 | 56
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 4 | 218 | 109512 | 0.20136 | 0.00040084 | 502.3486
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 2 | 7 | 1090 | 0.001994 | 1.2806e-05 | 155.7143
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | METERING | 7 | 12 | 985 | 0.0018111 | 2.2065e-05 | 82.0833
AEP-SEP | 2023 | 551114 | PARTIAL POWER | U | FUSE | 5 | 12 | 1598 | 0.0028996 | 2.1774e-05 | 133.1667
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | SPLICE, OH | 3 | 4 | 480 | 0.00088258 | 7.3548e-06 | 120
AEP-SEP | 2020 | 543859 | PARTIAL POWER | ERF | NONE | 4 | 12 | 973 | 0.0017891 | 2.2065e-05 | 81.0833
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 21 | 1092 | 138970 | 0.25216 | 0.0019814 | 127.2619
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | ARRESTER | 3 | 17 | 2727 | 0.0050142 | 3.1258e-05 | 160.4118
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 85 | 0.00015629 | 1.8387e-06 | 85
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 3 | 94 | 43679 | 0.079256 | 0.00017056 | 464.6702
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | OL | FUSE | 2 | 8 | 522 | 0.00095981 | 1.471e-05 | 65.25
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | SWITCH, OH | 9 | 24 | 2098 | 0.0038068 | 4.3548e-05 | 87.4167
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | BREAKER | 3 | 1193 | 86881 | 0.15975 | 0.0021936 | 72.8256
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 294 | 324209 | 0.5849 | 0.0005304 | 1102.7517
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERF | NONE | 31 | 3323 | 84897 | 0.15316 | 0.005995 | 25.5483
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | FUSE | 1 | 1 | 78 | 0.00014153 | 1.8145e-06 | 78
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TR | POLE | 11 | 257 | 50288 | 0.091996 | 0.00047015 | 195.6732
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 10 | 190 | 33469 | 0.060381 | 0.00034278 | 176.1526
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | TRANSFORMER, UG | 1 | 7 | 1113 | 0.0020079 | 1.2629e-05 | 159
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 143 | 9253 | 1581474 | 2.8531 | 0.016693 | 170.9147
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | METERING | 1 | 7 | 2330 | 0.0042278 | 1.2702e-05 | 332.8571
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | CUTOUT | 9 | 137 | 17800 | 0.032113 | 0.00024716 | 129.927
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | POLE HARDWARE | 1 | 78 | 18736 | 0.033801 | 0.00014072 | 240.2051
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WL | SWITCH, OH | 1 | 3 | 795 | 0.0014342 | 5.4123e-06 | 265
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 12 | 6668 | 0.012198 | 2.1953e-05 | 555.6667
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERF | FUSE | 1 | 2 | 266 | 0.0004891 | 3.6774e-06 | 133
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | FO | PEDESTAL | 2 | 10 | 928 | 0.0016742 | 1.8041e-05 | 92.8
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | CF | JUMPER/RISER | 1 | 39 | 2964 | 0.0053473 | 7.0359e-05 | 76
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 20 | 3628 | 0.0065452 | 3.6082e-05 | 181.4
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 1114 | 271485 | 0.49918 | 0.0020483 | 243.7029
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VIN | POLE | 1 | 3 | 594 | 0.0010716 | 5.4123e-06 | 198
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | POLE | 1 | 1 | 177 | 0.0003238 | 1.8294e-06 | 177
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | CAPACITOR | 1 | 1 | 52 | 9.5128e-05 | 1.8294e-06 | 52
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 94 | 19620 | 0.035396 | 0.00016958 | 208.7234
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VIN | POLE | 1 | 4 | 1088 | 0.0019779 | 7.2718e-06 | 272
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 3 | 13 | 1448 | 0.0026274 | 2.3589e-05 | 111.3846
AEP-SEP | 2020 | 543859 | PARTIAL POWER | OL | CONN/CLAMP | 1 | 3 | 237 | 0.00043577 | 5.5161e-06 | 79
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TR | OTHER EQUIPMENT | 1 | 5 | 595 | 0.0010885 | 9.1469e-06 | 119
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 16 | 1403 | 0.0025666 | 2.927e-05 | 87.6875
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | CROSSARM | 5 | 1383 | 75616 | 0.13642 | 0.0024951 | 54.6753
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 2 | 250 | 0.00045102 | 3.6082e-06 | 125
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 6 | 1554 | 0.0028197 | 1.0887e-05 | 259
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 435 | 130284 | 0.2364 | 0.00078931 | 299.5034
AEP-SEP | 2024 | 554297 | PARTIAL POWER | FO | TRANSFORMER, OH | 1 | 4 | 900 | 0.0016237 | 7.2163e-06 | 225
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 1 | 109 | 0.00019778 | 1.8145e-06 | 109
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 3 | 638 | 374876 | 0.68579 | 0.0011671 | 587.5799
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WI | FUSE | 1 | 1 | 1157 | 0.0020994 | 1.8145e-06 | 1157
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WI | SWITCH, OH | 1 | 4 | 464 | 0.00084883 | 7.3175e-06 | 116
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | NETWORK LIMITER | 1 | 13 | 11609 | 0.021105 | 2.3633e-05 | 893
AEP-SEP | 2023 | 551114 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 3 | 1335 | 0.0024224 | 5.4435e-06 | 445
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 2 | 242 | 0.00043911 | 3.629e-06 | 121
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 47 | 4374 | 0.0079517 | 8.5444e-05 | 93.0638
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TR | NONE | 124 | 6328 | 638249 | 1.1676 | 0.011576 | 100.8611
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 12 | 48 | 19416 | 0.035297 | 8.7261e-05 | 404.5
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 9 | 22 | 2469 | 0.0045167 | 4.0246e-05 | 112.2273
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 76 | 5223 | 1453162 | 2.6719 | 0.0096036 | 278.2236
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 18 | 6163 | 0.011204 | 3.2723e-05 | 342.3889
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | INSULATOR | 21 | 2629 | 719649 | 1.3232 | 0.004834 | 273.7349
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | CROSSARM | 27 | 5145 | 1304215 | 2.3981 | 0.0094602 | 253.4917
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 2 | 985 | 0.0018111 | 3.6774e-06 | 492.5
AEP-SEP | 2022 | 550071 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 10 | 704 | 0.0012798 | 1.8179e-05 | 70.4
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 796 | 125760 | 0.23006 | 0.0014562 | 157.9899
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | EQF | SWITCH, OH | 4 | 1416 | 170964 | 0.31276 | 0.0025904 | 120.7373
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | SECTIONALIZER | 1 | 8 | 8968 | 0.01649 | 1.471e-05 | 1121
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 21 | 5203 | 795189 | 1.4429 | 0.0094409 | 152.8328
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 226 | 6984 | 1117359 | 2.0158 | 0.0126 | 159.9884
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 6 | 38 | 3966 | 0.0071963 | 6.8951e-05 | 104.3684
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 376 | 27096 | 4194787 | 7.5678 | 0.048884 | 154.812
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 5 | 10 | 2134 | 0.0038499 | 1.8041e-05 | 213.4
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 19 | 2039 | 0.0036785 | 3.4278e-05 | 107.3158
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 14 | 44 | 20491 | 0.036968 | 7.938e-05 | 465.7045
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ABI | FUSE | 1 | 1 | 55 | 0.00010062 | 1.8294e-06 | 55
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 13 | 2743 | 0.0049772 | 2.3589e-05 | 211
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | OL | SWITCH, UG | 1 | 60 | 23280 | 0.042805 | 0.00011032 | 388
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | U | CUTOUT | 1 | 1 | 73 | 0.00013423 | 1.8387e-06 | 73
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 14 | 4928 | 0.0090612 | 2.5742e-05 | 352
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 89 | 13814 | 0.025066 | 0.00016149 | 155.2135
AEP-SEP | 2023 | 551114 | PARTIAL POWER | OL | FUSE | 4 | 14 | 1205 | 0.0021865 | 2.5403e-05 | 86.0714
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WT | NONE | 9 | 66 | 38606 | 0.070051 | 0.00011976 | 584.9394
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 6 | 370 | 0.00067137 | 1.0887e-05 | 61.6667
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 1 | 279 | 0.00050625 | 1.8145e-06 | 279
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | EQF | BREAKER | 5 | 3954 | 484996 | 0.89177 | 0.0072703 | 122.6596
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | NETWORK TRANSFORMER | 1 | 185 | 61235 | 0.11111 | 0.00033568 | 331
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 7 | 19 | 5627 | 0.01021 | 3.4476e-05 | 296.1579
AEP-SEP | 2024 | 554297 | DISTRIBUTION STATION | AB | NONE | 6 | 4267 | 503426 | 0.90822 | 0.007698 | 117.9813
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | FUSE | 1 | 2 | 104 | 0.00019123 | 3.6774e-06 | 52
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 4 | 420 | 0.00076209 | 7.258e-06 | 105
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | ARRESTER | 3 | 139 | 15952 | 0.028779 | 0.00025077 | 114.7626
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 4 | 14 | 14856 | 0.026802 | 2.5257e-05 | 1061.1429
AEP-SEP | 2025 | 554297 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 12 | 35 | 6560 | 0.011835 | 6.3143e-05 | 187.4286
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 124 | 11730 | 0.021162 | 0.00022371 | 94.5968
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 3 | 37 | 10058 | 0.018146 | 6.6751e-05 | 271.8378
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 1 | 109 | 0.00019665 | 1.8041e-06 | 109
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | WL | INSULATOR | 1 | 608 | 32832 | 0.059687 | 0.0011053 | 54
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | O | NONE | 1 | 1067 | 8536 | 0.015518 | 0.0019397 | 8
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ABI | NONE | 15 | 65 | 5944 | 0.010723 | 0.00011727 | 91.4462
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | SWITCH, OH | 2 | 6 | 822 | 0.0015037 | 1.0976e-05 | 137
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | POLE | 3 | 3 | 815 | 0.0014703 | 5.4123e-06 | 271.6667
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TR | NONE | 1 | 8 | 2336 | 0.0042734 | 1.4635e-05 | 292
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CF | NONE | 1 | 2 | 698 | 0.0012834 | 3.6774e-06 | 349
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | CUTOUT | 1 | 3 | 630 | 0.0011453 | 5.4538e-06 | 210
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | CONN/CLAMP | 1 | 2 | 162 | 0.00029395 | 3.629e-06 | 81
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | SPLICE, UG | 1 | 1 | 238 | 0.00043761 | 1.8387e-06 | 238
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | CUTOUT | 3 | 4 | 739 | 0.0013332 | 7.2163e-06 | 184.75
AEP-SEP | 2024 | 554297 | PARTIAL POWER | U | FUSE | 1 | 1 | 104 | 0.00018763 | 1.8041e-06 | 104
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | POLE | 1 | 37 | 3552 | 0.0064081 | 6.6751e-05 | 96
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 4 | 552 | 0.00099586 | 7.2163e-06 | 138
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 2 | 798 | 0.0014673 | 3.6774e-06 | 399
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | NONE | 613 | 27314 | 3909874 | 7.0945 | 0.049561 | 143.1454
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ABI | NONE | 102 | 984 | 70426 | 0.12803 | 0.0017889 | 71.5711
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 2 | 74 | 22082 | 0.040144 | 0.00013453 | 298.4054
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WL | ARRESTER | 6 | 12 | 965 | 0.0017543 | 2.1815e-05 | 80.4167
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | WL | NONE | 7 | 3556 | 603846 | 1.0978 | 0.0064646 | 169.8105
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 93 | 17763 | 0.032292 | 0.00016907 | 191
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 12 | 129 | 92009 | 0.16727 | 0.00023452 | 713.2481
AEP-SEP | 2022 | 550071 | PARTIAL POWER | A | NONE | 42 | 298 | 15495 | 0.028169 | 0.00054175 | 51.9966
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | POLE | 29 | 4210 | 808003 | 1.4857 | 0.007741 | 191.9247
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 16 | 2128 | 341486 | 0.6208 | 0.0038686 | 160.4727
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 5 | 41 | 16105 | 0.029278 | 7.4536e-05 | 392.8049
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 87 | 3225 | 283705 | 0.519 | 0.0058997 | 87.9705
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | OL | FUSE | 17 | 503 | 57043 | 0.1037 | 0.00091443 | 113.4056
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 141 | 1542 | 356424 | 0.65203 | 0.0028209 | 231.144
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | NONE | 1974 | 29522 | 1935053 | 3.558 | 0.054282 | 65.5461
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | EQF | BREAKER | 6 | 4647 | 341219 | 0.62422 | 0.0085011 | 73.4278
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 5 | 391 | 0.00071529 | 9.1469e-06 | 78.2
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WI | NONE | 54 | 1511 | 911738 | 1.6679 | 0.0027642 | 603.4004
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 706 | 36109 | 0.066057 | 0.0012915 | 51.1459
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 3 | 30 | 3950 | 0.0071809 | 5.4538e-05 | 131.6667
AEP-SEP | 2022 | 550071 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 24 | 1538 | 0.002796 | 4.3631e-05 | 64.0833
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | FO | NONE | 60 | 1517 | 165769 | 0.30079 | 0.0027526 | 109.2742
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 50 | 42311 | 0.076919 | 9.0897e-05 | 846.22
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | OL | FUSE | 9 | 586 | 50712 | 0.092771 | 0.001072 | 86.5392
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | SWITCH, OH | 2 | 3 | 226 | 0.00041344 | 5.4881e-06 | 75.3333
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | AF | NONE | 3 | 459 | 70686 | 0.12931 | 0.00083968 | 154
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 2 | 276 | 0.00050175 | 3.6359e-06 | 138
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 2 | 1376 | 0.0025015 | 3.6359e-06 | 688
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 7 | 1252 | 0.0023021 | 1.2871e-05 | 178.8571
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WW | POLE | 11 | 197 | 56250 | 0.10207 | 0.00035746 | 285.533
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TR | POLE | 4 | 790 | 79617 | 0.14447 | 0.0014335 | 100.781
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WW | POLE | 5 | 1297 | 102544 | 0.185 | 0.0023399 | 79.0625
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | O | NONE | 23 | 1308 | 105335 | 0.19113 | 0.0023734 | 80.5313
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | FUSE | 4 | 5 | 266 | 0.00048661 | 9.1469e-06 | 53.2
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | TRANSFORMER, UG | 2 | 6 | 3841 | 0.0070625 | 1.1032e-05 | 640.1667
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 1 | 8 | 312 | 0.00057368 | 1.471e-05 | 39
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 5 | 33 | 8632 | 0.015573 | 5.9535e-05 | 261.5758
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | ARRESTER | 4 | 36 | 2476 | 0.0044927 | 6.5322e-05 | 68.7778
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WFS | POLE | 2 | 667 | 66731 | 0.12039 | 0.0012033 | 100.0465
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | CUTOUT | 2 | 66 | 3291 | 0.0059829 | 0.00011998 | 49.8636
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 29 | 2606 | 0.0047286 | 5.2621e-05 | 89.8621
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TOR | OTHER EQUIPMENT | 1 | 11 | 1749 | 0.0031736 | 1.996e-05 | 159
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TR | FUSE | 1 | 5 | 285 | 0.00051811 | 9.0897e-06 | 57
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 12 | 1980 | 0.0035721 | 2.1649e-05 | 165
AEP-SEP | 2022 | 550071 | PARTIAL POWER | U | CONN/CLAMP | 2 | 13 | 654 | 0.0011889 | 2.3633e-05 | 50.3077
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 51 | 2144 | 96544 | 0.17417 | 0.003868 | 45.0299
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | VA | POLE | 25 | 3371 | 370429 | 0.66829 | 0.0060816 | 109.887
AEP-SEP | 2025 | 554297 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 4 | 4 | 530 | 0.00095617 | 7.2163e-06 | 132.5
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WW | NONE | 30 | 653 | 58869 | 0.1062 | 0.0011781 | 90.1516
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 1 | 8 | 1344 | 0.0024247 | 1.4433e-05 | 168
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WU | POLE | 3 | 5 | 1628 | 0.0029371 | 9.0204e-06 | 325.6
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 4 | 3394 | 337571 | 0.61754 | 0.0062089 | 99.4611
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | ARRESTER | 9 | 18 | 2592 | 0.0047032 | 3.2661e-05 | 144
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 3 | 89 | 50334 | 0.09255 | 0.00016365 | 565.5506
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 425 | 0.00077117 | 1.8145e-06 | 425
AEP-SEP | 2020 | 543859 | PARTIAL POWER | U | NONE | 25 | 370 | 12080 | 0.022212 | 0.00068032 | 32.6486
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | U | FUSE | 37 | 1035 | 140500 | 0.25494 | 0.001878 | 135.7488
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | CABLE TERMINATOR | 1 | 116 | 17671 | 0.03188 | 0.00020927 | 152.3362
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | POLE | 3 | 44 | 24044 | 0.043986 | 8.0493e-05 | 546.4545
AEP-SEP | 2024 | 554297 | PARTIAL POWER | ERF | METERING | 1 | 5 | 540 | 0.00097421 | 9.0204e-06 | 108
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TR | FUSE | 2 | 44 | 3003 | 0.0055217 | 8.0903e-05 | 68.25
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | METERING | 4 | 13 | 1301 | 0.0023607 | 2.3589e-05 | 100.0769
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | FUSE | 1 | 1 | 53 | 9.6169e-05 | 1.8145e-06 | 53
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 6 | 2346 | 0.0042568 | 1.0887e-05 | 391
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | METERING | 3 | 148 | 17918 | 0.032326 | 0.000267 | 121.0676
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 13 | 2710 | 0.0049173 | 2.3589e-05 | 208.4615
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 150 | 14691 | 3114958 | 5.6197 | 0.026504 | 212.0317
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | ARRESTER | 54 | 1116 | 174259 | 0.31438 | 0.0020134 | 156.1461
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 4 | 1009 | 134874 | 0.24332 | 0.0018203 | 133.671
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | SPLICE, OH | 3 | 162 | 86892 | 0.15676 | 0.00029226 | 536.3704
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WT | NONE | 17 | 75 | 27284 | 0.049223 | 0.00013531 | 363.7867
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WW | POLE | 4 | 138 | 106126 | 0.19146 | 0.00024896 | 769.029
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 183 | 32982 | 0.060337 | 0.00033478 | 180.2295
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | SWITCH, OH | 9 | 603 | 74049 | 0.13359 | 0.0010879 | 122.801
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 145 | 14240 | 0.02605 | 0.00026526 | 98.2069
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 27 | 4680 | 0.0086052 | 4.9645e-05 | 173.3333
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | CAPACITOR | 1 | 22 | 1430 | 0.0025997 | 3.9995e-05 | 65
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 2 | 544 | 0.00098896 | 3.6359e-06 | 272
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 20 | 3900 | 0.0070766 | 3.629e-05 | 195
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 2 | 41 | 4525 | 0.0081635 | 7.3968e-05 | 110.3659
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 4 | 478 | 0.00086235 | 7.2163e-06 | 119.5
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 14 | 5613 | 0.010126 | 2.5257e-05 | 400.9286
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 105 | 19845 | 0.035802 | 0.00018943 | 189
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | NONE | 3822 | 184101 | 25616800 | 46.8628 | 0.33679 | 139.1454
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 50 | 8232 | 0.014965 | 9.0897e-05 | 164.64
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | AO | NONE | 6 | 3737 | 315035 | 0.57272 | 0.0067937 | 84.3016
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | ARRESTER | 10 | 187 | 14107 | 0.025807 | 0.00034209 | 75.4385
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | NONE | 23 | 5369 | 195491 | 0.35763 | 0.0098219 | 36.4111
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 2 | 33 | 10104 | 0.018484 | 6.0369e-05 | 306.1818
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 36 | 8432 | 0.015504 | 6.6194e-05 | 234.2222
AEP-SEP | 2020 | 543859 | PARTIAL POWER | A | NONE | 49 | 143 | 9709 | 0.017852 | 0.00026294 | 67.8951
AEP-SEP | 2022 | 550071 | DISTRIBUTION SOURCE | EQF | TRANSFORMER, OH | 1 | 3 | 2409 | 0.0043794 | 5.4538e-06 | 803
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | CROSSARM | 20 | 3375 | 1219527 | 2.231 | 0.0061741 | 361.3413
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 99 | 6878 | 867263 | 1.5946 | 0.012647 | 126.0923
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | NONE | 2459 | 33823 | 2786921 | 5.0278 | 0.06102 | 82.3972
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | SWITCH, OH | 4 | 9 | 706 | 0.0012981 | 1.6548e-05 | 78.4444
AEP-SEP | 2023 | 551114 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 10 | 458 | 0.00083104 | 1.8145e-05 | 45.8
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WL | CONDUCTOR UG | 2 | 18 | 1291 | 0.002347 | 3.2723e-05 | 71.7222
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 50 | 3250 | 0.0059758 | 9.1936e-05 | 65
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | ARRESTER | 1 | 1 | 350 | 0.00064355 | 1.8387e-06 | 350
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | ERF | NONE | 5 | 4247 | 227534 | 0.41837 | 0.007809 | 53.5752
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 14 | 359 | 69383 | 0.1259 | 0.00065141 | 193.2674
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TOR | NONE | 9 | 14 | 1712 | 0.0030886 | 2.5257e-05 | 122.2857
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TIR | NONE | 42 | 249 | 35530 | 0.064099 | 0.00044922 | 142.6908
AEP-SEP | 2020 | 543859 | PARTIAL POWER | VIN | NONE | 19 | 63 | 5389 | 0.0099088 | 0.00011584 | 85.5397
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 2 | 10 | 2526 | 0.0046446 | 1.8387e-05 | 252.6
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 2914 | 327822 | 0.60277 | 0.005358 | 112.499
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 5 | 19 | 2072 | 0.0037597 | 3.4476e-05 | 109.0526
AEP-SEP | 2023 | 551114 | PARTIAL POWER | ERF | NONE | 3 | 27 | 1925 | 0.0034929 | 4.8992e-05 | 71.2963
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 8 | 61 | 8777 | 0.015834 | 0.00011005 | 143.8852
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | POLE | 64 | 4262 | 727610 | 1.3127 | 0.007689 | 170.7203
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ERF | NONE | 30 | 1893 | 93112 | 0.16798 | 0.0034151 | 49.1875
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TIR | OTHER EQUIPMENT | 1 | 6 | 600 | 0.0010825 | 1.0825e-05 | 100
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 1067 | 75561 | 0.13632 | 0.001925 | 70.8163
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | FUSE | 7 | 12 | 1105 | 0.0019935 | 2.1649e-05 | 92.0833
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | JUMPER/RISER | 7 | 232 | 17905 | 0.032755 | 0.00042442 | 77.1767
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 69 | 61504 | 0.11251 | 0.00012623 | 891.3623
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 56 | 13328 | 0.02423 | 0.00010181 | 238
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 824 | 33784 | 0.061418 | 0.001498 | 41
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CO | CUTOUT | 8 | 428 | 48514 | 0.08875 | 0.00078297 | 113.3505
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 447 | 23095 | 4495986 | 8.158 | 0.041906 | 194.6736
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WL | ARRESTER | 3 | 8 | 1352 | 0.0024733 | 1.4635e-05 | 169
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 5 | 10 | 1337 | 0.0024584 | 1.8387e-05 | 133.7
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | CROSSARM | 48 | 8844 | 1832775 | 3.3256 | 0.016047 | 207.2337
AEP-SEP | 2022 | 550071 | DISTRIBUTION SOURCE | WU | NONE | 1 | 1 | 105 | 0.00019088 | 1.8179e-06 | 105
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | EQF | RELAY | 1 | 419 | 111873 | 0.20338 | 0.00076172 | 267
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 4 | 1216 | 0.0022106 | 7.2718e-06 | 304
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | FUSE | 44 | 543 | 72344 | 0.13127 | 0.00098528 | 133.2302
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 4 | 57 | 18132 | 0.03334 | 0.00010481 | 318.1053
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 8 | 39 | 5913 | 0.010872 | 7.171e-05 | 151.6154
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TR | ARRESTER | 1 | 2 | 334 | 0.00060719 | 3.6359e-06 | 167
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ABI | SWITCH, OH | 1 | 1 | 123 | 0.00022501 | 1.8294e-06 | 123
AEP-SEP | 2023 | 551114 | PARTIAL POWER | U | SPLICE, UG | 1 | 10 | 2700 | 0.0048992 | 1.8145e-05 | 270
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ABI | NONE | 82 | 1172 | 200794 | 0.36225 | 0.0021144 | 171.3259
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | METERING | 9 | 13 | 1655 | 0.0030276 | 2.3782e-05 | 127.3077
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VA | NONE | 114 | 16065 | 1595785 | 2.8789 | 0.028983 | 99.333
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | FUSE | 1 | 2 | 298 | 0.00054072 | 3.629e-06 | 149
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 1 | 57 | 0.00010362 | 1.8179e-06 | 57
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 12 | 12240 | 0.022082 | 2.1649e-05 | 1020
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | FUSE | 1 | 1 | 68 | 0.00012362 | 1.8179e-06 | 68
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | BREAKER | 1 | 54 | 4266 | 0.0077554 | 9.8169e-05 | 79
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | ABI | SWITCH, OH | 4 | 3254 | 851443 | 1.5656 | 0.0059832 | 261.6604
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 1 | 156 | 0.00028538 | 1.8294e-06 | 156
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | U | NONE | 7 | 4109 | 196192 | 0.35891 | 0.0075169 | 47.7469
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WL | NONE | 369 | 5903 | 709591 | 1.2802 | 0.01065 | 120.2085
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | FUSE | 77 | 1610 | 173771 | 0.3135 | 0.0029046 | 107.9323
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 90 | 0.00016548 | 1.8387e-06 | 90
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 71 | 39084 | 0.071499 | 0.00012989 | 550.4789
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 11 | 1963 | 0.0035414 | 1.9845e-05 | 178.4545
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CO | TRANSFORMER, OH | 2 | 8 | 2621 | 0.0047285 | 1.4433e-05 | 327.625
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WI | TRANSFORMER, OH | 1 | 2 | 532 | 0.00097323 | 3.6588e-06 | 266
AEP-SEP | 2023 | 551114 | PARTIAL POWER | A | SPLICE, OH | 1 | 1 | 64 | 0.00011613 | 1.8145e-06 | 64
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 728 | 98472 | 0.17765 | 0.0013134 | 135.2637
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WH | NONE | 2 | 3 | 222 | 0.00040051 | 5.4123e-06 | 74
AEP-SEP | 2025 | 554297 | DISTRIBUTION SOURCE | EQF | SPLICE, OH | 1 | 972 | 15552 | 0.028057 | 0.0017536 | 16
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | SWITCH, UG | 1 | 9 | 2538 | 0.0045788 | 1.6237e-05 | 282
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 5 | 1275 | 0.0023002 | 9.0204e-06 | 255
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 2 | 6 | 1938 | 0.0034963 | 1.0825e-05 | 323
AEP-SEP | 2024 | 554297 | PARTIAL POWER | A | TRANSFORMER, UG | 1 | 1 | 397 | 0.00071622 | 1.8041e-06 | 397
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 10 | 1198 | 0.0021613 | 1.8041e-05 | 119.8
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | SWITCH, UG | 1 | 3 | 297 | 0.0005461 | 5.5161e-06 | 99
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 1 | 2 | 32 | 5.8064e-05 | 3.629e-06 | 16
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 4 | 704 | 0.0012774 | 7.258e-06 | 176
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | POLE | 38 | 2125 | 521179 | 0.94748 | 0.0038631 | 245.2607
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | WL | ARRESTER | 1 | 9 | 1395 | 0.002552 | 1.6464e-05 | 155
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | POLE | 34 | 4277 | 1120479 | 2.0498 | 0.0078242 | 261.9778
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | ARRESTER | 4 | 30 | 2981 | 0.0054193 | 5.4538e-05 | 99.3667
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 161 | 5442 | 483890 | 0.87802 | 0.0098745 | 88.9177
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | NONE | 881 | 58759 | 8980562 | 16.2953 | 0.10662 | 152.8372
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 2 | 20 | 2626 | 0.0048039 | 3.6588e-05 | 131.3
AEP-SEP | 2022 | 550071 | DISTRIBUTION SOURCE | U | NONE | 1 | 62 | 15252 | 0.027727 | 0.00011271 | 246
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | UB | NONE | 9 | 4516 | 209030 | 0.38435 | 0.0083036 | 46.2865
AEP-SEP | 2021 | 546634 | PARTIAL POWER | EQF | CUTOUT | 9 | 20 | 5179 | 0.0094743 | 3.6588e-05 | 258.95
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | ARRESTER | 5 | 8 | 2519 | 0.0046317 | 1.471e-05 | 314.875
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 5 | 930 | 0.0017013 | 9.1469e-06 | 186
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TOR | POLE | 41 | 4259 | 916329 | 1.6627 | 0.007728 | 215.1512
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 2 | 196 | 22311 | 0.041024 | 0.00036039 | 113.8316
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | FUSE | 97 | 1426 | 194780 | 0.35343 | 0.0025875 | 136.5919
AEP-SEP | 2022 | 550071 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 7 | 1883 | 0.0034232 | 1.2726e-05 | 269
AEP-SEP | 2024 | 554297 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 9 | 7000 | 817797 | 1.4754 | 0.012629 | 116.8281
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WFS | METERING | 1 | 1 | 95 | 0.00017139 | 1.8041e-06 | 95
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | POLE | 4 | 43 | 5832 | 0.010521 | 7.7576e-05 | 135.6279
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | POLE | 1 | 26 | 2184 | 0.0039629 | 4.7177e-05 | 84
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | OL | SWITCH, OH | 1 | 100 | 34435 | 0.062483 | 0.00018145 | 344.35
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | ARRESTER | 1 | 45 | 1845 | 0.0033285 | 8.1184e-05 | 41
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WL | FUSE | 2 | 2 | 385 | 0.00069457 | 3.6082e-06 | 192.5
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | EQF | SWITCH, OH | 3 | 2036 | 245947 | 0.44627 | 0.0036943 | 120.7991
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 115 | 7843 | 1022025 | 1.8697 | 0.014348 | 130.3105
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | FO | POLE | 3 | 5 | 1624 | 0.0029709 | 9.1469e-06 | 324.8
AEP-SEP | 2022 | 550071 | PARTIAL POWER | ABI | NONE | 2 | 2 | 133 | 0.00024179 | 3.6359e-06 | 66.5
AEP-SEP | 2022 | 550071 | PARTIAL POWER | VIN | NONE | 19 | 45 | 5786 | 0.010519 | 8.1808e-05 | 128.5778
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | NONE | 606 | 30767 | 6215600 | 11.4287 | 0.056572 | 202.0216
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 60 | 4648 | 0.0084498 | 0.00010908 | 77.4667
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | SWITCH, OH | 15 | 201 | 54206 | 0.098544 | 0.00036541 | 269.6816
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WU | NONE | 371 | 18322 | 2574919 | 4.7345 | 0.033689 | 140.537
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 2 | 16 | 9360 | 0.017016 | 2.9087e-05 | 585
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | METERING | 6 | 10 | 721 | 0.0013107 | 1.8179e-05 | 72.1
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | SWITCH, OH | 2 | 64 | 5208 | 0.0094679 | 0.00011635 | 81.375
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WL | NONE | 84 | 180 | 22859 | 0.042031 | 0.00033097 | 126.9944
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | POLE | 68 | 4815 | 1379415 | 2.5363 | 0.0088534 | 286.4829
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 4 | 945 | 94026 | 0.17093 | 0.001718 | 99.4984
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 22 | 694 | 175164 | 0.32208 | 0.0012761 | 252.3977
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 7 | 117 | 14181 | 0.025942 | 0.00021404 | 121.2051
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 1 | 97 | 0.00017745 | 1.8294e-06 | 97
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 4 | 1499 | 485730 | 0.88858 | 0.0027422 | 324.036
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 7 | 44 | 10958 | 0.019921 | 7.999e-05 | 249.0455
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | CF | CUTOUT | 2 | 2 | 511 | 0.00093481 | 3.6588e-06 | 255.5
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | CONN/CLAMP | 1 | 0 | 0 | 0 | 0
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 25 | 91 | 11920 | 0.021629 | 0.00016512 | 130.989
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 8 | 114 | 23469 | 0.042585 | 0.00020685 | 205.8684
AEP-SEP | 2022 | 550071 | PARTIAL POWER | A | FUSE | 1 | 1 | 74 | 0.00013453 | 1.8179e-06 | 74
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 5 | 970 | 0.0017601 | 9.0725e-06 | 194
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TIR | CONN/CLAMP | 2 | 8 | 905 | 0.001664 | 1.471e-05 | 113.125
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 853 | 26689 | 0.048427 | 0.0015478 | 31.2884
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | CUTOUT | 5 | 126 | 27511 | 0.049919 | 0.00022863 | 218.3413
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | CUTOUT | 15 | 142 | 22324 | 0.040274 | 0.00025618 | 157.2113
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 8 | 186 | 44804 | 0.08083 | 0.00033556 | 240.8817
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WU | INSULATOR | 3 | 696 | 166116 | 0.29969 | 0.0012556 | 238.6724
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | POLE | 2 | 65 | 4918 | 0.0088725 | 0.00011727 | 75.6615
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 8 | 130 | 15752 | 0.028418 | 0.00023453 | 121.1692
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 8 | 105 | 25589 | 0.046165 | 0.00018943 | 243.7048
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 79 | 10343 | 0.019018 | 0.00014526 | 130.9241
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | CUTOUT | 8 | 18 | 4519 | 0.0081527 | 3.2474e-05 | 251.0556
AEP-SEP | 2021 | 546634 | PARTIAL POWER | A | SPLICE, OH | 1 | 8 | 184 | 0.00033661 | 1.4635e-05 | 23
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 2 | 38 | 24296 | 0.044447 | 6.9516e-05 | 639.3684
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WT | FUSE | 1 | 2 | 300 | 0.00055161 | 3.6774e-06 | 150
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 8 | 1648 | 0.0029903 | 1.4516e-05 | 206
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 79 | 4156 | 379074 | 0.68388 | 0.0074978 | 91.2113
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 75 | 5811 | 0.010484 | 0.00013531 | 77.48
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 14 | 1663 | 173433 | 0.31289 | 0.0030002 | 104.2892
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 4 | 326 | 0.00058813 | 7.2163e-06 | 81.5
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WT | POLE | 1 | 5 | 705 | 0.0012719 | 9.0204e-06 | 141
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TIR | METERING | 1 | 1 | 77 | 0.00013891 | 1.8041e-06 | 77
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 2 | 4 | 1005 | 0.0018479 | 7.3548e-06 | 251.25
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 358 | 43318 | 0.079245 | 0.00065492 | 121
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 21 | 1575 | 0.002896 | 3.8613e-05 | 75
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | BREAKER | 1 | 150 | 22950 | 0.041643 | 0.00027218 | 153
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 49 | 17346 | 0.031894 | 9.0097e-05 | 354
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CO | CONN/CLAMP | 49 | 137 | 11966 | 0.021754 | 0.00024906 | 87.3431
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | NONE | 148 | 16846 | 2151591 | 3.9115 | 0.030625 | 127.7212
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | SWITCH, UG | 6 | 1402 | 40184 | 0.073052 | 0.0025488 | 28.6619
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 3 | 764 | 24799 | 0.045598 | 0.0014048 | 32.4594
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 18 | 1778 | 198034 | 0.36413 | 0.0032692 | 111.3802
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 1 | 813 | 0.0014873 | 1.8294e-06 | 813
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 6 | 1186 | 0.0021696 | 1.0976e-05 | 197.6667
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 1 | 84 | 0.00015367 | 1.8294e-06 | 84
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | JUMPER/RISER | 1 | 1 | 159 | 0.00029087 | 1.8294e-06 | 159
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 1 | 535 | 0.00096519 | 1.8041e-06 | 535
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 5 | 674 | 0.001233 | 9.1469e-06 | 134.8
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 4 | 584 | 0.0010738 | 7.3548e-06 | 146
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 10 | 1390 | 0.0025222 | 1.8145e-05 | 139
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 3 | 56 | 14861 | 0.026811 | 0.00010103 | 265.375
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | WL | JUMPER/RISER | 1 | 4 | 612 | 0.0011041 | 7.2163e-06 | 153
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 120 | 9480 | 0.017103 | 0.00021649 | 79
AEP-SEP | 2020 | 543859 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 1 | 46 | 8.4581e-05 | 1.8387e-06 | 46
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 31 | 6262 | 0.011297 | 5.5927e-05 | 202
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 13 | 1534 | 0.0027675 | 2.3453e-05 | 118
AEP-SEP | 2024 | 554297 | PARTIAL POWER | TIR | POLE | 1 | 5 | 940 | 0.0016958 | 9.0204e-06 | 188
AEP-SEP | 2024 | 554297 | PARTIAL POWER | U | CABLE TERMINATOR | 1 | 7 | 11508 | 0.020761 | 1.2629e-05 | 1644
AEP-SEP | 2025 | 554297 | PARTIAL POWER | CO | PEDESTAL | 1 | 1 | 165 | 0.00029767 | 1.8041e-06 | 165
AEP-SEP | 2025 | 554297 | PARTIAL POWER | TIR | OTHER EQUIPMENT | 1 | 5 | 295 | 0.00053221 | 9.0204e-06 | 59
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 3 | 1383 | 0.0024951 | 5.4123e-06 | 461
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | SPLICE, OH | 2 | 5 | 457 | 0.00082447 | 9.0204e-06 | 91.4
AEP-SEP | 2020 | 543859 | DISTRIBUTION STATION | WL | REGULATOR | 3 | 1617 | 423654 | 0.77898 | 0.0029732 | 262
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 215 | 14269 | 1722135 | 3.1308 | 0.02594 | 120.6907
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | ABI | NONE | 107 | 580 | 32106 | 0.059034 | 0.0010665 | 55.3552
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | U | ARRESTER | 3 | 3 | 195 | 0.00035855 | 5.5161e-06 | 65
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | SWITCH, OH | 3 | 93 | 16617 | 0.030399 | 0.00017013 | 178.6774
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 46 | 25279 | 0.046481 | 8.4581e-05 | 549.5435
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 3 | 1134 | 0.0020745 | 5.4881e-06 | 378
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | AF | NONE | 4 | 2749 | 113357 | 0.20569 | 0.0049881 | 41.2357
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 103 | 2675 | 884964 | 1.5966 | 0.0048259 | 330.8277
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 2 | 203 | 0.00037136 | 3.6588e-06 | 101.5
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 9 | 828 | 0.0015225 | 1.6548e-05 | 92
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 4 | 33 | 5105 | 0.0092631 | 5.9879e-05 | 154.697
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 6 | 1332 | 0.0024169 | 1.0887e-05 | 222
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | FO | POLE | 2 | 29 | 11009 | 0.019976 | 5.2621e-05 | 379.6207
AEP-SEP | 2024 | 554297 | PARTIAL POWER | WL | NONE | 41 | 121 | 8843 | 0.015954 | 0.00021829 | 73.0826
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 10 | 178 | 47869 | 0.08636 | 0.00032113 | 268.927
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 1 | 1 | 10 | 1.8041e-05 | 1.8041e-06 | 10
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 3 | 348 | 0.00063662 | 5.4881e-06 | 116
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 73 | 9490 | 0.017252 | 0.00013271 | 130
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 39 | 4336 | 0.0079727 | 7.171e-05 | 111.1795
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CF | CONN/CLAMP | 2 | 10 | 980 | 0.0018019 | 1.8387e-05 | 98
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CF | ARRESTER | 1 | 2 | 86 | 0.00015813 | 3.6774e-06 | 43
AEP-SEP | 2020 | 543859 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 3 | 8 | 896 | 0.0016475 | 1.471e-05 | 112
AEP-SEP | 2024 | 554297 | PARTIAL POWER | EQF | FUSE | 14 | 46 | 5923 | 0.010686 | 8.2988e-05 | 128.7609
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 2 | 95 | 12870 | 0.023353 | 0.00017238 | 135.4737
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERO | NONE | 4 | 13 | 1878 | 0.0033881 | 2.3453e-05 | 144.4615
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | ARRESTER | 11 | 117 | 58562 | 0.10565 | 0.00021108 | 500.5299
AEP-SEP | 2025 | 554297 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 4 | 344 | 0.00062061 | 7.2163e-06 | 86
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TR | NONE | 22 | 810 | 88274 | 0.15925 | 0.0014613 | 108.9802
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WFS | NONE | 1 | 1 | 48 | 8.7261e-05 | 1.8179e-06 | 48
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 6 | 293 | 0.0005286 | 1.0825e-05 | 48.8333
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 3 | 33 | 6.0369e-05 | 5.4881e-06 | 11
AEP-SEP | 2021 | 546634 | DISTRIBUTION STATION | WU | NONE | 5 | 2766 | 409706 | 0.74951 | 0.0050601 | 148.1222
AEP-SEP | 2022 | 550071 | DISTRIBUTION STATION | EQF | SWITCH, OH | 3 | 1310 | 173686 | 0.31575 | 0.0023815 | 132.5847
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | A | SWITCH, OH | 4 | 122 | 9877 | 0.017819 | 0.0002201 | 80.959
AEP-SEP | 2024 | 554297 | PARTIAL POWER | CO | CONN/CLAMP | 10 | 26 | 1941 | 0.0035017 | 4.6906e-05 | 74.6538
AEP-SEP | 2022 | 550071 | PARTIAL POWER | CF | CABLE TERMINATOR | 1 | 9 | 864 | 0.0015707 | 1.6362e-05 | 96
AEP-SEP | 2025 | 554297 | PARTIAL POWER | WL | ARRESTER | 1 | 2 | 160 | 0.00028865 | 3.6082e-06 | 80
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | REGULATOR | 4 | 936 | 136497 | 0.24625 | 0.0016886 | 145.8301
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 1 | 85 | 0.00015335 | 1.8041e-06 | 85
AEP-SEP | 2023 | 551114 | DISTRIBUTION SOURCE | A | NONE | 1 | 245 | 32095 | 0.058237 | 0.00044455 | 131
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 73 | 5216 | 0.009542 | 0.00013354 | 71.4521
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ABI | SWITCH, OH | 1 | 16 | 3456 | 0.0062828 | 2.9087e-05 | 216
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 3 | 681 | 0.0012458 | 5.4881e-06 | 227
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TIR | POLE | 12 | 587 | 239291 | 0.4317 | 0.001059 | 407.6508
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | FO | NONE | 18 | 339 | 25314 | 0.045669 | 0.00061159 | 74.6726
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | BREAKER | 1 | 31 | 1116 | 0.0020134 | 5.5927e-05 | 36
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 1 | 191 | 0.00034458 | 1.8041e-06 | 191
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WI | FUSE | 1 | 4 | 176 | 0.00031996 | 7.2718e-06 | 44
AEP-SEP | 2025 | 554297 | PARTIAL POWER | VIN | NONE | 5 | 48 | 5345 | 0.0096428 | 8.6596e-05 | 111.3542
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 563 | 239545 | 0.43822 | 0.0010299 | 425.4796
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TIR | SWITCH, OH | 1 | 3 | 96 | 0.00017562 | 5.4881e-06 | 32
AEP-SEP | 2020 | 543859 | PARTIAL POWER | VIN | CONDUCTOR UG | 1 | 1 | 227 | 0.00041739 | 1.8387e-06 | 227
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | CO | JUMPER/RISER | 2 | 480 | 74804 | 0.13495 | 0.00086596 | 155.8417
AEP-SEP | 2025 | 554297 | PARTIAL POWER | WL | TRANSFORMER, UG | 1 | 7 | 1246 | 0.0022479 | 1.2629e-05 | 178
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | CROSSARM | 1 | 32 | 4448 | 0.0080709 | 5.8064e-05 | 139
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | CROSSARM | 2 | 113 | 15432 | 0.028375 | 0.00020777 | 136.5664
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 5 | 870 | 0.0015916 | 9.1469e-06 | 174
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WI | NONE | 1 | 3 | 768 | 0.001405 | 5.4881e-06 | 256
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CF | CUTOUT | 1 | 2 | 224 | 0.00040978 | 3.6588e-06 | 112
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | STATIC WIRE | 1 | 1053 | 60021 | 0.10912 | 0.0019143 | 57
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 2 | 578 | 0.0010488 | 3.629e-06 | 289
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | VIN | SWITCH, OH | 2 | 12 | 471 | 0.00084972 | 2.1649e-05 | 39.25
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 2 | 408 | 0.00074032 | 3.629e-06 | 204
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WT | POLE | 1 | 348 | 84019 | 0.15158 | 0.00062782 | 241.4339
AEP-SEP | 2025 | 554297 | PARTIAL POWER | CO | CONN/CLAMP | 1 | 1 | 83 | 0.00014974 | 1.8041e-06 | 83
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | AF | NONE | 1 | 138 | 1242 | 0.0022536 | 0.0002504 | 9
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | ARRESTER | 1 | 2 | 96 | 0.00017319 | 3.6082e-06 | 48
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ABI | NONE | 83 | 3036 | 337150 | 0.61677 | 0.005554 | 111.0507
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | CROSSARM | 5 | 1251 | 231734 | 0.42128 | 0.0022743 | 185.239
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | NONE | 341 | 29258 | 2752860 | 5.036 | 0.053524 | 94.0891
AEP-SEP | 2021 | 546634 | PARTIAL POWER | A | NONE | 26 | 328 | 33041 | 0.060444 | 0.00060004 | 100.7348
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | FUSE | 46 | 560 | 68509 | 0.12533 | 0.0010245 | 122.3375
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | BREAKER | 2 | 644 | 7378 | 0.013413 | 0.0011708 | 11.4565
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | CUTOUT | 13 | 277 | 51133 | 0.093542 | 0.00050674 | 184.5957
AEP-SEP | 2022 | 550071 | DISTRIBUTION SOURCE | TIR | NONE | 4 | 921 | 50542 | 0.091883 | 0.0016743 | 54.8773
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 62 | 2957 | 448103 | 0.82393 | 0.0054371 | 151.5397
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 101 | 13251 | 0.02409 | 0.00018361 | 131.198
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ERF | POLE | 1 | 27 | 38556 | 0.070093 | 4.9085e-05 | 1428
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TR | POLE | 6 | 388 | 140891 | 0.25613 | 0.00070536 | 363.1211
AEP-SEP | 2021 | 546634 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 367 | 0.00067138 | 1.8294e-06 | 367
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 1 | 111 | 40404 | 0.073914 | 0.00020306 | 364
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WI | NONE | 57 | 2536 | 1212510 | 2.2001 | 0.0046016 | 478.1191
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 623 | 44981 | 0.081773 | 0.0011326 | 72.2006
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | SWITCH, UG | 1 | 1 | 201 | 0.00036541 | 1.8179e-06 | 201
AEP-SEP | 2023 | 551114 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 10 | 930 | 0.0016875 | 1.8145e-05 | 93
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | A | CONDUCTOR UG | 11 | 186 | 40560 | 0.073596 | 0.0003375 | 218.0645
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 11 | 630 | 71509 | 0.13148 | 0.0011584 | 113.5063
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 16 | 2195 | 106167 | 0.19153 | 0.00396 | 48.3677
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | INSULATOR | 3 | 166 | 33080 | 0.060825 | 0.00030523 | 199.2771
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 9 | 78 | 19347 | 0.035105 | 0.00014153 | 248.0385
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | OL | FUSE | 18 | 158 | 25095 | 0.045274 | 0.00028505 | 158.8291
AEP-SEP | 2024 | 554297 | PARTIAL POWER | A | NONE | 69 | 355 | 39235 | 0.070783 | 0.00064045 | 110.5211
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 1 | 229 | 0.00041552 | 1.8145e-06 | 229
AEP-SEP | 2024 | 554297 | PARTIAL POWER | OL | NONE | 15 | 41 | 4635 | 0.0083619 | 7.3968e-05 | 113.0488
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 3 | 1179 | 0.0021393 | 5.4435e-06 | 393
AEP-SEP | 2023 | 551114 | DISTRIBUTION STATION | WU | NONE | 3 | 2196 | 652883 | 1.1847 | 0.0039847 | 297.3056
AEP-SEP | 2022 | 550071 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 3 | 5 | 469 | 0.00085262 | 9.0897e-06 | 93.8
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 2 | 358 | 0.00064959 | 3.629e-06 | 179
AEP-SEP | 2025 | 554297 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 2 | 398 | 0.00071803 | 3.6082e-06 | 199
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | POLE | 21 | 1971 | 633970 | 1.1437 | 0.0035559 | 321.6489
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1475 | 185029 | 0.33849 | 0.0026983 | 125.4434
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VA | CIRCUIT SWITCHER | 1 | 1655 | 215150 | 0.3956 | 0.0030431 | 130
AEP-SEP | 2022 | 550071 | PARTIAL POWER | WI | NONE | 1 | 1 | 53 | 9.6351e-05 | 1.8179e-06 | 53
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | AF | CROSSARM | 2 | 53 | 2197 | 0.0040396 | 9.7452e-05 | 41.4528
AEP-SEP | 2020 | 543859 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 2 | 612 | 0.0011253 | 3.6774e-06 | 306
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 7 | 924 | 0.001699 | 1.2871e-05 | 132
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | POLE | 1 | 2 | 528 | 0.00095256 | 3.6082e-06 | 264
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 14 | 2386 | 275006 | 0.49613 | 0.0043046 | 115.2582
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | O | JUMPER/RISER | 3 | 61 | 4719 | 0.0085135 | 0.00011005 | 77.3607
AEP-SEP | 2023 | 551114 | PARTIAL POWER | WL | ARRESTER | 7 | 15 | 896 | 0.0016258 | 2.7218e-05 | 59.7333
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 7 | 469 | 30637 | 0.055272 | 0.00084612 | 65.3241
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 687 | 57013 | 0.10365 | 0.0012489 | 82.9884
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 37 | 8066 | 0.014664 | 6.7264e-05 | 218
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | CROSSARM | 18 | 4212 | 1051058 | 1.8962 | 0.0075988 | 249.5389
AEP-SEP | 2024 | 554297 | DISTRIBUTION STATION | O | NONE | 3 | 1681 | 136462 | 0.24619 | 0.0030327 | 81.1791
AEP-SEP | 2020 | 543859 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 7 | 1248 | 0.0022947 | 1.2871e-05 | 178.2857
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 34 | 8364 | 0.015177 | 6.1693e-05 | 246
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | TRANSFORMER, OH | 12 | 52 | 9002 | 0.01624 | 9.3813e-05 | 173.1154
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 73 | 17301 | 0.03165 | 0.00013354 | 237
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 4 | 412 | 0.00074328 | 7.2163e-06 | 103
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WH | POLE | 2 | 2 | 428 | 0.00078697 | 3.6774e-06 | 214
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TOR | CUTOUT | 5 | 177 | 39015 | 0.070386 | 0.00031932 | 220.4237
AEP-SEP | 2020 | 543859 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 6 | 351 | 0.00064539 | 1.1032e-05 | 58.5
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 69 | 8625 | 0.015778 | 0.00012623 | 125
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 81 | 0.00014818 | 1.8294e-06 | 81
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WFS | POLE | 1 | 554 | 57484 | 0.10516 | 0.0010135 | 103.7617
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WFS | NONE | 1 | 25 | 2675 | 0.0048936 | 4.5734e-05 | 107
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | TIR | BREAKER | 3 | 1102 | 65133 | 0.11751 | 0.0019881 | 59.1044
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | FO | FUSE | 3 | 55 | 4409 | 0.0079542 | 9.9225e-05 | 80.1636
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 3 | 1758 | 0.0031716 | 5.4123e-06 | 586
AEP-SEP | 2020 | 543859 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 1 | 667 | 0.0012264 | 1.8387e-06 | 667
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 26 | 1066 | 0.0019501 | 4.7564e-05 | 41
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | OL | ARRESTER | 2 | 121 | 10517 | 0.019119 | 0.00021997 | 86.9174
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 3 | 1095 | 0.0020032 | 5.4881e-06 | 365
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 15 | 2100 | 0.0038105 | 2.7218e-05 | 140
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 298 | 187144 | 0.3441 | 0.00054794 | 628
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 1 | 60 | 3720 | 0.00684 | 0.00011032 | 62
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 3 | 675 | 0.0012271 | 5.4538e-06 | 225
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | VIN | CONDUCTOR UG | 1 | 3 | 654 | 0.0012025 | 5.5161e-06 | 218
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | OL | TRANSFORMER, POWER - LTC | 1 | 22 | 6448 | 0.0117 | 3.9919e-05 | 293.0909
AEP-SEP | 2025 | 554297 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 8 | 548 | 0.00098864 | 1.4433e-05 | 68.5
AEP-SEP | 2025 | 554297 | PARTIAL POWER | ERF | SPLICE, OH | 1 | 7 | 466 | 0.0008407 | 1.2629e-05 | 66.5714
AEP-SEP | 2025 | 554297 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 882 | 0.0015912 | 1.8041e-06 | 882
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 326 | 1871 | 513018 | 0.93264 | 0.0034014 | 274.1945
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 7 | 931 | 116900 | 0.21252 | 0.0016925 | 125.5639
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 148 | 1059 | 341858 | 0.6203 | 0.0019216 | 322.8121
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | UB | NONE | 4 | 351 | 12508 | 0.022882 | 0.00064211 | 35.6353
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 31 | 3523 | 0.0064046 | 5.6356e-05 | 113.6452
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | SPLICE, OH | 3 | 11 | 2079 | 0.0037795 | 1.9997e-05 | 189
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WL | JUMPER/RISER | 11 | 825 | 182904 | 0.3346 | 0.0015092 | 221.7018
AEP-SEP | 2022 | 550071 | PARTIAL POWER | FO | PEDESTAL | 1 | 1 | 1058 | 0.0019234 | 1.8179e-06 | 1058
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | FUSE | 102 | 1780 | 614199 | 1.1145 | 0.0032298 | 345.0556
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | FO | FUSE | 5 | 85 | 7029 | 0.012754 | 0.00015423 | 82.6941
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | POLE | 141 | 9343 | 1818365 | 3.2994 | 0.016953 | 194.6232
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | METERING | 22 | 50 | 6665 | 0.012094 | 9.0725e-05 | 133.3
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | ARRESTER | 13 | 130 | 8238 | 0.014862 | 0.00023453 | 63.3692
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | FO | TRANSFORMER, UG | 1 | 6 | 1164 | 0.0021294 | 1.0976e-05 | 194
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 13 | 3461 | 0.00628 | 2.3589e-05 | 266.2308
AEP-SEP | 2022 | 550071 | PARTIAL POWER | O | CABLE TERMINATOR | 1 | 1 | 52 | 9.4533e-05 | 1.8179e-06 | 52
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | INSULATOR | 44 | 5675 | 777319 | 1.4024 | 0.010238 | 136.9725
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | SWITCH, OH | 68 | 9140 | 605100 | 1.0917 | 0.016489 | 66.2035
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 1 | 85 | 0.00015629 | 1.8387e-06 | 85
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 2 | 4 | 332 | 0.00061045 | 7.3548e-06 | 83
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 10 | 720 | 0.0013064 | 1.8145e-05 | 72
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | CONN/CLAMP | 2 | 5 | 2002 | 0.0036624 | 9.1469e-06 | 400.4
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | TIR | CUTOUT | 12 | 187 | 30817 | 0.055918 | 0.00033931 | 164.7968
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TR | NONE | 2 | 3 | 545 | 0.00098891 | 5.4435e-06 | 181.6667
AEP-SEP | 2024 | 554297 | PARTIAL POWER | A | CONDUCTOR UG | 4 | 8 | 2052 | 0.003702 | 1.4433e-05 | 256.5
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 4 | 14 | 2535 | 0.0045998 | 2.5403e-05 | 181.0714
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | ERF | FUSE | 1 | 3 | 357 | 0.00064406 | 5.4123e-06 | 119
AEP-SEP | 2025 | 554297 | DISTRIBUTION LINE | TOR | FUSE | 15 | 197 | 32218 | 0.058124 | 0.00035541 | 163.5431
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 1309 | 226116 | 0.41107 | 0.0023797 | 172.7395
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | U | NONE | 319 | 16258 | 1229630 | 2.2609 | 0.029894 | 75.6323
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 246 | 1288 | 301402 | 0.55138 | 0.0023562 | 234.0078
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WL | CONN/CLAMP | 9 | 511 | 138099 | 0.25106 | 0.00092897 | 270.2524
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | FUSE | 30 | 778 | 114749 | 0.20861 | 0.0014144 | 147.4923
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 7 | 84 | 19933 | 0.036465 | 0.00015367 | 237.2976
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | TRANSFORMER, OH | 23 | 86 | 25629 | 0.046592 | 0.00015634 | 298.0116
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CO | CONN/CLAMP | 45 | 838 | 109591 | 0.19923 | 0.0015234 | 130.7768
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 77 | 10545 | 1166114 | 2.1199 | 0.01917 | 110.5845
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | POLE | 62 | 6991 | 1499464 | 2.7259 | 0.012709 | 214.4849
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | SWITCH, OH | 75 | 5609 | 664631 | 1.2083 | 0.010197 | 118.4937
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TOR | CROSSARM | 19 | 2411 | 451733 | 0.82639 | 0.0044106 | 187.3633
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | CUTOUT | 6 | 52 | 4417 | 0.0081216 | 9.5613e-05 | 84.9423
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 3 | 16 | 3421 | 0.0062192 | 2.9087e-05 | 213.8125
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 42 | 5393 | 0.0098042 | 7.6354e-05 | 128.4048
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | NONE | 111 | 10955 | 1337173 | 2.4462 | 0.020041 | 122.0605
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 3 | 102 | 0.00018543 | 5.4538e-06 | 34
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TR | NONE | 116 | 8136 | 1198041 | 2.2029 | 0.01496 | 147.2518
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | FO | SWITCH, OH | 1 | 151 | 25972 | 0.047216 | 0.00027451 | 172
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | CF | NONE | 7 | 97 | 7596 | 0.013809 | 0.00017634 | 78.3093
AEP-SEP | 2021 | 546634 | PARTIAL POWER | TIR | NONE | 64 | 305 | 44205 | 0.080868 | 0.00055796 | 144.9344
AEP-SEP | 2021 | 546634 | PARTIAL POWER | O | NONE | 24 | 90 | 8481 | 0.015515 | 0.00016464 | 94.2333
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | POLE | 37 | 2473 | 769783 | 1.3994 | 0.0044958 | 311.275
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | EQF | FUSE | 100 | 1134 | 121227 | 0.22038 | 0.0020616 | 106.9021
AEP-SEP | 2022 | 550071 | PARTIAL POWER | EQF | TRANSFORMER, UG | 5 | 21 | 8194 | 0.014896 | 3.8177e-05 | 390.1905
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | WW | NONE | 108 | 14281 | 2125792 | 3.8646 | 0.025962 | 148.8546
AEP-SEP | 2021 | 546634 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 2 | 404 | 0.00073907 | 3.6588e-06 | 202
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 197 | 8648 | 2597035 | 4.7213 | 0.015722 | 300.3047
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | O | NONE | 242 | 7603 | 498172 | 0.90565 | 0.013822 | 65.5231
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | U | NONE | 397 | 16721 | 1685667 | 3.0837 | 0.030589 | 100.8114
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | A | FUSE | 29 | 241 | 26839 | 0.048792 | 0.00043813 | 111.3651
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WT | NONE | 16 | 991 | 334957 | 0.61589 | 0.0018222 | 337.999
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 37 | 1820 | 627999 | 1.1547 | 0.0033465 | 345.0544
AEP-SEP | 2021 | 546634 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 209 | 0.00038234 | 1.8294e-06 | 209
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WW | NONE | 39 | 785 | 100567 | 0.18398 | 0.0014361 | 128.1108
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 5 | 8 | 725 | 0.0013331 | 1.471e-05 | 90.625
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 10 | 1275 | 165123 | 0.30207 | 0.0023325 | 129.5082
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | WU | POLE | 13 | 3907 | 697730 | 1.2764 | 0.0071474 | 178.5846
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | OL | NONE | 68 | 3018 | 256442 | 0.47152 | 0.0055492 | 84.9708
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | WL | ARRESTER | 69 | 3792 | 313220 | 0.57592 | 0.0069724 | 82.6002
AEP-SEP | 2022 | 550071 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 6 | 348 | 0.00063265 | 1.0908e-05 | 58
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | ERO | NONE | 7 | 15 | 1797 | 0.0032669 | 2.7269e-05 | 119.8
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 68 | 5934 | 283400 | 0.51845 | 0.010856 | 47.7587
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | O | POLE | 8 | 315 | 68227 | 0.12481 | 0.00057625 | 216.5937
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WL | NONE | 2388 | 63228 | 7409625 | 13.4448 | 0.11473 | 117.189
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 196 | 7372 | 1937733 | 3.516 | 0.013377 | 262.8504
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 1 | 101 | 0.00018477 | 1.8294e-06 | 101
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VA | CROSSARM | 2 | 56 | 8369 | 0.015214 | 0.00010181 | 149.4464
AEP-SEP | 2023 | 551114 | PARTIAL POWER | EQF | TRANSFORMER, OH | 39 | 116 | 27866 | 0.050563 | 0.00021048 | 240.2241
AEP-SEP | 2023 | 551114 | PARTIAL POWER | VIN | NONE | 25 | 80 | 7234 | 0.013126 | 0.00014516 | 90.425
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 9 | 217 | 36538 | 0.065918 | 0.00039149 | 168.3779
AEP-SEP | 2023 | 551114 | DISTRIBUTION LINE | WU | FUSE | 30 | 398 | 64623 | 0.11726 | 0.00072217 | 162.3693
AEP-SEP | 2021 | 546634 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 92 | 8556 | 0.015652 | 0.0001683 | 93
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 12 | 420 | 53526 | 0.098419 | 0.00077226 | 127.4429
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | EQF | ARRESTER | 173 | 5227 | 682838 | 1.2319 | 0.00943 | 130.6367
AEP-SEP | 2022 | 550071 | DISTRIBUTION SOURCE | EQF | POLE | 1 | 2 | 810 | 0.0014725 | 3.6359e-06 | 405
AEP-SEP | 2023 | 551114 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 7 | 625 | 0.0011341 | 1.2702e-05 | 89.2857
AEP-SEP | 2024 | 554297 | PARTIAL POWER | VIN | NONE | 27 | 87 | 10950 | 0.019755 | 0.00015696 | 125.8621
AEP-SEP | 2024 | 554297 | DISTRIBUTION LINE | U | FUSE | 64 | 1109 | 125597 | 0.22659 | 0.0020007 | 113.2525
AEP-SEP | 2020 | 543859 | DISTRIBUTION LINE | TR | POLE | 5 | 81 | 21162 | 0.038911 | 0.00014894 | 261.2593
AEP-SEP | 2024 | 554297 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 629 | 46546 | 0.083973 | 0.0011348 | 74
AEP-SEP | 2023 | 551114 | PARTIAL POWER | ABI | NONE | 5 | 8 | 1068 | 0.0019379 | 1.4516e-05 | 133.5
AEP-SEP | 2022 | 550071 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 6 | 900 | 0.0016362 | 1.0908e-05 | 150
AEP-SEP | 2021 | 546634 | PARTIAL POWER | WW | NONE | 3 | 11 | 1162 | 0.0021257 | 2.0123e-05 | 105.6364
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 107 | 814 | 132144 | 0.12113 | 0.00074616 | 162.3391
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 2 | 207 | 0.00018975 | 1.8333e-06 | 103.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 14 | 48 | 7851 | 0.0073727 | 4.5076e-05 | 163.5625
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AB | NONE | 6 | 3693 | 982521 | 0.91005 | 0.0034206 | 266.0496
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | INSULATOR | 14 | 5642 | 614012 | 0.56872 | 0.0052259 | 108.8288
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 474 | 43484 | 0.040277 | 0.00043904 | 91.7384
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | SPLICE, OH | 17 | 1032 | 186225 | 0.17249 | 0.00095588 | 180.4506
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | CABLE TERMINATOR | 6 | 70 | 14801 | 0.013568 | 6.4166e-05 | 211.4429
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WL | CONN/CLAMP | 2 | 2 | 380 | 0.00034833 | 1.8333e-06 | 190
AEP-TX | 2022 | 1090914 | PARTIAL POWER | A | NONE | 53 | 132 | 17856 | 0.016368 | 0.000121 | 135.2727
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 112 | 11813 | 1449225 | 1.3285 | 0.010829 | 122.6805
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | POLE | 376 | 17313 | 3897096 | 3.5723 | 0.01587 | 225.0965
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | POLE | 74 | 22236 | 1849209 | 1.6951 | 0.020383 | 83.1628
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | NONE | 1265 | 45574 | 4760762 | 4.4096 | 0.042213 | 104.4622
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | SPLICE, OH | 7 | 7 | 1957 | 0.0017939 | 6.4166e-06 | 279.5714
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 90 | 15799 | 1872876 | 1.7347 | 0.014634 | 118.544
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERF | NONE | 23 | 4523 | 90964 | 0.083383 | 0.0041461 | 20.1114
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 262 | 1257 | 445828 | 0.41294 | 0.0011643 | 354.6762
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | TRANSFORMER, UG | 10 | 88 | 29512 | 0.027053 | 8.0666e-05 | 335.3636
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | CONDUCTOR UG | 68 | 201 | 52052 | 0.047714 | 0.00018425 | 258.9652
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | METERING | 1 | 1 | 112 | 0.00010374 | 9.2624e-07 | 112
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | REGULATOR | 9 | 5190 | 623123 | 0.57716 | 0.0048072 | 120.0622
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 441 | 11219 | 2356902 | 2.2133 | 0.010536 | 210.0813
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | CROSSARM | 14 | 496 | 114817 | 0.10635 | 0.00045942 | 231.4859
AEP-TX | 2022 | 1090914 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 335 | 0.00030708 | 9.1666e-07 | 335
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | BREAKER | 3 | 2233 | 187791 | 0.17214 | 0.0020469 | 84.0981
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 18 | 343 | 52347 | 0.048486 | 0.0003177 | 152.6152
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | CONN/CLAMP | 950 | 1966 | 259798 | 0.24064 | 0.001821 | 132.1455
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | CUTOUT | 10 | 19 | 2476 | 0.0022697 | 1.7417e-05 | 130.3158
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | JUMPER/RISER | 4 | 479 | 46257 | 0.042402 | 0.00043908 | 96.5699
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AO | INSULATOR | 2 | 398 | 157629 | 0.14449 | 0.00036483 | 396.0528
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 12 | 202 | 31122 | 0.028826 | 0.0001871 | 154.0693
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | POLE | 66 | 8246 | 1868466 | 1.7546 | 0.0077436 | 226.5906
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 86 | 11404 | 1256372 | 1.1798 | 0.010709 | 110.1694
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 9 | 1685 | 0.0015607 | 8.3362e-06 | 187.2222
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | TRANSFORMER, OH | 52 | 143 | 30975 | 0.029088 | 0.00013429 | 216.6084
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | ARRESTER | 5 | 213 | 16604 | 0.015592 | 0.00020002 | 77.9531
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | POLE HARDWARE | 18 | 352 | 46912 | 0.044054 | 0.00033056 | 133.2727
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 45 | 5220 | 0.004835 | 4.1681e-05 | 116
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | NONE | 45 | 14017 | 1505405 | 1.3799 | 0.012849 | 107.3985
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TIR | CONN/CLAMP | 44 | 196 | 29591 | 0.027125 | 0.00017967 | 150.9745
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | ARRESTER | 27 | 1239 | 118581 | 0.10983 | 0.0011476 | 95.707
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | POLE | 286 | 66844 | 9550489 | 8.8461 | 0.061914 | 142.8773
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 123 | 26032 | 4752442 | 4.3564 | 0.023863 | 182.5615
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 15 | 133 | 22811 | 0.02091 | 0.00012192 | 171.5113
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | METERING | 143 | 157 | 12721 | 0.011783 | 0.00014542 | 81.0255
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | CONN/CLAMP | 88 | 207 | 26349 | 0.024406 | 0.00019173 | 127.2899
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | INSULATOR | 10 | 117 | 26320 | 0.024127 | 0.00010725 | 224.9573
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | JUMPER/RISER | 2 | 2 | 363 | 0.00033275 | 1.8333e-06 | 181.5
AEP-TX | 2022 | 1090914 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 6 | 22 | 5093 | 0.0046686 | 2.0167e-05 | 231.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 2089 | 17487 | 2006341 | 1.8841 | 0.016422 | 114.7333
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 14 | 182 | 22218 | 0.020864 | 0.00017091 | 122.0769
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 7 | 3352 | 427512 | 0.40147 | 0.0031478 | 127.5394
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 82 | 454 | 59437 | 0.055816 | 0.00042634 | 130.9185
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | NONE | 44 | 1086 | 786436 | 0.73852 | 0.0010198 | 724.1584
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | PEDESTAL | 5 | 19 | 5886 | 0.0053955 | 1.7417e-05 | 309.7895
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | CUTOUT | 11 | 393 | 57204 | 0.052437 | 0.00036025 | 145.5573
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | NONE | 9 | 11 | 921 | 0.00085307 | 1.0189e-05 | 83.7273
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | CF | CAPACITOR | 1 | 1451 | 31922 | 0.029567 | 0.001344 | 22
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | FO | CONN/CLAMP | 2 | 41 | 4236 | 0.0039236 | 3.7976e-05 | 103.3171
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WFS | NONE | 1 | 41 | 70159 | 0.064312 | 3.7583e-05 | 1711.1951
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | BREAKER | 45 | 38792 | 4148030 | 3.773 | 0.035285 | 106.93
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WL | TRANSFORMER, OH | 3 | 10 | 1283 | 0.001167 | 9.0959e-06 | 128.3
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 9 | 64 | 10205 | 0.0092824 | 5.8214e-05 | 159.4531
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | FO | ARRESTER | 2 | 4 | 422 | 0.00038683 | 3.6667e-06 | 105.5
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 4 | 29 | 11790 | 0.010807 | 2.6583e-05 | 406.5517
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 24 | 116 | 19378 | 0.017626 | 0.00010551 | 167.0517
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | NONE | 72 | 6977 | 384031 | 0.34931 | 0.0063462 | 55.0424
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | REGULATOR | 15 | 14457 | 1364703 | 1.2413 | 0.01315 | 94.3974
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TR | CONN/CLAMP | 4 | 12 | 1870 | 0.0017561 | 1.1269e-05 | 155.8333
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 38 | 4482 | 0.0042089 | 3.5685e-05 | 117.9474
AEP-TX | 2020 | 1064875 | PARTIAL POWER | UB | NONE | 2 | 2 | 576 | 0.00054091 | 1.8782e-06 | 288
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | ABI | RECLOSER, LINE/OCR/BR | 1 | 1283 | 198290 | 0.18177 | 0.0011761 | 154.5518
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 1 | 181 | 0.00016464 | 9.0959e-07 | 181
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | CONN/CLAMP | 8 | 20 | 2572 | 0.0023395 | 1.8192e-05 | 128.6
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | ARRESTER | 15 | 111 | 14951 | 0.013599 | 0.00010096 | 134.6937
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WL | CUTOUT | 2 | 6 | 1337 | 0.0012161 | 5.4576e-06 | 222.8333
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 2097 | 44415 | 0.039931 | 0.0018853 | 21.1803
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | CABLE TERMINATOR | 3 | 32 | 4418 | 0.0040186 | 2.9107e-05 | 138.0625
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 6 | 5776 | 562449 | 0.5116 | 0.0052538 | 97.3769
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WH | NONE | 2 | 2 | 339 | 0.00030835 | 1.8192e-06 | 169.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 32 | 73 | 13373 | 0.012023 | 6.5631e-05 | 183.1918
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | CONDUCTOR UG | 47 | 78 | 12970 | 0.011661 | 7.0126e-05 | 166.2821
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 3 | 237 | 0.00021557 | 2.7288e-06 | 79
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | POLE HARDWARE | 1 | 67 | 16750 | 0.015059 | 6.0236e-05 | 250
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 635 | 91753 | 0.082491 | 0.0005709 | 144.4929
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 5 | 12 | 3749 | 0.0034101 | 1.0915e-05 | 312.4167
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | POLE HARDWARE | 2 | 7 | 1288 | 0.0011807 | 6.4166e-06 | 184
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WH | CONN/CLAMP | 1 | 1 | 43 | 3.9828e-05 | 9.2624e-07 | 43
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | CONN/CLAMP | 4 | 9 | 480 | 0.00045076 | 8.4517e-06 | 53.3333
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WL | CONN/CLAMP | 7 | 7 | 1016 | 0.0009541 | 6.5735e-06 | 145.1429
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 10 | 35 | 2627 | 0.002467 | 3.2868e-05 | 75.0571
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | RECLOSER, LINE/OCR/BR | 1 | 26 | 1586 | 0.0014259 | 2.3375e-05 | 61
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | SPLICE, UG | 1 | 1 | 114 | 0.00010559 | 9.2624e-07 | 114
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | SPLICE, OH | 6 | 23 | 3330 | 0.0029938 | 2.0678e-05 | 144.7826
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 5 | 49 | 6724 | 0.0060452 | 4.4054e-05 | 137.2245
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | CUTOUT | 11 | 55 | 7496 | 0.0067393 | 4.9448e-05 | 136.2909
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | FO | NONE | 1 | 1 | 16 | 1.4385e-05 | 8.9905e-07 | 16
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 1 | 115 | 0.00010339 | 8.9905e-07 | 115
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | UB | CONN/CLAMP | 2 | 3 | 283 | 0.00025443 | 2.6972e-06 | 94.3333
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | SPLICE, OH | 5 | 17 | 1792 | 0.0016828 | 1.5964e-05 | 105.4118
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 5 | 174 | 19035 | 0.017113 | 0.00015644 | 109.3966
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 54 | 9666 | 0.0086902 | 4.8549e-05 | 179
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 15 | 810 | 0.00072823 | 1.3486e-05 | 54
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | INSULATOR | 2 | 2 | 177 | 0.00015913 | 1.7981e-06 | 88.5
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | TRANSFORMER, STATION SERVICE | 1 | 3 | 57 | 5.1246e-05 | 2.6972e-06 | 19
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 2 | 218 | 0.00019599 | 1.7981e-06 | 109
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 1 | 68 | 6.2333e-05 | 9.1666e-07 | 68
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | WL | ARRESTER | 3 | 1671 | 62818 | 0.058185 | 0.0015477 | 37.5931
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AO | REGULATOR | 2 | 1122 | 113938 | 0.10444 | 0.0010285 | 101.549
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 7 | 203 | 0.00018465 | 6.3672e-06 | 29
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 2263 | 72279 | 0.064983 | 0.0020346 | 31.9395
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 4 | 820 | 0.00073722 | 3.5962e-06 | 205
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CF | CUTOUT | 1 | 1 | 104 | 9.3501e-05 | 8.9905e-07 | 104
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 3 | 537 | 0.00048279 | 2.6972e-06 | 179
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 112 | 18923 | 1785553 | 1.6367 | 0.017346 | 94.3589
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 350 | 5010 | 1367922 | 1.2539 | 0.0045925 | 273.0383
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 10 | 64 | 13798 | 0.012648 | 5.8666e-05 | 215.5938
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | POLE | 294 | 58926 | 7230234 | 6.6277 | 0.054015 | 122.7002
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 107 | 109 | 14950 | 0.013704 | 9.9916e-05 | 137.156
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | PEDESTAL | 24 | 143 | 19691 | 0.01805 | 0.00013108 | 137.6993
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WH | NONE | 14 | 1356 | 1044918 | 0.96785 | 0.001256 | 770.5885
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | CUTOUT | 90 | 1769 | 200565 | 0.18577 | 0.0016385 | 113.3776
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 22 | 147 | 31009 | 0.028425 | 0.00013475 | 210.9456
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | NONE | 171 | 31345 | 3089329 | 2.8615 | 0.029033 | 98.5589
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | RELAY | 6 | 5064 | 408614 | 0.37456 | 0.004642 | 80.69
AEP-TX | 2021 | 1079632 | PARTIAL POWER | OL | CUTOUT | 1 | 1 | 67 | 6.2058e-05 | 9.2624e-07 | 67
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | POLE | 13 | 388 | 122166 | 0.11198 | 0.00035567 | 314.8608
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | CAPACITOR | 3 | 1141 | 40867 | 0.037461 | 0.0010459 | 35.8168
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 129 | 368 | 63379 | 0.058704 | 0.00034086 | 172.2255
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | CONN/CLAMP | 1491 | 3135 | 351832 | 0.3304 | 0.002944 | 112.2271
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | CROSSARM | 6 | 158 | 32603 | 0.029886 | 0.00014483 | 206.3481
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 287 | 22300 | 2402779 | 2.2564 | 0.020941 | 107.7479
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1093 | 111878 | 13037334 | 12.2431 | 0.10506 | 116.5317
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | METERING | 20 | 21 | 2867 | 0.0026555 | 1.9451e-05 | 136.5238
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 9 | 1386 | 0.0013016 | 8.4517e-06 | 154
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | POLE | 9 | 35 | 5472 | 0.0051386 | 3.2868e-05 | 156.3429
AEP-TX | 2021 | 1079632 | PARTIAL POWER | VIN | NONE | 13 | 31 | 2735 | 0.0025333 | 2.8713e-05 | 88.2258
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 300 | 0.00027787 | 1.8525e-06 | 150
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 5 | 257 | 45992 | 0.0426 | 0.00023804 | 178.9572
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | CROSSARM | 4 | 1416 | 17126 | 0.015863 | 0.0013116 | 12.0946
AEP-TX | 2021 | 1079632 | PARTIAL POWER | OL | TRANSFORMER, OH | 1 | 6 | 1332 | 0.0012338 | 5.5574e-06 | 222
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 83 | 17596 | 0.01613 | 7.6083e-05 | 212
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | REGULATOR | 3 | 2287 | 169576 | 0.15924 | 0.0021477 | 74.1478
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 9 | 769 | 0.00071228 | 8.3362e-06 | 85.4444
AEP-TX | 2021 | 1079632 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 12 | 54 | 9274 | 0.00859 | 5.0017e-05 | 171.7407
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | POLE | 19 | 85 | 29786 | 0.027093 | 7.7316e-05 | 350.4235
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 6 | 1455 | 53278 | 0.050032 | 0.0013664 | 36.6172
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | CROSSARM | 1 | 1 | 99 | 9.075e-05 | 9.1666e-07 | 99
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 79 | 376 | 55534 | 0.050513 | 0.00034201 | 147.6968
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | NONE | 38 | 13853 | 1937566 | 1.7624 | 0.012601 | 139.8662
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 8 | 184 | 73508 | 0.066862 | 0.00016737 | 399.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 149 | 57365 | 0.05387 | 0.00013992 | 385
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 9 | 258 | 143617 | 0.13487 | 0.00024228 | 556.655
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 47 | 5455 | 0.0050526 | 4.3533e-05 | 116.0638
AEP-TX | 2024 | 1112283 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 15 | 43 | 5449 | 0.0048989 | 3.8659e-05 | 126.7209
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | SPLICE, UG | 2 | 11 | 997 | 0.00091391 | 1.0083e-05 | 90.6364
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | NONE | 303 | 303 | 38932 | 0.035002 | 0.00027241 | 128.4884
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | METERING | 5 | 35 | 856 | 0.00077861 | 3.1836e-05 | 24.4571
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | POLE HARDWARE | 3 | 1986 | 573770 | 0.5219 | 0.0018065 | 288.9074
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | CONDUCTOR UG | 4 | 7 | 650 | 0.0006104 | 6.5735e-06 | 92.8571
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 2 | 21 | 2471 | 0.0022651 | 1.925e-05 | 117.6667
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | METERING | 3 | 3 | 8547 | 0.0076842 | 2.6972e-06 | 2849
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | JUMPER/RISER | 1 | 57 | 4731 | 0.004382 | 5.2796e-05 | 83
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | AO | NONE | 15 | 10499 | 1137190 | 1.0224 | 0.0094391 | 108.3141
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 24 | 265 | 149082 | 0.14 | 0.00024886 | 562.5736
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 25 | 2800 | 0.0026294 | 2.3477e-05 | 112
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 20 | 5354 | 0.0049078 | 1.8333e-05 | 267.7
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 392 | 70959 | 0.065725 | 0.00036309 | 181.0179
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 4 | 29 | 7568 | 0.006804 | 2.6073e-05 | 260.9655
AEP-TX | 2025 | 1112283 | PARTIAL POWER | OL | CONN/CLAMP | 14 | 41 | 4483 | 0.0040304 | 3.6861e-05 | 109.3415
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TOR | CONN/CLAMP | 38 | 38 | 3497 | 0.003144 | 3.4164e-05 | 92.0263
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | NONE | 39 | 3318 | 282498 | 0.25398 | 0.0029831 | 85.141
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | INSULATOR | 33 | 2410 | 130393 | 0.11723 | 0.0021667 | 54.105
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | POLE HARDWARE | 9 | 3071 | 362385 | 0.3258 | 0.002761 | 118.0023
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AF | NONE | 4 | 746 | 113458 | 0.10509 | 0.00069098 | 152.0885
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | CUTOUT | 5 | 5 | 477 | 0.00044182 | 4.6312e-06 | 95.4
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | ARRESTER | 5 | 17 | 2166 | 0.0020062 | 1.5746e-05 | 127.4118
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | UB | TRANSFORMER, OH | 1 | 1 | 6 | 5.5574e-06 | 9.2624e-07 | 6
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | JUMPER/RISER | 22 | 312 | 31753 | 0.028882 | 0.00028379 | 101.7724
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 40 | 3140 | 258066 | 0.23474 | 0.0028561 | 82.1866
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 29 | 2551 | 537823 | 0.50506 | 0.0023956 | 210.8283
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | REGULATOR | 4 | 466 | 66148 | 0.060168 | 0.00042387 | 141.9485
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | CUTOUT | 11 | 12 | 1975 | 0.0018547 | 1.1269e-05 | 164.5833
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | ARRESTER | 6 | 20 | 2348 | 0.002205 | 1.8782e-05 | 117.4
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 210 | 690 | 71670 | 0.064435 | 0.00062035 | 103.8696
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | CONN/CLAMP | 12 | 1015 | 293729 | 0.26717 | 0.00092324 | 289.3882
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 193 | 400 | 46281 | 0.041609 | 0.00035962 | 115.7025
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | CUTOUT | 48 | 465 | 48723 | 0.043804 | 0.00041806 | 104.7806
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 4 | 86 | 22874 | 0.021187 | 7.9657e-05 | 265.9767
AEP-TX | 2023 | 1099391 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 88 | 8.0044e-05 | 9.0959e-07 | 88
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | UB | NONE | 4 | 22 | 791 | 0.00074281 | 2.066e-05 | 35.9545
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | FUSE | 3 | 3 | 241 | 0.00022632 | 2.8172e-06 | 80.3333
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | U | NONE | 27 | 19792 | 2134058 | 1.9411 | 0.018003 | 107.8243
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 63 | 4682 | 0.0043968 | 5.9162e-05 | 74.3175
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERO | METERING | 2 | 2 | 162 | 0.00015005 | 1.8525e-06 | 81
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | CONN/CLAMP | 3 | 225 | 15347 | 0.01396 | 0.00020466 | 68.2089
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | CAPACITOR | 8 | 2819 | 165834 | 0.1536 | 0.0026111 | 58.8272
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | CABLE TERMINATOR | 2 | 2 | 887 | 0.00082158 | 1.8525e-06 | 443.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | CROSSARM | 53 | 13532 | 1909869 | 1.7171 | 0.012166 | 141.1372
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | POLE | 18 | 1274 | 223566 | 0.20995 | 0.0011964 | 175.4835
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | TRANSFORMER, OH | 2 | 991 | 70067 | 0.065798 | 0.00093063 | 70.7033
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | CROSSARM | 16 | 174 | 15081 | 0.013559 | 0.00015644 | 86.6724
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 2 | 1146 | 126903 | 0.11543 | 0.0010424 | 110.7356
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | RECLOSER, LINE/OCR/BR | 2 | 106 | 14424 | 0.01312 | 9.6417e-05 | 136.0755
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | CONN/CLAMP | 6 | 8 | 12918 | 0.012131 | 7.5126e-06 | 1614.75
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | SWITCH, UG | 1 | 13 | 1690 | 0.0015372 | 1.1825e-05 | 130
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | POLE | 10 | 4371 | 540536 | 0.48597 | 0.0039298 | 123.6642
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AO | NONE | 9 | 7933 | 737694 | 0.671 | 0.0072158 | 92.9905
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 1 | 183 | 0.00016646 | 9.0959e-07 | 183
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | CONN/CLAMP | 711 | 2467 | 333529 | 0.29986 | 0.002218 | 135.1962
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | POLE HARDWARE | 20 | 820 | 87978 | 0.079097 | 0.00073722 | 107.2902
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 11 | 149 | 33014 | 0.029681 | 0.00013396 | 221.5705
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 5 | 14 | 1864 | 0.0016758 | 1.2587e-05 | 133.1429
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 247 | 68304 | 0.062612 | 0.00022642 | 276.5344
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 3 | 160 | 23021 | 0.020697 | 0.00014385 | 143.8812
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | SPLICE, OH | 2 | 2 | 114 | 0.00010559 | 1.8525e-06 | 57
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 1 | 77 | 7.0039e-05 | 9.0959e-07 | 77
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | POLE HARDWARE | 1 | 9 | 243 | 0.00022275 | 8.25e-06 | 27
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | OL | NONE | 1 | 240 | 8400 | 0.0078882 | 0.00022538 | 35
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | FUSE | 4 | 15 | 967 | 0.00089568 | 1.3894e-05 | 64.4667
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | OL | RELAY | 1 | 1340 | 16080 | 0.014894 | 0.0012412 | 12
AEP-TX | 2025 | 1112283 | PARTIAL POWER | U | NONE | 3 | 20 | 3821 | 0.0034353 | 1.7981e-05 | 191.05
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 11 | 627 | 0.0005888 | 1.033e-05 | 57
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | SECTIONALIZER | 1 | 12 | 5448 | 0.0051161 | 1.1269e-05 | 454
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | POLE | 1 | 3 | 315 | 0.00029581 | 2.8172e-06 | 105
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | CABLE TERMINATOR | 1 | 3 | 204 | 0.00018341 | 2.6972e-06 | 68
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WT | POLE | 1 | 472 | 105237 | 0.094614 | 0.00042435 | 222.9597
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | WU | NONE | 3 | 3425 | 478731 | 0.4304 | 0.0030793 | 139.7755
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | FO | OTHER EQUIPMENT | 1 | 1 | 289 | 0.00027139 | 9.3908e-07 | 289
AEP-TX | 2025 | 1112283 | PARTIAL POWER | VIN | NONE | 2 | 4 | 330 | 0.00029669 | 3.5962e-06 | 82.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 6 | 450 | 0.00040457 | 5.3943e-06 | 75
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 186 | 24738 | 0.022241 | 0.00016722 | 133
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1579 | 9521 | 2036856 | 1.8671 | 0.0087275 | 213.933
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | NONE | 1271 | 16283 | 1380253 | 1.2784 | 0.015082 | 84.7665
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | FO | NONE | 116 | 13199 | 1095045 | 1.0038 | 0.012099 | 82.9642
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | PEDESTAL | 6 | 47 | 1098 | 0.001017 | 4.3533e-05 | 23.3617
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 582 | 13651 | 2533446 | 2.3044 | 0.012417 | 185.5868
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 83 | 415 | 100270 | 0.092874 | 0.00038439 | 241.6145
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 108 | 1538 | 166802 | 0.1529 | 0.0014098 | 108.4538
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | CUTOUT | 27 | 130 | 14777 | 0.013546 | 0.00011917 | 113.6692
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 3704 | 338025 | 0.30985 | 0.0033953 | 91.2594
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 80 | 606 | 109301 | 0.10124 | 0.0005613 | 180.3647
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | CONN/CLAMP | 13 | 45 | 4318 | 0.0039995 | 4.1681e-05 | 95.9556
AEP-TX | 2022 | 1090914 | PARTIAL POWER | VIN | NONE | 13 | 21 | 3073 | 0.0028169 | 1.925e-05 | 146.3333
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | SPLICE, OH | 13 | 39 | 5756 | 0.0052763 | 3.575e-05 | 147.5897
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | SWITCH, OH | 1 | 1218 | 63336 | 0.058058 | 0.0011165 | 52
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | NONE | 1049 | 11938 | 845208 | 0.79372 | 0.011211 | 70.7998
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | CROSSARM | 226 | 32275 | 3839932 | 3.606 | 0.030309 | 118.9754
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 94 | 51284 | 0.04816 | 8.8273e-05 | 545.5745
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 3 | 16 | 4588 | 0.0042496 | 1.482e-05 | 286.75
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 29 | 146 | 30441 | 0.028196 | 0.00013523 | 208.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | ARRESTER | 30 | 220 | 24857 | 0.023343 | 0.0002066 | 112.9864
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | CUTOUT | 3 | 7 | 840 | 0.00077804 | 6.4837e-06 | 120
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 2 | 11 | 758 | 0.00070209 | 1.0189e-05 | 68.9091
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | NONE | 198 | 33546 | 3745030 | 3.4065 | 0.030513 | 111.6386
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | U | NONE | 3551 | 119350 | 7214200 | 6.562 | 0.10856 | 60.4457
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 12 | 20 | 3244 | 0.0030464 | 1.8782e-05 | 162.2
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | INSULATOR | 15 | 1966 | 269673 | 0.25324 | 0.0018462 | 137.1684
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | POLE | 4 | 94 | 804310 | 0.74499 | 8.7067e-05 | 8556.4894
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | CUTOUT | 28 | 501 | 63349 | 0.05949 | 0.00047048 | 126.4451
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | CONN/CLAMP | 5 | 11 | 1271 | 0.0011773 | 1.0189e-05 | 115.5455
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ABI | CUTOUT | 5 | 173 | 21091 | 0.019333 | 0.00015858 | 121.9133
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | CF | JUMPER/RISER | 2 | 2903 | 267405 | 0.24768 | 0.0026889 | 92.1133
AEP-TX | 2022 | 1090914 | PARTIAL POWER | A | CUTOUT | 1 | 1 | 57 | 5.225e-05 | 9.1666e-07 | 57
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | SWITCH, OH | 1 | 214 | 8774 | 0.0079808 | 0.00019465 | 41
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | U | NONE | 1629 | 166493 | 6361944 | 5.7197 | 0.14969 | 38.2115
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 5 | 11 | 3185 | 0.002991 | 1.033e-05 | 289.5455
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 2 | 37 | 6211 | 0.0056495 | 3.3655e-05 | 167.8649
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 36 | 147 | 30511 | 0.027753 | 0.00013371 | 207.5578
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | CONDUCTOR UG | 74 | 190 | 36790 | 0.033464 | 0.00017282 | 193.6316
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 31 | 2959 | 0.0026915 | 2.8197e-05 | 95.4516
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | POLE | 13 | 1272 | 451887 | 0.42436 | 0.0011945 | 355.2571
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TIR | ARRESTER | 3 | 7 | 376 | 0.00035309 | 6.5735e-06 | 53.7143
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | METERING | 124 | 147 | 11397 | 0.010246 | 0.00013216 | 77.5306
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | INSULATOR | 4 | 2607 | 170027 | 0.15466 | 0.0023713 | 65.2194
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TOR | TRANSFORMER, OH | 1 | 1 | 461 | 0.00041446 | 8.9905e-07 | 461
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ABI | ARRESTER | 10 | 80 | 11520 | 0.010479 | 7.2768e-05 | 144
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | POLE | 48 | 10983 | 2607702 | 2.3445 | 0.0098743 | 237.4308
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | POLE HARDWARE | 2 | 7 | 980 | 0.00088107 | 6.2934e-06 | 140
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | CONN/CLAMP | 68 | 392 | 48929 | 0.04399 | 0.00035243 | 124.8189
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | SPLICE, OH | 7 | 57 | 6059 | 0.0055112 | 5.1847e-05 | 106.2982
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | CF | NONE | 18 | 21744 | 1772373 | 1.5935 | 0.019549 | 81.5109
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | SPLICE, UG | 4 | 204 | 61567 | 0.055352 | 0.00018341 | 301.799
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | CROSSARM | 15 | 1818 | 465013 | 0.41807 | 0.0016345 | 255.7827
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | ARRESTER | 8 | 95 | 14853 | 0.013354 | 8.541e-05 | 156.3474
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 9 | 586 | 30150 | 0.027106 | 0.00052684 | 51.4505
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 28 | 3882 | 0.003531 | 2.5469e-05 | 138.6429
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 9 | 3059 | 330798 | 0.2974 | 0.0027502 | 108.1393
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 2 | 305 | 0.00028642 | 1.8782e-06 | 152.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 805 | 95676 | 0.089847 | 0.00075596 | 118.8522
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | CUTOUT | 7 | 22 | 1211 | 0.0010888 | 1.9779e-05 | 55.0455
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | CABLE TERMINATOR | 5 | 36 | 11260 | 0.010123 | 3.2366e-05 | 312.7778
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | A | NONE | 280 | 3460 | 217930 | 0.19593 | 0.0031107 | 62.9855
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | NONE | 304 | 15289 | 1249597 | 1.1235 | 0.013746 | 81.7318
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 14 | 76 | 10158 | 0.0094088 | 7.0394e-05 | 133.6579
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | INSULATOR | 2 | 63 | 11833 | 0.01096 | 5.8353e-05 | 187.8254
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | NONE | 28 | 4606 | 104764 | 0.098382 | 0.0043254 | 22.7451
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 6 | 69 | 31414 | 0.029097 | 6.3911e-05 | 455.2754
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | POLE | 3 | 15 | 767 | 0.00071043 | 1.3894e-05 | 51.1333
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | CF | MOAB | 5 | 4483 | 32142 | 0.029771 | 0.0041523 | 7.1698
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | SPLICE, UG | 5 | 19 | 6198 | 0.0056815 | 1.7417e-05 | 326.2105
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 46 | 11697 | 0.010722 | 4.2166e-05 | 254.2826
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 11 | 4279 | 0.0039224 | 1.0083e-05 | 389
AEP-TX | 2023 | 1099391 | PARTIAL POWER | VIN | NONE | 13 | 29 | 2420 | 0.0022012 | 2.6378e-05 | 83.4483
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | JUMPER/RISER | 6 | 139 | 21005 | 0.019456 | 0.00012875 | 151.1151
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | CONDUCTOR UG | 100 | 380 | 65239 | 0.058653 | 0.00034164 | 171.6816
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | CONN/CLAMP | 1328 | 2826 | 281482 | 0.25307 | 0.0025407 | 99.6044
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | SWITCH, UG | 2 | 4 | 53 | 4.9771e-05 | 3.7563e-06 | 13.25
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | SPLICE, UG | 1 | 1 | 70 | 6.3672e-05 | 9.0959e-07 | 70
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 92 | 14452 | 0.013145 | 8.3683e-05 | 157.087
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | INSULATOR | 10 | 579 | 82636 | 0.075165 | 0.00052666 | 142.7219
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | CROSSARM | 38 | 12119 | 1113458 | 1.0128 | 0.011023 | 91.8771
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 200 | 35800 | 0.033619 | 0.00018782 | 179
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | JUMPER/RISER | 17 | 2722 | 391285 | 0.35179 | 0.0024472 | 143.7491
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 1 | 29 | 2.6861e-05 | 9.2624e-07 | 29
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | INSULATOR | 3 | 116 | 25170 | 0.023072 | 0.00010633 | 216.9828
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 455 | 237739 | 0.21625 | 0.00041387 | 522.5033
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | SWITCH, OH | 6 | 6285 | 349385 | 0.31412 | 0.0056505 | 55.5903
AEP-TX | 2024 | 1112283 | PARTIAL POWER | VIN | NONE | 13 | 23 | 2061 | 0.0018529 | 2.0678e-05 | 89.6087
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WT | NONE | 9 | 285 | 132535 | 0.12446 | 0.00026764 | 465.0351
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 26 | 13847 | 0.012595 | 2.3649e-05 | 532.5769
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WT | TRANSFORMER, UG | 1 | 10 | 12950 | 0.011779 | 9.0959e-06 | 1295
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WT | POLE | 1 | 1 | 305 | 0.00027743 | 9.0959e-07 | 305
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | INSULATOR | 5 | 1904 | 295804 | 0.27115 | 0.0017453 | 155.3592
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 3 | 8 | 938 | 0.00084331 | 7.1924e-06 | 117.25
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | CONN/CLAMP | 465 | 998 | 108186 | 0.097265 | 0.00089725 | 108.4028
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | CROSSARM | 3 | 13 | 2326 | 0.0020912 | 1.1688e-05 | 178.9231
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 893 | 50545 | 0.045975 | 0.00081227 | 56.6013
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | JUMPER/RISER | 7 | 46 | 2499 | 0.0022467 | 4.1356e-05 | 54.3261
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 2 | 165 | 0.00014834 | 1.7981e-06 | 82.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | FUSE | 4 | 54 | 3874 | 0.0034829 | 4.8549e-05 | 71.7407
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | JUMPER/RISER | 5 | 56 | 4587 | 0.004124 | 5.0347e-05 | 81.9107
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | TRANSFORMER, UG | 2 | 2 | 927 | 0.00085863 | 1.8525e-06 | 463.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | JUMPER/RISER | 1 | 4 | 1120 | 0.0010518 | 3.7563e-06 | 280
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 287 | 41615 | 0.03908 | 0.00026952 | 145
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 72 | 2340 | 0.0021974 | 6.7614e-05 | 32.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 99 | 9798 | 0.0088089 | 8.9006e-05 | 98.9697
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 12 | 569 | 40614 | 0.036514 | 0.00051156 | 71.3779
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | OTHER EQUIPMENT | 1 | 1 | 100 | 9.3908e-05 | 9.3908e-07 | 100
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 9 | 1715 | 0.0015419 | 8.0915e-06 | 190.5556
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERF | FUSE | 2 | 38 | 3116 | 0.0028563 | 3.4833e-05 | 82
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WL | CUTOUT | 1 | 1 | 132 | 0.000121 | 9.1666e-07 | 132
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 1 | 1 | 311 | 0.00028806 | 9.2624e-07 | 311
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AO | BREAKER | 3 | 8290 | 472694 | 0.4333 | 0.0075991 | 57.0198
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | OL | NONE | 1 | 4 | 336 | 0.00030562 | 3.6384e-06 | 84
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 258 | 0.0002365 | 9.1666e-07 | 258
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | TRANSFORMER, STATION SERVICE | 1 | 1 | 47 | 4.2255e-05 | 8.9905e-07 | 47
AEP-TX | 2023 | 1099391 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 9 | 1044 | 0.00094962 | 8.1864e-06 | 116
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | FUSE | 1 | 3 | 174 | 0.00015644 | 2.6972e-06 | 58
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | NONE | 2828 | 101449 | 10525256 | 9.6481 | 0.092994 | 103.7492
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 443 | 15767 | 2276982 | 2.0872 | 0.014453 | 144.4144
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | INSULATOR | 114 | 13898 | 1492383 | 1.368 | 0.01274 | 107.3811
AEP-TX | 2022 | 1090914 | PARTIAL POWER | ABI | NONE | 36 | 74 | 4590 | 0.0042075 | 6.7833e-05 | 62.027
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | POLE HARDWARE | 22 | 1543 | 280351 | 0.25699 | 0.0014144 | 181.6922
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | ARRESTER | 9 | 39 | 4107 | 0.0037647 | 3.575e-05 | 105.3077
AEP-TX | 2022 | 1090914 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 2 | 13 | 410 | 0.00037583 | 1.1917e-05 | 31.5385
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 14 | 94 | 22415 | 0.020762 | 8.7067e-05 | 238.4574
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WL | JUMPER/RISER | 2 | 2 | 563 | 0.0005287 | 1.8782e-06 | 281.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | INSULATOR | 6 | 2185 | 196703 | 0.18472 | 0.0020519 | 90.0243
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | POLE HARDWARE | 9 | 1057 | 98479 | 0.092479 | 0.0009926 | 93.1684
AEP-TX | 2021 | 1079632 | PARTIAL POWER | ERF | NONE | 1 | 1 | 118 | 0.0001093 | 9.2624e-07 | 118
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 287 | 21238 | 0.019944 | 0.00026952 | 74
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | POLE | 291 | 59931 | 9223239 | 8.3894 | 0.054513 | 153.8976
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | ARRESTER | 26 | 1231 | 58747 | 0.054414 | 0.0011402 | 47.723
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | FUSE | 2 | 3 | 657 | 0.00060225 | 2.75e-06 | 219
AEP-TX | 2020 | 1064875 | PARTIAL POWER | A | NONE | 38 | 85 | 4420 | 0.0041507 | 7.9822e-05 | 52
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AF | ARRESTER | 4 | 1929 | 730511 | 0.67663 | 0.0017867 | 378.6993
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TOR | POLE | 3 | 3 | 855 | 0.00080291 | 2.8172e-06 | 285
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | CUTOUT | 89 | 930 | 124275 | 0.11304 | 0.00084592 | 133.629
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | SPLICE, OH | 3 | 221 | 11788 | 0.01107 | 0.00020754 | 53.3394
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 138 | 11057 | 0.010383 | 0.00012959 | 80.1232
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 11 | 521 | 46031 | 0.04187 | 0.0004739 | 88.3512
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | ARRESTER | 10 | 23 | 4927 | 0.0044816 | 2.0921e-05 | 214.2174
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 14 | 211 | 27674 | 0.025172 | 0.00019192 | 131.1564
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | FUSE | 5 | 16 | 2772 | 0.0025675 | 1.482e-05 | 173.25
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 9 | 4067 | 188972 | 0.17503 | 0.003767 | 46.4647
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 8 | 3408 | 0.0031566 | 7.4099e-06 | 426
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | JUMPER/RISER | 50 | 384 | 41453 | 0.037268 | 0.00034524 | 107.9505
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 7 | 1099 | 0.00098806 | 6.2934e-06 | 157
AEP-TX | 2023 | 1099391 | PARTIAL POWER | A | METERING | 1 | 1 | 74 | 6.731e-05 | 9.0959e-07 | 74
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 54 | 4.9118e-05 | 9.0959e-07 | 54
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | CONN/CLAMP | 32 | 123 | 13188 | 0.011857 | 0.00011058 | 107.2195
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 6 | 18 | 6787 | 0.0061734 | 1.6373e-05 | 377.0556
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | SPLICE, OH | 8 | 15 | 1488 | 0.0013378 | 1.3486e-05 | 99.2
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WU | ARRESTER | 2 | 2 | 161 | 0.00014644 | 1.8192e-06 | 80.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | ABI | NONE | 8 | 2227 | 383816 | 0.34507 | 0.0020022 | 172.3467
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | WL | MOAB | 2 | 2 | 5083 | 0.0046235 | 1.8192e-06 | 2541.5
AEP-TX | 2024 | 1112283 | PARTIAL POWER | OL | TRANSFORMER, OH | 5 | 17 | 3649 | 0.0032806 | 1.5284e-05 | 214.6471
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ABI | CIRCUIT SWITCHER | 2 | 883 | 35703 | 0.032475 | 0.00080317 | 40.4337
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | CROSSARM | 126 | 13614 | 1590037 | 1.4295 | 0.01224 | 116.7943
AEP-TX | 2025 | 1112283 | PARTIAL POWER | OL | NONE | 39 | 115 | 9372 | 0.0084259 | 0.00010339 | 81.4957
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 138 | 0.00012407 | 8.9905e-07 | 138
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 5 | 1035 | 0.00094875 | 4.5833e-06 | 207
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 24 | 299 | 22063 | 0.019836 | 0.00026882 | 73.7893
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | JUMPER/RISER | 9 | 124 | 14848 | 0.013349 | 0.00011148 | 119.7419
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | ARRESTER | 2 | 13 | 1012 | 0.00095035 | 1.2208e-05 | 77.8462
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TR | NONE | 13 | 389 | 27454 | 0.024683 | 0.00034973 | 70.5758
AEP-TX | 2020 | 1064875 | PARTIAL POWER | FO | TRANSFORMER, OH | 1 | 1 | 71 | 6.6674e-05 | 9.3908e-07 | 71
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | SWITCH, OH | 4 | 2759 | 164265 | 0.14768 | 0.0024805 | 59.5379
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ABI | ARRESTER | 4 | 40 | 5082 | 0.004569 | 3.5962e-05 | 127.05
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | TRANSFORMER, UG | 1 | 1 | 98 | 8.8107e-05 | 8.9905e-07 | 98
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 2 | 5 | 488 | 0.00045201 | 4.6312e-06 | 97.6
AEP-TX | 2020 | 1064875 | PARTIAL POWER | OL | TRANSFORMER, OH | 5 | 33 | 4649 | 0.0043658 | 3.099e-05 | 140.8788
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 152 | 17176 | 0.01613 | 0.00014274 | 113
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | JUMPER/RISER | 2 | 1433 | 217029 | 0.20381 | 0.0013457 | 151.4508
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | INSULATOR | 3 | 13 | 4987 | 0.0045361 | 1.1825e-05 | 383.6154
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TR | POLE | 1 | 1 | 501 | 0.00047048 | 9.3908e-07 | 501
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | AB | REGULATOR | 3 | 2384 | 118464 | 0.11125 | 0.0022388 | 49.6913
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 67 | 6.0943e-05 | 9.0959e-07 | 67
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 13 | 1296 | 0.0011652 | 1.1688e-05 | 99.6923
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | SPLICE, UG | 2 | 5 | 993 | 0.0009325 | 4.6954e-06 | 198.6
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 158 | 30336 | 0.027274 | 0.00014205 | 192
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | CIRCUIT SWITCHER | 1 | 1 | 178 | 0.00016716 | 9.3908e-07 | 178
AEP-TX | 2024 | 1112283 | PARTIAL POWER | UB | CONN/CLAMP | 1 | 3 | 300 | 0.00026972 | 2.6972e-06 | 100
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WI | NONE | 1 | 1 | 35 | 3.2868e-05 | 9.3908e-07 | 35
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 1 | 446 | 0.00040098 | 8.9905e-07 | 446
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | CF | JUMPER/RISER | 1 | 536 | 8040 | 0.0072284 | 0.00048189 | 15
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 27 | 2244 | 535125 | 0.50252 | 0.0021073 | 238.4693
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | POLE | 1 | 1 | 27 | 2.5355e-05 | 9.3908e-07 | 27
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 12 | 240 | 0.00022538 | 1.1269e-05 | 20
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | CONN/CLAMP | 103 | 1030 | 89779 | 0.083157 | 0.00095403 | 87.1641
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | CF | SWITCH, OH | 3 | 3969 | 383776 | 0.35179 | 0.0036382 | 96.6934
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | TRANSFORMER, OH | 4 | 8 | 1683 | 0.0015427 | 7.3333e-06 | 210.375
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1047 | 114656 | 14793479 | 13.4561 | 0.10429 | 129.0249
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 5 | 118 | 11581 | 0.010727 | 0.0001093 | 98.1441
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | SWITCH, OH | 4 | 711 | 10445 | 0.0096746 | 0.00065856 | 14.6906
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | POLE | 82 | 36860 | 3929109 | 3.5739 | 0.033528 | 106.5955
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | METERING | 4 | 4 | 224 | 0.00020748 | 3.705e-06 | 56
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 11 | 2193 | 0.0020102 | 1.0083e-05 | 199.3636
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 75 | 355 | 75375 | 0.068561 | 0.00032291 | 212.3239
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | INSULATOR | 1 | 1 | 125 | 0.00011738 | 9.3908e-07 | 125
AEP-TX | 2023 | 1099391 | PARTIAL POWER | AF | CONDUCTOR UG | 1 | 2 | 778 | 0.00070766 | 1.8192e-06 | 389
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 11 | 3215 | 0.0030191 | 1.033e-05 | 292.2727
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | BREAKER | 3 | 3775 | 726478 | 0.66594 | 0.0034604 | 192.4445
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 1 | 111 | 0.00010175 | 9.1666e-07 | 111
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 4 | 19 | 2610 | 0.0024175 | 1.7599e-05 | 137.3684
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 36 | 7299 | 693981 | 0.62392 | 0.0065622 | 95.0789
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | CO | CONN/CLAMP | 1 | 1 | 14 | 1.2734e-05 | 9.0959e-07 | 14
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | U | NONE | 37 | 33687 | 2729259 | 2.4537 | 0.030286 | 81.0182
AEP-TX | 2024 | 1112283 | PARTIAL POWER | OL | CONN/CLAMP | 60 | 164 | 19803 | 0.017804 | 0.00014744 | 120.75
AEP-TX | 2020 | 1064875 | PARTIAL POWER | VA | CONDUCTOR UG | 2 | 2 | 279 | 0.000262 | 1.8782e-06 | 139.5
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | PEDESTAL | 4 | 14 | 259 | 0.00023558 | 1.2734e-05 | 18.5
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 783 | 43694 | 0.039744 | 0.00071221 | 55.8033
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AF | NONE | 7 | 4347 | 383896 | 0.3519 | 0.0039847 | 88.3129
AEP-TX | 2023 | 1099391 | PARTIAL POWER | ABI | CONN/CLAMP | 1 | 1 | 99 | 9.005e-05 | 9.0959e-07 | 99
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 24 | 334 | 54099 | 0.048638 | 0.00030028 | 161.9731
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | CONN/CLAMP | 5 | 6 | 826 | 0.00075133 | 5.4576e-06 | 137.6667
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ABI | CUTOUT | 2 | 23 | 898 | 0.00080735 | 2.0678e-05 | 39.0435
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 1 | 88 | 8.1509e-05 | 9.2624e-07 | 88
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 1 | 112 | 0.00010518 | 9.3908e-07 | 112
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | CONN/CLAMP | 332 | 899 | 94311 | 0.08479 | 0.00080825 | 104.9066
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | CUTOUT | 52 | 859 | 74391 | 0.066881 | 0.00077229 | 86.6019
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VIN | NONE | 20 | 118 | 11009 | 0.0098977 | 0.00010609 | 93.2966
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | SPLICE, OH | 1 | 1 | 210 | 0.0001888 | 8.9905e-07 | 210
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 44 | 10325 | 0.0092827 | 3.9558e-05 | 234.6591
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 8 | 424 | 0.00039817 | 7.5126e-06 | 53
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 93 | 17467 | 0.016403 | 8.7334e-05 | 187.8172
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | ARRESTER | 6 | 6 | 528 | 0.0004747 | 5.3943e-06 | 88
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 4 | 105 | 38004 | 0.034168 | 9.44e-05 | 361.9429
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | JUMPER/RISER | 9 | 616 | 45629 | 0.041023 | 0.00055382 | 74.0731
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 2 | 4 | 138 | 0.00012407 | 3.5962e-06 | 34.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | CROSSARM | 4 | 1857 | 537738 | 0.48345 | 0.0016695 | 289.5735
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 1 | 53 | 4.765e-05 | 8.9905e-07 | 53
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | CROSSARM | 1 | 2 | 386 | 0.00035383 | 1.8333e-06 | 193
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 2 | 1940 | 328443 | 0.30422 | 0.0017969 | 169.3005
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 1 | 468 | 79560 | 0.073692 | 0.00043348 | 170
AEP-TX | 2024 | 1112283 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 6 | 586 | 0.00052684 | 5.3943e-06 | 97.6667
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | ERF | RELAY | 1 | 898 | 33226 | 0.030775 | 0.00083176 | 37
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 552 | 46920 | 0.042678 | 0.0005021 | 85
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CF | TRANSFORMER, OH | 1 | 83 | 25066 | 0.022536 | 7.4621e-05 | 302
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | SPLICE, UG | 1 | 74 | 1282 | 0.0011526 | 6.653e-05 | 17.3243
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | METERING | 1 | 3 | 78 | 7.0126e-05 | 2.6972e-06 | 26
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 13 | 2249 | 0.002022 | 1.1688e-05 | 173
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 38 | 3762 | 0.0033822 | 3.4164e-05 | 99
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 19 | 969 | 0.0008814 | 1.7282e-05 | 51
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 160 | 23483 | 0.021526 | 0.00014667 | 146.7688
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WT | NONE | 4 | 318 | 375872 | 0.34455 | 0.0002915 | 1181.9874
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 84 | 7375 | 913462 | 0.83734 | 0.0067604 | 123.8593
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 69 | 341 | 76683 | 0.071027 | 0.00031585 | 224.8768
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | ARRESTER | 109 | 2391 | 270803 | 0.24823 | 0.0021917 | 113.2593
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | CONN/CLAMP | 18 | 705 | 78386 | 0.071854 | 0.00064625 | 111.1858
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 3 | 42 | 4039 | 0.0037411 | 3.8902e-05 | 96.1667
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | NONE | 713 | 6427 | 457518 | 0.42964 | 0.0060355 | 71.1869
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 3 | 5 | 855 | 0.00078375 | 4.5833e-06 | 171
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | CUTOUT | 18 | 260 | 27940 | 0.026238 | 0.00024416 | 107.4615
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 19 | 236 | 181663 | 0.16826 | 0.00021859 | 769.7585
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | NONE | 35 | 132 | 8763 | 0.0081167 | 0.00012226 | 66.3864
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 2704 | 432310 | 0.40042 | 0.0025046 | 159.878
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 5529 | 629682 | 0.58324 | 0.0051212 | 113.8871
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 4 | 1256 | 101937 | 0.094418 | 0.0011634 | 81.16
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 12 | 254 | 0.00023527 | 1.1115e-05 | 21.1667
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | U | NONE | 33 | 22151 | 2490846 | 2.3071 | 0.020517 | 112.4485
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | NONE | 1080 | 46844 | 4700625 | 4.2757 | 0.042609 | 100.3464
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | NONE | 4214 | 104810 | 16029556 | 14.5804 | 0.095335 | 152.9392
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 649 | 0.00059491 | 9.1666e-07 | 649
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WU | CONN/CLAMP | 8 | 17 | 1682 | 0.0015122 | 1.5284e-05 | 98.9412
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | JUMPER/RISER | 7 | 171 | 25151 | 0.023296 | 0.00015839 | 147.0819
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | POLE | 13 | 499 | 25650 | 0.023512 | 0.00045741 | 51.4028
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | METERING | 7 | 13 | 1249 | 0.0011569 | 1.2041e-05 | 96.0769
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | CUTOUT | 13 | 132 | 17244 | 0.015685 | 0.00012007 | 130.6364
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | ARRESTER | 10 | 261 | 33256 | 0.030803 | 0.00024175 | 127.4176
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 1 | 1 | 238 | 0.0002235 | 9.3908e-07 | 238
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | WL | NONE | 12 | 3676 | 925515 | 0.84184 | 0.0033437 | 251.7723
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | CONN/CLAMP | 5 | 9 | 2748 | 0.0024996 | 8.1864e-06 | 305.3333
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | METERING | 5 | 11 | 1347 | 0.0012649 | 1.033e-05 | 122.4545
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | CROSSARM | 3 | 3162 | 710751 | 0.66745 | 0.0029694 | 224.7789
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | BREAKER | 1 | 2468 | 207312 | 0.19004 | 0.0022623 | 84
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | ARRESTER | 378 | 6633 | 679278 | 0.61071 | 0.0059634 | 102.4089
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | POLE | 103 | 28530 | 2831486 | 2.5457 | 0.02565 | 99.2459
AEP-TX | 2023 | 1099391 | PARTIAL POWER | FO | NONE | 11 | 15 | 1721 | 0.0015654 | 1.3644e-05 | 114.7333
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ABI | NONE | 27 | 33735 | 1937668 | 1.7625 | 0.030685 | 57.4379
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | CROSSARM | 29 | 6760 | 791262 | 0.71139 | 0.0060776 | 117.0506
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VIN | ARRESTER | 3 | 12 | 815 | 0.00074132 | 1.0915e-05 | 67.9167
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 34 | 944 | 109059 | 0.09805 | 0.0008487 | 115.5286
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | FUSE | 2 | 43 | 4020 | 0.0037751 | 4.038e-05 | 93.4884
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | TRANSFORMER, UG | 10 | 23 | 5651 | 0.0050805 | 2.0678e-05 | 245.6957
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 85 | 350 | 47152 | 0.042392 | 0.00031467 | 134.72
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ABI | TRANSFORMER, STATION SERVICE | 3 | 1023 | 400449 | 0.36425 | 0.00093052 | 391.4457
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 13 | 12248 | 2391642 | 2.2459 | 0.011502 | 195.268
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | POLE | 1 | 3 | 459 | 0.00041266 | 2.6972e-06 | 153
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | CUTOUT | 9 | 152 | 12578 | 0.011308 | 0.00013666 | 82.75
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 2 | 722 | 46622 | 0.043782 | 0.00067801 | 64.5734
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 65 | 113 | 10683 | 0.0096046 | 0.00010159 | 94.5398
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 26 | 6207 | 653686 | 0.5877 | 0.0055804 | 105.3143
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | NONE | 107 | 7140 | 745801 | 0.67051 | 0.0064192 | 104.4539
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 39 | 245 | 32758 | 0.029451 | 0.00022027 | 133.7061
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | SPLICE, OH | 7 | 59 | 6959 | 0.0062565 | 5.3044e-05 | 117.9492
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | JUMPER/RISER | 2 | 8 | 410 | 0.00036861 | 7.1924e-06 | 51.25
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 686 | 60755 | 0.055692 | 0.00062883 | 88.5641
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | EQF | RELAY | 1 | 260 | 5720 | 0.0051426 | 0.00023375 | 22
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 2 | 88 | 8.2639e-05 | 1.8782e-06 | 44
AEP-TX | 2021 | 1079632 | PARTIAL POWER | AF | NONE | 1 | 1 | 108 | 0.00010003 | 9.2624e-07 | 108
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 16 | 2464 | 0.0022823 | 1.482e-05 | 154
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VIN | POLE | 1 | 1 | 50 | 4.6312e-05 | 9.2624e-07 | 50
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 4 | 799 | 89786 | 0.080722 | 0.00071834 | 112.373
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AF | SWITCH, UG | 1 | 903 | 140868 | 0.12813 | 0.00082136 | 156
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 1 | 106 | 9.5299e-05 | 8.9905e-07 | 106
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 2 | 6 | 767 | 0.00068957 | 5.3943e-06 | 127.8333
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 9 | 30 | 7959 | 0.0071556 | 2.6972e-05 | 265.3
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | INSULATOR | 6 | 2222 | 184071 | 0.16549 | 0.0019977 | 82.8402
AEP-TX | 2025 | 1112283 | PARTIAL POWER | UB | CONN/CLAMP | 2 | 2 | 150 | 0.00013486 | 1.7981e-06 | 75
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 8 | 168 | 0.00015776 | 7.5126e-06 | 21
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CF | JUMPER/RISER | 1 | 16 | 1760 | 0.0015823 | 1.4385e-05 | 110
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 22 | 1936 | 0.0017406 | 1.9779e-05 | 88
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | CAPACITOR | 4 | 107 | 8282 | 0.0074459 | 9.6199e-05 | 77.4019
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 10 | 520 | 0.00046751 | 8.9905e-06 | 52
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | EQF | INSULATOR | 3 | 3476 | 167745 | 0.15081 | 0.0031251 | 48.2581
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 34 | 3.0568e-05 | 8.9905e-07 | 34
AEP-TX | 2020 | 1064875 | PARTIAL POWER | ABI | ARRESTER | 2 | 2 | 169 | 0.0001587 | 1.8782e-06 | 84.5
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 5 | 415 | 0.00038041 | 4.5833e-06 | 83
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | SWITCH, UG | 1 | 797 | 29489 | 0.027314 | 0.00073821 | 37
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 3 | 1386 | 0.0012607 | 2.7288e-06 | 462
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | POLE | 1 | 6 | 894 | 0.00081318 | 5.4576e-06 | 149
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TOR | METERING | 1 | 1 | 93 | 8.7334e-05 | 9.3908e-07 | 93
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | CROSSARM | 1 | 42 | 7584 | 0.0068984 | 3.8203e-05 | 180.5714
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VIN | NONE | 148 | 2529 | 174758 | 0.16019 | 0.0023182 | 69.1016
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 406 | 41677 | 4035015 | 3.6987 | 0.038204 | 96.8163
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 221 | 5148 | 643799 | 0.59015 | 0.004719 | 125.0581
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | POLE | 42 | 10191 | 682686 | 0.63233 | 0.0094393 | 66.9891
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 196 | 49284 | 7968459 | 7.3807 | 0.045649 | 161.6845
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | CUTOUT | 2 | 19 | 5690 | 0.0052158 | 1.7417e-05 | 299.4737
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 99 | 648 | 142510 | 0.13063 | 0.000594 | 219.9228
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WT | CONDUCTOR UG | 1 | 1 | 39 | 3.575e-05 | 9.1666e-07 | 39
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WH | NONE | 1 | 16 | 864 | 0.000792 | 1.4667e-05 | 54
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | U | NONE | 27 | 16605 | 1321275 | 1.2112 | 0.015221 | 79.5709
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 90 | 24445 | 2415829 | 2.2687 | 0.022956 | 98.8271
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 150 | 3944 | 520145 | 0.48846 | 0.0037037 | 131.8826
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TIR | CONN/CLAMP | 57 | 170 | 43221 | 0.040588 | 0.00015964 | 254.2412
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 11 | 1512 | 92230 | 0.086611 | 0.0014199 | 60.9987
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | METERING | 5 | 5 | 803 | 0.00075408 | 4.6954e-06 | 160.6
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TIR | CONN/CLAMP | 34 | 86 | 13283 | 0.012303 | 7.9657e-05 | 154.4535
AEP-TX | 2020 | 1064875 | PARTIAL POWER | A | CONN/CLAMP | 1 | 10 | 950 | 0.00089212 | 9.3908e-06 | 95
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | NONE | 62 | 816 | 141709 | 0.13126 | 0.00075581 | 173.663
AEP-TX | 2021 | 1079632 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 273 | 0.00025286 | 9.2624e-07 | 273
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | OTHER EQUIPMENT | 1 | 33 | 5742 | 0.0053185 | 3.0566e-05 | 174
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | PEDESTAL | 5 | 45 | 36831 | 0.033762 | 4.125e-05 | 818.4667
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TIR | JUMPER/RISER | 3 | 26 | 3348 | 0.003069 | 2.3833e-05 | 128.7692
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 11 | 23 | 4722 | 0.0044343 | 2.1599e-05 | 205.3043
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | PEDESTAL | 1 | 13 | 13533 | 0.012405 | 1.1917e-05 | 1041
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WL | ARRESTER | 7 | 149 | 36041 | 0.033845 | 0.00013992 | 241.8859
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 7 | 34 | 4666 | 0.0043817 | 3.1929e-05 | 137.2353
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | CUTOUT | 3 | 5 | 533 | 0.00048481 | 4.548e-06 | 106.6
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | REGULATOR | 1 | 360 | 6480 | 0.006002 | 0.00033345 | 18
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1348 | 5672 | 609491 | 0.54796 | 0.0050994 | 107.4561
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1642 | 10966 | 1207989 | 1.086 | 0.009859 | 110.1577
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 4 | 35 | 12593 | 0.011455 | 3.1836e-05 | 359.8
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | NONE | 1304 | 54908 | 4918163 | 4.4217 | 0.049365 | 89.571
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 115 | 1794 | 299817 | 0.26955 | 0.0016129 | 167.1221
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | NONE | 73 | 7562 | 1203338 | 1.0819 | 0.0067986 | 159.1296
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 12 | 303 | 77686 | 0.070663 | 0.00027561 | 256.3894
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | CONDUCTOR UG | 4 | 4 | 685 | 0.00064327 | 3.7563e-06 | 171.25
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 11 | 93 | 15317 | 0.013932 | 8.4592e-05 | 164.6989
AEP-TX | 2022 | 1090914 | PARTIAL POWER | OL | JUMPER/RISER | 3 | 51 | 9617 | 0.0088155 | 4.675e-05 | 188.5686
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 1 | 178 | 0.00016487 | 9.2624e-07 | 178
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | PEDESTAL | 1 | 4 | 448 | 0.0004075 | 3.6384e-06 | 112
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 6 | 27 | 4769 | 0.0042876 | 2.4274e-05 | 176.6296
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | CUTOUT | 36 | 2005 | 152562 | 0.13716 | 0.0018026 | 76.0908
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | CABLE TERMINATOR | 1 | 3 | 297 | 0.00026702 | 2.6972e-06 | 99
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | POLE | 5 | 5 | 600 | 0.00054576 | 4.548e-06 | 120
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WW | NONE | 5 | 55 | 4581 | 0.0041186 | 4.9448e-05 | 83.2909
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 18 | 1332 | 0.0012116 | 1.6373e-05 | 74
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ABI | ARRESTER | 21 | 1930 | 190412 | 0.17119 | 0.0017352 | 98.6591
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 3 | 10 | 1204 | 0.0010825 | 8.9905e-06 | 120.4
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | WL | NONE | 8 | 3924 | 250924 | 0.22559 | 0.0035279 | 63.946
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | SWITCH, OH | 4 | 1166 | 23443 | 0.021076 | 0.0010483 | 20.1055
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | POLE | 1 | 1 | 108 | 9.9e-05 | 9.1666e-07 | 108
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | CAPACITOR | 1 | 129 | 3999 | 0.003704 | 0.00011949 | 31
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 1944 | 337427 | 0.30931 | 0.001782 | 173.5736
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 89 | 8.0016e-05 | 8.9905e-07 | 89
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | WU | TRANSFORMER, STATION SERVICE | 3 | 103 | 7107 | 0.006674 | 9.6725e-05 | 69
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 136 | 10744 | 0.010089 | 0.00012771 | 79
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | TRANSFORMER, OH | 2 | 12 | 953 | 0.0008568 | 1.0789e-05 | 79.4167
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 2 | 3 | 564 | 0.00050707 | 2.6972e-06 | 188
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | BREAKER | 1 | 1 | 284 | 0.00025533 | 8.9905e-07 | 284
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ERF | POLE | 1 | 15 | 1620 | 0.0014565 | 1.3486e-05 | 108
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | ERO | NONE | 2 | 1031 | 43302 | 0.038931 | 0.00092692 | 42
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | POLE | 1 | 1 | 220 | 0.0002066 | 9.3908e-07 | 220
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ERF | METERING | 3 | 3 | 101 | 9.0804e-05 | 2.6972e-06 | 33.6667
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WU | ARRESTER | 1 | 1 | 261 | 0.00023465 | 8.9905e-07 | 261
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 715 | 72369 | 0.065063 | 0.00064282 | 101.2154
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 20 | 1.7981e-05 | 8.9905e-07 | 20
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 1 | 227 | 0.00021317 | 9.3908e-07 | 227
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | WL | REGULATOR | 2 | 1218 | 113276 | 0.10384 | 0.0011165 | 93.0016
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 1 | 127 | 0.00011418 | 8.9905e-07 | 127
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | TRANSFORMER, OH | 1 | 2 | 704 | 0.00064035 | 1.8192e-06 | 352
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | U | NONE | 3932 | 143253 | 8353072 | 7.737 | 0.13269 | 58.3099
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | CUTOUT | 437 | 12376 | 1531725 | 1.4041 | 0.011345 | 123.7658
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | CUTOUT | 17 | 175 | 20224 | 0.018539 | 0.00016042 | 115.5657
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | TRANSFORMER, UG | 8 | 77 | 16594 | 0.01537 | 7.1321e-05 | 215.5065
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | FUSE | 11 | 569 | 35575 | 0.03261 | 0.00052158 | 62.522
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 13 | 3259 | 116383 | 0.1078 | 0.0030186 | 35.7113
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | WL | NONE | 21 | 8180 | 1355520 | 1.2426 | 0.0074983 | 165.7115
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 85 | 85 | 12100 | 0.011208 | 7.8731e-05 | 142.3529
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 51 | 17331 | 2409204 | 2.2315 | 0.016053 | 139.0113
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | CONN/CLAMP | 111 | 345 | 53731 | 0.049253 | 0.00031625 | 155.742
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | ARRESTER | 155 | 2845 | 616900 | 0.5714 | 0.0026352 | 216.8366
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | METERING | 3 | 3 | 106 | 9.7166e-05 | 2.75e-06 | 35.3333
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERO | NONE | 3 | 9 | 402 | 0.00037235 | 8.3362e-06 | 44.6667
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | CONDUCTOR UG | 111 | 353 | 106641 | 0.098775 | 0.00032696 | 302.0992
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 11 | 3212 | 0.0030163 | 1.033e-05 | 292
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | NONE | 289 | 10861 | 843632 | 0.79224 | 0.010199 | 77.6754
AEP-TX | 2020 | 1064875 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 8 | 56 | 7225 | 0.0067848 | 5.2588e-05 | 129.0179
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | POLE | 291 | 67999 | 7678412 | 7.2106 | 0.063856 | 112.9195
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 167 | 370 | 38176 | 0.03585 | 0.00034746 | 103.1784
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | CONN/CLAMP | 5 | 95 | 29282 | 0.027122 | 8.7993e-05 | 308.2316
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WW | NONE | 2 | 2 | 170 | 0.00015746 | 1.8525e-06 | 85
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | SWITCH, UG | 2 | 91 | 3305 | 0.0030612 | 8.4288e-05 | 36.3187
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1524 | 19267 | 1656370 | 1.5066 | 0.017525 | 85.9693
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | FUSE | 7 | 22 | 2001 | 0.0018201 | 2.0011e-05 | 90.9545
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | ARRESTER | 6 | 7 | 1966 | 0.001821 | 6.4837e-06 | 280.8571
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AF | RELAY | 3 | 1654 | 34798 | 0.032231 | 0.001532 | 21.0387
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | CROSSARM | 32 | 7347 | 1403126 | 1.3176 | 0.0068994 | 190.9794
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 2359 | 561578 | 0.52737 | 0.0022153 | 238.0577
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 37 | 4107 | 0.0037647 | 3.3917e-05 | 111
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | TRANSFORMER, OH | 6 | 39 | 30820 | 0.028942 | 3.6624e-05 | 790.2564
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | POLE HARDWARE | 9 | 1352 | 111668 | 0.10486 | 0.0012696 | 82.5947
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | TRANSFORMER, OH | 2 | 3 | 670 | 0.00061416 | 2.75e-06 | 223.3333
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | JUMPER/RISER | 1 | 1 | 54 | 5.0017e-05 | 9.2624e-07 | 54
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | WU | NONE | 29 | 24464 | 2086292 | 1.9592 | 0.022974 | 85.2801
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | PEDESTAL | 1 | 1 | 1151 | 0.0010469 | 9.0959e-07 | 1151
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 2 | 389 | 0.0003653 | 1.8782e-06 | 194.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | CONN/CLAMP | 4 | 31 | 6821 | 0.0061324 | 2.7871e-05 | 220.0323
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 25 | 951 | 102698 | 0.092331 | 0.000855 | 107.9895
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 29 | 29 | 2648 | 0.0023807 | 2.6073e-05 | 91.3103
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 160 | 20741 | 0.018647 | 0.00014385 | 129.6312
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 6 | 480 | 0.00043154 | 5.3943e-06 | 80
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 15 | 64 | 9323 | 0.0083819 | 5.7539e-05 | 145.6719
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WW | JUMPER/RISER | 2 | 3 | 588 | 0.00052864 | 2.6972e-06 | 196
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | CF | ARRESTER | 2 | 196 | 17168 | 0.015435 | 0.00017621 | 87.5918
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | CF | SWITCH, OH | 2 | 2114 | 132167 | 0.12412 | 0.0019852 | 62.5199
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | ARRESTER | 4 | 46 | 3802 | 0.0034182 | 4.1356e-05 | 82.6522
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TOR | SPLICE, OH | 2 | 2 | 111 | 9.9795e-05 | 1.7981e-06 | 55.5
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 1 | 88 | 17072 | 0.015813 | 8.1509e-05 | 194
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | CABLE TERMINATOR | 2 | 5 | 1070 | 0.00096199 | 4.4953e-06 | 214
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 11 | 815 | 138999 | 0.12497 | 0.00073273 | 170.5509
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 17 | 4301 | 0.0038668 | 1.5284e-05 | 253
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | AF | POLE HARDWARE | 1 | 67 | 3953 | 0.003554 | 6.0236e-05 | 59
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 6 | 534 | 0.00048009 | 5.3943e-06 | 89
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 2 | 194 | 0.00017442 | 1.7981e-06 | 97
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 1049 | 58744 | 0.052814 | 0.00094311 | 56
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 132 | 0.00012226 | 9.2624e-07 | 132
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 284 | 0.00026305 | 9.2624e-07 | 284
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WL | CUTOUT | 1 | 36 | 10152 | 0.0095335 | 3.3807e-05 | 282
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 538 | 17291 | 3480475 | 3.1904 | 0.01585 | 201.2882
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | JUMPER/RISER | 68 | 2639 | 314469 | 0.28826 | 0.0024191 | 119.1622
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | METERING | 1911 | 2088 | 194278 | 0.17995 | 0.001934 | 93.045
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 370 | 386 | 60360 | 0.05533 | 0.00035383 | 156.3731
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | NONE | 587 | 10974 | 834989 | 0.7734 | 0.010165 | 76.0879
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 7 | 40 | 7666 | 0.0070271 | 3.6667e-05 | 191.65
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 72 | 21947 | 3674169 | 3.368 | 0.020118 | 167.411
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | JUMPER/RISER | 2 | 4 | 1001 | 0.00092717 | 3.705e-06 | 250.25
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AO | NONE | 24 | 10672 | 788410 | 0.72271 | 0.0097826 | 73.8765
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 1 | 127 | 0.00011642 | 9.1666e-07 | 127
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 19 | 249 | 59693 | 0.054718 | 0.00022825 | 239.7309
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | CONN/CLAMP | 45 | 683 | 77558 | 0.071837 | 0.00063262 | 113.5549
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | REGULATOR | 1 | 791 | 59325 | 0.054949 | 0.00073266 | 75
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | ARRESTER | 5 | 7 | 1690 | 0.0015492 | 6.4166e-06 | 241.4286
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 5 | 17 | 4217 | 0.0038656 | 1.5583e-05 | 248.0588
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | POLE HARDWARE | 11 | 2850 | 287722 | 0.26374 | 0.0026125 | 100.9551
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 118 | 859 | 115700 | 0.10865 | 0.00080667 | 134.6915
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | CUTOUT | 16 | 492 | 134054 | 0.12589 | 0.00046203 | 272.4675
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | CROSSARM | 20 | 7227 | 655020 | 0.61511 | 0.0067867 | 90.6351
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | JUMPER/RISER | 11 | 57 | 8771 | 0.0082366 | 5.3527e-05 | 153.8772
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 99 | 14896 | 0.013988 | 9.2969e-05 | 150.4646
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 8 | 71 | 13098 | 0.0123 | 6.6674e-05 | 184.4789
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WFS | CONDUCTOR UG | 1 | 1 | 279 | 0.00025842 | 9.2624e-07 | 279
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | TRANSFORMER, OH | 76 | 315 | 92235 | 0.083896 | 0.00028652 | 292.8095
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | METERING | 1196 | 1389 | 121329 | 0.11036 | 0.0012634 | 87.3499
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | POLE | 2 | 1189 | 48950 | 0.044871 | 0.0010899 | 41.169
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | AB | NONE | 4 | 1647 | 128087 | 0.12028 | 0.0015467 | 77.7699
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | POLE | 9 | 4588 | 688528 | 0.63774 | 0.0042496 | 150.0715
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | SPLICE, OH | 4 | 11 | 3705 | 0.0033962 | 1.0083e-05 | 336.8182
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 1272 | 125568 | 0.11631 | 0.0011782 | 98.717
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | BREAKER | 3 | 3920 | 1189393 | 1.1017 | 0.0036309 | 303.4166
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 2 | 77 | 18767 | 0.017383 | 7.1321e-05 | 243.7273
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | POLE | 61 | 11364 | 2449994 | 2.2285 | 0.010337 | 215.5926
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | INSULATOR | 22 | 671 | 127581 | 0.11605 | 0.00061034 | 190.1356
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | CROSSARM | 289 | 33517 | 5128330 | 4.6106 | 0.030134 | 153.0068
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 4 | 18 | 1000 | 0.00090959 | 1.6373e-05 | 55.5556
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | CONDUCTOR UG | 3 | 14 | 7410 | 0.0067925 | 1.2833e-05 | 529.2857
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 138 | 138 | 18245 | 0.016403 | 0.00012407 | 132.2101
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | NONE | 159 | 27573 | 2601805 | 2.3392 | 0.02479 | 94.3606
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | JUMPER/RISER | 11 | 56 | 7159 | 0.006631 | 5.187e-05 | 127.8393
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WW | NONE | 17 | 43 | 10969 | 0.0099773 | 3.9113e-05 | 255.093
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | METERING | 1 | 3 | 282 | 0.0002585 | 2.75e-06 | 94
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | POLE | 5 | 3910 | 179351 | 0.16842 | 0.0036718 | 45.8698
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | ARRESTER | 30 | 87 | 10553 | 0.0099101 | 8.17e-05 | 121.2989
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 2093 | 197686 | 0.1831 | 0.0019386 | 94.451
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 19 | 706 | 175916 | 0.16001 | 0.00064217 | 249.1728
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 13 | 35 | 5470 | 0.0051368 | 3.2868e-05 | 156.2857
AEP-TX | 2024 | 1112283 | PARTIAL POWER | U | NONE | 100 | 233 | 23686 | 0.021295 | 0.00020948 | 101.6567
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 4 | 2221 | 272835 | 0.25621 | 0.0020857 | 122.8433
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | ARRESTER | 2 | 1860 | 18600 | 0.017467 | 0.0017467 | 10
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 1 | 216 | 0.00019647 | 9.0959e-07 | 216
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | CROSSARM | 6 | 633 | 63876 | 0.059985 | 0.00059444 | 100.91
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | SWITCH, OH | 4 | 3614 | 278092 | 0.25295 | 0.0032873 | 76.9485
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TOR | SPLICE, OH | 5 | 5 | 615 | 0.00055292 | 4.4953e-06 | 123
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | SWITCH, OH | 18 | 10810 | 1403522 | 1.2618 | 0.0097187 | 129.8355
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | METERING | 5 | 5 | 708 | 0.00065578 | 4.6312e-06 | 141.6
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | JUMPER/RISER | 5 | 907 | 66309 | 0.060783 | 0.00083141 | 73.108
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 6 | 27 | 4120 | 0.0037041 | 2.4274e-05 | 152.5926
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | CONDUCTOR UG | 14 | 35 | 10512 | 0.0094508 | 3.1467e-05 | 300.3429
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 1 | 103 | 9.2602e-05 | 8.9905e-07 | 103
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 212 | 45594 | 0.040991 | 0.0001906 | 215.066
AEP-TX | 2025 | 1112283 | PARTIAL POWER | FO | NONE | 3 | 11 | 1312 | 0.0011796 | 9.8896e-06 | 119.2727
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | CUTOUT | 13 | 101 | 8489 | 0.0076321 | 9.0804e-05 | 84.0495
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | POLE | 10 | 66 | 17690 | 0.015904 | 5.9337e-05 | 268.0303
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | CUTOUT | 15 | 1728 | 34759 | 0.03125 | 0.0015536 | 20.1152
AEP-TX | 2023 | 1099391 | PARTIAL POWER | OL | SPLICE, OH | 1 | 12 | 2856 | 0.0025978 | 1.0915e-05 | 238
AEP-TX | 2024 | 1112283 | PARTIAL POWER | OL | SPLICE, OH | 1 | 1 | 55 | 4.9448e-05 | 8.9905e-07 | 55
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | METERING | 4 | 6 | 394 | 0.00037 | 5.6345e-06 | 65.6667
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | TRANSFORMER, UG | 1 | 7 | 147 | 0.00013804 | 6.5735e-06 | 21
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 4 | 148 | 0.00013567 | 3.6667e-06 | 37
AEP-TX | 2020 | 1064875 | PARTIAL POWER | ABI | TRANSFORMER, OH | 1 | 1 | 49 | 4.6015e-05 | 9.3908e-07 | 49
AEP-TX | 2025 | 1112283 | PARTIAL POWER | VA | NONE | 1 | 6 | 1266 | 0.0011382 | 5.3943e-06 | 211
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | TRANSFORMER, GROUNDING | 1 | 1 | 117 | 0.00010519 | 8.9905e-07 | 117
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 119 | 0.00010699 | 8.9905e-07 | 119
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | CAPACITOR | 1 | 1 | 222 | 0.00019959 | 8.9905e-07 | 222
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | ARRESTER | 1 | 1 | 30 | 2.6972e-05 | 8.9905e-07 | 30
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | METERING | 5 | 15 | 3581 | 0.0032195 | 1.3486e-05 | 238.7333
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 148 | 53428 | 0.048035 | 0.00013306 | 361
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 2 | 45 | 18810 | 0.016911 | 4.0457e-05 | 418
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WW | NONE | 1 | 1 | 46 | 4.3198e-05 | 9.3908e-07 | 46
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 11 | 3289 | 0.0029917 | 1.0006e-05 | 299
AEP-TX | 2020 | 1064875 | PARTIAL POWER | ERF | NONE | 2 | 2 | 139 | 0.00013053 | 1.8782e-06 | 69.5
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 2070 | 98820 | 0.091531 | 0.0019173 | 47.7391
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | WL | CROSSARM | 2 | 58 | 4012 | 0.003607 | 5.2145e-05 | 69.1724
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 1415 | 139504 | 0.12788 | 0.0012971 | 98.5894
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 1 | 31 | 23312 | 0.021593 | 2.8713e-05 | 752
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | SWITCH, OH | 1 | 1254 | 24768 | 0.022268 | 0.0011274 | 19.7512
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | NONE | 2860 | 70396 | 9310091 | 8.5342 | 0.064529 | 132.2531
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | CONN/CLAMP | 1198 | 2670 | 323051 | 0.29922 | 0.0024731 | 120.9929
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 99 | 20096 | 2354928 | 2.1812 | 0.018614 | 117.1839
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | SWITCH, OH | 22 | 9638 | 543738 | 0.49842 | 0.0088348 | 56.4161
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | CUTOUT | 7 | 23 | 2428 | 0.0022489 | 2.1304e-05 | 105.5652
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | CUTOUT | 460 | 13636 | 1846475 | 1.7103 | 0.01263 | 135.4118
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 6 | 178 | 53472 | 0.049528 | 0.00016487 | 300.4045
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 5 | 93 | 19223 | 0.017621 | 8.525e-05 | 206.6989
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AO | ARRESTER | 3 | 1914 | 194448 | 0.17824 | 0.0017545 | 101.5925
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 19 | 5459 | 877706 | 0.81297 | 0.0050564 | 160.7815
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 674 | 22229 | 4074688 | 3.8264 | 0.020875 | 183.3051
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | POLE | 354 | 24504 | 3000719 | 2.8179 | 0.023011 | 122.4583
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 36 | 3.2366e-05 | 8.9905e-07 | 36
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 1 | 13 | 3328 | 0.002992 | 1.1688e-05 | 256
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | NONE | 243 | 2625 | 296113 | 0.27144 | 0.0024062 | 112.805
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 42 | 6835 | 0.0062654 | 3.85e-05 | 162.7381
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | CUTOUT | 9 | 74 | 8334 | 0.0077193 | 6.8542e-05 | 112.6216
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 10 | 96 | 18414 | 0.016879 | 8.8e-05 | 191.8125
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | NONE | 177 | 35900 | 3540478 | 3.2454 | 0.032908 | 98.6206
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | CONN/CLAMP | 80 | 449 | 48331 | 0.044303 | 0.00041158 | 107.6414
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 23 | 7146 | 854299 | 0.7831 | 0.0065505 | 119.5493
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WU | NONE | 66 | 125 | 13274 | 0.012168 | 0.00011458 | 106.192
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 10 | 152 | 22719 | 0.021043 | 0.00014079 | 149.4671
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | POLE | 20 | 373 | 80859 | 0.07412 | 0.00034192 | 216.7802
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | ARRESTER | 323 | 6668 | 755744 | 0.7097 | 0.0062618 | 113.3389
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | CONN/CLAMP | 985 | 1977 | 220558 | 0.20712 | 0.0018566 | 111.562
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | SPLICE, OH | 3 | 13 | 2154 | 0.0019745 | 1.1917e-05 | 165.6923
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 10 | 959 | 0.00090058 | 9.3908e-06 | 95.9
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | ABI | NONE | 14 | 8163 | 891905 | 0.82612 | 0.0075609 | 109.2619
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WU | NONE | 62 | 97 | 10444 | 0.0096737 | 8.9845e-05 | 107.6701
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | REGULATOR | 5 | 1529 | 16884 | 0.015477 | 0.0014016 | 11.0425
AEP-TX | 2021 | 1079632 | PARTIAL POWER | VA | NONE | 4 | 158 | 12497 | 0.011575 | 0.00014635 | 79.0949
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ABI | SWITCH, OH | 2 | 869 | 44769 | 0.040722 | 0.00079044 | 51.5178
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | JUMPER/RISER | 8 | 93 | 9649 | 0.0090612 | 8.7334e-05 | 103.7527
AEP-TX | 2023 | 1099391 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 5 | 150 | 0.00013644 | 4.548e-06 | 30
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 506 | 86186 | 0.079003 | 0.00046383 | 170.3281
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AF | CIRCUIT SWITCHER | 1 | 221 | 11934 | 0.011054 | 0.0002047 | 54
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | PEDESTAL | 6 | 28 | 7284 | 0.006677 | 2.5667e-05 | 260.1429
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 127 | 127 | 18992 | 0.017275 | 0.00011552 | 149.5433
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 176 | 993 | 293035 | 0.26654 | 0.00090323 | 295.1007
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 6 | 1182 | 80742 | 0.073442 | 0.0010751 | 68.3096
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | METERING | 14 | 16 | 5008 | 0.0045552 | 1.4554e-05 | 313
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 82 | 13326 | 1144924 | 1.0293 | 0.011981 | 85.9166
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | POLE | 24 | 1269 | 483921 | 0.44017 | 0.0011543 | 381.3404
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WW | NONE | 4 | 50 | 4413 | 0.0040452 | 4.5833e-05 | 88.26
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | NONE | 12 | 23 | 1722 | 0.0016171 | 2.1599e-05 | 74.8696
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WU | CONN/CLAMP | 7 | 14 | 1324 | 0.0012043 | 1.2734e-05 | 94.5714
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | RELAY | 1 | 503 | 15090 | 0.013726 | 0.00045753 | 30
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | ARRESTER | 22 | 295 | 17107 | 0.01538 | 0.00026522 | 57.9898
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | CUTOUT | 24 | 82 | 8129 | 0.0073084 | 7.3722e-05 | 99.1341
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 567 | 24318 | 0.02212 | 0.00051574 | 42.8889
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 15 | 52 | 7738 | 0.0069569 | 4.6751e-05 | 148.8077
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | SWITCH, UG | 1 | 352 | 3520 | 0.0031647 | 0.00031647 | 10
AEP-TX | 2024 | 1112283 | PARTIAL POWER | A | NONE | 94 | 351 | 24381 | 0.02192 | 0.00031557 | 69.4615
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | JUMPER/RISER | 65 | 1836 | 246794 | 0.22188 | 0.0016507 | 134.4194
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 10 | 1760 | 0.0016009 | 9.0959e-06 | 176
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 320 | 0.00029107 | 1.8192e-06 | 160
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | FUSE | 3 | 12 | 939 | 0.00088179 | 1.1269e-05 | 78.25
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | NONE | 42 | 257 | 24236 | 0.021789 | 0.00023106 | 94.3035
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | NONE | 705 | 9839 | 972015 | 0.87389 | 0.0088458 | 98.7921
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | ARRESTER | 36 | 265 | 28000 | 0.025173 | 0.00023825 | 105.6604
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | CROSSARM | 10 | 152 | 23366 | 0.021007 | 0.00013666 | 153.7237
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | CF | JUMPER/RISER | 1 | 2095 | 206679 | 0.18582 | 0.0018835 | 98.6535
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 1532 | 154732 | 0.13911 | 0.0013773 | 101
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WU | TRANSFORMER, OH | 1 | 1 | 190 | 0.00017082 | 8.9905e-07 | 190
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 775 | 64103 | 0.060198 | 0.00072778 | 82.7135
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 9 | 1170 | 0.0010725 | 8.25e-06 | 130
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | METERING | 1 | 1 | 211 | 0.00019192 | 9.0959e-07 | 211
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 12 | 19200 | 0.01803 | 1.1269e-05 | 1600
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 4 | 212 | 0.00019908 | 3.7563e-06 | 53
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | STATIC WIRE | 1 | 18 | 3888 | 0.0036511 | 1.6903e-05 | 216
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 163 | 35860 | 0.03224 | 0.00014655 | 220
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 154 | 0.00013845 | 1.7981e-06 | 77
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | POLE | 1 | 1 | 260 | 0.00023375 | 8.9905e-07 | 260
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | UB | TRANSFORMER, UG | 1 | 1 | 102 | 9.5786e-05 | 9.3908e-07 | 102
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 1 | 397 | 0.00035692 | 8.9905e-07 | 397
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | TRANSFORMER, OH | 2 | 29 | 4308 | 0.0038731 | 2.6073e-05 | 148.5517
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WFS | METERING | 2 | 2 | 77 | 6.9227e-05 | 1.7981e-06 | 38.5
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WU | CUTOUT | 1 | 1 | 161 | 0.00014475 | 8.9905e-07 | 161
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 8 | 1072 | 0.00096378 | 7.1924e-06 | 134
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 15 | 1965 | 0.0018201 | 1.3894e-05 | 131
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 143 | 0.00013108 | 9.1666e-07 | 143
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 8 | 1376 | 0.0012371 | 7.1924e-06 | 172
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1087 | 6199 | 572255 | 0.52052 | 0.0056386 | 92.3141
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | NONE | 240 | 240 | 29380 | 0.026724 | 0.0002183 | 122.4167
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | CUTOUT | 34 | 189 | 32018 | 0.029656 | 0.00017506 | 169.4074
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 26 | 111 | 12667 | 0.011611 | 0.00010175 | 114.1171
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 10 | 3483 | 431322 | 0.39538 | 0.0031927 | 123.8363
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | CF | BREAKER | 7 | 6790 | 755422 | 0.69247 | 0.0062241 | 111.2551
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | POLE | 44 | 13978 | 1420853 | 1.3024 | 0.012813 | 101.6492
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | POLE | 19 | 2039 | 330371 | 0.30284 | 0.0018691 | 162.026
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | CONN/CLAMP | 23 | 34 | 3948 | 0.0037075 | 3.1929e-05 | 116.1176
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ABI | ARRESTER | 8 | 1254 | 101367 | 0.092919 | 0.0011495 | 80.8349
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | CONDUCTOR UG | 83 | 158 | 31846 | 0.029906 | 0.00014837 | 201.557
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 176 | 176 | 24433 | 0.022944 | 0.00016528 | 138.8239
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | PEDESTAL | 4 | 29 | 6176 | 0.0057997 | 2.7233e-05 | 212.9655
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | PEDESTAL | 4 | 4 | 703 | 0.00066017 | 3.7563e-06 | 175.75
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | INSULATOR | 89 | 13082 | 1694972 | 1.57 | 0.012117 | 129.5652
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 7 | 514 | 31968 | 0.02961 | 0.00047609 | 62.1946
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | RECLOSER, LINE/OCR/BR | 1 | 1638 | 276208 | 0.25584 | 0.0015172 | 168.6252
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 89 | 8.2435e-05 | 9.2624e-07 | 89
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | SPLICE, OH | 17 | 207 | 48236 | 0.044216 | 0.00018975 | 233.0242
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 1 | 264 | 16632 | 0.015405 | 0.00024453 | 63
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 4 | 997 | 0.00093626 | 3.7563e-06 | 249.25
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | FO | NONE | 108 | 9932 | 862317 | 0.78436 | 0.0090341 | 86.8221
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 99 | 9702 | 0.0088935 | 9.075e-05 | 98
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | NONE | 315 | 2216 | 198786 | 0.18081 | 0.0020157 | 89.7049
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 3 | 313 | 0.00028991 | 2.7787e-06 | 104.3333
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 211 | 21151 | 0.019591 | 0.00019544 | 100.2417
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 26 | 3012 | 0.002761 | 2.3833e-05 | 115.8462
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 2 | 47 | 22287 | 0.020643 | 4.3533e-05 | 474.1915
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | RECLOSER, LINE/OCR/BR | 1 | 1 | 126 | 0.00011671 | 9.2624e-07 | 126
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | METERING | 4 | 4 | 325 | 0.00029792 | 3.6667e-06 | 81.25
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 27 | 1469 | 0.0013362 | 2.4559e-05 | 54.4074
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 10 | 14667 | 2346902 | 2.2039 | 0.013773 | 160.0124
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | ARRESTER | 14 | 147 | 9644 | 0.0090565 | 0.00013804 | 65.6054
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 3 | 57 | 5.2796e-05 | 2.7787e-06 | 19
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VIN | ARRESTER | 3 | 3 | 242 | 0.00022726 | 2.8172e-06 | 80.6667
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | ARRESTER | 12 | 319 | 50917 | 0.046314 | 0.00029016 | 159.6144
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | INSULATOR | 2 | 21 | 3903 | 0.0035501 | 1.9101e-05 | 185.8571
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | POLE | 15 | 341 | 43176 | 0.039273 | 0.00031017 | 126.6158
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | CROSSARM | 5 | 94 | 29368 | 0.027202 | 8.7067e-05 | 312.4255
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | ARRESTER | 24 | 656 | 43157 | 0.0388 | 0.00058978 | 65.7881
AEP-TX | 2022 | 1090914 | PARTIAL POWER | VIN | CONN/CLAMP | 3 | 18 | 1242 | 0.0011385 | 1.65e-05 | 69
AEP-TX | 2024 | 1112283 | PARTIAL POWER | FO | NONE | 13 | 55 | 3552 | 0.0031934 | 4.9448e-05 | 64.5818
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | POLE | 52 | 7898 | 1239857 | 1.1147 | 0.0071007 | 156.9837
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 16 | 5656 | 388983 | 0.34972 | 0.005085 | 68.7735
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 17 | 234 | 79416 | 0.071399 | 0.00021038 | 339.3846
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 2 | 8 | 242 | 0.00021757 | 7.1924e-06 | 30.25
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TR | NONE | 15 | 4198 | 245363 | 0.22059 | 0.0037742 | 58.4476
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | POLE HARDWARE | 2 | 23 | 4944 | 0.004532 | 2.1083e-05 | 214.9565
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | INSULATOR | 23 | 671 | 61069 | 0.054904 | 0.00060326 | 91.0119
AEP-TX | 2023 | 1099391 | PARTIAL POWER | VIN | ARRESTER | 1 | 3 | 276 | 0.00025105 | 2.7288e-06 | 92
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ABI | NONE | 68 | 3930 | 175240 | 0.15755 | 0.0035333 | 44.5903
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | INSULATOR | 1 | 1 | 224 | 0.00020139 | 8.9905e-07 | 224
AEP-TX | 2020 | 1064875 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 102 | 9.5786e-05 | 9.3908e-07 | 102
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TIR | ARRESTER | 1 | 2 | 322 | 0.00028949 | 1.7981e-06 | 161
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 3 | 259 | 0.00023285 | 2.6972e-06 | 86.3333
AEP-TX | 2024 | 1112283 | PARTIAL POWER | A | CONN/CLAMP | 1 | 5 | 1020 | 0.00091703 | 4.4953e-06 | 204
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | SPLICE, OH | 1 | 3 | 639 | 0.00060007 | 2.8172e-06 | 213
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 32 | 9660 | 0.0086848 | 2.877e-05 | 301.875
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 34 | 6086 | 0.0054716 | 3.0568e-05 | 179
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | ABI | RECLOSER, LINE/OCR/BR | 1 | 1016 | 61976 | 0.05572 | 0.00091344 | 61
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VIN | NONE | 186 | 2084 | 222996 | 0.20655 | 0.0019303 | 107.0038
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | ARRESTER | 15 | 2280 | 120844 | 0.11077 | 0.00209 | 53.0018
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | NONE | 113 | 3112 | 396519 | 0.36347 | 0.0028527 | 127.4161
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 57 | 540 | 113973 | 0.10447 | 0.000495 | 211.0611
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | FO | NONE | 128 | 9152 | 586344 | 0.5431 | 0.008477 | 64.0673
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | CUTOUT | 26 | 195 | 24367 | 0.022336 | 0.00017875 | 124.959
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | FUSE | 20 | 170 | 13827 | 0.012985 | 0.00015964 | 81.3353
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 4 | 21 | 5881 | 0.0055227 | 1.9721e-05 | 280.0476
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | ARRESTER | 12 | 208 | 15533 | 0.014387 | 0.00019266 | 74.6779
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 702 | 21472 | 0.019888 | 0.00065022 | 30.5869
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WU | CONN/CLAMP | 4 | 20 | 3291 | 0.0030167 | 1.8333e-05 | 164.55
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | SPLICE, OH | 9 | 13 | 2847 | 0.002637 | 1.2041e-05 | 219
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 19 | 314 | 81032 | 0.076095 | 0.00029487 | 258.0637
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 297 | 29491 | 3227014 | 2.9353 | 0.026825 | 109.4237
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | SPLICE, OH | 5 | 13 | 4128 | 0.0037548 | 1.1825e-05 | 317.5385
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | JUMPER/RISER | 9 | 71 | 16862 | 0.015338 | 6.4581e-05 | 237.493
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 19 | 185 | 39341 | 0.036944 | 0.00017373 | 212.6541
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 3 | 3 | 246 | 0.00022376 | 2.7288e-06 | 82
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | NONE | 3802 | 139443 | 13597477 | 12.2248 | 0.12537 | 97.5128
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | CROSSARM | 1 | 19 | 3781 | 0.0033993 | 1.7082e-05 | 199
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | NONE | 1497 | 15817 | 1081554 | 0.97237 | 0.01422 | 68.3792
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AO | NONE | 24 | 12844 | 595614 | 0.55168 | 0.011897 | 46.3729
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | METERING | 5 | 5 | 1156 | 0.0010515 | 4.548e-06 | 231.2
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | PEDESTAL | 5 | 46 | 8442 | 0.0079277 | 4.3198e-05 | 183.5217
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 6 | 9 | 2568 | 0.002354 | 8.25e-06 | 285.3333
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 1175 | 79084 | 0.072493 | 0.0010771 | 67.3055
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | FUSE | 1 | 1 | 597 | 0.00055297 | 9.2624e-07 | 597
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | ARRESTER | 4 | 6 | 597 | 0.00054303 | 5.4576e-06 | 99.5
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 2 | 349 | 0.00032326 | 1.8525e-06 | 174.5
AEP-TX | 2024 | 1112283 | PARTIAL POWER | ABI | NONE | 45 | 168 | 10405 | 0.0093546 | 0.00015104 | 61.9345
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TOR | NONE | 40 | 40 | 4427 | 0.0039801 | 3.5962e-05 | 110.675
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | JUMPER/RISER | 12 | 245 | 35246 | 0.031688 | 0.00022027 | 143.8612
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | PEDESTAL | 3 | 14 | 1490 | 0.0013553 | 1.2734e-05 | 106.4286
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 10 | 44 | 7503 | 0.0068247 | 4.0022e-05 | 170.5227
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AF | NONE | 10 | 773 | 46649 | 0.042432 | 0.00070312 | 60.348
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 2 | 14 | 518 | 0.00048644 | 1.3147e-05 | 37
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 6 | 2232 | 0.0020302 | 5.4576e-06 | 372
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 5 | 197 | 44737 | 0.041437 | 0.00018247 | 227.0914
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | SWITCH, UG | 4 | 22 | 1649 | 0.0014999 | 2.0011e-05 | 74.9545
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 9 | 26 | 2308 | 0.002075 | 2.3375e-05 | 88.7692
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | CUTOUT | 4 | 12 | 750 | 0.00070431 | 1.1269e-05 | 62.5
AEP-TX | 2023 | 1099391 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 4 | 14 | 2486 | 0.0022613 | 1.2734e-05 | 177.5714
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 115 | 1748 | 339343 | 0.30509 | 0.0015715 | 194.1322
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | CUTOUT | 172 | 3088 | 339762 | 0.30546 | 0.0027763 | 110.0266
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 173 | 3618 | 478224 | 0.42995 | 0.0032528 | 132.1791
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | POLE | 28 | 12272 | 1087551 | 0.97776 | 0.011033 | 88.6205
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | CROSSARM | 14 | 3650 | 656353 | 0.5901 | 0.0032815 | 179.8227
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 21 | 381 | 113458 | 0.102 | 0.00034254 | 297.79
AEP-TX | 2024 | 1112283 | PARTIAL POWER | OL | CUTOUT | 1 | 9 | 1017 | 0.00091434 | 8.0915e-06 | 113
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | SPLICE, UG | 3 | 17 | 2187 | 0.0019662 | 1.5284e-05 | 128.6471
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | FO | CONN/CLAMP | 3 | 141 | 13112 | 0.012313 | 0.00013241 | 92.9929
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | JUMPER/RISER | 3 | 158 | 20504 | 0.018434 | 0.00014205 | 129.7722
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 5 | 305 | 51020 | 0.04587 | 0.00027421 | 167.2787
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | SWITCH, UG | 5 | 5183 | 1168517 | 1.0629 | 0.0047144 | 225.4519
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | TRANSFORMER, GROUNDING | 1 | 7 | 938 | 0.0008532 | 6.3672e-06 | 134
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 1 | 193 | 0.00017352 | 8.9905e-07 | 193
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | SPLICE, OH | 1 | 1 | 102 | 9.5786e-05 | 9.3908e-07 | 102
AEP-TX | 2024 | 1112283 | PARTIAL POWER | A | ARRESTER | 2 | 2 | 54 | 4.8549e-05 | 1.7981e-06 | 27
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 74 | 8584 | 0.0077175 | 6.653e-05 | 116
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 122 | 0.00010968 | 8.9905e-07 | 122
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ERF | NONE | 2 | 347 | 12201 | 0.010969 | 0.00031197 | 35.1614
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | TRANSFORMER, UG | 1 | 27 | 2484 | 0.0022332 | 2.4274e-05 | 92
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 1 | 84 | 7.7804e-05 | 9.2624e-07 | 84
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | METERING | 1 | 176 | 28718 | 0.0266 | 0.00016302 | 163.1705
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | CUTOUT | 1 | 31 | 57381 | 0.053885 | 2.9111e-05 | 1851
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 9 | 1080 | 0.00098236 | 8.1864e-06 | 120
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | BREAKER | 1 | 1418 | 100678 | 0.094544 | 0.0013316 | 71
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | NONE | 4509 | 113438 | 15280518 | 14.1535 | 0.10507 | 134.7037
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | U | NONE | 2845 | 131458 | 8329835 | 7.6356 | 0.1205 | 63.365
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 127 | 127 | 21113 | 0.019353 | 0.00011642 | 166.2441
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 477 | 11082 | 2103925 | 1.9487 | 0.010265 | 189.8507
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 404 | 8222 | 1779885 | 1.619 | 0.0074787 | 216.4784
AEP-TX | 2021 | 1079632 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 8 | 1155 | 0.0010698 | 7.4099e-06 | 144.375
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 114 | 114 | 15274 | 0.014147 | 0.00010559 | 133.9825
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | ARRESTER | 27 | 46 | 9101 | 0.0083425 | 4.2166e-05 | 197.8478
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | NONE | 50 | 93 | 11354 | 0.010408 | 8.525e-05 | 122.086
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 9 | 68 | 12703 | 0.011929 | 6.3857e-05 | 186.8088
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WL | NONE | 83 | 458 | 86188 | 0.080937 | 0.0004301 | 188.1834
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | BREAKER | 17 | 15417 | 1045079 | 0.98141 | 0.014478 | 67.7874
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | INSULATOR | 11 | 516 | 85302 | 0.07901 | 0.00047794 | 165.314
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | ARRESTER | 11 | 294 | 40905 | 0.037496 | 0.0002695 | 139.1327
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 1 | 3 | 450 | 0.00041681 | 2.7787e-06 | 150
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TIR | SPLICE, OH | 3 | 6 | 374 | 0.00034283 | 5.5e-06 | 62.3333
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | POLE HARDWARE | 6 | 112 | 4079 | 0.0037391 | 0.00010267 | 36.4196
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | CONN/CLAMP | 8 | 29 | 2734 | 0.0025062 | 2.6583e-05 | 94.2759
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | JUMPER/RISER | 32 | 448 | 43083 | 0.040458 | 0.00042071 | 96.1674
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 41 | 1929 | 302068 | 0.28367 | 0.0018115 | 156.5931
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WT | POLE | 2 | 17 | 7888 | 0.0074074 | 1.5964e-05 | 464
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | BREAKER | 1 | 5 | 50 | 4.6312e-05 | 4.6312e-06 | 10
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 186 | 357 | 49108 | 0.044668 | 0.00032473 | 137.5574
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AB | NONE | 7 | 8769 | 300176 | 0.27516 | 0.0080382 | 34.2315
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 55 | 245 | 36269 | 0.034059 | 0.00023007 | 148.0367
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | CONDUCTOR UG | 60 | 125 | 31546 | 0.028694 | 0.0001137 | 252.368
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | POLE | 372 | 20919 | 3630566 | 3.2641 | 0.018807 | 173.5535
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | FO | CUTOUT | 2 | 41 | 4020 | 0.0037235 | 3.7976e-05 | 98.0488
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ERF | NONE | 20 | 1421 | 80343 | 0.07308 | 0.0012925 | 56.5398
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | POLE HARDWARE | 15 | 3994 | 479132 | 0.43582 | 0.0036329 | 119.9629
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 81 | 553 | 109961 | 0.098861 | 0.00049718 | 198.8445
AEP-TX | 2020 | 1064875 | PARTIAL POWER | ERF | METERING | 2 | 3 | 878 | 0.00082451 | 2.8172e-06 | 292.6667
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | SPLICE, UG | 2 | 2 | 488 | 0.00044388 | 1.8192e-06 | 244
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WI | NONE | 6 | 1407 | 61840 | 0.056686 | 0.0012897 | 43.9517
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | SWITCH, OH | 1 | 1 | 371 | 0.00034008 | 9.1666e-07 | 371
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | ABX | NONE | 6 | 1849 | 205591 | 0.19043 | 0.0017126 | 111.1904
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | JUMPER/RISER | 22 | 120 | 13372 | 0.012022 | 0.00010789 | 111.4333
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VIN | METERING | 1 | 45 | 2655 | 0.0024592 | 4.1681e-05 | 59
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | SPLICE, OH | 3 | 27 | 11546 | 0.010502 | 2.4559e-05 | 427.6296
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WI | NONE | 11 | 80 | 5848 | 0.0052577 | 7.1924e-05 | 73.1
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | CROSSARM | 27 | 8856 | 910405 | 0.8185 | 0.007962 | 102.8009
AEP-TX | 2024 | 1112283 | PARTIAL POWER | A | METERING | 2 | 2 | 366 | 0.00032905 | 1.7981e-06 | 183
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CF | CONN/CLAMP | 15 | 66 | 8507 | 0.0076482 | 5.9337e-05 | 128.8939
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 130 | 0.00012041 | 9.2624e-07 | 130
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | CONDUCTOR UG | 17 | 43 | 7448 | 0.0066961 | 3.8659e-05 | 173.2093
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | FO | ARRESTER | 2 | 6 | 851 | 0.00076509 | 5.3943e-06 | 141.8333
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 1 | 60 | 5.3943e-05 | 8.9905e-07 | 60
AEP-TX | 2023 | 1099391 | PARTIAL POWER | OL | CONN/CLAMP | 39 | 170 | 27951 | 0.025424 | 0.00015463 | 164.4176
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | SPLICE, OH | 13 | 712 | 237777 | 0.21628 | 0.00064763 | 333.9565
AEP-TX | 2021 | 1079632 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 124 | 0.00011485 | 9.2624e-07 | 124
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 375 | 29292 | 0.026644 | 0.0003411 | 78.112
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 1842 | 81178 | 0.073839 | 0.0016755 | 44.0706
AEP-TX | 2024 | 1112283 | PARTIAL POWER | VA | NONE | 3 | 4 | 329 | 0.00029579 | 3.5962e-06 | 82.25
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | INSULATOR | 1 | 291 | 32883 | 0.029564 | 0.00026162 | 113
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | METERING | 42 | 45 | 3691 | 0.0033184 | 4.0457e-05 | 82.0222
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 6 | 1914 | 0.0017208 | 5.3943e-06 | 319
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | PEDESTAL | 5 | 39 | 11766 | 0.010578 | 3.5063e-05 | 301.6923
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | INSULATOR | 18 | 532 | 86285 | 0.077575 | 0.0004783 | 162.1898
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 4 | 485 | 0.00043604 | 3.5962e-06 | 121.25
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | CONN/CLAMP | 11 | 136 | 19297 | 0.017349 | 0.00012227 | 141.8897
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | CAPACITOR | 1 | 1503 | 48096 | 0.044088 | 0.0013777 | 32
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WI | NONE | 2 | 2 | 55 | 4.9448e-05 | 1.7981e-06 | 27.5
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 673 | 0.000632 | 1.8782e-06 | 336.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | CIRCUIT SWITCHER | 1 | 2874 | 145536 | 0.13667 | 0.0026989 | 50.6388
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | ARRESTER | 2 | 12 | 3577 | 0.0032159 | 1.0789e-05 | 298.0833
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | FUSE | 1 | 1 | 64 | 5.9279e-05 | 9.2624e-07 | 64
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 1 | 63 | 5.9162e-05 | 9.3908e-07 | 63
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | AF | JUMPER/RISER | 2 | 971 | 14565 | 0.013095 | 0.00087298 | 15
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 139 | 0.00012497 | 8.9905e-07 | 139
AEP-TX | 2024 | 1112283 | PARTIAL POWER | O | METERING | 1 | 1 | 74 | 6.653e-05 | 8.9905e-07 | 74
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | SPLICE, UG | 4 | 5 | 1305 | 0.0011733 | 4.4953e-06 | 261
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 3 | 516 | 0.00046391 | 2.6972e-06 | 172
AEP-TX | 2023 | 1099391 | PARTIAL POWER | A | CONN/CLAMP | 2 | 2 | 184 | 0.00016737 | 1.8192e-06 | 92
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | POLE | 2 | 1594 | 3957664 | 3.5581 | 0.0014331 | 2482.8507
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | CONN/CLAMP | 2 | 2 | 1784 | 0.0016039 | 1.7981e-06 | 892
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 46 | 12896 | 0.01173 | 4.1841e-05 | 280.3478
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | TRANSFORMER, GROUNDING | 1 | 15 | 3780 | 0.003465 | 1.375e-05 | 252
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ABI | RECLOSER, LINE/OCR/BR | 3 | 6165 | 463793 | 0.42186 | 0.0056077 | 75.23
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 7 | 357 | 0.00032473 | 6.3672e-06 | 51
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TR | METERING | 1 | 1 | 115 | 0.00010652 | 9.2624e-07 | 115
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | SPLICE, OH | 1 | 1 | 94 | 8.8273e-05 | 9.3908e-07 | 94
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 6 | 1734 | 0.0015772 | 5.4576e-06 | 289
AEP-TX | 2020 | 1064875 | PARTIAL POWER | OL | JUMPER/RISER | 1 | 19 | 3648 | 0.0034258 | 1.7842e-05 | 192
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | WU | OTHER EQUIPMENT | 2 | 873 | 178020 | 0.16717 | 0.00081981 | 203.9175
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | NONE | 739 | 12742 | 1276790 | 1.1614 | 0.01159 | 100.2033
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1087 | 115763 | 17035977 | 15.7794 | 0.10722 | 147.1625
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | JUMPER/RISER | 14 | 4615 | 909172 | 0.8334 | 0.0042304 | 197.0037
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 36 | 6386 | 748875 | 0.69364 | 0.005915 | 117.2682
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 5 | 451 | 81917 | 0.07509 | 0.00041341 | 181.6341
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | FO | NONE | 88 | 6460 | 481001 | 0.4517 | 0.0060664 | 74.4584
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 30 | 2.75e-05 | 9.1666e-07 | 30
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 4 | 101 | 29096 | 0.026671 | 9.2583e-05 | 288.0792
AEP-TX | 2020 | 1064875 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 145 | 0.00013617 | 1.8782e-06 | 72.5
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | ARRESTER | 13 | 115 | 21206 | 0.019642 | 0.00010652 | 184.4
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 3 | 170 | 92778 | 0.085046 | 0.00015583 | 545.7529
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WT | NONE | 3 | 14 | 1726 | 0.0015987 | 1.2967e-05 | 123.2857
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | PEDESTAL | 7 | 14 | 2708 | 0.0025083 | 1.2967e-05 | 193.4286
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | CUTOUT | 63 | 1400 | 186567 | 0.1752 | 0.0013147 | 133.2621
AEP-TX | 2022 | 1090914 | PARTIAL POWER | A | CONN/CLAMP | 2 | 2 | 236 | 0.00021633 | 1.8333e-06 | 118
AEP-TX | 2021 | 1079632 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 52 | 4.8165e-05 | 9.2624e-07 | 52
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | POLE | 11 | 225 | 122924 | 0.11386 | 0.0002084 | 546.3289
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | CROSSARM | 11 | 4732 | 782495 | 0.71728 | 0.0043376 | 165.3624
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 149 | 143848 | 0.13186 | 0.00013658 | 965.4228
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | CROSSARM | 38 | 9461 | 1005665 | 0.91475 | 0.0086057 | 106.2958
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | BREAKER | 6 | 6030 | 375753 | 0.34444 | 0.0055275 | 62.3139
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | BREAKER | 2 | 1788 | 236289 | 0.21886 | 0.0016561 | 132.1527
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | NONE | 3150 | 80410 | 10474971 | 9.4175 | 0.072293 | 130.2695
AEP-TX | 2020 | 1064875 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 4 | 4 | 382 | 0.00035873 | 3.7563e-06 | 95.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | POLE HARDWARE | 40 | 1618 | 215099 | 0.19339 | 0.0014547 | 132.9413
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | R | RELAY | 7 | 5628 | 308611 | 0.28071 | 0.0051192 | 54.8349
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | ARRESTER | 47 | 139 | 12270 | 0.011031 | 0.00012497 | 88.2734
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | CROSSARM | 8 | 367 | 81563 | 0.074189 | 0.00033382 | 222.2425
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 136 | 1360 | 0.001237 | 0.0001237 | 10
AEP-TX | 2021 | 1079632 | PARTIAL POWER | UB | NONE | 1 | 1 | 54 | 5.0017e-05 | 9.2624e-07 | 54
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | FO | NONE | 3 | 6777 | 644132 | 0.59662 | 0.0062771 | 95.0468
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | CROSSARM | 2 | 756 | 122346 | 0.11 | 0.00067968 | 161.8333
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | POLE | 3 | 3 | 465 | 0.00041806 | 2.6972e-06 | 155
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | NONE | 174 | 950 | 88436 | 0.079509 | 0.0008541 | 93.0905
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CF | NONE | 5 | 6 | 542 | 0.00048729 | 5.3943e-06 | 90.3333
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | ARRESTER | 7 | 8 | 2502 | 0.0022494 | 7.1924e-06 | 312.75
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | AF | NONE | 11 | 5916 | 243901 | 0.21928 | 0.0053188 | 41.2273
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 59 | 12324 | 1365530 | 1.2277 | 0.01108 | 110.8025
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 4 | 71 | 10240 | 0.0092063 | 6.3833e-05 | 144.2254
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 44 | 431 | 88402 | 0.079478 | 0.00038749 | 205.109
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 3178 | 373787 | 0.33605 | 0.0028572 | 117.6171
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | O | NONE | 2 | 2 | 510 | 0.00045852 | 1.7981e-06 | 255
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | AB | NONE | 8 | 5052 | 613909 | 0.55194 | 0.004542 | 121.518
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 506 | 0.00046868 | 1.8525e-06 | 253
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | RECLOSER, LINE/OCR/BR | 2 | 244 | 18787 | 0.017642 | 0.00022913 | 76.9959
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 4 | 1552 | 308657 | 0.2775 | 0.0013953 | 198.8769
AEP-TX | 2020 | 1064875 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 249 | 0.00023383 | 9.3908e-07 | 249
AEP-TX | 2025 | 1112283 | PARTIAL POWER | OL | TRANSFORMER, UG | 1 | 3 | 564 | 0.00050707 | 2.6972e-06 | 188
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | SPLICE, OH | 2 | 12 | 4226 | 0.0037994 | 1.0789e-05 | 352.1667
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 60 | 3380 | 0.0030388 | 5.3943e-05 | 56.3333
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | CAPACITOR | 1 | 62 | 992 | 0.00091883 | 5.7427e-05 | 16
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 408 | 0.00037111 | 1.8192e-06 | 204
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | TRANSFORMER, GROUNDING | 1 | 4 | 436 | 0.00039658 | 3.6384e-06 | 109
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | PEDESTAL | 1 | 1 | 1561 | 0.0014034 | 8.9905e-07 | 1561
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | FUSE | 1 | 7 | 147 | 0.00013616 | 6.4837e-06 | 21
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | WI | NONE | 3 | 587 | 76650 | 0.070996 | 0.0005437 | 130.5792
AEP-TX | 2021 | 1079632 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 108 | 0.00010003 | 9.2624e-07 | 108
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 1 | 107 | 9.8083e-05 | 9.1666e-07 | 107
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | NONE | 1310 | 14091 | 1020710 | 0.93565 | 0.012917 | 72.437
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | CONN/CLAMP | 1312 | 2835 | 310128 | 0.28209 | 0.0025787 | 109.3926
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | CONN/CLAMP | 1200 | 3235 | 351024 | 0.31929 | 0.0029425 | 108.5082
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | ARRESTER | 32 | 1228 | 100417 | 0.092049 | 0.0011257 | 81.7728
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TOR | NONE | 66 | 66 | 9637 | 0.0088339 | 6.05e-05 | 146.0152
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 29 | 179 | 57143 | 0.052381 | 0.00016408 | 319.2346
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1000 | 2911 | 357535 | 0.33116 | 0.0026963 | 122.8221
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | CUTOUT | 78 | 1200 | 141907 | 0.13008 | 0.0011 | 118.2558
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 38 | 896 | 122519 | 0.11348 | 0.00082991 | 136.74
AEP-TX | 2022 | 1090914 | PARTIAL POWER | OL | CONN/CLAMP | 49 | 136 | 16393 | 0.015027 | 0.00012467 | 120.5368
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | METERING | 1 | 14 | 2856 | 0.002618 | 1.2833e-05 | 204
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TOR | NONE | 227 | 227 | 29662 | 0.027855 | 0.00021317 | 130.6696
AEP-TX | 2022 | 1090914 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 5 | 11 | 1007 | 0.00092308 | 1.0083e-05 | 91.5455
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 13 | 3487 | 149530 | 0.1385 | 0.0032298 | 42.8821
AEP-TX | 2021 | 1079632 | PARTIAL POWER | A | NONE | 51 | 89 | 7787 | 0.0072126 | 8.2435e-05 | 87.4944
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | NONE | 43 | 6334 | 773838 | 0.72669 | 0.0059481 | 122.1721
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 10 | 1180 | 0.001093 | 9.2624e-06 | 118
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 60 | 15780 | 0.014616 | 5.5574e-05 | 263
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | CONDUCTOR UG | 4 | 17 | 1643 | 0.0015218 | 1.5746e-05 | 96.6471
AEP-TX | 2021 | 1079632 | PARTIAL POWER | UB | CONN/CLAMP | 3 | 3 | 390 | 0.00036123 | 2.7787e-06 | 130
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | SPLICE, OH | 11 | 70 | 16712 | 0.015319 | 6.4166e-05 | 238.7429
AEP-TX | 2022 | 1090914 | PARTIAL POWER | UB | TRANSFORMER, UG | 1 | 9 | 720 | 0.00066 | 8.25e-06 | 80
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | ARRESTER | 50 | 87 | 10418 | 0.0094762 | 7.9135e-05 | 119.7471
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | CONN/CLAMP | 66 | 1821 | 273111 | 0.24842 | 0.0016564 | 149.9786
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WI | NONE | 15 | 146 | 36020 | 0.032764 | 0.0001328 | 246.7123
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TR | NONE | 11 | 581 | 53735 | 0.048877 | 0.00052847 | 92.4871
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | CF | NONE | 2 | 83 | 14204 | 0.013339 | 7.7943e-05 | 171.1325
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | U | NONE | 26 | 20930 | 1510389 | 1.4184 | 0.019655 | 72.1638
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | NONE | 89 | 1744 | 146221 | 0.13731 | 0.0016378 | 83.8423
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | CONDUCTOR UG | 48 | 87 | 16025 | 0.015049 | 8.17e-05 | 184.1954
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 24 | 66 | 12408 | 0.011493 | 6.1132e-05 | 188
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | INSULATOR | 17 | 705 | 83660 | 0.078563 | 0.00066205 | 118.6667
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | PEDESTAL | 3 | 7 | 1491 | 0.001381 | 6.4837e-06 | 213
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 18 | 1198 | 0.0011096 | 1.6672e-05 | 66.5556
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 14 | 963 | 144067 | 0.13344 | 0.00089197 | 149.6023
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | CUTOUT | 15 | 280 | 47849 | 0.04432 | 0.00025935 | 170.8893
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | INSULATOR | 7 | 220 | 50810 | 0.046576 | 0.00020167 | 230.9545
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | CONN/CLAMP | 21 | 256 | 37150 | 0.03441 | 0.00023712 | 145.1172
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TR | NONE | 21 | 945 | 48163 | 0.044611 | 0.0008753 | 50.9661
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | SPLICE, OH | 4 | 71 | 6438 | 0.0059631 | 6.5763e-05 | 90.6761
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | NONE | 79 | 137 | 14224 | 0.012938 | 0.00012461 | 103.8248
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 3081 | 191073 | 0.17943 | 0.0028933 | 62.0166
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WL | ARRESTER | 7 | 12 | 1098 | 0.0010065 | 1.1e-05 | 91.5
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | NONE | 187 | 9558 | 2066532 | 1.8797 | 0.0086939 | 216.2097
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 2 | 180 | 0.000165 | 1.8333e-06 | 90
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VIN | ARRESTER | 3 | 6 | 301 | 0.00027592 | 5.5e-06 | 50.1667
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | WL | BREAKER | 5 | 6534 | 948700 | 0.86293 | 0.0059433 | 145.1944
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AF | BREAKER | 4 | 1659 | 174921 | 0.15911 | 0.001509 | 105.4376
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | TRANSFORMER, UG | 1 | 8 | 2400 | 0.0022 | 7.3333e-06 | 300
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 341 | 16869 | 2547270 | 2.2901 | 0.015166 | 151.003
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 25 | 2933 | 727908 | 0.67422 | 0.0027167 | 248.1787
AEP-TX | 2022 | 1090914 | PARTIAL POWER | A | JUMPER/RISER | 1 | 1 | 51 | 4.675e-05 | 9.1666e-07 | 51
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | TRANSFORMER, GROUNDING | 1 | 1 | 106 | 9.7166e-05 | 9.1666e-07 | 106
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 315 | 315 | 48942 | 0.044001 | 0.0002832 | 155.3714
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | INSULATOR | 3 | 3877 | 409886 | 0.37283 | 0.0035265 | 105.7225
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 113 | 19631 | 2873174 | 2.5831 | 0.017649 | 146.359
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | SPLICE, UG | 6 | 58 | 12430 | 0.011306 | 5.2756e-05 | 214.3103
AEP-TX | 2024 | 1112283 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 3 | 243 | 0.00021847 | 2.6972e-06 | 81
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 1 | 1 | 465 | 0.00042296 | 9.0959e-07 | 465
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | NONE | 141 | 391 | 44775 | 0.040255 | 0.00035153 | 114.5141
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | SWITCH, UG | 1 | 559 | 17778 | 0.016171 | 0.00050846 | 31.8032
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 4 | 26384 | 0.023721 | 3.5962e-06 | 6596
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 8 | 27 | 6221 | 0.005593 | 2.4274e-05 | 230.4074
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | JUMPER/RISER | 9 | 347 | 59126 | 0.053157 | 0.00031197 | 170.3919
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 4 | 3077 | 93508 | 0.087811 | 0.0028895 | 30.3893
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | POLE | 11 | 260 | 80052 | 0.071971 | 0.00023375 | 307.8923
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | ARRESTER | 5 | 14 | 1397 | 0.001256 | 1.2587e-05 | 99.7857
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | SWITCH, OH | 5 | 4236 | 422341 | 0.37971 | 0.0038084 | 99.7028
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 295 | 0.00026522 | 8.9905e-07 | 295
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 11 | 171 | 103804 | 0.093325 | 0.00015374 | 607.0409
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 12 | 2904 | 0.0026898 | 1.1115e-05 | 242
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 2 | 517 | 12275 | 0.011252 | 0.00047391 | 23.7427
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 158 | 12324 | 0.011415 | 0.00014635 | 78
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | BREAKER | 6 | 3267 | 261031 | 0.23468 | 0.0029372 | 79.8993
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | FUSE | 2 | 13 | 2015 | 0.0018471 | 1.1917e-05 | 155
AEP-TX | 2023 | 1099391 | PARTIAL POWER | ABI | JUMPER/RISER | 1 | 15 | 2175 | 0.0019784 | 1.3644e-05 | 145
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 18 | 5598 | 0.005257 | 1.6903e-05 | 311
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 106 | 38796 | 0.03488 | 9.5299e-05 | 366
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 1 | 60 | 5.3943e-05 | 8.9905e-07 | 60
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 1 | 94 | 8.4511e-05 | 8.9905e-07 | 94
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | SWITCH, UG | 1 | 160 | 22720 | 0.020426 | 0.00014385 | 142
AEP-TX | 2023 | 1099391 | PARTIAL POWER | A | ARRESTER | 2 | 2 | 101 | 9.1869e-05 | 1.8192e-06 | 50.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | CROSSARM | 1 | 1 | 96 | 9.0151e-05 | 9.3908e-07 | 96
AEP-TX | 2020 | 1064875 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 22 | 2.066e-05 | 9.3908e-07 | 22
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AF | SWITCH, OH | 1 | 49 | 1813 | 0.0016793 | 4.5386e-05 | 37
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 160 | 385 | 57509 | 0.052716 | 0.00035292 | 149.374
AEP-TX | 2022 | 1090914 | PARTIAL POWER | U | NONE | 152 | 362 | 33767 | 0.030953 | 0.00033183 | 93.279
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | CUTOUT | 12 | 281 | 25113 | 0.02302 | 0.00025758 | 89.3701
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | SWITCH, OH | 28 | 17818 | 1654159 | 1.5322 | 0.016504 | 92.8364
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | CROSSARM | 9 | 2652 | 148821 | 0.13642 | 0.002431 | 56.1165
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | NONE | 52 | 2248 | 328198 | 0.30399 | 0.0020822 | 145.9956
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | CUTOUT | 32 | 511 | 82557 | 0.075677 | 0.00046841 | 161.5597
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | CUTOUT | 475 | 12933 | 1500766 | 1.4093 | 0.012145 | 116.0416
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 19 | 6016 | 0.0055146 | 1.7417e-05 | 316.6316
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | NONE | 3139 | 118774 | 12186532 | 11.4441 | 0.11154 | 102.6027
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | CONN/CLAMP | 38 | 248 | 22412 | 0.021047 | 0.00023289 | 90.371
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | POLE | 17 | 678 | 118011 | 0.11082 | 0.00063669 | 174.0575
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | METERING | 9 | 9 | 749 | 0.00070337 | 8.4517e-06 | 83.2222
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 371 | 49435 | 0.046423 | 0.0003484 | 133.248
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | BREAKER | 22 | 15897 | 1658029 | 1.5357 | 0.014724 | 104.2982
AEP-TX | 2023 | 1099391 | PARTIAL POWER | A | NONE | 68 | 133 | 11270 | 0.010251 | 0.00012098 | 84.7368
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | CONN/CLAMP | 9 | 247 | 18360 | 0.017241 | 0.00023195 | 74.332
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | TRANSFORMER, UG | 1 | 4 | 1900 | 0.0017599 | 3.705e-06 | 475
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | CONDUCTOR UG | 1 | 1 | 489 | 0.00045293 | 9.2624e-07 | 489
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 21 | 505 | 56738 | 0.05201 | 0.00046291 | 112.3525
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | CUTOUT | 528 | 13490 | 1636620 | 1.4887 | 0.01227 | 121.321
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 40 | 217 | 55275 | 0.051908 | 0.00020378 | 254.7235
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | POLE HARDWARE | 9 | 3668 | 542254 | 0.50922 | 0.0034445 | 147.8337
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | SWITCH, OH | 18 | 13308 | 1262459 | 1.1855 | 0.012497 | 94.8647
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 105 | 20887 | 0.019146 | 9.625e-05 | 198.9238
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | O | NONE | 5 | 12 | 2613 | 0.0024538 | 1.1269e-05 | 217.75
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | TRANSFORMER, OH | 3 | 8 | 1144 | 0.0010406 | 7.2768e-06 | 143
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | SPLICE, OH | 7 | 17 | 1368 | 0.0012847 | 1.5964e-05 | 80.4706
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 11 | 51 | 8425 | 0.0078036 | 4.7238e-05 | 165.1961
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | CABLE TERMINATOR | 2 | 3 | 402 | 0.00036566 | 2.7288e-06 | 134
AEP-TX | 2020 | 1064875 | PARTIAL POWER | VA | NONE | 6 | 12 | 1095 | 0.0010283 | 1.1269e-05 | 91.25
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | ARRESTER | 167 | 3141 | 336904 | 0.30289 | 0.0028239 | 107.2601
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 89 | 8.0954e-05 | 9.0959e-07 | 89
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | METERING | 4 | 5 | 222 | 0.00020193 | 4.548e-06 | 44.4
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 6 | 1173 | 23030 | 0.020948 | 0.001067 | 19.6334
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | CF | NONE | 6 | 10439 | 1242350 | 1.13 | 0.0094953 | 119.0104
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 27 | 1004 | 0.00091323 | 2.4559e-05 | 37.1852
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 135 | 18090 | 3200064 | 2.877 | 0.016264 | 176.8968
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 3 | 40 | 3.6384e-05 | 2.7288e-06 | 13.3333
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | SPLICE, UG | 2 | 6 | 2083 | 0.0018947 | 5.4576e-06 | 347.1667
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | TRANSFORMER, OH | 5 | 24 | 7780 | 0.0069946 | 2.1577e-05 | 324.1667
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | CUTOUT | 20 | 1331 | 183626 | 0.16509 | 0.0011966 | 137.9609
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | JUMPER/RISER | 4 | 34 | 3923 | 0.0035683 | 3.0926e-05 | 115.3824
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | CONN/CLAMP | 14 | 1529 | 246709 | 0.2218 | 0.0013747 | 161.3532
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | CONN/CLAMP | 16 | 57 | 12710 | 0.011427 | 5.1246e-05 | 222.9825
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 3 | 71 | 6805 | 0.0063904 | 6.6674e-05 | 95.8451
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | GUY/ANCHOR | 1 | 1 | 129 | 0.00011598 | 8.9905e-07 | 129
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | ARRESTER | 88 | 707 | 75614 | 0.067981 | 0.00063563 | 106.9505
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | JUMPER/RISER | 16 | 201 | 22954 | 0.020637 | 0.00018071 | 114.199
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 2 | 5 | 1100 | 0.00098896 | 4.4953e-06 | 220
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | PEDESTAL | 6 | 39 | 3669 | 0.0032986 | 3.5063e-05 | 94.0769
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WU | NONE | 14 | 17 | 2420 | 0.0021757 | 1.5284e-05 | 142.3529
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | TRANSFORMER, OH | 19 | 46 | 6993 | 0.0062871 | 4.1356e-05 | 152.0217
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | JUMPER/RISER | 40 | 1096 | 135197 | 0.12155 | 0.00098536 | 123.3549
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | INSULATOR | 7 | 1377 | 329930 | 0.29662 | 0.001238 | 239.6006
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 363 | 0.00033623 | 9.2624e-07 | 363
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 1 | 37 | 3700 | 0.0033917 | 3.3917e-05 | 100
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ABI | CUTOUT | 4 | 148 | 11283 | 0.010263 | 0.00013462 | 76.2365
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | FUSE | 1 | 19 | 1425 | 0.0012811 | 1.7082e-05 | 75
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 47 | 4.2255e-05 | 8.9905e-07 | 47
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | SWITCH, OH | 1 | 232 | 19488 | 0.017521 | 0.00020858 | 84
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | BREAKER | 2 | 3112 | 459644 | 0.41809 | 0.0028307 | 147.7005
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | METERING | 2 | 3 | 310 | 0.00028197 | 2.7288e-06 | 103.3333
AEP-TX | 2024 | 1112283 | PARTIAL POWER | OL | TRANSFORMER, UG | 1 | 13 | 3016 | 0.0027115 | 1.1688e-05 | 232
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | SPLICE, OH | 3 | 7 | 547 | 0.00049178 | 6.2934e-06 | 78.1429
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 53 | 341 | 69452 | 0.062441 | 0.00030658 | 203.6716
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TOR | NONE | 96 | 96 | 14197 | 0.012764 | 8.6309e-05 | 147.8854
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | POLE | 5 | 14 | 3855 | 0.0034658 | 1.2587e-05 | 275.3571
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 1 | 50 | 4.4953e-05 | 8.9905e-07 | 50
AEP-TX | 2024 | 1112283 | PARTIAL POWER | VIN | ARRESTER | 1 | 3 | 231 | 0.00020768 | 2.6972e-06 | 77
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AF | SWITCH, OH | 2 | 517 | 41996 | 0.038496 | 0.00047391 | 81.2302
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | CAPACITOR | 3 | 1608 | 186348 | 0.175 | 0.00151 | 115.8881
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 995 | 154225 | 0.13866 | 0.00089456 | 155
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 1 | 1 | 251 | 0.00023249 | 9.2624e-07 | 251
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 1 | 1 | 45 | 4.1681e-05 | 9.2624e-07 | 45
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | JUMPER/RISER | 3 | 34 | 9054 | 0.0085024 | 3.1929e-05 | 266.2941
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 2 | 112 | 0.00010069 | 1.7981e-06 | 56
AEP-TX | 2024 | 1112283 | PARTIAL POWER | VA | POLE | 1 | 3 | 600 | 0.00053943 | 2.6972e-06 | 200
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 257 | 35902 | 0.032278 | 0.00023106 | 139.6965
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 2 | 50 | 6348 | 0.0057072 | 4.4953e-05 | 126.96
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 291 | 0.00026162 | 8.9905e-07 | 291
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 2 | 292 | 0.00026767 | 1.8333e-06 | 146
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TOR | METERING | 4 | 4 | 308 | 0.00028924 | 3.7563e-06 | 77
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | RECLOSER, LINE/OCR/BR | 3 | 1875 | 136988 | 0.12316 | 0.0016857 | 73.0603
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | AF | NONE | 1 | 41 | 2091 | 0.0018799 | 3.6861e-05 | 51
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | AB | INSULATOR | 5 | 3054 | 321937 | 0.28944 | 0.0027457 | 105.4149
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WFS | CONDUCTOR UG | 1 | 1 | 174 | 0.00015644 | 8.9905e-07 | 174
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | FUSE | 1 | 1 | 113 | 0.00010467 | 9.2624e-07 | 113
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 247 | 0.00022878 | 9.2624e-07 | 247
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TR | CONDUCTOR UG | 1 | 1 | 55 | 5.0943e-05 | 9.2624e-07 | 55
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 117 | 7020 | 0.0063113 | 0.00010519 | 60
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 150 | 0.00014086 | 9.3908e-07 | 150
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | CONN/CLAMP | 1191 | 2857 | 318154 | 0.29164 | 0.0026189 | 111.3595
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | BREAKER | 1 | 612 | 76874 | 0.070468 | 0.000561 | 125.6111
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | POLE HARDWARE | 13 | 1129 | 274041 | 0.2512 | 0.0010349 | 242.729
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | NONE | 629 | 11007 | 1054873 | 0.97707 | 0.010195 | 95.8366
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | JUMPER/RISER | 70 | 4015 | 378228 | 0.35033 | 0.0037189 | 94.2037
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | POLE | 64 | 7890 | 1479517 | 1.3704 | 0.007308 | 187.518
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 622 | 22823 | 3836342 | 3.5534 | 0.02114 | 168.091
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 168 | 483 | 79687 | 0.073809 | 0.00044737 | 164.9834
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 8 | 60 | 18267 | 0.016745 | 5.5e-05 | 304.45
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | METERING | 21 | 86 | 13771 | 0.012755 | 7.9657e-05 | 160.1279
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | JUMPER/RISER | 16 | 327 | 32227 | 0.02985 | 0.00030288 | 98.5535
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VIN | NONE | 122 | 1126 | 147981 | 0.13897 | 0.0010574 | 131.4218
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | CUTOUT | 25 | 623 | 50283 | 0.046574 | 0.00057705 | 80.7111
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 2 | 1408 | 0.0013222 | 1.8782e-06 | 704
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 12 | 639 | 30370 | 0.02852 | 0.00060007 | 47.5274
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WI | TRANSFORMER, OH | 1 | 1 | 68 | 6.2984e-05 | 9.2624e-07 | 68
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 1 | 97 | 8.9845e-05 | 9.2624e-07 | 97
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | CABLE TERMINATOR | 4 | 12 | 9474 | 0.0088968 | 1.1269e-05 | 789.5
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | FUSE | 1 | 1 | 182 | 0.00016858 | 9.2624e-07 | 182
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | CUTOUT | 39 | 161 | 23542 | 0.022108 | 0.00015119 | 146.2236
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 3 | 20 | 2584 | 0.0023934 | 1.8525e-05 | 129.2
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 91 | 19918 | 1602995 | 1.4581 | 0.018117 | 80.4797
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 50 | 7247 | 1082124 | 0.98429 | 0.0065918 | 149.3203
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 89 | 6651 | 1266231 | 1.1518 | 0.0060497 | 190.382
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 99 | 9.005e-05 | 1.8192e-06 | 49.5
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | POLE HARDWARE | 6 | 393 | 54516 | 0.049587 | 0.00035747 | 138.7176
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | INSULATOR | 6 | 720 | 44161 | 0.041471 | 0.00067614 | 61.3347
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 4 | 11 | 4310 | 0.0039508 | 1.0083e-05 | 391.8182
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 28 | 1570 | 149055 | 0.13401 | 0.0014115 | 94.9395
AEP-TX | 2020 | 1064875 | PARTIAL POWER | ABI | NONE | 39 | 54 | 6169 | 0.0057932 | 5.071e-05 | 114.2407
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | SPLICE, OH | 13 | 45 | 6296 | 0.0057268 | 4.0932e-05 | 139.9111
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TOR | CONN/CLAMP | 123 | 123 | 18218 | 0.016379 | 0.00011058 | 148.1138
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 1 | 48 | 4.446e-05 | 9.2624e-07 | 48
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | POLE HARDWARE | 23 | 424 | 58188 | 0.052927 | 0.00038567 | 137.2358
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | SPLICE, OH | 3 | 7 | 1129 | 0.0010269 | 6.3672e-06 | 161.2857
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 1 | 98 | 65668 | 0.059731 | 8.914e-05 | 670.0816
AEP-TX | 2023 | 1099391 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 4 | 16 | 1502 | 0.0013662 | 1.4554e-05 | 93.875
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 25 | 2100 | 0.0019101 | 2.274e-05 | 84
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | CAPACITOR | 1 | 1 | 153 | 0.00014368 | 9.3908e-07 | 153
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | ARRESTER | 2 | 6 | 872 | 0.00079933 | 5.5e-06 | 145.3333
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | NONE | 92 | 7804 | 899302 | 0.80852 | 0.0070162 | 115.236
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | INSULATOR | 12 | 1889 | 81765 | 0.073511 | 0.0016983 | 43.2848
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | ERF | NONE | 4 | 4299 | 54278 | 0.048799 | 0.003865 | 12.6257
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | POLE | 23 | 204 | 41581 | 0.037383 | 0.00018341 | 203.8284
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | NONE | 533 | 8723 | 908656 | 0.81693 | 0.0078424 | 104.1678
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 230 | 0.00020678 | 1.7981e-06 | 115
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CO | METERING | 3 | 3 | 460 | 0.00041356 | 2.6972e-06 | 153.3333
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 35 | 7694 | 2211488 | 1.9882 | 0.0069173 | 287.4302
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TIR | NONE | 18 | 110 | 7872 | 0.0070773 | 9.8896e-05 | 71.5636
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 1 | 4 | 348 | 0.00031287 | 3.5962e-06 | 87
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | UB | NONE | 4 | 16 | 1311 | 0.0011787 | 1.4385e-05 | 81.9375
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | POLE | 1 | 6 | 1278 | 0.0012001 | 5.6345e-06 | 213
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 9 | 29 | 3280 | 0.0030067 | 2.6583e-05 | 113.1034
AEP-TX | 2024 | 1112283 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 3 | 278 | 0.00024994 | 2.6972e-06 | 92.6667
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 5 | 820 | 22485 | 0.021115 | 0.00077004 | 27.4207
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ERO | NONE | 1 | 36 | 396 | 0.00035602 | 3.2366e-05 | 11
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | SPLICE, UG | 1 | 1 | 166 | 0.00014924 | 8.9905e-07 | 166
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | TRANSFORMER, UG | 2 | 13 | 1586 | 0.0014259 | 1.1688e-05 | 122
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 340 | 18010 | 0.016382 | 0.00030926 | 52.9706
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | INSULATOR | 7 | 5076 | 343571 | 0.30889 | 0.0045636 | 67.6854
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | ABX | NONE | 1 | 140 | 13300 | 0.011957 | 0.00012587 | 95
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 1 | 115 | 0.00010339 | 8.9905e-07 | 115
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 40 | 3.5962e-05 | 8.9905e-07 | 40
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 5 | 460 | 0.00041356 | 4.4953e-06 | 92
AEP-TX | 2021 | 1079632 | PARTIAL POWER | U | CONN/CLAMP | 2 | 4 | 308 | 0.00028528 | 3.705e-06 | 77
AEP-TX | 2020 | 1064875 | PARTIAL POWER | ERF | FUSE | 1 | 1 | 71 | 6.6674e-05 | 9.3908e-07 | 71
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WFS | NONE | 1 | 9 | 585 | 0.00053211 | 8.1864e-06 | 65
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | CAPACITOR | 1 | 652 | 4564 | 0.0041033 | 0.00058618 | 7
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 7 | 882 | 0.00081695 | 6.4837e-06 | 126
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 1332 | 49284 | 0.045649 | 0.0012338 | 37
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | ABI | ARRESTER | 1 | 1200 | 66945 | 0.060187 | 0.0010789 | 55.7875
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | TRANSFORMER, POWER - LTC | 1 | 1 | 47 | 4.4137e-05 | 9.3908e-07 | 47
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 1 | 149 | 0.00013396 | 8.9905e-07 | 149
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | SWITCH, OH | 1 | 3038 | 244838 | 0.2227 | 0.0027633 | 80.5918
AEP-TX | 2021 | 1079632 | PARTIAL POWER | U | NONE | 229 | 635 | 71473 | 0.066201 | 0.00058816 | 112.5559
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | WU | NONE | 4 | 831 | 70179 | 0.06433 | 0.00076175 | 84.4513
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TOR | CONN/CLAMP | 93 | 93 | 10035 | 0.0091278 | 8.4592e-05 | 107.9032
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | METERING | 123 | 126 | 10361 | 0.0094975 | 0.0001155 | 82.2302
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | ARRESTER | 401 | 4346 | 534263 | 0.48596 | 0.0039531 | 122.9321
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | TRANSFORMER, OH | 53 | 194 | 45745 | 0.041933 | 0.00017783 | 235.799
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | METERING | 10 | 11 | 2491 | 0.0022834 | 1.0083e-05 | 226.4545
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 167 | 7651 | 1248683 | 1.1566 | 0.0070867 | 163.2052
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 42 | 2196 | 164407 | 0.15071 | 0.002013 | 74.8666
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | PEDESTAL | 13 | 58 | 6981 | 0.0064661 | 5.3722e-05 | 120.3621
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 933 | 26124 | 0.023947 | 0.00085525 | 28
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TOR | NONE | 204 | 204 | 25251 | 0.023389 | 0.00018895 | 123.7794
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | UB | NONE | 2 | 11 | 198 | 0.0001815 | 1.0083e-05 | 18
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 62 | 5.6833e-05 | 9.1666e-07 | 62
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | CONN/CLAMP | 118 | 563 | 69700 | 0.065454 | 0.0005287 | 123.8011
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | POLE | 4 | 7 | 1723 | 0.0015959 | 6.4837e-06 | 246.1429
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 5 | 2748 | 416434 | 0.39106 | 0.0025806 | 151.5408
AEP-TX | 2020 | 1064875 | PARTIAL POWER | OL | NONE | 21 | 88 | 5777 | 0.005425 | 8.2639e-05 | 65.6477
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TIR | ARRESTER | 2 | 5 | 1658 | 0.0015198 | 4.5833e-06 | 331.6
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 82 | 82 | 12174 | 0.011073 | 7.4587e-05 | 148.4634
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 10 | 1543 | 0.001449 | 9.3908e-06 | 154.3
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | FUSE | 22 | 200 | 21413 | 0.019834 | 0.00018525 | 107.065
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 22 | 390 | 78108 | 0.071047 | 0.00035474 | 200.2769
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 14 | 1120 | 0.0010187 | 1.2734e-05 | 80
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | CAPACITOR | 6 | 2853 | 192284 | 0.18057 | 0.0026792 | 67.3971
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | U | FUSE | 2 | 6 | 338 | 0.00031307 | 5.5574e-06 | 56.3333
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AB | REGULATOR | 1 | 2 | 688 | 0.00063066 | 1.8333e-06 | 344
AEP-TX | 2023 | 1099391 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 214 | 0.00019465 | 9.0959e-07 | 214
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 2 | 5 | 510 | 0.00045852 | 4.4953e-06 | 102
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WT | NONE | 8 | 18 | 3311 | 0.0029768 | 1.6183e-05 | 183.9444
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | TRANSFORMER, OH | 1 | 1 | 204 | 0.00018895 | 9.2624e-07 | 204
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 20 | 1000 | 0.00090959 | 1.8192e-05 | 50
AEP-TX | 2023 | 1099391 | PARTIAL POWER | ABI | TRANSFORMER, OH | 1 | 1 | 60 | 5.4576e-05 | 9.0959e-07 | 60
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | NONE | 2863 | 120686 | 11625630 | 10.5746 | 0.10978 | 96.3296
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 160 | 490 | 88415 | 0.081047 | 0.00044916 | 180.4388
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | JUMPER/RISER | 51 | 343 | 51318 | 0.047041 | 0.00031442 | 149.6152
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 322 | 4829 | 1163094 | 1.0773 | 0.0044728 | 240.8561
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 18 | 73 | 36974 | 0.033893 | 6.6916e-05 | 506.4932
AEP-TX | 2021 | 1079632 | PARTIAL POWER | OL | CONN/CLAMP | 41 | 158 | 16084 | 0.014898 | 0.00014635 | 101.7975
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 11 | 380 | 68373 | 0.062675 | 0.00034833 | 179.9289
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | CONN/CLAMP | 21 | 235 | 69202 | 0.063435 | 0.00021542 | 294.4766
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 115 | 115 | 18418 | 0.017296 | 0.00010799 | 160.1565
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 46 | 474 | 113184 | 0.10629 | 0.00044512 | 238.7848
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 5 | 226 | 74002 | 0.069494 | 0.00021223 | 327.4425
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 35 | 167 | 19653 | 0.018456 | 0.00015683 | 117.6826
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | POLE HARDWARE | 12 | 308 | 48674 | 0.045084 | 0.00028528 | 158.0325
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 480 | 69018 | 0.064813 | 0.00045076 | 143.7875
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 7 | 581 | 0.00053258 | 6.4166e-06 | 83
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | METERING | 4 | 9 | 684 | 0.000627 | 8.25e-06 | 76
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 24 | 543 | 184155 | 0.17294 | 0.00050992 | 339.1436
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 4 | 10 | 1672 | 0.0015487 | 9.2624e-06 | 167.2
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | INSULATOR | 6 | 6478 | 466870 | 0.43243 | 0.0060002 | 72.0701
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 41 | 312 | 78074 | 0.071016 | 0.00028379 | 250.2372
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | ARRESTER | 196 | 3232 | 370477 | 0.33698 | 0.0029398 | 114.6278
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | POLE HARDWARE | 6 | 1018 | 86069 | 0.079721 | 0.00094291 | 84.5472
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | CUTOUT | 38 | 410 | 72890 | 0.0663 | 0.00037293 | 177.7805
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | CAPACITOR | 5 | 2351 | 277841 | 0.24979 | 0.0021137 | 118.1799
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 19 | 86 | 12057 | 0.01084 | 7.7318e-05 | 140.1977
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERO | NONE | 8 | 360 | 13158 | 0.012356 | 0.00033807 | 36.55
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | TRANSFORMER, OH | 2 | 2 | 261 | 0.00024175 | 1.8525e-06 | 130.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | CROSSARM | 13 | 2788 | 391898 | 0.36802 | 0.0026181 | 140.566
AEP-TX | 2021 | 1079632 | PARTIAL POWER | FO | CONN/CLAMP | 2 | 5 | 504 | 0.00046683 | 4.6312e-06 | 100.8
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 7 | 111 | 19808 | 0.018017 | 0.00010096 | 178.4505
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 4 | 760 | 0.00069129 | 3.6384e-06 | 190
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 361 | 5530 | 1176565 | 1.0578 | 0.0049718 | 212.7604
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 6 | 551 | 70560 | 0.064181 | 0.00050119 | 128.0581
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 4 | 424 | 0.00038567 | 3.6384e-06 | 106
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | SPLICE, OH | 2 | 3 | 211 | 0.00019544 | 2.7787e-06 | 70.3333
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | ARRESTER | 2 | 5 | 604 | 0.0005494 | 4.548e-06 | 120.8
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 386 | 5422 | 0.0048747 | 0.00034703 | 14.0466
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | SPLICE, OH | 1 | 1 | 104 | 9.6329e-05 | 9.2624e-07 | 104
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 12 | 239 | 31492 | 0.028313 | 0.00021487 | 131.7657
AEP-TX | 2024 | 1112283 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 7 | 17 | 1387 | 0.001247 | 1.5284e-05 | 81.5882
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 135 | 7520 | 1212302 | 1.0899 | 0.0067609 | 161.2104
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 100 | 3689 | 471914 | 0.42428 | 0.0033166 | 127.9246
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | CONN/CLAMP | 35 | 479 | 61926 | 0.055675 | 0.00043065 | 129.2818
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | A | ARRESTER | 4 | 33 | 2947 | 0.0026495 | 2.9669e-05 | 89.303
AEP-TX | 2020 | 1064875 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 1 | 160 | 0.00015025 | 9.3908e-07 | 160
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 1 | 60 | 5.5e-05 | 9.1666e-07 | 60
AEP-TX | 2020 | 1064875 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 89 | 8.3578e-05 | 9.3908e-07 | 89
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WH | CONN/CLAMP | 3 | 19 | 17119 | 0.016076 | 1.7842e-05 | 901
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 129 | 0.00011949 | 9.2624e-07 | 129
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 1 | 132 | 0.00012396 | 9.3908e-07 | 132
AEP-TX | 2021 | 1079632 | PARTIAL POWER | VA | POLE | 1 | 1 | 361 | 0.00033437 | 9.2624e-07 | 361
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | METERING | 2 | 73 | 10085 | 0.0094706 | 6.8553e-05 | 138.1507
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 235 | 0.00021767 | 9.2624e-07 | 235
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | CAPACITOR | 2 | 626 | 49447 | 0.044455 | 0.00056281 | 78.9888
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WT | CONN/CLAMP | 1 | 4 | 280 | 0.00025173 | 3.5962e-06 | 70
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 1 | 330 | 0.00029669 | 8.9905e-07 | 330
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 5 | 4665 | 0.0043209 | 4.6312e-06 | 933
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 1 | 1 | 92 | 8.2713e-05 | 8.9905e-07 | 92
AEP-TX | 2024 | 1112283 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 3 | 305 | 0.00027421 | 2.6972e-06 | 101.6667
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | R | NONE | 3 | 1653 | 64070 | 0.057602 | 0.0014861 | 38.7598
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 38 | 4522 | 0.0041132 | 3.4565e-05 | 119
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WFS | CONN/CLAMP | 4 | 4 | 319 | 0.0002868 | 3.5962e-06 | 79.75
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 1 | 72 | 6.4732e-05 | 8.9905e-07 | 72
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 556 | 89516 | 0.082913 | 0.00051499 | 161
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 16 | 4904 | 0.0044953 | 1.4667e-05 | 306.5
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 44 | 5263 | 0.0048244 | 4.0333e-05 | 119.6136
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1472 | 9500 | 2181433 | 1.9842 | 0.0086411 | 229.6245
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1836 | 14156 | 1590755 | 1.4734 | 0.013112 | 112.3732
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | SPLICE, OH | 4 | 62 | 6488 | 0.0059473 | 5.6833e-05 | 104.6452
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | CONDUCTOR UG | 49 | 119 | 28491 | 0.026117 | 0.00010908 | 239.4202
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERO | NONE | 8 | 3312 | 126370 | 0.11584 | 0.003036 | 38.1552
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TOR | NONE | 36 | 36 | 4618 | 0.0042774 | 3.3345e-05 | 128.2778
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | CUTOUT | 4 | 28 | 5997 | 0.0054972 | 2.5667e-05 | 214.1786
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 64 | 5.8666e-05 | 9.1666e-07 | 64
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | CROSSARM | 50 | 16503 | 2366494 | 2.1693 | 0.015128 | 143.3978
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 187 | 794 | 318662 | 0.29925 | 0.00074563 | 401.3375
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | WL | BREAKER | 7 | 4660 | 496653 | 0.4664 | 0.0043761 | 106.5779
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | JUMPER/RISER | 26 | 4631 | 543966 | 0.51083 | 0.0043489 | 117.4619
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | NONE | 46 | 23539 | 2150149 | 2.0192 | 0.022105 | 91.3441
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | JUMPER/RISER | 42 | 1949 | 218921 | 0.20558 | 0.0018303 | 112.3248
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TOR | CONN/CLAMP | 71 | 71 | 8239 | 0.0076313 | 6.5763e-05 | 116.0423
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | CROSSARM | 17 | 1694 | 144303 | 0.13366 | 0.0015691 | 85.1848
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | CF | NONE | 5 | 2718 | 171509 | 0.15722 | 0.0024915 | 63.1012
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | CROSSARM | 230 | 29109 | 3094066 | 2.8143 | 0.026477 | 106.2924
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | TRANSFORMER, UG | 1 | 1 | 10 | 9.2624e-06 | 9.2624e-07 | 10
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | INSULATOR | 109 | 17947 | 2231981 | 2.0302 | 0.016324 | 124.3651
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 102 | 12815 | 1505105 | 1.369 | 0.011656 | 117.4487
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1394 | 9066 | 1473308 | 1.3246 | 0.0081508 | 162.5092
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | BREAKER | 2 | 1143 | 116504 | 0.10941 | 0.0010734 | 101.9283
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | ERF | NONE | 6 | 4930 | 181092 | 0.16773 | 0.0045664 | 36.7327
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | JUMPER/RISER | 11 | 6408 | 671508 | 0.6108 | 0.0058287 | 104.7921
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 3 | 7 | 989 | 0.00089959 | 6.3672e-06 | 141.2857
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AO | REGULATOR | 1 | 60 | 5160 | 0.0046935 | 5.4576e-05 | 86
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | CUTOUT | 27 | 467 | 42211 | 0.03795 | 0.00041986 | 90.3876
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | JUMPER/RISER | 8 | 330 | 26111 | 0.02375 | 0.00030017 | 79.1242
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | WL | TRANSFORMER, POWER - LTC | 3 | 3811 | 463626 | 0.42499 | 0.0034934 | 121.6547
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | FO | NONE | 111 | 9526 | 767434 | 0.68996 | 0.0085644 | 80.562
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 42 | 5669 | 919704 | 0.82686 | 0.0050967 | 162.2339
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 81 | 562 | 86205 | 0.077503 | 0.00050527 | 153.3897
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | JUMPER/RISER | 1 | 4 | 760 | 0.00069129 | 3.6384e-06 | 190
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | UB | TRANSFORMER, GROUNDING | 2 | 2 | 279 | 0.00025842 | 1.8525e-06 | 139.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | CUTOUT | 3 | 5 | 477 | 0.00042885 | 4.4953e-06 | 95.4
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | ARRESTER | 4 | 4 | 253 | 0.00022746 | 3.5962e-06 | 63.25
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | PEDESTAL | 5 | 9 | 2273 | 0.0020435 | 8.0915e-06 | 252.5556
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | U | NONE | 184 | 36746 | 1534555 | 1.3796 | 0.033037 | 41.7611
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | CONN/CLAMP | 24 | 168 | 23025 | 0.020701 | 0.00015104 | 137.0536
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TIR | CONN/CLAMP | 21 | 48 | 7013 | 0.0063051 | 4.3154e-05 | 146.1042
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | CUTOUT | 5 | 29 | 3008 | 0.0027043 | 2.6073e-05 | 103.7241
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | SPLICE, UG | 2 | 2 | 437 | 0.00039289 | 1.7981e-06 | 218.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | FO | CONN/CLAMP | 2 | 2 | 157 | 0.00014115 | 1.7981e-06 | 78.5
AEP-TX | 2025 | 1112283 | PARTIAL POWER | ABI | NONE | 6 | 108 | 9817 | 0.008826 | 9.7098e-05 | 90.8981
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | SPLICE, OH | 7 | 156 | 43032 | 0.038688 | 0.00014025 | 275.8462
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | PEDESTAL | 2 | 44 | 2380 | 0.002235 | 4.1319e-05 | 54.0909
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | TRANSFORMER, OH | 1 | 2 | 506 | 0.00047517 | 1.8782e-06 | 253
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | CROSSARM | 12 | 133 | 29342 | 0.026689 | 0.00012098 | 220.6165
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | AF | NONE | 7 | 1593 | 120894 | 0.11353 | 0.001496 | 75.8908
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 1012 | 23590 | 0.02185 | 0.00093736 | 23.3103
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | POLE | 2 | 71 | 12621 | 0.01169 | 6.5763e-05 | 177.7606
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 1 | 70 | 6.3672e-05 | 9.0959e-07 | 70
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 12 | 1044 | 0.000967 | 1.1115e-05 | 87
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | REGULATOR | 9 | 9456 | 1483715 | 1.3339 | 0.0085014 | 156.9073
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 5 | 31 | 24544 | 0.023049 | 2.9111e-05 | 791.7419
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | RELAY | 6 | 8820 | 898940 | 0.84417 | 0.0082827 | 101.9206
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WW | NONE | 1 | 3 | 159 | 0.00014295 | 2.6972e-06 | 53
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TOR | POLE | 2 | 2 | 281 | 0.00025263 | 1.7981e-06 | 140.5
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TOR | NONE | 8 | 8 | 775 | 0.00069677 | 7.1924e-06 | 96.875
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | SPLICE, OH | 13 | 61 | 7007 | 0.0062997 | 5.4842e-05 | 114.8689
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | METERING | 1 | 1 | 56 | 5.1333e-05 | 9.1666e-07 | 56
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1 | 212 | 0.00019433 | 9.1666e-07 | 212
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | JUMPER/RISER | 3 | 59 | 8387 | 0.0075403 | 5.3044e-05 | 142.1525
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 2 | 10 | 2203 | 0.0020405 | 9.2624e-06 | 220.3
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | SPLICE, OH | 2 | 4 | 498 | 0.00044773 | 3.5962e-06 | 124.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 2 | 2421 | 67788 | 0.060945 | 0.0021766 | 28
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | POLE HARDWARE | 2 | 28 | 80024 | 0.071946 | 2.5173e-05 | 2858
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 19 | 3439 | 0.0030918 | 1.7082e-05 | 181
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | CUTOUT | 1 | 1 | 99 | 8.9006e-05 | 8.9905e-07 | 99
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 12 | 1104 | 0.00099255 | 1.0789e-05 | 92
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 726 | 62436 | 0.056791 | 0.00066037 | 86
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 3 | 101 | 29048 | 0.026422 | 9.1869e-05 | 287.604
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | CAPACITOR | 1 | 1 | 34 | 3.1167e-05 | 9.1666e-07 | 34
AEP-TX | 2024 | 1112283 | PARTIAL POWER | ABI | ARRESTER | 2 | 2 | 53 | 4.765e-05 | 1.7981e-06 | 26.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | AO | CIRCUIT SWITCHER | 3 | 2489 | 237289 | 0.22283 | 0.0023374 | 95.3351
AEP-TX | 2020 | 1064875 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 20 | 6300 | 0.0059162 | 1.8782e-05 | 315
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | CUTOUT | 1 | 1 | 94 | 8.5502e-05 | 9.0959e-07 | 94
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | CROSSARM | 1 | 1 | 98 | 8.8107e-05 | 8.9905e-07 | 98
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | NETWORK TRANSFORMER | 1 | 8 | 712 | 0.00066862 | 7.5126e-06 | 89
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1150 | 134422 | 16146611 | 14.801 | 0.12322 | 120.1188
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 11 | 111 | 21403 | 0.019619 | 0.00010175 | 192.8198
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TIR | NONE | 73 | 918 | 74994 | 0.069463 | 0.00085029 | 81.6928
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | NONE | 25 | 4272 | 347880 | 0.32222 | 0.0039569 | 81.4326
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 23 | 65 | 17993 | 0.016666 | 6.0206e-05 | 276.8154
AEP-TX | 2022 | 1090914 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 44 | 4.0333e-05 | 9.1666e-07 | 44
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | BREAKER | 39 | 34823 | 3541105 | 3.246 | 0.031921 | 101.6887
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERO | METERING | 4 | 4 | 326 | 0.00029883 | 3.6667e-06 | 81.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | FO | NONE | 5 | 6516 | 768258 | 0.72145 | 0.006119 | 117.9033
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | SWITCH, UG | 1 | 6 | 378 | 0.00035497 | 5.6345e-06 | 63
AEP-TX | 2020 | 1064875 | PARTIAL POWER | FO | NONE | 3 | 4 | 414 | 0.00038878 | 3.7563e-06 | 103.5
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TOR | CONN/CLAMP | 115 | 115 | 12553 | 0.011788 | 0.00010799 | 109.1565
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | POLE | 45 | 10417 | 1107668 | 1.0402 | 0.0097824 | 106.3327
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | CONN/CLAMP | 5 | 73 | 4455 | 0.0041264 | 6.7616e-05 | 61.0274
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 85 | 551 | 99127 | 0.091816 | 0.00051036 | 179.9038
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | WL | NONE | 24 | 11874 | 1533562 | 1.4401 | 0.011151 | 129.1529
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | METERING | 146 | 163 | 18979 | 0.017263 | 0.00014826 | 116.4356
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 63 | 2204 | 0.0020203 | 5.775e-05 | 34.9841
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | POLE HARDWARE | 6 | 944 | 162942 | 0.15092 | 0.00087437 | 172.6081
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 5 | 99 | 14119 | 0.013078 | 9.1698e-05 | 142.6162
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | CONN/CLAMP | 56 | 173 | 21295 | 0.01937 | 0.00015736 | 123.0925
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | JUMPER/RISER | 22 | 4587 | 739238 | 0.67241 | 0.0041723 | 161.1594
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 110 | 10084 | 1113778 | 1.0013 | 0.009066 | 110.45
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | METERING | 15 | 16 | 1783 | 0.0016218 | 1.4554e-05 | 111.4375
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | SPLICE, OH | 2 | 2 | 676 | 0.00061966 | 1.8333e-06 | 338
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 2 | 7 | 554 | 0.00051314 | 6.4837e-06 | 79.1429
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | POLE HARDWARE | 7 | 1450 | 156950 | 0.14111 | 0.0013036 | 108.2414
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | INSULATOR | 4 | 194 | 60468 | 0.055429 | 0.00017783 | 311.6907
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | CUTOUT | 32 | 1620 | 169259 | 0.15217 | 0.0014565 | 104.4809
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 69 | 541 | 166919 | 0.15007 | 0.00048639 | 308.5379
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | SPLICE, UG | 1 | 1 | 500 | 0.0004548 | 9.0959e-07 | 500
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | CIRCUIT SWITCHER | 3 | 311 | 23526 | 0.021399 | 0.00028288 | 75.6463
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | NONE | 830 | 26632 | 2365373 | 2.1266 | 0.023944 | 88.8169
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WH | NONE | 6 | 6 | 1002 | 0.00094096 | 5.6345e-06 | 167
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | POLE | 5 | 316 | 31103 | 0.027963 | 0.0002841 | 98.4272
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 3 | 858 | 0.00077139 | 2.6972e-06 | 286
AEP-TX | 2025 | 1112283 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 84 | 7.552e-05 | 8.9905e-07 | 84
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | INSULATOR | 5 | 664 | 96398 | 0.089288 | 0.00061502 | 145.1777
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | POLE | 3 | 3 | 628 | 0.0005646 | 2.6972e-06 | 209.3333
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 123 | 0.00011551 | 9.3908e-07 | 123
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 3 | 1002 | 0.00090085 | 2.6972e-06 | 334
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 4 | 32 | 3688 | 0.0033157 | 2.877e-05 | 115.25
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | METERING | 3 | 3 | 136 | 0.00012771 | 2.8172e-06 | 45.3333
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 1 | 254 | 0.00023853 | 9.3908e-07 | 254
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 5 | 715 | 0.00064282 | 4.4953e-06 | 143
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 218 | 0.00019599 | 8.9905e-07 | 218
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | GUY/ANCHOR | 1 | 57 | 11400 | 0.010369 | 5.1847e-05 | 200
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | METERING | 2 | 2 | 231 | 0.00020768 | 1.7981e-06 | 115.5
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 3 | 90 | 8.3362e-05 | 2.7787e-06 | 30
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 4 | 59 | 13833 | 0.012582 | 5.3666e-05 | 234.4576
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 36 | 4572 | 0.0041587 | 3.2745e-05 | 127
AEP-TX | 2024 | 1112283 | PARTIAL POWER | ERF | NONE | 1 | 3 | 261 | 0.00023465 | 2.6972e-06 | 87
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | R | POLE | 2 | 58 | 15156 | 0.013786 | 5.2756e-05 | 261.3103
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | CROSSARM | 285 | 42915 | 5084592 | 4.6609 | 0.039339 | 118.4805
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | CONN/CLAMP | 1391 | 3779 | 424981 | 0.38956 | 0.0034641 | 112.4586
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | ARRESTER | 324 | 8314 | 873184 | 0.80878 | 0.0077008 | 105.0257
AEP-TX | 2021 | 1079632 | PARTIAL POWER | OL | NONE | 14 | 33 | 2490 | 0.0023063 | 3.0566e-05 | 75.4545
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 5 | 2883 | 188742 | 0.17301 | 0.0026427 | 65.4672
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | JUMPER/RISER | 5 | 2444 | 517298 | 0.47419 | 0.0022403 | 211.6604
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | ARRESTER | 122 | 2534 | 357856 | 0.33605 | 0.0023796 | 141.2218
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | NONE | 163 | 25044 | 2651049 | 2.4895 | 0.023518 | 105.8557
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | CONN/CLAMP | 32 | 411 | 64403 | 0.060479 | 0.00038596 | 156.6983
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 141 | 0.00013241 | 9.3908e-07 | 141
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 1 | 285 | 0.00026398 | 9.2624e-07 | 285
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | JUMPER/RISER | 22 | 1969 | 339629 | 0.31458 | 0.0018238 | 172.4881
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 58 | 13965 | 0.012801 | 5.3166e-05 | 240.7759
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | CUTOUT | 59 | 582 | 98028 | 0.092056 | 0.00054654 | 168.433
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | CUTOUT | 5 | 19 | 1568 | 0.0014523 | 1.7599e-05 | 82.5263
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | NONE | 109 | 640 | 82947 | 0.075448 | 0.00058214 | 129.6047
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WT | POLE | 3 | 74 | 116463 | 0.10787 | 6.8542e-05 | 1573.8243
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | TRANSFORMER, OH | 4 | 39 | 10491 | 0.0097172 | 3.6123e-05 | 269
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | ARRESTER | 36 | 822 | 81897 | 0.076908 | 0.00077192 | 99.6314
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | CROSSARM | 9 | 4885 | 489674 | 0.45984 | 0.0045874 | 100.2403
AEP-TX | 2022 | 1090914 | PARTIAL POWER | ERF | NONE | 3 | 14 | 739 | 0.00067741 | 1.2833e-05 | 52.7857
AEP-TX | 2023 | 1099391 | PARTIAL POWER | ABI | NONE | 31 | 98 | 6755 | 0.0061443 | 8.914e-05 | 68.9286
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VIN | NONE | 125 | 1185 | 115907 | 0.10543 | 0.0010779 | 97.8118
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | METERING | 1085 | 1357 | 131907 | 0.11859 | 0.00122 | 97.2049
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | CONN/CLAMP | 1237 | 2746 | 260469 | 0.23418 | 0.0024688 | 94.854
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | CUTOUT | 475 | 14372 | 1295451 | 1.1647 | 0.012921 | 90.1371
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 12 | 19 | 5710 | 0.0051938 | 1.7282e-05 | 300.5263
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | NONE | 1622 | 24115 | 2186035 | 1.9654 | 0.021681 | 90.6504
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 10 | 3941 | 317033 | 0.29061 | 0.0036126 | 80.4448
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | CROSSARM | 2 | 3 | 153 | 0.00013917 | 2.7288e-06 | 51
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 1 | 116 | 0.00010744 | 9.2624e-07 | 116
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 4 | 799 | 0.00074007 | 3.705e-06 | 199.75
AEP-TX | 2021 | 1079632 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 96 | 22752 | 0.021074 | 8.8919e-05 | 237
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | CONDUCTOR UG | 6 | 10 | 1932 | 0.0017573 | 9.0959e-06 | 193.2
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 776 | 14293 | 0.013001 | 0.00070585 | 18.4188
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 3 | 1119 | 979136 | 0.89062 | 0.0010178 | 875.0098
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 71 | 6.5083e-05 | 9.1666e-07 | 71
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AF | SWITCH, OH | 1 | 16 | 1568 | 0.0014262 | 1.4554e-05 | 98
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | NETWORK LIMITER | 1 | 2 | 298 | 0.00026792 | 1.7981e-06 | 149
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TIR | JUMPER/RISER | 2 | 29 | 6068 | 0.0056204 | 2.6861e-05 | 209.2414
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 1 | 90 | 8.4517e-05 | 9.3908e-07 | 90
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 863 | 6904 | 0.0062071 | 0.00077588 | 8
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | UB | TRANSFORMER, OH | 1 | 3 | 804 | 0.00072284 | 2.6972e-06 | 268
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | INSULATOR | 1 | 1 | 99 | 9.005e-05 | 9.0959e-07 | 99
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | NONE | 189 | 9531 | 1081841 | 0.99168 | 0.0087367 | 113.5076
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | CROSSARM | 18 | 1987 | 180656 | 0.16733 | 0.0018404 | 90.919
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | SWITCH, OH | 2 | 430 | 48320 | 0.044293 | 0.00039416 | 112.3721
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 292 | 292 | 45927 | 0.042539 | 0.00027046 | 157.2842
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | INSULATOR | 13 | 331 | 48603 | 0.044553 | 0.00030342 | 146.8369
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 9 | 37 | 3187 | 0.0029214 | 3.3917e-05 | 86.1351
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | JUMPER/RISER | 13 | 904 | 86059 | 0.078887 | 0.00082866 | 95.198
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 3 | 14 | 1074 | 0.00099478 | 1.2967e-05 | 76.7143
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 90 | 18309 | 0.016783 | 8.25e-05 | 203.4333
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | CONDUCTOR UG | 74 | 187 | 30969 | 0.028685 | 0.00017321 | 165.6096
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 390 | 4397 | 978810 | 0.91918 | 0.0041291 | 222.6086
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TOR | NONE | 56 | 56 | 9056 | 0.0085043 | 5.2588e-05 | 161.7143
AEP-TX | 2022 | 1090914 | PARTIAL POWER | VA | POLE | 1 | 1 | 49 | 4.4916e-05 | 9.1666e-07 | 49
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | NONE | 63 | 8477 | 650322 | 0.6107 | 0.0079606 | 76.7161
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | CUTOUT | 9 | 14 | 4580 | 0.0042422 | 1.2967e-05 | 327.1429
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 16 | 76 | 9608 | 0.0088993 | 7.0394e-05 | 126.4211
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | ARRESTER | 8 | 23 | 2380 | 0.0021817 | 2.1083e-05 | 103.4783
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 12 | 124 | 34470 | 0.031597 | 0.00011367 | 277.9839
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 22 | 76 | 20550 | 0.019298 | 7.137e-05 | 270.3947
AEP-TX | 2022 | 1090914 | PARTIAL POWER | UB | NONE | 1 | 1 | 144 | 0.000132 | 9.1666e-07 | 144
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | CUTOUT | 58 | 124 | 17116 | 0.015569 | 0.00011279 | 138.0323
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | SPLICE, OH | 5 | 352 | 29378 | 0.027211 | 0.00032604 | 83.4602
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | CIRCUIT SWITCHER | 8 | 5598 | 418173 | 0.38733 | 0.0051851 | 74.7004
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | SWITCH, OH | 6 | 6770 | 744601 | 0.68255 | 0.0062058 | 109.9854
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 247 | 2782 | 416369 | 0.37873 | 0.0025305 | 149.6653
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 5 | 5 | 477 | 0.00044794 | 4.6954e-06 | 95.4
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | TRANSFORMER, UG | 1 | 32 | 11968 | 0.011239 | 3.005e-05 | 374
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | TRANSFORMER, UG | 12 | 101 | 18172 | 0.017065 | 9.4847e-05 | 179.9208
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 135 | 0.00012375 | 9.1666e-07 | 135
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | POLE HARDWARE | 4 | 94 | 19135 | 0.017969 | 8.8273e-05 | 203.5638
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | ARRESTER | 18 | 412 | 24002 | 0.021832 | 0.00037475 | 58.2573
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 52 | 339 | 55610 | 0.050583 | 0.00030835 | 164.0413
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | POLE HARDWARE | 3 | 613 | 128627 | 0.117 | 0.00055758 | 209.832
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | PEDESTAL | 1 | 22 | 14366 | 0.013306 | 2.0377e-05 | 653
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WU | NONE | 54 | 114 | 11681 | 0.010625 | 0.00010369 | 102.4649
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | ABX | NONE | 3 | 102 | 11554 | 0.010591 | 9.35e-05 | 113.2745
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WT | NONE | 1 | 11 | 2728 | 0.0024814 | 1.0006e-05 | 248
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | AF | NONE | 42 | 17260 | 1322968 | 1.1894 | 0.015518 | 76.6494
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WW | CONN/CLAMP | 3 | 8 | 976 | 0.00088776 | 7.2768e-06 | 122
AEP-TX | 2023 | 1099391 | PARTIAL POWER | OL | JUMPER/RISER | 2 | 23 | 3133 | 0.0028498 | 2.0921e-05 | 136.2174
AEP-TX | 2022 | 1090914 | PARTIAL POWER | OL | TRANSFORMER, OH | 2 | 19 | 1907 | 0.0017481 | 1.7417e-05 | 100.3684
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WH | CONN/CLAMP | 1 | 1 | 1120 | 0.0010069 | 8.9905e-07 | 1120
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 2 | 1032 | 111643 | 0.10155 | 0.0009387 | 108.1812
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TR | METERING | 1 | 24 | 1224 | 0.0011133 | 2.183e-05 | 51
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 52 | 135 | 26977 | 0.024254 | 0.00012137 | 199.8296
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 5 | 28 | 1457 | 0.0013099 | 2.5173e-05 | 52.0357
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | POLE | 11 | 362 | 43048 | 0.038702 | 0.00032546 | 118.9171
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 175 | 0.00015733 | 8.9905e-07 | 175
AEP-TX | 2025 | 1112283 | PARTIAL POWER | A | NONE | 11 | 101 | 3684 | 0.0033121 | 9.0804e-05 | 36.4752
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | RECLOSER, LINE/OCR/BR | 2 | 600 | 47334 | 0.04445 | 0.00056345 | 78.89
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 189 | 0.00017325 | 1.8333e-06 | 94.5
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | SWITCH, UG | 1 | 1 | 88 | 8.2639e-05 | 9.3908e-07 | 88
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 4 | 330 | 0.00029669 | 3.5962e-06 | 82.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | FO | INSULATOR | 1 | 741 | 6669 | 0.0059958 | 0.0006662 | 9
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 3 | 232 | 21478 | 0.02017 | 0.00021787 | 92.5776
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | CROSSARM | 1 | 3 | 2082 | 0.0018718 | 2.6972e-06 | 694
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 40 | 20217 | 0.018389 | 3.6384e-05 | 505.425
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 3 | 11 | 4316 | 0.0040531 | 1.033e-05 | 392.3636
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 3 | 3 | 621 | 0.00056486 | 2.7288e-06 | 207
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 2 | 68 | 17696 | 0.01591 | 6.1136e-05 | 260.2353
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | AO | INSULATOR | 3 | 974 | 392849 | 0.35319 | 0.00087568 | 403.3357
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | GUY/ANCHOR | 1 | 2 | 488 | 0.00044388 | 1.8192e-06 | 244
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | METERING | 1 | 2 | 182 | 0.00016363 | 1.7981e-06 | 91
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 8 | 2616 | 0.0023795 | 7.2768e-06 | 327
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | ARRESTER | 3 | 333 | 7659 | 0.0071924 | 0.00031271 | 23
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 7 | 1295 | 0.0012161 | 6.5735e-06 | 185
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 996 | 73718 | 0.067575 | 0.000913 | 74.0141
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | AF | CONDUCTOR OVERHEAD | 1 | 19 | 3078 | 0.002851 | 1.7599e-05 | 162
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | INSULATOR | 1 | 1 | 105 | 9.625e-05 | 9.1666e-07 | 105
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AB | BREAKER | 1 | 1406 | 102638 | 0.094084 | 0.0012888 | 73
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 1 | 57 | 5.3527e-05 | 9.3908e-07 | 57
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | POLE | 364 | 23265 | 3338105 | 3.0363 | 0.021162 | 143.4818
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | METERING | 1606 | 1832 | 171532 | 0.15724 | 0.0016793 | 93.631
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | NONE | 48 | 19322 | 1710253 | 1.5841 | 0.017897 | 88.5132
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TR | NONE | 21 | 735 | 64357 | 0.058994 | 0.00067375 | 87.5605
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1207 | 6214 | 635937 | 0.58294 | 0.0056961 | 102.3394
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | NONE | 218 | 1618 | 157907 | 0.14626 | 0.0014987 | 97.5939
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 1 | 141 | 0.00012925 | 9.1666e-07 | 141
AEP-TX | 2022 | 1090914 | PARTIAL POWER | A | OTHER EQUIPMENT | 1 | 1 | 47 | 4.3083e-05 | 9.1666e-07 | 47
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERO | CONN/CLAMP | 1 | 1 | 161 | 0.00014758 | 9.1666e-07 | 161
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TIR | NONE | 90 | 414 | 62143 | 0.058357 | 0.00038878 | 150.1039
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | NONE | 224 | 618 | 66303 | 0.062264 | 0.00058035 | 107.2864
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | INSULATOR | 76 | 15788 | 1703279 | 1.5995 | 0.014826 | 107.8844
AEP-TX | 2020 | 1064875 | PARTIAL POWER | U | NONE | 88 | 255 | 33629 | 0.03158 | 0.00023946 | 131.8784
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 301 | 0.0002788 | 1.8525e-06 | 150.5
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | NONE | 1060 | 9903 | 816211 | 0.74242 | 0.0090077 | 82.4206
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WFS | SPLICE, UG | 1 | 1 | 196 | 0.00018154 | 9.2624e-07 | 196
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | ABI | NONE | 8 | 9038 | 863880 | 0.79189 | 0.0082848 | 95.5831
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | SWITCH, OH | 8 | 1913 | 111543 | 0.10225 | 0.0017536 | 58.3079
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 4 | 13 | 1898 | 0.001758 | 1.2041e-05 | 146
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 4 | 3386 | 162832 | 0.14926 | 0.0031038 | 48.0898
AEP-TX | 2023 | 1099391 | PARTIAL POWER | OL | TRANSFORMER, OH | 6 | 15 | 1525 | 0.0013871 | 1.3644e-05 | 101.6667
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 1150 | 8050 | 0.0074562 | 0.0010652 | 7
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 85 | 7.8731e-05 | 9.2624e-07 | 85
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | PEDESTAL | 19 | 73 | 13404 | 0.012192 | 6.64e-05 | 183.6164
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | POLE | 53 | 1869 | 489853 | 0.44557 | 0.0017 | 262.0936
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WL | NONE | 99 | 351 | 52111 | 0.0474 | 0.00031927 | 148.4644
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | SWITCH, OH | 12 | 7874 | 960815 | 0.87395 | 0.0071621 | 122.0237
AEP-TX | 2023 | 1099391 | PARTIAL POWER | VA | POLE | 2 | 27 | 2159 | 0.0019638 | 2.4559e-05 | 79.963
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | NONE | 43 | 1824 | 865517 | 0.81279 | 0.0017129 | 474.5159
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | CROSSARM | 4 | 121 | 3639 | 0.0034173 | 0.00011363 | 30.0744
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | CUTOUT | 8 | 18 | 2439 | 0.0022904 | 1.6903e-05 | 135.5
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | JUMPER/RISER | 1 | 10 | 3010 | 0.0028266 | 9.3908e-06 | 301
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | NONE | 74 | 184 | 22562 | 0.020284 | 0.00016543 | 122.6196
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | A | CUTOUT | 9 | 58 | 3253 | 0.0029589 | 5.2756e-05 | 56.0862
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | PEDESTAL | 1 | 16 | 4832 | 0.0043952 | 1.4554e-05 | 302
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | JUMPER/RISER | 20 | 4965 | 643515 | 0.57855 | 0.0044638 | 129.6103
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 1 | 368 | 0.00033473 | 9.0959e-07 | 368
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WH | POLE | 2 | 19 | 918 | 0.00085029 | 1.7599e-05 | 48.3158
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | WU | NONE | 5 | 3289 | 399712 | 0.37023 | 0.0030464 | 121.5299
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 19 | 1355 | 332185 | 0.29865 | 0.0012182 | 245.155
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 3506 | 396533 | 0.36068 | 0.003189 | 113.1013
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ERF | NONE | 11 | 9301 | 149024 | 0.13398 | 0.0083621 | 16.0224
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | INSULATOR | 3 | 628 | 35077 | 0.031536 | 0.0005646 | 55.8551
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | METERING | 7 | 7 | 696 | 0.0006536 | 6.5735e-06 | 99.4286
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | NONE | 35 | 209 | 51745 | 0.048593 | 0.00019627 | 247.5837
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | JUMPER/RISER | 4 | 302 | 31863 | 0.028982 | 0.0002747 | 105.5066
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | INSULATOR | 11 | 1224 | 112856 | 0.10265 | 0.0011133 | 92.2026
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | JUMPER/RISER | 89 | 2192 | 252152 | 0.22936 | 0.0019938 | 115.0328
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | POLE | 2 | 2 | 159 | 0.00014575 | 1.8333e-06 | 79.5
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 2 | 5 | 822 | 0.00076137 | 4.6312e-06 | 164.4
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | CUTOUT | 17 | 983 | 72355 | 0.065814 | 0.00089413 | 73.6063
AEP-TX | 2020 | 1064875 | PARTIAL POWER | OL | CABLE TERMINATOR | 2 | 2 | 237 | 0.00022256 | 1.8782e-06 | 118.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 688 | 29232 | 4967870 | 4.4664 | 0.026281 | 169.9463
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | CONN/CLAMP | 45 | 139 | 18313 | 0.016464 | 0.00012497 | 131.7482
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | CUTOUT | 7 | 377 | 38364 | 0.036027 | 0.00035403 | 101.7613
AEP-TX | 2020 | 1064875 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 159 | 0.00014931 | 9.3908e-07 | 159
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | WU | NONE | 13 | 8656 | 875585 | 0.79643 | 0.0078734 | 101.1535
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 3 | 29 | 10149 | 0.0092315 | 2.6378e-05 | 349.9655
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 3 | 11 | 2062 | 0.0018538 | 9.8896e-06 | 187.4545
AEP-TX | 2024 | 1112283 | PARTIAL POWER | VIN | CONN/CLAMP | 4 | 4 | 421 | 0.0003785 | 3.5962e-06 | 105.25
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | ARRESTER | 19 | 110 | 17683 | 0.015898 | 9.8896e-05 | 160.7545
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TOR | JUMPER/RISER | 2 | 2 | 218 | 0.00019829 | 1.8192e-06 | 109
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CF | NONE | 19 | 32 | 3103 | 0.0027898 | 2.877e-05 | 96.9688
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | BREAKER | 4 | 2056 | 251366 | 0.22864 | 0.0018701 | 122.2597
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | CROSSARM | 14 | 424 | 128610 | 0.11563 | 0.0003812 | 303.3255
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 10 | 964 | 130224 | 0.11708 | 0.00086669 | 135.0871
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ABI | REGULATOR | 1 | 159 | 13674 | 0.012438 | 0.00014463 | 86
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WU | CUTOUT | 1 | 2 | 90 | 8.0915e-05 | 1.7981e-06 | 45
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | CROSSARM | 3 | 14 | 2086 | 0.0019589 | 1.3147e-05 | 149
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 577 | 5969 | 676205 | 0.60794 | 0.0053664 | 113.2861
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 216 | 10398 | 968023 | 0.8703 | 0.0093483 | 93.097
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 99 | 99 | 13435 | 0.012079 | 8.9006e-05 | 135.7071
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | METERING | 254 | 289 | 23591 | 0.02121 | 0.00025983 | 81.6298
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | ARRESTER | 10 | 152 | 23718 | 0.021324 | 0.00013666 | 156.0395
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 10 | 1158 | 95102 | 0.085502 | 0.0010411 | 82.1261
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | JUMPER/RISER | 4 | 726 | 73687 | 0.066248 | 0.00065271 | 101.4972
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 7 | 794 | 97213 | 0.0874 | 0.00071385 | 122.4345
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | CABLE TERMINATOR | 1 | 1 | 45 | 4.125e-05 | 9.1666e-07 | 45
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 1 | 26 | 2.3833e-05 | 9.1666e-07 | 26
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 3 | 57 | 9425 | 0.0087298 | 5.2796e-05 | 165.3509
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | SPLICE, UG | 2 | 7 | 1999 | 0.0018324 | 6.4166e-06 | 285.5714
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | GUY/ANCHOR | 1 | 1 | 151 | 0.00013842 | 9.1666e-07 | 151
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 3 | 1361 | 211554 | 0.1902 | 0.0012236 | 155.4401
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | METERING | 11 | 13 | 963 | 0.00086579 | 1.1688e-05 | 74.0769
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 1 | 113 | 0.00010159 | 8.9905e-07 | 113
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 271 | 49051 | 0.044617 | 0.0002465 | 181
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AO | BREAKER | 2 | 291 | 16196 | 0.014732 | 0.00026469 | 55.6564
AEP-TX | 2024 | 1112283 | PARTIAL POWER | OL | JUMPER/RISER | 7 | 76 | 8778 | 0.0078919 | 6.8328e-05 | 115.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 1 | 241 | 0.00021667 | 8.9905e-07 | 241
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 8 | 192 | 0.00017262 | 7.1924e-06 | 24
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | O | NONE | 2 | 2711 | 181878 | 0.16352 | 0.0024373 | 67.0889
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | EQF | CROSSARM | 1 | 3 | 1365 | 0.0012272 | 2.6972e-06 | 455
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 1 | 96 | 8.6309e-05 | 8.9905e-07 | 96
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | SWITCH, UG | 1 | 65 | 8255 | 0.0074217 | 5.8438e-05 | 127
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 167 | 7123 | 0.0065294 | 0.00015308 | 42.6527
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 28 | 26328 | 0.024134 | 2.5667e-05 | 940.2857
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | RECLOSER, LINE/OCR/BR | 1 | 491 | 64321 | 0.057828 | 0.00044143 | 131
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 6 | 552 | 0.0005021 | 5.4576e-06 | 92
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WI | NONE | 1 | 7 | 392 | 0.00035243 | 6.2934e-06 | 56
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | NONE | 1944 | 40101 | 4241498 | 3.888 | 0.036759 | 105.7704
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | CROSSARM | 261 | 27466 | 3829509 | 3.5471 | 0.02544 | 139.4273
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 2 | 38 | 1288 | 0.0011807 | 3.4833e-05 | 33.8947
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | NONE | 152 | 483 | 90594 | 0.083912 | 0.00044737 | 187.5652
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | FO | CUTOUT | 5 | 33 | 6595 | 0.0060454 | 3.025e-05 | 199.8485
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | A | METERING | 14 | 14 | 1613 | 0.0014786 | 1.2833e-05 | 115.2143
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 133 | 10085 | 0.0092445 | 0.00012192 | 75.8271
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1814 | 10414 | 2040376 | 1.9161 | 0.0097796 | 195.9263
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | JUMPER/RISER | 30 | 234 | 30285 | 0.027761 | 0.0002145 | 129.4231
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | NONE | 3360 | 90323 | 14354959 | 13.4804 | 0.08482 | 158.9292
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 4 | 1991 | 309149 | 0.29031 | 0.0018697 | 155.2732
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | METERING | 15 | 16 | 3301 | 0.0030999 | 1.5025e-05 | 206.3125
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | SPLICE, OH | 3 | 3 | 262 | 0.00024604 | 2.8172e-06 | 87.3333
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 167 | 50219 | 7587415 | 7.1252 | 0.04716 | 151.0865
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TR | NONE | 33 | 1113 | 102428 | 0.096188 | 0.0010452 | 92.0288
AEP-TX | 2021 | 1079632 | PARTIAL POWER | ABI | ARRESTER | 2 | 2 | 515 | 0.00047701 | 1.8525e-06 | 257.5
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 604 | 135590 | 0.12559 | 0.00055945 | 224.4868
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 2 | 63 | 8778 | 0.0080465 | 5.775e-05 | 139.3333
AEP-TX | 2021 | 1079632 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 5 | 5 | 456 | 0.00042237 | 4.6312e-06 | 91.2
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | POLE | 14 | 56 | 12953 | 0.011998 | 5.187e-05 | 231.3036
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | POLE | 14 | 352 | 102346 | 0.094797 | 0.00032604 | 290.7557
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 1 | 516 | 0.000473 | 9.1666e-07 | 516
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 4 | 15 | 1826 | 0.0016913 | 1.3894e-05 | 121.7333
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 211 | 0.00019544 | 9.2624e-07 | 211
AEP-TX | 2022 | 1090914 | PARTIAL POWER | OL | METERING | 2 | 2 | 273 | 0.00025025 | 1.8333e-06 | 136.5
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 599 | 15269 | 0.013997 | 0.00054908 | 25.4908
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 58 | 27176 | 0.02552 | 5.4466e-05 | 468.5517
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WW | POLE HARDWARE | 2 | 133 | 62417 | 0.058614 | 0.0001249 | 469.3008
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | METERING | 11 | 12 | 1330 | 0.0012098 | 1.0915e-05 | 110.8333
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | JUMPER/RISER | 55 | 416 | 52128 | 0.047415 | 0.00037839 | 125.3077
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 8 | 77 | 21023 | 0.019122 | 7.0039e-05 | 273.026
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | ERF | NONE | 3 | 5736 | 235863 | 0.22149 | 0.0053865 | 41.1198
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 22 | 8529 | 1225431 | 1.1146 | 0.0077579 | 143.6782
AEP-TX | 2024 | 1112283 | PARTIAL POWER | OL | NONE | 105 | 342 | 27955 | 0.025133 | 0.00030748 | 81.7398
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 91 | 8.2773e-05 | 9.0959e-07 | 91
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | CUTOUT | 29 | 2348 | 127550 | 0.11602 | 0.0021357 | 54.3228
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WU | NONE | 75 | 143 | 16186 | 0.014552 | 0.00012856 | 113.1888
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TR | POLE | 2 | 128 | 27916 | 0.025098 | 0.00011508 | 218.0938
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | SPLICE, OH | 14 | 35 | 4945 | 0.0044458 | 3.1467e-05 | 141.2857
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | JUMPER/RISER | 4 | 13 | 841 | 0.00077091 | 1.1917e-05 | 64.6923
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 5 | 380 | 0.00034565 | 4.548e-06 | 76
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AB | NONE | 10 | 8288 | 792941 | 0.72125 | 0.0075387 | 95.6734
AEP-TX | 2023 | 1099391 | PARTIAL POWER | VIN | CONN/CLAMP | 3 | 3 | 255 | 0.00023195 | 2.7288e-06 | 85
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | INSULATOR | 6 | 1691 | 298757 | 0.2686 | 0.0015203 | 176.6747
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | INSULATOR | 1 | 2360 | 292706 | 0.26831 | 0.0021633 | 124.028
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | OL | CUTOUT | 4 | 95 | 17363 | 0.016082 | 8.7993e-05 | 182.7684
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | ARRESTER | 2 | 384 | 92928 | 0.084527 | 0.00034928 | 242
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 1082 | 88292 | 0.079379 | 0.00097277 | 81.6007
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | REGULATOR | 5 | 1422 | 25953 | 0.023333 | 0.0012785 | 18.2511
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 10 | 144 | 25370 | 0.022809 | 0.00012946 | 176.1806
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | POLE | 73 | 8616 | 916167 | 0.82368 | 0.0077462 | 106.3332
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 21 | 1587 | 168628 | 0.15161 | 0.0014268 | 106.2558
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | PEDESTAL | 4 | 24 | 3636 | 0.003269 | 2.1577e-05 | 151.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | CF | NONE | 1 | 414 | 50922 | 0.045782 | 0.00037221 | 123
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 2 | 354 | 0.00033243 | 1.8782e-06 | 177
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 126 | 0.00011832 | 9.3908e-07 | 126
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WI | NONE | 3 | 3 | 503 | 0.0004659 | 2.7787e-06 | 167.6667
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | TRANSFORMER, UG | 1 | 1 | 467 | 0.00042478 | 9.0959e-07 | 467
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | CF | INSULATOR | 1 | 398 | 87162 | 0.078363 | 0.00035782 | 219
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | CONDUCTOR UG | 2 | 3 | 7163 | 0.0067266 | 2.8172e-06 | 2387.6667
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | CUTOUT | 5 | 38 | 6291 | 0.0056559 | 3.4164e-05 | 165.5526
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WH | CONDUCTOR OVERHEAD | 1 | 1 | 77 | 7.2309e-05 | 9.3908e-07 | 77
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | CROSSARM | 1 | 1 | 50 | 4.4953e-05 | 8.9905e-07 | 50
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 582 | 96319 | 0.086596 | 0.00052325 | 165.4966
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 1 | 65 | 5.8438e-05 | 8.9905e-07 | 65
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | POLE | 1 | 1 | 84 | 7.552e-05 | 8.9905e-07 | 84
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 4207 | 208847 | 0.18776 | 0.0037823 | 49.6427
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | UB | CONN/CLAMP | 2 | 4 | 163 | 0.00014655 | 3.5962e-06 | 40.75
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 1 | 48 | 4.446e-05 | 9.2624e-07 | 48
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 11 | 1826 | 0.0017148 | 1.033e-05 | 166
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | INSULATOR | 4 | 26 | 2298 | 0.002066 | 2.3375e-05 | 88.3846
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 1 | 6 | 1428 | 0.0012838 | 5.3943e-06 | 238
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VIN | ARRESTER | 4 | 21 | 3788 | 0.0034056 | 1.888e-05 | 180.381
AEP-TX | 2025 | 1112283 | PARTIAL POWER | OL | CUTOUT | 1 | 13 | 260 | 0.00023375 | 1.1688e-05 | 20
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | TRANSFORMER, GROUNDING | 1 | 3 | 166 | 0.00014924 | 2.6972e-06 | 55.3333
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | AF | CROSSARM | 2 | 1711 | 131034 | 0.11781 | 0.0015383 | 76.5833
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | OL | POLE HARDWARE | 1 | 5 | 690 | 0.00062035 | 4.4953e-06 | 138
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 1 | 79 | 7.2416e-05 | 9.1666e-07 | 79
AEP-TX | 2023 | 1099391 | PARTIAL POWER | OL | TRANSFORMER, UG | 1 | 22 | 2508 | 0.0022813 | 2.0011e-05 | 114
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | RELAY | 1 | 933 | 124089 | 0.11653 | 0.00087616 | 133
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | NETWORK LIMITER | 1 | 362 | 60092 | 0.056431 | 0.00033995 | 166
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 5 | 128 | 46677 | 0.043833 | 0.0001202 | 364.6641
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WU | JUMPER/RISER | 1 | 26 | 4004 | 0.003642 | 2.3649e-05 | 154
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 25 | 4125 | 0.0037086 | 2.2476e-05 | 165
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | ABX | NONE | 3 | 202 | 13368 | 0.012554 | 0.00018969 | 66.1782
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | TRANSFORMER, UG | 1 | 1 | 58 | 5.4466e-05 | 9.3908e-07 | 58
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1982 | 10456 | 2164273 | 2.0046 | 0.0096848 | 206.9886
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 65 | 321 | 64565 | 0.059184 | 0.00029425 | 201.1371
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | NONE | 340 | 351 | 45177 | 0.041412 | 0.00032175 | 128.7094
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | ARRESTER | 351 | 8452 | 919247 | 0.84264 | 0.0077476 | 108.7609
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | REGULATOR | 6 | 2944 | 153641 | 0.14084 | 0.0026987 | 52.1878
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | POLE | 322 | 18272 | 3505561 | 3.247 | 0.016924 | 191.8543
AEP-TX | 2022 | 1090914 | PARTIAL POWER | OL | NONE | 99 | 331 | 29474 | 0.027018 | 0.00030342 | 89.0453
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | NONE | 86 | 10646 | 1025263 | 0.94964 | 0.0098608 | 96.305
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 26 | 461 | 131345 | 0.12166 | 0.000427 | 284.9132
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | AF | ARRESTER | 2 | 756 | 75216 | 0.068948 | 0.000693 | 99.4921
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CO | ARRESTER | 11 | 96 | 8775 | 0.0080437 | 8.8e-05 | 91.4062
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | ARRESTER | 10 | 87 | 5016 | 0.0047104 | 8.17e-05 | 57.6552
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | POLE HARDWARE | 6 | 2277 | 520350 | 0.47699 | 0.0020872 | 228.5244
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 89 | 9547 | 1075458 | 1.0099 | 0.0089654 | 112.6488
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 431 | 431 | 67485 | 0.063374 | 0.00040474 | 156.5777
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | CONN/CLAMP | 659 | 2649 | 388090 | 0.36445 | 0.0024876 | 146.5043
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 17 | 247 | 118047 | 0.11086 | 0.00023195 | 477.9231
AEP-TX | 2021 | 1079632 | PARTIAL POWER | FO | NONE | 12 | 43 | 2900 | 0.0026861 | 3.9828e-05 | 67.4419
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CF | CONN/CLAMP | 96 | 192 | 22122 | 0.020774 | 0.0001803 | 115.2188
AEP-TX | 2021 | 1079632 | PARTIAL POWER | ABI | NONE | 33 | 82 | 5742 | 0.0053185 | 7.5952e-05 | 70.0244
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | RECLOSER, LINE/OCR/BR | 3 | 736 | 91300 | 0.083691 | 0.00067466 | 124.0489
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | CROSSARM | 13 | 511 | 122991 | 0.11274 | 0.00046841 | 240.6869
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 4 | 1370 | 119036 | 0.11178 | 0.0012865 | 86.8876
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 187 | 477 | 67937 | 0.061795 | 0.00043388 | 142.4256
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CF | ARRESTER | 6 | 33 | 2189 | 0.0020275 | 3.0566e-05 | 66.3333
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 19 | 118 | 18073 | 0.016972 | 0.00011081 | 153.161
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | ARRESTER | 9 | 4498 | 495978 | 0.4594 | 0.0041662 | 110.2663
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 3 | 4 | 1073 | 0.00098358 | 3.6667e-06 | 268.25
AEP-TX | 2023 | 1099391 | PARTIAL POWER | U | NONE | 239 | 603 | 52198 | 0.047479 | 0.00054849 | 86.5638
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 303 | 4441 | 1030270 | 0.93713 | 0.0040395 | 231.9905
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 4 | 13 | 584 | 0.00054842 | 1.2208e-05 | 44.9231
AEP-TX | 2020 | 1064875 | PARTIAL POWER | VA | POLE | 2 | 4 | 644 | 0.00060477 | 3.7563e-06 | 161
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | METERING | 2 | 2 | 1022 | 0.00093683 | 1.8333e-06 | 511
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 21 | 6867 | 1219395 | 1.1092 | 0.0062462 | 177.5732
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | NONE | 13 | 35 | 3186 | 0.002898 | 3.1836e-05 | 91.0286
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 12 | 39 | 5243 | 0.004769 | 3.5474e-05 | 134.4359
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | ARRESTER | 3 | 269 | 105873 | 0.09705 | 0.00024658 | 393.5799
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | ABI | NONE | 25 | 21448 | 2507256 | 2.3545 | 0.020141 | 116.8993
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 89 | 6978 | 0.0063965 | 8.1583e-05 | 78.4045
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | INSULATOR | 115 | 14238 | 1765461 | 1.5872 | 0.012801 | 123.9964
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | NONE | 104 | 288 | 23983 | 0.021562 | 0.00025893 | 83.2743
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 21 | 281 | 72269 | 0.064974 | 0.00025263 | 257.1851
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | CROSSARM | 4 | 44 | 2615 | 0.0024221 | 4.0755e-05 | 59.4318
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 6 | 30 | 2584 | 0.0024266 | 2.8172e-05 | 86.1333
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 4 | 91 | 30792 | 0.028008 | 8.2773e-05 | 338.3736
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | POLE | 6 | 2504 | 338865 | 0.30823 | 0.0022776 | 135.3295
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | REGULATOR | 2 | 726 | 42038 | 0.037794 | 0.00065271 | 57.9036
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 3 | 395 | 0.00037094 | 2.8172e-06 | 131.6667
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | NONE | 22 | 1916 | 5225938 | 4.6984 | 0.0017226 | 2727.5251
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 5 | 8 | 1303 | 0.0011715 | 7.1924e-06 | 162.875
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | POLE | 1 | 1 | 77 | 6.9227e-05 | 8.9905e-07 | 77
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 381 | 16875 | 0.015171 | 0.00034254 | 44.2913
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 5 | 695 | 0.00062484 | 4.4953e-06 | 139
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 42 | 2643 | 238898 | 0.21478 | 0.0023762 | 90.389
AEP-TX | 2021 | 1079632 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 1 | 131 | 0.00012134 | 9.2624e-07 | 131
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | POLE | 6 | 424 | 14985 | 0.013472 | 0.0003812 | 35.342
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 1280 | 129099 | 0.11607 | 0.0011508 | 100.8586
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 5 | 1573 | 0.0014142 | 4.4953e-06 | 314.6
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | AF | POLE | 3 | 224 | 6100 | 0.0054842 | 0.00020139 | 27.2321
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | O | NONE | 2 | 38 | 3595 | 0.0033298 | 3.5197e-05 | 94.6053
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | POLE HARDWARE | 3 | 87 | 17205 | 0.016157 | 8.17e-05 | 197.7586
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 10 | 980 | 0.0009203 | 9.3908e-06 | 98
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | SWITCH, UG | 1 | 8 | 2704 | 0.0025046 | 7.4099e-06 | 338
AEP-TX | 2022 | 1090914 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 402 | 0.0003685 | 1.8333e-06 | 201
AEP-TX | 2021 | 1079632 | PARTIAL POWER | VIN | CONN/CLAMP | 3 | 3 | 342 | 0.00031677 | 2.7787e-06 | 114
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 9 | 43 | 3689 | 0.0033166 | 3.8659e-05 | 85.7907
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | AB | BREAKER | 2 | 1230 | 225976 | 0.20316 | 0.0011058 | 183.7203
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 1 | 100 | 9.1666e-05 | 9.1666e-07 | 100
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | TRANSFORMER, OH | 4 | 4 | 181 | 0.00016997 | 3.7563e-06 | 45.25
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 11 | 385 | 0.00034613 | 9.8896e-06 | 35
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 192 | 33392 | 0.030021 | 0.00017262 | 173.9167
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | BREAKER | 1 | 11 | 3542 | 0.0032218 | 1.0006e-05 | 322
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | REGULATOR | 1 | 402 | 26532 | 0.023854 | 0.00036142 | 66
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 1 | 90 | 8.0915e-05 | 8.9905e-07 | 90
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | SPLICE, UG | 1 | 1 | 345 | 0.00031017 | 8.9905e-07 | 345
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | SWITCH, OH | 1 | 11 | 1606 | 0.0014439 | 9.8896e-06 | 146
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 110 | 9.8896e-05 | 8.9905e-07 | 110
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WI | POLE | 1 | 5 | 2515 | 0.0022611 | 4.4953e-06 | 503
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 30 | 2.6972e-05 | 8.9905e-07 | 30
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 2 | 180 | 0.000165 | 1.8333e-06 | 90
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 14 | 6286 | 0.0057177 | 1.2734e-05 | 449
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | CROSSARM | 3 | 2932 | 221178 | 0.20118 | 0.0026669 | 75.4359
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WL | TRANSFORMER, OH | 3 | 13 | 4521 | 0.0042456 | 1.2208e-05 | 347.7692
AEP-TX | 2022 | 1090914 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 91 | 8.3416e-05 | 9.1666e-07 | 91
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WFS | NONE | 2 | 13 | 1831 | 0.0016655 | 1.1825e-05 | 140.8462
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | FUSE | 1 | 1 | 44 | 4.0755e-05 | 9.2624e-07 | 44
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | POLE | 1 | 7 | 1561 | 0.0014659 | 6.5735e-06 | 223
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TOR | METERING | 1 | 1 | 85 | 7.6419e-05 | 8.9905e-07 | 85
AEP-TX | 2022 | 1090914 | PARTIAL POWER | OL | TRANSFORMER, UG | 1 | 19 | 4161 | 0.0038142 | 1.7417e-05 | 219
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 1 | 5 | 1005 | 0.00093087 | 4.6312e-06 | 201
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 1 | 55 | 5.1649e-05 | 9.3908e-07 | 55
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WW | CROSSARM | 1 | 2 | 146 | 0.00013523 | 1.8525e-06 | 73
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ABX | NONE | 1 | 229 | 89310 | 0.081236 | 0.0002083 | 390
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | GUY/ANCHOR | 1 | 47 | 63309 | 0.059452 | 4.4137e-05 | 1347
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | CROSSARM | 1 | 2 | 446 | 0.00040098 | 1.7981e-06 | 223
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | NONE | 1375 | 41337 | 3702260 | 3.3937 | 0.037892 | 89.5629
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 303 | 30864 | 2684097 | 2.4861 | 0.028588 | 86.9653
AEP-TX | 2022 | 1090914 | PARTIAL POWER | FO | NONE | 6 | 22 | 1516 | 0.0013897 | 2.0167e-05 | 68.9091
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TIR | NONE | 71 | 302 | 45201 | 0.041434 | 0.00027683 | 149.6722
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | UB | NONE | 4 | 349 | 25561 | 0.023676 | 0.00032326 | 73.2407
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WL | CUTOUT | 52 | 1600 | 259374 | 0.24024 | 0.001482 | 162.1087
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | CONN/CLAMP | 11 | 33 | 4485 | 0.0041112 | 3.025e-05 | 135.9091
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 14 | 8277 | 564518 | 0.51747 | 0.0075872 | 68.2032
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | POLE | 23 | 4504 | 915375 | 0.84786 | 0.0041718 | 203.236
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 8 | 1676 | 47982 | 0.043644 | 0.0015245 | 28.6289
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 16 | 2444 | 598837 | 0.5447 | 0.002223 | 245.0233
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VIN | NONE | 222 | 2524 | 212810 | 0.19133 | 0.0022692 | 84.3146
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 1 | 279 | 132893 | 0.1248 | 0.000262 | 476.319
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | METERING | 3 | 3 | 206 | 0.00018738 | 2.7288e-06 | 68.6667
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | CUTOUT | 7 | 74 | 9024 | 0.0082082 | 6.731e-05 | 121.9459
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CF | CONN/CLAMP | 63 | 1128 | 153614 | 0.13811 | 0.0010141 | 136.1826
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | POLE HARDWARE | 12 | 923 | 83310 | 0.0749 | 0.00082982 | 90.26
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | PEDESTAL | 18 | 192 | 43144 | 0.038789 | 0.00017262 | 224.7083
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | FO | NONE | 46 | 2458 | 281235 | 0.25284 | 0.0022099 | 114.4162
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | SPLICE, OH | 12 | 417 | 22368 | 0.02011 | 0.0003749 | 53.6403
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 1 | 122 | 0.00010968 | 8.9905e-07 | 122
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 7 | 57 | 30432 | 0.02736 | 5.1246e-05 | 533.8947
AEP-TX | 2020 | 1064875 | PARTIAL POWER | CO | FUSE | 1 | 6 | 510 | 0.00047893 | 5.6345e-06 | 85
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 30 | 2.8172e-05 | 9.3908e-07 | 30
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 10 | 968 | 0.00090903 | 9.3908e-06 | 96.8
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | ABI | METERING | 1 | 1 | 132 | 0.00012396 | 9.3908e-07 | 132
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 2 | 2 | 183 | 0.00016646 | 1.8192e-06 | 91.5
AEP-TX | 2020 | 1064875 | PARTIAL POWER | A | ARRESTER | 1 | 3 | 174 | 0.0001634 | 2.8172e-06 | 58
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 229 | 12025 | 0.011292 | 0.00021505 | 52.5109
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | ARRESTER | 1 | 1 | 53 | 4.765e-05 | 8.9905e-07 | 53
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 31 | 5393 | 0.0048486 | 2.7871e-05 | 173.9677
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | POLE HARDWARE | 2 | 2 | 326 | 0.00029309 | 1.7981e-06 | 163
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 1 | 300 | 0.00026972 | 8.9905e-07 | 300
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 1 | 1069 | 0.00096109 | 8.9905e-07 | 1069
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | ARRESTER | 2 | 2 | 223 | 0.00020941 | 1.8782e-06 | 111.5
AEP-TX | 2023 | 1099391 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 11 | 1903 | 0.001731 | 1.0006e-05 | 173
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | REGULATOR | 1 | 24 | 240 | 0.0002183 | 2.183e-05 | 10
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WU | POLE | 1 | 1 | 13 | 1.2041e-05 | 9.2624e-07 | 13
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WH | CROSSARM | 2 | 102 | 351644 | 0.33022 | 9.5786e-05 | 3447.4902
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 2 | 938 | 64992 | 0.059576 | 0.00085983 | 69.2878
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TOR | METERING | 1 | 1 | 151 | 0.00013986 | 9.2624e-07 | 151
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | CF | ARRESTER | 2 | 816 | 51408 | 0.04676 | 0.00074223 | 63
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | TRANSFORMER, UG | 1 | 3 | 2796 | 0.0025137 | 2.6972e-06 | 932
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | METERING | 11 | 15 | 2595 | 0.002333 | 1.3486e-05 | 173
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | POLE | 125 | 7700 | 893211 | 0.80304 | 0.0069227 | 116.0014
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 48 | 48 | 5922 | 0.0053242 | 4.3154e-05 | 123.375
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 16 | 101 | 29608 | 0.026619 | 9.0804e-05 | 293.1485
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | NONE | 29 | 55 | 6778 | 0.0060938 | 4.9448e-05 | 123.2364
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | CUTOUT | 7 | 49 | 18923 | 0.017013 | 4.4054e-05 | 386.1837
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | ARRESTER | 6 | 8 | 430 | 0.00038659 | 7.1924e-06 | 53.75
AEP-TX | 2025 | 1112283 | PARTIAL POWER | WL | NONE | 8 | 9 | 1406 | 0.0012641 | 8.0915e-06 | 156.2222
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 774 | 167842 | 0.1509 | 0.00069587 | 216.8501
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TR | CUTOUT | 1 | 2 | 58 | 5.3166e-05 | 1.8333e-06 | 29
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CF | ARRESTER | 2 | 2 | 229 | 0.00020588 | 1.7981e-06 | 114.5
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CO | SPLICE, OH | 7 | 14 | 5185 | 0.0046616 | 1.2587e-05 | 370.3571
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WU | JUMPER/RISER | 1 | 1 | 188 | 0.00017413 | 9.2624e-07 | 188
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 13 | 286 | 0.00026491 | 1.2041e-05 | 22
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 5 | 215 | 0.0001933 | 4.4953e-06 | 43
AEP-TX | 2025 | 1112283 | PARTIAL POWER | CF | PEDESTAL | 1 | 1 | 53 | 4.765e-05 | 8.9905e-07 | 53
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | AB | CIRCUIT SWITCHER | 3 | 1505 | 113014 | 0.10161 | 0.0013531 | 75.0924
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 1272 | 0.0011436 | 8.9905e-07 | 1272
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | SPLICE, OH | 2 | 485 | 77689 | 0.069846 | 0.00043604 | 160.1835
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 3 | 543 | 0.00050992 | 2.8172e-06 | 181
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | METERING | 1 | 1 | 205 | 0.00018431 | 8.9905e-07 | 205
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | FUSE | 1 | 1 | 22 | 2.0011e-05 | 9.0959e-07 | 22
AEP-TX | 2024 | 1112283 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 95 | 8.541e-05 | 8.9905e-07 | 95
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 61 | 9821 | 0.0092227 | 5.7284e-05 | 161
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WW | POLE | 1 | 1 | 120 | 0.00011269 | 9.3908e-07 | 120
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 2 | 199 | 96788 | 0.087017 | 0.00017891 | 486.3719
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 319 | 0.00029242 | 9.1666e-07 | 319
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | TRANSFORMER, POWER - LTC | 1 | 4 | 1348 | 0.0012261 | 3.6384e-06 | 337
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WH | POLE HARDWARE | 1 | 14 | 26908 | 0.025269 | 1.3147e-05 | 1922
AEP-TX | 2023 | 1099391 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 6 | 774 | 0.00070403 | 5.4576e-06 | 129
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 2041 | 13834 | 1698807 | 1.5572 | 0.012681 | 122.7994
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | ABI | NONE | 434 | 9160 | 615671 | 0.56436 | 0.0083966 | 67.213
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | TRANSFORMER, OH | 65 | 229 | 62141 | 0.057558 | 0.00021211 | 271.3581
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | ARRESTER | 35 | 292 | 25180 | 0.023323 | 0.00027046 | 86.2329
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 13 | 468 | 24302 | 0.02251 | 0.00043348 | 51.9274
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | METERING | 1924 | 2143 | 189415 | 0.17788 | 0.0020124 | 88.3878
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | REGULATOR | 12 | 5808 | 318341 | 0.29486 | 0.0053796 | 54.8108
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 225 | 686 | 115606 | 0.10856 | 0.00064421 | 168.5219
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | POLE | 60 | 5267 | 610479 | 0.57329 | 0.0049461 | 115.9064
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 111 | 0.00010175 | 9.1666e-07 | 111
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 13 | 1661 | 71825 | 0.065839 | 0.0015226 | 43.242
AEP-TX | 2021 | 1079632 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 145 | 0.00013431 | 9.2624e-07 | 145
AEP-TX | 2022 | 1090914 | PARTIAL POWER | VA | NONE | 3 | 54 | 3492 | 0.003201 | 4.95e-05 | 64.6667
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 7 | 54 | 10150 | 0.0095316 | 5.071e-05 | 187.963
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TOR | NONE | 51 | 51 | 6229 | 0.0056659 | 4.6389e-05 | 122.1373
AEP-TX | 2020 | 1064875 | PARTIAL POWER | VIN | NONE | 10 | 73 | 5299 | 0.0049762 | 6.8553e-05 | 72.589
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | CONN/CLAMP | 59 | 123 | 16783 | 0.015266 | 0.00011188 | 136.4472
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 1 | 67 | 10759 | 0.0099654 | 6.2058e-05 | 160.5821
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 83 | 7.6878e-05 | 9.2624e-07 | 83
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | CROSSARM | 5 | 1162 | 136889 | 0.12451 | 0.0010569 | 117.8046
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 2 | 31 | 4683 | 0.0043376 | 2.8713e-05 | 151.0645
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WL | ARRESTER | 7 | 23 | 3633 | 0.0033046 | 2.0921e-05 | 157.9565
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | AO | NONE | 19 | 5342 | 774785 | 0.72758 | 0.0050166 | 145.0365
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | METERING | 18 | 18 | 1407 | 0.001265 | 1.6183e-05 | 78.1667
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 9 | 2721 | 164092 | 0.14753 | 0.0024463 | 60.3058
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CO | CUTOUT | 15 | 26 | 2040 | 0.0018556 | 2.3649e-05 | 78.4615
AEP-TX | 2023 | 1099391 | PARTIAL POWER | EQF | TRANSFORMER, UG | 17 | 100 | 27253 | 0.024789 | 9.0959e-05 | 272.53
AEP-TX | 2023 | 1099391 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 11 | 132 | 0.00012007 | 1.0006e-05 | 12
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 104 | 104 | 11879 | 0.01068 | 9.3501e-05 | 114.2212
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | AF | TRANSFORMER, POWER - LTC | 2 | 698 | 36250 | 0.032973 | 0.0006349 | 51.9341
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TR | METERING | 1 | 1 | 135 | 0.00012504 | 9.2624e-07 | 135
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | POLE | 24 | 525 | 264742 | 0.23802 | 0.000472 | 504.2705
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TIR | ARRESTER | 18 | 654 | 70973 | 0.063808 | 0.00058798 | 108.5214
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | A | METERING | 9 | 9 | 770 | 0.00072309 | 8.4517e-06 | 85.5556
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | ARRESTER | 12 | 166 | 44168 | 0.039709 | 0.00014924 | 266.0723
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | INSULATOR | 6 | 285 | 50113 | 0.045054 | 0.00025623 | 175.8351
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | A | CUTOUT | 3 | 6 | 415 | 0.00037311 | 5.3943e-06 | 69.1667
AEP-TX | 2025 | 1112283 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 18 | 66 | 10755 | 0.0096693 | 5.9337e-05 | 162.9545
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 10 | 2240 | 0.0020533 | 9.1666e-06 | 224
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | U | NONE | 10 | 8064 | 424789 | 0.38191 | 0.00725 | 52.6772
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 1 | 150 | 0.00013486 | 8.9905e-07 | 150
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 68 | 3332 | 0.0030862 | 6.2984e-05 | 49
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 59 | 10394 | 0.0093447 | 5.3044e-05 | 176.1695
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | POLE HARDWARE | 9 | 919 | 198692 | 0.17863 | 0.00082623 | 216.2046
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 2 | 2 | 179 | 0.00016093 | 1.7981e-06 | 89.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 3 | 25 | 9858 | 0.0092574 | 2.3477e-05 | 394.32
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 5 | 1115 | 55750 | 0.051638 | 0.0010328 | 50
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 2 | 3880 | 855779 | 0.76939 | 0.0034883 | 220.5616
AEP-TX | 2024 | 1112283 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 1 | 737 | 0.0006626 | 8.9905e-07 | 737
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | AF | NONE | 8 | 1431 | 74427 | 0.066914 | 0.0012865 | 52.0105
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | CONN/CLAMP | 5 | 11 | 2103 | 0.0018907 | 9.8896e-06 | 191.1818
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | AF | INSULATOR | 2 | 590 | 27730 | 0.024931 | 0.00053044 | 47
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 17 | 8966 | 0.0080609 | 1.5284e-05 | 527.4118
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | METERING | 2 | 2 | 290 | 0.00026073 | 1.7981e-06 | 145
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 3 | 5 | 1751 | 0.0016051 | 4.5833e-06 | 350.2
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ERF | BREAKER | 2 | 2 | 116 | 0.00010551 | 1.8192e-06 | 58
AEP-TX | 2023 | 1099391 | PARTIAL POWER | CF | OTHER EQUIPMENT | 1 | 1 | 110 | 0.00010006 | 9.0959e-07 | 110
AEP-TX | 2024 | 1112283 | PARTIAL POWER | CO | INSULATOR | 1 | 2 | 298 | 0.00026792 | 1.7981e-06 | 149
AEP-TX | 2020 | 1064875 | PARTIAL POWER | WU | CUTOUT | 4 | 4 | 277 | 0.00026012 | 3.7563e-06 | 69.25
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | BREAKER | 3 | 3666 | 313826 | 0.29471 | 0.0034427 | 85.6045
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 1 | 2 | 102 | 9.4477e-05 | 1.8525e-06 | 51
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 1 | 442 | 0.0004094 | 9.2624e-07 | 442
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | FUSE | 1 | 164 | 55671 | 0.051565 | 0.0001519 | 339.4573
AEP-TX | 2023 | 1099391 | PARTIAL POWER | ERF | METERING | 1 | 1 | 441 | 0.00040113 | 9.0959e-07 | 441
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 1 | 156 | 0.0001419 | 9.0959e-07 | 156
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | CF | INSULATOR | 2 | 5096 | 609154 | 0.55408 | 0.0046353 | 119.5357
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 1 | 255 | 0.00023946 | 9.3908e-07 | 255
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 295 | 0.00027042 | 1.8333e-06 | 147.5
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 88 | 394 | 85435 | 0.08023 | 0.00037 | 216.8401
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | JUMPER/RISER | 35 | 312 | 48676 | 0.045086 | 0.00028899 | 156.0128
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 55 | 9557 | 1434315 | 1.3285 | 0.0088521 | 150.08
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | CONN/CLAMP | 39 | 553 | 45481 | 0.041691 | 0.00050691 | 82.2441
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 3 | 631 | 343841 | 0.31519 | 0.00057841 | 544.9144
AEP-TX | 2023 | 1099391 | PARTIAL POWER | OL | NONE | 45 | 155 | 15818 | 0.014388 | 0.00014099 | 102.0516
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | ERF | NONE | 3 | 7492 | 108476 | 0.099436 | 0.0068676 | 14.4789
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TOR | POLE | 2 | 2 | 214 | 0.00019822 | 1.8525e-06 | 107
AEP-TX | 2022 | 1090914 | PARTIAL POWER | EQF | POLE | 2 | 2 | 864 | 0.000792 | 1.8333e-06 | 432
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 13 | 1436 | 0.0013301 | 1.2041e-05 | 110.4615
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | ARRESTER | 27 | 488 | 41489 | 0.037738 | 0.00044388 | 85.0184
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ABI | NONE | 641 | 7983 | 787043 | 0.70759 | 0.0071771 | 98.5899
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | TRANSFORMER, OH | 81 | 343 | 76176 | 0.068486 | 0.00030837 | 222.0875
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 291 | 2563 | 360628 | 0.32422 | 0.0023043 | 140.7054
AEP-TX | 2020 | 1064875 | PARTIAL POWER | TR | NONE | 1 | 24 | 3282 | 0.0030821 | 2.2538e-05 | 136.75
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 499 | 16240 | 0.015042 | 0.00046219 | 32.5451
AEP-TX | 2024 | 1112283 | PARTIAL POWER | EQF | PEDESTAL | 5 | 22 | 1716 | 0.0015428 | 1.9779e-05 | 78
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | METERING | 6 | 6 | 609 | 0.00054752 | 5.3943e-06 | 101.5
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 3 | 22 | 5044 | 0.004588 | 2.0011e-05 | 229.2727
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | CUTOUT | 107 | 1056 | 110168 | 0.099047 | 0.0009494 | 104.3258
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | ERF | NONE | 12 | 4145 | 55122 | 0.050139 | 0.0037703 | 13.2984
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 5 | 34 | 5637 | 0.005068 | 3.0568e-05 | 165.7941
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 94 | 8.8273e-05 | 9.3908e-07 | 94
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | WU | NONE | 20 | 15665 | 1270573 | 1.1423 | 0.014084 | 81.109
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 33 | 5023 | 0.0046525 | 3.0566e-05 | 152.2121
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | PEDESTAL | 7 | 16 | 2347 | 0.0021101 | 1.4385e-05 | 146.6875
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | ARRESTER | 2 | 26 | 2513 | 0.0022858 | 2.3649e-05 | 96.6538
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 12 | 1634 | 0.0014691 | 1.0789e-05 | 136.1667
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | OL | POLE | 2 | 2 | 647 | 0.00058169 | 1.7981e-06 | 323.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 158 | 0.00014205 | 8.9905e-07 | 158
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | POLE | 23 | 740 | 133368 | 0.1199 | 0.0006653 | 180.227
AEP-TX | 2022 | 1090914 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 1 | 15 | 1.375e-05 | 9.1666e-07 | 15
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 5 | 700 | 0.00062934 | 4.4953e-06 | 140
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 13 | 2224 | 0.0019995 | 1.1688e-05 | 171.0769
AEP-TX | 2025 | 1112283 | PARTIAL POWER | EQF | SPLICE, OH | 2 | 2 | 157 | 0.00014115 | 1.7981e-06 | 78.5
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 1 | 94 | 8.4511e-05 | 8.9905e-07 | 94
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | AF | CIRCUIT SWITCHER | 1 | 1054 | 31620 | 0.029694 | 0.00098979 | 30
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | SWITCH, OH | 1 | 14 | 3987 | 0.0036547 | 1.2833e-05 | 284.7857
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | OL | POLE | 2 | 11 | 1149 | 0.0010532 | 1.0083e-05 | 104.4545
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | CF | ARRESTER | 2 | 1548 | 271647 | 0.2551 | 0.0014537 | 175.4826
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | POLE HARDWARE | 2 | 1123 | 228926 | 0.21204 | 0.0010402 | 203.8522
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | FO | CROSSARM | 2 | 15 | 2961 | 0.0027142 | 1.375e-05 | 197.4
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | ERF | CROSSARM | 1 | 29 | 4263 | 0.0039486 | 2.6861e-05 | 147
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | O | NONE | 3 | 4 | 545 | 0.00048998 | 3.5962e-06 | 136.25
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 1 | 213 | 25773 | 0.023171 | 0.0001915 | 121
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 3 | 126 | 0.00011328 | 2.6972e-06 | 42
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 1 | 238 | 0.00021397 | 8.9905e-07 | 238
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | BREAKER | 1 | 16 | 1904 | 0.0017319 | 1.4554e-05 | 119
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 61 | 13969 | 0.012805 | 5.5916e-05 | 229
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 17 | 1598 | 0.0014801 | 1.5746e-05 | 94
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 1 | 1127 | 61985 | 0.055728 | 0.0010132 | 55
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | TRANSFORMER, GROUNDING | 1 | 7 | 1827 | 0.0016922 | 6.4837e-06 | 261
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WI | CABLE TERMINATOR | 1 | 89 | 15130 | 0.014208 | 8.3578e-05 | 170
AEP-TX | 2022 | 1090914 | PARTIAL POWER | VA | CONN/CLAMP | 1 | 2 | 218 | 0.00019983 | 1.8333e-06 | 109
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 80 | 35474 | 0.032267 | 7.2768e-05 | 443.425
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 1 | 51 | 4.6389e-05 | 9.0959e-07 | 51
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WW | OTHER EQUIPMENT | 1 | 1 | 115 | 0.00010542 | 9.1666e-07 | 115
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 807 | 533427 | 0.50093 | 0.00075784 | 661
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | BREAKER | 1 | 1563 | 35949 | 0.033759 | 0.0014678 | 23
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | CF | SWITCH, OH | 1 | 785 | 7065 | 0.0063518 | 0.00070576 | 9
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 1426 | 71300 | 0.064102 | 0.001282 | 50
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | EQF | INSULATOR | 3 | 4472 | 1010733 | 0.9265 | 0.0040993 | 226.0136
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WL | METERING | 1 | 1 | 26 | 2.3649e-05 | 9.0959e-07 | 26
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 3 | 216 | 0.00020284 | 2.8172e-06 | 72
AEP-TX | 2020 | 1064875 | PARTIAL POWER | VA | METERING | 1 | 1 | 76 | 7.137e-05 | 9.3908e-07 | 76
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 5 | 180 | 0.00016183 | 4.4953e-06 | 36
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 69 | 1173 | 0.0011015 | 6.4796e-05 | 17
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 592 | 44992 | 0.04045 | 0.00053224 | 76
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WW | CUTOUT | 1 | 1 | 146 | 0.0001328 | 9.0959e-07 | 146
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 2 | 434 | 0.00039783 | 1.8333e-06 | 217
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | TIR | NONE | 3340 | 124300 | 13055694 | 12.0927 | 0.11513 | 105.0337
AEP-TX | 2022 | 1090914 | PARTIAL POWER | TOR | CONN/CLAMP | 97 | 97 | 12748 | 0.011686 | 8.8916e-05 | 131.4227
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 24 | 285 | 72283 | 0.066259 | 0.00026125 | 253.6246
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 31 | 8678 | 1579483 | 1.4479 | 0.0079548 | 182.01
AEP-TX | 2022 | 1090914 | PARTIAL POWER | WL | NONE | 77 | 191 | 29628 | 0.027159 | 0.00017508 | 155.1204
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 3 | 523 | 0.00048442 | 2.7787e-06 | 174.3333
AEP-TX | 2021 | 1079632 | DISTRIBUTION STATION | WL | NONE | 22 | 15706 | 1997749 | 1.8504 | 0.014548 | 127.1965
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 30 | 209 | 37862 | 0.035069 | 0.00019358 | 181.1579
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AF | BREAKER | 3 | 1028 | 148682 | 0.13629 | 0.00094233 | 144.6323
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | CF | CROSSARM | 42 | 8978 | 1366929 | 1.253 | 0.0082298 | 152.2532
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CF | NONE | 13 | 31 | 2649 | 0.0024282 | 2.8417e-05 | 85.4516
AEP-TX | 2021 | 1079632 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 85 | 7.8731e-05 | 9.2624e-07 | 85
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | WU | NONE | 3787 | 80491 | 8451737 | 7.9368 | 0.075587 | 105.0023
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | U | NONE | 1693 | 86725 | 5264287 | 4.9436 | 0.081441 | 60.7009
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 47 | 12104 | 1472994 | 1.3833 | 0.011367 | 121.6948
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | METERING | 190 | 204 | 20367 | 0.019126 | 0.00019157 | 99.8382
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | TIR | ARRESTER | 13 | 230 | 23193 | 0.02178 | 0.00021599 | 100.8391
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 268 | 268 | 42971 | 0.039086 | 0.00024377 | 160.3396
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 191 | 35852 | 0.033668 | 0.00017936 | 187.7068
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | ABI | NONE | 475 | 6359 | 463698 | 0.42178 | 0.0057841 | 72.92
AEP-TX | 2021 | 1079632 | PARTIAL POWER | WL | POLE HARDWARE | 1 | 7 | 2562 | 0.002373 | 6.4837e-06 | 366
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | CF | INSULATOR | 11 | 2781 | 80412 | 0.074481 | 0.0025759 | 28.9148
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | EQF | SPLICE, UG | 6 | 42 | 15408 | 0.014124 | 3.85e-05 | 366.8571
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | CF | JUMPER/RISER | 23 | 2002 | 311672 | 0.29268 | 0.00188 | 155.6803
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 166 | 52828 | 8597812 | 7.8205 | 0.048052 | 162.751
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 25 | 159 | 36592 | 0.033284 | 0.00014463 | 230.1384
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | CO | NONE | 502 | 4556 | 530872 | 0.47728 | 0.0040961 | 116.5215
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 7 | 63 | 16338 | 0.014861 | 5.7304e-05 | 259.3333
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 271 | 23528 | 2551211 | 2.2937 | 0.021153 | 108.433
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 989 | 126198 | 14334212 | 12.8872 | 0.11346 | 113.5851
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | EQF | REGULATOR | 11 | 3356 | 207382 | 0.19475 | 0.0031515 | 61.7944
AEP-TX | 2023 | 1099391 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 3 | 149 | 0.00013553 | 2.7288e-06 | 49.6667
AEP-TX | 2020 | 1064875 | PARTIAL POWER | OL | CONN/CLAMP | 14 | 49 | 7375 | 0.0069257 | 4.6015e-05 | 150.5102
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | CABLE TERMINATOR | 6 | 10 | 1469 | 0.0013606 | 9.2624e-06 | 146.9
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | AF | POLE HARDWARE | 1 | 40 | 3360 | 0.0030562 | 3.6384e-05 | 84
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | POLE | 291 | 46921 | 7537853 | 6.7769 | 0.042184 | 160.6499
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 9 | 712 | 141633 | 0.12883 | 0.00064763 | 198.9228
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | OL | CONN/CLAMP | 25 | 88 | 9594 | 0.0087266 | 8.0044e-05 | 109.0227
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 10 | 3890 | 0.003653 | 9.3908e-06 | 389
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 1 | 165 | 0.00015008 | 9.0959e-07 | 165
AEP-TX | 2023 | 1099391 | PARTIAL POWER | VA | CONN/CLAMP | 3 | 6 | 1292 | 0.0011752 | 5.4576e-06 | 215.3333
AEP-TX | 2023 | 1099391 | DISTRIBUTION LINE | WW | CUTOUT | 4 | 22 | 4149 | 0.0037739 | 2.0011e-05 | 188.5909
AEP-TX | 2023 | 1099391 | DISTRIBUTION STATION | EQF | SWITCH, OH | 6 | 6993 | 609382 | 0.55429 | 0.0063608 | 87.1417
AEP-TX | 2022 | 1090914 | PARTIAL POWER | CO | PEDESTAL | 3 | 20 | 3172 | 0.0029077 | 1.8333e-05 | 158.6
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | EQF | SPLICE, OH | 24 | 977 | 125855 | 0.11315 | 0.00087837 | 128.8178
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 4 | 23 | 82748 | 0.074395 | 2.0678e-05 | 3597.7391
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 416 | 45299 | 4696859 | 4.2227 | 0.040726 | 103.6857
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 489 | 2759 | 592247 | 0.53246 | 0.0024805 | 214.66
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 30 | 108 | 22984 | 0.020664 | 9.7098e-05 | 212.8148
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 14 | 2712 | 0.0024382 | 1.2587e-05 | 193.7143
AEP-TX | 2023 | 1099391 | PARTIAL POWER | TIR | ARRESTER | 1 | 1 | 39 | 3.5474e-05 | 9.0959e-07 | 39
AEP-TX | 2025 | 1112283 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 5 | 34 | 6111 | 0.0054941 | 3.0568e-05 | 179.7353
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WU | CONN/CLAMP | 7 | 392 | 11738 | 0.010553 | 0.00035243 | 29.9439
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 2 | 3 | 820 | 0.00073722 | 2.6972e-06 | 273.3333
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | TOR | SPLICE, OH | 8 | 8 | 1226 | 0.0011022 | 7.1924e-06 | 153.25
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 5 | 293 | 13448 | 0.01209 | 0.00026342 | 45.8976
AEP-TX | 2025 | 1112283 | PARTIAL POWER | OL | JUMPER/RISER | 3 | 48 | 6160 | 0.0055382 | 4.3154e-05 | 128.3333
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | AF | BREAKER | 1 | 642 | 79608 | 0.071572 | 0.00057719 | 124
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | AB | NONE | 17 | 13529 | 735613 | 0.66135 | 0.012163 | 54.3731
AEP-TX | 2025 | 1112283 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 178 | 0.00016003 | 8.9905e-07 | 178
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 3 | 234 | 0.00021038 | 2.6972e-06 | 78
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | CF | SPLICE, OH | 1 | 1 | 87 | 7.8218e-05 | 8.9905e-07 | 87
AEP-TX | 2020 | 1064875 | PARTIAL POWER | EQF | TRANSFORMER, GROUNDING | 1 | 3 | 1398 | 0.0013128 | 2.8172e-06 | 466
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | WI | POLE | 1 | 90 | 24189 | 0.022173 | 8.25e-05 | 268.7667
AEP-TX | 2022 | 1090914 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 104 | 21424 | 0.019639 | 9.5333e-05 | 206
AEP-TX | 2025 | 1112283 | DISTRIBUTION STATION | WI | NONE | 3 | 934 | 552280 | 0.49653 | 0.00083971 | 591.3062
AEP-TX | 2020 | 1064875 | DISTRIBUTION LINE | VA | CUTOUT | 2 | 2 | 187 | 0.00017561 | 1.8782e-06 | 93.5
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | VA | SWITCH, UG | 1 | 13 | 2483 | 0.0022323 | 1.1688e-05 | 191
AEP-TX | 2024 | 1112283 | PARTIAL POWER | O | NONE | 2 | 2 | 132 | 0.00011867 | 1.7981e-06 | 66
AEP-TX | 2024 | 1112283 | PARTIAL POWER | WL | RECLOSER, LINE/OCR/BR | 1 | 59 | 2773 | 0.0024931 | 5.3044e-05 | 47
AEP-TX | 2024 | 1112283 | DISTRIBUTION STATION | WL | CIRCUIT SWITCHER | 5 | 760 | 72566 | 0.065241 | 0.00068328 | 95.4816
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | WU | ARRESTER | 5 | 1815 | 439230 | 0.41247 | 0.0017044 | 242
AEP-TX | 2023 | 1099391 | PARTIAL POWER | WL | CONN/CLAMP | 2 | 4 | 2256 | 0.002052 | 3.6384e-06 | 564
AEP-TX | 2025 | 1112283 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 9 | 819 | 0.00073632 | 8.0915e-06 | 91
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 2 | 333 | 17670 | 0.015886 | 0.00029938 | 53.0631
AEP-TX | 2024 | 1112283 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 4 | 1110 | 0.00099795 | 3.5962e-06 | 277.5
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 1533 | 345026 | 0.32401 | 0.0014396 | 225.0659
AEP-TX | 2021 | 1079632 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 767 | 13689 | 0.012679 | 0.00071043 | 17.8475
AEP-TX | 2022 | 1090914 | DISTRIBUTION STATION | AF | TRANSFORMER, POWER - LTC | 1 | 1033 | 50617 | 0.046399 | 0.00094691 | 49
AEP-TX | 2021 | 1079632 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 68 | 6.2984e-05 | 9.2624e-07 | 68
AEP-TX | 2020 | 1064875 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 828 | 169740 | 0.1594 | 0.00077756 | 205
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 65 | 1.1852e-05 | 1.8234e-07 | 65
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CROSSARM | 1 | 305 | 91039 | 0.016482 | 5.5219e-05 | 298.4885
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | GUY/ANCHOR | 1 | 1 | 17 | 3.0778e-06 | 1.8105e-07 | 17
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | FUSE | 1 | 13 | 1508 | 0.00027302 | 2.3536e-06 | 116
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CUTOUT | 3 | 16 | 8992 | 0.001628 | 2.8967e-06 | 562
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | ARRESTER | 1 | 2 | 290 | 5.2503e-05 | 3.6209e-07 | 145
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | NONE | 3 | 6 | 661 | 0.00011903 | 1.0804e-06 | 110.1667
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | TR | NONE | 4 | 88 | 42900 | 0.0076941 | 1.5783e-05 | 487.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE HARDWARE | 1 | 1 | 372 | 6.6987e-05 | 1.8007e-07 | 372
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | ARRESTER | 1 | 4 | 404 | 7.2457e-05 | 7.174e-07 | 101
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 127 | 53120 | 0.0095654 | 2.2869e-05 | 418.2677
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 12 | 37 | 57290 | 0.010202 | 6.589e-06 | 1548.3784
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 10 | 13 | 425 | 7.5684e-05 | 2.315e-06 | 32.6923
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 3 | 96 | 14475 | 0.0025777 | 1.7096e-05 | 150.7812
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 207 | 1740 | 523549 | 0.093234 | 0.00030986 | 300.8902
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 26 | 1212 | 500518 | 0.089132 | 0.00021583 | 412.9686
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | SCO | NONE | 11 | 6609 | 1007374 | 0.17939 | 0.0011769 | 152.4246
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 1 | 94 | 32900 | 0.0058588 | 1.674e-05 | 350
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CUTOUT | 1 | 4 | 112 | 2.0087e-05 | 7.174e-07 | 28
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | ARRESTER | 6 | 274 | 107265 | 0.019102 | 4.8794e-05 | 391.4781
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 1517 | 389403 | 0.069345 | 0.00027015 | 256.6928
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 3 | 201 | 31394 | 0.0056305 | 3.6049e-05 | 156.1891
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | METERING | 2 | 5 | 3498 | 0.00062989 | 9.0036e-07 | 699.6
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | OV | NONE | 1 | 82 | 12382 | 0.0022417 | 1.4846e-05 | 151
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 1 | 180 | 3.2588e-05 | 1.8105e-07 | 180
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | TR | CONDUCTOR OVERHEAD | 1 | 38 | 5738 | 0.0010333 | 6.8427e-06 | 151
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 80 | 1.4406e-05 | 1.8007e-07 | 80
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 2 | 7 | 691 | 0.00012305 | 1.2466e-06 | 98.7143
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 6 | 7 | 978 | 0.00017416 | 1.2466e-06 | 139.7143
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 18 | 2060 | 538398 | 0.095878 | 0.00036684 | 261.3583
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, UG | 3 | 11 | 13470 | 0.0023987 | 1.9589e-06 | 1224.5455
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 56 | 786 | 93785 | 0.016701 | 0.00013997 | 119.3193
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | SPLICE, OH | 4 | 15 | 65120 | 0.011597 | 2.6712e-06 | 4341.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 3 | 33 | 4475 | 0.00079691 | 5.8766e-06 | 135.6061
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | POLE | 6 | 1400 | 365432 | 0.065076 | 0.00024931 | 261.0229
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | NONE | 64 | 1342 | 430430 | 0.076651 | 0.00023898 | 320.7377
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 78 | 24414 | 0.0043963 | 1.4046e-05 | 313
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 1 | 264 | 4.7796e-05 | 1.8105e-07 | 264
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 1214 | 234037 | 0.041677 | 0.00021619 | 192.7817
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 306 | 324798 | 0.05784 | 5.4492e-05 | 1061.4314
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | F | CONDUCTOR OVERHEAD | 2 | 132 | 10296 | 0.0018335 | 2.3507e-05 | 78
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 9 | 30 | 30624 | 0.0054535 | 5.3424e-06 | 1020.8
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 1 | 83 | 1.4781e-05 | 1.7808e-07 | 83
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TIN | NONE | 12 | 10001 | 931980 | 0.16597 | 0.001781 | 93.1887
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 3 | 946 | 0.00016846 | 5.3424e-07 | 315.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 2 | 1142 | 182132 | 0.032434 | 0.00020337 | 159.4851
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | EQF | CONN/CLAMP | 2 | 761 | 310210 | 0.055242 | 0.00013552 | 407.6347
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | NONE | 2 | 4 | 247 | 4.3986e-05 | 7.1232e-07 | 61.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | REGULATOR | 1 | 257 | 98431 | 0.017654 | 4.6093e-05 | 383
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 225 | 4.0068e-05 | 1.7808e-07 | 225
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 2 | 7 | 1549 | 0.00027585 | 1.2466e-06 | 221.2857
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 296 | 5.3301e-05 | 1.8007e-07 | 296
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | F | NONE | 2 | 152 | 27749 | 0.0049415 | 2.7068e-05 | 182.5592
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CUTOUT | 3 | 86 | 21404 | 0.0038116 | 1.5315e-05 | 248.8837
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 2 | 3 | 113 | 2.0123e-05 | 5.3424e-07 | 37.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | WFS | NONE | 1 | 124 | 523404 | 0.093208 | 2.2082e-05 | 4221
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | FUSE | 3 | 5 | 5064 | 0.0009018 | 8.904e-07 | 1012.8
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 906 | 30804 | 0.0054856 | 0.00016134 | 34
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 11 | 3080 | 0.00054849 | 1.9589e-06 | 280
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 239 | 41825 | 0.0075315 | 4.3037e-05 | 175
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | METERING | 1 | 14 | 210 | 3.8292e-05 | 2.5528e-06 | 15
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 8 | 7056 | 0.0012655 | 1.4348e-06 | 882
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | BE | CONDUCTOR OVERHEAD | 2 | 427 | 142565 | 0.025388 | 7.604e-05 | 333.8759
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | OU | NONE | 2 | 999 | 228447 | 0.040682 | 0.0001779 | 228.6757
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 5 | 610 | 0.00010863 | 8.904e-07 | 122
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | V | TRANSFORMER, POWER - NON LTC | 1 | 1552 | 107268 | 0.019316 | 0.00027947 | 69.116
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | R | NONE | 3 | 2396 | 390902 | 0.070771 | 0.00043379 | 163.1477
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 3 | 4 | 3195 | 0.00057844 | 7.2419e-07 | 798.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CUTOUT | 8 | 30 | 6372 | 0.0011536 | 5.4314e-06 | 212.4
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 1000 | 149000 | 0.026976 | 0.00018105 | 149
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | POLE | 2 | 41 | 8736 | 0.0015929 | 7.476e-06 | 213.0732
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | INSULATOR | 2 | 1565 | 70581 | 0.01287 | 0.00028537 | 45.0997
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | PEDESTAL | 6 | 43 | 15410 | 0.0028099 | 7.8407e-06 | 358.3721
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | NONE | 1 | 1050 | 140700 | 0.025473 | 0.0001901 | 134
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 159 | 18138 | 0.0032838 | 2.8786e-05 | 114.0755
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 2 | 11 | 878 | 0.00015896 | 1.9915e-06 | 79.8182
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | NONE | 2885 | 22667 | 2817468 | 0.50735 | 0.0040817 | 124.2982
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | ARRESTER | 4 | 135 | 83589 | 0.015052 | 2.431e-05 | 619.1778
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | ARRESTER | 34 | 548 | 176399 | 0.031765 | 9.8679e-05 | 321.896
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | ARRESTER | 35 | 123 | 6694 | 0.0012054 | 2.2149e-05 | 54.4228
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | FUSE | 141 | 2055 | 597159 | 0.10753 | 0.00037005 | 290.5883
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 62 | 177 | 107312 | 0.019324 | 3.1873e-05 | 606.2825
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE | 11 | 344 | 49353 | 0.0088871 | 6.1945e-05 | 143.468
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 14 | 1453 | 2696981 | 0.48565 | 0.00026164 | 1856.1466
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 5 | 367 | 32313 | 0.0058187 | 6.6086e-05 | 88.0463
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WFS | NONE | 1 | 4 | 496 | 9.0442e-05 | 7.2937e-07 | 124
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | ARRESTER | 1 | 1 | 99 | 1.8052e-05 | 1.8234e-07 | 99
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WL | NONE | 11 | 9841 | 867194 | 0.15813 | 0.0017944 | 88.1205
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | INSULATOR | 2 | 12 | 1692 | 0.00030852 | 2.1881e-06 | 141
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 2 | 173 | 3.1545e-05 | 3.6468e-07 | 86.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 77 | 1309 | 0.00023869 | 1.404e-05 | 17
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 2 | 73 | 9782 | 0.0017837 | 1.3311e-05 | 134
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NONE | 3639 | 173393 | 44430841 | 7.9687 | 0.031098 | 256.2436
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1422 | 32314 | 4931766 | 0.88451 | 0.0057955 | 152.6201
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | FUSE | 577 | 4037 | 623169 | 0.11177 | 0.00072404 | 154.3644
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 3 | 383 | 32290 | 0.0057912 | 6.8691e-05 | 84.3081
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 10 | 220 | 29516 | 0.0052937 | 3.9457e-05 | 134.1636
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 28 | 2819 | 876945 | 0.15728 | 0.00050559 | 311.0837
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | FUSE | 26 | 595 | 203925 | 0.036574 | 0.00010671 | 342.7311
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | FUSE | 950 | 4954 | 545083 | 0.097068 | 0.00088221 | 110.0289
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | FUSE | 8 | 76 | 10268 | 0.0018416 | 1.3631e-05 | 135.1053
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, UG | 7 | 23 | 5511 | 0.0009884 | 4.1251e-06 | 239.6087
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | REGULATOR | 7 | 4599 | 166492 | 0.02986 | 0.00082483 | 36.2018
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | INSULATOR | 8 | 3586 | 458219 | 0.082182 | 0.00064315 | 127.78
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | ARRESTER | 28 | 105 | 3733 | 0.00066951 | 1.8832e-05 | 35.5524
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | FUSE | 3 | 9 | 438 | 7.8555e-05 | 1.6142e-06 | 48.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CUTOUT | 1 | 93 | 92652 | 0.016617 | 1.668e-05 | 996.2581
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 3 | 106 | 11508 | 0.002064 | 1.9011e-05 | 108.566
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 47 | 115 | 4048 | 0.00072087 | 2.0479e-05 | 35.2
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | INSULATOR | 5 | 37 | 2144 | 0.00038453 | 6.636e-06 | 57.9459
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 3 | 3 | 317 | 5.7083e-05 | 5.4022e-07 | 105.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 8 | 124 | 19103 | 0.0034399 | 2.2329e-05 | 154.0565
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | NONE | 68 | 2750 | 1040513 | 0.18737 | 0.0004952 | 378.3684
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | TOR | NONE | 31 | 21007 | 3960171 | 0.71312 | 0.0037828 | 188.5167
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 2 | 40 | 7.2029e-06 | 3.6014e-07 | 20
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | CONDUCTOR UG | 1 | 1 | 265 | 4.7719e-05 | 1.8007e-07 | 265
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 7 | 1117 | 135646 | 0.024426 | 0.00020114 | 121.4378
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONN/CLAMP | 2 | 9 | 2495 | 0.00044928 | 1.6206e-06 | 277.2222
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 23 | 8211 | 0.0014726 | 4.1251e-06 | 357
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | NONE | 7 | 8 | 824 | 0.00014838 | 1.4406e-06 | 103
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 3 | 522 | 9.3998e-05 | 5.4022e-07 | 174
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | POLE | 3 | 7 | 4457 | 0.00080258 | 1.2605e-06 | 636.7143
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | FUSE | 2 | 2 | 198 | 3.5511e-05 | 3.587e-07 | 99
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 9 | 3393 | 0.00061098 | 1.6206e-06 | 377
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 29 | 2348 | 0.00042281 | 5.2221e-06 | 80.9655
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | NONE | 15 | 13631 | 2053746 | 0.36834 | 0.0024447 | 150.6673
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 422 | 28300 | 0.0051603 | 7.6948e-05 | 67.0616
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 4 | 934 | 0.00017031 | 7.2937e-07 | 233.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 1 | 1 | 71 | 1.2946e-05 | 1.8234e-07 | 71
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 1 | 1 | 385 | 7.0202e-05 | 1.8234e-07 | 385
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | POLE HARDWARE | 1 | 1 | 201 | 3.6194e-05 | 1.8007e-07 | 201
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 2 | 4 | 2905 | 0.00052311 | 7.2029e-07 | 726.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 14 | 6230 | 0.0011218 | 2.521e-06 | 445
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | NONE | 20 | 3194 | 43970 | 0.0078302 | 0.00056879 | 13.7664
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SO | NONE | 6 | 21 | 4847 | 0.00086315 | 3.7397e-06 | 230.8095
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 1466 | 0.00026106 | 1.7808e-07 | 1466
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 17 | 796 | 289052 | 0.051474 | 0.00014175 | 363.1307
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 4 | 1443 | 585398 | 0.10425 | 0.00025697 | 405.6812
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 5 | 216 | 45374 | 0.0080802 | 3.8465e-05 | 210.0648
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 5 | 13 | 3484 | 0.00062043 | 2.315e-06 | 268
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 10 | 412 | 65711 | 0.011702 | 7.3369e-05 | 159.4927
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TIR | NONE | 16 | 16288 | 1274728 | 0.227 | 0.0029006 | 78.2618
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 2 | 13836 | 0.002505 | 3.6209e-07 | 6918
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | REGULATOR | 1 | 635 | 138734 | 0.024882 | 0.00011389 | 218.4787
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 4 | 4 | 1379 | 0.00024557 | 7.1232e-07 | 344.75
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | NONE | 2 | 3 | 172 | 3.063e-05 | 5.3424e-07 | 57.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 2 | 12 | 2.137e-06 | 3.5616e-07 | 6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 277 | 70912 | 0.012628 | 4.9328e-05 | 256
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 2 | 7 | 600 | 0.00010685 | 1.2466e-06 | 85.7143
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | FUSE | 1 | 3 | 231 | 4.1136e-05 | 5.3424e-07 | 77
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 29 | 4092 | 0.0007287 | 5.1643e-06 | 141.1034
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 3 | 24 | 4.2739e-06 | 5.3424e-07 | 8
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 120 | 2.137e-05 | 1.7808e-07 | 120
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 1 | 363 | 6.4643e-05 | 1.7808e-07 | 363
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 1953 | 262277 | 0.046706 | 0.00034779 | 134.2944
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | INSULATOR | 1 | 7 | 5866 | 0.0010446 | 1.2466e-06 | 838
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 1 | 5 | 3045 | 0.00054832 | 9.0036e-07 | 609
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | O | NONE | 1 | 28 | 224 | 4.0336e-05 | 5.042e-06 | 8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 27 | 2808 | 0.00050564 | 4.8619e-06 | 104
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | GUY/ANCHOR | 1 | 132 | 88308 | 0.015902 | 2.3769e-05 | 669
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | FUSE | 3 | 10 | 2689 | 0.00047886 | 1.7808e-06 | 268.9
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, UG | 2 | 19 | 743 | 0.00013231 | 3.3835e-06 | 39.1053
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 11 | 1009 | 0.00017968 | 1.9589e-06 | 91.7273
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | METERING | 1 | 3 | 351 | 6.2506e-05 | 5.3424e-07 | 117
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | WW | NONE | 1 | 273 | 92274 | 0.016432 | 4.8616e-05 | 338
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | SPLICE, OH | 1 | 12 | 287 | 5.1109e-05 | 2.137e-06 | 23.9167
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 9 | 531 | 9.456e-05 | 1.6027e-06 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | METERING | 4 | 10 | 880 | 0.00015671 | 1.7808e-06 | 88
AEP Total | 2025 | 5615460 | PARTIAL POWER | CE | NONE | 1 | 3 | 501 | 8.9218e-05 | 5.3424e-07 | 167
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 173 | 3.0808e-05 | 1.7808e-07 | 173
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 1 | 958 | 0.00017468 | 1.8234e-07 | 958
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 1 | 124 | 2.261e-05 | 1.8234e-07 | 124
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | POLE | 1 | 3 | 816 | 0.00014635 | 5.3805e-07 | 272
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | SWITCH, OH | 1 | 29 | 2407 | 0.0004317 | 5.2012e-06 | 83
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | NONE | 1164 | 8210 | 1384016 | 0.25057 | 0.0014864 | 168.5769
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONN/CLAMP | 219 | 576 | 124076 | 0.022464 | 0.00010428 | 215.4097
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | NONE | 2893 | 23966 | 3148626 | 0.57005 | 0.004339 | 131.3789
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | NONE | 114 | 3719 | 576497 | 0.10437 | 0.00067331 | 155.014
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE | 254 | 21740 | 10525738 | 1.9056 | 0.0039359 | 484.1646
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | NONE | 5 | 8 | 5849 | 0.0010589 | 1.4484e-06 | 731.125
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | FUSE | 1 | 2 | 25824 | 0.0046753 | 3.6209e-07 | 12912
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 126 | 3309 | 0.00059908 | 2.2812e-05 | 26.2619
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | OU | NONE | 17 | 10919 | 957543 | 0.17336 | 0.0019768 | 87.6951
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | NONE | 8 | 4942 | 525654 | 0.095168 | 0.00089473 | 106.3646
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | REGULATOR | 1 | 512 | 198656 | 0.035966 | 9.2696e-05 | 388
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CUTOUT | 11 | 95 | 18200 | 0.003295 | 1.7199e-05 | 191.5789
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | POLE | 2 | 60 | 17786 | 0.0032201 | 1.0863e-05 | 296.4333
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | RELAY | 6 | 594 | 68310 | 0.012367 | 0.00010754 | 115
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 6 | 1889 | 159327 | 0.028846 | 0.000342 | 84.3446
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | JUMPER/RISER | 1 | 18 | 108 | 1.9553e-05 | 3.2588e-06 | 6
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | NONE | 10 | 2257 | 182779 | 0.033091 | 0.00040862 | 80.9832
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | NONE | 27 | 15200 | 2401268 | 0.43474 | 0.0027519 | 157.9782
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 3 | 387 | 7.0065e-05 | 5.4314e-07 | 129
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | U | NONE | 4 | 2627 | 310743 | 0.056259 | 0.00047561 | 118.2882
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 2 | 132 | 5713 | 0.0010417 | 2.4069e-05 | 43.2803
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 121 | 86783 | 0.015824 | 2.2063e-05 | 717.2149
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CIRCUIT SWITCHER | 1 | 1 | 35 | 6.382e-06 | 1.8234e-07 | 35
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | FUSE | 5 | 52 | 56579 | 0.010317 | 9.4818e-06 | 1088.0577
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | CONDUCTOR UG | 1 | 3 | 1068 | 0.00019474 | 5.4703e-07 | 356
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 3 | 4 | 5864 | 0.0010693 | 7.2937e-07 | 1466
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | NONE | 4 | 6 | 1345 | 0.00024525 | 1.0941e-06 | 224.1667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SPLICE, OH | 2 | 2 | 1294 | 0.00023595 | 3.6468e-07 | 647
AEP Total | 2020 | 5484199 | PARTIAL POWER | WH | NONE | 1 | 7 | 1148 | 0.00020933 | 1.2764e-06 | 164
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | AO | NONE | 1 | 8 | 2728 | 0.00049743 | 1.4587e-06 | 341
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | NONE | 218 | 16680 | 4972150 | 0.89176 | 0.0029916 | 298.0905
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | NONE | 25 | 713 | 41921 | 0.0075185 | 0.00012788 | 58.7952
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CROSSARM | 166 | 40916 | 7263996 | 1.3028 | 0.0073383 | 177.5344
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR UG | 62 | 136 | 57327 | 0.010282 | 2.4392e-05 | 421.5221
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | NONE | 28 | 2384 | 721857 | 0.12947 | 0.00042757 | 302.7924
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 23 | 323 | 105234 | 0.01874 | 5.752e-05 | 325.8019
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 761 | 8703 | 3056138 | 0.54424 | 0.0015498 | 351.1591
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 24 | 3105 | 300067 | 0.053817 | 0.00055688 | 96.6399
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | REGULATOR | 8 | 2999 | 101305 | 0.018169 | 0.00053787 | 33.7796
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 30 | 2874 | 606230 | 0.10873 | 0.00051545 | 210.936
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE | 14 | 640 | 414209 | 0.074288 | 0.00011478 | 647.2016
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | ARRESTER | 9 | 237 | 59559 | 0.010682 | 4.2506e-05 | 251.3038
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 1271 | 10529 | 1442150 | 0.25682 | 0.001875 | 136.9693
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 6 | 33 | 15528 | 0.002785 | 5.9186e-06 | 470.5455
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 53 | 653 | 58851 | 0.01048 | 0.00011629 | 90.124
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 1 | 512 | 9.1827e-05 | 1.7935e-07 | 512
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | SPLICE, OH | 6 | 24 | 1962 | 0.00035776 | 4.3762e-06 | 81.75
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | FUSE | 1 | 2 | 132 | 2.4069e-05 | 3.6468e-07 | 66
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 194 | 3.5374e-05 | 1.8234e-07 | 194
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | INSULATOR | 1 | 96 | 19968 | 0.0036151 | 1.738e-05 | 208
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | NONE | 12 | 1945 | 163787 | 0.029493 | 0.00035024 | 84.2093
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | SCO | NONE | 7 | 2528 | 223594 | 0.040263 | 0.00045522 | 88.447
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE | 16 | 721 | 290289 | 0.052273 | 0.00012983 | 402.62
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 7 | 52 | 32037 | 0.005769 | 9.3637e-06 | 616.0962
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, UG | 9 | 16 | 7592 | 0.0013671 | 2.8812e-06 | 474.5
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | V | OTHER EQUIPMENT | 1 | 547 | 67828 | 0.012214 | 9.8499e-05 | 124
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 6 | 3882 | 0.00069904 | 1.0804e-06 | 647
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WU | NONE | 1 | 1584 | 543312 | 0.097835 | 0.00028523 | 343
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CABLE TERMINATOR | 1 | 3 | 477 | 8.5894e-05 | 5.4022e-07 | 159
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | POLE | 3 | 1126 | 146982 | 0.026361 | 0.00020195 | 130.5346
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | TIR | NONE | 2 | 26 | 247 | 4.43e-05 | 4.6631e-06 | 9.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 9 | 119 | 113829 | 0.020497 | 2.1429e-05 | 956.5462
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | O | NONE | 5 | 1544 | 126481 | 0.022684 | 0.00027692 | 81.9177
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE | 42 | 2187 | 1583493 | 0.28199 | 0.00038946 | 724.048
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 55 | 5120 | 901554 | 0.16055 | 0.00091177 | 176.0848
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | POLE | 12 | 3356 | 737778 | 0.13138 | 0.00059764 | 219.8385
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | RELAY | 3 | 2327 | 1011663 | 0.18016 | 0.00041439 | 434.7499
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 45 | 339 | 51370 | 0.009148 | 6.0369e-05 | 151.5339
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 1168 | 237507 | 0.042597 | 0.00020948 | 203.345
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 2 | 2 | 54 | 9.6849e-06 | 3.587e-07 | 27
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 10 | 196 | 92255 | 0.016429 | 3.4904e-05 | 470.6888
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 12 | 1224 | 619165 | 0.11026 | 0.00021797 | 505.8538
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 55 | 9.7944e-06 | 1.7808e-07 | 55
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 9 | 144 | 30730 | 0.0054724 | 2.5643e-05 | 213.4028
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 66 | 4950 | 0.00089136 | 1.1885e-05 | 75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 296 | 2628 | 579201 | 0.10314 | 0.00046799 | 220.3961
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CUTOUT | 113 | 1286 | 72006 | 0.012823 | 0.00022901 | 55.9922
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | METERING | 2 | 2 | 356 | 6.3396e-05 | 3.5616e-07 | 178
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 19 | 5073 | 0.00091845 | 3.4399e-06 | 267
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | REGULATOR | 1 | 65 | 26390 | 0.0047521 | 1.1705e-05 | 406
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | INSULATOR | 4 | 88 | 13553 | 0.0024405 | 1.5846e-05 | 154.0114
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABX | NONE | 3 | 180 | 50221 | 0.0090434 | 3.2413e-05 | 279.0056
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | REGULATOR | 1 | 552 | 79065 | 0.014417 | 0.00010065 | 143.2337
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 9 | 117 | 2.1182e-05 | 1.6294e-06 | 13
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 6 | 33 | 13050 | 0.0023239 | 5.8766e-06 | 395.4545
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | REGULATOR | 1 | 144 | 40320 | 0.0071802 | 2.5643e-05 | 280
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 1 | 87 | 1.5493e-05 | 1.7808e-07 | 87
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CABLE TERMINATOR | 1 | 14 | 462 | 8.3643e-05 | 2.5346e-06 | 33
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | SPLICE, OH | 2 | 2 | 2752 | 0.00049008 | 3.5616e-07 | 1376
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 6 | 300 | 5.3424e-05 | 1.0685e-06 | 50
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | PEDESTAL | 1 | 1 | 553 | 9.9181e-05 | 1.7935e-07 | 553
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 158 | 24332 | 0.004333 | 2.8137e-05 | 154
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | POLE HARDWARE | 1 | 65 | 7194 | 0.0012811 | 1.1575e-05 | 110.6769
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CROSSARM | 2 | 356 | 84932 | 0.015125 | 6.3396e-05 | 238.573
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 132 | 172128 | 0.030653 | 2.3507e-05 | 1304
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | WU | NONE | 3 | 1822 | 366262 | 0.065224 | 0.00032446 | 201.022
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 108 | 1.9233e-05 | 3.5616e-07 | 54
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 9 | 2421 | 0.00043595 | 1.6206e-06 | 269
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 2 | 760 | 0.00013534 | 3.5616e-07 | 380
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 1790 | 184131 | 0.03279 | 0.00031876 | 102.8665
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | VA | CONDUCTOR OVERHEAD | 1 | 623 | 56070 | 0.010056 | 0.00011174 | 90
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 21 | 1104 | 0.00020131 | 3.8292e-06 | 52.5714
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 13 | 3003 | 0.00054368 | 2.3536e-06 | 231
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 7 | 497 | 9.0624e-05 | 1.2764e-06 | 71
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | FUSE | 1 | 1 | 80 | 1.4348e-05 | 1.7935e-07 | 80
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | TOR | NONE | 5 | 113 | 36846 | 0.0067186 | 2.0605e-05 | 326.0708
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 11 | 5291 | 0.00094222 | 1.9589e-06 | 481
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 167 | 60693 | 0.010988 | 3.0235e-05 | 363.4311
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CUTOUT | 1 | 3 | 381 | 6.8979e-05 | 5.4314e-07 | 127
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | NONE | 379 | 49408 | 10405576 | 1.8839 | 0.0089451 | 210.6051
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR UG | 128 | 291 | 125989 | 0.02281 | 5.2684e-05 | 432.9519
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | REGULATOR | 7 | 7372 | 312020 | 0.05649 | 0.0013347 | 42.325
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONN/CLAMP | 19 | 72 | 14498 | 0.0026248 | 1.3035e-05 | 201.3611
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 2 | 2 | 229 | 4.146e-05 | 3.6209e-07 | 114.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | FUSE | 246 | 3076 | 1185825 | 0.21469 | 0.0005569 | 385.5088
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 68 | 5754 | 922341 | 0.16699 | 0.0010417 | 160.2956
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | ARRESTER | 5 | 13 | 2145 | 0.00038834 | 2.3536e-06 | 165
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | FUSE | 24 | 252 | 236492 | 0.042816 | 4.5624e-05 | 938.4603
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 33 | 919 | 97755 | 0.017698 | 0.00016638 | 106.3711
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | CONN/CLAMP | 2 | 3 | 320 | 5.7935e-05 | 5.4314e-07 | 106.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | METERING | 5 | 5 | 698 | 0.00012637 | 9.0523e-07 | 139.6
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | TOR | NONE | 27 | 11848 | 4510328 | 0.81658 | 0.002145 | 380.6826
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | SCO | NONE | 4 | 2078 | 1287736 | 0.23314 | 0.00037621 | 619.6997
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 32 | 13502 | 0.0024445 | 5.7935e-06 | 421.9375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | POLE | 3 | 84 | 17503 | 0.0031689 | 1.5208e-05 | 208.369
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 4 | 28 | 5308 | 0.00096099 | 5.0693e-06 | 189.5714
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | NONE | 4 | 5 | 1716 | 0.00031068 | 9.0523e-07 | 343.2
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | O | NONE | 1 | 83 | 2573 | 0.00046583 | 1.5027e-05 | 31
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | NONE | 2781 | 40411 | 7238420 | 1.3034 | 0.0072769 | 179.12
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE | 374 | 98238 | 22515430 | 4.0544 | 0.01769 | 229.1927
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, OH | 8 | 9 | 1543 | 0.00027785 | 1.6206e-06 | 171.4444
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | NONE | 9 | 33 | 14500 | 0.002611 | 5.9424e-06 | 439.3939
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 242 | 4840 | 0.00087155 | 4.3577e-05 | 20
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | NONE | 20 | 81 | 40906 | 0.007366 | 1.4586e-05 | 505.0123
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 81 | 1.4665e-05 | 1.8105e-07 | 81
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 5 | 850 | 0.00015389 | 9.0523e-07 | 170
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | NONE | 8617 | 548680 | 168627766 | 30.7479 | 0.10005 | 307.3335
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE | 145 | 35539 | 7441657 | 1.3569 | 0.0064803 | 209.3941
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | NONE | 126 | 283 | 67606 | 0.012327 | 5.1603e-05 | 238.8905
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | ARRESTER | 313 | 23546 | 3371720 | 0.61481 | 0.0042934 | 143.1971
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 9 | 32 | 8613 | 0.0015705 | 5.8349e-06 | 269.1562
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | NONE | 89 | 2661 | 646815 | 0.11794 | 0.00048521 | 243.0722
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 4 | 351 | 6.4002e-05 | 7.2937e-07 | 87.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 4 | 442 | 24365 | 0.0044428 | 8.0595e-05 | 55.1244
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | METERING | 44 | 75 | 17825 | 0.0032502 | 1.3676e-05 | 237.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 459 | 114770 | 0.020927 | 8.3695e-05 | 250.0436
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 30 | 2360 | 743444 | 0.13556 | 0.00043033 | 315.0186
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 31 | 10558 | 1705500 | 0.31098 | 0.0019252 | 161.5363
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | METERING | 2 | 65 | 10140 | 0.0018259 | 1.1705e-05 | 156
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 7 | 763 | 0.00013739 | 1.2605e-06 | 109
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 6 | 72 | 98464 | 0.017731 | 1.2965e-05 | 1367.5556
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | ARRESTER | 2 | 3710 | 394290 | 0.071001 | 0.00066807 | 106.2776
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | NONE | 5 | 15 | 3876 | 0.00069516 | 2.6903e-06 | 258.4
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | FUSE | 1 | 3 | 915 | 0.00016477 | 5.4022e-07 | 305
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONN/CLAMP | 3 | 6 | 6092 | 0.0010926 | 1.0761e-06 | 1015.3333
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 472 | 60888 | 0.01092 | 8.4653e-05 | 129
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | ARRESTER | 10 | 7480 | 1570803 | 0.28172 | 0.0013415 | 210.0004
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 25 | 11775 | 0.0021203 | 4.5018e-06 | 471
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | FUSE | 3 | 5 | 626 | 0.00011273 | 9.0036e-07 | 125.2
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 53 | 17650 | 0.0031655 | 9.5056e-06 | 333.0189
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CROSSARM | 1 | 23 | 1380 | 0.0002475 | 4.1251e-06 | 60
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 22 | 1893 | 982934 | 0.17504 | 0.00033711 | 519.2467
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | NONE | 3 | 6 | 411 | 7.3713e-05 | 1.0761e-06 | 68.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 14 | 210 | 3.7397e-05 | 2.4931e-06 | 15
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 30 | 8055 | 0.0014688 | 5.4703e-06 | 268.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | FUSE | 1 | 2 | 136 | 2.449e-05 | 3.6014e-07 | 68
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CUTOUT | 30 | 570 | 144499 | 0.025732 | 0.00010151 | 253.507
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | NONE | 23 | 34 | 3055 | 0.00054403 | 6.0547e-06 | 89.8529
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 1 | 627 | 0.00011166 | 1.7808e-07 | 627
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | ARRESTER | 1 | 1 | 7 | 1.2466e-06 | 1.7808e-07 | 7
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | WW | POLE | 1 | 90 | 29700 | 0.005289 | 1.6027e-05 | 330
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | RECLOSER, LINE/OCR/BR | 1 | 2 | 98 | 1.7452e-05 | 3.5616e-07 | 49
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 2 | 7 | 805 | 0.00014335 | 1.2466e-06 | 115
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | ARRESTER | 1 | 4 | 508 | 9.0465e-05 | 7.1232e-07 | 127
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | SPLICE, OH | 1 | 1 | 354 | 6.304e-05 | 1.7808e-07 | 354
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 8 | 280 | 5.1056e-05 | 1.4587e-06 | 35
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | NONE | 1 | 1 | 229 | 4.1071e-05 | 1.7935e-07 | 229
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WL | TRANSFORMER, STATION SERVICE | 1 | 996 | 93624 | 0.017072 | 0.00018161 | 94
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | FUSE | 1 | 821 | 113298 | 0.020659 | 0.0001497 | 138
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 24 | 171 | 35229 | 0.0062736 | 3.0452e-05 | 206.0175
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 24 | 339 | 14125 | 0.0025154 | 6.0369e-05 | 41.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | O | NONE | 1 | 69 | 621 | 0.00011059 | 1.2288e-05 | 9
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 3560 | 78320 | 0.014047 | 0.00063849 | 22
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | EQF | POLE | 1 | 5 | 1805 | 0.00032143 | 8.904e-07 | 361
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | INSULATOR | 6 | 203 | 6705 | 0.001194 | 3.615e-05 | 33.0296
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 10 | 39 | 8912 | 0.001587 | 6.9451e-06 | 228.5128
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | INSULATOR | 2 | 1619 | 233136 | 0.042208 | 0.00029311 | 144
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 1 | 322 | 5.8297e-05 | 1.8105e-07 | 322
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | NONE | 552 | 18888 | 2367631 | 0.42163 | 0.0033636 | 125.3511
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | FUSE | 174 | 1817 | 251892 | 0.044857 | 0.00032357 | 138.6307
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | NONE | 316 | 7771 | 940917 | 0.16756 | 0.0013839 | 121.0806
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 8 | 157 | 12359 | 0.0022009 | 2.7959e-05 | 78.7197
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 39 | 2593 | 1243784 | 0.22149 | 0.00046176 | 479.6699
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | VIN | NONE | 1 | 594 | 4752 | 0.00086033 | 0.00010754 | 8
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 4 | 1818 | 66022 | 0.011953 | 0.00032914 | 36.3157
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 43 | 43008 | 0.0077445 | 7.7431e-06 | 1000.186
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 10 | 27 | 3067 | 0.00054617 | 4.8082e-06 | 113.5926
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 3 | 74 | 3443 | 0.00061313 | 1.3178e-05 | 46.527
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 13 | 55 | 20573 | 0.0036636 | 9.7944e-06 | 374.0545
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 12 | 1929 | 186361 | 0.033187 | 0.00034352 | 96.6102
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | VA | NONE | 1 | 1 | 268 | 4.8259e-05 | 1.8007e-07 | 268
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 24 | 979 | 365046 | 0.065007 | 0.00017434 | 372.8764
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 9 | 12 | 1688 | 0.0003006 | 2.137e-06 | 140.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 6 | 189 | 152911 | 0.02723 | 3.3657e-05 | 809.0529
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 11 | 27 | 6332 | 0.0011276 | 4.8082e-06 | 234.5185
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 3 | 22 | 410 | 7.3013e-05 | 3.9178e-06 | 18.6364
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 7 | 204 | 48093 | 0.0085644 | 3.6328e-05 | 235.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 14 | 225 | 43526 | 0.0077511 | 4.0068e-05 | 193.4489
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | BREAKER | 2 | 574 | 108754 | 0.019367 | 0.00010222 | 189.4669
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 1 | 397 | 7.0698e-05 | 1.7808e-07 | 397
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | FUSE | 3 | 12 | 1862 | 0.00033158 | 2.137e-06 | 155.1667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | POLE | 2 | 240 | 133335 | 0.023744 | 4.2739e-05 | 555.5625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 3 | 811 | 96509 | 0.017598 | 0.00014788 | 119
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 8 | 98 | 95246 | 0.017367 | 1.787e-05 | 971.898
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | FUSE | 8 | 42 | 2806 | 0.00050326 | 7.5327e-06 | 66.8095
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 95 | 2363 | 778822 | 0.13968 | 0.0004238 | 329.5904
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 28 | 3442 | 456213 | 0.081822 | 0.00061732 | 132.543
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | FUSE | 8 | 10 | 988 | 0.00017594 | 1.7808e-06 | 98.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1012 | 10141 | 2728054 | 0.48581 | 0.0018059 | 269.0123
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 142 | 273 | 40387 | 0.0071921 | 4.8616e-05 | 147.9377
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | INSULATOR | 2 | 156 | 39012 | 0.0069968 | 2.7979e-05 | 250.0769
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 340 | 1064 | 106482 | 0.018962 | 0.00018948 | 100.0771
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONN/CLAMP | 26 | 121 | 10365 | 0.001859 | 2.1701e-05 | 85.6612
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONN/CLAMP | 4 | 9 | 2314 | 0.00041502 | 1.6142e-06 | 257.1111
AEP Total | 2023 | 5575683 | PARTIAL POWER | UG | CONDUCTOR UG | 6 | 15 | 4828 | 0.0008659 | 2.6903e-06 | 321.8667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | INSULATOR | 18 | 1461 | 239810 | 0.04301 | 0.00026203 | 164.141
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CABLE TERMINATOR | 5 | 18 | 3924 | 0.00070377 | 3.2283e-06 | 218
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | NONE | 2 | 11 | 2735 | 0.00049052 | 1.9729e-06 | 248.6364
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | METERING | 4 | 5 | 986 | 0.00017684 | 8.9675e-07 | 197.2
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 171 | 9353 | 2360110 | 0.42029 | 0.0016656 | 252.3372
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | NONE | 54 | 2700 | 1272313 | 0.22657 | 0.00048082 | 471.227
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | CUTOUT | 1 | 2 | 140 | 2.4931e-05 | 3.5616e-07 | 70
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | R | NONE | 3 | 2096 | 393585 | 0.070874 | 0.00037743 | 187.7791
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 62 | 20185 | 5998292 | 1.0682 | 0.0035945 | 297.1658
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 2 | 136 | 2.4219e-05 | 3.5616e-07 | 68
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | V | REGULATOR | 3 | 688 | 136696 | 0.024343 | 0.00012252 | 198.686
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CROSSARM | 1 | 4 | 540 | 9.6163e-05 | 7.1232e-07 | 135
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 1 | 364 | 6.4821e-05 | 1.7808e-07 | 364
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | SPLICE, OH | 2 | 8 | 7466 | 0.0013295 | 1.4246e-06 | 933.25
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | METERING | 9 | 11 | 951 | 0.00016935 | 1.9589e-06 | 86.4545
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 2 | 68 | 20678 | 0.0036823 | 1.2109e-05 | 304.0882
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 8 | 451 | 93524 | 0.016655 | 8.0314e-05 | 207.3703
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | VA | GUY/ANCHOR | 1 | 822 | 247422 | 0.044795 | 0.00014882 | 301
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | NONE | 4 | 952 | 119333 | 0.021251 | 0.00016953 | 125.3498
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 2 | 284 | 5.0575e-05 | 3.5616e-07 | 142
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 3 | 73 | 24441 | 0.0043524 | 1.3e-05 | 334.8082
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 6 | 4918 | 1152264 | 0.20519 | 0.0008758 | 234.2952
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | WL | RELAY | 2 | 606 | 199044 | 0.035446 | 0.00010792 | 328.4554
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WU | NONE | 3 | 5558 | 107420 | 0.019129 | 0.00098977 | 19.3271
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | ARRESTER | 7 | 12307 | 2651931 | 0.47754 | 0.0022161 | 215.4815
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | CONDUCTOR UG | 2 | 0 | 0 | 0 | 0
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 4 | 296 | 5.3088e-05 | 7.174e-07 | 74
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | JUMPER/RISER | 2 | 26 | 3114 | 0.00056074 | 4.6819e-06 | 119.7692
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 3 | 258 | 4.6272e-05 | 5.3805e-07 | 86
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 36 | 30348 | 0.0054429 | 6.4566e-06 | 843
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 572 | 318104 | 0.056648 | 0.00010186 | 556.1259
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 1 | 315 | 5.6095e-05 | 1.7808e-07 | 315
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | NONE | 3 | 2241 | 403741 | 0.071898 | 0.00039908 | 180.1611
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | INSULATOR | 1 | 1 | 1281 | 0.00022812 | 1.7808e-07 | 1281
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | METERING | 1 | 1 | 124 | 2.2082e-05 | 1.7808e-07 | 124
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | POLE | 1 | 1 | 58 | 1.0329e-05 | 1.7808e-07 | 58
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 142 | 46588 | 0.0082964 | 2.5287e-05 | 328.0845
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 6 | 1698 | 0.00030238 | 1.0685e-06 | 283
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CAPACITOR | 3 | 745 | 200367 | 0.035936 | 0.00013362 | 268.949
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 94 | 13254 | 0.0023603 | 1.674e-05 | 141
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 3 | 531 | 9.456e-05 | 5.3424e-07 | 177
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | FW | CIRCUIT SWITCHER | 4 | 3049 | 24392 | 0.0043437 | 0.00054297 | 8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 7 | 1256 | 200631 | 0.035983 | 0.00022526 | 159.7381
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | CONDUCTOR OVERHEAD | 2 | 377 | 57967 | 0.010396 | 6.7615e-05 | 153.7586
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 101 | 13650 | 0.0024481 | 1.8114e-05 | 135.1485
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | NONE | 7 | 514 | 101825 | 0.018262 | 9.2186e-05 | 198.1031
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 1 | 67 | 1.2016e-05 | 1.7935e-07 | 67
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | METERING | 34 | 48 | 7944 | 0.0014147 | 8.5478e-06 | 165.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 137 | 21149 | 0.0038083 | 2.467e-05 | 154.3723
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | NONE | 1 | 5 | 370 | 6.636e-05 | 8.9675e-07 | 74
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONN/CLAMP | 4 | 11 | 796 | 0.00014334 | 1.9808e-06 | 72.3636
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | NONE | 2013 | 65103 | 15226246 | 2.7764 | 0.011871 | 233.8793
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONN/CLAMP | 29 | 263 | 38141 | 0.0069547 | 4.7956e-05 | 145.0228
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | NONE | 58 | 810 | 96908 | 0.01767 | 0.0001477 | 119.6395
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 56 | 2023 | 566397 | 0.10328 | 0.00036888 | 279.9787
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | NONE | 25 | 61 | 5424 | 0.00098902 | 1.1123e-05 | 88.918
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CROSSARM | 74 | 25360 | 7712989 | 1.4064 | 0.0046242 | 304.1399
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, UG | 8 | 276 | 116158 | 0.02118 | 5.0326e-05 | 420.8623
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 704 | 155864 | 0.028421 | 0.00012837 | 221.3977
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | ARRESTER | 8 | 2124 | 323629 | 0.059011 | 0.00038729 | 152.3677
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | NONE | 21 | 15877 | 1983566 | 0.36169 | 0.002895 | 124.9333
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CIRCUIT SWITCHER | 1 | 6 | 660 | 0.00012035 | 1.0941e-06 | 110
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 49 | 2159 | 251392 | 0.044768 | 0.00038447 | 116.4391
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 154 | 2.762e-05 | 1.7935e-07 | 154
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | FW | NONE | 2 | 2171 | 931892 | 0.16714 | 0.00038937 | 429.2455
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | FUSE | 1 | 1 | 353 | 6.3909e-05 | 1.8105e-07 | 353
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CROSSARM | 1 | 840 | 180240 | 0.032865 | 0.00015317 | 214.5714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 156 | 2.8091e-05 | 1.8007e-07 | 156
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | CROSSARM | 3 | 2242 | 475116 | 0.085555 | 0.00040372 | 211.9161
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 2 | 81 | 115582 | 0.020813 | 1.4586e-05 | 1426.9383
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | WL | NONE | 2 | 242 | 45880 | 0.0082286 | 4.3403e-05 | 189.5868
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | METERING | 1 | 1 | 157 | 2.8158e-05 | 1.7935e-07 | 157
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 3 | 607 | 0.00010887 | 5.3805e-07 | 202.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 384 | 27214 | 5730240 | 1.0204 | 0.0048463 | 210.5622
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 301 | 1210 | 223949 | 0.039881 | 0.00021548 | 185.0818
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 253 | 2324 | 737220 | 0.13128 | 0.00041386 | 317.2203
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | POLE | 21 | 1582 | 346510 | 0.061706 | 0.00028172 | 219.0329
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | A | NONE | 11 | 5618 | 679540 | 0.12101 | 0.0010005 | 120.9576
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | NONE | 18 | 1472 | 203699 | 0.036275 | 0.00026213 | 138.3825
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CROSSARM | 2 | 1529 | 218146 | 0.038847 | 0.00027228 | 142.6723
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 38 | 2774 | 0.00049752 | 6.8153e-06 | 73
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | NONE | 6 | 27 | 4403 | 0.00078409 | 4.8082e-06 | 163.0741
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 81 | 23490 | 0.0041831 | 1.4424e-05 | 290
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 12 | 2406 | 607419 | 0.10817 | 0.00042846 | 252.4601
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | JUMPER/RISER | 1 | 53 | 30327 | 0.0054392 | 9.5056e-06 | 572.2075
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 7 | 3616 | 1019307 | 0.18355 | 0.00065114 | 281.888
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 1 | 34 | 4454 | 0.00081215 | 6.1996e-06 | 131
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 1 | 1037 | 0.00018909 | 1.8234e-07 | 1037
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 1 | 3477 | 1109079 | 0.20223 | 0.000634 | 318.9758
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 3 | 1628 | 0.00029316 | 5.4022e-07 | 542.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 131 | 31422 | 0.0056582 | 2.3589e-05 | 239.8626
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 227 | 4.1392e-05 | 1.8234e-07 | 227
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | BREAKER | 5 | 5457 | 571598 | 0.10293 | 0.00098265 | 104.7458
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WL | CONDUCTOR OVERHEAD | 3 | 1522 | 293383 | 0.05283 | 0.00027407 | 192.7615
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 40 | 11320 | 0.0020384 | 7.2029e-06 | 283
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | POLE | 4 | 1407 | 139811 | 0.025176 | 0.00025336 | 99.3682
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | SPLICE, OH | 2 | 6 | 3452 | 0.00061912 | 1.0761e-06 | 575.3333
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | NONE | 9 | 11 | 1548 | 0.00028227 | 2.0058e-06 | 140.7273
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 144 | 17568 | 0.0032034 | 2.6257e-05 | 122
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | U | NONE | 2 | 497 | 57652 | 0.010512 | 9.0624e-05 | 116
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABI | NONE | 3 | 1486 | 531656 | 0.096943 | 0.00027096 | 357.7766
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | NONE | 3 | 198 | 90077 | 0.016308 | 3.5847e-05 | 454.9343
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | METERING | 3 | 5 | 947 | 0.00017145 | 9.0523e-07 | 189.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1 | 238 | 4.3089e-05 | 1.8105e-07 | 238
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 47 | 1672 | 294565 | 0.053043 | 0.00030108 | 176.1752
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | INSULATOR | 245 | 47841 | 7838038 | 1.4114 | 0.0086148 | 163.8352
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | FUSE | 184 | 1583 | 616788 | 0.11107 | 0.00028505 | 389.6323
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | NONE | 68 | 4700 | 982708 | 0.17696 | 0.00084634 | 209.0868
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | PEDESTAL | 2 | 498 | 67872 | 0.012222 | 8.9676e-05 | 136.2892
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 88 | 635 | 68872 | 0.012402 | 0.00011435 | 108.4598
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 116 | 4251 | 2731942 | 0.49195 | 0.00076549 | 642.6587
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CROSSARM | 161 | 43501 | 18605661 | 3.3504 | 0.0078333 | 427.7065
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | POLE | 1 | 1 | 150 | 2.7011e-05 | 1.8007e-07 | 150
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 201 | 2861 | 748308 | 0.13421 | 0.00051312 | 261.5547
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | POLE | 5 | 81 | 20109 | 0.0036066 | 1.4527e-05 | 248.2593
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CUTOUT | 22 | 1631 | 382154 | 0.069683 | 0.0002974 | 234.3066
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | JUMPER/RISER | 10 | 165 | 34718 | 0.0063306 | 3.0086e-05 | 210.4121
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | NONE | 15 | 92 | 19840 | 0.0036177 | 1.6775e-05 | 215.6522
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | METERING | 1 | 3 | 33 | 6.0173e-06 | 5.4703e-07 | 11
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 9 | 3253 | 512509 | 0.093452 | 0.00059316 | 157.5496
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | ARRESTER | 34 | 2520 | 851442 | 0.15525 | 0.0004595 | 337.8738
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 45 | 282 | 129485 | 0.023611 | 5.142e-05 | 459.1667
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | STATIC WIRE | 1 | 2 | 66 | 1.2035e-05 | 3.6468e-07 | 33
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 754 | 180960 | 0.032997 | 0.00013749 | 240
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 268 | 4.8868e-05 | 1.8234e-07 | 268
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 139 | 48677 | 0.0088759 | 2.5346e-05 | 350.1942
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CUTOUT | 2701 | 84440 | 14170323 | 2.5415 | 0.015144 | 167.8153
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 33 | 3370 | 688111 | 0.12391 | 0.00060684 | 204.1872
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 60 | 4219 | 559047 | 0.10067 | 0.00075972 | 132.507
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE | 18 | 1154 | 482711 | 0.086923 | 0.0002078 | 418.2938
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | U | NONE | 50 | 24573 | 4160395 | 0.74917 | 0.0044249 | 169.3076
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CUTOUT | 21 | 896 | 71542 | 0.012883 | 0.00016134 | 79.846
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | NONE | 1072 | 32112 | 7411748 | 1.3293 | 0.0057593 | 230.8093
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CUTOUT | 18 | 267 | 84346 | 0.015188 | 4.8079e-05 | 315.9026
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | FUSE | 9 | 32 | 2612 | 0.00047035 | 5.7623e-06 | 81.625
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 3 | 26 | 4064 | 0.00073181 | 4.6819e-06 | 156.3077
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | METERING | 15 | 31 | 3033 | 0.00054616 | 5.5822e-06 | 97.8387
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | POLE | 2 | 45 | 2270 | 0.00040876 | 8.1032e-06 | 50.4444
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CUTOUT | 3 | 4 | 1299 | 0.00023391 | 7.2029e-07 | 324.75
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | TRANSFORMER, STATION SERVICE | 4 | 2242 | 313401 | 0.056209 | 0.0004021 | 139.7864
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CUTOUT | 15 | 307 | 73933 | 0.01326 | 5.5061e-05 | 240.8241
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 44 | 866 | 196851 | 0.035305 | 0.00015532 | 227.3106
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | NONE | 31 | 2824 | 251217 | 0.045056 | 0.00050649 | 88.9579
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 27 | 86 | 16354 | 0.0029331 | 1.5424e-05 | 190.1628
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | TRANSFORMER, OH | 4 | 4404 | 692395 | 0.12418 | 0.00078986 | 157.2196
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | FUSE | 27 | 1289 | 322294 | 0.058036 | 0.00023211 | 250.0341
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | NONE | 2 | 2 | 587 | 0.0001057 | 3.6014e-07 | 293.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | POLE | 2 | 18 | 4594 | 0.00082725 | 3.2413e-06 | 255.2222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 5 | 222 | 54566 | 0.0097171 | 3.9534e-05 | 245.7928
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | METERING | 2 | 19 | 1205 | 0.00021612 | 3.4077e-06 | 63.4211
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 2 | 26 | 4.6631e-06 | 3.587e-07 | 13
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | NONE | 1920 | 65504 | 14656799 | 2.6101 | 0.011665 | 223.7543
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | TRANSFORMER, OH | 1 | 3 | 423 | 7.617e-05 | 5.4022e-07 | 141
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 89 | 98968 | 0.01775 | 1.5962e-05 | 1112
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 1110 | 64380 | 0.011593 | 0.00019988 | 58
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 230 | 4.1939e-05 | 3.6468e-07 | 115
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | TOR | NONE | 1 | 1 | 131 | 2.3589e-05 | 1.8007e-07 | 131
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 4 | 896 | 0.00016134 | 7.2029e-07 | 224
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | NONE | 56 | 1787 | 555957 | 0.10065 | 0.00032353 | 311.1119
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | NONE | 58 | 109 | 35964 | 0.0065112 | 1.9734e-05 | 329.945
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 51 | 2358 | 520817 | 0.094292 | 0.00042691 | 220.8723
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CROSSARM | 150 | 60401 | 10809308 | 1.957 | 0.010935 | 178.9591
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, OH | 74 | 3033 | 552293 | 0.099991 | 0.00054911 | 182.0946
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 37 | 679 | 486841 | 0.088141 | 0.00012293 | 716.9971
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | FUSE | 97 | 1894 | 606649 | 0.10983 | 0.0003429 | 320.3004
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SPLICE, OH | 18 | 24 | 3992 | 0.00072274 | 4.3451e-06 | 166.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | NONE | 9 | 29 | 6417 | 0.0011618 | 5.2503e-06 | 221.2759
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | ARRESTER | 29 | 24994 | 4069329 | 0.73674 | 0.0045251 | 162.8122
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 1 | 1 | 48 | 8.6902e-06 | 1.8105e-07 | 48
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 1 | 57 | 125805 | 0.022777 | 1.032e-05 | 2207.1053
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 232 | 4.2003e-05 | 1.8105e-07 | 232
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 8 | 168 | 27851 | 0.0050423 | 3.0416e-05 | 165.7798
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | PEDESTAL | 5 | 24 | 3926 | 0.00071079 | 4.3451e-06 | 163.5833
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WU | NONE | 4 | 3575 | 63214 | 0.011445 | 0.00064724 | 17.6822
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | POLE | 1 | 72 | 28728 | 0.0052011 | 1.3035e-05 | 399
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | METERING | 9 | 9 | 1196 | 0.00021653 | 1.6294e-06 | 132.8889
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 11 | 26 | 901 | 0.00016312 | 4.7072e-06 | 34.6538
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | U | NONE | 9 | 3794 | 564335 | 0.10217 | 0.00068689 | 148.7441
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | INSULATOR | 183 | 43344 | 7666078 | 1.3978 | 0.0079034 | 176.866
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 1209 | 558558 | 0.10185 | 0.00022045 | 462
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | SCO | CROSSARM | 1 | 4 | 1208 | 0.00021753 | 7.2029e-07 | 302
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | POLE | 7 | 794 | 418180 | 0.074469 | 0.0001414 | 526.6751
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 18 | 665 | 253807 | 0.045198 | 0.00011842 | 381.6647
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 11 | 1673 | 147727 | 0.026307 | 0.00029793 | 88.3007
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 3 | 6 | 950 | 0.00016918 | 1.0685e-06 | 158.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 3 | 861 | 0.00015333 | 5.3424e-07 | 287
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 8 | 237 | 93502 | 0.016651 | 4.2205e-05 | 394.5232
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | WI | CONDUCTOR OVERHEAD | 1 | 28 | 14560 | 0.0025928 | 4.9862e-06 | 520
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 26 | 325 | 136058 | 0.024229 | 5.7876e-05 | 418.64
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | JUMPER/RISER | 1 | 2 | 5662 | 0.0010083 | 3.5616e-07 | 2831
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 2 | 406 | 7.2816e-05 | 3.587e-07 | 203
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | WL | NONE | 3 | 3571 | 776632 | 0.1383 | 0.00063592 | 217.4831
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | FUSE | 3 | 6 | 1200 | 0.0002137 | 1.0685e-06 | 200
AEP Total | 2024 | 5615460 | PARTIAL POWER | UG | CONDUCTOR UG | 3 | 4 | 732 | 0.00013035 | 7.1232e-07 | 183
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR UG | 1 | 30 | 5120 | 0.00091177 | 5.3424e-06 | 170.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 2 | 2978 | 0.00053032 | 3.5616e-07 | 1489
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | SWITCH, OH | 1 | 2057 | 460768 | 0.082053 | 0.00036631 | 224
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | U | CONDUCTOR OVERHEAD | 1 | 53 | 19907 | 0.003545 | 9.4382e-06 | 375.6038
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 82 | 12546 | 0.0022342 | 1.4603e-05 | 153
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 1 | 234 | 4.1671e-05 | 1.7808e-07 | 234
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 50 | 9.0036e-06 | 1.8007e-07 | 50
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 2 | 1492 | 0.00026867 | 3.6014e-07 | 746
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 2 | 566 | 0.00010192 | 3.6014e-07 | 283
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 38 | 3790 | 0.00067492 | 6.767e-06 | 99.7368
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | CONN/CLAMP | 1 | 4 | 88 | 1.5671e-05 | 7.1232e-07 | 22
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | NONE | 3 | 12 | 1273 | 0.0002267 | 2.137e-06 | 106.0833
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 1 | 86 | 1.5315e-05 | 1.7808e-07 | 86
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 196 | 83692 | 0.014904 | 3.4904e-05 | 427
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | INSULATOR | 1 | 1720 | 531671 | 0.09468 | 0.0003063 | 309.111
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | WFS | NONE | 2 | 368 | 88890 | 0.01583 | 6.5533e-05 | 241.5489
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | V | NONE | 2 | 696 | 34158 | 0.0060828 | 0.00012394 | 49.0776
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 4 | 4 | 353 | 6.2862e-05 | 7.1232e-07 | 88.25
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | OTHER EQUIPMENT | 1 | 1 | 97 | 1.7274e-05 | 1.7808e-07 | 97
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 41 | 7.3013e-06 | 1.7808e-07 | 41
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | INSULATOR | 1 | 534 | 399894 | 0.071213 | 9.5095e-05 | 748.8652
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | PEDESTAL | 1 | 3 | 630 | 0.00011219 | 5.3424e-07 | 210
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 464 | 6032 | 0.0010742 | 8.2629e-05 | 13
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | EQF | ARRESTER | 1 | 68 | 9792 | 0.0017438 | 1.2109e-05 | 144
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CUTOUT | 2 | 82 | 23691 | 0.0042892 | 1.4846e-05 | 288.9146
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CUTOUT | 16 | 198 | 38825 | 0.0070291 | 3.5847e-05 | 196.0859
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 1227 | 217875 | 0.039445 | 0.00022214 | 177.5672
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 7 | 16219 | 0.0029364 | 1.2673e-06 | 2317
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CUTOUT | 6 | 364 | 37454 | 0.0067809 | 6.5901e-05 | 102.8956
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | F | NONE | 1 | 1 | 73 | 1.3216e-05 | 1.8105e-07 | 73
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 2 | 11 | 416 | 7.5315e-05 | 1.9915e-06 | 37.8182
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WL | NONE | 3 | 2308 | 269172 | 0.048733 | 0.00041786 | 116.6256
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | V | NONE | 4 | 1625 | 634733 | 0.11492 | 0.0002942 | 390.6049
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | SCO | NONE | 3 | 3782 | 54957 | 0.0099498 | 0.00068472 | 14.5312
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | JUMPER/RISER | 2 | 8 | 2044 | 0.00037006 | 1.4484e-06 | 255.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | NONE | 348 | 18842 | 11416705 | 2.0558 | 0.0033929 | 605.9179
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 5678 | 273209 | 114451850 | 20.6096 | 0.049197 | 418.9168
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | NONE | 693 | 6775 | 1112716 | 0.20037 | 0.00122 | 164.2385
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 3 | 75 | 1.3578e-05 | 5.4314e-07 | 25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 23 | 21735 | 0.003935 | 4.1641e-06 | 945
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | FUSE | 162 | 2528 | 980467 | 0.17878 | 0.00046096 | 387.843
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | NONE | 2029 | 69858 | 18311426 | 3.3389 | 0.012738 | 262.1235
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CUTOUT | 2712 | 122834 | 20078324 | 3.6611 | 0.022398 | 163.459
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | NONE | 37 | 154 | 42723 | 0.0077902 | 2.8081e-05 | 277.4221
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | NONE | 50 | 5098 | 1020616 | 0.1861 | 0.00092958 | 200.1993
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | SWITCH, OH | 9 | 6299 | 496371 | 0.090509 | 0.0011486 | 78.8016
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 36 | 2008 | 1230094 | 0.2243 | 0.00036614 | 612.5966
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE | 14 | 1751 | 1851379 | 0.33758 | 0.00031928 | 1057.3267
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | NONE | 11 | 673 | 73965 | 0.013487 | 0.00012272 | 109.9034
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 5 | 7 | 509 | 9.0643e-05 | 1.2466e-06 | 72.7143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 554 | 3846 | 348677 | 0.062092 | 0.00068489 | 90.6596
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 1398 | 315948 | 0.056665 | 0.00025073 | 226
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 40 | 5520 | 0.00099001 | 7.174e-06 | 138
AEP Total | 2023 | 5575683 | PARTIAL POWER | OU | NONE | 1 | 1 | 114 | 2.0446e-05 | 1.7935e-07 | 114
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | FUSE | 2 | 10 | 231 | 4.143e-05 | 1.7935e-06 | 23.1
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 179 | 64061 | 19994496 | 3.5606 | 0.011408 | 312.1165
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | NONE | 11 | 67 | 11685 | 0.0021307 | 1.2217e-05 | 174.403
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 5 | 215 | 3.9204e-05 | 9.1171e-07 | 43
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CUTOUT | 7 | 51 | 25310 | 0.0045394 | 9.1469e-06 | 496.2745
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 963 | 65604 | 0.011683 | 0.00017149 | 68.1246
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | METERING | 10 | 38 | 10483 | 0.0018668 | 6.767e-06 | 275.8684
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WU | NONE | 1 | 982 | 154174 | 0.027651 | 0.00017612 | 157
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 18 | 2418 | 0.00043367 | 3.2283e-06 | 134.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 56 | 1090 | 443351 | 0.078952 | 0.00019411 | 406.744
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | NONE | 15 | 4200 | 956607 | 0.17035 | 0.00074794 | 227.7636
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | ARRESTER | 3 | 3528 | 3216899 | 0.57286 | 0.00062827 | 911.8194
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | CONN/CLAMP | 3 | 10 | 1678 | 0.00030095 | 1.7935e-06 | 167.8
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 1 | 177 | 1947 | 0.00034919 | 3.1745e-05 | 11
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 4 | 83 | 24941 | 0.0044912 | 1.4946e-05 | 300.494
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | FUSE | 21 | 220 | 297402 | 0.053554 | 3.9616e-05 | 1351.8273
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 2 | 1554 | 0.00027983 | 3.6014e-07 | 777
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | CONDUCTOR UG | 1 | 2 | 356 | 6.4106e-05 | 3.6014e-07 | 178
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 7 | 399 | 7.1849e-05 | 1.2605e-06 | 57
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 8 | 6317 | 949536 | 0.16909 | 0.0011249 | 150.3144
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CUTOUT | 2 | 6 | 2022 | 0.00036008 | 1.0685e-06 | 337
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | TIR | NONE | 2 | 190 | 31644 | 0.0056352 | 3.3835e-05 | 166.5474
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 1401 | 0.00024949 | 1.7808e-07 | 1401
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | FUSE | 2 | 8 | 488 | 8.6903e-05 | 1.4246e-06 | 61
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | ARRESTER | 1 | 681 | 110322 | 0.019786 | 0.00012214 | 162
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 289 | 5.1832e-05 | 1.7935e-07 | 289
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 2 | 2872 | 0.00051145 | 3.5616e-07 | 1436
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 32 | 3232 | 0.00057555 | 5.6986e-06 | 101
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 55 | 37070 | 0.0066753 | 9.904e-06 | 674
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | V | TRANSFORMER, GROUNDING | 2 | 1205 | 180750 | 0.032548 | 0.00021699 | 150
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 29 | 16948 | 0.0030519 | 5.2221e-06 | 584.4138
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 3 | 239 | 4.2561e-05 | 5.3424e-07 | 79.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 267 | 4.7547e-05 | 1.7808e-07 | 267
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | WU | NONE | 1 | 1 | 94 | 1.6859e-05 | 1.7935e-07 | 94
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 26 | 22958 | 0.0041341 | 4.6819e-06 | 883
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 3196 | 60724 | 0.011073 | 0.00058277 | 19
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | WW | STATIC WIRE | 1 | 1865 | 85790 | 0.015386 | 0.00033449 | 46
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | FUSE | 1 | 84 | 7026 | 0.0012811 | 1.5317e-05 | 83.6429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 4 | 312 | 5.6891e-05 | 7.2937e-07 | 78
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 1436 | 0.00025572 | 1.7808e-07 | 1436
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | FUSE | 1 | 513 | 39240 | 0.0069879 | 9.1355e-05 | 76.4912
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 6 | 14472 | 0.0025772 | 1.0685e-06 | 2412
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | REGULATOR | 1 | 405 | 36045 | 0.0064647 | 7.2637e-05 | 89
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 74 | 5402 | 0.00098501 | 1.3493e-05 | 73
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | NONE | 73 | 876 | 1754108 | 0.31757 | 0.0001586 | 2002.4064
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | METERING | 64 | 300 | 22423 | 0.0040596 | 5.4314e-05 | 74.7433
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | FUSE | 93 | 1153 | 302642 | 0.054792 | 0.00020875 | 262.4822
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 43 | 277 | 89736 | 0.016246 | 5.015e-05 | 323.9567
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 62 | 140 | 85024 | 0.015393 | 2.5346e-05 | 607.3143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CUTOUT | 5 | 19 | 9576 | 0.0017337 | 3.4399e-06 | 504
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 22 | 31514 | 0.0057055 | 3.983e-06 | 1432.4545
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 7 | 13 | 13822 | 0.0024614 | 2.315e-06 | 1063.2308
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | SWITCH, OH | 1 | 42 | 17346 | 0.003089 | 7.4794e-06 | 413
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 51 | 1140 | 685253 | 0.12203 | 0.00020301 | 601.0991
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 2 | 6 | 12436 | 0.0022146 | 1.0685e-06 | 2072.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | NONE | 14 | 525 | 78207 | 0.013927 | 9.3492e-05 | 148.9657
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 20 | 27 | 7723 | 0.0013753 | 4.8082e-06 | 286.037
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 18 | 198 | 3.526e-05 | 3.2054e-06 | 11
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | EQF | TRANSFORMER, GROUNDING | 1 | 196 | 49000 | 0.0088713 | 3.5485e-05 | 250
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 2 | 1338 | 0.00024094 | 3.6014e-07 | 669
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | POLE | 14 | 4693 | 1004969 | 0.18024 | 0.00084169 | 214.1421
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 12 | 3771 | 0.00067633 | 2.1522e-06 | 314.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | NONE | 6 | 332 | 22549 | 0.0040442 | 5.9544e-05 | 67.9187
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 7 | 33 | 3799 | 0.00067653 | 5.8766e-06 | 115.1212
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CROSSARM | 1 | 70 | 6720 | 0.0012166 | 1.2673e-05 | 96
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 46 | 13054 | 0.0023803 | 8.3877e-06 | 283.7826
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 2038 | 0.00037161 | 1.8234e-07 | 2038
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | POLE | 2 | 60 | 6585 | 0.0012007 | 1.0941e-05 | 109.75
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | NONE | 3 | 374 | 160756 | 0.029104 | 6.7711e-05 | 429.8289
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 6 | 3441 | 194578 | 0.035228 | 0.00062298 | 56.5469
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | OTHER EQUIPMENT | 1 | 1 | 350 | 6.382e-05 | 1.8234e-07 | 350
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONN/CLAMP | 7 | 16 | 8160 | 0.0014694 | 2.8812e-06 | 510
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 13 | 2169 | 802818 | 0.14456 | 0.00039058 | 370.1328
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | CE | OTHER EQUIPMENT | 1 | 441 | 98435 | 0.017725 | 7.9412e-05 | 223.2086
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONN/CLAMP | 4 | 13 | 899 | 0.00016124 | 2.3316e-06 | 69.1538
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | CUTOUT | 1 | 1 | 1000 | 0.00018007 | 1.8007e-07 | 1000
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 4 | 5 | 2247 | 0.00040015 | 8.904e-07 | 449.4
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 81 | 84417 | 0.01514 | 1.4527e-05 | 1042.1852
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | AO | NONE | 3 | 968 | 144631 | 0.025756 | 0.00017238 | 149.4122
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 80 | 8931 | 1289124 | 0.22957 | 0.0015904 | 144.3426
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | NONE | 26 | 2991 | 517939 | 0.092234 | 0.00053264 | 173.1658
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | NONE | 14 | 153 | 108739 | 0.019364 | 2.7246e-05 | 710.7124
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 11 | 1398 | 184814 | 0.032912 | 0.00024896 | 132.1989
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE | 39 | 2180 | 900989 | 0.16045 | 0.00038821 | 413.2977
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 23 | 3245 | 0.00057787 | 4.0958e-06 | 141.087
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 4 | 19 | 2243 | 0.00039943 | 3.3835e-06 | 118.0526
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | NONE | 1 | 1 | 66 | 1.1837e-05 | 1.7935e-07 | 66
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 2 | 936 | 0.00016787 | 3.587e-07 | 468
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 1 | 54 | 2700 | 0.00049232 | 9.8465e-06 | 50
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 4 | 6212 | 0.0011327 | 7.2937e-07 | 1553
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CUTOUT | 2 | 59 | 8035 | 0.0014651 | 1.0758e-05 | 136.1864
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | METERING | 1 | 1 | 60 | 1.0804e-05 | 1.8007e-07 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 1 | 1878 | 0.00033818 | 1.8007e-07 | 1878
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | INSULATOR | 2 | 17 | 2827 | 0.00050906 | 3.0612e-06 | 166.2941
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | V | TRANSFORMER, GROUNDING | 1 | 620 | 304243 | 0.054786 | 0.00011164 | 490.7145
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 1 | 110 | 1.9729e-05 | 1.7935e-07 | 110
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 532 | 23593 | 3385222 | 0.60284 | 0.0042014 | 143.4842
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 37 | 3561 | 644516 | 0.11478 | 0.00063414 | 180.993
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | NONE | 253 | 4513 | 3555945 | 0.63324 | 0.00080367 | 787.9337
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | NONE | 8 | 18 | 1546 | 0.00027531 | 3.2054e-06 | 85.8889
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 24 | 666 | 341095 | 0.060742 | 0.0001186 | 512.1547
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | NONE | 25 | 1613 | 2284313 | 0.40679 | 0.00028724 | 1416.1891
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 25 | 6461 | 664055 | 0.11825 | 0.0011506 | 102.779
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 6 | 11 | 2038 | 0.00036293 | 1.9589e-06 | 185.2727
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CUTOUT | 2 | 69 | 4661 | 0.00083003 | 1.2288e-05 | 67.5507
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 9 | 501 | 8.9218e-05 | 1.6027e-06 | 55.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 37 | 6.589e-06 | 1.7808e-07 | 37
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 38 | 405 | 83420 | 0.014855 | 7.2122e-05 | 205.9753
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 73 | 19598 | 3340086 | 0.5948 | 0.00349 | 170.4299
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 6 | 212 | 3.7753e-05 | 1.0685e-06 | 35.3333
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 1 | 1 | 274 | 4.934e-05 | 1.8007e-07 | 274
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 1 | 3 | 576 | 0.00010372 | 5.4022e-07 | 192
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | BREAKER | 2 | 1470 | 238740 | 0.04299 | 0.00026471 | 162.4082
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | SPLICE, OH | 7 | 18 | 6960 | 0.0012394 | 3.2054e-06 | 386.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 7 | 507 | 105337 | 0.018758 | 9.0286e-05 | 207.7653
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | WI | NONE | 5 | 5392 | 349799 | 0.062292 | 0.00096021 | 64.8737
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 15 | 65 | 8970 | 0.0015974 | 1.1575e-05 | 138
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | PEDESTAL | 5 | 19 | 1362 | 0.00024254 | 3.3835e-06 | 71.6842
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 733 | 84705 | 34209583 | 6.092 | 0.015084 | 403.8673
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 84 | 2091 | 450557 | 0.080235 | 0.00037236 | 215.4744
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | NONE | 2410 | 14343 | 1602639 | 0.2854 | 0.0025542 | 111.7367
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | NONE | 62 | 5941 | 553833 | 0.098626 | 0.001058 | 93.2222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 181 | 56415 | 9109637 | 1.6222 | 0.010046 | 161.4754
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 12 | 155 | 100669 | 0.018055 | 2.7799e-05 | 649.4774
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | NONE | 114 | 12923 | 1543428 | 0.27681 | 0.0023177 | 119.4326
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 2 | 17 | 3518 | 0.00063095 | 3.049e-06 | 206.9412
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | METERING | 8 | 8 | 858 | 0.00015388 | 1.4348e-06 | 107.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 3 | 31 | 7135 | 0.0012797 | 5.5599e-06 | 230.1613
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 145 | 156802 | 0.028388 | 2.6252e-05 | 1081.3931
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CUTOUT | 228 | 2128 | 209713 | 0.037763 | 0.00038319 | 98.5493
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | METERING | 70 | 336 | 58897 | 0.010606 | 6.0504e-05 | 175.2887
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 777 | 9325 | 2727112 | 0.49108 | 0.0016792 | 292.4517
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 34 | 940 | 136229 | 0.024531 | 0.00016927 | 144.9245
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CUTOUT | 7 | 47 | 7445 | 0.0013406 | 8.4634e-06 | 158.4043
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 13 | 1419 | 585337 | 0.1054 | 0.00025552 | 412.4996
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | PEDESTAL | 7 | 16 | 2045 | 0.00036825 | 2.8812e-06 | 127.8125
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | NONE | 41 | 1619 | 205455 | 0.036997 | 0.00029154 | 126.9024
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | NONE | 77 | 879 | 123541 | 0.022246 | 0.00015828 | 140.5472
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 9 | 93 | 22386 | 0.0040311 | 1.6747e-05 | 240.7097
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 6 | 2940 | 705305 | 0.12861 | 0.00053609 | 239.8997
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | INSULATOR | 8 | 2162 | 336518 | 0.061361 | 0.00039422 | 155.6512
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 17 | 18802 | 0.0034284 | 3.0998e-06 | 1106
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | NONE | 23 | 90 | 28325 | 0.0051648 | 1.6411e-05 | 314.7222
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 3 | 9 | 1002 | 0.00018271 | 1.6411e-06 | 111.3333
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | NONE | 36 | 154 | 40622 | 0.0074071 | 2.8081e-05 | 263.7792
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | GUY/ANCHOR | 1 | 14 | 756 | 0.00013785 | 2.5528e-06 | 54
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | FUSE | 7 | 151 | 25783 | 0.0047013 | 2.7534e-05 | 170.7483
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | FUSE | 47 | 446 | 114011 | 0.020789 | 8.1325e-05 | 255.63
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CABLE TERMINATOR | 1 | 3 | 90 | 1.6411e-05 | 5.4703e-07 | 30
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | CROSSARM | 3 | 282 | 104950 | 0.019137 | 5.142e-05 | 372.1631
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | ARRESTER | 1 | 15 | 2100 | 0.00038292 | 2.7351e-06 | 140
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 39 | 6006 | 0.0010951 | 7.1113e-06 | 154
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 2 | 104 | 66389 | 0.012106 | 1.8964e-05 | 638.3558
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | CE | METERING | 1 | 1272 | 145008 | 0.026441 | 0.00023194 | 114
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR UG | 3 | 5 | 2285 | 0.00041665 | 9.1171e-07 | 457
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 98 | 1021 | 103773 | 0.018612 | 0.00018312 | 101.6386
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | NONE | 32 | 735 | 176725 | 0.031696 | 0.00013182 | 240.4422
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | RECLOSER, LINE/OCR/BR | 1 | 13 | 2145 | 0.00038625 | 2.3409e-06 | 165
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WL | ARRESTER | 1 | 1006 | 1259512 | 0.2268 | 0.00018115 | 1252
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | BREAKER | 5 | 5440 | 1338613 | 0.24105 | 0.00097959 | 246.0686
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | AB | NONE | 6 | 2627 | 494605 | 0.088708 | 0.00047115 | 188.2775
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 246 | 4.412e-05 | 1.7935e-07 | 246
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | POLE | 2 | 462 | 25135 | 0.0045261 | 8.3193e-05 | 54.4048
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 7 | 41 | 31366 | 0.0056481 | 7.3829e-06 | 765.0244
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | FUSE | 15 | 166 | 19122 | 0.0034295 | 2.9772e-05 | 115.1928
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | WU | NONE | 3 | 638 | 443544 | 0.07987 | 0.00011489 | 695.21
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 168 | 9744 | 0.0017476 | 3.0131e-05 | 58
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | POLE | 5 | 217 | 32247 | 0.0057835 | 3.8919e-05 | 148.6037
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CUTOUT | 4 | 7 | 3760 | 0.00067436 | 1.2555e-06 | 537.1429
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 11 | 111 | 14099 | 0.0025287 | 1.9908e-05 | 127.018
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CAPACITOR | 1 | 584 | 51392 | 0.0092543 | 0.00010516 | 88
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | WU | NONE | 6 | 4506 | 58578 | 0.010506 | 0.00080815 | 13
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 8 | 1640 | 0.00029532 | 1.4406e-06 | 205
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 674 | 0.00012137 | 3.6014e-07 | 337
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | METERING | 3 | 3 | 297 | 5.3267e-05 | 5.3805e-07 | 99
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | METERING | 3 | 9 | 351 | 6.3205e-05 | 1.6206e-06 | 39
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | SWITCH, OH | 8 | 2493 | 567211 | 0.10173 | 0.00044712 | 227.5215
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 2 | 1568 | 0.00028122 | 3.587e-07 | 784
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 21 | 53 | 2203 | 0.00039511 | 9.5056e-06 | 41.566
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 5 | 149 | 34392 | 0.006193 | 2.6831e-05 | 230.8188
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | POLE | 26 | 3419 | 2593921 | 0.46709 | 0.00061567 | 758.6783
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 9 | 113 | 18105 | 0.0032471 | 2.0267e-05 | 160.2212
AEP Total | 2022 | 5553337 | PARTIAL POWER | SCO | NONE | 1 | 1 | 75 | 1.3505e-05 | 1.8007e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 5 | 4588 | 747487 | 0.1346 | 0.00082617 | 162.9222
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | JUMPER/RISER | 1 | 105 | 13755 | 0.0024769 | 1.8908e-05 | 131
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | SWITCH, OH | 3 | 2978 | 177190 | 0.031907 | 0.00053625 | 59.4997
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | PEDESTAL | 3 | 11 | 896 | 0.0001607 | 1.9729e-06 | 81.4545
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | EQF | MOAB | 2 | 1476 | 96638 | 0.017496 | 0.00026722 | 65.4729
AEP Total | 2021 | 5523447 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 101 | 1.8286e-05 | 1.8105e-07 | 101
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | MOAB | 3 | 1189 | 10956 | 0.0019835 | 0.00021526 | 9.2145
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | NONE | 3 | 48 | 14252 | 0.0025803 | 8.6902e-06 | 296.9167
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | SCO | NONE | 1 | 5 | 7740 | 0.0014013 | 9.0523e-07 | 1548
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | REGULATOR | 15 | 14948 | 2144325 | 0.38822 | 0.0027063 | 143.4523
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1470 | 52387 | 20545623 | 3.7463 | 0.0095524 | 392.1893
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | FUSE | 1102 | 11378 | 1569980 | 0.28627 | 0.0020747 | 137.9838
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 147 | 6973 | 1901981 | 0.34681 | 0.0012715 | 272.7637
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 8 | 2300 | 284046 | 0.051794 | 0.00041939 | 123.4983
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 17 | 686 | 0.00012509 | 3.0998e-06 | 40.3529
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 3 | 841 | 0.00015335 | 5.4703e-07 | 280.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | FUSE | 6 | 17 | 2179 | 0.0003945 | 3.0778e-06 | 128.1765
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | CE | NONE | 4 | 1860 | 168961 | 0.03059 | 0.00033675 | 90.8392
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 13 | 978 | 0.00017706 | 2.3536e-06 | 75.2308
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | INSULATOR | 1 | 2 | 82 | 1.4846e-05 | 3.6209e-07 | 41
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | POLE | 1 | 584 | 36208 | 0.0065553 | 0.00010573 | 62
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | SPLICE, OH | 2 | 250 | 33000 | 0.0059745 | 4.5262e-05 | 132
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 4 | 2346 | 0.00042473 | 7.2419e-07 | 586.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 2 | 24 | 4.3451e-06 | 3.6209e-07 | 12
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 5 | 650 | 0.00011768 | 9.0523e-07 | 130
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 331 | 5.9926e-05 | 1.8105e-07 | 331
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | ARRESTER | 5 | 42 | 6589 | 0.0011929 | 7.6039e-06 | 156.881
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CUTOUT | 2 | 225 | 41790 | 0.0075659 | 4.0735e-05 | 185.7333
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONN/CLAMP | 1 | 13 | 14937 | 0.0027043 | 2.3536e-06 | 1149
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CUTOUT | 9 | 193 | 25620 | 0.0046384 | 3.4942e-05 | 132.7461
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 8 | 520 | 9.4144e-05 | 1.4484e-06 | 65
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | NONE | 3421 | 65476 | 10165360 | 1.8536 | 0.011939 | 155.2532
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | V | CONDUCTOR OVERHEAD | 1 | 92 | 66884 | 0.012109 | 1.6656e-05 | 727
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | INSULATOR | 2 | 635 | 34804 | 0.0063011 | 0.00011496 | 54.8094
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE | 584 | 51245 | 25617754 | 4.613 | 0.0092278 | 499.9074
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | FUSE | 34 | 516 | 192886 | 0.034733 | 9.2917e-05 | 373.8101
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 26 | 51 | 43092 | 0.0077597 | 9.1837e-06 | 844.9412
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | CONN/CLAMP | 1 | 3 | 8832 | 0.0015904 | 5.4022e-07 | 2944
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 7 | 15 | 1012 | 0.00018223 | 2.7011e-06 | 67.4667
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | NONE | 20 | 126 | 9517 | 0.0017137 | 2.2689e-05 | 75.5317
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | POLE | 2413 | 28854 | 5783412 | 1.0373 | 0.005175 | 200.4371
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CUTOUT | 49 | 1223 | 120822 | 0.021669 | 0.00021935 | 98.7915
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | NONE | 1819 | 67602 | 14446374 | 2.591 | 0.012124 | 213.6974
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | NONE | 15 | 1783 | 352627 | 0.063244 | 0.00031978 | 197.7717
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 213 | 764 | 77508 | 0.013901 | 0.00013702 | 101.4503
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | FUSE | 31 | 221 | 30682 | 0.0055028 | 3.9636e-05 | 138.8326
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 79 | 10270 | 0.0018493 | 1.4226e-05 | 130
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 11 | 848 | 477956 | 0.086066 | 0.0001527 | 563.6274
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | NONE | 3142 | 76856 | 11688881 | 2.1314 | 0.014014 | 152.0881
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | NONE | 1077 | 25788 | 5244668 | 0.95632 | 0.0047022 | 203.3763
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | TR | NONE | 15 | 10294 | 750767 | 0.1369 | 0.001877 | 72.9325
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CUTOUT | 10 | 139 | 13742 | 0.0025057 | 2.5346e-05 | 98.8633
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 3 | 3 | 215 | 3.9204e-05 | 5.4703e-07 | 71.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 3 | 42 | 7449 | 0.0013583 | 7.6584e-06 | 177.3571
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | ERF | NONE | 5 | 1084 | 119210 | 0.021737 | 0.00019766 | 109.9723
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 2 | 2940 | 0.00053609 | 3.6468e-07 | 1470
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | FUSE | 1 | 10 | 200 | 3.6468e-05 | 1.8234e-06 | 20
AEP Total | 2020 | 5484199 | PARTIAL POWER | F | NONE | 1 | 7 | 1554 | 0.00028336 | 1.2764e-06 | 222
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | NETWORK TRANSFORMER | 9 | 182 | 206998 | 0.037744 | 3.3186e-05 | 1137.3516
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | SCO | NONE | 2 | 184 | 10484 | 0.0019117 | 3.3551e-05 | 56.9783
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | NONE | 7 | 12 | 3633 | 0.00066245 | 2.1881e-06 | 302.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 5536 | 258692 | 89775807 | 16.1013 | 0.046396 | 347.0374
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | NONE | 2758 | 58704 | 8726658 | 1.5651 | 0.010529 | 148.6553
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | FUSE | 486 | 5569 | 1398148 | 0.25076 | 0.0009988 | 251.0591
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | NONE | 120 | 16011 | 1726236 | 0.3096 | 0.0028716 | 107.8156
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | METERING | 68 | 90 | 9596 | 0.001721 | 1.6142e-05 | 106.6222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 29 | 1027 | 328100 | 0.058428 | 0.00018289 | 319.4742
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 2 | 13 | 1579 | 0.00028319 | 2.3316e-06 | 121.4615
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE | 10 | 575 | 262376 | 0.047502 | 0.0001041 | 456.3061
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 8 | 800 | 0.00014484 | 1.4484e-06 | 100
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | NONE | 31 | 121 | 16557 | 0.0029976 | 2.1907e-05 | 136.8347
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 16 | 2531 | 310414 | 0.056199 | 0.00045823 | 122.6448
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CUTOUT | 7 | 3738 | 453262 | 0.082061 | 0.00067675 | 121.2579
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 6 | 150 | 43328 | 0.0078444 | 2.7157e-05 | 288.8533
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 28 | 7586 | 718248 | 0.13004 | 0.0013734 | 94.6807
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | EQF | SWITCH, OH | 1 | 4 | 716 | 0.00012963 | 7.2419e-07 | 179
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | NONE | 5 | 8 | 600 | 0.00010685 | 1.4246e-06 | 75
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | V | NONE | 17 | 7199 | 713837 | 0.12712 | 0.001282 | 99.1578
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | NONE | 25 | 5820 | 1096959 | 0.19535 | 0.0010364 | 188.4809
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 6 | 102 | 49682 | 0.0088474 | 1.8164e-05 | 487.0784
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | METERING | 3 | 3 | 355 | 6.3218e-05 | 5.3424e-07 | 118.3333
AEP Total | 2025 | 5615460 | PARTIAL POWER | UG | CONDUCTOR UG | 1 | 4 | 768 | 0.00013677 | 7.1232e-07 | 192
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 3 | 2 | 326 | 5.8054e-05 | 3.5616e-07 | 163
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | EQF | CIRCUIT SWITCHER | 2 | 570 | 115551 | 0.020577 | 0.00010151 | 202.7211
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | INSULATOR | 6 | 2674 | 167832 | 0.029887 | 0.00047619 | 62.7644
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | FUSE | 19 | 42 | 4639 | 0.00082611 | 7.4794e-06 | 110.4524
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | GUY/ANCHOR | 1 | 1 | 868 | 0.00015457 | 1.7808e-07 | 868
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 8 | 16 | 14448 | 0.0025729 | 2.8493e-06 | 903
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | O | NONE | 1 | 524 | 123314 | 0.02196 | 9.3314e-05 | 235.3321
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | WW | NONE | 3 | 368 | 34225 | 0.0060948 | 6.5533e-05 | 93.0027
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | METERING | 2 | 2 | 176 | 3.1342e-05 | 3.5616e-07 | 88
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CUTOUT | 8 | 194 | 5793 | 0.0010316 | 3.4547e-05 | 29.8608
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 3 | 4 | 1167 | 0.00020782 | 7.1232e-07 | 291.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | INSULATOR | 1 | 717 | 170646 | 0.030389 | 0.00012768 | 238
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | RECLOSER, LINE/OCR/BR | 2 | 1066 | 287724 | 0.051238 | 0.00018983 | 269.9099
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | OTHER EQUIPMENT | 1 | 1 | 79 | 1.4068e-05 | 1.7808e-07 | 79
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | TOR | NONE | 1 | 242 | 418579 | 0.07454 | 4.3095e-05 | 1729.6653
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 3 | 3285 | 0.00058499 | 5.3424e-07 | 1095
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | SPLICE, OH | 1 | 1 | 74 | 1.3272e-05 | 1.7935e-07 | 74
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 1 | 64 | 1.1525e-05 | 1.8007e-07 | 64
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | ARRESTER | 1 | 45 | 3375 | 0.00060102 | 8.0136e-06 | 75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | OTHER EQUIPMENT | 1 | 1 | 258 | 4.5945e-05 | 1.7808e-07 | 258
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RELAY | 1 | 750 | 94500 | 0.016829 | 0.00013356 | 126
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 459 | 119544 | 0.021288 | 8.1739e-05 | 260.4444
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 5 | 730 | 0.00013 | 8.904e-07 | 146
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 1 | 999 | 0.0001779 | 1.7808e-07 | 999
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 2 | 142 | 11007 | 0.0019601 | 2.5287e-05 | 77.5141
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | SPLICE, OH | 1 | 2 | 5586 | 0.00099475 | 3.5616e-07 | 2793
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 2977 | 0.00053014 | 1.7808e-07 | 2977
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 2 | 84 | 1.4959e-05 | 3.5616e-07 | 42
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | JUMPER/RISER | 1 | 2 | 270 | 4.8082e-05 | 3.5616e-07 | 135
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | SPLICE, OH | 1 | 1 | 149 | 2.6831e-05 | 1.8007e-07 | 149
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 72 | 1.2822e-05 | 1.7808e-07 | 72
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 5 | 1985 | 0.00035349 | 8.904e-07 | 397
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 42 | 13188 | 0.0023485 | 7.4794e-06 | 314
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 3 | 23 | 2800 | 0.00049862 | 4.0958e-06 | 121.7391
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | NONE | 4 | 50 | 6191 | 0.0011025 | 8.904e-06 | 123.82
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 1369 | 0.00024379 | 1.7808e-07 | 1369
AEP Total | 2025 | 5615460 | PARTIAL POWER | TR | NONE | 1 | 5 | 259 | 4.6123e-05 | 8.904e-07 | 51.8
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | ERF | NONE | 1 | 189 | 18522 | 0.0032984 | 3.3657e-05 | 98
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | POLE | 2 | 329 | 36810 | 0.006712 | 5.9991e-05 | 111.8845
AEP Total | 2023 | 5575683 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 108 | 1.937e-05 | 1.7935e-07 | 108
AEP Total | 2025 | 5615460 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 1 | 2 | 202 | 3.5972e-05 | 3.5616e-07 | 101
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | POLE HARDWARE | 1 | 3 | 831 | 0.00014964 | 5.4022e-07 | 277
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CROSSARM | 112 | 39032 | 13180364 | 2.3863 | 0.0070666 | 337.681
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | NONE | 12 | 24 | 17184 | 0.0031111 | 4.3451e-06 | 716
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 2 | 751 | 0.00013597 | 3.6209e-07 | 375.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CUTOUT | 18 | 2125 | 417671 | 0.075618 | 0.00038472 | 196.5511
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CROSSARM | 6 | 2306 | 229168 | 0.04149 | 0.00041749 | 99.379
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 326 | 92062 | 0.016667 | 5.9021e-05 | 282.3988
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 23 | 924 | 203941 | 0.036923 | 0.00016729 | 220.7154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | FUSE | 13 | 1560 | 106606 | 0.019301 | 0.00028243 | 68.3372
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CUTOUT | 3 | 35 | 1844 | 0.00032838 | 6.2328e-06 | 52.6857
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | AB | NONE | 7 | 5168 | 881314 | 0.15694 | 0.00092032 | 170.5329
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 18 | 234 | 86049 | 0.015324 | 4.1671e-05 | 367.7308
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 70 | 850 | 214059 | 0.03812 | 0.00015137 | 251.8341
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, GROUNDING | 1 | 2 | 1008 | 0.0001795 | 3.5616e-07 | 504
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | FUSE | 6 | 36 | 5020 | 0.00089396 | 6.4109e-06 | 139.4444
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 20 | 161 | 84695 | 0.015082 | 2.8671e-05 | 526.0559
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WFS | NONE | 3 | 1394 | 428052 | 0.077497 | 0.00025238 | 307.0674
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 2 | 1852 | 0.0003353 | 3.6209e-07 | 926
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CIRCUIT SWITCHER | 1 | 4 | 140 | 2.5346e-05 | 7.2419e-07 | 35
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | NONE | 1 | 6 | 54 | 9.7765e-06 | 1.0863e-06 | 9
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 134 | 3752 | 0.00067929 | 2.426e-05 | 28
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WL | SWITCH, OH | 2 | 638 | 553784 | 0.10026 | 0.00011551 | 868
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | TIR | NONE | 6 | 5453 | 1808540 | 0.32567 | 0.00098193 | 331.6596
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 3 | 2898 | 0.00052467 | 5.4314e-07 | 966
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | NONE | 9 | 5009 | 694140 | 0.125 | 0.00090198 | 138.5786
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 3 | 4 | 4420 | 0.00079592 | 7.2029e-07 | 1105
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CROSSARM | 3 | 75 | 8082 | 0.0014737 | 1.3676e-05 | 107.76
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | INSULATOR | 2 | 269 | 61594 | 0.011091 | 4.8439e-05 | 228.974
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | SCO | NONE | 6 | 2928 | 23088 | 0.0041408 | 0.00052514 | 7.8852
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | FUSE | 1 | 3 | 63 | 1.1406e-05 | 5.4314e-07 | 21
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 64 | 370 | 71164 | 0.012673 | 6.589e-05 | 192.3351
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 290 | 2801 | 439536 | 0.078272 | 0.0004988 | 156.9211
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 125 | 1375 | 378218 | 0.067353 | 0.00024486 | 275.0676
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 82 | 18771 | 2854198 | 0.50828 | 0.0033427 | 152.0536
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 26 | 1356 | 187476 | 0.033386 | 0.00024148 | 138.2566
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE | 21 | 1714 | 558951 | 0.099538 | 0.00030523 | 326.1091
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | POLE | 10 | 171 | 43487 | 0.0077442 | 3.0452e-05 | 254.3099
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | NONE | 5 | 18 | 2866 | 0.00051038 | 3.2054e-06 | 159.2222
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | O | NONE | 2 | 321 | 22256 | 0.0040077 | 5.7803e-05 | 69.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 3 | 1396 | 0.0002486 | 5.3424e-07 | 465.3333
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | INSULATOR | 1 | 19 | 456 | 8.2113e-05 | 3.4214e-06 | 24
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | OL | NONE | 1 | 853 | 49474 | 0.0089089 | 0.0001536 | 58
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | AO | NONE | 3 | 3133 | 373559 | 0.066523 | 0.00055792 | 119.2336
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 618 | 286752 | 0.051065 | 0.00011005 | 464
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 60 | 14820 | 0.0026391 | 1.0685e-05 | 247
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 3 | 23 | 9160 | 0.0016312 | 4.0958e-06 | 398.2609
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | NONE | 6 | 69 | 6941 | 0.0012361 | 1.2288e-05 | 100.5942
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 15 | 7922 | 0.0014107 | 2.6712e-06 | 528.1333
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | NONE | 1 | 17 | 1360 | 0.00024219 | 3.0274e-06 | 80
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | TOR | SWITCH, OH | 1 | 182 | 50960 | 0.0090749 | 3.2411e-05 | 280
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 1 | 595 | 0.00010596 | 1.7808e-07 | 595
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CUTOUT | 3 | 6 | 1655 | 0.00029472 | 1.0685e-06 | 275.8333
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | SPLICE, OH | 3 | 15 | 4527 | 0.00081519 | 2.7011e-06 | 301.8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 7 | 343 | 6.1765e-05 | 1.2605e-06 | 49
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | V | NONE | 3 | 1750 | 113753 | 0.020484 | 0.00031513 | 65.0017
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 30 | 26771 | 0.0048207 | 5.4022e-06 | 892.3667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 208 | 10816 | 0.0019582 | 3.7658e-05 | 52
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 855 | 64980 | 0.011849 | 0.0001559 | 76
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | VA | POLE | 1 | 302 | 35758 | 0.0064132 | 5.4164e-05 | 118.404
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 5 | 981 | 0.00017594 | 8.9675e-07 | 196.2
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 7 | 343 | 6.1517e-05 | 1.2555e-06 | 49
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | TOR | CROSSARM | 1 | 1 | 486 | 8.7515e-05 | 1.8007e-07 | 486
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | NONE | 1 | 1 | 104 | 1.8727e-05 | 1.8007e-07 | 104
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 3 | 411 | 7.3191e-05 | 5.3424e-07 | 137
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2617 | 116159 | 50009130 | 9.054 | 0.02103 | 430.5231
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | FUSE | 1087 | 7090 | 1198440 | 0.21697 | 0.0012836 | 169.0324
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 835 | 11720 | 2449141 | 0.44341 | 0.0021219 | 208.9711
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | NONE | 202 | 12325 | 1133069 | 0.20514 | 0.0022314 | 91.9326
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 14 | 54 | 26076 | 0.004721 | 9.7765e-06 | 482.8889
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | ARRESTER | 293 | 27352 | 3653498 | 0.66145 | 0.004952 | 133.5733
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | NONE | 47 | 137 | 17238 | 0.0031209 | 2.4803e-05 | 125.8248
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | ARRESTER | 41 | 1580 | 354091 | 0.064107 | 0.00028605 | 224.1082
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 5 | 76 | 6906 | 0.0012503 | 1.376e-05 | 90.8684
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 70 | 5201 | 0.00093655 | 1.2605e-05 | 74.3
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | F | NONE | 5 | 3406 | 521660 | 0.093936 | 0.00061332 | 153.1591
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WFS | NONE | 1 | 145 | 164399 | 0.029485 | 2.6006e-05 | 1133.7862
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | INSULATOR | 3 | 91 | 11496 | 0.0020962 | 1.6593e-05 | 126.3297
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 508 | 70735 | 0.012686 | 9.111e-05 | 139.2421
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | SPLICE, OH | 2 | 46 | 9661 | 0.0017327 | 8.2501e-06 | 210.0217
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 6 | 16 | 3862 | 0.00069265 | 2.8696e-06 | 241.375
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CUTOUT | 6 | 16 | 2426 | 0.0004351 | 2.8696e-06 | 151.625
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | PEDESTAL | 4 | 30 | 964 | 0.00017289 | 5.3805e-06 | 32.1333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 8 | 29 | 1306 | 0.00023423 | 5.2012e-06 | 45.0345
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CABLE TERMINATOR | 1 | 1 | 59 | 1.0582e-05 | 1.7935e-07 | 59
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | PEDESTAL | 29 | 99 | 15302 | 0.002725 | 1.763e-05 | 154.5657
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 534 | 539354 | 0.097648 | 9.6679e-05 | 1010.0262
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | EQF | BREAKER | 9 | 5135 | 723705 | 0.13196 | 0.00093633 | 140.9357
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WTO | FUSE | 1 | 3 | 315 | 5.7438e-05 | 5.4703e-07 | 105
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 4 | 330 | 5.9424e-05 | 7.2029e-07 | 82.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 7 | 3812 | 532409 | 0.094811 | 0.00067884 | 139.6666
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 4 | 716 | 319801 | 0.05695 | 0.00012751 | 446.6494
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 5 | 6 | 289 | 5.1465e-05 | 1.0685e-06 | 48.1667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | FUSE | 4 | 6 | 965 | 0.00017185 | 1.0685e-06 | 160.8333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | NONE | 11 | 758 | 23082 | 0.0041104 | 0.00013498 | 30.4512
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CABLE TERMINATOR | 5 | 17 | 4975 | 0.00089586 | 3.0612e-06 | 292.6471
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | V | TRANSFORMER, GROUNDING | 4 | 3027 | 314233 | 0.055959 | 0.00053905 | 103.81
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 8 | 1784 | 168707 | 0.030043 | 0.00031769 | 94.5667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | POLE | 1 | 11 | 5236 | 0.00093243 | 1.9589e-06 | 476
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | INSULATOR | 3 | 1166 | 126316 | 0.022494 | 0.00020764 | 108.3328
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 4 | 6 | 200 | 3.5616e-05 | 1.0685e-06 | 33.3333
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 34 | 48 | 18135 | 0.0032295 | 8.5478e-06 | 377.8125
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 2 | 381 | 6.7848e-05 | 3.5616e-07 | 190.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | ARRESTER | 5 | 617 | 91236 | 0.016247 | 0.00010988 | 147.8703
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 13 | 29 | 13193 | 0.0023494 | 5.1643e-06 | 454.931
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 2420 | 543779 | 0.096836 | 0.00043095 | 224.7021
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | ARRESTER | 3 | 1903 | 154143 | 0.028107 | 0.000347 | 81
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | CE | NONE | 3 | 1498 | 152642 | 0.027833 | 0.00027315 | 101.8972
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 498 | 9.0806e-05 | 1.8234e-07 | 498
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | POLE | 1 | 2 | 438 | 7.9298e-05 | 3.6209e-07 | 219
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | R | NONE | 3 | 2994 | 105688 | 0.019271 | 0.00054593 | 35.2999
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | U | CONDUCTOR OVERHEAD | 1 | 9 | 3519 | 0.00064166 | 1.6411e-06 | 391
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 4926 | 751440 | 0.13702 | 0.00089822 | 152.5457
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | POLE | 1 | 1 | 186 | 3.3493e-05 | 1.8007e-07 | 186
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | OTHER EQUIPMENT | 1 | 11 | 704 | 0.00012677 | 1.9808e-06 | 64
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | ABI | NONE | 4 | 2248 | 406646 | 0.072415 | 0.00040032 | 180.8923
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 1 | 118 | 2.1013e-05 | 1.7808e-07 | 118
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | REGULATOR | 5 | 1387 | 60626 | 0.010796 | 0.000247 | 43.7102
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 839 | 288616 | 0.051763 | 0.00015047 | 344
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | CUTOUT | 7 | 1013 | 101932 | 0.018152 | 0.00018039 | 100.6239
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 10 | 4314 | 491078 | 0.087451 | 0.00076824 | 113.8336
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | METERING | 1 | 4 | 200 | 3.5616e-05 | 7.1232e-07 | 50
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 1 | 45 | 8.0136e-06 | 1.7808e-07 | 45
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | ARRESTER | 1 | 2 | 150 | 2.6712e-05 | 3.5616e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | ARRESTER | 7 | 30 | 14552 | 0.0026204 | 5.4022e-06 | 485.0667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 3488 | 639887 | 0.11476 | 0.00062557 | 183.4538
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 5 | 8090 | 0.0014568 | 9.0036e-07 | 1618
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 7 | 30 | 5091 | 0.0009066 | 5.3424e-06 | 169.7
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 13 | 7472 | 1313827 | 0.23397 | 0.0013306 | 175.8334
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 3 | 1668 | 0.00029916 | 5.3805e-07 | 556
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 4 | 3799 | 386985 | 0.068914 | 0.00067653 | 101.865
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | U | NONE | 3 | 3320 | 314040 | 0.055924 | 0.00059122 | 94.5904
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 3 | 1179 | 0.00020996 | 5.3424e-07 | 393
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 218 | 1349 | 122246 | 0.02177 | 0.00024023 | 90.6197
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 31 | 384 | 151907 | 0.027052 | 6.8383e-05 | 395.5911
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | FUSE | 1 | 2 | 128 | 2.2957e-05 | 3.587e-07 | 64
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | NONE | 18 | 1649 | 279498 | 0.049773 | 0.00029365 | 169.4955
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 26 | 2915 | 441654 | 0.07865 | 0.0005191 | 151.5108
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 9 | 3438 | 0.00061224 | 1.6027e-06 | 382
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 35 | 1333 | 312378 | 0.055628 | 0.00023738 | 234.3421
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AB | NONE | 2 | 756 | 69525 | 0.012381 | 0.00013463 | 91.9643
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 65 | 1041 | 368033 | 0.065539 | 0.00018538 | 353.5379
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | NONE | 44 | 1232 | 145861 | 0.025975 | 0.00021939 | 118.3937
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | NONE | 48 | 355 | 38167 | 0.0067968 | 6.3218e-05 | 107.5127
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONN/CLAMP | 3 | 3 | 466 | 8.2985e-05 | 5.3424e-07 | 155.3333
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | FUSE | 17 | 35 | 5224 | 0.00093693 | 6.2773e-06 | 149.2571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CUTOUT | 9 | 113 | 22244 | 0.0039895 | 2.0267e-05 | 196.8496
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 5270 | 706489 | 0.12581 | 0.00093848 | 134.0586
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 2 | 138 | 181826 | 0.032611 | 2.475e-05 | 1317.5797
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | INSULATOR | 1 | 208 | 62368 | 0.011291 | 3.7658e-05 | 299.8462
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 1 | 191 | 3.458e-05 | 1.8105e-07 | 191
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CROSSARM | 2 | 23 | 1693 | 0.00030651 | 4.1641e-06 | 73.6087
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | FUSE | 17 | 227 | 22670 | 0.0040371 | 4.0424e-05 | 99.8678
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | METERING | 16 | 30 | 975 | 0.00017363 | 5.3424e-06 | 32.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | FUSE | 2 | 32 | 7947 | 0.0014152 | 5.6986e-06 | 248.3438
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 1 | 1556 | 0.00027907 | 1.7935e-07 | 1556
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 132 | 2.3769e-05 | 1.8007e-07 | 132
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | R | NONE | 3 | 1100 | 89075 | 0.016127 | 0.00019915 | 80.9773
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | FUSE | 31 | 98 | 23561 | 0.0042427 | 1.7647e-05 | 240.4184
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | NONE | 34 | 649 | 86915 | 0.015651 | 0.00011687 | 133.9214
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 56 | 7322 | 749265 | 0.13492 | 0.0013185 | 102.3306
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 106 | 1385 | 473224 | 0.085214 | 0.0002494 | 341.678
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | NONE | 33 | 2480 | 43942 | 0.0079127 | 0.00044658 | 17.7185
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 122 | 42368 | 0.0076706 | 2.2088e-05 | 347.2787
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 2 | 2554 | 0.00046239 | 3.6209e-07 | 1277
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | RECLOSER, LINE/OCR/BR | 1 | 44 | 24242 | 0.0043889 | 7.966e-06 | 550.9545
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | NONE | 41 | 5374 | 1810871 | 0.3302 | 0.00097991 | 336.9689
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | NONE | 51 | 2137 | 240301 | 0.043817 | 0.00038966 | 112.4478
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CABLE TERMINATOR | 12 | 23 | 4982 | 0.00090843 | 4.1939e-06 | 216.6087
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | A | NONE | 3 | 3108 | 342156 | 0.062389 | 0.00056672 | 110.0888
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 14 | 54 | 20413 | 0.0037221 | 9.8465e-06 | 378.0185
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 8 | 28 | 1500 | 0.00027351 | 5.1056e-06 | 53.5714
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | FUSE | 2 | 6 | 3426 | 0.0006247 | 1.0941e-06 | 571
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CAPACITOR | 2 | 19 | 16930 | 0.0030871 | 3.4645e-06 | 891.0526
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | ARRESTER | 17 | 155 | 75135 | 0.0137 | 2.8263e-05 | 484.7419
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | ARRESTER | 8 | 225 | 87010 | 0.015866 | 4.1027e-05 | 386.7111
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CROSSARM | 3 | 14 | 6329 | 0.001154 | 2.5528e-06 | 452.0714
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 17 | 2438 | 0.00044455 | 3.0998e-06 | 143.4118
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | PEDESTAL | 14 | 61 | 8815 | 0.0015873 | 1.0984e-05 | 144.5082
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 28 | 373 | 125291 | 0.022561 | 6.7167e-05 | 335.9008
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 25 | 252 | 45089 | 0.0081193 | 4.5378e-05 | 178.9246
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | INSULATOR | 23 | 1305 | 402675 | 0.07251 | 0.00023499 | 308.5632
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 36 | 79 | 24997 | 0.0045013 | 1.4226e-05 | 316.4177
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CUTOUT | 6 | 93 | 16769 | 0.0030196 | 1.6747e-05 | 180.3118
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE | 433 | 113290 | 26990712 | 4.8408 | 0.020319 | 238.2444
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 866 | 8924 | 2081687 | 0.37335 | 0.0016005 | 233.2684
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 6 | 1003 | 341369 | 0.061225 | 0.00017989 | 340.348
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 1 | 1533 | 311168 | 0.056033 | 0.00027605 | 202.9798
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 8 | 698 | 135666 | 0.02443 | 0.00012569 | 194.3639
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | ARRESTER | 25 | 985 | 300343 | 0.054083 | 0.00017737 | 304.9168
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 10 | 290 | 97791 | 0.017609 | 5.2221e-05 | 337.2103
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 75 | 2472 | 2018163 | 0.36341 | 0.00044514 | 816.409
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | FUSE | 178 | 2097 | 678545 | 0.1217 | 0.0003761 | 323.5789
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | ARRESTER | 289 | 23115 | 4112493 | 0.73758 | 0.0041457 | 177.9145
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | POLE | 16 | 494 | 345236 | 0.061918 | 8.8599e-05 | 698.8583
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | REGULATOR | 10 | 2938 | 267630 | 0.048193 | 0.00052905 | 91.0926
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, GROUNDING | 3 | 1836 | 1063585 | 0.19075 | 0.00032929 | 579.2947
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 89 | 1955 | 316663 | 0.056794 | 0.00035063 | 161.976
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | V | NONE | 1 | 104 | 22568 | 0.0040639 | 1.8727e-05 | 217
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 1609 | 743413 | 0.13387 | 0.00028974 | 462.0342
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE HARDWARE | 5 | 2017 | 260089 | 0.046835 | 0.00036321 | 128.9484
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | FUSE | 287 | 2439 | 632060 | 0.11336 | 0.00043744 | 259.1472
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 8 | 54 | 15913 | 0.0029016 | 9.8465e-06 | 294.6852
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CUTOUT | 8 | 50 | 17402 | 0.0031731 | 9.1171e-06 | 348.04
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | TRANSFORMER, OH | 1 | 1 | 1539 | 0.00028062 | 1.8234e-07 | 1539
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 1 | 571 | 0.00010412 | 1.8234e-07 | 571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | POLE | 21 | 1341 | 1039176 | 0.18638 | 0.00024051 | 774.9262
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | TOR | NONE | 47 | 19074 | 3337532 | 0.59859 | 0.0034209 | 174.9781
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | PEDESTAL | 20 | 260 | 42350 | 0.0075955 | 4.6631e-05 | 162.8846
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 35 | 11919 | 2326735 | 0.4173 | 0.0021377 | 195.2123
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 16 | 19082 | 0.0034361 | 2.8812e-06 | 1192.625
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | NONE | 7 | 5498 | 108522 | 0.019542 | 0.00099004 | 19.7385
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | O | ARRESTER | 1 | 2 | 150 | 2.6903e-05 | 3.587e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 42 | 4956 | 0.00089244 | 7.563e-06 | 118
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | POLE HARDWARE | 1 | 174 | 45868 | 0.0082595 | 3.1333e-05 | 263.6092
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 3 | 72 | 1.2965e-05 | 5.4022e-07 | 24
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 34 | 15733 | 0.0028331 | 6.1224e-06 | 462.7353
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 1 | 5 | 265 | 4.7719e-05 | 9.0036e-07 | 53
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | FUSE | 2 | 3 | 215 | 3.8287e-05 | 5.3424e-07 | 71.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | POLE | 3 | 32 | 3250 | 0.00057876 | 5.6986e-06 | 101.5625
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | FUSE | 1 | 3 | 171 | 3.0452e-05 | 5.3424e-07 | 57
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | R | NONE | 1 | 3 | 18 | 3.2054e-06 | 5.3424e-07 | 6
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 1 | 463 | 8.4424e-05 | 1.8234e-07 | 463
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | VA | NONE | 1 | 1 | 60 | 1.0761e-05 | 1.7935e-07 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | METERING | 1 | 1 | 113 | 2.0348e-05 | 1.8007e-07 | 113
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 3 | 480 | 8.6088e-05 | 5.3805e-07 | 160
AEP Total | 2022 | 5553337 | PARTIAL POWER | OU | NONE | 1 | 1 | 38 | 6.8427e-06 | 1.8007e-07 | 38
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | ERF | NONE | 3 | 2846 | 93070 | 0.016574 | 0.00050682 | 32.702
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | BE | OTHER EQUIPMENT | 2 | 0 | 0 | 0 | 0
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | FUSE | 1 | 31 | 2976 | 0.00052997 | 5.5205e-06 | 96
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | SPLICE, UG | 1 | 1 | 91 | 1.6205e-05 | 1.7808e-07 | 91
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 1 | 172 | 3.063e-05 | 1.7808e-07 | 172
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | NONE | 946 | 22910 | 4693879 | 0.84981 | 0.0041478 | 204.8834
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | NONE | 7310 | 375526 | 109857527 | 19.8893 | 0.067988 | 292.5431
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | NONE | 1837 | 56762 | 16187860 | 2.9308 | 0.010277 | 285.1883
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | ARRESTER | 4 | 36 | 46630 | 0.0084422 | 6.5177e-06 | 1295.2778
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | NONE | 143 | 7284 | 2122048 | 0.38419 | 0.0013187 | 291.33
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 249 | 9412 | 3707550 | 0.67124 | 0.001704 | 393.9173
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 28 | 8443 | 2359845 | 0.42724 | 0.0015286 | 279.5031
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | ABI | NONE | 6 | 5321 | 677861 | 0.12272 | 0.00096335 | 127.3935
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 13 | 1070 | 658070 | 0.11914 | 0.00019372 | 615.0187
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | TOR | NONE | 1 | 1413 | 804336 | 0.14562 | 0.00025582 | 569.2399
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | AF | NONE | 1 | 32 | 1472 | 0.0002665 | 5.7935e-06 | 46
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | INSULATOR | 1 | 1431 | 508721 | 0.092102 | 0.00025908 | 355.5003
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | PEDESTAL | 13 | 84 | 16418 | 0.0029724 | 1.5208e-05 | 195.4524
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CUTOUT | 14 | 258 | 86976 | 0.015747 | 4.671e-05 | 337.1163
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 21 | 2373 | 0.00042962 | 3.802e-06 | 113
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | POLE | 4 | 103 | 32338 | 0.0058547 | 1.8648e-05 | 313.9612
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | ARRESTER | 6 | 212 | 97290 | 0.017614 | 3.8382e-05 | 458.9151
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | ARRESTER | 8 | 1417 | 170905 | 0.030652 | 0.00025414 | 120.6104
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | INSULATOR | 3 | 3598 | 472265 | 0.084701 | 0.0006453 | 131.2576
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 3 | 7 | 1367 | 0.00024616 | 1.2605e-06 | 195.2857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 314 | 335122 | 0.060104 | 5.6316e-05 | 1067.2675
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | NONE | 28 | 329 | 106974 | 0.019186 | 5.9006e-05 | 325.1489
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | PEDESTAL | 11 | 130 | 33321 | 0.0059761 | 2.3316e-05 | 256.3154
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 3 | 225 | 104968 | 0.018826 | 4.0354e-05 | 466.5244
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | EQF | CROSSARM | 3 | 1121 | 373717 | 0.067026 | 0.00020105 | 333.3782
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 1712 | 285585 | 0.051426 | 0.00030828 | 166.8137
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SWITCH, OH | 11 | 587 | 100228 | 0.017976 | 0.00010528 | 170.7462
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | OU | NONE | 5 | 3049 | 250560 | 0.044938 | 0.00054684 | 82.1778
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 3 | 162 | 28462 | 0.0051252 | 2.9172e-05 | 175.6914
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 9 | 487 | 305825 | 0.054461 | 8.6725e-05 | 627.9774
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 777 | 6212 | 834191 | 0.14855 | 0.0011062 | 134.287
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 173 | 6390 | 2298690 | 0.40935 | 0.0011379 | 359.7324
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 14 | 240 | 35741 | 0.0063648 | 4.2739e-05 | 148.9208
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | NONE | 262 | 11354 | 4390173 | 0.7818 | 0.0020219 | 386.6631
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | FUSE | 13 | 131 | 13734 | 0.0024731 | 2.3589e-05 | 104.8397
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | FUSE | 4 | 9 | 781 | 0.00014007 | 1.6142e-06 | 86.7778
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | METERING | 41 | 91 | 6917 | 0.0012406 | 1.6321e-05 | 76.011
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | NONE | 2 | 1784 | 199752 | 0.03597 | 0.00032125 | 111.9686
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | FO | NONE | 1 | 463 | 84266 | 0.015365 | 8.4424e-05 | 182
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 2 | 296 | 300736 | 0.054837 | 5.3973e-05 | 1016
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 370 | 21830 | 0.0039805 | 6.7467e-05 | 59
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 13 | 1339 | 0.00024242 | 2.3536e-06 | 103
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 159 | 215127 | 0.038948 | 2.8786e-05 | 1353
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 3 | 357 | 159155 | 0.028814 | 6.4634e-05 | 445.8123
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 54 | 7506 | 0.0013589 | 9.7765e-06 | 139
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 2 | 418 | 7.5677e-05 | 3.6209e-07 | 209
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | NONE | 1 | 103 | 2678 | 0.00048831 | 1.8781e-05 | 26
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 57 | 674 | 491136 | 0.087461 | 0.00012003 | 728.6884
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | BREAKER | 1 | 2 | 1522 | 0.00027407 | 3.6014e-07 | 761
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | POLE | 34 | 239 | 364683 | 0.064943 | 4.2561e-05 | 1525.8703
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 1 | 276 | 4.915e-05 | 1.7808e-07 | 276
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 1 | 747 | 60507 | 0.010775 | 0.00013303 | 81
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 41 | 1700 | 477666 | 0.085063 | 0.00030274 | 280.98
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 2 | 2 | 204 | 3.6328e-05 | 3.5616e-07 | 102
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | POLE | 9 | 453 | 70460 | 0.012548 | 8.067e-05 | 155.5408
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | FUSE | 5 | 12 | 2321 | 0.00041332 | 2.137e-06 | 193.4167
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | POLE | 4 | 131 | 12011 | 0.0021389 | 2.3328e-05 | 91.687
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 4 | 1305 | 0.00023239 | 7.1232e-07 | 326.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | NONE | 4 | 10 | 3167 | 0.00056398 | 1.7808e-06 | 316.7
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | SCO | NONE | 2 | 7 | 13760 | 0.0024504 | 1.2466e-06 | 1965.7143
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 3 | 1056 | 0.00018805 | 5.3424e-07 | 352
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 18 | 2520 | 0.00044876 | 3.2054e-06 | 140
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 17 | 1840 | 54450 | 0.0096964 | 0.00032767 | 29.5924
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | TIN | NONE | 2 | 2641 | 541768 | 0.096478 | 0.00047031 | 205.1374
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | TRANSFORMER, GROUNDING | 1 | 271 | 41192 | 0.0073355 | 4.826e-05 | 152
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, STATION SERVICE | 1 | 83 | 23987 | 0.0042716 | 1.4781e-05 | 289
AEP Total | 2024 | 5615460 | PARTIAL POWER | UG | SPLICE, UG | 1 | 1 | 137 | 2.4397e-05 | 1.7808e-07 | 137
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | INSULATOR | 1 | 12 | 14786 | 0.0026331 | 2.137e-06 | 1232.1667
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | STATIC WIRE | 1 | 181 | 170502 | 0.030703 | 3.2593e-05 | 942
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | METERING | 10 | 14 | 2406 | 0.00043325 | 2.521e-06 | 171.8571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 282 | 5.078e-05 | 1.8007e-07 | 282
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 264 | 4.8138e-05 | 1.8234e-07 | 264
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | NONE | 4 | 11 | 3327 | 0.0005991 | 1.9808e-06 | 302.4545
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CROSSARM | 65 | 9391 | 1824251 | 0.32718 | 0.0016843 | 194.2552
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | NONE | 6 | 108 | 81303 | 0.01464 | 1.9448e-05 | 752.8056
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, OH | 8 | 49 | 13704 | 0.0024677 | 8.8235e-06 | 279.6735
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | FUSE | 1 | 4 | 1124 | 0.0002024 | 7.2029e-07 | 281
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 8 | 3088 | 0.00055606 | 1.4406e-06 | 386
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | FUSE | 139 | 440 | 47572 | 0.008532 | 7.8914e-05 | 108.1182
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 37 | 82 | 11821 | 0.0021201 | 1.4707e-05 | 144.1585
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 1225 | 154764 | 0.028019 | 0.00022178 | 126.338
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | POLE | 3 | 12 | 3788 | 0.0006858 | 2.1726e-06 | 315.6667
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 5 | 19810 | 0.0035865 | 9.0523e-07 | 3962
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 160 | 85760 | 0.015527 | 2.8967e-05 | 536
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 3 | 636 | 0.00011515 | 5.4314e-07 | 212
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 4 | 4 | 1345 | 0.00024351 | 7.2419e-07 | 336.25
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABI | NONE | 1 | 1540 | 214060 | 0.038755 | 0.00027881 | 139
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | PEDESTAL | 1 | 13 | 1950 | 0.00035304 | 2.3536e-06 | 150
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 86 | 1251 | 372570 | 0.067935 | 0.00022811 | 297.8177
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | NONE | 2882 | 35645 | 4311746 | 0.78621 | 0.0064996 | 120.9636
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | NONE | 6 | 22 | 8123 | 0.0014812 | 4.0115e-06 | 369.2273
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | NONE | 512 | 93415 | 18522696 | 3.3775 | 0.017033 | 198.284
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 4 | 4 | 786 | 0.00014332 | 7.2937e-07 | 196.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 5 | 8 | 1044 | 0.00019037 | 1.4587e-06 | 130.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 26 | 4281 | 801841 | 0.14621 | 0.00078061 | 187.3023
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | ARRESTER | 1 | 108 | 92340 | 0.016837 | 1.9693e-05 | 855
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | V | NONE | 4 | 4034 | 436737 | 0.079636 | 0.00073557 | 108.264
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WL | INSULATOR | 1 | 1 | 645 | 0.00011761 | 1.8234e-07 | 645
AEP Total | 2020 | 5484199 | PARTIAL POWER | OU | NONE | 1 | 1 | 104 | 1.8964e-05 | 1.8234e-07 | 104
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | FUSE | 28 | 131 | 18236 | 0.0033252 | 2.3887e-05 | 139.2061
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 3 | 311 | 5.6708e-05 | 5.4703e-07 | 103.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CUTOUT | 4 | 104 | 16558 | 0.0030192 | 1.8964e-05 | 159.2115
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | R | NONE | 7 | 3764 | 433489 | 0.079043 | 0.00068634 | 115.1671
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 6 | 6141 | 705277 | 0.12649 | 0.0011014 | 114.8473
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | FUSE | 4 | 157 | 19493 | 0.0034961 | 2.8158e-05 | 124.1592
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 57 | 1.0223e-05 | 1.7935e-07 | 57
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 6 | 3090 | 0.00055419 | 1.0761e-06 | 515
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 4 | 1432 | 0.00025683 | 7.174e-07 | 358
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | FO | NONE | 7 | 395 | 71038 | 0.012741 | 7.0843e-05 | 179.843
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | FUSE | 6 | 36 | 2321 | 0.00041627 | 6.4566e-06 | 64.4722
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 639 | 67125 | 0.012039 | 0.0001146 | 105.0469
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | ARRESTER | 3 | 21 | 8314 | 0.0014911 | 3.7664e-06 | 395.9048
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 228 | 53730 | 9236750 | 1.6449 | 0.0095682 | 171.9105
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | FUSE | 825 | 6114 | 914202 | 0.1628 | 0.0010888 | 149.526
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CUTOUT | 342 | 1676 | 108809 | 0.019377 | 0.00029846 | 64.9218
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | NONE | 858 | 20406 | 3224003 | 0.57413 | 0.0036339 | 157.9929
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 83 | 2999 | 348529 | 0.062066 | 0.00053406 | 116.2151
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | U | NONE | 18 | 16977 | 1842473 | 0.32811 | 0.0030233 | 108.5276
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 85 | 1534 | 380411 | 0.067744 | 0.00027317 | 247.9863
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | AO | NONE | 3 | 850 | 229132 | 0.041095 | 0.00015245 | 269.5671
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | NONE | 1 | 1 | 919 | 0.00016482 | 1.7935e-07 | 919
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 28 | 60 | 38570 | 0.0068685 | 1.0685e-05 | 642.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | FUSE | 1 | 11 | 110 | 1.9729e-05 | 1.9729e-06 | 10
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 251 | 11295 | 0.0020449 | 4.5443e-05 | 45
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | FUSE | 2 | 50 | 15600 | 0.0028243 | 9.0523e-06 | 312
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 20 | 142 | 72998 | 0.012999 | 2.5287e-05 | 514.0704
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 1017 | 42894 | 6570215 | 1.17 | 0.0076386 | 153.1733
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | POLE | 943 | 6832 | 1092116 | 0.19448 | 0.0012166 | 159.853
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 10 | 9203 | 827903 | 0.14743 | 0.0016389 | 89.9601
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 392 | 4290 | 1140980 | 0.20319 | 0.00076396 | 265.9627
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | POLE | 2 | 30 | 5091 | 0.00091307 | 5.3805e-06 | 169.7
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | ERF | NONE | 3 | 3970 | 283716 | 0.051366 | 0.00071875 | 71.465
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | F | NONE | 2 | 2044 | 42924 | 0.0076439 | 0.000364 | 21
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | JUMPER/RISER | 1 | 66 | 71346 | 0.012705 | 1.1753e-05 | 1081
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CUTOUT | 2848 | 97930 | 18208912 | 3.2967 | 0.01773 | 185.938
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 16 | 1577 | 751050 | 0.13597 | 0.00028551 | 476.2524
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | POLE | 2 | 101 | 17691 | 0.0032029 | 1.8286e-05 | 175.1584
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | NONE | 15 | 79 | 8028 | 0.0014534 | 1.4303e-05 | 101.6203
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CUTOUT | 90 | 1108 | 224482 | 0.040642 | 0.0002006 | 202.6011
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | ARRESTER | 18 | 1926 | 207796 | 0.037621 | 0.0003487 | 107.8899
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CROSSARM | 22 | 3577 | 467065 | 0.08456 | 0.0006476 | 130.5745
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 45 | 143 | 16047 | 0.0029053 | 2.589e-05 | 112.2168
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | NONE | 50 | 2882 | 5879610 | 1.0645 | 0.00052178 | 2040.1145
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CUTOUT | 8 | 121 | 119685 | 0.021669 | 2.1907e-05 | 989.1322
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 2 | 222 | 4.0192e-05 | 3.6209e-07 | 111
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | ARRESTER | 7 | 150 | 28848 | 0.0052228 | 2.7157e-05 | 192.32
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CROSSARM | 3 | 325 | 302509 | 0.054768 | 5.884e-05 | 930.7969
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | FUSE | 4 | 11 | 1367 | 0.00024749 | 1.9915e-06 | 124.2727
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONN/CLAMP | 3 | 7 | 753 | 0.00013633 | 1.2673e-06 | 107.5714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, OH | 68 | 1127 | 267025 | 0.048084 | 0.00020294 | 236.9343
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | NONE | 25 | 1465 | 699606 | 0.12598 | 0.00026381 | 477.5468
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 9 | 118 | 14651 | 0.0026382 | 2.1248e-05 | 124.161
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONN/CLAMP | 64 | 266 | 44143 | 0.0079489 | 4.7899e-05 | 165.9511
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | NONE | 4 | 11 | 6396 | 0.0011517 | 1.9808e-06 | 581.4545
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 68 | 3008 | 761420 | 0.13711 | 0.00054166 | 253.1316
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | NONE | 98 | 6855 | 1160746 | 0.20902 | 0.0012344 | 169.3284
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONN/CLAMP | 101 | 622 | 175208 | 0.03155 | 0.000112 | 281.6849
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | NONE | 40 | 3316 | 439668 | 0.079172 | 0.00059712 | 132.5899
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 23 | 174 | 37525 | 0.0067572 | 3.1333e-05 | 215.6609
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | FUSE | 19 | 229 | 24009 | 0.0043233 | 4.1236e-05 | 104.8428
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | FUSE | 847 | 5036 | 642079 | 0.11516 | 0.00090321 | 127.4978
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONN/CLAMP | 115 | 231 | 53613 | 0.0096155 | 4.143e-05 | 232.0909
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | FUSE | 5 | 10 | 502 | 9.0396e-05 | 1.8007e-06 | 50.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 7 | 16 | 9118 | 0.0016419 | 2.8812e-06 | 569.875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | FUSE | 306 | 1616 | 245389 | 0.044011 | 0.00028983 | 151.8496
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | WU | NONE | 6 | 1547 | 71088 | 0.01275 | 0.00027745 | 45.9522
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 11 | 235 | 4.2317e-05 | 1.9808e-06 | 21.3636
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SWITCH, OH | 6 | 413 | 46384 | 0.0083525 | 7.437e-05 | 112.3099
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CROSSARM | 6 | 1021 | 130622 | 0.023521 | 0.00018385 | 127.9354
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | FUSE | 10 | 738 | 39184 | 0.0070559 | 0.00013289 | 53.0949
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | NONE | 1 | 0 | 0 | 0 | 0
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | NONE | 29 | 939 | 108156 | 0.019398 | 0.00016841 | 115.1821
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 3 | 688 | 46740 | 0.0084166 | 0.00012389 | 67.936
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | INSULATOR | 4 | 7204 | 823660 | 0.14832 | 0.0012972 | 114.3337
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | ARRESTER | 4 | 3425 | 1231089 | 0.22168 | 0.00061675 | 359.442
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 9 | 15 | 2635 | 0.00047259 | 2.6903e-06 | 175.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | FUSE | 12 | 127 | 29770 | 0.0053607 | 2.2869e-05 | 234.4094
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 3 | 16 | 1642 | 0.00029449 | 2.8696e-06 | 102.625
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONN/CLAMP | 1 | 10 | 1370 | 0.0002467 | 1.8007e-06 | 137
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | FUSE | 64 | 568 | 91882 | 0.016754 | 0.00010357 | 161.7641
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CUTOUT | 32 | 99 | 14602 | 0.0026626 | 1.8052e-05 | 147.4949
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 161 | 52325 | 0.009541 | 2.9357e-05 | 325
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 4 | 10 | 2361 | 0.00043051 | 1.8234e-06 | 236.1
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR UG | 8 | 149 | 40293 | 0.0073471 | 2.7169e-05 | 270.4228
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 14 | 1259 | 1154483 | 0.20559 | 0.0002242 | 916.9841
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | AB | INSULATOR | 1 | 65 | 11460 | 0.0020408 | 1.1575e-05 | 176.3077
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONN/CLAMP | 1 | 1 | 261 | 4.6479e-05 | 1.7808e-07 | 261
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 226 | 29601 | 0.0052713 | 4.0246e-05 | 130.9779
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CROSSARM | 2 | 1414 | 170768 | 0.03041 | 0.0002518 | 120.7694
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | FW | NONE | 2 | 1042 | 32302 | 0.0057523 | 0.00018556 | 31
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 2 | 522 | 343326 | 0.061139 | 9.2958e-05 | 657.7126
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | NONE | 4 | 193 | 43311 | 0.0077128 | 3.4369e-05 | 224.4093
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 1 | 181 | 3.2593e-05 | 1.8007e-07 | 181
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 886 | 261488 | 0.04768 | 0.00016156 | 295.1332
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | METERING | 1 | 1 | 97 | 1.7561e-05 | 1.8105e-07 | 97
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | FUSE | 1 | 2 | 90 | 1.6206e-05 | 3.6014e-07 | 45
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | ERF | NONE | 3 | 2657 | 120718 | 0.021738 | 0.00047845 | 45.4339
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 1 | 206 | 3.6684e-05 | 1.7808e-07 | 206
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | METERING | 2 | 2 | 25 | 4.452e-06 | 3.5616e-07 | 12.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 1 | 406 | 103362 | 0.018407 | 7.23e-05 | 254.5862
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CROSSARM | 2 | 656 | 230235 | 0.041 | 0.00011682 | 350.968
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 1 | 104 | 4264 | 0.00075933 | 1.852e-05 | 41
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 1 | 333 | 5.9964e-05 | 1.8007e-07 | 333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 3 | 243 | 4.3757e-05 | 5.4022e-07 | 81
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | SCO | NONE | 3 | 2511 | 277046 | 0.049336 | 0.00044716 | 110.3329
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | FUSE | 7 | 110 | 24920 | 0.0044377 | 1.9589e-05 | 226.5455
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | NONE | 1 | 1 | 241 | 4.2917e-05 | 1.7808e-07 | 241
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | RELAY | 1 | 1 | 9 | 1.6027e-06 | 1.7808e-07 | 9
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 9 | 351 | 6.2506e-05 | 1.6027e-06 | 39
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 6 | 2322 | 0.0004135 | 1.0685e-06 | 387
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 4 | 58 | 4352 | 0.000775 | 1.0329e-05 | 75.0345
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 9 | 1440 | 0.00025643 | 1.6027e-06 | 160
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | INSULATOR | 1 | 1 | 181 | 3.2232e-05 | 1.7808e-07 | 181
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | POLE | 1 | 189 | 18333 | 0.0032647 | 3.3657e-05 | 97
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | TRANSFORMER, UG | 3 | 19 | 3004 | 0.00053495 | 3.3835e-06 | 158.1053
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | INSULATOR | 2 | 3880 | 467916 | 0.083921 | 0.00069588 | 120.5969
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | TRANSFORMER, GROUNDING | 1 | 1 | 265 | 4.8321e-05 | 1.8234e-07 | 265
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 1 | 77 | 1.404e-05 | 1.8234e-07 | 77
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 1 | 122 | 2.1881e-05 | 1.7935e-07 | 122
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 1 | 1106 | 0.00019916 | 1.8007e-07 | 1106
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | NONE | 1 | 1 | 285 | 5.0753e-05 | 1.7808e-07 | 285
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 8 | 299 | 99708 | 0.018181 | 5.452e-05 | 333.4716
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CUTOUT | 13 | 214 | 122152 | 0.022273 | 3.9021e-05 | 570.8037
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | NONE | 16 | 30 | 4492 | 0.00081908 | 5.4703e-06 | 149.7333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CUTOUT | 2 | 403 | 58420 | 0.010652 | 7.3484e-05 | 144.9628
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | POLE | 4 | 248 | 311016 | 0.056711 | 4.5221e-05 | 1254.0968
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 6 | 408 | 7.3469e-05 | 1.0804e-06 | 68
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 2 | 260 | 4.6819e-05 | 3.6014e-07 | 130
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | NONE | 13 | 26 | 5390 | 0.00095985 | 4.6301e-06 | 207.3077
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 5 | 155 | 2.7602e-05 | 8.904e-07 | 31
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CUTOUT | 1 | 7 | 889 | 0.00015831 | 1.2466e-06 | 127
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | CONN/CLAMP | 2 | 648 | 67454 | 0.012012 | 0.0001154 | 104.0957
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 1 | 906 | 0.00016134 | 1.7808e-07 | 906
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 12 | 916 | 0.00016312 | 2.137e-06 | 76.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CUTOUT | 27 | 164 | 56876 | 0.010128 | 2.9205e-05 | 346.8049
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | NONE | 5 | 7 | 1149 | 0.00020461 | 1.2466e-06 | 164.1429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 3 | 1212 | 0.00021583 | 5.3424e-07 | 404
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CUTOUT | 7 | 505 | 77246 | 0.013756 | 8.993e-05 | 152.9624
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 3 | 16 | 6871 | 0.0012236 | 2.8493e-06 | 429.4375
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | POLE HARDWARE | 2 | 6 | 3394 | 0.0006044 | 1.0685e-06 | 565.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 23 | 101 | 12818 | 0.0022826 | 1.7986e-05 | 126.9109
AEP Total | 2024 | 5615460 | PARTIAL POWER | WFS | CONDUCTOR OVERHEAD | 3 | 5 | 1488 | 0.00026498 | 8.904e-07 | 297.6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 7 | 11557 | 0.0020581 | 1.2466e-06 | 1651
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | NONE | 2 | 2 | 67 | 1.1931e-05 | 3.5616e-07 | 33.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 1 | 1 | 1149 | 0.00020461 | 1.7808e-07 | 1149
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 5 | 15 | 2115 | 0.00037664 | 2.6712e-06 | 141
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | NONE | 1 | 1627 | 218018 | 0.038825 | 0.00028974 | 134
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 17 | 353 | 148874 | 0.026511 | 6.2862e-05 | 421.7394
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | RECLOSER, LINE/OCR/BR | 2 | 1508 | 2513810 | 0.45512 | 0.00027302 | 1666.9828
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 3 | 16 | 3452 | 0.00062497 | 2.8967e-06 | 215.75
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | OU | NONE | 1 | 242 | 20812 | 0.0037062 | 4.3095e-05 | 86
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 1 | 1574 | 0.0002803 | 1.7808e-07 | 1574
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | BE | NONE | 1 | 47 | 4747 | 0.00084534 | 8.3698e-06 | 101
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 3 | 537 | 9.5629e-05 | 5.3424e-07 | 179
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 43 | 9288 | 0.0016936 | 7.8407e-06 | 216
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 559 | 150084 | 0.027172 | 0.0001012 | 268.4866
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | FUSE | 137 | 512 | 114043 | 0.020647 | 9.2696e-05 | 222.7402
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CUTOUT | 38 | 721 | 272008 | 0.049246 | 0.00013053 | 377.2649
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 9 | 505 | 49707 | 0.0089993 | 9.1428e-05 | 98.4297
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 18 | 237 | 75683 | 0.013702 | 4.2908e-05 | 319.3376
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 7 | 31 | 3309 | 0.00059908 | 5.6124e-06 | 106.7419
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 3 | 3 | 460 | 8.3281e-05 | 5.4314e-07 | 153.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 54 | 620 | 164653 | 0.02981 | 0.00011225 | 265.5694
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CUTOUT | 12 | 49 | 15172 | 0.0027468 | 8.8713e-06 | 309.6327
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 43 | 6966 | 889186 | 0.16098 | 0.0012612 | 127.6466
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | FUSE | 12 | 227 | 189252 | 0.034263 | 4.1098e-05 | 833.7093
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 9 | 10440 | 0.0018901 | 1.6294e-06 | 1160
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CABLE TERMINATOR | 12 | 19 | 6787 | 0.0012288 | 3.4399e-06 | 357.2105
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 7 | 163 | 28992 | 0.0052489 | 2.9511e-05 | 177.865
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 11 | 1954 | 0.00035376 | 1.9915e-06 | 177.6364
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | INSULATOR | 4 | 78 | 43520 | 0.0078791 | 1.4122e-05 | 557.9487
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 18 | 3042 | 0.00055074 | 3.2588e-06 | 169
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 2 | 25 | 2741 | 0.00049625 | 4.5262e-06 | 109.64
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | NONE | 847 | 20595 | 4722505 | 0.85039 | 0.0037086 | 229.3035
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | NONE | 2786 | 88753 | 25589811 | 4.608 | 0.015982 | 288.3262
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | NONE | 1228 | 46529 | 13729985 | 2.4724 | 0.0083786 | 295.0845
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | INSULATOR | 3 | 11 | 867 | 0.00015697 | 1.9915e-06 | 78.8182
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 2 | 23 | 5495 | 0.00099485 | 4.1641e-06 | 238.913
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | SO | NONE | 2 | 809 | 4854 | 0.0008788 | 0.00014647 | 6
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SO | NONE | 1 | 1 | 454 | 8.2195e-05 | 1.8105e-07 | 454
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 861 | 139584 | 0.025271 | 0.00015588 | 162.1185
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | U | NONE | 4 | 2464 | 398023 | 0.072061 | 0.0004461 | 161.5353
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 1 | 1086 | 0.00019662 | 1.8105e-07 | 1086
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE | 199 | 22373 | 4939114 | 0.90061 | 0.0040795 | 220.7623
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | U | NONE | 5 | 1087 | 81403 | 0.014843 | 0.00019821 | 74.8878
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 188 | 786 | 75850 | 0.013658 | 0.00014154 | 96.5013
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | FUSE | 459 | 3156 | 494768 | 0.089094 | 0.00056831 | 156.7706
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 31 | 4838 | 1564200 | 0.28167 | 0.00087119 | 323.3154
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CUTOUT | 20 | 2137 | 169903 | 0.030595 | 0.00038481 | 79.5054
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | NONE | 52 | 970 | 284715 | 0.051269 | 0.00017467 | 293.5206
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 845 | 59791 | 0.010648 | 0.00015048 | 70.7586
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 6 | 93 | 28360 | 0.0050503 | 1.6561e-05 | 304.9462
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 155 | 84010 | 0.015067 | 2.7799e-05 | 542
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | FUSE | 1 | 4 | 684 | 0.00012181 | 7.1232e-07 | 171
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | CONN/CLAMP | 5 | 2122 | 18893 | 0.0033645 | 0.00037789 | 8.9034
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TOR | POLE | 1 | 305 | 53091 | 0.0094544 | 5.4314e-05 | 174.0689
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | REGULATOR | 1 | 68 | 12920 | 0.0023559 | 1.2399e-05 | 190
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 1 | 4 | 680 | 0.00012311 | 7.2419e-07 | 170
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 7 | 4614 | 0.00083535 | 1.2673e-06 | 659.1429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 98 | 4606 | 0.0008339 | 1.7743e-05 | 47
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 1 | 408 | 7.3867e-05 | 1.8105e-07 | 408
AEP Total | 2021 | 5523447 | PARTIAL POWER | OU | CONN/CLAMP | 1 | 1 | 124 | 2.245e-05 | 1.8105e-07 | 124
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | BREAKER | 1 | 1 | 174 | 3.1502e-05 | 1.8105e-07 | 174
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | TRANSFORMER, OH | 1 | 4 | 180 | 3.2822e-05 | 7.2937e-07 | 45
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 4 | 13 | 3459 | 0.00062287 | 2.3409e-06 | 266.0769
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 86 | 1.5424e-05 | 1.7935e-07 | 86
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 1 | 275 | 4.9321e-05 | 1.7935e-07 | 275
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 5 | 17 | 3123 | 0.00055614 | 3.0274e-06 | 183.7059
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 3 | 809 | 0.00014407 | 5.3424e-07 | 269.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 4 | 327 | 43973 | 0.0078307 | 5.8232e-05 | 134.474
AEP Total | 2025 | 5615460 | PARTIAL POWER | VIN | NONE | 1 | 4 | 284 | 5.0575e-05 | 7.1232e-07 | 71
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 1 | 203 | 3.615e-05 | 1.7808e-07 | 203
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 1 | 116 | 2.0657e-05 | 1.7808e-07 | 116
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 54 | 9.6163e-06 | 1.7808e-07 | 54
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 2 | 215 | 3.8287e-05 | 3.5616e-07 | 107.5
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | U | NONE | 4 | 3494 | 171206 | 0.030706 | 0.00062665 | 49
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | FUSE | 1 | 4 | 396 | 7.1023e-05 | 7.174e-07 | 99
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 242 | 4.3095e-05 | 1.7808e-07 | 242
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | FUSE | 1 | 19 | 3002 | 0.0005346 | 3.3835e-06 | 158
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CROSSARM | 2 | 448 | 71428 | 0.01272 | 7.978e-05 | 159.4375
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 7 | 1843 | 0.0003282 | 1.2466e-06 | 263.2857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 2 | 756 | 0.00013463 | 3.5616e-07 | 378
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 1 | 258 | 4.671e-05 | 1.8105e-07 | 258
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | TRANSFORMER, UG | 1 | 4 | 2816 | 0.00050708 | 7.2029e-07 | 704
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | NONE | 1 | 5 | 675 | 0.00012106 | 8.9675e-07 | 135
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 4 | 3624 | 0.00064997 | 7.174e-07 | 906
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | ARRESTER | 1 | 1 | 98 | 1.7576e-05 | 1.7935e-07 | 98
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | TRANSFORMER, STATION SERVICE | 1 | 2 | 166 | 2.9772e-05 | 3.587e-07 | 83
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | POLE HARDWARE | 2 | 21 | 28727 | 0.0052009 | 3.802e-06 | 1367.9524
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 123 | 2.2428e-05 | 1.8234e-07 | 123
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RELAY | 3 | 2618 | 451508 | 0.082329 | 0.00047737 | 172.4629
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | FUSE | 1 | 1 | 134 | 2.4434e-05 | 1.8234e-07 | 134
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 4 | 396 | 7.2207e-05 | 7.2937e-07 | 99
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | VA | NONE | 3 | 734 | 194040 | 0.035382 | 0.00013384 | 264.3597
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | ERF | NONE | 5 | 2986 | 38818 | 0.0070782 | 0.00054447 | 13
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | A | NONE | 3 | 1675 | 412325 | 0.075184 | 0.00030542 | 246.1642
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 6 | 5948 | 0.0010769 | 1.0863e-06 | 991.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 2 | 862 | 0.00015606 | 3.6209e-07 | 431
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | SWITCH, OH | 1 | 13 | 11284 | 0.0020429 | 2.3536e-06 | 868
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | NONE | 1 | 50 | 26500 | 0.0048321 | 9.1171e-06 | 530
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | INSULATOR | 1 | 4 | 232 | 4.1777e-05 | 7.2029e-07 | 58
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SWITCH, OH | 6 | 568 | 97511 | 0.017559 | 0.00010228 | 171.6743
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 2 | 281 | 5.06e-05 | 3.6014e-07 | 140.5
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | VIN | NONE | 2 | 2565 | 327768 | 0.059022 | 0.00046188 | 127.7848
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2247 | 114610 | 35181617 | 6.2651 | 0.02041 | 306.9681
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | NONE | 605 | 25481 | 6866141 | 1.2227 | 0.0045377 | 269.4612
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 253 | 8596 | 2884658 | 0.5137 | 0.0015308 | 335.5814
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE | 132 | 23229 | 5629016 | 1.0024 | 0.0041366 | 242.3271
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | NONE | 350 | 2620 | 197671 | 0.035201 | 0.00046657 | 75.4469
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 111 | 777 | 67698 | 0.012056 | 0.00013837 | 87.1274
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 115 | 1032 | 232736 | 0.041446 | 0.00018378 | 225.5194
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 14 | 715 | 79161 | 0.014097 | 0.00012733 | 110.7147
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | METERING | 2 | 2 | 321 | 5.7164e-05 | 3.5616e-07 | 160.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 15 | 54 | 6441 | 0.001147 | 9.6163e-06 | 119.2778
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | POLE | 10 | 287 | 132938 | 0.023842 | 5.1474e-05 | 463.1986
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 38 | 17363 | 0.0031141 | 6.8153e-06 | 456.9211
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 1525 | 52129 | 0.0093493 | 0.00027351 | 34.183
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SECTIONALIZER | 1 | 35 | 630 | 0.00011345 | 6.3025e-06 | 18
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 3 | 196 | 2697 | 0.00048371 | 3.5153e-05 | 13.7602
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | POLE | 15 | 328 | 79735 | 0.014358 | 5.9064e-05 | 243.0945
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | ARRESTER | 4 | 55 | 49209 | 0.0088256 | 9.8643e-06 | 894.7091
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | SCO | NONE | 2 | 1019 | 7610 | 0.0013649 | 0.00018276 | 7.4681
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | NONE | 1 | 1 | 84 | 1.5065e-05 | 1.7935e-07 | 84
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 84 | 1988 | 654345 | 0.11653 | 0.00035402 | 329.1474
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 162 | 11719 | 1770675 | 0.31532 | 0.0020869 | 151.0944
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 275 | 9606 | 1785331 | 0.31793 | 0.0017106 | 185.8558
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 95 | 130 | 58904 | 0.01049 | 2.315e-05 | 453.1077
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 2 | 9 | 5984 | 0.0010656 | 1.6027e-06 | 664.8889
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | ARRESTER | 8 | 202 | 25926 | 0.0046169 | 3.5972e-05 | 128.3465
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | NONE | 37 | 1718 | 149448 | 0.026614 | 0.00030594 | 86.9895
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 3 | 1371 | 0.00024589 | 5.3805e-07 | 457
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | POLE | 13 | 1125 | 728229 | 0.12968 | 0.00020034 | 647.3147
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 6 | 131 | 91711 | 0.016332 | 2.3328e-05 | 700.084
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 19 | 1124 | 85451 | 0.015217 | 0.00020016 | 76.024
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | METERING | 1 | 4 | 184 | 3.3e-05 | 7.174e-07 | 46
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | TOR | NONE | 5 | 1892 | 471321 | 0.084532 | 0.00033933 | 249.1126
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 11 | 108 | 22175 | 0.0039489 | 1.9233e-05 | 205.3241
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 1 | 993 | 0.00017809 | 1.7935e-07 | 993
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | INSULATOR | 2 | 16 | 1752 | 0.000312 | 2.8493e-06 | 109.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | ARRESTER | 6 | 13 | 163 | 2.9027e-05 | 2.315e-06 | 12.5385
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 266 | 15216 | 1688634 | 0.30071 | 0.0027097 | 110.9775
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 2057 | 231923 | 0.041301 | 0.00036631 | 112.7482
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 5 | 685 | 177384 | 0.031589 | 0.00012198 | 258.9547
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 1964 | 548866 | 0.098439 | 0.00035224 | 279.4633
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | AO | INSULATOR | 3 | 808 | 177796 | 0.031662 | 0.00014389 | 220.0446
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 16 | 102 | 17501 | 0.0031166 | 1.8164e-05 | 171.5784
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | NONE | 10 | 28 | 5270 | 0.00094518 | 5.0218e-06 | 188.2143
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | FUSE | 5 | 17 | 4251 | 0.00075702 | 3.0274e-06 | 250.0588
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | NONE | 5 | 11 | 2168 | 0.00038883 | 1.9729e-06 | 197.0909
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | POLE | 4 | 29 | 22394 | 0.0040325 | 5.2221e-06 | 772.2069
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CUTOUT | 1 | 36 | 11880 | 0.0021662 | 6.5643e-06 | 330
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 50 | 4850 | 0.00086985 | 8.9675e-06 | 97
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | OU | NONE | 1 | 251 | 33634 | 0.0060323 | 4.5017e-05 | 134
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 1 | 47 | 8.4295e-06 | 1.7935e-07 | 47
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 15 | 5535 | 0.0009927 | 2.6903e-06 | 369
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | REGULATOR | 3 | 2338 | 25718 | 0.0046125 | 0.00041932 | 11
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 1 | 243 | 4.3582e-05 | 1.7935e-07 | 243
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 1 | 407 | 7.2996e-05 | 1.7935e-07 | 407
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 17 | 7872 | 0.0014118 | 3.049e-06 | 463.0588
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 2 | 4 | 1012 | 0.00018453 | 7.2937e-07 | 253
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | FUSE | 2 | 77 | 8789 | 0.0016026 | 1.404e-05 | 114.1429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 636 | 15342 | 2132221 | 0.37971 | 0.0027321 | 138.9793
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 10 | 35 | 5649 | 0.001006 | 6.2328e-06 | 161.4
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 93 | 3803 | 884494 | 0.15751 | 0.00067724 | 232.578
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 61 | 170 | 28176 | 0.0050176 | 3.0274e-05 | 165.7412
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 1 | 1 | 468 | 8.4274e-05 | 1.8007e-07 | 468
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | ERF | NONE | 4 | 781 | 171309 | 0.030848 | 0.00014064 | 219.3457
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TOR | INSULATOR | 2 | 1284 | 29532 | 0.0052591 | 0.00022865 | 23
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 49 | 767 | 1277767 | 0.22754 | 0.00013659 | 1665.9283
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | FUSE | 20 | 65 | 99296 | 0.017683 | 1.1575e-05 | 1527.6308
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 9 | 1577 | 150940 | 0.026879 | 0.00028083 | 95.7134
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 38 | 1811 | 190666 | 0.033954 | 0.0003225 | 105.2822
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 24 | 2856 | 0.0005086 | 4.2739e-06 | 119
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 5 | 82 | 17859 | 0.0031803 | 1.4603e-05 | 217.7927
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | WL | TRANSFORMER, GROUNDING | 1 | 3 | 60 | 1.0685e-05 | 5.3424e-07 | 20
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 1272 | 0.00022652 | 1.7808e-07 | 1272
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | ARRESTER | 4 | 2260 | 399800 | 0.072382 | 0.00040916 | 176.9027
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | RECLOSER, LINE/OCR/BR | 2 | 93 | 38147 | 0.0069064 | 1.6837e-05 | 410.1828
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | POLE | 3 | 14 | 14613 | 0.0026646 | 2.5528e-06 | 1043.7857
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WW | NONE | 5 | 3105 | 793065 | 0.14461 | 0.00056617 | 255.4155
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | NONE | 70 | 1335 | 495003 | 0.09026 | 0.00024343 | 370.7888
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, OH | 24 | 14587 | 1768192 | 0.32242 | 0.0026598 | 121.217
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 4 | 13 | 7084 | 0.0012705 | 2.3316e-06 | 544.9231
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | SCO | NONE | 6 | 1793 | 190451 | 0.034157 | 0.00032157 | 106.2192
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 2 | 197 | 22346 | 0.0040457 | 3.5666e-05 | 113.4315
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | NONE | 6 | 1029 | 48334 | 0.0087507 | 0.0001863 | 46.9718
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | PEDESTAL | 4 | 75 | 7419 | 0.0013432 | 1.3578e-05 | 98.92
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 726 | 34848 | 0.0063091 | 0.00013144 | 48
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 5 | 3575 | 0.00064724 | 9.0523e-07 | 715
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 147 | 2.6614e-05 | 1.8105e-07 | 147
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 859 | 38770 | 0.0070192 | 0.00015552 | 45.1339
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 944 | 8343 | 2102349 | 0.38335 | 0.0015213 | 251.9896
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 793 | 34947 | 6245398 | 1.1388 | 0.0063723 | 178.7106
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR UG | 225 | 448 | 182970 | 0.033363 | 8.1689e-05 | 408.4152
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE | 161 | 14371 | 5524103 | 1.0073 | 0.0026204 | 384.3924
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONN/CLAMP | 418 | 1066 | 180689 | 0.032947 | 0.00019438 | 169.5019
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 142 | 341 | 54989 | 0.010027 | 6.2179e-05 | 161.2581
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 29 | 854 | 250275 | 0.045636 | 0.00015572 | 293.0621
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 5 | 845 | 170980 | 0.031177 | 0.00015408 | 202.3432
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | NONE | 52 | 107 | 13487 | 0.0024592 | 1.9511e-05 | 126.0467
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, OH | 20 | 53 | 27335 | 0.0049843 | 9.6641e-06 | 515.7547
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | FUSE | 66 | 185 | 47653 | 0.0086891 | 3.3733e-05 | 257.5838
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 48 | 120 | 27195 | 0.0049588 | 2.1881e-05 | 226.625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 9 | 603 | 0.00010995 | 1.6411e-06 | 67
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WU | NONE | 6 | 2252 | 221241 | 0.040342 | 0.00041063 | 98.242
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 5 | 25 | 18004 | 0.0032829 | 4.5586e-06 | 720.16
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | ARRESTER | 11 | 8291 | 1176232 | 0.21448 | 0.0015118 | 141.8685
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 386 | 7.0384e-05 | 3.6468e-07 | 193
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CROSSARM | 3 | 234 | 11733 | 0.0021394 | 4.2668e-05 | 50.141
AEP Total | 2020 | 5484199 | PARTIAL POWER | UG | CONDUCTOR UG | 5 | 5 | 1987 | 0.00036231 | 9.1171e-07 | 397.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | ARRESTER | 4 | 14 | 1783 | 0.00032512 | 2.5528e-06 | 127.3571
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 1218 | 0.00022209 | 1.8234e-07 | 1218
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | BREAKER | 6 | 2972 | 1266766 | 0.23098 | 0.00054192 | 426.2335
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 21 | 1995 | 0.00036377 | 3.8292e-06 | 95
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | OTHER EQUIPMENT | 1 | 11 | 627 | 0.00011433 | 2.0058e-06 | 57
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | POLE | 3 | 215 | 62035 | 0.011312 | 3.9204e-05 | 288.5349
AEP Total | 2023 | 5575683 | PARTIAL POWER | UG | NONE | 2 | 2 | 289 | 5.1832e-05 | 3.587e-07 | 144.5
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 1556 | 39891 | 0.0071545 | 0.00027907 | 25.6369
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | POLE | 5 | 124 | 29942 | 0.0053917 | 2.2329e-05 | 241.4677
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CUTOUT | 4 | 28 | 6822 | 0.0012285 | 5.042e-06 | 243.6429
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 20 | 13808 | 3665500 | 0.65741 | 0.0024765 | 265.4621
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 7 | 36 | 10975 | 0.0019684 | 6.4566e-06 | 304.8611
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 30 | 17277 | 0.0030986 | 5.3805e-06 | 575.9
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 10 | 3140 | 1254283 | 0.22496 | 0.00056316 | 399.4532
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1428 | 45901 | 6495455 | 1.1567 | 0.008174 | 141.5101
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 148 | 3935 | 2292614 | 0.40827 | 0.00070074 | 582.6211
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 2821 | 182833 | 42877623 | 7.6356 | 0.032559 | 234.518
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 157 | 12448 | 2263653 | 0.40311 | 0.0022167 | 181.8487
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | NONE | 49 | 568 | 55358 | 0.0098581 | 0.00010115 | 97.4613
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | METERING | 15 | 45 | 12709 | 0.0023174 | 8.2054e-06 | 282.4222
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 29 | 1923 | 853166 | 0.15557 | 0.00035064 | 443.6641
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CUTOUT | 12 | 1659 | 465828 | 0.08494 | 0.00030251 | 280.7884
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | ARRESTER | 7 | 197 | 178907 | 0.032622 | 3.5921e-05 | 908.1574
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 4 | 1180 | 289685 | 0.052822 | 0.00021516 | 245.4958
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 14 | 1568 | 0.00028591 | 2.5528e-06 | 112
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 4 | 63 | 9354 | 0.0017056 | 1.1488e-05 | 148.4762
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CUTOUT | 8 | 157 | 71909 | 0.013112 | 2.8628e-05 | 458.0191
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | TRANSFORMER, OH | 1 | 13 | 3783 | 0.00067848 | 2.3316e-06 | 291
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | NONE | 6 | 9 | 2279 | 0.00040874 | 1.6142e-06 | 253.2222
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | ARRESTER | 3 | 1758 | 462086 | 0.082875 | 0.0003153 | 262.8476
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 7 | 6552 | 0.0011751 | 1.2555e-06 | 936
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 8 | 150 | 22061 | 0.0039566 | 2.6903e-05 | 147.0733
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 9 | 1109 | 0.0001997 | 1.6206e-06 | 123.2222
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 11 | 30 | 878 | 0.0001581 | 5.4022e-06 | 29.2667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 857 | 8265 | 1274302 | 0.22855 | 0.0014823 | 154.1805
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 5 | 231 | 97451 | 0.017478 | 4.143e-05 | 421.8658
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | NONE | 1907 | 35981 | 5033317 | 0.90273 | 0.0064532 | 139.8882
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 45 | 432 | 54465 | 0.0098076 | 7.7791e-05 | 126.0764
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | NONE | 871 | 4581 | 800700 | 0.14361 | 0.0008216 | 174.7872
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 2 | 1305 | 1502182 | 0.2705 | 0.00023499 | 1151.0973
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | NONE | 52 | 1978 | 229314 | 0.041128 | 0.00035475 | 115.9323
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | ARRESTER | 1 | 21 | 31788 | 0.0057241 | 3.7815e-06 | 1513.7143
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | BREAKER | 3 | 4036 | 1080790 | 0.19462 | 0.00072677 | 267.7874
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | ARRESTER | 15 | 713 | 166888 | 0.029931 | 0.00012788 | 234.0645
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | NONE | 1 | 5 | 2590 | 0.00046639 | 9.0036e-07 | 518
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | NONE | 7 | 122 | 16495 | 0.0029584 | 2.1881e-05 | 135.2049
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 28 | 419 | 45450 | 0.0081515 | 7.5148e-05 | 108.4726
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CUTOUT | 7 | 277 | 188124 | 0.033876 | 4.988e-05 | 679.148
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | NONE | 26 | 66 | 7952 | 0.0014262 | 1.1837e-05 | 120.4848
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | METERING | 1 | 5 | 1420 | 0.0002557 | 9.0036e-07 | 284
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 3 | 312 | 5.6182e-05 | 5.4022e-07 | 104
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | JUMPER/RISER | 4 | 15 | 6753 | 0.0012112 | 2.6903e-06 | 450.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 5 | 6925 | 0.001247 | 9.0036e-07 | 1385
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WH | FUSE | 1 | 3 | 1605 | 0.00028902 | 5.4022e-07 | 535
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 1 | 582 | 0.00010438 | 1.7935e-07 | 582
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE HARDWARE | 4 | 620 | 162194 | 0.02909 | 0.0001112 | 261.6032
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 424 | 4885 | 710783 | 0.12799 | 0.00087965 | 145.5032
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | FUSE | 213 | 2490 | 823765 | 0.14834 | 0.00044838 | 330.8293
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | NONE | 3393 | 98463 | 13816561 | 2.488 | 0.01773 | 140.3224
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | FUSE | 1204 | 12747 | 1933846 | 0.34823 | 0.0022954 | 151.7099
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1224 | 52940 | 10553657 | 1.9004 | 0.009533 | 199.3513
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 56 | 1514 | 873115 | 0.15722 | 0.00027263 | 576.6942
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | NONE | 202 | 25860 | 8042964 | 1.4483 | 0.0046567 | 311.0195
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | NONE | 1073 | 11377 | 2328218 | 0.41925 | 0.0020487 | 204.6425
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CUTOUT | 58 | 1575 | 667606 | 0.12022 | 0.00028361 | 423.8768
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CROSSARM | 41 | 3369 | 528790 | 0.09522 | 0.00060666 | 156.9576
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | INSULATOR | 6 | 504 | 45530 | 0.0081987 | 9.0756e-05 | 90.3373
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CUTOUT | 18 | 34 | 6797 | 0.0012239 | 6.1224e-06 | 199.9118
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 61 | 15737 | 0.0028338 | 1.0984e-05 | 257.9836
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | METERING | 2 | 5 | 228 | 4.1056e-05 | 9.0036e-07 | 45.6
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | R | NONE | 3 | 4003 | 656492 | 0.11822 | 0.00072083 | 164
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 54 | 790 | 298628 | 0.053775 | 0.00014226 | 378.0101
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | FUSE | 78 | 418 | 55925 | 0.010071 | 7.527e-05 | 133.7919
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | NONE | 2 | 7 | 557 | 0.0001003 | 1.2605e-06 | 79.5714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | BREAKER | 3 | 486 | 130623 | 0.023522 | 8.7515e-05 | 268.7716
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | INSULATOR | 2 | 120 | 30965 | 0.0055759 | 2.1609e-05 | 258.0417
AEP Total | 2022 | 5553337 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 202 | 3.6375e-05 | 1.8007e-07 | 202
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 27 | 102 | 4725 | 0.00084743 | 1.8294e-05 | 46.3235
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 6 | 1278 | 0.00022921 | 1.0761e-06 | 213
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE | 561 | 41744 | 20874194 | 3.7438 | 0.0074868 | 500.0526
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | WU | NONE | 3 | 60 | 6000 | 0.0010804 | 1.0804e-05 | 100
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 83 | 6815 | 3418806 | 0.61316 | 0.0012223 | 501.659
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CROSSARM | 6 | 832 | 102764 | 0.018505 | 0.00014982 | 123.5144
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 22 | 14059 | 0.0025316 | 3.9616e-06 | 639.0455
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | POLE | 3 | 2304 | 397950 | 0.071372 | 0.00041322 | 172.7214
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 6 | 118 | 29685 | 0.005324 | 2.1163e-05 | 251.5678
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | NONE | 4 | 16 | 2442 | 0.00043797 | 2.8696e-06 | 152.625
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 55 | 2179 | 470248 | 0.084339 | 0.0003908 | 215.8091
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONN/CLAMP | 40 | 146 | 36669 | 0.0066863 | 2.6622e-05 | 251.1575
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | U | NONE | 27 | 16292 | 1561774 | 0.28478 | 0.0029707 | 95.8614
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 6 | 476 | 147583 | 0.026911 | 8.6795e-05 | 310.0483
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | NONE | 84 | 1673 | 303368 | 0.055317 | 0.00030506 | 181.3317
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, OH | 18 | 23 | 4198 | 0.00076547 | 4.1939e-06 | 182.5217
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE | 4 | 1167 | 202094 | 0.03685 | 0.00021279 | 173.174
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | NONE | 47 | 1075 | 227694 | 0.041518 | 0.00019602 | 211.8084
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CUTOUT | 16 | 87 | 7740 | 0.0014113 | 1.5864e-05 | 88.9655
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | FUSE | 271 | 2035 | 349468 | 0.06327 | 0.00036843 | 171.7287
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE | 232 | 55738 | 14346519 | 2.5974 | 0.010091 | 257.3921
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | NONE | 92 | 1398 | 562736 | 0.10188 | 0.0002531 | 402.5293
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | NONE | 15 | 66 | 10316 | 0.0018677 | 1.1949e-05 | 156.303
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE | 4 | 41 | 9686 | 0.0017536 | 7.4229e-06 | 236.2439
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | NONE | 66 | 4518 | 132038 | 0.023905 | 0.00081797 | 29.2249
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 36 | 22325 | 0.0040419 | 6.5177e-06 | 620.1389
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 3 | 5 | 3213 | 0.0005817 | 9.0523e-07 | 642.6
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | BREAKER | 5 | 66 | 29331 | 0.0053103 | 1.1949e-05 | 444.4091
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CROSSARM | 4 | 2114 | 595846 | 0.10788 | 0.00038273 | 281.8571
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 16 | 3493 | 0.00063239 | 2.8967e-06 | 218.3125
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | NONE | 5 | 23 | 6560 | 0.0011877 | 4.1641e-06 | 285.2174
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | POLE | 2 | 93 | 28671 | 0.0051908 | 1.6837e-05 | 308.2903
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | CONDUCTOR UG | 4 | 5 | 1134 | 0.00020531 | 9.0523e-07 | 226.8
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | ARRESTER | 2 | 39 | 510 | 9.2334e-05 | 7.0608e-06 | 13.0769
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | NONE | 14 | 40 | 5735 | 0.0010383 | 7.2419e-06 | 143.375
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | FUSE | 5 | 15 | 1072 | 0.00019408 | 2.7157e-06 | 71.4667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 1 | 3 | 90 | 1.6294e-05 | 5.4314e-07 | 30
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | POLE | 1384 | 25540 | 5383738 | 0.96946 | 0.004599 | 210.7963
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | ARRESTER | 1 | 1000 | 293736 | 0.052894 | 0.00018007 | 293.736
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | O | NONE | 12 | 7112 | 1077995 | 0.19334 | 0.0012755 | 151.5741
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | U | NONE | 2 | 2107 | 143276 | 0.025697 | 0.00037789 | 68
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | POLE | 1 | 36 | 5472 | 0.00098535 | 6.4826e-06 | 152
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 10 | 100 | 1.7935e-05 | 1.7935e-06 | 10
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | METERING | 2 | 11 | 510 | 9.0821e-05 | 1.9589e-06 | 46.3636
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | POLE HARDWARE | 3 | 2373 | 238452 | 0.042463 | 0.00042258 | 100.4855
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | FW | NONE | 2 | 336 | 15981 | 0.0028459 | 5.9835e-05 | 47.5625
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | F | NONE | 4 | 488 | 10697 | 0.0019049 | 8.6903e-05 | 21.9201
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | R | NONE | 3 | 2547 | 65205 | 0.011695 | 0.00045681 | 25.6007
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | FUSE | 1 | 28 | 1792 | 0.0003214 | 5.0218e-06 | 64
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 4 | 1200 | 0.00021522 | 7.174e-07 | 300
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 1 | 104 | 1.8652e-05 | 1.7935e-07 | 104
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONN/CLAMP | 1 | 1 | 259 | 4.7227e-05 | 1.8234e-07 | 259
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | OTHER EQUIPMENT | 1 | 3 | 435 | 7.7465e-05 | 5.3424e-07 | 145
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | ARRESTER | 1 | 1 | 1885 | 0.00033568 | 1.7808e-07 | 1885
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | NONE | 1796 | 56447 | 12976479 | 2.3493 | 0.01022 | 229.8878
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | POLE | 321 | 14713 | 2160567 | 0.39116 | 0.0026637 | 146.8475
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 84 | 2515 | 422713 | 0.076531 | 0.00045533 | 168.0767
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | ARRESTER | 31 | 2587 | 735524 | 0.13316 | 0.00046837 | 284.3154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 90 | 1333 | 174672 | 0.031624 | 0.00024133 | 131.0368
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 27 | 382 | 60091 | 0.010879 | 6.916e-05 | 157.3063
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | NONE | 43 | 1211 | 182783 | 0.033092 | 0.00021925 | 150.9356
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 11 | 63 | 19809 | 0.0035863 | 1.1406e-05 | 314.4286
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, OH | 9 | 22 | 16214 | 0.0029355 | 3.983e-06 | 737
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | FUSE | 19 | 47 | 6103 | 0.0011049 | 8.5092e-06 | 129.8511
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR UG | 5 | 25 | 13915 | 0.0025193 | 4.5262e-06 | 556.6
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | WI | NONE | 1 | 953 | 81958 | 0.014838 | 0.00017254 | 86
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | NONE | 1 | 65 | 205393 | 0.037186 | 1.1768e-05 | 3159.8923
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONN/CLAMP | 1 | 8 | 392 | 7.097e-05 | 1.4484e-06 | 49
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | POLE | 16 | 1185 | 1054649 | 0.19094 | 0.00021454 | 889.9992
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 3 | 1706 | 53538 | 0.0096929 | 0.00030887 | 31.3822
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 73 | 13613 | 0.0024646 | 1.3216e-05 | 186.4795
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 224 | 4.0554e-05 | 1.8105e-07 | 224
AEP Total | 2021 | 5523447 | PARTIAL POWER | F | CONDUCTOR OVERHEAD | 1 | 3 | 228 | 4.1279e-05 | 5.4314e-07 | 76
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 18 | 216 | 3.9106e-05 | 3.2588e-06 | 12
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | METERING | 1 | 1 | 20 | 3.6209e-06 | 1.8105e-07 | 20
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 3 | 972 | 0.00017598 | 5.4314e-07 | 324
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, OH | 56 | 782 | 152146 | 0.027743 | 0.00014259 | 194.5601
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | NONE | 37 | 3070 | 382273 | 0.069704 | 0.00055979 | 124.5189
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 71 | 10295 | 1417924 | 0.25855 | 0.0018772 | 137.7294
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WH | NONE | 1 | 2 | 80 | 1.4484e-05 | 3.6209e-07 | 40
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 3 | 27 | 4.8619e-06 | 5.4022e-07 | 9
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | METERING | 3 | 20 | 5441 | 0.00097977 | 3.6014e-06 | 272.05
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WL | NONE | 6 | 6589 | 496148 | 0.089342 | 0.0011865 | 75.2994
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | F | POLE | 4 | 1819 | 573835 | 0.10219 | 0.00032393 | 315.4673
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 490 | 136102 | 0.024237 | 8.7259e-05 | 277.7592
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 0 | 0 | 0 | 0
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 11 | 737 | 0.00013124 | 1.9589e-06 | 67
AEP Total | 2025 | 5615460 | SUBTRANSMISSION LINE | WU | POLE | 1 | 90 | 66600 | 0.01186 | 1.6027e-05 | 740
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 293 | 9083 | 0.0016175 | 5.2177e-05 | 31
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 164 | 42232 | 0.0075207 | 2.9205e-05 | 257.5122
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 1 | 294 | 5.2355e-05 | 1.7808e-07 | 294
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WFS | NONE | 6 | 2904 | 2315470 | 0.41695 | 0.00052293 | 797.3382
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 3 | 10 | 6669 | 0.001216 | 1.8234e-06 | 666.9
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WFS | NONE | 2 | 433 | 223288 | 0.040208 | 7.7971e-05 | 515.6767
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 18 | 255 | 82275 | 0.014652 | 4.541e-05 | 322.6471
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CROSSARM | 2 | 100 | 25721 | 0.0046316 | 1.8007e-05 | 257.21
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | INSULATOR | 3 | 1927 | 371770 | 0.066945 | 0.000347 | 192.9268
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | FUSE | 16 | 36 | 3038 | 0.00054101 | 6.4109e-06 | 84.3889
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 3 | 98 | 33739 | 0.0060082 | 1.7452e-05 | 344.2755
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 58 | 66364 | 0.011818 | 1.0329e-05 | 1144.2069
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 13 | 2206 | 0.00039284 | 2.315e-06 | 169.6923
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | POLE | 2 | 161 | 8458 | 0.0015062 | 2.8671e-05 | 52.5342
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | NONE | 8 | 35 | 10237 | 0.001823 | 6.2328e-06 | 292.4857
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 31 | 5.5205e-06 | 1.7808e-07 | 31
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | CUTOUT | 1 | 200 | 4800 | 0.00086902 | 3.6209e-05 | 24
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 189 | 3.3657e-05 | 1.7808e-07 | 189
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 6 | 131 | 38650 | 0.0068828 | 2.3328e-05 | 295.0382
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | PEDESTAL | 4 | 50 | 1972 | 0.00035117 | 8.904e-06 | 39.44
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 14 | 6776 | 0.0012153 | 2.5109e-06 | 484
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | POLE | 4 | 334 | 68066 | 0.012121 | 5.9479e-05 | 203.7904
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 2 | 256 | 203512 | 0.036241 | 4.5588e-05 | 794.9688
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 8 | 341 | 48180 | 0.0085799 | 6.0725e-05 | 141.2903
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TOR | CROSSARM | 2 | 385 | 47740 | 0.0085015 | 6.8561e-05 | 124
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 2 | 36 | 55304 | 0.0098485 | 6.4109e-06 | 1536.2222
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 2 | 5 | 443 | 7.8889e-05 | 8.904e-07 | 88.6
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | EQF | GUY/ANCHOR | 1 | 3 | 186 | 3.3123e-05 | 5.3424e-07 | 62
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | VA | POLE | 3 | 912 | 273908 | 0.048777 | 0.00016241 | 300.3377
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 220 | 159720 | 0.028761 | 3.9616e-05 | 726
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | ERF | POLE HARDWARE | 2 | 827 | 19021 | 0.0034251 | 0.00014892 | 23
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | A | NONE | 5 | 3564 | 469574 | 0.084557 | 0.00064178 | 131.7548
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 95 | 43700 | 0.0078691 | 1.7107e-05 | 460
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | ARRESTER | 4 | 4290 | 359494 | 0.064019 | 0.00076396 | 83.7981
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | NONE | 2 | 374 | 143658 | 0.026195 | 6.8196e-05 | 384.1123
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | POLE | 1 | 8 | 2848 | 0.00051284 | 1.4406e-06 | 356
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | ARRESTER | 1 | 1 | 147 | 2.6178e-05 | 1.7808e-07 | 147
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 21 | 126 | 2.2438e-05 | 3.7397e-06 | 6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 13 | 10244 | 0.0018242 | 2.315e-06 | 788
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 1127 | 1166548 | 0.20774 | 0.0002007 | 1035.0914
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 2 | 1885 | 151707 | 0.027016 | 0.00033568 | 80.4812
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | PEDESTAL | 1 | 5 | 225 | 4.0068e-05 | 8.904e-07 | 45
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 178 | 18294 | 0.0032578 | 3.1698e-05 | 102.7753
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 1 | 116 | 2.0657e-05 | 1.7808e-07 | 116
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 2 | 322 | 5.8714e-05 | 3.6468e-07 | 161
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 156 | 2.7979e-05 | 3.587e-07 | 78
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | O | NONE | 1 | 2348 | 147924 | 0.026973 | 0.00042814 | 63
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | ARRESTER | 1 | 10 | 2060 | 0.00036946 | 1.7935e-06 | 206
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | EQF | ARRESTER | 2 | 774 | 273219 | 0.049819 | 0.00014113 | 352.9961
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 1260 | 85225 | 0.01554 | 0.00022975 | 67.6389
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 2 | 256 | 4.6098e-05 | 3.6014e-07 | 128
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | INSULATOR | 1 | 274 | 54800 | 0.0098284 | 4.9142e-05 | 200
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 555 | 9.9539e-05 | 1.7935e-07 | 555
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 1 | 0 | 0 | 0 | 0
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 2 | 270 | 4.8082e-05 | 3.5616e-07 | 135
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 1 | 1 | 60 | 1.0685e-05 | 1.7808e-07 | 60
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | POLE | 1 | 1 | 3188 | 0.00056772 | 1.7808e-07 | 3188
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1137 | 35696 | 5833448 | 1.0561 | 0.0064626 | 163.4202
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | NONE | 808 | 10524 | 1232926 | 0.22322 | 0.0019053 | 117.1537
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CROSSARM | 3 | 854 | 206867 | 0.036839 | 0.00015208 | 242.233
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | NONE | 7 | 36 | 3054 | 0.00054774 | 6.4566e-06 | 84.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 73 | 1.3093e-05 | 1.7935e-07 | 73
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | FUSE | 2 | 7 | 374 | 6.7077e-05 | 1.2555e-06 | 53.4286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 5 | 35 | 7984 | 0.0014377 | 6.3025e-06 | 228.1143
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 3 | 6 | 2213 | 0.0003985 | 1.0804e-06 | 368.8333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 58 | 56363 | 0.010149 | 1.0444e-05 | 971.7759
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 522 | 38958 | 0.0070152 | 9.3998e-05 | 74.6322
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 822 | 799692 | 0.14342 | 0.00014743 | 972.8613
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | ARRESTER | 9 | 16 | 2277 | 0.00041002 | 2.8812e-06 | 142.3125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 998 | 43364 | 11403263 | 2.0307 | 0.0077223 | 262.9661
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 447 | 3925 | 930254 | 0.16566 | 0.00069896 | 237.0074
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 151 | 3375 | 753280 | 0.13414 | 0.00060102 | 223.1941
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | CUTOUT | 1 | 51 | 2754 | 0.00049393 | 9.1469e-06 | 54
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 24 | 4398 | 614621 | 0.10945 | 0.00078319 | 139.7501
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 23 | 266 | 93110 | 0.016581 | 4.7369e-05 | 350.0376
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 3 | 297 | 131803 | 0.023639 | 5.3267e-05 | 443.7811
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 1 | 24 | 4.3044e-06 | 1.7935e-07 | 24
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 1 | 20 | 1040 | 0.00018652 | 3.587e-06 | 52
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 6 | 378 | 50269 | 0.0089519 | 6.7314e-05 | 132.9868
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 57 | 603 | 55443 | 0.0098733 | 0.00010738 | 91.9453
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 22 | 12870 | 0.0023082 | 3.9457e-06 | 585
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 25 | 21500 | 0.0038715 | 4.5018e-06 | 860
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 37 | 8177 | 0.0014804 | 6.6987e-06 | 221
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | POLE | 9 | 222 | 59390 | 0.010576 | 3.9534e-05 | 267.5225
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | NONE | 21 | 692 | 333542 | 0.059397 | 0.00012323 | 481.9971
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 40 | 812 | 172532 | 0.030724 | 0.0001446 | 212.4778
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 36 | 939 | 145815 | 0.025967 | 0.00016722 | 155.2875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 2 | 1442 | 0.00025862 | 3.587e-07 | 721
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | PEDESTAL | 1 | 1 | 138 | 2.5163e-05 | 1.8234e-07 | 138
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 5 | 8 | 6443 | 0.0011748 | 1.4587e-06 | 805.375
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 2 | 7 | 4685 | 0.00085427 | 1.2764e-06 | 669.2857
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 27 | 4.9232e-06 | 1.8234e-07 | 27
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 195 | 60567 | 0.011044 | 3.5557e-05 | 310.6
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 98 | 1.787e-05 | 1.8234e-07 | 98
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | ARRESTER | 1 | 3 | 432 | 7.8772e-05 | 5.4703e-07 | 144
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | INSULATOR | 4 | 298 | 23476 | 0.0042807 | 5.4338e-05 | 78.7785
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 358 | 175774 | 0.032051 | 6.5278e-05 | 490.9888
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | CROSSARM | 1 | 456 | 212952 | 0.03883 | 8.3148e-05 | 467
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | FUSE | 1 | 464 | 120176 | 0.021913 | 8.4607e-05 | 259
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 1 | 210 | 3.8292e-05 | 1.8234e-07 | 210
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 107 | 14507 | 0.0026452 | 1.9511e-05 | 135.5794
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 3 | 3921 | 373446 | 0.068095 | 0.00071496 | 95.2425
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 4 | 178 | 98238 | 0.017494 | 3.1698e-05 | 551.8989
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE | 5 | 47 | 49770 | 0.0090752 | 8.5701e-06 | 1058.9362
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONN/CLAMP | 1 | 5 | 75 | 1.3676e-05 | 9.1171e-07 | 15
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 11 | 2453 | 0.00044411 | 1.9915e-06 | 223
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 185 | 66230 | 0.011991 | 3.3494e-05 | 358
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 1 | 12 | 2196 | 0.00040042 | 2.1881e-06 | 183
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | NONE | 7 | 6558 | 563775 | 0.10152 | 0.0011809 | 85.9675
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 2 | 424 | 7.635e-05 | 3.6014e-07 | 212
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 580 | 0.00010444 | 1.8007e-07 | 580
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CROSSARM | 1 | 496 | 238080 | 0.043412 | 9.0442e-05 | 480
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 48 | 2928 | 0.00052725 | 8.6435e-06 | 61
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | INSULATOR | 1 | 254 | 33782 | 0.0060159 | 4.5232e-05 | 133
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | WU | NONE | 5 | 1856 | 299988 | 0.053422 | 0.00033052 | 161.6315
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | FUSE | 2 | 8 | 6204 | 0.0011048 | 1.4246e-06 | 775.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | SCO | JUMPER/RISER | 1 | 1 | 218 | 3.8821e-05 | 1.7808e-07 | 218
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | BE | NONE | 1 | 1 | 52 | 9.2601e-06 | 1.7808e-07 | 52
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 2 | 19 | 868 | 0.00015457 | 3.3835e-06 | 45.6842
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1 | 270 | 4.8619e-05 | 1.8007e-07 | 270
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | CROSSARM | 2 | 41 | 5224 | 0.00093029 | 7.3013e-06 | 127.4146
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 8 | 1964 | 0.00034975 | 1.4246e-06 | 245.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE | 4 | 1367 | 616017 | 0.1097 | 0.00024344 | 450.6342
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 5 | 2130 | 210490 | 0.037903 | 0.00038355 | 98.8216
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CROSSARM | 15 | 4561 | 477466 | 0.085634 | 0.00081802 | 104.6845
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | METERING | 25 | 26 | 5168 | 0.00092688 | 4.6631e-06 | 198.7692
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | REGULATOR | 2 | 240 | 50655 | 0.0091215 | 4.3217e-05 | 211.0625
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 19 | 2831 | 0.00050774 | 3.4077e-06 | 149
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | BE | CUTOUT | 1 | 11 | 3377 | 0.0006081 | 1.9808e-06 | 307
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | OTHER EQUIPMENT | 3 | 3432 | 372374 | 0.067054 | 0.00061801 | 108.5006
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 8 | 168 | 66961 | 0.012058 | 3.0252e-05 | 398.5774
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 217 | 3.8919e-05 | 1.7935e-07 | 217
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 4 | 280 | 45349 | 0.0081334 | 5.0218e-05 | 161.9607
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 15 | 547 | 443784 | 0.079593 | 9.8105e-05 | 811.3053
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 48 | 2694 | 0.00048317 | 8.6088e-06 | 56.125
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 611 | 43992 | 0.00789 | 0.00010958 | 72
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 140 | 23520 | 0.0042183 | 2.5109e-05 | 168
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CROSSARM | 5 | 1997 | 506829 | 0.0909 | 0.00035816 | 253.7952
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | ARRESTER | 3 | 773 | 140586 | 0.025635 | 0.00014095 | 181.8706
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 15 | 15465 | 0.0028199 | 2.7351e-06 | 1031
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | INSULATOR | 2 | 2 | 231 | 4.2121e-05 | 3.6468e-07 | 115.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 4 | 33 | 13960 | 0.0025455 | 6.0173e-06 | 423.0303
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 19 | 20634 | 0.0037624 | 3.4645e-06 | 1086
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CUTOUT | 16 | 111 | 44185 | 0.0079246 | 1.9908e-05 | 398.0631
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | NONE | 2674 | 77419 | 9545189 | 1.6998 | 0.013787 | 123.2926
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 16 | 244 | 33838 | 0.0060689 | 4.3761e-05 | 138.6803
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 71 | 3190 | 428020 | 0.076222 | 0.00056807 | 134.1755
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 2 | 533 | 9.5978e-05 | 3.6014e-07 | 266.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | FUSE | 3 | 13 | 8547 | 0.0015474 | 2.3536e-06 | 657.4615
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 7 | 1185 | 0.00021608 | 1.2764e-06 | 169.2857
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 4 | 1592 | 97321 | 0.017746 | 0.00029029 | 61.1313
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 79 | 24648 | 0.0044944 | 1.4405e-05 | 312
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 16 | 1074 | 176716 | 0.032223 | 0.00019584 | 164.54
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 9 | 1581 | 370987 | 0.067647 | 0.00028828 | 234.6534
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | NONE | 3 | 23 | 13198 | 0.0024066 | 4.1939e-06 | 573.8261
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | FUSE | 2 | 10 | 865 | 0.00015773 | 1.8234e-06 | 86.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | METERING | 1 | 4 | 460 | 8.3877e-05 | 7.2937e-07 | 115
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | SCO | POLE | 1 | 245 | 220500 | 0.039547 | 4.3941e-05 | 900
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | ARRESTER | 2 | 2 | 150 | 2.6712e-05 | 3.5616e-07 | 75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 974 | 56987 | 13979646 | 2.4895 | 0.010148 | 245.3129
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 441 | 3862 | 526947 | 0.093839 | 0.00068774 | 136.4441
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 249 | 22937 | 8527152 | 1.5185 | 0.0040846 | 371.764
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | NONE | 25 | 3721 | 849678 | 0.15131 | 0.00066263 | 228.3467
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 15 | 61 | 15363 | 0.0027358 | 1.0863e-05 | 251.8525
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CROSSARM | 11 | 657 | 46939 | 0.0083589 | 0.000117 | 71.4444
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | POLE | 36 | 2928 | 879958 | 0.1567 | 0.00052142 | 300.5321
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 37 | 15430 | 0.0027785 | 6.6627e-06 | 417.027
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 7 | 734 | 0.00013071 | 1.2466e-06 | 104.8571
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | POLE | 2 | 6 | 3680 | 0.00065533 | 1.0685e-06 | 613.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 6 | 106 | 47207 | 0.0084066 | 1.8876e-05 | 445.3491
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | INSULATOR | 5 | 2015 | 183826 | 0.032736 | 0.00035883 | 91.2288
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | FUSE | 15 | 179 | 95729 | 0.017047 | 3.1876e-05 | 534.7989
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CUTOUT | 6 | 135 | 14922 | 0.0026573 | 2.4041e-05 | 110.5333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 47 | 6165 | 0.0010979 | 8.3698e-06 | 131.1702
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | NONE | 8 | 97 | 59229 | 0.010547 | 1.7274e-05 | 610.6082
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 12 | 3497 | 0.00062275 | 2.137e-06 | 291.4167
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 11 | 54 | 42679 | 0.0076003 | 9.6163e-06 | 790.3519
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 1 | 596 | 333965 | 0.059472 | 0.00010614 | 560.344
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | TIN | NONE | 4 | 1949 | 142585 | 0.025392 | 0.00034708 | 73.158
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 1 | 14 | 3318 | 0.00059087 | 2.4931e-06 | 237
AEP Total | 2025 | 5615460 | PARTIAL POWER | WI | CONN/CLAMP | 1 | 2 | 2312 | 0.00041172 | 3.5616e-07 | 1156
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 509 | 302692 | 0.053903 | 9.0643e-05 | 594.6798
AEP Total | 2025 | 5615460 | PARTIAL POWER | WI | NONE | 2 | 6 | 7323 | 0.0013041 | 1.0685e-06 | 1220.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 29 | 12304 | 0.0021911 | 5.1643e-06 | 424.2759
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | NONE | 3 | 609 | 129572 | 0.023074 | 0.00010845 | 212.7619
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | R | NONE | 18 | 14091 | 2557198 | 0.45539 | 0.0025093 | 181.4774
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | FUSE | 3 | 18 | 2495 | 0.00044431 | 3.2054e-06 | 138.6111
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 2 | 4 | 700 | 0.00012555 | 7.174e-07 | 175
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CROSSARM | 7 | 1533 | 571709 | 0.10295 | 0.00027605 | 372.9348
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | ARRESTER | 1 | 2 | 554 | 9.976e-05 | 3.6014e-07 | 277
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | NONE | 2 | 2 | 1046 | 0.0001876 | 3.587e-07 | 523
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | SPLICE, OH | 2 | 7 | 509 | 9.1289e-05 | 1.2555e-06 | 72.7143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 2818 | 102071 | 16264604 | 2.8964 | 0.018177 | 159.346
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 6490 | 323783 | 102420422 | 18.239 | 0.057659 | 316.3243
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE | 491 | 101772 | 21199178 | 3.7751 | 0.018124 | 208.3007
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 100 | 888 | 105234 | 0.01874 | 0.00015813 | 118.5068
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | FUSE | 4 | 78 | 16389 | 0.0029394 | 1.3989e-05 | 210.1154
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 6 | 59 | 43491 | 0.0078001 | 1.0582e-05 | 737.1356
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 34 | 1349 | 240908 | 0.042901 | 0.00024023 | 178.5827
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 3 | 10 | 3933 | 0.00070039 | 1.7808e-06 | 393.3
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | CONN/CLAMP | 3 | 14 | 312 | 5.5957e-05 | 2.5109e-06 | 22.2857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 1143 | 138057 | 0.024761 | 0.000205 | 120.7848
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 13 | 287 | 9918 | 0.0017662 | 5.1109e-05 | 34.5575
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 18 | 1351 | 349619 | 0.06226 | 0.00024059 | 258.7853
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 3 | 727 | 379262 | 0.067539 | 0.00012946 | 521.6809
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 32 | 11697 | 0.0020979 | 5.7392e-06 | 365.5312
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CAPACITOR | 5 | 4845 | 411279 | 0.073763 | 0.00086895 | 84.8873
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, OH | 15 | 763 | 178039 | 0.031705 | 0.00013587 | 233.3408
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 5 | 31 | 12226 | 0.0022135 | 5.6124e-06 | 394.3871
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, OH | 20 | 8998 | 1523979 | 0.27591 | 0.0016291 | 169.3686
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | NONE | 81 | 1618 | 258186 | 0.046744 | 0.00029293 | 159.5711
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 28 | 46 | 23916 | 0.0043299 | 8.3281e-06 | 519.913
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE | 6 | 330 | 296733 | 0.053722 | 5.9745e-05 | 899.1909
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 14 | 483 | 312523 | 0.056581 | 8.7445e-05 | 647.0455
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | INSULATOR | 18 | 1305 | 356773 | 0.064592 | 0.00023627 | 273.3893
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 21 | 29655 | 0.0053689 | 3.802e-06 | 1412.1429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 15 | 9060 | 0.0016403 | 2.7157e-06 | 604
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | FUSE | 5 | 28 | 4403 | 0.00079715 | 5.0693e-06 | 157.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 75 | 11025 | 0.001996 | 1.3578e-05 | 147
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | STATIC WIRE | 8 | 8648 | 409473 | 0.074134 | 0.0015657 | 47.3489
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | NONE | 6802 | 339167 | 118893494 | 21.4094 | 0.061074 | 350.5456
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 35 | 919 | 234826 | 0.042286 | 0.00016549 | 255.5234
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE | 326 | 29417 | 8905782 | 1.6037 | 0.0052972 | 302.7427
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | NONE | 6 | 7 | 775 | 0.00014031 | 1.2673e-06 | 110.7143
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 4 | 10 | 19849 | 0.0035936 | 1.8105e-06 | 1984.9
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | FUSE | 1 | 1 | 1564 | 0.00028316 | 1.8105e-07 | 1564
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 9 | 1485 | 0.00026885 | 1.6294e-06 | 165
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | OV | NONE | 1 | 993 | 84405 | 0.015281 | 0.00017978 | 85
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 43 | 1464 | 438561 | 0.079968 | 0.00026695 | 299.5635
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | NONE | 190 | 11433 | 2429476 | 0.443 | 0.0020847 | 212.4968
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ERF | NONE | 2 | 1994 | 33898 | 0.006181 | 0.00036359 | 17
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | NONE | 37 | 629 | 81660 | 0.01489 | 0.00011469 | 129.8251
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 43 | 13676 | 2348065 | 0.42282 | 0.0024627 | 171.6924
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 21 | 254 | 51010 | 0.0091855 | 4.5738e-05 | 200.8268
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | POLE | 6 | 47 | 7082 | 0.0012753 | 8.4634e-06 | 150.6809
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 16 | 3339 | 218360 | 0.039321 | 0.00060126 | 65.3968
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 8 | 94 | 27820 | 0.0050096 | 1.6927e-05 | 295.9574
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 4 | 9 | 10477 | 0.0018866 | 1.6206e-06 | 1164.1111
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONN/CLAMP | 18 | 46 | 5275 | 0.00094988 | 8.2833e-06 | 114.6739
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 14 | 39 | 34454 | 0.0062042 | 7.0228e-06 | 883.4359
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | NONE | 2474 | 22931 | 2667385 | 0.4784 | 0.0041127 | 116.3222
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 696 | 13188 | 2921403 | 0.52395 | 0.0023653 | 221.5198
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 77 | 3593 | 1582021 | 0.28374 | 0.00064441 | 440.3064
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | NONE | 50 | 241 | 37839 | 0.0068137 | 4.3397e-05 | 157.0083
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 6 | 251 | 28609 | 0.005131 | 4.5017e-05 | 113.9801
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | FUSE | 172 | 1628 | 436803 | 0.078341 | 0.00029198 | 268.3065
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 1 | 5 | 135 | 2.4212e-05 | 8.9675e-07 | 27
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | FUSE | 72 | 552 | 77280 | 0.01386 | 9.9001e-05 | 140
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | POLE | 4 | 9 | 2078 | 0.00037269 | 1.6142e-06 | 230.8889
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CUTOUT | 4 | 396 | 52238 | 0.0094066 | 7.1308e-05 | 131.9141
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | NONE | 14 | 35 | 15109 | 0.0027098 | 6.2773e-06 | 431.6857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CUTOUT | 2 | 16 | 821 | 0.0001462 | 2.8493e-06 | 51.3125
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | FUSE | 450 | 5817 | 2045473 | 0.36833 | 0.0010475 | 351.6371
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CABLE TERMINATOR | 1 | 1 | 244 | 4.3938e-05 | 1.8007e-07 | 244
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 5 | 3739 | 0.00067693 | 9.0523e-07 | 747.8
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONN/CLAMP | 3 | 83 | 6035 | 0.0010926 | 1.5027e-05 | 72.7108
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | U | NONE | 8 | 795 | 150056 | 0.027167 | 0.00014393 | 188.7497
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | POLE | 11 | 1235 | 545551 | 0.099477 | 0.00022519 | 441.7417
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 223 | 4.0662e-05 | 1.8234e-07 | 223
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | NONE | 261 | 17432 | 1718575 | 0.31337 | 0.0031786 | 98.5874
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 4 | 5 | 1302 | 0.00023741 | 9.1171e-07 | 260.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 20 | 239 | 24239 | 0.0044198 | 4.358e-05 | 101.4184
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONN/CLAMP | 3 | 52 | 13483 | 0.0024585 | 9.4818e-06 | 259.2885
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 23 | 1581 | 85658 | 0.015619 | 0.00028828 | 54.1796
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | REGULATOR | 18 | 5953 | 832770 | 0.15185 | 0.0010855 | 139.8908
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | NONE | 831 | 9921 | 1317721 | 0.24028 | 0.001809 | 132.8214
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 14 | 784 | 0.00014296 | 2.5528e-06 | 56
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | NONE | 1 | 1311 | 301530 | 0.054982 | 0.00023905 | 230
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 108 | 6926 | 2581727 | 0.4649 | 0.0012472 | 372.7587
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | NONE | 18 | 78 | 35887 | 0.0064622 | 1.4046e-05 | 460.0897
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | NONE | 210 | 7990 | 6868650 | 1.2369 | 0.0014388 | 859.6558
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | FUSE | 17 | 45 | 10171 | 0.0018315 | 8.1032e-06 | 226.0222
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 14 | 2037 | 509122 | 0.091679 | 0.00036681 | 249.9372
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 5 | 581 | 23861 | 0.0042967 | 0.00010462 | 41.0688
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | INSULATOR | 220 | 45912 | 9728852 | 1.7449 | 0.0082343 | 211.9022
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 505 | 200520 | 0.036108 | 9.0936e-05 | 397.0693
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | GUY/ANCHOR | 2 | 4 | 264 | 4.7013e-05 | 7.1232e-07 | 66
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 1015 | 140193 | 0.024966 | 0.00018075 | 138.1212
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 2 | 574 | 0.00010222 | 3.5616e-07 | 287
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | POLE | 1 | 19 | 2774 | 0.00050222 | 3.4399e-06 | 146
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 1 | 137 | 2.4803e-05 | 1.8105e-07 | 137
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WW | CROSSARM | 1 | 22 | 22044 | 0.0039695 | 3.9616e-06 | 1002
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 3 | 237 | 4.2677e-05 | 5.4022e-07 | 79
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | WU | NETWORK LIMITER | 1 | 866 | 5196 | 0.00093565 | 0.00015594 | 6
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 6 | 3328 | 1428097 | 0.25716 | 0.00059928 | 429.1157
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CROSSARM | 1 | 384 | 73344 | 0.013154 | 6.887e-05 | 191
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | BREAKER | 1 | 954 | 216173 | 0.038496 | 0.00016989 | 226.5964
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CONN/CLAMP | 2 | 2 | 423 | 7.5328e-05 | 3.5616e-07 | 211.5
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | V | NONE | 8 | 3690 | 388396 | 0.069165 | 0.00065711 | 105.2564
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 473 | 351912 | 0.063369 | 8.5174e-05 | 744
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 135 | 17550 | 0.0031253 | 2.4041e-05 | 130
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 34 | 510 | 9.0821e-05 | 6.0547e-06 | 15
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 2 | 236 | 4.2027e-05 | 3.5616e-07 | 118
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | BE | POLE | 5 | 4334 | 1698720 | 0.30251 | 0.0007718 | 391.952
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | VA | STATIC WIRE | 1 | 8 | 4000 | 0.00071232 | 1.4246e-06 | 500
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | METERING | 1 | 1 | 118 | 2.1013e-05 | 1.7808e-07 | 118
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | STATIC WIRE | 2 | 849 | 891462 | 0.15875 | 0.00015119 | 1050.0141
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SWITCH, OH | 2 | 446 | 39566 | 0.0070459 | 7.9424e-05 | 88.713
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | FUSE | 1 | 8 | 1008 | 0.0001795 | 1.4246e-06 | 126
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | REGULATOR | 1 | 3 | 630 | 0.00011219 | 5.3424e-07 | 210
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 7 | 2254 | 0.000411 | 1.2764e-06 | 322
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 13 | 1014 | 0.00018186 | 2.3316e-06 | 78
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | RECLOSER, LINE/OCR/BR | 1 | 160 | 36160 | 0.0065114 | 2.8812e-05 | 226
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 22 | 360 | 86866 | 0.015579 | 6.4566e-05 | 241.2944
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | FUSE | 3 | 10 | 964 | 0.00017359 | 1.8007e-06 | 96.4
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | METERING | 2 | 2 | 136 | 2.4392e-05 | 3.587e-07 | 68
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | NONE | 59 | 1354 | 170836 | 0.030639 | 0.00024284 | 126.1713
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 58 | 3741 | 569726 | 0.10218 | 0.00067095 | 152.2924
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 30 | 487 | 126878 | 0.022756 | 8.7344e-05 | 260.5298
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR UG | 3 | 20 | 15860 | 0.0028559 | 3.6014e-06 | 793
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | ARRESTER | 9 | 5968 | 848987 | 0.15288 | 0.0010747 | 142.2565
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 3 | 469 | 8.4115e-05 | 5.3805e-07 | 156.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CUTOUT | 14 | 227 | 57117 | 0.010244 | 4.0713e-05 | 251.6167
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | BREAKER | 1 | 13 | 2262 | 0.00040732 | 2.3409e-06 | 174
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, OH | 2 | 2 | 387 | 6.9409e-05 | 3.587e-07 | 193.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 2 | 648 | 0.00011732 | 3.6209e-07 | 324
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WL | NONE | 9 | 4740 | 3026464 | 0.54793 | 0.00085816 | 638.4945
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 18 | 1890 | 0.00034218 | 3.2588e-06 | 105
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 3 | 362 | 22762 | 0.004121 | 6.5539e-05 | 62.8785
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 1 | 101 | 1.8286e-05 | 1.8105e-07 | 101
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 3109 | 1071232 | 0.19394 | 0.00056287 | 344.5584
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | FUSE | 1 | 14 | 544 | 9.8489e-05 | 2.5346e-06 | 38.8571
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | U | NONE | 16 | 9943 | 1177086 | 0.21111 | 0.0017833 | 118.3834
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 357 | 6.4286e-05 | 1.8007e-07 | 357
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 2 | 110 | 1.9808e-05 | 3.6014e-07 | 55
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | POLE | 10 | 323 | 159895 | 0.028677 | 5.793e-05 | 495.031
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | REGULATOR | 2 | 1198 | 226422 | 0.040772 | 0.00021573 | 189
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 5 | 23 | 4468 | 0.00080134 | 4.1251e-06 | 194.2609
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | BREAKER | 1 | 1 | 370 | 6.6627e-05 | 1.8007e-07 | 370
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | NONE | 8 | 10 | 925 | 0.0001659 | 1.7935e-06 | 92.5
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | TRANSFORMER, POWER - NON LTC | 5 | 3441 | 694827 | 0.12462 | 0.00061714 | 201.9259
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | V | NONE | 3 | 1397 | 120292 | 0.021574 | 0.00025055 | 86.1074
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | TOR | CROSSARM | 1 | 57 | 57114 | 0.010243 | 1.0223e-05 | 1002
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 73 | 138 | 13672 | 0.0024347 | 2.4575e-05 | 99.0725
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 921 | 10445 | 1738218 | 0.30954 | 0.00186 | 166.4163
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 13 | 111 | 36805 | 0.0065542 | 1.9767e-05 | 331.5766
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 14 | 24 | 8109 | 0.001444 | 4.2739e-06 | 337.875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 8 | 1364 | 231080 | 0.041444 | 0.00024463 | 169.4135
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | ARRESTER | 28 | 506 | 108222 | 0.01941 | 9.0751e-05 | 213.8775
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | NONE | 429 | 7408 | 1433861 | 0.25534 | 0.0013192 | 193.5558
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | INSULATOR | 3 | 234 | 108238 | 0.019275 | 4.1671e-05 | 462.5556
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 45 | 76 | 12464 | 0.0022196 | 1.3534e-05 | 164
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | METERING | 8 | 1468 | 188297 | 0.033532 | 0.00026142 | 128.2677
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | RECLOSER, LINE/OCR/BR | 1 | 27 | 2889 | 0.00051814 | 4.8425e-06 | 107
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 25 | 959 | 287401 | 0.05118 | 0.00017078 | 299.6882
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | POLE | 11 | 150 | 83706 | 0.014906 | 2.6712e-05 | 558.04
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 5 | 435 | 74566 | 0.013279 | 7.7465e-05 | 171.4161
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | WU | NONE | 28 | 18639 | 3293862 | 0.58657 | 0.0033192 | 176.7188
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 24 | 698 | 0.00012519 | 4.3044e-06 | 29.0833
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 4 | 1734 | 121756 | 0.021837 | 0.00031099 | 70.2168
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 6 | 1734 | 0.00031224 | 1.0804e-06 | 289
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 1 | 173 | 3.1321e-05 | 1.8105e-07 | 173
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 3 | 21 | 7975 | 0.0014361 | 3.7815e-06 | 379.7619
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 2 | 3 | 311 | 5.6002e-05 | 5.4022e-07 | 103.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | POLE | 2 | 27 | 3687 | 0.00066752 | 4.8883e-06 | 136.5556
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 34 | 555 | 99250 | 0.017674 | 9.8834e-05 | 178.8288
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 29 | 405 | 37663 | 0.006707 | 7.2122e-05 | 92.9951
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 36 | 488 | 18792 | 0.0033465 | 8.6903e-05 | 38.5082
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 2 | 8 | 510 | 9.1469e-05 | 1.4348e-06 | 63.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | ARRESTER | 1 | 5 | 230 | 4.1251e-05 | 8.9675e-07 | 46
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CROSSARM | 1 | 0 | 0 | 0 | 0
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | ARRESTER | 7 | 5803 | 3555508 | 0.63316 | 0.0010334 | 612.7017
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 3 | 1935 | 0.00035032 | 5.4314e-07 | 645
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | POLE | 1 | 7 | 511 | 9.3177e-05 | 1.2764e-06 | 73
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | FUSE | 1 | 17 | 9775 | 0.0017824 | 3.0998e-06 | 575
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | BREAKER | 2 | 2 | 286 | 5.215e-05 | 3.6468e-07 | 143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 19 | 20235 | 0.0036897 | 3.4645e-06 | 1065
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | FUSE | 3 | 42 | 24513 | 0.0044698 | 7.6584e-06 | 583.6429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | FUSE | 2 | 35 | 15231 | 0.0027575 | 6.3366e-06 | 435.1714
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | NONE | 16 | 95 | 17468 | 0.0031107 | 1.6918e-05 | 183.8737
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 1619 | 238760 | 0.042994 | 0.00029154 | 147.4737
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | PEDESTAL | 2 | 6 | 214 | 3.8109e-05 | 1.0685e-06 | 35.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONN/CLAMP | 2 | 2 | 180 | 3.2054e-05 | 3.5616e-07 | 90
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | METERING | 2 | 4 | 58 | 1.0329e-05 | 7.1232e-07 | 14.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | V | METERING | 1 | 1 | 71 | 1.2644e-05 | 1.7808e-07 | 71
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | SWITCH, OH | 1 | 6 | 9114 | 0.001623 | 1.0685e-06 | 1519
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | ERF | OTHER EQUIPMENT | 4 | 4008 | 185314 | 0.033001 | 0.00071374 | 46.236
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | BREAKER | 5 | 1767 | 319148 | 0.056834 | 0.00031467 | 180.6157
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | R | BREAKER | 1 | 928 | 310880 | 0.055756 | 0.00016644 | 335
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | INSULATOR | 4 | 506 | 115969 | 0.020883 | 9.1116e-05 | 229.1877
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1120 | 39674 | 7393142 | 1.326 | 0.0071155 | 186.3473
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 7 | 21 | 1948 | 0.00035078 | 3.7815e-06 | 92.7619
AEP Total | 2020 | 5484199 | PARTIAL POWER | UG | NONE | 3 | 3 | 2061 | 0.00037581 | 5.4703e-07 | 687
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | FUSE | 117 | 628 | 60558 | 0.011042 | 0.00011451 | 96.4299
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1074 | 40998 | 6151000 | 1.1216 | 0.0074757 | 150.0317
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | NONE | 1403 | 9661 | 1676699 | 0.30573 | 0.0017616 | 173.5534
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | FUSE | 37 | 103 | 13621 | 0.0024837 | 1.8781e-05 | 132.2427
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | NONE | 72 | 8028 | 1017659 | 0.18556 | 0.0014638 | 126.7637
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | NONE | 10 | 15 | 2023 | 0.00036888 | 2.7351e-06 | 134.8667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | NONE | 222 | 10508 | 4385813 | 0.79972 | 0.0019161 | 417.3785
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CROSSARM | 129 | 40068 | 7052053 | 1.2859 | 0.0073061 | 176.0021
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | POLE | 24 | 3237 | 389302 | 0.070986 | 0.00059024 | 120.2663
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 8 | 7296 | 580215 | 0.1058 | 0.0013304 | 79.5251
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | SPLICE, OH | 2 | 338 | 340028 | 0.062001 | 6.1632e-05 | 1006
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | FUSE | 56 | 699 | 247062 | 0.04505 | 0.00012746 | 353.4506
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | ARRESTER | 8 | 34 | 8998 | 0.0016407 | 6.1996e-06 | 264.6471
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | BREAKER | 3 | 1627 | 95430 | 0.017401 | 0.00029667 | 58.654
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 498 | 105122 | 0.019168 | 9.0806e-05 | 211.0884
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 22 | 463 | 154848 | 0.028235 | 8.4424e-05 | 334.4449
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 49 | 4655 | 0.0008488 | 8.9348e-06 | 95
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CAPACITOR | 4 | 2056 | 126705 | 0.023104 | 0.0003749 | 61.6269
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 96 | 16164 | 0.0029474 | 1.7505e-05 | 168.375
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 1 | 785 | 0.00014314 | 1.8234e-07 | 785
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | TRANSFORMER, OH | 1 | 1 | 1470 | 0.00026804 | 1.8234e-07 | 1470
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | FUSE | 1 | 1 | 141 | 2.571e-05 | 1.8234e-07 | 141
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 406 | 1384 | 152193 | 0.027296 | 0.00024822 | 109.966
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 3 | 15 | 2840 | 0.0005114 | 2.7011e-06 | 189.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 2610 | 322215 | 0.058022 | 0.00046999 | 123.454
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 94 | 5818 | 1472156 | 0.26403 | 0.0010435 | 253.0347
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | V | CONDUCTOR OVERHEAD | 2 | 1121 | 169491 | 0.030398 | 0.00020105 | 151.1963
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 16 | 4896 | 0.00088163 | 2.8812e-06 | 306
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 13 | 130 | 8572 | 0.0015374 | 2.3316e-05 | 65.9385
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | POLE | 19 | 971 | 779012 | 0.13972 | 0.00017415 | 802.2781
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 5 | 29 | 7950 | 0.0014258 | 5.2012e-06 | 274.1379
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | U | NONE | 6 | 6934 | 1793271 | 0.32292 | 0.0012486 | 258.62
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CUTOUT | 5 | 54 | 26898 | 0.0048242 | 9.6849e-06 | 498.1111
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | FUSE | 5 | 38 | 3501 | 0.00063043 | 6.8427e-06 | 92.1316
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, OH | 3 | 6 | 1404 | 0.00025181 | 1.0761e-06 | 234
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | INSULATOR | 3 | 620 | 187571 | 0.033776 | 0.00011164 | 302.5339
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 53 | 772 | 186558 | 0.033459 | 0.00013846 | 241.6554
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | WW | NONE | 1 | 558 | 64170 | 0.011509 | 0.00010008 | 115
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 5 | 7 | 1248 | 0.00022224 | 1.2466e-06 | 178.2857
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | FUSE | 3 | 15 | 2946 | 0.00052462 | 2.6712e-06 | 196.4
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | POLE | 1 | 4 | 1008 | 0.0001795 | 7.1232e-07 | 252
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 760 | 42797 | 0.0076213 | 0.00013534 | 56.3118
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | FUSE | 1 | 5 | 300 | 5.4022e-05 | 9.0036e-07 | 60
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 3 | 921 | 0.00016794 | 5.4703e-07 | 307
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | TRANSFORMER, POWER - NON LTC | 1 | 349 | 3141 | 0.00056561 | 6.2845e-05 | 9
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | FUSE | 1 | 2 | 142 | 2.5287e-05 | 3.5616e-07 | 71
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | POLE | 2 | 21 | 1179 | 0.00020996 | 3.7397e-06 | 56.1429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 4 | 216 | 3.8465e-05 | 7.1232e-07 | 54
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 312 | 22152 | 0.0039448 | 5.5561e-05 | 71
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 1 | 136 | 2.4219e-05 | 1.7808e-07 | 136
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | POLE | 2 | 10 | 1302 | 0.00023186 | 1.7808e-06 | 130.2
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | METERING | 1 | 5 | 5665 | 0.0010088 | 8.904e-07 | 1133
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | FUSE | 1 | 3 | 258 | 4.6459e-05 | 5.4022e-07 | 86
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 1 | 1 | 60 | 1.0863e-05 | 1.8105e-07 | 60
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | NONE | 35 | 149 | 15453 | 0.0027977 | 2.6976e-05 | 103.7114
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 10 | 747 | 179298 | 0.032461 | 0.00013524 | 240.0241
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 5 | 20 | 17857 | 0.0032329 | 3.6209e-06 | 892.85
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 1 | 50 | 52112 | 0.0094347 | 9.0523e-06 | 1042.24
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | NONE | 2 | 10 | 1212 | 0.00021943 | 1.8105e-06 | 121.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 11 | 73 | 25509 | 0.0046183 | 1.3216e-05 | 349.4384
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 881 | 26208 | 5504802 | 0.99662 | 0.0047449 | 210.0428
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 26 | 85 | 56446 | 0.010219 | 1.5389e-05 | 664.0706
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | FUSE | 172 | 2015 | 572780 | 0.1037 | 0.00036481 | 284.2581
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | NONE | 153 | 15315 | 6435050 | 1.165 | 0.0027727 | 420.1796
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 25 | 1201 | 164741 | 0.029826 | 0.00021744 | 137.1699
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 83 | 252 | 87823 | 0.0159 | 4.5624e-05 | 348.504
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | NONE | 44 | 2771 | 830664 | 0.15039 | 0.00050168 | 299.7705
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | METERING | 15 | 23 | 2866 | 0.00051888 | 4.1641e-06 | 124.6087
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 4 | 177 | 115930 | 0.020989 | 3.2045e-05 | 654.9718
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | TR | NONE | 9 | 4262 | 1201847 | 0.21759 | 0.00077162 | 281.9913
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | ARRESTER | 8 | 55 | 10227 | 0.0018516 | 9.9576e-06 | 185.9455
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 5 | 12 | 3130 | 0.00056668 | 2.1726e-06 | 260.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 9 | 1264 | 791198 | 0.14324 | 0.00022884 | 625.9478
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | AF | MOAB | 1 | 170 | 1530 | 0.000277 | 3.0778e-05 | 9
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | FUSE | 8 | 85 | 16354 | 0.0029608 | 1.5389e-05 | 192.4
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | V | NONE | 3 | 3522 | 210404 | 0.038093 | 0.00063765 | 59.7399
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | FUSE | 6 | 178 | 25304 | 0.0045812 | 3.2226e-05 | 142.1573
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 1877 | 30032 | 0.0054372 | 0.00033982 | 16
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 3 | 504 | 9.1247e-05 | 5.4314e-07 | 168
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | ARRESTER | 307 | 13643 | 2126301 | 0.38289 | 0.0024567 | 155.8529
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 106 | 5602 | 791934 | 0.14261 | 0.0010088 | 141.3663
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | POLE | 9 | 1958 | 727521 | 0.13101 | 0.00035258 | 371.5633
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1650 | 53337 | 9311041 | 1.6767 | 0.0096045 | 174.57
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 407 | 16891 | 6618502 | 1.1918 | 0.0030416 | 391.836
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WU | NONE | 21 | 17873 | 4126052 | 0.74299 | 0.0032184 | 230.8539
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, OH | 26 | 10047 | 1431059 | 0.25769 | 0.0018092 | 142.4364
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CUTOUT | 17 | 1000 | 261759 | 0.047135 | 0.00018007 | 261.759
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | NONE | 163 | 8184 | 8164718 | 1.454 | 0.0014574 | 997.6439
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 9 | 110 | 35617 | 0.0063427 | 1.9589e-05 | 323.7909
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 10 | 323 | 54635 | 0.0097294 | 5.752e-05 | 169.1486
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 30 | 39 | 4089 | 0.00072817 | 6.9451e-06 | 104.8462
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | NONE | 13 | 125 | 13334 | 0.0023745 | 2.226e-05 | 106.672
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | CROSSARM | 8 | 3546 | 329537 | 0.058684 | 0.00063147 | 92.932
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 5 | 22 | 10581 | 0.0018843 | 3.9178e-06 | 480.9545
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | R | NONE | 1 | 1625 | 123500 | 0.021993 | 0.00028938 | 76
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE | 7 | 250 | 218700 | 0.038946 | 4.452e-05 | 874.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 103 | 16418 | 0.0029237 | 1.8342e-05 | 159.3981
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 6 | 6437 | 2082336 | 0.37082 | 0.0011463 | 323.4948
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 3 | 277 | 4.9328e-05 | 5.3424e-07 | 92.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 3 | 11 | 1053 | 0.00018752 | 1.9589e-06 | 95.7273
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 6 | 331 | 25839 | 0.0046014 | 5.8944e-05 | 78.0634
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | TRANSFORMER, OH | 1 | 1 | 74 | 1.3178e-05 | 1.7808e-07 | 74
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | CONN/CLAMP | 3 | 25 | 399 | 7.1054e-05 | 4.452e-06 | 15.96
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 1 | 1 | 207 | 3.6863e-05 | 1.7808e-07 | 207
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CROSSARM | 1 | 4 | 776 | 0.00013819 | 7.1232e-07 | 194
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | NONE | 2 | 2 | 82 | 1.4603e-05 | 3.5616e-07 | 41
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 9 | 1002 | 210697 | 0.037521 | 0.00017844 | 210.2764
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | INSULATOR | 1 | 1 | 132 | 2.3507e-05 | 1.7808e-07 | 132
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 7 | 1813 | 0.00032286 | 1.2466e-06 | 259
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | OU | NONE | 1 | 529 | 138069 | 0.024587 | 9.4204e-05 | 261
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CROSSARM | 2 | 912 | 110170 | 0.020089 | 0.0001663 | 120.8004
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 5 | 3470 | 0.00062485 | 9.0036e-07 | 694
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 79 | 30336 | 0.0054627 | 1.4226e-05 | 384
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | CE | NONE | 3 | 995 | 10111 | 0.0018207 | 0.00017917 | 10.1618
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | FUSE | 1 | 2 | 290 | 5.2012e-05 | 3.587e-07 | 145
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 51 | 26637 | 0.0047966 | 9.1837e-06 | 522.2941
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | RELAY | 1 | 1305 | 129195 | 0.023171 | 0.00023405 | 99
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 5 | 2385 | 0.00042947 | 9.0036e-07 | 477
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | WU | NONE | 1 | 1442 | 333102 | 0.059742 | 0.00025862 | 231
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | TOR | POLE HARDWARE | 2 | 2201 | 656092 | 0.11814 | 0.00039634 | 298.0881
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | CROSSARM | 2 | 753 | 86396 | 0.015557 | 0.00013559 | 114.7357
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | METERING | 3 | 6 | 974 | 0.00017345 | 1.0685e-06 | 162.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | SWITCH, OH | 1 | 969 | 234498 | 0.041759 | 0.00017256 | 242
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 1 | 73 | 1.3e-05 | 1.7808e-07 | 73
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 1534 | 57009 | 9646077 | 1.7178 | 0.010152 | 169.2027
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 267 | 1074 | 162427 | 0.028925 | 0.00019126 | 151.2356
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 9 | 19 | 1080 | 0.00019233 | 3.3835e-06 | 56.8421
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 4 | 5 | 87 | 1.5493e-05 | 8.904e-07 | 17.4
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 9 | 5418 | 0.00096484 | 1.6027e-06 | 602
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 74 | 12136 | 0.0021612 | 1.3178e-05 | 164
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 1 | 45 | 8.0136e-06 | 1.7808e-07 | 45
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 2 | 230 | 4.0958e-05 | 3.5616e-07 | 115
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | V | NONE | 2 | 412 | 10716 | 0.0019083 | 7.3369e-05 | 26.0097
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | ERF | NONE | 12 | 6935 | 276161 | 0.049179 | 0.001235 | 39.8213
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 2 | 5 | 714 | 0.00012715 | 8.904e-07 | 142.8
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 3 | 4 | 2616 | 0.00046586 | 7.1232e-07 | 654
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1073 | 311170 | 0.055413 | 0.00019108 | 290
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | TRANSFORMER, OH | 2 | 4 | 1425 | 0.00025376 | 7.1232e-07 | 356.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 1 | 7 | 3269 | 0.00058214 | 1.2466e-06 | 467
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | FUSE | 1 | 2 | 220 | 3.9457e-05 | 3.587e-07 | 110
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 44 | 4356 | 0.00077572 | 7.8355e-06 | 99
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | U | POLE | 1 | 573 | 237795 | 0.042346 | 0.00010204 | 415
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | INSULATOR | 4 | 8 | 533 | 9.4917e-05 | 1.4246e-06 | 66.625
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 2 | 352 | 38708 | 0.0068931 | 6.2684e-05 | 109.9659
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 1 | 63 | 43659 | 0.0077748 | 1.1219e-05 | 693
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | METERING | 1 | 1 | 104 | 1.8829e-05 | 1.8105e-07 | 104
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | INSULATOR | 1 | 1084 | 53116 | 0.0095647 | 0.0001952 | 49
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | V | NONE | 1 | 439 | 21950 | 0.0039089 | 7.8177e-05 | 50
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 420 | 7.4794e-05 | 3.5616e-07 | 210
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 65 | 6890 | 0.001227 | 1.1575e-05 | 106
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 4 | 140 | 2.4931e-05 | 7.1232e-07 | 35
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 268 | 4.8066e-05 | 1.7935e-07 | 268
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | VA | NONE | 4 | 928 | 191883 | 0.03417 | 0.00016526 | 206.7705
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CROSSARM | 52 | 6928 | 1125857 | 0.20049 | 0.0012337 | 162.5082
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 8 | 44 | 10059 | 0.0017913 | 7.8355e-06 | 228.6136
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 16 | 4430 | 525472 | 0.093576 | 0.00078889 | 118.6167
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | FUSE | 4 | 22 | 4137 | 0.00073672 | 3.9178e-06 | 188.0455
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | BREAKER | 1 | 3 | 693 | 0.00012429 | 5.3805e-07 | 231
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 36 | 5021 | 640631 | 0.11408 | 0.00089414 | 127.5903
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 248 | 32943 | 0.0059083 | 4.4479e-05 | 132.8347
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | INSULATOR | 1 | 36 | 9684 | 0.0017368 | 6.4566e-06 | 269
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 1 | 89 | 35511 | 0.0063689 | 1.5962e-05 | 399
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 119 | 9163 | 0.0016434 | 2.1343e-05 | 77
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 6 | 1664 | 0.00029844 | 1.0761e-06 | 277.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 664 | 117276 | 0.021033 | 0.00011909 | 176.6205
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 609 | 75454 | 0.013533 | 0.00010922 | 123.8982
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | INSULATOR | 2 | 50 | 3682 | 0.00066661 | 9.0523e-06 | 73.64
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | TOR | NONE | 36 | 30265 | 4152093 | 0.7394 | 0.0053896 | 137.1912
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 342 | 14311 | 4289186 | 0.76382 | 0.0025485 | 299.7125
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | POLE | 2 | 21 | 5142 | 0.00091569 | 3.7397e-06 | 244.8571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 5 | 334 | 57606 | 0.010373 | 6.0144e-05 | 172.4731
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 3 | 3544 | 0.00064622 | 5.4703e-07 | 1181.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | INSULATOR | 3 | 2007 | 374551 | 0.068296 | 0.00036596 | 186.6223
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CUTOUT | 4 | 5628 | 410321 | 0.074819 | 0.0010262 | 72.9071
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | TIR | NONE | 4 | 4598 | 64372 | 0.011654 | 0.00083245 | 14
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 3 | 237 | 4.2908e-05 | 5.4314e-07 | 79
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | ARRESTER | 1 | 2 | 196 | 3.5485e-05 | 3.6209e-07 | 98
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 10 | 5600 | 0.0010084 | 1.8007e-06 | 560
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | NONE | 3 | 2244 | 84399 | 0.015198 | 0.00040408 | 37.611
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | NONE | 2 | 12 | 2385 | 0.00042947 | 2.1609e-06 | 198.75
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | NONE | 2 | 2 | 560 | 9.9725e-05 | 3.5616e-07 | 280
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | POLE HARDWARE | 1 | 8 | 11920 | 0.0021227 | 1.4246e-06 | 1490
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 68 | 4478 | 1288469 | 0.22945 | 0.00079744 | 287.7331
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | NONE | 8 | 22 | 3575 | 0.00063664 | 3.9178e-06 | 162.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 98 | 50078 | 0.0089179 | 1.7452e-05 | 511
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | RECLOSER, LINE/OCR/BR | 1 | 114 | 49476 | 0.0088107 | 2.0301e-05 | 434
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 1 | 1 | 78 | 1.389e-05 | 1.7808e-07 | 78
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 590 | 7876 | 2771553 | 0.50178 | 0.0014259 | 351.8986
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | FUSE | 3 | 34 | 7491 | 0.0013435 | 6.0979e-06 | 220.3235
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | JUMPER/RISER | 2 | 4 | 828 | 0.0001491 | 7.2029e-07 | 207
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONN/CLAMP | 6 | 42 | 21639 | 0.0038966 | 7.563e-06 | 515.2143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 124 | 13020 | 0.0023572 | 2.245e-05 | 105
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | FUSE | 172 | 851 | 78728 | 0.01402 | 0.00015155 | 92.5123
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 23 | 1366 | 159570 | 0.028416 | 0.00024326 | 116.8155
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 12 | 50 | 17430 | 0.0031039 | 8.904e-06 | 348.6
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | V | NONE | 5 | 4201 | 1141490 | 0.20555 | 0.00075648 | 271.7186
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 17 | 3.0778e-06 | 1.8105e-07 | 17
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | GUY/ANCHOR | 1 | 1 | 278 | 5.0331e-05 | 1.8105e-07 | 278
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 1 | 1 | 70 | 1.2673e-05 | 1.8105e-07 | 70
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 653 | 139742 | 0.024885 | 0.00011629 | 214
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 4 | 1462 | 316380 | 0.056341 | 0.00026035 | 216.4022
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 5 | 117 | 48696 | 0.0086718 | 2.0835e-05 | 416.2051
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | WL | NONE | 1 | 790 | 161950 | 0.029046 | 0.00014169 | 205
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 2 | 46 | 8.2501e-06 | 3.587e-07 | 23
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | TOR | NONE | 2 | 11 | 121 | 2.1907e-05 | 1.9915e-06 | 11
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 1 | 220 | 4.0115e-05 | 1.8234e-07 | 220
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 134 | 124044 | 0.022618 | 2.4434e-05 | 925.7015
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | NONE | 2 | 2 | 386 | 7.0384e-05 | 3.6468e-07 | 193
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 13 | 1482 | 0.00027023 | 2.3704e-06 | 114
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CUTOUT | 6 | 19 | 2408 | 0.00043908 | 3.4645e-06 | 126.7368
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 9 | 675 | 0.00012308 | 1.6411e-06 | 75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | INSULATOR | 1 | 27 | 13554 | 0.0024715 | 4.9232e-06 | 502
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | RECLOSER, LINE/OCR/BR | 1 | 244 | 29524 | 0.0053452 | 4.4175e-05 | 121
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | METERING | 1 | 1 | 140 | 2.5346e-05 | 1.8105e-07 | 140
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 15 | 490 | 45647 | 0.0081288 | 8.7259e-05 | 93.1571
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | FUSE | 3 | 47 | 7298 | 0.0012996 | 8.3698e-06 | 155.2766
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 2 | 248 | 4.4164e-05 | 3.5616e-07 | 124
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 34 | 16167 | 0.002879 | 6.0547e-06 | 475.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 3 | 7 | 2928 | 0.00052142 | 1.2466e-06 | 418.2857
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | NONE | 9 | 102 | 14409 | 0.0025947 | 1.8367e-05 | 141.2647
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 562 | 101972 | 0.018362 | 0.0001012 | 181.4448
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 13 | 801 | 210185 | 0.037697 | 0.00014366 | 262.4032
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | NONE | 439 | 9174 | 2269863 | 0.4071 | 0.0016454 | 247.4235
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CUTOUT | 20 | 648 | 219548 | 0.039376 | 0.00011622 | 338.8086
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 49 | 23599 | 0.0042325 | 8.7882e-06 | 481.6122
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | TOR | POLE | 1 | 330 | 87120 | 0.015625 | 5.9186e-05 | 264
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 80 | 4320 | 0.00077479 | 1.4348e-05 | 54
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 44 | 4727 | 400393 | 0.071811 | 0.00084779 | 84.7034
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | REGULATOR | 3 | 3555 | 486778 | 0.087304 | 0.00063759 | 136.9277
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | METERING | 3 | 3 | 388 | 7.0749e-05 | 5.4703e-07 | 129.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 1 | 158 | 2.881e-05 | 1.8234e-07 | 158
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | FUSE | 9 | 162 | 13379 | 0.0024396 | 2.9539e-05 | 82.5864
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 22 | 443 | 104072 | 0.018977 | 8.0778e-05 | 234.9255
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 17 | 76 | 6422 | 0.001171 | 1.3858e-05 | 84.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 5 | 2151 | 0.00039222 | 9.1171e-07 | 430.2
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | POLE | 6 | 224 | 126550 | 0.023075 | 4.0845e-05 | 564.9554
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 2352 | 0.00042887 | 3.6468e-07 | 1176
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 47 | 24534 | 0.0044736 | 8.5701e-06 | 522
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | NONE | 1 | 1 | 80 | 1.4587e-05 | 1.8234e-07 | 80
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 13 | 212 | 55938 | 0.0102 | 3.8657e-05 | 263.8585
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | NONE | 3 | 16 | 2236 | 0.00040772 | 2.9175e-06 | 139.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | TRANSFORMER, OH | 1 | 9 | 1441 | 0.00026275 | 1.6411e-06 | 160.1111
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | INSULATOR | 1 | 437 | 10925 | 0.0019921 | 7.9683e-05 | 25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | POLE | 2373 | 23911 | 4559000 | 0.81187 | 0.0042581 | 190.6654
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | CROSSARM | 13 | 9261 | 2716681 | 0.48724 | 0.001661 | 293.3464
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CUTOUT | 9 | 189 | 29793 | 0.0053434 | 3.3897e-05 | 157.6349
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONN/CLAMP | 6 | 44 | 2647 | 0.00047474 | 7.8914e-06 | 60.1591
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CROSSARM | 3 | 4119 | 959645 | 0.17211 | 0.00073874 | 232.9801
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 2 | 28 | 12411 | 0.0022259 | 5.0218e-06 | 443.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | POLE | 2 | 21 | 2793 | 0.00050294 | 3.7815e-06 | 133
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 8 | 1044 | 0.00018724 | 1.4348e-06 | 130.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 430 | 5288 | 1571998 | 0.27994 | 0.00094169 | 297.2765
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 57 | 18243 | 0.0032851 | 1.0264e-05 | 320.0526
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE | 23 | 429 | 284458 | 0.051018 | 7.6941e-05 | 663.0723
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 77 | 24975 | 0.0044793 | 1.381e-05 | 324.3506
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | ARRESTER | 9 | 1114 | 192453 | 0.034516 | 0.0001998 | 172.7585
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | POLE | 4 | 47 | 14035 | 0.0025172 | 8.4295e-06 | 298.617
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1289 | 50990 | 8182287 | 1.4571 | 0.0090803 | 160.4685
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | METERING | 1 | 1 | 135 | 2.4041e-05 | 1.7808e-07 | 135
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | FUSE | 69 | 555 | 77567 | 0.013813 | 9.8834e-05 | 139.7604
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | TOR | NONE | 93 | 46220 | 11091031 | 2.0224 | 0.0084278 | 239.9617
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | V | NONE | 10 | 4759 | 1068936 | 0.19491 | 0.00086777 | 224.6136
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | POLE | 2 | 788 | 162691 | 0.029665 | 0.00014369 | 206.4607
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | NONE | 15 | 268 | 68427 | 0.012477 | 4.8868e-05 | 255.3246
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 8 | 19 | 1451 | 0.00026458 | 3.4645e-06 | 76.3684
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 153 | 14994 | 0.002734 | 2.7898e-05 | 98
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | METERING | 1 | 6 | 552 | 0.00010065 | 1.0941e-06 | 92
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | ARRESTER | 5 | 26 | 1043 | 0.00019018 | 4.7409e-06 | 40.1154
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | FUSE | 3 | 164 | 22124 | 0.0040341 | 2.9904e-05 | 134.9024
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | U | NONE | 3 | 321 | 56001 | 0.010211 | 5.8532e-05 | 174.4579
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 31 | 1457 | 0.00026567 | 5.6526e-06 | 47
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONN/CLAMP | 6 | 7 | 4023 | 0.00073356 | 1.2764e-06 | 574.7143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | FUSE | 7 | 34 | 4628 | 0.00083003 | 6.0979e-06 | 136.1176
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TOR | NONE | 56 | 24965 | 2497125 | 0.44469 | 0.0044458 | 100.025
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 404 | 46930 | 0.0084169 | 7.2457e-05 | 116.1634
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | NONE | 19 | 41 | 24775 | 0.0044119 | 7.3013e-06 | 604.2683
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 3 | 3456 | 0.0006257 | 5.4314e-07 | 1152
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 12 | 625 | 0.00011315 | 2.1726e-06 | 52.0833
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1160 | 9009 | 3933013 | 0.70823 | 0.0016223 | 436.5649
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CUTOUT | 3331 | 127319 | 22341360 | 4.0231 | 0.022927 | 175.4755
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CROSSARM | 193 | 76031 | 9836573 | 1.7713 | 0.013691 | 129.3758
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | FUSE | 513 | 2547 | 294722 | 0.053071 | 0.00045864 | 115.7134
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CUTOUT | 6 | 167 | 210845 | 0.037967 | 3.0072e-05 | 1262.5449
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CUTOUT | 11 | 441 | 74165 | 0.013355 | 7.9412e-05 | 168.1746
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | NONE | 46 | 1191 | 203595 | 0.036662 | 0.00021447 | 170.9446
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 4 | 13 | 3398 | 0.00061188 | 2.3409e-06 | 261.3846
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | POLE | 28 | 1798 | 2985429 | 0.5405 | 0.00032552 | 1660.4166
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | NONE | 12 | 21 | 15314 | 0.0027725 | 3.802e-06 | 729.2381
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1495 | 55647 | 0.010075 | 0.00027066 | 37.2221
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | NONE | 3 | 4 | 705 | 0.00012764 | 7.2419e-07 | 176.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 3 | 4 | 1375 | 0.00024894 | 7.2419e-07 | 343.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 2 | 42 | 16100 | 0.0029148 | 7.6039e-06 | 383.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | V | NONE | 1 | 1433 | 230813 | 0.041788 | 0.00025944 | 161.0698
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | METERING | 1 | 15 | 810 | 0.00014665 | 2.7157e-06 | 54
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 99 | 1.7924e-05 | 1.8105e-07 | 99
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | POLE | 1 | 2 | 250 | 4.5262e-05 | 3.6209e-07 | 125
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 38 | 843 | 261430 | 0.04767 | 0.00015371 | 310.1186
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 529 | 9400 | 3017055 | 0.55014 | 0.001714 | 320.9633
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | FUSE | 189 | 1078 | 140107 | 0.025547 | 0.00019656 | 129.9694
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | FUSE | 29 | 391 | 43509 | 0.0078347 | 7.0408e-05 | 111.2762
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | ARRESTER | 17 | 3727 | 547295 | 0.098552 | 0.00067113 | 146.846
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE | 22 | 2819 | 1854497 | 0.33394 | 0.00050762 | 657.8563
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 5 | 143 | 4908 | 0.00088379 | 2.575e-05 | 34.3217
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | FUSE | 3 | 39 | 2865 | 0.00051591 | 7.0228e-06 | 73.4615
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | FUSE | 997 | 7973 | 1014219 | 0.1819 | 0.00143 | 127.2067
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 19 | 81 | 3875 | 0.00069778 | 1.4586e-05 | 47.8395
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | FUSE | 5 | 32 | 3171 | 0.00057101 | 5.7623e-06 | 99.0938
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CUTOUT | 67 | 1796 | 574982 | 0.10312 | 0.00032211 | 320.1459
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 25 | 347 | 88753 | 0.015918 | 6.2235e-05 | 255.7723
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | NONE | 544 | 4530 | 331076 | 0.059379 | 0.00081246 | 73.0852
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | ARRESTER | 6 | 193 | 29088 | 0.0052379 | 3.4754e-05 | 150.715
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 21 | 264 | 98104 | 0.017595 | 4.7348e-05 | 371.6061
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | ARRESTER | 7 | 25 | 4081 | 0.00073487 | 4.5018e-06 | 163.24
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SPLICE, UG | 2 | 4 | 730 | 0.00013093 | 7.174e-07 | 182.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 4 | 5 | 208 | 3.7305e-05 | 8.9675e-07 | 41.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | POLE | 2 | 3 | 380 | 6.8153e-05 | 5.3805e-07 | 126.6667
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | FUSE | 3 | 8 | 2307 | 0.00041767 | 1.4484e-06 | 288.375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 4 | 363 | 17640 | 0.0031937 | 6.572e-05 | 48.595
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 119 | 2303 | 758692 | 0.13662 | 0.00041471 | 329.4364
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | NONE | 198 | 15767 | 1134211 | 0.20424 | 0.0028392 | 71.9358
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | FUSE | 187 | 815 | 197951 | 0.035645 | 0.00014676 | 242.8847
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR UG | 67 | 188 | 88783 | 0.015987 | 3.3854e-05 | 472.25
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 2172 | 225784 | 0.040657 | 0.00039112 | 103.9521
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | METERING | 12 | 33 | 1612 | 0.00029028 | 5.9424e-06 | 48.8485
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | U | NONE | 9 | 6629 | 726714 | 0.13086 | 0.0011937 | 109.6265
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 24 | 925 | 138146 | 0.024876 | 0.00016657 | 149.347
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | AO | NONE | 5 | 5465 | 576934 | 0.10389 | 0.00098409 | 105.5689
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 113 | 2482 | 2285943 | 0.41386 | 0.00044936 | 921.0085
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 3 | 5484 | 0.00099286 | 5.4314e-07 | 1828
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CUTOUT | 2 | 109 | 18361 | 0.0033242 | 1.9734e-05 | 168.4495
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | SPLICE, OH | 3 | 11 | 8708 | 0.0015766 | 1.9915e-06 | 791.6364
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 30 | 14772 | 0.0026744 | 5.4314e-06 | 492.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | REGULATOR | 8 | 1348 | 53656 | 0.0097142 | 0.00024405 | 39.8042
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 3 | 17 | 9313 | 0.0016861 | 3.0778e-06 | 547.8235
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1795 | 67947 | 0.012302 | 0.00032498 | 37.8535
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 14 | 4228 | 0.00076546 | 2.5346e-06 | 302
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 1 | 649 | 0.0001175 | 1.8105e-07 | 649
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 5 | 8 | 1042 | 0.00018865 | 1.4484e-06 | 130.25
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ERF | NONE | 2 | 3379 | 533873 | 0.096656 | 0.00061176 | 157.9973
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | FUSE | 2 | 10 | 643 | 0.00011641 | 1.8105e-06 | 64.3
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | TRANSFORMER, GROUNDING | 1 | 1 | 22 | 3.983e-06 | 1.8105e-07 | 22
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 93 | 38683 | 0.0070535 | 1.6958e-05 | 415.9462
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CUTOUT | 695 | 3224 | 262071 | 0.047002 | 0.00057823 | 81.2875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 476 | 20931 | 9380337 | 1.6824 | 0.003754 | 448.1552
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CROSSARM | 139 | 41856 | 15018199 | 2.6935 | 0.0075069 | 358.8064
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 45 | 1187 | 278441 | 0.049938 | 0.00021289 | 234.5754
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE | 359 | 37868 | 10823397 | 1.9412 | 0.0067916 | 285.8191
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, OH | 31 | 11596 | 1219164 | 0.21866 | 0.0020797 | 105.1366
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | NONE | 39 | 3932 | 425438 | 0.076302 | 0.00070521 | 108.1989
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, OH | 50 | 925 | 155624 | 0.027911 | 0.0001659 | 168.2422
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | ARRESTER | 2 | 45 | 9414 | 0.0016884 | 8.0708e-06 | 209.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 1 | 145 | 2.611e-05 | 1.8007e-07 | 145
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | NONE | 3241 | 60045 | 10150699 | 1.8377 | 0.010871 | 169.0515
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 18 | 8552 | 0.0015483 | 3.2588e-06 | 475.1111
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | NONE | 9 | 69 | 8020 | 0.001452 | 1.2492e-05 | 116.2319
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 5 | 540 | 9.7765e-05 | 9.0523e-07 | 108
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SWITCH, OH | 3 | 448 | 17567 | 0.0031804 | 8.1109e-05 | 39.2121
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | NONE | 7 | 1515 | 399380 | 0.072306 | 0.00027429 | 263.6172
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 5 | 87 | 75787 | 0.013721 | 1.5751e-05 | 871.1149
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 851 | 78550 | 0.014221 | 0.00015407 | 92.3032
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | INSULATOR | 196 | 32927 | 4950846 | 0.89633 | 0.0059613 | 150.3582
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 57 | 6451 | 610322 | 0.1105 | 0.0011679 | 94.6089
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE | 232 | 20583 | 6459937 | 1.1695 | 0.0037265 | 313.8482
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | FUSE | 63 | 233 | 30119 | 0.0054529 | 4.2184e-05 | 129.2661
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | FUSE | 307 | 2375 | 362196 | 0.065574 | 0.00042999 | 152.5036
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | NONE | 3276 | 89444 | 11652480 | 2.1096 | 0.016194 | 130.2768
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | NONE | 933 | 19787 | 25172554 | 4.5574 | 0.0035824 | 1272.1764
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 9 | 1867 | 301890 | 0.054656 | 0.00033801 | 161.6979
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | ARRESTER | 3 | 37 | 38632 | 0.0069942 | 6.6987e-06 | 1044.1081
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | POLE | 7 | 1679 | 265334 | 0.048038 | 0.00030398 | 158.031
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABI | OTHER EQUIPMENT | 2 | 1197 | 167679 | 0.030358 | 0.00021671 | 140.0827
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CAPACITOR | 1 | 71 | 8520 | 0.0015425 | 1.2854e-05 | 120
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 266 | 17766 | 0.0032165 | 4.8158e-05 | 66.7895
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | NONE | 40 | 1856 | 437126 | 0.07914 | 0.00033602 | 235.5205
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | NONE | 4 | 7 | 894 | 0.00016186 | 1.2673e-06 | 127.7143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 26 | 1113 | 268339 | 0.048582 | 0.0002015 | 241.0952
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONN/CLAMP | 54 | 653 | 119231 | 0.021586 | 0.00011822 | 182.5896
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 25 | 1096 | 788269 | 0.14271 | 0.00019843 | 719.2235
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | NONE | 3 | 7 | 2571 | 0.00046296 | 1.2605e-06 | 367.2857
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 3 | 5401 | 724700 | 0.12998 | 0.00096867 | 134.1789
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 16 | 100 | 24183 | 0.0043065 | 1.7808e-05 | 241.83
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 7 | 51 | 3233 | 0.00057573 | 9.0821e-06 | 63.3922
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 15 | 2520 | 0.00044876 | 2.6712e-06 | 168
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONN/CLAMP | 2 | 2 | 340 | 6.1224e-05 | 3.6014e-07 | 170
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | POLE | 1 | 10 | 1535 | 0.0002753 | 1.7935e-06 | 153.5
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 3 | 2936 | 407138 | 0.07302 | 0.00052657 | 138.671
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 2 | 190 | 3.4077e-05 | 3.587e-07 | 95
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 13 | 1943 | 336550 | 0.059933 | 0.00034601 | 173.2115
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 25 | 961 | 300625 | 0.053535 | 0.00017113 | 312.8252
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 5 | 15 | 599 | 0.00010667 | 2.6712e-06 | 39.9333
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | FUSE | 18 | 31 | 2792 | 0.0004972 | 5.5205e-06 | 90.0645
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 51 | 3104 | 1039969 | 0.1852 | 0.00055276 | 335.0416
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 9 | 137 | 18577 | 0.0033082 | 2.4397e-05 | 135.5985
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 21 | 7266 | 0.0012939 | 3.7397e-06 | 346
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | NONE | 9 | 2978 | 317485 | 0.056538 | 0.00053032 | 106.6101
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 73 | 21900 | 0.0039649 | 1.3216e-05 | 300
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 2 | 48 | 6861 | 0.0012355 | 8.6435e-06 | 142.9375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | NONE | 1 | 1 | 229 | 4.146e-05 | 1.8105e-07 | 229
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AB | SWITCH, OH | 4 | 4757 | 501956 | 0.089388 | 0.00084713 | 105.5194
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 5 | 26 | 1295 | 0.00023061 | 4.6301e-06 | 49.8077
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 155 | 15560 | 0.0027709 | 2.7602e-05 | 100.3871
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 3 | 10 | 1255 | 0.00022349 | 1.7808e-06 | 125.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CUTOUT | 1 | 1 | 85 | 1.5389e-05 | 1.8105e-07 | 85
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | FUSE | 2 | 301 | 56114 | 0.0099928 | 5.3602e-05 | 186.4252
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 267 | 27016 | 0.004811 | 4.7547e-05 | 101.1835
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 2 | 276 | 4.97e-05 | 3.6014e-07 | 138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CROSSARM | 1 | 199 | 52735 | 0.0094961 | 3.5834e-05 | 265
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 5958 | 1006902 | 0.17931 | 0.001061 | 169
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 15 | 2682 | 0.00047761 | 2.6712e-06 | 178.8
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 24 | 2499 | 0.00044502 | 4.2739e-06 | 104.125
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 52 | 57262 | 0.010197 | 9.2601e-06 | 1101.1923
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 182 | 3.2411e-05 | 1.7808e-07 | 182
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | POLE | 4 | 937 | 556505 | 0.099102 | 0.00016686 | 593.9221
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 3 | 6 | 3387 | 0.00060316 | 1.0685e-06 | 564.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | NONE | 2 | 2 | 77 | 1.3712e-05 | 3.5616e-07 | 38.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | BE | CONDUCTOR UG | 1 | 8 | 1392 | 0.00024789 | 1.4246e-06 | 174
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 224 | 16784 | 0.0029889 | 3.989e-05 | 74.9286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 19 | 3.4214e-06 | 1.8007e-07 | 19
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | STATIC WIRE | 7 | 4853 | 1394619 | 0.2543 | 0.00088491 | 287.3726
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | METERING | 1 | 1 | 48 | 8.6435e-06 | 1.8007e-07 | 48
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 10 | 1920 | 0.00034191 | 1.7808e-06 | 192
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1 | 111 | 1.9767e-05 | 1.7808e-07 | 111
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 1038 | 92382 | 0.016451 | 0.00018485 | 89
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | CONDUCTOR UG | 2 | 2 | 427 | 7.786e-05 | 3.6468e-07 | 213.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | PEDESTAL | 1 | 10 | 150 | 2.7157e-05 | 1.8105e-06 | 15
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 25 | 353 | 154697 | 0.028208 | 6.4367e-05 | 438.2351
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CUTOUT | 9 | 389 | 72492 | 0.013218 | 7.0931e-05 | 186.3548
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 5 | 1808 | 223109 | 0.040682 | 0.00032967 | 123.401
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 1 | 307 | 5.5581e-05 | 1.8105e-07 | 307
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | FUSE | 2 | 77 | 5274 | 0.00095484 | 1.3941e-05 | 68.4935
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR UG | 2 | 2 | 335 | 6.0651e-05 | 3.6209e-07 | 167.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | PEDESTAL | 1 | 1 | 163 | 2.9511e-05 | 1.8105e-07 | 163
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 227 | 23608 | 0.0042741 | 4.1098e-05 | 104
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE | 3 | 156 | 26360 | 0.0047724 | 2.8243e-05 | 168.9744
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 75 | 1390 | 878838 | 0.15825 | 0.0002503 | 632.2576
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | NONE | 870 | 25219 | 2932971 | 0.52815 | 0.0045412 | 116.3001
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 41 | 1242 | 170552 | 0.030712 | 0.00022365 | 137.3205
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 404 | 74100 | 0.013512 | 7.3666e-05 | 183.4158
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 3 | 663 | 0.00012089 | 5.4703e-07 | 221
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CROSSARM | 4 | 546 | 85458 | 0.015583 | 9.9559e-05 | 156.5165
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 7 | 161 | 9492 | 0.0017308 | 2.9357e-05 | 58.9565
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 22 | 2392 | 0.00043616 | 4.0115e-06 | 108.7273
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | NONE | 8 | 10 | 3470 | 0.00063273 | 1.8234e-06 | 347
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | FUSE | 3 | 103 | 8518 | 0.0015532 | 1.8781e-05 | 82.699
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 359 | 4053 | 418351 | 0.075031 | 0.00072691 | 103.2201
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 3 | 71 | 1.2734e-05 | 5.3805e-07 | 23.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, OH | 7 | 7 | 747 | 0.00013397 | 1.2555e-06 | 106.7143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 3 | 9 | 2342 | 0.00042004 | 1.6142e-06 | 260.2222
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 12 | 2710 | 0.00048604 | 2.1522e-06 | 225.8333
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | OL | NONE | 1 | 423 | 2961 | 0.00053106 | 7.5865e-05 | 7
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 1 | 337 | 6.0441e-05 | 1.7935e-07 | 337
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | BREAKER | 6 | 8106 | 199723 | 0.03582 | 0.0014538 | 24.6389
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 3 | 423 | 7.5865e-05 | 5.3805e-07 | 141
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 467 | 27257 | 3581100 | 0.63772 | 0.0048539 | 131.3828
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CUTOUT | 4 | 67 | 10129 | 0.0018166 | 1.2016e-05 | 151.1791
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 60 | 859 | 91622 | 0.016499 | 0.00015468 | 106.6612
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 7 | 1060 | 0.00019088 | 1.2605e-06 | 151.4286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | NONE | 6 | 407 | 5773 | 0.0010354 | 7.2996e-05 | 14.1843
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | NONE | 13 | 1061 | 54563 | 0.0098253 | 0.00019106 | 51.426
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 5 | 5 | 682 | 0.00012281 | 9.0036e-07 | 136.4
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 9 | 152 | 38023 | 0.0068469 | 2.7371e-05 | 250.1513
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 904 | 193994 | 0.034933 | 0.00016279 | 214.5951
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | NONE | 5 | 23 | 4240 | 0.0007635 | 4.1417e-06 | 184.3478
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | TOR | NONE | 2 | 1730 | 130074 | 0.023329 | 0.00031028 | 75.1873
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 17 | 3298 | 0.00059388 | 3.0612e-06 | 194
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 19 | 513 | 9.2007e-05 | 3.4077e-06 | 27
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CROSSARM | 65 | 986 | 39039 | 0.0069521 | 0.00017559 | 39.5933
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONN/CLAMP | 3 | 14 | 724 | 0.00013108 | 2.5346e-06 | 51.7143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 121 | 21748 | 0.0039374 | 2.1907e-05 | 179.7355
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 2 | 2 | 133 | 2.4251e-05 | 3.6468e-07 | 66.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | NONE | 4 | 5 | 816 | 0.00014879 | 9.1171e-07 | 163.2
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | CUTOUT | 1 | 1 | 298 | 5.4338e-05 | 1.8234e-07 | 298
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 276 | 20838 | 0.0037996 | 5.0326e-05 | 75.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 4 | 280 | 5.0693e-05 | 7.2419e-07 | 70
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 272 | 4.9245e-05 | 1.8105e-07 | 272
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR UG | 3 | 30 | 9367 | 0.0016867 | 5.4022e-06 | 312.2333
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | REGULATOR | 1 | 490 | 9800 | 0.001787 | 8.9348e-05 | 20
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 5 | 3250 | 454519 | 0.081846 | 0.00058523 | 139.852
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 5 | 1010 | 0.00018187 | 9.0036e-07 | 202
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 2 | 78 | 1.3989e-05 | 3.587e-07 | 39
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 47 | 3486 | 538519 | 0.095899 | 0.00062079 | 154.4805
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 844 | 37086 | 6322837 | 1.126 | 0.0066043 | 170.4912
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 8 | 257 | 110810 | 0.019733 | 4.5767e-05 | 431.1673
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 28 | 223 | 24303 | 0.0043279 | 3.9712e-05 | 108.9821
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | NONE | 24 | 4786 | 348990 | 0.062148 | 0.00085229 | 72.9189
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 102 | 651 | 88176 | 0.015702 | 0.00011593 | 135.447
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | NONE | 71 | 268 | 24673 | 0.0043938 | 4.7725e-05 | 92.0634
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | SCO | CONDUCTOR OVERHEAD | 2 | 1137 | 6946 | 0.0012458 | 0.00020392 | 6.1091
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 6 | 6 | 400 | 7.1232e-05 | 1.0685e-06 | 66.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 3721 | 807457 | 0.14379 | 0.00066263 | 217
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 12 | 160 | 37123 | 0.0066109 | 2.8493e-05 | 232.0188
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 9 | 256 | 118477 | 0.021098 | 4.5588e-05 | 462.8008
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 65 | 1246 | 225357 | 0.040132 | 0.00022189 | 180.8644
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 7 | 612 | 76455 | 0.013615 | 0.00010898 | 124.9265
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | EQF | SWITCH, OH | 3 | 3083 | 561715 | 0.1017 | 0.00055817 | 182.1975
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | NONE | 7 | 399 | 241566 | 0.043735 | 7.2237e-05 | 605.4286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | NETWORK PROTECTOR | 1 | 2 | 56 | 1.0084e-05 | 3.6014e-07 | 28
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 23 | 2208 | 0.00039601 | 4.1251e-06 | 96
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 1 | 109 | 1.9628e-05 | 1.8007e-07 | 109
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | POLE | 1 | 8 | 1216 | 0.00021809 | 1.4348e-06 | 152
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | POLE | 2 | 376 | 357094 | 0.064045 | 6.7436e-05 | 949.7181
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | FUSE | 2 | 65 | 11661 | 0.0020766 | 1.1575e-05 | 179.4
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 178 | 16616 | 0.002959 | 3.1698e-05 | 93.3483
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | CONDUCTOR UG | 3 | 3 | 506 | 9.0108e-05 | 5.3424e-07 | 168.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 4 | 56 | 4878 | 0.00086867 | 9.9725e-06 | 87.1071
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 3 | 352 | 69240 | 0.01233 | 6.2684e-05 | 196.7045
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 1 | 65 | 1.1575e-05 | 1.7808e-07 | 65
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 10 | 360 | 6.4109e-05 | 1.7808e-06 | 36
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 6 | 37 | 4970 | 0.00088506 | 6.589e-06 | 134.3243
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 154 | 34804 | 0.0061979 | 2.7424e-05 | 226
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CUTOUT | 3 | 6 | 805 | 0.00014335 | 1.0685e-06 | 134.1667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 17 | 2130 | 0.00037931 | 3.0274e-06 | 125.2941
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | JUMPER/RISER | 2 | 6 | 310 | 5.5205e-05 | 1.0685e-06 | 51.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 3 | 163 | 63797 | 0.011361 | 2.9027e-05 | 391.3926
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 3 | 250 | 41006 | 0.0073023 | 4.452e-05 | 164.024
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 3 | 3 | 433 | 7.7109e-05 | 5.3424e-07 | 144.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | NONE | 59 | 771 | 209844 | 0.037369 | 0.0001373 | 272.1712
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 2 | 1260 | 0.00022438 | 3.5616e-07 | 630
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 4 | 6 | 450 | 8.0136e-05 | 1.0685e-06 | 75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 1 | 82 | 1.4603e-05 | 1.7808e-07 | 82
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 10 | 2144 | 0.0003818 | 1.7808e-06 | 214.4
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 2 | 176 | 3.1342e-05 | 3.5616e-07 | 88
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 3 | 3 | 169 | 3.0095e-05 | 5.3424e-07 | 56.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | FUSE | 2 | 1833 | 71616 | 0.012753 | 0.00032642 | 39.0704
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | NONE | 2 | 3 | 212 | 3.7753e-05 | 5.3424e-07 | 70.6667
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CROSSARM | 1 | 11 | 1650 | 0.00029383 | 1.9589e-06 | 150
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 4 | 712 | 0.00012821 | 7.2029e-07 | 178
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 214 | 3.9021e-05 | 1.8234e-07 | 214
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 1719 | 403965 | 0.07366 | 0.00031345 | 235
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | NONE | 1 | 6 | 480 | 8.6435e-05 | 1.0804e-06 | 80
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CUTOUT | 1 | 98 | 17729 | 0.0031925 | 1.7647e-05 | 180.9082
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 11 | 3438 | 0.00061909 | 1.9808e-06 | 312.5455
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 680 | 150960 | 0.027331 | 0.00012311 | 222
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 197 | 250 | 85475 | 0.015475 | 4.5262e-05 | 341.9
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CUTOUT | 20 | 1931 | 658607 | 0.11924 | 0.0003496 | 341.0704
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 47 | 4096 | 549080 | 0.099409 | 0.00074157 | 134.0527
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 305 | 7148 | 786157 | 0.14233 | 0.0012941 | 109.9828
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 260 | 14852 | 4687914 | 0.84873 | 0.0026889 | 315.6419
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | NONE | 267 | 20495 | 6775779 | 1.2267 | 0.0037105 | 330.6064
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 104 | 2354 | 371937 | 0.067338 | 0.00042618 | 158.0021
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 155 | 290 | 44654 | 0.0080844 | 5.2503e-05 | 153.9793
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | NONE | 2 | 8 | 584 | 0.00010573 | 1.4484e-06 | 73
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 10 | 2754 | 268325 | 0.048579 | 0.0004986 | 97.431
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 47 | 652 | 223012 | 0.040376 | 0.00011804 | 342.0429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 105 | 1.901e-05 | 3.6209e-07 | 52.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 18 | 4668 | 0.00084512 | 3.2588e-06 | 259.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | NONE | 2 | 2 | 162 | 2.933e-05 | 3.6209e-07 | 81
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, OH | 6 | 77 | 10092 | 0.0018271 | 1.3941e-05 | 131.0649
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | NONE | 2 | 2 | 235 | 4.2546e-05 | 3.6209e-07 | 117.5
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CUTOUT | 1 | 1467 | 410760 | 0.074367 | 0.0002656 | 280
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 39 | 122 | 50407 | 0.009126 | 2.2088e-05 | 413.1721
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 216 | 11914 | 3436390 | 0.6266 | 0.0021724 | 288.4329
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 305 | 20081 | 0.0036616 | 5.5614e-05 | 65.8393
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | NONE | 5 | 2612 | 264829 | 0.048289 | 0.00047628 | 101.3894
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 9 | 11 | 3439 | 0.00062707 | 2.0058e-06 | 312.6364
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 18 | 246 | 61043 | 0.011131 | 4.4856e-05 | 248.1423
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | NONE | 19 | 337 | 51984 | 0.0094789 | 6.1449e-05 | 154.2552
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | BREAKER | 2 | 1614 | 464612 | 0.084718 | 0.0002943 | 287.8637
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 68 | 6811 | 0.0012419 | 1.2399e-05 | 100.1618
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 3 | 32 | 1964 | 0.00035812 | 5.8349e-06 | 61.375
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 3 | 2444 | 137441 | 0.025061 | 0.00044564 | 56.2361
AEP Total | 2020 | 5484199 | PARTIAL POWER | V | METERING | 1 | 1 | 71 | 1.2946e-05 | 1.8234e-07 | 71
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 27 | 18441 | 0.0033626 | 4.9232e-06 | 683
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | OL | NONE | 1 | 1440 | 125280 | 0.022844 | 0.00026257 | 87
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | R | NONE | 1 | 1480 | 433640 | 0.079071 | 0.00026987 | 293
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | INSULATOR | 2 | 270 | 9794 | 0.0017859 | 4.9232e-05 | 36.2741
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | METERING | 3 | 3 | 3170 | 0.00057802 | 5.4703e-07 | 1056.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | NONE | 855 | 34825 | 3554585 | 0.63752 | 0.0062459 | 102.0699
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | NONE | 218 | 1573 | 144507 | 0.025917 | 0.00028212 | 91.8671
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 6 | 84 | 52544 | 0.0094238 | 1.5065e-05 | 625.5238
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | FUSE | 27 | 874 | 171181 | 0.030701 | 0.00015675 | 195.8593
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 345 | 4509 | 1174610 | 0.20917 | 0.00080296 | 260.5034
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CUTOUT | 267 | 1750 | 136648 | 0.024508 | 0.00031386 | 78.0846
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONDUCTOR UG | 4 | 4 | 788 | 0.00014133 | 7.174e-07 | 197
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | INSULATOR | 42 | 7491 | 1278165 | 0.22924 | 0.0013435 | 170.6268
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | NONE | 38 | 717 | 111057 | 0.019918 | 0.00012859 | 154.8912
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | FUSE | 18 | 55 | 4012 | 0.00071955 | 9.8643e-06 | 72.9455
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 11 | 11 | 1317 | 0.0002362 | 1.9729e-06 | 119.7273
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | POLE | 9 | 825 | 150217 | 0.026941 | 0.00014796 | 182.0812
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 3 | 232 | 109361 | 0.019614 | 4.1609e-05 | 471.3836
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | POLE | 4 | 115 | 14460 | 0.0025934 | 2.0625e-05 | 125.7391
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 493 | 2042 | 210130 | 0.03742 | 0.00036364 | 102.904
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CUTOUT | 3 | 14 | 1710 | 0.00030959 | 2.5346e-06 | 122.1429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 1 | 314 | 5.6849e-05 | 1.8105e-07 | 314
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 3 | 54 | 9142 | 0.001667 | 9.8465e-06 | 169.2963
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 77 | 4389 | 0.0008003 | 1.404e-05 | 57
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | INSULATOR | 1 | 1427 | 573654 | 0.1046 | 0.0002602 | 402
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 389 | 7.0931e-05 | 3.6468e-07 | 194.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 5 | 18 | 2358 | 0.00042996 | 3.2822e-06 | 131
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 2 | 198 | 3.6104e-05 | 3.6468e-07 | 99
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | ARRESTER | 1 | 1 | 60 | 1.0941e-05 | 1.8234e-07 | 60
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | SWITCH, OH | 6 | 6742 | 876195 | 0.15863 | 0.0012206 | 129.9607
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | FUSE | 33 | 438 | 82892 | 0.014927 | 7.8871e-05 | 189.2511
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CABLE TERMINATOR | 15 | 30 | 3182 | 0.00057299 | 5.4022e-06 | 106.0667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, OH | 6 | 50 | 9379 | 0.0016889 | 9.0036e-06 | 187.58
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | FUSE | 1 | 16 | 800 | 0.00014406 | 2.8812e-06 | 50
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 7 | 1039 | 95941 | 0.017276 | 0.00018709 | 92.3397
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | ARRESTER | 3 | 16 | 1444 | 0.00026002 | 2.8812e-06 | 90.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR UG | 2 | 2 | 440 | 7.9232e-05 | 3.6014e-07 | 220
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | R | NONE | 2 | 2677 | 708739 | 0.12762 | 0.00048205 | 264.7512
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | METERING | 1 | 1 | 157 | 2.8271e-05 | 1.8007e-07 | 157
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | METERING | 2 | 2 | 741 | 0.00013343 | 3.6014e-07 | 370.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | NONE | 3 | 17 | 3216 | 0.00057911 | 3.0612e-06 | 189.1765
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 1 | 75 | 1.3451e-05 | 1.7935e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | MOAB | 1 | 1 | 46 | 8.2833e-06 | 1.8007e-07 | 46
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 133 | 33782 | 0.0060588 | 2.3854e-05 | 254
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | POLE HARDWARE | 2 | 52 | 2258 | 0.00040497 | 9.3262e-06 | 43.4231
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CUTOUT | 752 | 4018 | 116735 | 0.020788 | 0.00071552 | 29.053
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 82 | 100 | 14401 | 0.0025645 | 1.7808e-05 | 144.01
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 67 | 723 | 60968 | 0.010857 | 0.00012875 | 84.3264
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 716 | 0.00012751 | 3.5616e-07 | 358
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | NONE | 35 | 208 | 30181 | 0.0053746 | 3.7041e-05 | 145.101
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | JUMPER/RISER | 1 | 3 | 93 | 1.668e-05 | 5.3805e-07 | 31
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CROSSARM | 2 | 493 | 4106 | 0.0007312 | 8.7793e-05 | 8.3286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, STATION SERVICE | 1 | 1 | 94 | 1.6859e-05 | 1.7935e-07 | 94
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CONDUCTOR UG | 4 | 4 | 963 | 0.00017341 | 7.2029e-07 | 240.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, OH | 7 | 4518 | 914126 | 0.16279 | 0.00080456 | 202.3298
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 4 | 1400 | 0.00024931 | 7.1232e-07 | 350
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 4 | 46 | 10215 | 0.0018191 | 8.1917e-06 | 222.0652
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 8 | 413 | 54202 | 0.0096523 | 7.3547e-05 | 131.2397
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, GROUNDING | 1 | 558 | 74772 | 0.013315 | 9.9369e-05 | 134
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 7 | 1338 | 0.00023827 | 1.2466e-06 | 191.1429
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | ERO | NONE | 2 | 2884 | 60564 | 0.010785 | 0.00051358 | 21
AEP Total | 2024 | 5615460 | PARTIAL POWER | V | METERING | 1 | 1 | 44 | 7.8355e-06 | 1.7808e-07 | 44
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 4 | 80 | 1.4246e-05 | 7.1232e-07 | 20
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 3 | 520 | 9.3637e-05 | 5.4022e-07 | 173.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 1 | 252 | 4.5378e-05 | 1.8007e-07 | 252
AEP Total | 2022 | 5553337 | PARTIAL POWER | UB | NONE | 1 | 1 | 6 | 1.0804e-06 | 1.8007e-07 | 6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | METERING | 9 | 15 | 318 | 5.6629e-05 | 2.6712e-06 | 21.2
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | POLE | 1 | 1 | 91 | 1.6205e-05 | 1.7808e-07 | 91
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 32 | 6402 | 0.0011401 | 5.6986e-06 | 200.0625
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CROSSARM | 1 | 82 | 4291 | 0.00076414 | 1.4603e-05 | 52.3293
AEP Total | 2025 | 5615460 | PARTIAL POWER | UG | CONDUCTOR OVERHEAD | 1 | 1 | 60 | 1.0685e-05 | 1.7808e-07 | 60
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | NONE | 2 | 2 | 147 | 2.6804e-05 | 3.6468e-07 | 73.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | SPLICE, OH | 1 | 14 | 1929 | 0.00034597 | 2.5109e-06 | 137.7857
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 1 | 634 | 0.0001156 | 1.8234e-07 | 634
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | JUMPER/RISER | 2 | 21 | 7206 | 0.001314 | 3.8292e-06 | 343.1429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 5 | 3005 | 0.00054794 | 9.1171e-07 | 601
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 154 | 22022 | 0.0040155 | 2.8081e-05 | 143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 12 | 4773 | 0.00086413 | 2.1726e-06 | 397.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | BREAKER | 1 | 211 | 31650 | 0.0056362 | 3.7575e-05 | 150
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CUTOUT | 132 | 1570 | 100546 | 0.018203 | 0.00028424 | 64.042
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | FUSE | 405 | 3391 | 391641 | 0.070905 | 0.00061393 | 115.4942
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | NONE | 837 | 44232 | 9420617 | 1.7056 | 0.008008 | 212.9819
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 10 | 86 | 5543 | 0.0010035 | 1.557e-05 | 64.4535
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CROSSARM | 17 | 901 | 91137 | 0.0165 | 0.00016312 | 101.1509
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | CONDUCTOR UG | 28 | 31 | 7960 | 0.0014411 | 5.6124e-06 | 256.7742
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 69 | 1.2492e-05 | 1.8105e-07 | 69
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | NONE | 32 | 32 | 10122 | 0.0018326 | 5.7935e-06 | 316.3125
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | ABI | NONE | 6 | 4515 | 882560 | 0.15978 | 0.00081742 | 195.4729
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 96 | 1.738e-05 | 1.8105e-07 | 96
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 3 | 18 | 630 | 0.00011406 | 3.2588e-06 | 35
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | NONE | 12 | 1871 | 398224 | 0.072097 | 0.00033874 | 212.8402
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | ARRESTER | 10 | 7217 | 1687703 | 0.30555 | 0.0013066 | 233.851
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | CF | NONE | 3 | 3335 | 926130 | 0.16767 | 0.00060379 | 277.7001
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | FUSE | 11 | 167 | 132720 | 0.024028 | 3.0235e-05 | 794.7305
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | SWITCH, OH | 1 | 353 | 23298 | 0.004218 | 6.3909e-05 | 66
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 1 | 558 | 0.00010102 | 1.8105e-07 | 558
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE | 370 | 62428 | 9533047 | 1.7166 | 0.011242 | 152.7047
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 319 | 2837 | 561854 | 0.10117 | 0.00051086 | 198.0451
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | NONE | 782 | 31985 | 6064317 | 1.092 | 0.0057596 | 189.5988
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | FUSE | 138 | 821 | 95543 | 0.017205 | 0.00014784 | 116.3739
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 28 | 76 | 8709 | 0.0015682 | 1.3685e-05 | 114.5921
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | POLE | 42 | 2072 | 158871 | 0.028608 | 0.00037311 | 76.6752
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | FUSE | 13 | 19 | 1240 | 0.00022329 | 3.4214e-06 | 65.2632
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 109 | 1304 | 243891 | 0.043918 | 0.00023481 | 187.033
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | NONE | 3 | 3 | 372 | 6.6987e-05 | 5.4022e-07 | 124
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 52 | 9.3637e-06 | 1.8007e-07 | 52
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | NONE | 52 | 123 | 10476 | 0.0019102 | 2.2428e-05 | 85.1707
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | INSULATOR | 60 | 12205 | 1783501 | 0.32521 | 0.0022255 | 146.1287
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | NONE | 233 | 9323 | 2169289 | 0.39555 | 0.0017 | 232.6814
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | POLE | 68 | 2116 | 179543 | 0.032738 | 0.00038584 | 84.8502
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | TR | INSULATOR | 4 | 3492 | 1774030 | 0.32348 | 0.00063674 | 508.0269
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | NONE | 4 | 492 | 46735 | 0.0085218 | 8.9712e-05 | 94.9898
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | ARRESTER | 54 | 4010 | 826425 | 0.15069 | 0.00073119 | 206.091
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CROSSARM | 47 | 24437 | 2710942 | 0.49432 | 0.0044559 | 110.936
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ERF | NONE | 8 | 8685 | 765323 | 0.13955 | 0.0015836 | 88.1201
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | NONE | 2 | 2 | 243 | 4.4309e-05 | 3.6468e-07 | 121.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | FUSE | 121 | 1770 | 227881 | 0.041552 | 0.00032275 | 128.7463
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | FUSE | 65 | 718 | 201410 | 0.036726 | 0.00013092 | 280.5153
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 2 | 10 | 2022 | 0.0003687 | 1.8234e-06 | 202.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 379 | 6.8247e-05 | 1.8007e-07 | 379
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 89 | 57494 | 0.010353 | 1.6026e-05 | 646
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | INSULATOR | 6 | 3884 | 92573 | 0.016485 | 0.00069166 | 23.8344
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 534 | 9.5773e-05 | 1.7935e-07 | 534
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1018 | 31735 | 7440858 | 1.3251 | 0.0056514 | 234.4685
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 108 | 181 | 26340 | 0.0046906 | 3.2232e-05 | 145.5249
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 82 | 18614 | 0.0033384 | 1.4707e-05 | 227
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 286 | 352 | 64200 | 0.011433 | 6.2684e-05 | 182.3864
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | FUSE | 7 | 10 | 1019 | 0.00018349 | 1.8007e-06 | 101.9
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | METERING | 2 | 2 | 224 | 4.0336e-05 | 3.6014e-07 | 112
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, OH | 7 | 2131 | 105360 | 0.018972 | 0.00038373 | 49.4416
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 10 | 1304 | 83377 | 0.015014 | 0.00023481 | 63.9394
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | FUSE | 4 | 13 | 381 | 6.8332e-05 | 2.3316e-06 | 29.3077
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 1 | 104 | 1.8727e-05 | 1.8007e-07 | 104
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 1 | 125 | 2.2419e-05 | 1.7935e-07 | 125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | NONE | 1045 | 53616 | 3415622 | 0.60825 | 0.0095479 | 63.7053
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 78 | 1237 | 202313 | 0.036028 | 0.00022028 | 163.5513
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 85 | 5525 | 0.00099091 | 1.5245e-05 | 65
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | METERING | 1 | 1 | 161 | 2.9148e-05 | 1.8105e-07 | 161
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 1 | 113 | 2.0458e-05 | 1.8105e-07 | 113
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 5 | 1155 | 0.00021061 | 9.1171e-07 | 231
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 90 | 18450 | 0.0033642 | 1.6411e-05 | 205
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 2663 | 325072 | 0.059274 | 0.00048558 | 122.0698
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 1 | 1448 | 0.00026403 | 1.8234e-07 | 1448
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 3 | 705 | 0.00012855 | 5.4703e-07 | 235
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | ARRESTER | 1 | 3 | 207 | 3.7745e-05 | 5.4703e-07 | 69
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 1 | 587 | 0.00010703 | 1.8234e-07 | 587
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CABLE TERMINATOR | 1 | 1 | 190 | 3.4645e-05 | 1.8234e-07 | 190
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CUTOUT | 2 | 2 | 469 | 8.5518e-05 | 3.6468e-07 | 234.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CUTOUT | 1 | 53 | 2515 | 0.00045533 | 9.5955e-06 | 47.4528
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | POLE | 6 | 179 | 25577 | 0.0046306 | 3.2407e-05 | 142.8883
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | ERF | CONDUCTOR OVERHEAD | 1 | 1846 | 88608 | 0.016042 | 0.00033421 | 48
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CROSSARM | 1 | 83 | 5478 | 0.00098643 | 1.4946e-05 | 66
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | VA | NONE | 1 | 1110 | 6660 | 0.0012144 | 0.0002024 | 6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | INSULATOR | 1 | 2 | 312 | 5.6891e-05 | 3.6468e-07 | 156
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 41 | 4114 | 323782 | 0.057659 | 0.00073262 | 78.7025
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 3 | 645 | 0.00011568 | 5.3805e-07 | 215
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 15 | 960 | 118391 | 0.021083 | 0.00017096 | 123.324
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONN/CLAMP | 2 | 2 | 213 | 3.7931e-05 | 3.5616e-07 | 106.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 9 | 142 | 143579 | 0.025569 | 2.5287e-05 | 1011.1197
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 1177 | 56392 | 0.010042 | 0.0002096 | 47.9116
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 1780 | 221376 | 0.039423 | 0.00031698 | 124.3685
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | CUTOUT | 1 | 2 | 670 | 0.00012217 | 3.6468e-07 | 335
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CUTOUT | 1 | 1 | 75 | 1.3676e-05 | 1.8234e-07 | 75
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 203 | 3.6555e-05 | 1.8007e-07 | 203
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 1038 | 151111 | 0.027554 | 0.00018927 | 145.579
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | EQF | INSULATOR | 1 | 654 | 89598 | 0.016221 | 0.0001184 | 137
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 1 | 93 | 1.668e-05 | 1.7935e-07 | 93
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CABLE TERMINATOR | 1 | 2 | 386 | 6.9229e-05 | 3.587e-07 | 193
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | BREAKER | 1 | 819 | 109369 | 0.019615 | 0.00014689 | 133.5397
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | REGULATOR | 2 | 317 | 7504 | 0.0013513 | 5.7083e-05 | 23.6719
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 115 | 3182 | 385042 | 0.068568 | 0.00056665 | 121.0063
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 17 | 24 | 6392 | 0.0011383 | 4.2739e-06 | 266.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | PEDESTAL | 17 | 83 | 7495 | 0.0013347 | 1.4781e-05 | 90.3012
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 24 | 2208 | 125831 | 0.022408 | 0.0003932 | 56.9887
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 7 | 749 | 95232 | 0.016959 | 0.00013338 | 127.1455
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 19 | 1520 | 0.00027068 | 3.3835e-06 | 80
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 8 | 35 | 7815 | 0.0013917 | 6.2328e-06 | 223.2857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 2 | 962 | 0.00017131 | 3.5616e-07 | 481
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 11 | 99 | 100336 | 0.017868 | 1.763e-05 | 1013.4949
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 2 | 79 | 9633 | 0.0017154 | 1.4068e-05 | 121.9367
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | POLE | 2 | 17 | 8690 | 0.0015475 | 3.0274e-06 | 511.1765
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 455 | 8.1026e-05 | 1.7808e-07 | 455
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 12 | 4902 | 0.00087295 | 2.137e-06 | 408.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 17 | 5505 | 0.00099666 | 3.0778e-06 | 323.8235
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 162 | 2.933e-05 | 1.8105e-07 | 162
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 377 | 6.7887e-05 | 1.8007e-07 | 377
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 52 | 15236 | 0.0027584 | 9.4144e-06 | 293
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | POLE | 3 | 210 | 61941 | 0.011154 | 3.7815e-05 | 294.9571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | PEDESTAL | 1 | 23 | 1150 | 0.00020708 | 4.1417e-06 | 50
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | POLE HARDWARE | 1 | 1 | 55 | 9.9576e-06 | 1.8105e-07 | 55
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | POLE HARDWARE | 2 | 335 | 20905 | 0.0037644 | 6.0324e-05 | 62.403
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | POLE | 1 | 288 | 52039 | 0.0094215 | 5.2141e-05 | 180.691
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 1 | 232 | 4.2003e-05 | 1.8105e-07 | 232
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | FUSE | 724 | 6204 | 576941 | 0.10389 | 0.0011172 | 92.995
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONN/CLAMP | 466 | 569 | 77947 | 0.014036 | 0.00010246 | 136.9895
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 85 | 709 | 84247 | 0.015171 | 0.00012767 | 118.8251
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | NONE | 161 | 4051 | 639483 | 0.11515 | 0.00072947 | 157.8581
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | NONE | 53 | 2862 | 299607 | 0.053951 | 0.00051537 | 104.6845
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 22 | 437 | 138973 | 0.025025 | 7.8691e-05 | 318.016
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 45 | 225 | 60930 | 0.010972 | 4.0516e-05 | 270.8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CUTOUT | 14 | 356 | 106359 | 0.019152 | 6.4106e-05 | 298.7612
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | ARRESTER | 6 | 607 | 199092 | 0.035851 | 0.0001093 | 327.9934
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, OH | 4 | 39 | 7091 | 0.001293 | 7.1113e-06 | 181.8205
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 2292 | 316428 | 0.057698 | 0.00041793 | 138.0576
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 4 | 119 | 104951 | 0.019137 | 2.1699e-05 | 881.9412
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 55 | 1897 | 719959 | 0.13128 | 0.0003459 | 379.525
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 7 | 214 | 6177 | 0.0011263 | 3.9021e-05 | 28.8645
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CUTOUT | 1 | 3 | 216 | 3.9386e-05 | 5.4703e-07 | 72
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 2 | 240 | 4.3762e-05 | 3.6468e-07 | 120
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 1 | 348 | 6.3455e-05 | 1.8234e-07 | 348
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CUTOUT | 3 | 5 | 953 | 0.00017377 | 9.1171e-07 | 190.6
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 352 | 6.4184e-05 | 1.8234e-07 | 352
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | METERING | 10 | 24 | 2981 | 0.00054356 | 4.3762e-06 | 124.2083
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 210 | 889 | 90938 | 0.01631 | 0.00015944 | 102.2925
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | NONE | 37 | 1071 | 43717 | 0.0078407 | 0.00019208 | 40.8189
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | NONE | 9 | 10 | 795 | 0.00014157 | 1.7808e-06 | 79.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, OH | 10 | 6191 | 765717 | 0.13733 | 0.0011104 | 123.6823
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | SPLICE, OH | 1 | 1 | 355 | 6.3669e-05 | 1.7935e-07 | 355
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 7 | 198 | 16075 | 0.0028626 | 3.526e-05 | 81.1869
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 4 | 15 | 1479 | 0.00026338 | 2.6712e-06 | 98.6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 6 | 24 | 3115 | 0.00055472 | 4.2739e-06 | 129.7917
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | NONE | 39 | 1363 | 227707 | 0.04055 | 0.00024272 | 167.0631
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | FUSE | 1 | 1 | 74 | 1.3178e-05 | 1.7808e-07 | 74
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | NONE | 80 | 774 | 165267 | 0.029431 | 0.00013783 | 213.5233
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 145 | 2.5822e-05 | 1.7808e-07 | 145
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 4 | 11 | 13477 | 0.0024268 | 1.9808e-06 | 1225.1818
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 14 | 18 | 3292 | 0.00058624 | 3.2054e-06 | 182.8889
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 7 | 828 | 92068 | 0.016395 | 0.00014745 | 111.1932
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | NONE | 10 | 25 | 3324 | 0.00059194 | 4.452e-06 | 132.96
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | FUSE | 1 | 1 | 77 | 1.3712e-05 | 1.7808e-07 | 77
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 5 | 122 | 24741 | 0.0044059 | 2.1726e-05 | 202.7951
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 4 | 15 | 4833 | 0.00086066 | 2.6712e-06 | 322.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 58 | 696 | 0.00012394 | 1.0329e-05 | 12
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 8 | 763 | 257577 | 0.045869 | 0.00013587 | 337.5845
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONN/CLAMP | 1 | 1 | 34 | 6.0547e-06 | 1.7808e-07 | 34
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | FUSE | 5 | 11 | 676 | 0.00012038 | 1.9589e-06 | 61.4545
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 1 | 112 | 1.9945e-05 | 1.7808e-07 | 112
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 3 | 2549 | 114705 | 0.020572 | 0.00045716 | 45
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 51 | 9.0821e-06 | 1.7808e-07 | 51
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 4 | 46 | 9271 | 0.001651 | 8.1917e-06 | 201.5435
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 47 | 8.3698e-06 | 1.7808e-07 | 47
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 19 | 1387 | 0.000247 | 3.3835e-06 | 73
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 1 | 1396 | 0.0002486 | 1.7808e-07 | 1396
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 144 | 26352 | 0.0046928 | 2.5643e-05 | 183
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 385 | 63620 | 0.011329 | 6.8561e-05 | 165.2468
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 486 | 84660 | 0.015076 | 8.6547e-05 | 174.1975
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | NONE | 1 | 1 | 155 | 2.7911e-05 | 1.8007e-07 | 155
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | FUSE | 43 | 1054 | 175681 | 0.031508 | 0.00018904 | 166.6803
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | NONE | 32 | 610 | 56751 | 0.010178 | 0.0001094 | 93.0344
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 730 | 273020 | 0.048966 | 0.00013093 | 374
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONN/CLAMP | 9 | 14 | 2370 | 0.00042506 | 2.5109e-06 | 169.2857
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 1 | 56 | 9352 | 0.001684 | 1.0084e-05 | 167
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | NONE | 13 | 24 | 2140 | 0.00038381 | 4.3044e-06 | 89.1667
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 5 | 5 | 709 | 0.00012767 | 9.0036e-07 | 141.8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 19 | 1607 | 0.00028822 | 3.4077e-06 | 84.5789
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 5 | 38 | 1105 | 0.00019818 | 6.8153e-06 | 29.0789
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | POLE | 3 | 22 | 4011 | 0.00071937 | 3.9457e-06 | 182.3182
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | POLE | 2 | 31 | 1341 | 0.00024051 | 5.5599e-06 | 43.2581
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 133 | 2.3854e-05 | 1.7935e-07 | 133
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | SCO | NONE | 3 | 2303 | 36394 | 0.0065273 | 0.00041304 | 15.8029
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CUTOUT | 1 | 398 | 4776 | 0.00085658 | 7.1381e-05 | 12
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 1 | 80 | 1.4348e-05 | 1.7935e-07 | 80
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 7 | 378 | 6.7794e-05 | 1.2555e-06 | 54
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 797 | 6981 | 617709 | 0.11 | 0.0012432 | 88.4843
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 375 | 20250 | 0.0036061 | 6.678e-05 | 54
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | SWITCH, OH | 1 | 1740 | 432375 | 0.077547 | 0.00031207 | 248.4914
AEP Total | 2020 | 5484199 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 474 | 8.643e-05 | 1.8234e-07 | 474
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 1 | 44 | 7.8914e-06 | 1.7935e-07 | 44
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | SWITCH, OH | 1 | 498 | 4212 | 0.00076802 | 9.0806e-05 | 8.4578
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 1 | 285 | 5.1967e-05 | 1.8234e-07 | 285
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 151 | 2.7534e-05 | 1.8234e-07 | 151
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 2 | 168 | 3.0252e-05 | 3.6014e-07 | 84
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE | 317 | 57678 | 9406103 | 1.7029 | 0.010442 | 163.0796
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | FUSE | 48 | 1600 | 320367 | 0.058001 | 0.00028967 | 200.2294
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | NONE | 69 | 383 | 35006 | 0.0063377 | 6.9341e-05 | 91.3995
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | ARRESTER | 33 | 891 | 144681 | 0.026194 | 0.00016131 | 162.3805
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | REGULATOR | 2 | 81 | 13994 | 0.0025336 | 1.4665e-05 | 172.7654
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | NONE | 85 | 762 | 151224 | 0.027379 | 0.00013796 | 198.4567
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | FUSE | 3 | 59 | 8939 | 0.0016184 | 1.0682e-05 | 151.5085
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | FUSE | 32 | 356 | 54275 | 0.0098263 | 6.4453e-05 | 152.4579
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 466 | 8.4368e-05 | 1.8105e-07 | 466
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 1255 | 139335 | 0.025226 | 0.00022721 | 111.0239
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | NONE | 1283 | 14647 | 1250404 | 0.228 | 0.0026708 | 85.3693
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, OH | 12 | 25 | 7355 | 0.0013411 | 4.5586e-06 | 294.2
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | VA | POLE | 4 | 2830 | 65090 | 0.011869 | 0.00051603 | 23
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | NONE | 703 | 30473 | 7806452 | 1.4234 | 0.0055565 | 256.176
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 46 | 2504 | 459613 | 0.083807 | 0.00045658 | 183.5515
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | NONE | 19 | 819 | 374428 | 0.068274 | 0.00014934 | 457.177
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CROSSARM | 11 | 4853 | 546063 | 0.09957 | 0.00088491 | 112.5207
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 1 | 87 | 1.5864e-05 | 1.8234e-07 | 87
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 10 | 456 | 106725 | 0.01946 | 8.3148e-05 | 234.0461
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | JUMPER/RISER | 6 | 34 | 6368 | 0.0011612 | 6.1996e-06 | 187.2941
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 33 | 3344 | 0.00059975 | 5.9186e-06 | 101.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | METERING | 4 | 4 | 2700 | 0.00049232 | 7.2937e-07 | 675
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 1 | 122 | 2.2246e-05 | 1.8234e-07 | 122
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 8 | 1071 | 0.00019208 | 1.4348e-06 | 133.875
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 936 | 0.00016855 | 1.8007e-07 | 936
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 44 | 5508 | 0.00098786 | 7.8914e-06 | 125.1818
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 16 | 1268 | 0.00022742 | 2.8696e-06 | 79.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 21 | 16212 | 0.0029076 | 3.7664e-06 | 772
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 11 | 4456 | 657433 | 0.11708 | 0.00079352 | 147.5388
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 5 | 53 | 16357 | 0.0029129 | 9.4382e-06 | 308.6226
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 1 | 76 | 1.3631e-05 | 1.7935e-07 | 76
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CUTOUT | 3 | 49 | 14315 | 0.0025674 | 8.7882e-06 | 292.1429
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 99 | 4950 | 0.00088778 | 1.7756e-05 | 50
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | CONN/CLAMP | 1 | 1 | 49 | 8.7882e-06 | 1.7935e-07 | 49
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 1 | 62 | 1.1305e-05 | 1.8234e-07 | 62
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 2 | 1168 | 0.00021298 | 3.6468e-07 | 584
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 1 | 6 | 1080 | 0.00019553 | 1.0863e-06 | 180
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | ARRESTER | 1 | 9 | 909 | 0.00016457 | 1.6294e-06 | 101
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 2 | 3 | 233 | 4.2184e-05 | 5.4314e-07 | 77.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 1225 | 155575 | 0.028368 | 0.00022337 | 127
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | METERING | 1 | 1 | 87 | 1.5603e-05 | 1.7935e-07 | 87
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CUTOUT | 2 | 116 | 3006 | 0.00053531 | 2.0657e-05 | 25.9138
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 7 | 1575 | 203038 | 0.036157 | 0.00028048 | 128.913
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1709 | 121339 | 0.021608 | 0.00030434 | 71
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | SPLICE, OH | 1 | 1 | 49 | 8.7259e-06 | 1.7808e-07 | 49
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 2 | 260 | 4.6301e-05 | 3.5616e-07 | 130
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 5 | 773 | 74136 | 0.013202 | 0.00013766 | 95.9069
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 322 | 11592 | 0.0020874 | 5.7983e-05 | 36
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 2 | 222 | 3.9534e-05 | 3.5616e-07 | 111
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 3 | 17 | 2023 | 0.00036026 | 3.0274e-06 | 119
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | WW | POLE | 1 | 1 | 1524 | 0.00027139 | 1.7808e-07 | 1524
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 7 | 756 | 0.00013463 | 1.2466e-06 | 108
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | NONE | 3 | 26 | 28450 | 0.0050664 | 4.6301e-06 | 1094.2308
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | NONE | 2 | 21 | 2673 | 0.00048394 | 3.802e-06 | 127.2857
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | NONE | 4 | 4 | 1063 | 0.00019245 | 7.2419e-07 | 265.75
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | A | NONE | 1 | 646 | 202844 | 0.036724 | 0.00011696 | 314
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | NONE | 17 | 1456 | 220622 | 0.039943 | 0.0002636 | 151.5261
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | FUSE | 3 | 3 | 1960 | 0.00035485 | 5.4314e-07 | 653.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | NONE | 3 | 3 | 572 | 0.00010356 | 5.4314e-07 | 190.6667
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 234 | 4.2365e-05 | 1.8105e-07 | 234
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | NONE | 18 | 62 | 10862 | 0.0019665 | 1.1225e-05 | 175.1935
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 2 | 518 | 16252 | 0.0029424 | 9.3782e-05 | 31.3745
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 2 | 209 | 3.7839e-05 | 3.6209e-07 | 104.5
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | CROSSARM | 2 | 212 | 67474 | 0.012216 | 3.8382e-05 | 318.2736
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WH | NONE | 1 | 1 | 1803 | 0.00032643 | 1.8105e-07 | 1803
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | METERING | 4 | 5 | 856 | 0.00015498 | 9.0523e-07 | 171.2
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | JUMPER/RISER | 4 | 13 | 3970 | 0.00071875 | 2.3536e-06 | 305.3846
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CUTOUT | 719 | 24503 | 2984820 | 0.53748 | 0.0044123 | 121.8145
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | FUSE | 166 | 1465 | 220082 | 0.039631 | 0.00026381 | 150.2266
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 128 | 175 | 41769 | 0.0075214 | 3.1513e-05 | 238.68
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 311 | 1893 | 218608 | 0.039365 | 0.00034088 | 115.4823
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | NONE | 82 | 350 | 39238 | 0.0070657 | 6.3025e-05 | 112.1086
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 15 | 519 | 367673 | 0.066566 | 9.3963e-05 | 708.4258
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | NONE | 93 | 12541 | 1078135 | 0.19659 | 0.0022868 | 85.9688
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1137 | 30777 | 8649540 | 1.5772 | 0.0056119 | 281.0391
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | POLE | 309 | 7574 | 847150 | 0.15447 | 0.0013811 | 111.8497
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | ERF | NONE | 12 | 6531 | 227893 | 0.041554 | 0.0011909 | 34.894
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 6 | 4097 | 0.00074706 | 1.0941e-06 | 682.8333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | FUSE | 62 | 1861 | 404366 | 0.073733 | 0.00033934 | 217.2843
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | ABI | NONE | 3 | 3023 | 729638 | 0.13304 | 0.00055122 | 241.3622
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1363 | 241251 | 0.04399 | 0.00024853 | 177
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CUTOUT | 13 | 965 | 10512 | 0.0019168 | 0.00017596 | 10.8933
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABI | NONE | 1 | 10 | 640 | 0.0001167 | 1.8234e-06 | 64
AEP Total | 2020 | 5484199 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 80 | 1.4587e-05 | 1.8234e-07 | 80
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | NONE | 3 | 39 | 1644 | 0.00029977 | 7.1113e-06 | 42.1538
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 5 | 41 | 11917 | 0.002173 | 7.476e-06 | 290.6585
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | FUSE | 11 | 207 | 87799 | 0.016009 | 3.7745e-05 | 424.1498
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONN/CLAMP | 10 | 16 | 2908 | 0.00053025 | 2.9175e-06 | 181.75
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | A | CONDUCTOR OVERHEAD | 1 | 1282 | 161965 | 0.029533 | 0.00023376 | 126.3378
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | FUSE | 2 | 11 | 475 | 8.6612e-05 | 2.0058e-06 | 43.1818
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | FUSE | 2 | 3 | 306 | 5.5797e-05 | 5.4703e-07 | 102
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 1166 | 235532 | 0.042947 | 0.00021261 | 202
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 1212 | 131184 | 0.023623 | 0.00021825 | 108.2376
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | FUSE | 479 | 7743 | 736331 | 0.13206 | 0.0013887 | 95.0963
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 40 | 2077 | 464229 | 0.083595 | 0.00037401 | 223.5094
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CABLE TERMINATOR | 33 | 50 | 4292 | 0.00076977 | 8.9675e-06 | 85.84
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, OH | 9 | 1909 | 423766 | 0.076003 | 0.00034238 | 221.9832
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 19 | 17913 | 0.0032256 | 3.4214e-06 | 942.7895
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 12 | 63 | 5849 | 0.001049 | 1.1299e-05 | 92.8413
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | NONE | 8 | 45 | 5267 | 0.00094844 | 8.1032e-06 | 117.0444
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | RECLOSER, LINE/OCR/BR | 1 | 434 | 65895 | 0.011866 | 7.8151e-05 | 151.8318
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | FUSE | 7 | 303 | 13218 | 0.0023802 | 5.4562e-05 | 43.6238
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 103 | 10918 | 0.001966 | 1.8547e-05 | 106
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 1 | 332 | 5.9544e-05 | 1.7935e-07 | 332
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | CUTOUT | 1 | 1 | 63 | 1.1299e-05 | 1.7935e-07 | 63
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | POLE | 10 | 2521 | 351322 | 0.062563 | 0.00044894 | 139.3582
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 2 | 10 | 6429 | 0.0011723 | 1.8234e-06 | 642.9
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | TIR | CROSSARM | 1 | 580 | 56968 | 0.010388 | 0.00010576 | 98.2207
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | NONE | 1 | 1 | 111 | 2.024e-05 | 1.8234e-07 | 111
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CUTOUT | 1 | 1 | 276 | 4.9969e-05 | 1.8105e-07 | 276
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 16 | 158 | 29016 | 0.0051672 | 2.8137e-05 | 183.6456
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SWITCH, OH | 3 | 1104 | 7148 | 0.001282 | 0.000198 | 6.4746
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 17 | 81 | 20662 | 0.0036795 | 1.4424e-05 | 255.0864
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | NONE | 22 | 1326 | 149219 | 0.026573 | 0.00023613 | 112.5332
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | POLE | 4 | 50 | 120983 | 0.021545 | 8.904e-06 | 2419.66
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | NONE | 1 | 1 | 64 | 1.1397e-05 | 1.7808e-07 | 64
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 9 | 43 | 2160 | 0.00038465 | 7.6574e-06 | 50.2326
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 40 | 693 | 171948 | 0.03062 | 0.00012341 | 248.1212
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | METERING | 5 | 5 | 488 | 8.6903e-05 | 8.904e-07 | 97.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 14 | 3990 | 0.00071561 | 2.5109e-06 | 285
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | NONE | 686 | 4833 | 438761 | 0.078134 | 0.00086066 | 90.7844
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CUTOUT | 432 | 2229 | 99176 | 0.017661 | 0.00039694 | 44.4935
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 26 | 123 | 25351 | 0.0045145 | 2.1904e-05 | 206.1057
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | NONE | 78 | 666 | 115169 | 0.020509 | 0.0001186 | 172.9264
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | FUSE | 1 | 3 | 282 | 5.1055e-05 | 5.4314e-07 | 94
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 93 | 1.6837e-05 | 1.8105e-07 | 93
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CROSSARM | 1 | 1 | 78 | 1.389e-05 | 1.7808e-07 | 78
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | NONE | 5 | 7 | 933 | 0.00016615 | 1.2466e-06 | 133.2857
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 1 | 958 | 16286 | 0.0029002 | 0.0001706 | 17
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | TRANSFORMER, OH | 2 | 2 | 484 | 8.6191e-05 | 3.5616e-07 | 242
AEP Total | 2024 | 5615460 | PARTIAL POWER | FW | NONE | 1 | 1 | 16 | 2.8493e-06 | 1.7808e-07 | 16
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | ERF | NONE | 2 | 1059 | 20121 | 0.0035831 | 0.00018859 | 19
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 3 | 19 | 999 | 0.0001779 | 3.3835e-06 | 52.5789
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 6 | 2757 | 350543 | 0.062425 | 0.00049097 | 127.1465
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 14 | 3443 | 0.00061313 | 2.4931e-06 | 245.9286
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 2 | 2 | 197 | 3.5082e-05 | 3.5616e-07 | 98.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 15 | 525 | 9.3492e-05 | 2.6712e-06 | 35
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 188 | 3.3479e-05 | 1.7808e-07 | 188
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 28 | 3274 | 0.00058303 | 4.9862e-06 | 116.9286
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | FUSE | 1 | 4 | 384 | 6.9148e-05 | 7.2029e-07 | 96
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 2 | 280 | 5.042e-05 | 3.6014e-07 | 140
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 2 | 552 | 35360 | 0.0063673 | 9.94e-05 | 64.058
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE | 13 | 711 | 131967 | 0.023501 | 0.00012661 | 185.6076
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 47 | 15308 | 0.002726 | 8.3698e-06 | 325.7021
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 4 | 212 | 3.7753e-05 | 7.1232e-07 | 53
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CAPACITOR | 2 | 1845 | 51855 | 0.0092343 | 0.00032856 | 28.1057
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 23 | 1725 | 0.00030719 | 4.0958e-06 | 75
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 66 | 1.1753e-05 | 1.7808e-07 | 66
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 1 | 57 | 1.0151e-05 | 1.7808e-07 | 57
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | BREAKER | 1 | 1 | 108 | 1.9233e-05 | 1.7808e-07 | 108
AEP Total | 2022 | 5553337 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 1 | 12 | 1500 | 0.00027011 | 2.1609e-06 | 125
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 101 | 1.8114e-05 | 1.7935e-07 | 101
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CUTOUT | 1 | 1 | 55 | 9.9576e-06 | 1.8105e-07 | 55
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 2168 | 126707 | 0.02294 | 0.00039251 | 58.4442
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | FUSE | 106 | 2298 | 498056 | 0.090171 | 0.00041604 | 216.7346
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 13 | 26 | 3755 | 0.00067983 | 4.7072e-06 | 144.4231
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CROSSARM | 6 | 1495 | 102708 | 0.018595 | 0.00027066 | 68.701
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONN/CLAMP | 12 | 16 | 6248 | 0.0011312 | 2.8967e-06 | 390.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | ARRESTER | 5 | 38 | 3860 | 0.00069884 | 6.8798e-06 | 101.5789
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 4 | 257 | 72006 | 0.013036 | 4.6529e-05 | 280.179
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | NONE | 4 | 911 | 55761 | 0.0099299 | 0.00016223 | 61.2086
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 18 | 1859 | 129605 | 0.02308 | 0.00033105 | 69.7176
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 20 | 2080 | 0.00037927 | 3.6468e-06 | 104
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | INSULATOR | 1 | 1 | 132 | 2.3769e-05 | 1.8007e-07 | 132
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR UG | 1 | 21 | 3456 | 0.00062233 | 3.7815e-06 | 164.5714
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 1 | 118 | 2.1516e-05 | 1.8234e-07 | 118
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | SCO | BREAKER | 2 | 2674 | 16044 | 0.0028891 | 0.00048151 | 6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE | 28 | 2962 | 1595172 | 0.28725 | 0.00053337 | 538.5456
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | NONE | 7 | 7 | 791 | 0.00014244 | 1.2605e-06 | 113
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CABLE TERMINATOR | 37 | 41 | 6695 | 0.0012056 | 7.3829e-06 | 163.2927
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | POLE | 11 | 1650 | 200034 | 0.036021 | 0.00029712 | 121.2327
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONN/CLAMP | 3 | 3 | 378 | 6.8067e-05 | 5.4022e-07 | 126
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 19 | 1130 | 172432 | 0.030926 | 0.00020267 | 152.5947
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONN/CLAMP | 7 | 40 | 1405 | 0.000253 | 7.2029e-06 | 35.125
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CABLE TERMINATOR | 1 | 1 | 93 | 1.6747e-05 | 1.8007e-07 | 93
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CUTOUT | 2 | 3 | 287 | 5.1681e-05 | 5.4022e-07 | 95.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 5 | 145 | 2.611e-05 | 9.0036e-07 | 29
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 5 | 16 | 3357 | 0.0006045 | 2.8812e-06 | 209.8125
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 5 | 20 | 1183 | 0.00021217 | 3.587e-06 | 59.15
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | FUSE | 4 | 22 | 3618 | 0.00064889 | 3.9457e-06 | 164.4545
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | METERING | 9 | 9 | 867 | 0.0001555 | 1.6142e-06 | 96.3333
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | NONE | 3 | 3 | 373 | 6.6898e-05 | 5.3805e-07 | 124.3333
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | ERF | NONE | 6 | 9276 | 334680 | 0.060025 | 0.0016637 | 36.0802
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 2 | 278 | 4.9859e-05 | 3.587e-07 | 139
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | REGULATOR | 2 | 460 | 11740 | 0.0021056 | 8.2501e-05 | 25.5217
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | NONE | 2 | 2 | 252 | 4.5196e-05 | 3.587e-07 | 126
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 1 | 66 | 1.2035e-05 | 1.8234e-07 | 66
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 15 | 570 | 0.0001032 | 2.7157e-06 | 38
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 8 | 152 | 2.7519e-05 | 1.4484e-06 | 19
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 2 | 21 | 2279 | 0.00041038 | 3.7815e-06 | 108.5238
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | FUSE | 3 | 3 | 1553 | 0.00027965 | 5.4022e-07 | 517.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 7 | 49 | 2851 | 0.00051339 | 8.8235e-06 | 58.1837
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 1 | 222 | 3.9816e-05 | 1.7935e-07 | 222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 110 | 787 | 59714 | 0.010634 | 0.00014015 | 75.8755
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | OL | TRANSFORMER, POWER - NON LTC | 1 | 228 | 2736 | 0.0004907 | 4.0892e-05 | 12
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 4 | 4 | 376 | 6.6958e-05 | 7.1232e-07 | 94
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | NONE | 66 | 2482 | 741276 | 0.13201 | 0.00044199 | 298.6608
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | METERING | 1 | 1 | 20 | 3.587e-06 | 1.7935e-07 | 20
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 9 | 749 | 0.00013338 | 1.6027e-06 | 83.2222
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 8 | 10 | 1034 | 0.00018413 | 1.7808e-06 | 103.4
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1 | 310 | 5.5822e-05 | 1.8007e-07 | 310
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 1 | 206 | 3.7095e-05 | 1.8007e-07 | 206
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | FUSE | 3 | 45 | 9060 | 0.0016315 | 8.1032e-06 | 201.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 435 | 7.8331e-05 | 1.8007e-07 | 435
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | FUSE | 2 | 10 | 1211 | 0.00021807 | 1.8007e-06 | 121.1
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 2 | 18 | 7109 | 0.0012801 | 3.2413e-06 | 394.9444
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 25 | 3575 | 0.00064376 | 4.5018e-06 | 143
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | SCO | SWITCH, OH | 1 | 351 | 19305 | 0.0034763 | 6.3205e-05 | 55
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | BREAKER | 2 | 2111 | 361851 | 0.065159 | 0.00038013 | 171.4121
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 31 | 5146 | 0.00092294 | 5.5599e-06 | 166
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 61 | 7217 | 0.0012944 | 1.094e-05 | 118.3115
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | BREAKER | 3 | 2207 | 617109 | 0.11112 | 0.00039742 | 279.6144
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 112 | 2.0087e-05 | 3.587e-07 | 56
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 190 | 67545 | 0.012114 | 3.4077e-05 | 355.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CUTOUT | 1 | 53 | 12137 | 0.0021855 | 9.5438e-06 | 229
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | INSULATOR | 1 | 308 | 12628 | 0.0022739 | 5.5462e-05 | 41
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 31 | 38 | 5039 | 0.00089734 | 6.767e-06 | 132.6053
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | METERING | 11 | 21 | 6184 | 0.0011012 | 3.7397e-06 | 294.4762
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | INSULATOR | 3 | 5 | 315 | 5.6095e-05 | 8.904e-07 | 63
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | NONE | 6 | 884 | 36785 | 0.0065507 | 0.00015742 | 41.612
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 11 | 387 | 43866 | 0.0078116 | 6.8917e-05 | 113.3488
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 197 | 4555 | 699413 | 0.12455 | 0.00081115 | 153.5484
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | VA | POLE | 3 | 1361 | 948617 | 0.17174 | 0.0002464 | 697
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 1 | 39 | 6.9451e-06 | 1.7808e-07 | 39
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 241 | 32048 | 0.0057709 | 4.3397e-05 | 132.9793
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 1 | 76 | 1.376e-05 | 1.8105e-07 | 76
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 194 | 9606 | 0.0017228 | 3.4794e-05 | 49.5155
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 47 | 17898 | 2332425 | 0.41536 | 0.0031873 | 130.3176
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | FUSE | 525 | 6605 | 501684 | 0.08934 | 0.0011762 | 75.9552
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | NONE | 96 | 6335 | 1052046 | 0.18735 | 0.0011281 | 166.0688
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 87 | 1.5603e-05 | 1.7935e-07 | 87
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | NONE | 1389 | 19502 | 2279749 | 0.40887 | 0.0034977 | 116.8982
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UB | CUTOUT | 1 | 2 | 674 | 0.00012137 | 3.6014e-07 | 337
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 468 | 7116 | 932150 | 0.16718 | 0.0012763 | 130.9935
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 1 | 166 | 3.0054e-05 | 1.8105e-07 | 166
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 274 | 7036 | 1888473 | 0.34435 | 0.001283 | 268.4015
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 48 | 6532 | 671720 | 0.12248 | 0.0011911 | 102.8353
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | NONE | 78 | 559 | 106467 | 0.019413 | 0.00010193 | 190.4597
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | POLE | 3 | 2048 | 299111 | 0.054541 | 0.00037344 | 146.0503
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | FUSE | 22 | 60 | 8050 | 0.0014679 | 1.0941e-05 | 134.1667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 27 | 325 | 24064 | 0.0043879 | 5.9261e-05 | 74.0431
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 1 | 109 | 1.9875e-05 | 1.8234e-07 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | PEDESTAL | 3 | 26 | 1272 | 0.00023194 | 4.7409e-06 | 48.9231
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | NONE | 6 | 2067 | 424307 | 0.077369 | 0.0003769 | 205.2767
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | NONE | 20 | 2452 | 313169 | 0.056167 | 0.00043977 | 127.7198
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | NONE | 45 | 2619 | 120405 | 0.021595 | 0.00046972 | 45.9737
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | FUSE | 11 | 347 | 39491 | 0.0070827 | 6.2235e-05 | 113.8069
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | NONE | 6 | 5620 | 400726 | 0.07187 | 0.0010079 | 71.3036
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE | 19 | 2541 | 1321924 | 0.23709 | 0.00045573 | 520.2377
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | NONE | 205 | 9888 | 2185648 | 0.38922 | 0.0017609 | 221.0405
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 2 | 306 | 5.4881e-05 | 3.587e-07 | 153
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ERF | NONE | 11 | 12139 | 1008963 | 0.18096 | 0.0021771 | 83.1175
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 43 | 948 | 163784 | 0.029493 | 0.00017071 | 172.7679
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 24 | 2845 | 517499 | 0.093187 | 0.0005123 | 181.8977
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR UG | 316 | 421 | 111505 | 0.020079 | 7.581e-05 | 264.8575
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE | 66 | 1705 | 897923 | 0.16169 | 0.00030702 | 526.6411
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | METERING | 29 | 50 | 12060 | 0.0021717 | 9.0036e-06 | 241.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | NONE | 35 | 1265 | 31985 | 0.0057596 | 0.00022779 | 25.2846
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 11 | 239 | 26657 | 0.0048002 | 4.3037e-05 | 111.5356
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | METERING | 2 | 6 | 436 | 7.8511e-05 | 1.0804e-06 | 72.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 5 | 884 | 0.00015918 | 9.0036e-07 | 176.8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 1 | 269 | 4.8439e-05 | 1.8007e-07 | 269
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | NONE | 34 | 72 | 21974 | 0.0039569 | 1.2965e-05 | 305.1944
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 7 | 35 | 6238 | 0.0011233 | 6.3025e-06 | 178.2286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | FUSE | 372 | 5122 | 559256 | 0.10198 | 0.00093396 | 109.187
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 100 | 3195 | 242817 | 0.044276 | 0.00058258 | 75.9991
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | METERING | 11 | 11 | 908 | 0.00016557 | 2.0058e-06 | 82.5455
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | NONE | 1 | 69 | 8211 | 0.0014972 | 1.2582e-05 | 119
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 73 | 2052 | 114413 | 0.020862 | 0.00037417 | 55.7568
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | FUSE | 22 | 84 | 16414 | 0.002993 | 1.5317e-05 | 195.4048
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CUTOUT | 37 | 459 | 55236 | 0.010072 | 8.3695e-05 | 120.3399
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | NONE | 2 | 2 | 1605 | 0.00029266 | 3.6468e-07 | 802.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | UG | NONE | 2 | 3 | 597 | 0.00010886 | 5.4703e-07 | 199
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | PEDESTAL | 1 | 12 | 4116 | 0.00075052 | 2.1881e-06 | 343
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 30 | 6000 | 0.0010941 | 5.4703e-06 | 200
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 2 | 7 | 3945 | 0.00071934 | 1.2764e-06 | 563.5714
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 1 | 31 | 5.6526e-06 | 1.8234e-07 | 31
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | FUSE | 9 | 16 | 1897 | 0.0003459 | 2.9175e-06 | 118.5625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 3 | 37 | 22508 | 0.0041042 | 6.7467e-06 | 608.3243
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | NONE | 5 | 112 | 15660 | 0.0028086 | 2.0087e-05 | 139.8214
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | EQF | INSULATOR | 6 | 2181 | 131914 | 0.023659 | 0.00039116 | 60.4833
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | TRANSFORMER, OH | 3 | 13 | 5360 | 0.00096519 | 2.3409e-06 | 412.3077
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 20 | 217 | 11491 | 0.0020609 | 3.8919e-05 | 52.9539
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | RELAY | 2 | 2 | 396 | 7.1023e-05 | 3.587e-07 | 198
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 3 | 43 | 20102 | 0.0036198 | 7.7431e-06 | 467.4884
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 15 | 542 | 22524 | 0.0040559 | 9.7599e-05 | 41.5572
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONN/CLAMP | 7 | 10 | 2019 | 0.00036357 | 1.8007e-06 | 201.9
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 3 | 108 | 24744 | 0.0044378 | 1.937e-05 | 229.1111
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CROSSARM | 2 | 2 | 387 | 6.9688e-05 | 3.6014e-07 | 193.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 39 | 4961 | 0.00089334 | 7.0228e-06 | 127.2051
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | INSULATOR | 3 | 2204 | 98319 | 0.017704 | 0.00039688 | 44.6093
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | FUSE | 1 | 8 | 1376 | 0.00024778 | 1.4406e-06 | 172
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | POLE HARDWARE | 1 | 1 | 103 | 1.8473e-05 | 1.7935e-07 | 103
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CROSSARM | 8 | 1569 | 252986 | 0.045373 | 0.0002814 | 161.2403
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | JUMPER/RISER | 2 | 533 | 84626 | 0.015239 | 9.5978e-05 | 158.773
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | SPLICE, OH | 1 | 1 | 248 | 4.4164e-05 | 1.7808e-07 | 248
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | CONN/CLAMP | 3 | 2191 | 282464 | 0.050301 | 0.00039017 | 128.9201
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 3 | 3 | 291 | 5.1821e-05 | 5.3424e-07 | 97
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 2 | 216 | 3.874e-05 | 3.587e-07 | 108
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1 | 31 | 5.5205e-06 | 1.7808e-07 | 31
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | NONE | 2 | 2 | 1012 | 0.00018022 | 3.5616e-07 | 506
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 44 | 572 | 0.00010186 | 7.8355e-06 | 13
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 8 | 4032 | 0.00071802 | 1.4246e-06 | 504
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | FUSE | 1 | 28 | 6664 | 0.0011867 | 4.9862e-06 | 238
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 1 | 1 | 83 | 1.4781e-05 | 1.7808e-07 | 83
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 2 | 284 | 5.114e-05 | 3.6014e-07 | 142
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | INSULATOR | 1 | 26 | 650 | 0.00011575 | 4.6301e-06 | 25
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | POLE | 1 | 4 | 308 | 5.4849e-05 | 7.1232e-07 | 77
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 41 | 2665 | 0.00047458 | 7.3013e-06 | 65
AEP Total | 2025 | 5615460 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 41 | 7.3013e-06 | 1.7808e-07 | 41
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, GROUNDING | 1 | 1 | 53 | 9.4382e-06 | 1.7808e-07 | 53
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | REGULATOR | 1 | 13 | 2895 | 0.00051554 | 2.315e-06 | 222.6923
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 1 | 2 | 92 | 1.6383e-05 | 3.5616e-07 | 46
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 96 | 1.7505e-05 | 1.8234e-07 | 96
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 1 | 119 | 38318 | 0.006987 | 2.1699e-05 | 322
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 2 | 3318 | 0.00060501 | 3.6468e-07 | 1659
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | CROSSARM | 1 | 21 | 6132 | 0.0011181 | 3.8292e-06 | 292
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 304 | 93766 | 0.017097 | 5.5432e-05 | 308.4408
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | NONE | 1 | 330 | 54450 | 0.0098049 | 5.9424e-05 | 165
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1502 | 46318 | 13081910 | 2.3684 | 0.0083857 | 282.4368
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | NONE | 28 | 554 | 43024 | 0.0077893 | 0.0001003 | 77.6606
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | FUSE | 167 | 2202 | 349751 | 0.063321 | 0.00039866 | 158.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 100 | 5466 | 488141 | 0.088376 | 0.0009896 | 89.305
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 13 | 224 | 44777 | 0.0081067 | 4.0554e-05 | 199.8973
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | NONE | 25 | 139 | 25979 | 0.0047034 | 2.5165e-05 | 186.8993
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONN/CLAMP | 14 | 14 | 1967 | 0.00035612 | 2.5346e-06 | 140.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 5 | 404 | 7.3143e-05 | 9.0523e-07 | 80.8
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CABLE TERMINATOR | 11 | 26 | 2939 | 0.0005321 | 4.7072e-06 | 113.0385
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 6 | 7578 | 0.001372 | 1.0863e-06 | 1263
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 17 | 1377 | 0.0002493 | 3.0778e-06 | 81
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 5 | 5 | 772 | 0.00013977 | 9.0523e-07 | 154.4
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 516 | 9.342e-05 | 1.8105e-07 | 516
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONN/CLAMP | 611 | 830 | 124284 | 0.022662 | 0.00015134 | 149.7398
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | NONE | 28 | 1826 | 460136 | 0.083902 | 0.00033296 | 251.9912
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 10 | 760 | 0.00013858 | 1.8234e-06 | 76
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | SWITCH, OH | 2 | 46 | 1939 | 0.00035356 | 8.3877e-06 | 42.1522
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 1 | 1 | 145 | 2.6252e-05 | 1.8105e-07 | 145
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | R | NONE | 2 | 2 | 301 | 5.4885e-05 | 3.6468e-07 | 150.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 56 | 5432 | 0.00098344 | 1.0139e-05 | 97
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 4 | 28 | 5570 | 0.0010084 | 5.0693e-06 | 198.9286
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | ARRESTER | 1 | 342 | 23256 | 0.0042104 | 6.1918e-05 | 68
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 6 | 989 | 72096 | 0.013053 | 0.00017905 | 72.8979
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | ARRESTER | 4 | 57 | 9711 | 0.0017581 | 1.032e-05 | 170.3684
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 1 | 1481 | 0.00026813 | 1.8105e-07 | 1481
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | NONE | 1 | 1 | 84 | 1.5208e-05 | 1.8105e-07 | 84
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 2 | 64 | 5082 | 0.00092008 | 1.1587e-05 | 79.4062
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 10 | 3400 | 0.00061556 | 1.8105e-06 | 340
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | POLE | 1 | 1504 | 665155 | 0.12042 | 0.00027229 | 442.2573
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | FUSE | 49 | 694 | 33439 | 0.0060214 | 0.00012497 | 48.183
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | NONE | 259 | 2426 | 182850 | 0.032926 | 0.00043685 | 75.371
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | NONE | 60 | 234 | 20650 | 0.0037185 | 4.2137e-05 | 88.2479
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | NONE | 220 | 7765 | 1534925 | 0.2764 | 0.0013983 | 197.6722
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | JUMPER/RISER | 8 | 43 | 3657 | 0.00065852 | 7.7431e-06 | 85.0465
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | CONDUCTOR UG | 20 | 44 | 18431 | 0.0033189 | 7.9232e-06 | 418.8864
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CUTOUT | 4 | 14 | 24836 | 0.0044723 | 2.521e-06 | 1774
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONN/CLAMP | 42 | 808 | 106855 | 0.019242 | 0.0001455 | 132.2463
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 16 | 279 | 44331 | 0.0079828 | 5.024e-05 | 158.8925
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | METERING | 23 | 24 | 2322 | 0.00041813 | 4.3217e-06 | 96.75
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | NONE | 1 | 1 | 207 | 3.7275e-05 | 1.8007e-07 | 207
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 2 | 2 | 1369 | 0.00024785 | 3.6209e-07 | 684.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | POLE | 1 | 567 | 6804 | 0.0012252 | 0.0001021 | 12
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | CUTOUT | 1 | 2 | 156 | 2.8091e-05 | 3.6014e-07 | 78
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | FUSE | 1 | 8 | 2056 | 0.0003749 | 1.4587e-06 | 257
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | GUY/ANCHOR | 1 | 914 | 16452 | 0.0029999 | 0.00016666 | 18
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 56 | 5936 | 0.0010824 | 1.0211e-05 | 106
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | CUTOUT | 3 | 3265 | 1294248 | 0.23306 | 0.00058793 | 396.4006
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | SCO | TRANSFORMER, POWER - LTC | 4 | 1839 | 446877 | 0.07958 | 0.00032749 | 243
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 4 | 4 | 633 | 0.00011272 | 7.1232e-07 | 158.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 7 | 2548 | 0.00045375 | 1.2466e-06 | 364
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 6 | 3780 | 0.00067314 | 1.0685e-06 | 630
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 25 | 2199 | 0.0003916 | 4.452e-06 | 87.96
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1 | 560 | 9.9725e-05 | 1.7808e-07 | 560
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 1 | 10 | 15420 | 0.002746 | 1.7808e-06 | 1542
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 6 | 163 | 31741 | 0.0056524 | 2.9027e-05 | 194.7301
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 4 | 4 | 791 | 0.00014244 | 7.2029e-07 | 197.75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | NONE | 6 | 132 | 16544 | 0.0029791 | 2.3769e-05 | 125.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | PEDESTAL | 115 | 472 | 23708 | 0.0042219 | 8.4054e-05 | 50.2288
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | NONE | 25 | 27 | 5447 | 0.00097 | 4.8082e-06 | 201.7407
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 40 | 2168 | 534172 | 0.095125 | 0.00038608 | 246.3893
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 5 | 167 | 101444 | 0.018065 | 2.9739e-05 | 607.4491
AEP Total | 2023 | 5575683 | PARTIAL POWER | UG | NONE | 5 | 6 | 1097 | 0.00019675 | 1.0761e-06 | 182.8333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 48 | 989 | 223289 | 0.039763 | 0.00017612 | 225.7725
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | NONE | 4 | 637 | 44849 | 0.0079867 | 0.00011344 | 70.4066
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | FUSE | 22 | 48 | 3979 | 0.00070858 | 8.5478e-06 | 82.8958
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 2 | 289 | 5.2322e-05 | 3.6209e-07 | 144.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 1 | 66 | 1.1949e-05 | 1.8105e-07 | 66
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | SCO | INSULATOR | 3 | 1296 | 405648 | 0.073967 | 0.00023632 | 313
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | FUSE | 3 | 3 | 514 | 9.2557e-05 | 5.4022e-07 | 171.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 13 | 2522 | 0.0004566 | 2.3536e-06 | 194
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | METERING | 1 | 1 | 149 | 2.7169e-05 | 1.8234e-07 | 149
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | BREAKER | 1 | 2 | 198 | 3.5654e-05 | 3.6014e-07 | 99
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CROSSARM | 36 | 303 | 13433 | 0.0023921 | 5.3958e-05 | 44.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 4 | 35 | 1206 | 0.00021476 | 6.2328e-06 | 34.4571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 167 | 20708 | 0.0037289 | 3.0072e-05 | 124
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 17 | 81 | 19478 | 0.0034686 | 1.4424e-05 | 240.4691
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | SPLICE, OH | 1 | 34 | 1428 | 0.0002543 | 6.0547e-06 | 42
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | NONE | 2 | 2 | 535 | 9.5273e-05 | 3.5616e-07 | 267.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 551 | 7714 | 0.0013737 | 9.8122e-05 | 14
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 55 | 3726 | 0.00066353 | 9.7944e-06 | 67.7455
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 2 | 306 | 5.4492e-05 | 3.5616e-07 | 153
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | ARRESTER | 1 | 1 | 12 | 2.137e-06 | 1.7808e-07 | 12
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 69 | 1.2288e-05 | 1.7808e-07 | 69
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 3 | 591 | 0.00010525 | 5.3424e-07 | 197
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | FUSE | 3 | 132 | 6901 | 0.0012289 | 2.3507e-05 | 52.2803
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | REGULATOR | 1 | 175 | 57916 | 0.010314 | 3.1164e-05 | 330.9486
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CROSSARM | 1 | 31 | 5177 | 0.00094398 | 5.6526e-06 | 167
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 115 | 14795 | 0.0026978 | 2.0969e-05 | 128.6522
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 91 | 69797 | 0.012429 | 1.6205e-05 | 767
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 49 | 814 | 71358 | 0.012919 | 0.00014737 | 87.6634
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | NONE | 5 | 6 | 1025 | 0.00018557 | 1.0863e-06 | 170.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | FUSE | 52 | 159 | 13616 | 0.0024651 | 2.8786e-05 | 85.6352
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CUTOUT | 4 | 13 | 1124 | 0.0002035 | 2.3536e-06 | 86.4615
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 23 | 448 | 305395 | 0.055291 | 8.1109e-05 | 681.6853
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | INSULATOR | 48 | 7978 | 1370255 | 0.24808 | 0.0014444 | 171.7542
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CUTOUT | 7 | 635 | 564355 | 0.10217 | 0.00011496 | 888.748
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | POLE | 270 | 6513 | 844563 | 0.15291 | 0.0011792 | 129.6734
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 1 | 2 | 1542 | 0.00027917 | 3.6209e-07 | 771
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 1 | 75 | 1.3578e-05 | 1.8105e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | CUTOUT | 1 | 37 | 814 | 0.00014658 | 6.6627e-06 | 22
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 2 | 1168 | 0.00021032 | 3.6014e-07 | 584
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 5 | 1763 | 0.00031395 | 8.904e-07 | 352.6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 3 | 3 | 66 | 1.1753e-05 | 5.3424e-07 | 22
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 6 | 102 | 1.8164e-05 | 1.0685e-06 | 17
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | NONE | 2 | 2 | 367 | 6.6086e-05 | 3.6014e-07 | 183.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 9 | 216 | 3.8896e-05 | 1.6206e-06 | 24
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 8 | 195 | 34009 | 0.0060995 | 3.4973e-05 | 174.4051
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | REGULATOR | 1 | 1055 | 13715 | 0.0024697 | 0.00018998 | 13
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 379 | 18468 | 3262729 | 0.58517 | 0.0033122 | 176.6693
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | NONE | 5 | 34 | 2760 | 0.000497 | 6.1224e-06 | 81.1765
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 33 | 324 | 38369 | 0.0068815 | 5.8109e-05 | 118.4228
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 8 | 96 | 28624 | 0.0051544 | 1.7287e-05 | 298.1667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | NONE | 24 | 632 | 127450 | 0.02295 | 0.00011381 | 201.6614
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE | 26 | 1662 | 390387 | 0.070016 | 0.00029808 | 234.8899
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 42 | 1921 | 172867 | 0.031004 | 0.00034453 | 89.988
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 8 | 8 | 1761 | 0.00031584 | 1.4348e-06 | 220.125
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 2 | 20 | 2267 | 0.00040822 | 3.6014e-06 | 113.35
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | OTHER EQUIPMENT | 1 | 15 | 1290 | 0.00023229 | 2.7011e-06 | 86
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | NONE | 7 | 17 | 3812 | 0.00068368 | 3.049e-06 | 224.2353
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 9 | 11 | 5064 | 0.00091188 | 1.9808e-06 | 460.3636
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 1 | 105 | 22100 | 0.0039796 | 1.8908e-05 | 210.4762
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 238 | 4.2685e-05 | 1.7935e-07 | 238
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | NONE | 11 | 198 | 49391 | 0.0088583 | 3.5511e-05 | 249.4495
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | NONE | 2264 | 17797 | 1384961 | 0.24663 | 0.0031693 | 77.8199
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 10 | 7800 | 0.0013989 | 1.7935e-06 | 780
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | NONE | 29 | 400 | 192334 | 0.034495 | 7.174e-05 | 480.835
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CROSSARM | 15 | 8231 | 776201 | 0.13921 | 0.0014762 | 94.3022
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 1823 | 285087 | 0.05113 | 0.00032696 | 156.3834
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | FUSE | 2 | 206 | 32536 | 0.0058353 | 3.6946e-05 | 157.9417
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, UG | 3 | 3 | 330 | 5.9186e-05 | 5.3805e-07 | 110
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 4 | 1003 | 369588 | 0.066286 | 0.00017989 | 368.4826
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 19 | 4997 | 0.00089621 | 3.4077e-06 | 263
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 2 | 7 | 603 | 0.00010815 | 1.2555e-06 | 86.1429
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 199 | 65159 | 0.011686 | 3.5691e-05 | 327.4322
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 88 | 7845 | 981932 | 0.17486 | 0.001397 | 125.1666
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CIRCUIT SWITCHER | 2 | 24 | 31518 | 0.0057471 | 4.3762e-06 | 1313.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 2 | 3 | 1238 | 0.00022574 | 5.4703e-07 | 412.6667
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 11 | 2805 | 0.00051147 | 2.0058e-06 | 255
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | POLE | 2 | 816 | 212721 | 0.038788 | 0.00014879 | 260.6875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CUTOUT | 5 | 382 | 27338 | 0.0049031 | 6.8512e-05 | 71.5654
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | METERING | 3 | 3 | 1316 | 0.00023697 | 5.4022e-07 | 438.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONDUCTOR UG | 2 | 2 | 364 | 6.5283e-05 | 3.587e-07 | 182
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 4 | 731 | 0.00013111 | 7.174e-07 | 182.75
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | STATIC WIRE | 5 | 2929 | 65206 | 0.011695 | 0.00052532 | 22.2622
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | POLE | 786 | 3581 | 386425 | 0.068814 | 0.0006377 | 107.9098
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 180 | 9496 | 1701302 | 0.30297 | 0.001691 | 179.1599
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 143 | 163 | 30946 | 0.0055109 | 2.9027e-05 | 189.8528
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 21 | 7292 | 771850 | 0.13745 | 0.0012986 | 105.8489
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 3 | 58 | 5641 | 0.0010045 | 1.0329e-05 | 97.2586
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 10 | 10 | 1943 | 0.00034601 | 1.7808e-06 | 194.3
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 3 | 198 | 3.5654e-05 | 5.4022e-07 | 66
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 1043 | 23989 | 0.0043431 | 0.00018883 | 23
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | NONE | 12 | 12 | 1114 | 0.00019838 | 2.137e-06 | 92.8333
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | NONE | 5 | 5 | 481 | 8.5656e-05 | 8.904e-07 | 96.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE | 6 | 864 | 262711 | 0.046784 | 0.00015386 | 304.0637
AEP Total | 2024 | 5615460 | PARTIAL POWER | OU | NONE | 2 | 2 | 178 | 3.1698e-05 | 3.5616e-07 | 89
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 84 | 1.4959e-05 | 1.7808e-07 | 84
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 561 | 59466 | 0.01059 | 9.9903e-05 | 106
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 200 | 3.6468e-05 | 1.8234e-07 | 200
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 121 | 2.2063e-05 | 1.8234e-07 | 121
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CUTOUT | 5 | 190 | 44392 | 0.0080945 | 3.4645e-05 | 233.6421
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | FUSE | 3 | 13 | 1500 | 0.00027351 | 2.3704e-06 | 115.3846
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CUTOUT | 4 | 2292 | 208572 | 0.038031 | 0.00041793 | 91
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | CONN/CLAMP | 2 | 22 | 8444 | 0.0015397 | 4.0115e-06 | 383.8182
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | POLE | 1 | 52 | 5148 | 0.0009387 | 9.4818e-06 | 99
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 242 | 56551 | 0.010238 | 4.3813e-05 | 233.6818
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | INSULATOR | 2 | 1284 | 457692 | 0.083456 | 0.00023413 | 356.4579
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 61 | 55435 | 0.010036 | 1.1044e-05 | 908.7705
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | NONE | 44 | 1180 | 59911 | 0.010847 | 0.00021363 | 50.772
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 30 | 453 | 70170 | 0.012704 | 8.2014e-05 | 154.9007
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | JUMPER/RISER | 2 | 86 | 7018 | 0.0012706 | 1.557e-05 | 81.6047
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | NONE | 10 | 7057 | 145826 | 0.026401 | 0.0012776 | 20.664
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 10 | 122 | 430099 | 0.077868 | 2.2088e-05 | 3525.4016
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 6 | 6 | 901 | 0.00016312 | 1.0863e-06 | 150.1667
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | SCO | NONE | 9 | 8098 | 824816 | 0.14933 | 0.0014661 | 101.8543
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 80 | 10710 | 0.001939 | 1.4484e-05 | 133.875
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | METERING | 10 | 10 | 1513 | 0.00027392 | 1.8105e-06 | 151.3
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 3 | 35 | 54788 | 0.0099192 | 6.3366e-06 | 1565.3714
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 4 | 22 | 3388 | 0.00061339 | 3.983e-06 | 154
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | NONE | 1 | 1 | 64 | 1.1587e-05 | 1.8105e-07 | 64
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | BREAKER | 1 | 9 | 2385 | 0.00042947 | 1.6206e-06 | 265
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | FUSE | 3 | 12 | 1204 | 0.00021681 | 2.1609e-06 | 100.3333
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | EQF | INSULATOR | 2 | 813 | 380884 | 0.068587 | 0.0001464 | 468.492
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | METERING | 3 | 3 | 800 | 0.00014406 | 5.4022e-07 | 266.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 15 | 349 | 118564 | 0.02135 | 6.2845e-05 | 339.7249
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 1 | 377 | 6.7887e-05 | 1.8007e-07 | 377
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | FUSE | 1 | 8 | 424 | 7.635e-05 | 1.4406e-06 | 53
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | NONE | 25 | 27 | 6442 | 0.0011554 | 4.8425e-06 | 238.5926
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 16 | 635 | 237720 | 0.042635 | 0.00011389 | 374.3622
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 2 | 50 | 8.9675e-06 | 3.587e-07 | 25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 239 | 12213 | 2821485 | 0.50245 | 0.0021749 | 231.0231
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 6 | 798 | 0.00014211 | 1.0685e-06 | 133
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | FUSE | 3 | 19 | 3115 | 0.00055472 | 3.3835e-06 | 163.9474
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 4 | 4 | 521 | 9.278e-05 | 7.1232e-07 | 130.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 2 | 48 | 4672 | 0.0008519 | 8.7524e-06 | 97.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | SCO | SWITCH, OH | 1 | 238 | 2142 | 0.00039058 | 4.3397e-05 | 9
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | ARRESTER | 5 | 22 | 2401 | 0.00043062 | 3.9457e-06 | 109.1364
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 50 | 8.9675e-06 | 1.7935e-07 | 50
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 232 | 29464 | 0.0052844 | 4.1609e-05 | 127
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | FUSE | 2 | 8 | 1004 | 0.00018007 | 1.4348e-06 | 125.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 2 | 137 | 19571 | 0.0035101 | 2.4571e-05 | 142.854
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 20 | 2082 | 0.00037341 | 3.587e-06 | 104.1
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | NONE | 5 | 5 | 345 | 6.1876e-05 | 8.9675e-07 | 69
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | CONDUCTOR OVERHEAD | 1 | 1 | 124 | 2.2239e-05 | 1.7935e-07 | 124
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | CUTOUT | 1 | 4 | 452 | 8.1066e-05 | 7.174e-07 | 113
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | FW | NONE | 1 | 1499 | 113924 | 0.020432 | 0.00026885 | 76
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 1018 | 82641 | 0.014962 | 0.00018431 | 81.1798
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 49 | 821 | 197123 | 0.035104 | 0.0001462 | 240.1011
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 6 | 1593 | 512021 | 0.091181 | 0.00028368 | 321.4193
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 27 | 267 | 31942 | 0.0056882 | 4.7547e-05 | 119.633
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | SCO | NONE | 1 | 709 | 7090 | 0.0012836 | 0.00012836 | 10
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 53 | 9.5438e-06 | 1.8007e-07 | 53
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | BREAKER | 2 | 549 | 118584 | 0.021354 | 9.8859e-05 | 216
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CUTOUT | 6 | 553 | 145505 | 0.026343 | 0.00010012 | 263.1193
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 135 | 325 | 46423 | 0.0083595 | 5.8523e-05 | 142.84
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | NONE | 271 | 16917 | 4056388 | 0.73044 | 0.0030463 | 239.7818
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE | 67 | 9146 | 1909784 | 0.3439 | 0.0016469 | 208.8108
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONN/CLAMP | 1 | 1 | 116 | 2.1001e-05 | 1.8105e-07 | 116
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | POLE | 3 | 89 | 19405 | 0.0035132 | 1.6113e-05 | 218.0337
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | EQF | INSULATOR | 1 | 1186 | 520654 | 0.094263 | 0.00021472 | 439
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 2 | 491 | 8.8894e-05 | 3.6209e-07 | 245.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CUTOUT | 878 | 33063 | 5042742 | 0.9195 | 0.0060288 | 152.5192
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, OH | 24 | 117 | 48930 | 0.008922 | 2.1334e-05 | 418.2051
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 51 | 658 | 57534 | 0.010491 | 0.00011998 | 87.4377
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | SPLICE, OH | 3 | 3 | 1016 | 0.00018526 | 5.4703e-07 | 338.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONN/CLAMP | 38 | 141 | 21148 | 0.0038562 | 2.571e-05 | 149.9858
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | POLE | 13 | 811 | 131733 | 0.02402 | 0.00014788 | 162.4328
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 161 | 2.9357e-05 | 3.6468e-07 | 80.5
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | REGULATOR | 1 | 56 | 2016 | 0.0003676 | 1.0211e-05 | 36
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 176 | 30153 | 0.0054982 | 3.2092e-05 | 171.3239
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONN/CLAMP | 6 | 59 | 2033 | 0.0003707 | 1.0758e-05 | 34.4576
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 4 | 30 | 8408 | 0.001514 | 5.4022e-06 | 280.2667
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | NONE | 6 | 17 | 1706 | 0.0003072 | 3.0612e-06 | 100.3529
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | JUMPER/RISER | 3 | 1402 | 156104 | 0.02811 | 0.00025246 | 111.3438
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CUTOUT | 6 | 153 | 57633 | 0.010509 | 2.7898e-05 | 376.6863
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | SPLICE, UG | 2 | 4 | 3748 | 0.00068342 | 7.2937e-07 | 937
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 40 | 3452 | 0.00062944 | 7.2937e-06 | 86.3
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE | 10 | 399 | 260359 | 0.047474 | 7.2754e-05 | 652.5288
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 1 | 382 | 6.9655e-05 | 1.8234e-07 | 382
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CROSSARM | 2 | 338 | 20481 | 0.0037345 | 6.1632e-05 | 60.5947
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | GC | NONE | 4 | 2372 | 729177 | 0.13201 | 0.00042944 | 307.4102
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 39 | 14235 | 0.0025633 | 7.0228e-06 | 365
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | NONE | 5 | 5 | 440 | 7.8355e-05 | 8.904e-07 | 88
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | FO | NONE | 1 | 19 | 1957 | 0.0003485 | 3.3835e-06 | 103
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 1 | 104 | 1.852e-05 | 1.7808e-07 | 104
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 3 | 45 | 3498 | 0.00062292 | 8.0136e-06 | 77.7333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 61 | 1159 | 0.00020639 | 1.0863e-05 | 19
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 3 | 2004 | 0.00035687 | 5.3424e-07 | 668
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | NONE | 12 | 107 | 9261 | 0.0016492 | 1.9055e-05 | 86.5514
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 4 | 360 | 6.4109e-05 | 7.1232e-07 | 90
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 2 | 369 | 6.5711e-05 | 3.5616e-07 | 184.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | RECLOSER, LINE/OCR/BR | 1 | 40 | 4520 | 0.00080492 | 7.1232e-06 | 113
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 18 | 2772 | 0.00049364 | 3.2054e-06 | 154
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | SCO | POLE | 1 | 83 | 23240 | 0.0041386 | 1.4781e-05 | 280
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 2 | 553 | 9.8478e-05 | 3.5616e-07 | 276.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 2 | 16 | 2730 | 0.00048616 | 2.8493e-06 | 170.625
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 1 | 92 | 1.6383e-05 | 1.7808e-07 | 92
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 4 | 640 | 0.00011397 | 7.1232e-07 | 160
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 16 | 1648 | 0.00029348 | 2.8493e-06 | 103
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | NONE | 5 | 13 | 1204 | 0.00021441 | 2.315e-06 | 92.6154
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | TRANSFORMER, OH | 2 | 2 | 1421 | 0.00025305 | 3.5616e-07 | 710.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 1 | 1026 | 0.00018271 | 1.7808e-07 | 1026
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 281 | 33810 | 0.0060209 | 5.004e-05 | 120.3203
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 1 | 1 | 40 | 7.2029e-06 | 1.8007e-07 | 40
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 107 | 1807 | 230162 | 0.04128 | 0.00032409 | 127.3724
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | OU | NONE | 2 | 1429 | 156837 | 0.028242 | 0.00025732 | 109.753
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | INSULATOR | 1 | 10 | 1360 | 0.00024622 | 1.8105e-06 | 136
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | NONE | 129 | 5124 | 1184572 | 0.216 | 0.00093432 | 231.1811
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | FUSE | 129 | 2902 | 537079 | 0.097932 | 0.00052916 | 185.072
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | METERING | 19 | 19 | 1894 | 0.00034536 | 3.4645e-06 | 99.6842
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | NONE | 8 | 726 | 70342 | 0.012826 | 0.00013238 | 96.8898
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 7 | 60 | 3260 | 0.00059444 | 1.0941e-05 | 54.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 1 | 44 | 8.023e-06 | 1.8234e-07 | 44
AEP Total | 2020 | 5484199 | PARTIAL POWER | OU | CONDUCTOR UG | 2 | 2 | 234 | 4.2668e-05 | 3.6468e-07 | 117
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 1 | 183 | 3.3369e-05 | 1.8234e-07 | 183
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | RELAY | 1 | 1 | 129 | 2.3522e-05 | 1.8234e-07 | 129
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABI | REGULATOR | 1 | 153 | 13444 | 0.0024514 | 2.7898e-05 | 87.8693
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CIRCUIT SWITCHER | 2 | 62 | 40242 | 0.0073378 | 1.1305e-05 | 649.0645
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | GUY/ANCHOR | 2 | 9 | 1061 | 0.00019106 | 1.6206e-06 | 117.8889
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | FUSE | 51 | 153 | 17129 | 0.0030721 | 2.7441e-05 | 111.9542
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | ARRESTER | 7 | 30 | 2706 | 0.00048532 | 5.3805e-06 | 90.2
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | POLE | 3 | 3121 | 2246728 | 0.40457 | 0.000562 | 719.8744
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 24 | 6600 | 0.0011885 | 4.3217e-06 | 275
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 269 | 105398 | 0.018979 | 4.8439e-05 | 391.8141
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CROSSARM | 1 | 23 | 828 | 0.0001491 | 4.1417e-06 | 36
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 30 | 1768 | 0.00031709 | 5.3805e-06 | 58.9333
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | FUSE | 1 | 1 | 140 | 2.521e-05 | 1.8007e-07 | 140
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | METERING | 3 | 3 | 310 | 5.5205e-05 | 5.3424e-07 | 103.3333
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 1 | 1 | 503 | 8.9574e-05 | 1.7808e-07 | 503
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 394 | 27580 | 0.0049114 | 7.0163e-05 | 70
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | SPLICE, OH | 1 | 1 | 148 | 2.6544e-05 | 1.7935e-07 | 148
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | BREAKER | 1 | 207 | 31671 | 0.00564 | 3.6863e-05 | 153
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR UG | 391 | 486 | 116320 | 0.021059 | 8.7989e-05 | 239.3416
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 81 | 2098 | 122536 | 0.022185 | 0.00037984 | 58.4061
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | NONE | 8 | 1311 | 196649 | 0.035603 | 0.00023735 | 149.9992
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 12 | 34 | 7010 | 0.0012691 | 6.1556e-06 | 206.1765
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 8 | 7712 | 0.0013734 | 1.4246e-06 | 964
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 2 | 488 | 8.6903e-05 | 3.5616e-07 | 244
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | ARRESTER | 1 | 2 | 110 | 1.9589e-05 | 3.5616e-07 | 55
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 1 | 296 | 5.3301e-05 | 1.8007e-07 | 296
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 980 | 124494 | 0.022418 | 0.00017647 | 127.0347
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 5 | 6775 | 0.00122 | 9.0036e-07 | 1355
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | SCO | CONDUCTOR OVERHEAD | 1 | 39 | 351 | 6.3205e-05 | 7.0228e-06 | 9
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | REGULATOR | 5 | 2783 | 155665 | 0.028031 | 0.00050114 | 55.9342
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | REGULATOR | 3 | 1312 | 43550 | 0.0077554 | 0.00023364 | 33.1936
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 16 | 3648 | 0.00064964 | 2.8493e-06 | 228
AEP Total | 2025 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 109 | 1.9411e-05 | 1.7808e-07 | 109
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | CROSSARM | 1 | 1 | 75 | 1.3505e-05 | 1.8007e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | ARRESTER | 1 | 15 | 2115 | 0.00038085 | 2.7011e-06 | 141
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | POLE | 1 | 2 | 706 | 0.00012873 | 3.6468e-07 | 353
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | PEDESTAL | 1 | 4 | 472 | 8.6065e-05 | 7.2937e-07 | 118
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | ARRESTER | 1 | 923 | 17537 | 0.0031977 | 0.0001683 | 19
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | METERING | 1 | 1 | 66 | 1.2035e-05 | 1.8234e-07 | 66
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 1 | 188 | 3.4037e-05 | 1.8105e-07 | 188
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | FUSE | 1 | 3 | 183 | 3.2953e-05 | 5.4022e-07 | 61
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | NONE | 1 | 1 | 125 | 2.2793e-05 | 1.8234e-07 | 125
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | INSULATOR | 1 | 485 | 76145 | 0.013884 | 8.8436e-05 | 157
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 446 | 129984 | 0.023702 | 8.1325e-05 | 291.4439
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | NONE | 2240 | 21164 | 1849246 | 0.32931 | 0.0037689 | 87.377
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | POLE | 1422 | 9201 | 1488041 | 0.26499 | 0.0016385 | 161.726
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 1 | 108 | 1.937e-05 | 1.7935e-07 | 108
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 4 | 4145 | 453539 | 0.081342 | 0.00074341 | 109.4183
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR UG | 3 | 2284 | 527675 | 0.094639 | 0.00040964 | 231.0311
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 4 | 1450 | 0.0002611 | 7.2029e-07 | 362.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | NONE | 135 | 13505 | 1664573 | 0.29643 | 0.002405 | 123.2561
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 379 | 600 | 64416 | 0.011471 | 0.00010685 | 107.36
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 388 | 16412 | 3737107 | 0.6655 | 0.0029226 | 227.7058
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 115 | 742 | 67746 | 0.012064 | 0.00013214 | 91.3019
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | SCO | NONE | 1 | 4 | 140 | 2.4931e-05 | 7.1232e-07 | 35
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 35 | 213 | 35466 | 0.0063158 | 3.7931e-05 | 166.507
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 1056 | 47563 | 0.00847 | 0.00018805 | 45.0407
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 6 | 21 | 1669 | 0.00029722 | 3.7397e-06 | 79.4762
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | ARRESTER | 7 | 8004 | 1628439 | 0.29206 | 0.0014355 | 203.4531
AEP Total | 2024 | 5615460 | PARTIAL POWER | UG | CONDUCTOR UG | 7 | 12 | 3285 | 0.00058499 | 2.137e-06 | 273.75
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 72 | 1.2822e-05 | 1.7808e-07 | 72
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 4 | 380 | 6.8153e-05 | 7.174e-07 | 95
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 20 | 2100 | 30602 | 0.0054496 | 0.00037397 | 14.5724
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | NONE | 1 | 1 | 163 | 2.9027e-05 | 1.7808e-07 | 163
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 5 | 540 | 9.6163e-05 | 8.904e-07 | 108
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | FUSE | 2 | 8 | 10422 | 0.0018692 | 1.4348e-06 | 1302.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | NONE | 300 | 13569 | 1309460 | 0.23707 | 0.0024566 | 96.5038
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | FUSE | 185 | 2774 | 353107 | 0.063929 | 0.00050222 | 127.2916
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | FUSE | 18 | 37 | 4283 | 0.00077542 | 6.6987e-06 | 115.7568
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 16 | 28 | 4893 | 0.00088586 | 5.0693e-06 | 174.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CUTOUT | 3 | 23 | 24141 | 0.0043706 | 4.1641e-06 | 1049.6087
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 187 | 21824 | 0.0039512 | 3.3856e-05 | 116.7059
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ERF | NONE | 6 | 4370 | 55946 | 0.010129 | 0.00079117 | 12.8023
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | POLE | 390 | 4081 | 472396 | 0.085065 | 0.00073487 | 115.755
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | NONE | 593 | 15896 | 1542175 | 0.2777 | 0.0028624 | 97.0165
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CROSSARM | 42 | 13277 | 1389291 | 0.25017 | 0.0023908 | 104.6389
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | FUSE | 67 | 1686 | 352837 | 0.063536 | 0.0003036 | 209.2746
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 8 | 1.4406e-06 | 1.8007e-07 | 8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CUTOUT | 33 | 381 | 45902 | 0.0082657 | 6.8607e-05 | 120.4777
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | POLE | 1 | 1 | 49 | 8.8235e-06 | 1.8007e-07 | 49
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 309 | 4272 | 1031024 | 0.18491 | 0.00076618 | 241.3446
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONN/CLAMP | 468 | 741 | 94017 | 0.016862 | 0.0001329 | 126.8785
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 217 | 9124 | 3197632 | 0.5735 | 0.0016364 | 350.4638
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 13 | 163 | 79453 | 0.01425 | 2.9234e-05 | 487.4417
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | FUSE | 151 | 2573 | 253251 | 0.045421 | 0.00046147 | 98.4264
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CROSSARM | 3 | 169 | 12871 | 0.0023084 | 3.031e-05 | 76.1598
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | NONE | 1 | 14 | 1050 | 0.0001901 | 2.5346e-06 | 75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 1 | 329 | 5.9564e-05 | 1.8105e-07 | 329
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 380 | 6.8798e-05 | 3.6209e-07 | 190
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | NONE | 1 | 1 | 68 | 1.2311e-05 | 1.8105e-07 | 68
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 17 | 22 | 3022 | 0.00054418 | 3.9616e-06 | 137.3636
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 464 | 18057 | 3138313 | 0.56512 | 0.0032516 | 173.8004
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 470 | 156607 | 0.028353 | 8.5092e-05 | 333.2064
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | FUSE | 2 | 5 | 112 | 2.0277e-05 | 9.0523e-07 | 22.4
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 313 | 5.6668e-05 | 1.8105e-07 | 313
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 31 | 1760 | 0.00031864 | 5.6124e-06 | 56.7742
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | PEDESTAL | 8 | 64 | 5098 | 0.00092297 | 1.1587e-05 | 79.6562
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 1 | 96 | 1.738e-05 | 1.8105e-07 | 96
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | GUY/ANCHOR | 1 | 1 | 127 | 2.2993e-05 | 1.8105e-07 | 127
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 477 | 39393 | 0.007132 | 8.6359e-05 | 82.5849
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 7 | 30 | 11249 | 0.0020366 | 5.4314e-06 | 374.9667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 33 | 22770 | 0.0041224 | 5.9745e-06 | 690
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR UG | 331 | 435 | 119368 | 0.021766 | 7.9319e-05 | 274.4092
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 50 | 1545 | 307988 | 0.056159 | 0.00028172 | 199.345
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | NONE | 13 | 1954 | 86685 | 0.01561 | 0.00035186 | 44.3628
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 3 | 27 | 2228 | 0.0004012 | 4.8619e-06 | 82.5185
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | ARRESTER | 46 | 1520 | 219979 | 0.039612 | 0.00027371 | 144.723
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 3 | 513 | 9.2377e-05 | 5.4022e-07 | 171
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 5 | 5 | 1137 | 0.00020474 | 9.0036e-07 | 227.4
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CIRCUIT SWITCHER | 1 | 1 | 134 | 2.413e-05 | 1.8007e-07 | 134
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 281 | 5.06e-05 | 1.8007e-07 | 281
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CUTOUT | 443 | 13259 | 1427464 | 0.25602 | 0.002378 | 107.66
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | FUSE | 7 | 156 | 10639 | 0.0019158 | 2.8091e-05 | 68.1987
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | REGULATOR | 5 | 3690 | 260176 | 0.04685 | 0.00066447 | 70.5084
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | METERING | 2 | 2 | 205 | 3.6915e-05 | 3.6014e-07 | 102.5
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | NONE | 6 | 4629 | 705037 | 0.12696 | 0.00083355 | 152.3087
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 96 | 837 | 76045 | 0.013639 | 0.00015012 | 90.8542
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NONE | 705 | 22026 | 4323830 | 0.77548 | 0.0039504 | 196.3057
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 35 | 452 | 194755 | 0.034929 | 8.1066e-05 | 430.8739
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 265 | 2018 | 331787 | 0.059506 | 0.00036193 | 164.4138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | NONE | 10 | 18 | 2034 | 0.00036627 | 3.2413e-06 | 113
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 22 | 2816 | 0.00050708 | 3.9616e-06 | 128
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | OTHER EQUIPMENT | 1 | 1 | 169 | 3.0432e-05 | 1.8007e-07 | 169
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 3 | 51 | 4174 | 0.00075162 | 9.1837e-06 | 81.8431
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 25 | 402 | 124660 | 0.022358 | 7.2099e-05 | 310.0995
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | FUSE | 63 | 1184 | 177098 | 0.031763 | 0.00021235 | 149.576
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 386 | 18142 | 0.0032538 | 6.9229e-05 | 47
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 5 | 959 | 66038 | 0.012042 | 0.00017487 | 68.8613
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | NONE | 3 | 3 | 287 | 5.2332e-05 | 5.4703e-07 | 95.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CUTOUT | 7 | 3813 | 860838 | 0.15697 | 0.00069527 | 225.764
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | FUSE | 20 | 441 | 89904 | 0.016393 | 8.0413e-05 | 203.8639
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | NONE | 23 | 64 | 14491 | 0.0026423 | 1.167e-05 | 226.4219
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | NONE | 51 | 1684 | 712383 | 0.1299 | 0.00030706 | 423.0303
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | FUSE | 6 | 974 | 135879 | 0.024776 | 0.0001776 | 139.5062
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | NONE | 6 | 24 | 11276 | 0.0020561 | 4.3762e-06 | 469.8333
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | NONE | 1 | 1 | 35 | 6.2328e-06 | 1.7808e-07 | 35
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | NONE | 5 | 7 | 1779 | 0.0003168 | 1.2466e-06 | 254.1429
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 97 | 8277 | 0.001474 | 1.7274e-05 | 85.3299
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | POLE | 1 | 1 | 323 | 5.752e-05 | 1.7808e-07 | 323
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 47 | 3384 | 0.00061705 | 8.5701e-06 | 72
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | BREAKER | 1 | 2517 | 114752 | 0.020664 | 0.00045324 | 45.5908
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 1 | 1 | 342 | 6.1585e-05 | 1.8007e-07 | 342
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | SCO | NONE | 3 | 3457 | 636318 | 0.11458 | 0.00062251 | 184.0665
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 305 | 5.4922e-05 | 1.8007e-07 | 305
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 36 | 5220 | 0.00093998 | 6.4826e-06 | 145
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 1 | 148 | 2.6651e-05 | 1.8007e-07 | 148
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 3 | 345 | 6.1876e-05 | 5.3805e-07 | 115
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | SPLICE, UG | 1 | 1 | 278 | 5.006e-05 | 1.8007e-07 | 278
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | VA | POLE | 3 | 1962 | 58860 | 0.010482 | 0.00034939 | 30
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | FUSE | 1 | 552 | 71832 | 0.012792 | 9.83e-05 | 130.1304
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | REGULATOR | 3 | 5134 | 40221 | 0.0072819 | 0.00092949 | 7.8342
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | EQF | CONDUCTOR UG | 3 | 4119 | 686240 | 0.12513 | 0.00075107 | 166.6035
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 4 | 4468 | 0.0008147 | 7.2937e-07 | 1117
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 20 | 1380 | 0.00025163 | 3.6468e-06 | 69
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 8 | 1456 | 0.00026218 | 1.4406e-06 | 182
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | FUSE | 1 | 2 | 450 | 8.1032e-05 | 3.6014e-07 | 225
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 43 | 7.8407e-06 | 1.8234e-07 | 43
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONN/CLAMP | 2 | 2 | 874 | 0.00015738 | 3.6014e-07 | 437
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 8 | 1.4348e-06 | 1.7935e-07 | 8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1 | 63 | 1.1299e-05 | 1.7935e-07 | 63
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 27 | 945 | 0.00016829 | 4.8082e-06 | 35
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | METERING | 1 | 1 | 127 | 2.2616e-05 | 1.7808e-07 | 127
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | ERF | NONE | 1 | 255 | 22695 | 0.0040867 | 4.5918e-05 | 89
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 8 | 757 | 31479 | 0.0056058 | 0.00013481 | 41.5839
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | SWITCH, OH | 1 | 646 | 104006 | 0.018521 | 0.00011504 | 161
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 777 | 13986 | 0.0024906 | 0.00013837 | 18
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | POLE | 1 | 1 | 608 | 0.00010827 | 1.7808e-07 | 608
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 25 | 4800 | 0.00085478 | 4.452e-06 | 192
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | U | NONE | 3 | 3403 | 432181 | 0.078805 | 0.00062051 | 127
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 14 | 1890 | 0.00034463 | 2.5528e-06 | 135
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | POLE | 1 | 42 | 2730 | 0.00048616 | 7.4794e-06 | 65
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | TOR | CROSSARM | 1 | 1015 | 124802 | 0.022757 | 0.00018508 | 122.9576
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 2 | 5 | 3071 | 0.00055997 | 9.1171e-07 | 614.2
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | NONE | 1 | 2 | 68 | 1.2399e-05 | 3.6468e-07 | 34
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | ARRESTER | 7 | 188 | 19554 | 0.0035655 | 3.428e-05 | 104.0106
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | FUSE | 1 | 5 | 280 | 5.1056e-05 | 9.1171e-07 | 56
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | TRANSFORMER, OH | 1 | 12 | 1464 | 0.00026695 | 2.1881e-06 | 122
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CROSSARM | 2 | 126 | 54306 | 0.0099023 | 2.2975e-05 | 431
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 1 | 299 | 5.452e-05 | 1.8234e-07 | 299
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | POLE | 2 | 16 | 1173 | 0.00021389 | 2.9175e-06 | 73.3125
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CABLE TERMINATOR | 5 | 13 | 1270 | 0.00023157 | 2.3704e-06 | 97.6923
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | SCO | NONE | 3 | 2388 | 441003 | 0.080413 | 0.00043543 | 184.6746
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 124 | 121768 | 0.022203 | 2.261e-05 | 982
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 1 | 4 | 236 | 4.3033e-05 | 7.2937e-07 | 59
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | NONE | 1 | 513 | 85671 | 0.015621 | 9.3541e-05 | 167
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | POLE | 1 | 1279 | 670042 | 0.12131 | 0.00023156 | 523.8796
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 1 | 1 | 164 | 2.9692e-05 | 1.8105e-07 | 164
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | POLE | 1 | 1 | 135 | 2.4441e-05 | 1.8105e-07 | 135
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 207 | 24426 | 0.0044222 | 3.7477e-05 | 118
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 1 | 50 | 9.0036e-06 | 1.8007e-07 | 50
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | ERF | NONE | 1 | 655 | 34060 | 0.0061664 | 0.00011859 | 52
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 187 | 3.3856e-05 | 1.8105e-07 | 187
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WW | POLE | 1 | 15 | 5204 | 0.00093709 | 2.7011e-06 | 346.9333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 5 | 116 | 36871 | 0.006566 | 2.0657e-05 | 317.8534
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | SPLICE, OH | 5 | 5 | 568 | 0.00010115 | 8.904e-07 | 113.6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 4 | 37 | 8834 | 0.0015732 | 6.589e-06 | 238.7568
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 3 | 205 | 3.6506e-05 | 5.3424e-07 | 68.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | SPLICE, UG | 1 | 1 | 193 | 3.4369e-05 | 1.7808e-07 | 193
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 1 | 125 | 2.226e-05 | 1.7808e-07 | 125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 251 | 4267 | 0.00075987 | 4.4698e-05 | 17
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 10 | 300 | 5.4703e-05 | 1.8234e-06 | 30
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 7 | 714 | 0.00013019 | 1.2764e-06 | 102
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | VA | NONE | 1 | 186 | 31308 | 0.0056682 | 3.3675e-05 | 168.3226
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | NONE | 2 | 940 | 119404 | 0.021618 | 0.00017018 | 127.0255
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | NONE | 1191 | 15159 | 1544665 | 0.27966 | 0.0027445 | 101.8976
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 364 | 15141 | 2324087 | 0.42077 | 0.0027412 | 153.4963
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | NONE | 3 | 3 | 274 | 4.9607e-05 | 5.4314e-07 | 91.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 220 | 5197 | 634932 | 0.11495 | 0.0009409 | 122.1728
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | NONE | 13 | 45 | 4210 | 0.00076221 | 8.1471e-06 | 93.5556
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | POLE | 62 | 1319 | 101003 | 0.018286 | 0.0002388 | 76.5754
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CROSSARM | 2 | 2 | 417 | 7.5496e-05 | 3.6209e-07 | 208.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 14 | 1233 | 265519 | 0.048071 | 0.00022323 | 215.3439
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | ARRESTER | 2 | 24 | 5370 | 0.00097222 | 4.3451e-06 | 223.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | NONE | 2 | 572 | 166452 | 0.030136 | 0.00010356 | 291
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 23 | 70 | 57899 | 0.010311 | 1.2466e-05 | 827.1286
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | METERING | 1 | 1 | 119 | 2.1191e-05 | 1.7808e-07 | 119
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | SCO | MOAB | 1 | 1165 | 266785 | 0.048646 | 0.00021243 | 229
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 52 | 9.4818e-06 | 1.8234e-07 | 52
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CUTOUT | 8 | 44 | 12721 | 0.0023196 | 8.023e-06 | 289.1136
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | POLE | 2 | 17 | 2209 | 0.00040279 | 3.0998e-06 | 129.9412
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | ARRESTER | 3 | 3 | 243 | 4.4309e-05 | 5.4703e-07 | 81
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 2 | 55 | 22635 | 0.0041273 | 1.0029e-05 | 411.5455
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 57 | 2109 | 0.00038456 | 1.0393e-05 | 37
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONN/CLAMP | 3 | 3 | 736 | 0.0001342 | 5.4703e-07 | 245.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 107 | 14659 | 0.002673 | 1.9511e-05 | 137
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | FUSE | 3 | 4 | 745 | 0.00013584 | 7.2937e-07 | 186.25
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | FUSE | 2 | 2 | 203 | 3.7015e-05 | 3.6468e-07 | 101.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | PEDESTAL | 1 | 2 | 34 | 6.1996e-06 | 3.6468e-07 | 17
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | NONE | 1 | 5 | 615 | 0.0001103 | 8.9675e-07 | 123
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CUTOUT | 34 | 2685 | 382347 | 0.068574 | 0.00048156 | 142.4011
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 17 | 1516 | 77989 | 0.013888 | 0.00026997 | 51.4439
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | NONE | 4 | 4 | 631 | 0.00011363 | 7.2029e-07 | 157.75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UB | NONE | 4 | 54 | 4473 | 0.00080546 | 9.7239e-06 | 82.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 8 | 49 | 7425 | 0.0013317 | 8.7882e-06 | 151.5306
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | ARRESTER | 5 | 5 | 859 | 0.00015468 | 9.0036e-07 | 171.8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CUTOUT | 3 | 3 | 223 | 3.9995e-05 | 5.3805e-07 | 74.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | FUSE | 15 | 84 | 8032 | 0.0014405 | 1.5065e-05 | 95.619
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 59 | 43520 | 0.0078367 | 1.0624e-05 | 737.6271
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CROSSARM | 5 | 887 | 82589 | 0.014872 | 0.00015972 | 93.1105
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE | 261 | 38662 | 6153599 | 1.0958 | 0.0068849 | 159.164
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | NONE | 219 | 5850 | 705317 | 0.1256 | 0.0010418 | 120.567
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 132 | 2323 | 271211 | 0.048297 | 0.00041368 | 116.7503
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 59 | 2331 | 1045188 | 0.18613 | 0.0004151 | 448.3861
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | NONE | 1 | 1432 | 492648 | 0.088357 | 0.00025683 | 344.0279
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CUTOUT | 2 | 920 | 224374 | 0.039956 | 0.00016383 | 243.8848
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 3 | 495 | 8.815e-05 | 5.3424e-07 | 165
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 4 | 4 | 427 | 7.604e-05 | 7.1232e-07 | 106.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, POWER - LTC | 1 | 9 | 1017 | 0.00018111 | 1.6027e-06 | 113
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 6 | 1714 | 654908 | 0.11663 | 0.00030523 | 382.0933
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | POLE | 1 | 4 | 164 | 2.9205e-05 | 7.1232e-07 | 41
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 1 | 115 | 12535 | 0.0022482 | 2.0625e-05 | 109
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | EQF | POLE | 7 | 3349 | 458702 | 0.082268 | 0.00060064 | 136.9669
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 6 | 9 | 820 | 0.00014707 | 1.6142e-06 | 91.1111
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | INSULATOR | 1 | 2 | 390 | 6.9947e-05 | 3.587e-07 | 195
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | NONE | 1 | 1 | 116 | 2.0888e-05 | 1.8007e-07 | 116
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SWITCH, OH | 2 | 294 | 55933 | 0.010072 | 5.2941e-05 | 190.2483
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, UG | 2 | 2 | 309 | 5.6344e-05 | 3.6468e-07 | 154.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | POLE | 1 | 326 | 21842 | 0.0039174 | 5.8468e-05 | 67
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 625 | 34691 | 0.0062218 | 0.00011209 | 55.5056
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CUTOUT | 4 | 29 | 7583 | 0.0013827 | 5.2879e-06 | 261.4828
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 2 | 739 | 0.00013475 | 3.6468e-07 | 369.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | POLE | 3 | 190 | 16395 | 0.0029895 | 3.4645e-05 | 86.2895
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 211 | 1013 | 131532 | 0.023423 | 0.00018039 | 129.844
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 34 | 341 | 45029 | 0.0080188 | 6.0725e-05 | 132.0499
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 8 | 91 | 46105 | 0.0082104 | 1.6205e-05 | 506.6484
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 13 | 13 | 882 | 0.00015707 | 2.315e-06 | 67.8462
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 5 | 12 | 2218 | 0.00039498 | 2.137e-06 | 184.8333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 7 | 1070 | 24890 | 0.0044324 | 0.00019055 | 23.2617
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 4 | 856 | 215469 | 0.038371 | 0.00015244 | 251.7161
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | NONE | 1 | 1 | 193 | 3.4369e-05 | 1.7808e-07 | 193
AEP Total | 2025 | 5615460 | PARTIAL POWER | UG | CONDUCTOR UG | 4 | 10 | 2329 | 0.00041475 | 1.7808e-06 | 232.9
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 2 | 422 | 13150 | 0.0023417 | 7.515e-05 | 31.1611
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 6 | 59 | 22123 | 0.0039397 | 1.0507e-05 | 374.9661
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 202 | 25856 | 0.0046044 | 3.5972e-05 | 128
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | FUSE | 1 | 12 | 2477 | 0.0004411 | 2.137e-06 | 206.4167
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | U | NONE | 1 | 58 | 8526 | 0.0015183 | 1.0329e-05 | 147
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 19 | 66 | 2066 | 0.00036791 | 1.1753e-05 | 31.303
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 128 | 2.2794e-05 | 1.7808e-07 | 128
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 663 | 16932 | 4191859 | 0.75181 | 0.0030368 | 247.5702
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 100 | 145 | 24943 | 0.0044735 | 2.6006e-05 | 172.0207
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 131 | 229 | 37609 | 0.0067452 | 4.1071e-05 | 164.2314
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | NONE | 11 | 251 | 16040 | 0.0028884 | 4.5198e-05 | 63.9044
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | FUSE | 2 | 17 | 2624 | 0.00047251 | 3.0612e-06 | 154.3529
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 2 | 226 | 4.0696e-05 | 3.6014e-07 | 113
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | REGULATOR | 1 | 295 | 25871 | 0.0046586 | 5.3121e-05 | 87.6983
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | NONE | 122 | 11958 | 2085606 | 0.37405 | 0.0021447 | 174.4109
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | METERING | 15 | 16 | 1244 | 0.00022401 | 2.8812e-06 | 77.75
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | VIN | NONE | 2 | 1615 | 346457 | 0.062387 | 0.00029082 | 214.5245
AEP Total | 2022 | 5553337 | PARTIAL POWER | UB | CONDUCTOR UG | 3 | 3 | 598 | 0.00010768 | 5.4022e-07 | 199.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 4 | 19 | 1047 | 0.00018854 | 3.4214e-06 | 55.1053
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | FUSE | 12 | 34 | 4448 | 0.00080096 | 6.1224e-06 | 130.8235
AEP Total | 2023 | 5575683 | PARTIAL POWER | UG | CONDUCTOR UG | 18 | 96 | 23511 | 0.0042167 | 1.7218e-05 | 244.9062
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | METERING | 7 | 7 | 389 | 6.9767e-05 | 1.2555e-06 | 55.5714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 12 | 863 | 0.00015478 | 2.1522e-06 | 71.9167
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | METERING | 7 | 7 | 1013 | 0.00018241 | 1.2605e-06 | 144.7143
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | ARRESTER | 1 | 1 | 161 | 2.8992e-05 | 1.8007e-07 | 161
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | METERING | 7 | 21 | 491 | 8.8415e-05 | 3.7815e-06 | 23.381
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 7 | 8680 | 0.001563 | 1.2605e-06 | 1240
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | INSULATOR | 55 | 13892 | 1990929 | 0.35851 | 0.0025016 | 143.3148
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1146 | 28413 | 7398902 | 1.3323 | 0.0051164 | 260.4055
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 199 | 101025 | 0.018192 | 3.5834e-05 | 507.6633
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | NONE | 150 | 2300 | 1265180 | 0.22782 | 0.00041417 | 550.0783
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, OH | 18 | 99 | 31699 | 0.0057081 | 1.7827e-05 | 320.1919
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | NONE | 6 | 10 | 904 | 0.00016279 | 1.8007e-06 | 90.4
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CROSSARM | 18 | 5722 | 2586849 | 0.46582 | 0.0010304 | 452.0883
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 64 | 901 | 90731 | 0.016338 | 0.00016224 | 100.7003
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CROSSARM | 29 | 1226 | 89912 | 0.016191 | 0.00022077 | 73.3377
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | NONE | 18 | 152 | 10926 | 0.0019675 | 2.7371e-05 | 71.8816
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 19 | 124 | 16111 | 0.0029011 | 2.2329e-05 | 129.9274
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 29 | 278 | 88362 | 0.015912 | 5.006e-05 | 317.8489
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 2 | 2 | 403 | 7.2569e-05 | 3.6014e-07 | 201.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 11 | 51 | 6293 | 0.0011332 | 9.1837e-06 | 123.3922
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 7 | 185 | 54914 | 0.0098885 | 3.3313e-05 | 296.8324
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | PEDESTAL | 103 | 431 | 28954 | 0.0051929 | 7.73e-05 | 67.1787
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 69 | 557 | 53887 | 0.0096646 | 9.9898e-05 | 96.7451
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CROSSARM | 42 | 886 | 41370 | 0.0074197 | 0.0001589 | 46.693
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | NONE | 18 | 3143 | 170563 | 0.030591 | 0.0005637 | 54.2676
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CUTOUT | 3 | 87 | 41978 | 0.0075591 | 1.5666e-05 | 482.5057
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 2 | 5 | 477 | 8.5894e-05 | 9.0036e-07 | 95.4
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 11 | 2640 | 0.00047539 | 1.9808e-06 | 240
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | NONE | 4 | 4 | 683 | 0.0001225 | 7.174e-07 | 170.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | FUSE | 242 | 2457 | 384956 | 0.070194 | 0.00044801 | 156.6772
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CUTOUT | 1 | 1 | 289 | 5.2322e-05 | 1.8105e-07 | 289
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 7 | 1053 | 149884 | 0.02733 | 0.00019201 | 142.34
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | NONE | 661 | 13419 | 1749172 | 0.31895 | 0.0024468 | 130.3504
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 17 | 33 | 11137 | 0.0020307 | 6.0173e-06 | 337.4848
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 4 | 4 | 333 | 6.072e-05 | 7.2937e-07 | 83.25
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | NONE | 2 | 2 | 133 | 2.4251e-05 | 3.6468e-07 | 66.5
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABI | CONDUCTOR OVERHEAD | 1 | 2441 | 751828 | 0.13709 | 0.0004451 | 308
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | ARRESTER | 14 | 338 | 82102 | 0.014971 | 6.1632e-05 | 242.9053
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | REGULATOR | 4 | 758 | 5994 | 0.001093 | 0.00013822 | 7.9077
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | NONE | 19 | 313 | 28961 | 0.0052808 | 5.7073e-05 | 92.5272
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | FUSE | 19 | 197 | 21410 | 0.0039039 | 3.5921e-05 | 108.6802
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONN/CLAMP | 3 | 8 | 1458 | 0.00026585 | 1.4587e-06 | 182.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | FUSE | 7 | 339 | 31383 | 0.0057224 | 6.1814e-05 | 92.5752
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | POLE HARDWARE | 1 | 38 | 1900 | 0.00034645 | 6.929e-06 | 50
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | ABX | NONE | 2 | 2 | 308 | 5.524e-05 | 3.587e-07 | 154
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 9 | 14 | 1696 | 0.00030418 | 2.5109e-06 | 121.1429
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | FUSE | 1 | 2 | 142 | 2.5468e-05 | 3.587e-07 | 71
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 73 | 7165 | 0.001285 | 1.3093e-05 | 98.1507
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | INSULATOR | 6 | 2918 | 462555 | 0.082372 | 0.00051964 | 158.5178
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 351 | 1902 | 386363 | 0.068803 | 0.00033871 | 203.1351
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 40 | 31916 | 0.0056836 | 7.1232e-06 | 797.9
AEP Total | 2025 | 5615460 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 1 | 72 | 1.2822e-05 | 1.7808e-07 | 72
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE | 9 | 86 | 44539 | 0.0079315 | 1.5315e-05 | 517.8953
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 205 | 15580 | 0.0027745 | 3.6506e-05 | 76
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 3 | 168 | 2.9917e-05 | 5.3424e-07 | 56
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 3 | 1092 | 0.00019446 | 5.3424e-07 | 364
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | EQF | MOAB | 2 | 1746 | 533814 | 0.095061 | 0.00031093 | 305.7354
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | EQF | POLE | 1 | 75 | 14400 | 0.002593 | 1.3505e-05 | 192
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | POLE | 1 | 28 | 5096 | 0.00092922 | 5.1056e-06 | 182
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR UG | 1 | 1 | 195 | 3.4973e-05 | 1.7935e-07 | 195
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | FUSE | 1 | 1 | 116 | 2.0888e-05 | 1.8007e-07 | 116
AEP Total | 2020 | 5484199 | PARTIAL POWER | UG | CONDUCTOR OVERHEAD | 1 | 1 | 123 | 2.2428e-05 | 1.8234e-07 | 123
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 1 | 535 | 9.6338e-05 | 1.8007e-07 | 535
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CAPACITOR | 1 | 1 | 236 | 4.3033e-05 | 1.8234e-07 | 236
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | FUSE | 1 | 2 | 204 | 3.7198e-05 | 3.6468e-07 | 102
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 67 | 19698 | 0.0035663 | 1.213e-05 | 294
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 1 | 1097 | 211721 | 0.037703 | 0.00019535 | 193
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 2 | 232 | 4.1315e-05 | 3.5616e-07 | 116
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CUTOUT | 767 | 29541 | 3921322 | 0.70994 | 0.0053483 | 132.7417
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | NONE | 65 | 3313 | 420267 | 0.076088 | 0.00059981 | 126.8539
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | FUSE | 94 | 1045 | 297355 | 0.053835 | 0.00018919 | 284.5502
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONN/CLAMP | 26 | 290 | 10897 | 0.0019729 | 5.2503e-05 | 37.5759
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE | 72 | 5458 | 2432844 | 0.44046 | 0.00098815 | 445.7391
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 1473 | 183950 | 0.033303 | 0.00026668 | 124.8812
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 4 | 616 | 335064 | 0.060662 | 0.00011152 | 543.9351
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CUTOUT | 54 | 159 | 28068 | 0.0050816 | 2.8786e-05 | 176.5283
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | NONE | 2 | 2 | 263 | 4.7615e-05 | 3.6209e-07 | 131.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CABLE TERMINATOR | 1 | 1 | 61 | 1.1044e-05 | 1.8105e-07 | 61
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 197 | 7190 | 0.0013017 | 3.5666e-05 | 36.4975
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONDUCTOR UG | 2 | 2 | 471 | 8.5273e-05 | 3.6209e-07 | 235.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 2 | 520 | 67160 | 0.012045 | 9.3262e-05 | 129.1538
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | ABX | INSULATOR | 6 | 4865 | 842291 | 0.15107 | 0.00087254 | 173.1328
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | POLE | 1 | 220 | 24522 | 0.004398 | 3.9457e-05 | 111.4636
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | BE | CONDUCTOR OVERHEAD | 1 | 1 | 51 | 9.0821e-06 | 1.7808e-07 | 51
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 107 | 1488 | 0.00026498 | 1.9055e-05 | 13.9065
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | NONE | 1 | 22 | 1518 | 0.00027033 | 3.9178e-06 | 69
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 35 | 1820 | 0.00033186 | 6.382e-06 | 52
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | SWITCH, UG | 1 | 9 | 873 | 0.00015918 | 1.6411e-06 | 97
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | FUSE | 1 | 1 | 245 | 4.4356e-05 | 1.8105e-07 | 245
AEP Total | 2024 | 5615460 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 72 | 1.2822e-05 | 1.7808e-07 | 72
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | METERING | 29 | 33 | 2559 | 0.0004633 | 5.9745e-06 | 77.5455
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE HARDWARE | 4 | 78 | 7343 | 0.0013294 | 1.4122e-05 | 94.141
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 2 | 450 | 8.1471e-05 | 3.6209e-07 | 225
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONN/CLAMP | 42 | 91 | 16174 | 0.0029282 | 1.6475e-05 | 177.7363
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 1 | 1 | 250 | 4.5262e-05 | 1.8105e-07 | 250
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CUTOUT | 22 | 662 | 91723 | 0.016606 | 0.00011985 | 138.5544
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 11 | 111 | 8570 | 0.0015516 | 2.0096e-05 | 77.2072
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONN/CLAMP | 4 | 30 | 2777 | 0.00050277 | 5.4314e-06 | 92.5667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | FUSE | 2 | 4 | 532 | 9.6317e-05 | 7.2419e-07 | 133
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONN/CLAMP | 2 | 2 | 207 | 3.7477e-05 | 3.6209e-07 | 103.5
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | AF | NONE | 1 | 249 | 10458 | 0.0018934 | 4.5081e-05 | 42
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | NONE | 1 | 1 | 183 | 3.3131e-05 | 1.8105e-07 | 183
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 172 | 222 | 72485 | 0.013217 | 4.048e-05 | 326.509
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 339 | 14874 | 2351606 | 0.4288 | 0.0027122 | 158.1018
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | PEDESTAL | 79 | 437 | 28093 | 0.0050588 | 7.8691e-05 | 64.286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 31 | 14288 | 0.0025729 | 5.5822e-06 | 460.9032
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | METERING | 3 | 3 | 429 | 7.7669e-05 | 5.4314e-07 | 143
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CUTOUT | 1 | 1 | 80 | 1.4484e-05 | 1.8105e-07 | 80
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 1 | 107 | 1.9372e-05 | 1.8105e-07 | 107
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | POLE | 4 | 2029 | 219434 | 0.039728 | 0.00036734 | 108.1488
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | NONE | 16 | 39 | 4312 | 0.00077647 | 7.0228e-06 | 110.5641
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 45 | 737 | 181305 | 0.032648 | 0.00013271 | 246.0041
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CROSSARM | 1 | 13 | 2392 | 0.00043073 | 2.3409e-06 | 184
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CUTOUT | 8 | 885 | 78121 | 0.014067 | 0.00015936 | 88.2723
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | METERING | 1 | 1 | 632 | 0.00011524 | 1.8234e-07 | 632
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 2 | 6 | 1896 | 0.00034572 | 1.0941e-06 | 316
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | PEDESTAL | 1 | 4 | 2192 | 0.00039969 | 7.2937e-07 | 548
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | NONE | 1 | 1 | 258 | 4.7044e-05 | 1.8234e-07 | 258
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 37 | 29526 | 0.0053838 | 6.7467e-06 | 798
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE | 10 | 3315 | 714718 | 0.13032 | 0.00060446 | 215.6012
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | METERING | 1 | 2 | 168 | 3.0633e-05 | 3.6468e-07 | 84
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 965 | 161155 | 0.029177 | 0.00017471 | 167
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | EQF | POLE | 2 | 2 | 1707 | 0.00030905 | 3.6209e-07 | 853.5
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | REGULATOR | 1 | 555 | 172605 | 0.03125 | 0.00010048 | 311
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | CONN/CLAMP | 1 | 1 | 405 | 7.3324e-05 | 1.8105e-07 | 405
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 27 | 10415 | 0.0018754 | 4.8619e-06 | 385.7407
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 306 | 13426 | 0.0024176 | 5.5102e-05 | 43.8758
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 118 | 2.1516e-05 | 1.8234e-07 | 118
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 4 | 59 | 14077 | 0.0025068 | 1.0507e-05 | 238.5932
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | SPLICE, UG | 1 | 1 | 504 | 8.9752e-05 | 1.7808e-07 | 504
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | METERING | 1 | 8 | 1360 | 0.00024219 | 1.4246e-06 | 170
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 2 | 8 | 5052 | 0.00089966 | 1.4246e-06 | 631.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 1 | 6 | 228 | 4.0602e-05 | 1.0685e-06 | 38
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 166 | 18798 | 0.0033475 | 2.9561e-05 | 113.241
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | NONE | 1 | 3 | 18 | 3.2054e-06 | 5.3424e-07 | 6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | METERING | 2 | 3 | 76 | 1.3685e-05 | 5.4022e-07 | 25.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 8 | 1520 | 0.00027371 | 1.4406e-06 | 190
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 3 | 36 | 8220 | 0.0014638 | 6.4109e-06 | 228.3333
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | TRANSFORMER, OH | 1 | 2 | 880 | 0.00015671 | 3.5616e-07 | 440
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 8 | 72 | 6571 | 0.0011702 | 1.2822e-05 | 91.2639
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | SCO | NONE | 1 | 62 | 434 | 7.7287e-05 | 1.1041e-05 | 7
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 14 | 3598 | 0.00064073 | 2.4931e-06 | 257
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | MOAB | 1 | 29 | 10527 | 0.0018746 | 5.1643e-06 | 363
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | EQF | BREAKER | 7 | 3164 | 538025 | 0.097407 | 0.00057283 | 170.0458
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 2625 | 693000 | 0.12547 | 0.00047525 | 264
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 3 | 4 | 2368 | 0.00043179 | 7.2937e-07 | 592
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 1 | 270 | 4.8619e-05 | 1.8007e-07 | 270
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 9 | 355 | 98390 | 0.017521 | 6.3218e-05 | 277.1549
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 2 | 35 | 7742 | 0.0013787 | 6.2328e-06 | 221.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 6 | 87 | 16153 | 0.0028765 | 1.5493e-05 | 185.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 1 | 61 | 1.0863e-05 | 1.7808e-07 | 61
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 9 | 159 | 28831 | 0.0051342 | 2.8315e-05 | 181.327
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | METERING | 30 | 106 | 7299 | 0.0012998 | 1.8876e-05 | 68.8585
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 2 | 5 | 154 | 2.7424e-05 | 8.904e-07 | 30.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | METERING | 5 | 6 | 240 | 4.2739e-05 | 1.0685e-06 | 40
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 2 | 305 | 16283 | 0.0028997 | 5.4314e-05 | 53.3869
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 27 | 141 | 65304 | 0.011629 | 2.5109e-05 | 463.1489
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 3 | 1638 | 0.00029169 | 5.3424e-07 | 546
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 10 | 3690 | 0.00065711 | 1.7808e-06 | 369
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | METERING | 2 | 2 | 375 | 6.678e-05 | 3.5616e-07 | 187.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 2 | 290 | 5.1643e-05 | 3.5616e-07 | 145
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 58 | 1.0329e-05 | 1.7808e-07 | 58
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | INSULATOR | 4 | 1623 | 58722 | 0.010457 | 0.00028902 | 36.1811
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 2 | 58 | 1.0444e-05 | 3.6014e-07 | 29
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 1152 | 0.00020744 | 1.8007e-07 | 1152
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | FW | POLE | 1 | 281 | 170005 | 0.030999 | 5.1238e-05 | 605
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 57 | 1.0264e-05 | 1.8007e-07 | 57
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 110 | 407550 | 0.073785 | 1.9915e-05 | 3705
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 5 | 1345 | 0.0002422 | 9.0036e-07 | 269
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | SCO | BREAKER | 1 | 838 | 17598 | 0.0031689 | 0.0001509 | 21
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | CABLE TERMINATOR | 1 | 1 | 107 | 1.9268e-05 | 1.8007e-07 | 107
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | FUSE | 1 | 1 | 242 | 4.3577e-05 | 1.8007e-07 | 242
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 7 | 489 | 443558 | 0.079552 | 8.7702e-05 | 907.0716
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 51 | 9.1837e-06 | 1.8007e-07 | 51
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CABLE TERMINATOR | 1 | 39 | 10134 | 0.0018248 | 7.0228e-06 | 259.8462
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | METERING | 4 | 4 | 518 | 9.2245e-05 | 7.1232e-07 | 129.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | FUSE | 1 | 4 | 268 | 4.7725e-05 | 7.1232e-07 | 67
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 3 | 431 | 39567 | 0.0070461 | 7.6752e-05 | 91.8028
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 5 | 5 | 996 | 0.00018161 | 9.1171e-07 | 199.2
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | RECLOSER, LINE/OCR/BR | 1 | 1677 | 276667 | 0.050448 | 0.00030579 | 164.9773
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | NONE | 21 | 54 | 4581 | 0.00083531 | 9.8465e-06 | 84.8333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CUTOUT | 4 | 648 | 92801 | 0.016922 | 0.00011816 | 143.2114
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | FUSE | 1 | 21 | 1722 | 0.00031399 | 3.8292e-06 | 82
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 10 | 144 | 30400 | 0.0054522 | 2.5826e-05 | 211.1111
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | BREAKER | 1 | 1518 | 119922 | 0.021508 | 0.00027225 | 79
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | POLE | 1 | 102 | 51510 | 0.0092755 | 1.8367e-05 | 505
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | METERING | 1 | 1 | 150 | 2.7351e-05 | 1.8234e-07 | 150
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | NONE | 8 | 7297 | 1211528 | 0.22091 | 0.0013305 | 166.031
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 17 | 3856 | 0.00070311 | 3.0998e-06 | 226.8235
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 2 | 259 | 4.6452e-05 | 3.587e-07 | 129.5
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | SCO | NONE | 1 | 1 | 380 | 6.8153e-05 | 1.7935e-07 | 380
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 37 | 9620 | 0.0017253 | 6.636e-06 | 260
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | SCO | POLE | 1 | 4 | 80 | 1.4348e-05 | 7.174e-07 | 20
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | NONE | 214 | 3498 | 171817 | 0.030597 | 0.00062292 | 49.1186
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 132 | 177 | 16825 | 0.0029962 | 3.152e-05 | 95.0565
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 29 | 5502 | 438402 | 0.078071 | 0.0009798 | 79.6805
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 9 | 114 | 8294 | 0.001477 | 2.0301e-05 | 72.7544
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 14 | 1410 | 219843 | 0.03915 | 0.00025109 | 155.917
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | FUSE | 74 | 584 | 39695 | 0.0070689 | 0.000104 | 67.9709
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | FUSE | 31 | 327 | 53094 | 0.009455 | 5.8232e-05 | 162.367
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | FUSE | 3 | 5 | 766 | 0.00013641 | 8.904e-07 | 153.2
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | NONE | 1 | 73 | 9271 | 0.0016785 | 1.3216e-05 | 127
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 5 | 302 | 12913 | 0.0023253 | 5.4382e-05 | 42.7583
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 18 | 123 | 16945 | 0.0030176 | 2.1904e-05 | 137.7642
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 3 | 159 | 2.8315e-05 | 5.3424e-07 | 53
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | METERING | 2 | 2 | 333 | 5.9301e-05 | 3.5616e-07 | 166.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | ABI | NONE | 1 | 1 | 70 | 1.2466e-05 | 1.7808e-07 | 70
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 2612 | 60064 | 0.010696 | 0.00046514 | 22.9954
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | POLE | 1 | 7 | 854 | 0.00015208 | 1.2466e-06 | 122
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 1 | 1 | 51 | 9.0821e-06 | 1.7808e-07 | 51
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 1 | 96 | 1.738e-05 | 1.8105e-07 | 96
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, OH | 19 | 67 | 20448 | 0.0036674 | 1.2016e-05 | 305.194
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | ARRESTER | 3 | 2093 | 261092 | 0.046827 | 0.00037538 | 124.7453
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | JUMPER/RISER | 8 | 11 | 1781 | 0.00031942 | 1.9729e-06 | 161.9091
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | FUSE | 1 | 1 | 106 | 1.9011e-05 | 1.7935e-07 | 106
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 2 | 144 | 2.593e-05 | 3.6014e-07 | 72
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 1 | 787 | 0.00014172 | 1.8007e-07 | 787
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | FUSE | 1 | 1 | 130 | 2.3316e-05 | 1.7935e-07 | 130
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AB | NONE | 5 | 4591 | 307787 | 0.055202 | 0.0008234 | 67.0414
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 7 | 602 | 0.0001084 | 1.2605e-06 | 86
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 9 | 1741 | 202689 | 0.036095 | 0.00031004 | 116.421
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 26 | 1056 | 138049 | 0.024584 | 0.00018805 | 130.7282
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 47 | 4396 | 726749 | 0.12942 | 0.00078284 | 165.3205
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 23 | 1858 | 406278 | 0.07235 | 0.00033087 | 218.6642
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 29 | 126 | 36552 | 0.0065092 | 2.2438e-05 | 290.0952
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 50 | 426 | 33133 | 0.0059003 | 7.5862e-05 | 77.777
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 4 | 23 | 1685 | 0.00030006 | 4.0958e-06 | 73.2609
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | EQF | OTHER EQUIPMENT | 1 | 44 | 15400 | 0.002762 | 7.8914e-06 | 350
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 217 | 3.8919e-05 | 1.7935e-07 | 217
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 1 | 2 | 164 | 2.9413e-05 | 3.587e-07 | 82
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | CUTOUT | 1 | 912 | 109440 | 0.019628 | 0.00016357 | 120
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 2 | 76 | 24196 | 0.0043396 | 1.3631e-05 | 318.3684
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1 | 177 | 3.2045e-05 | 1.8105e-07 | 177
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CUTOUT | 4 | 19 | 2281 | 0.00041592 | 3.4645e-06 | 120.0526
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | NONE | 2 | 913 | 139335 | 0.025407 | 0.00016648 | 152.6123
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 41 | 6439 | 0.0011741 | 7.476e-06 | 157.0488
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 1 | 100 | 1.8234e-05 | 1.8234e-07 | 100
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1 | 158 | 2.881e-05 | 1.8234e-07 | 158
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 1 | 156 | 2.778e-05 | 1.7808e-07 | 156
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 3 | 177 | 3.2045e-05 | 5.4314e-07 | 59
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 3 | 320 | 86965 | 0.015857 | 5.8349e-05 | 271.7656
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 221 | 4.0298e-05 | 1.8234e-07 | 221
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1 | 136 | 2.4392e-05 | 1.7935e-07 | 136
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 77 | 1.3941e-05 | 1.8105e-07 | 77
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | NONE | 287 | 5538 | 1213213 | 0.21965 | 0.0010026 | 219.0706
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONN/CLAMP | 534 | 739 | 98371 | 0.01781 | 0.00013379 | 133.1137
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CROSSARM | 12 | 7116 | 691362 | 0.12517 | 0.0012883 | 97.156
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CUTOUT | 8 | 375 | 12932 | 0.0023287 | 6.7527e-05 | 34.4853
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CABLE TERMINATOR | 1 | 1 | 90 | 1.6206e-05 | 1.8007e-07 | 90
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | ARRESTER | 4 | 5 | 1198 | 0.00021486 | 8.9675e-07 | 239.6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | INSULATOR | 3 | 262 | 58450 | 0.010525 | 4.7179e-05 | 223.0916
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | POLE | 1 | 43 | 5246 | 0.00094466 | 7.7431e-06 | 122
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | NONE | 23 | 703 | 103326 | 0.018532 | 0.00012608 | 146.9787
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | NONE | 4 | 5 | 746 | 0.0001338 | 8.9675e-07 | 149.2
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 1 | 1755 | 470340 | 0.084695 | 0.00031603 | 268
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 65 | 73320 | 0.013203 | 1.1705e-05 | 1128
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 34 | 6.1224e-06 | 1.8007e-07 | 34
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 227 | 4.0713e-05 | 1.7935e-07 | 227
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | INSULATOR | 2 | 2939 | 278071 | 0.049872 | 0.00052711 | 94.6142
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | METERING | 2 | 3 | 409 | 7.3649e-05 | 5.4022e-07 | 136.3333
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 2 | 2 | 523 | 9.38e-05 | 3.587e-07 | 261.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CUTOUT | 4 | 8 | 939 | 0.00016841 | 1.4348e-06 | 117.375
AEP Total | 2022 | 5553337 | PARTIAL POWER | FW | METERING | 1 | 6 | 377 | 6.7887e-05 | 1.0804e-06 | 62.8333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 458 | 9698 | 742153 | 0.13216 | 0.001727 | 76.5264
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CROSSARM | 5 | 2309 | 641399 | 0.11504 | 0.00041412 | 277.7822
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | POLE HARDWARE | 1 | 3 | 465 | 8.3398e-05 | 5.3805e-07 | 155
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 1 | 164 | 2.9413e-05 | 1.7935e-07 | 164
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 5 | 183 | 52833 | 0.0095652 | 3.3131e-05 | 288.7049
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | NONE | 219 | 2364 | 292156 | 0.052894 | 0.00042799 | 123.5854
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | NONE | 60 | 161 | 14865 | 0.0026913 | 2.9148e-05 | 92.3292
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | NONE | 6 | 106 | 8794 | 0.0015921 | 1.9191e-05 | 82.9623
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, OH | 23 | 75 | 20152 | 0.0036484 | 1.3578e-05 | 268.6933
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | FUSE | 18 | 52 | 4407 | 0.00079787 | 9.4144e-06 | 84.75
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | NONE | 10 | 15 | 2338 | 0.00042329 | 2.7157e-06 | 155.8667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 8 | 41 | 5333 | 0.00096552 | 7.4229e-06 | 130.0732
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | INSULATOR | 8 | 9791 | 3323753 | 0.60175 | 0.0017726 | 339.4702
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 16 | 2117 | 320702 | 0.058062 | 0.00038328 | 151.4889
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | FUSE | 14 | 227 | 19484 | 0.0035275 | 4.1098e-05 | 85.8326
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | FUSE | 12 | 56 | 5485 | 0.00099304 | 1.0139e-05 | 97.9464
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | FUSE | 9 | 20 | 1979 | 0.00035829 | 3.6209e-06 | 98.95
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | TRANSFORMER, OH | 2 | 2 | 283 | 5.1236e-05 | 3.6209e-07 | 141.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | INSULATOR | 4 | 153 | 4321 | 0.0007823 | 2.77e-05 | 28.2418
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 299 | 6424 | 1520756 | 0.27385 | 0.0011568 | 236.7304
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 229 | 4962 | 332675 | 0.059905 | 0.00089352 | 67.0445
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | AF | NONE | 2 | 1387 | 264917 | 0.047962 | 0.00025111 | 191
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | FUSE | 2 | 50 | 1963 | 0.00035539 | 9.0523e-06 | 39.26
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | METERING | 1 | 1 | 149 | 2.6976e-05 | 1.8105e-07 | 149
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 573 | 6876 | 0.0012449 | 0.00010374 | 12
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE | 295 | 49183 | 10775284 | 1.9648 | 0.0089681 | 219.0855
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | NONE | 194 | 2845 | 356933 | 0.065084 | 0.00051876 | 125.4598
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 319 | 1909 | 506874 | 0.092424 | 0.00034809 | 265.5181
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | NONE | 116 | 2798 | 207116 | 0.037766 | 0.00051019 | 74.0229
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 10 | 1899 | 119533 | 0.021796 | 0.00034627 | 62.9452
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 88 | 2603 | 274081 | 0.049354 | 0.00046873 | 105.2943
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CUTOUT | 57 | 210 | 36628 | 0.0065957 | 3.7815e-05 | 174.419
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | NONE | 2135 | 23160 | 1795369 | 0.322 | 0.0041538 | 77.5203
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | NONE | 395 | 26922 | 4979791 | 0.89313 | 0.0048285 | 184.9711
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 6 | 41 | 4294 | 0.00077013 | 7.3534e-06 | 104.7317
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 7 | 203 | 3.6555e-05 | 1.2605e-06 | 29
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | NONE | 194 | 3007 | 484390 | 0.086875 | 0.00053931 | 161.0875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 17 | 2182 | 362977 | 0.0651 | 0.00039134 | 166.3506
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 1 | 115 | 2.0708e-05 | 1.8007e-07 | 115
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | FUSE | 1 | 4 | 532 | 9.5798e-05 | 7.2029e-07 | 133
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | PEDESTAL | 2 | 871 | 851566 | 0.15334 | 0.00015684 | 977.6877
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONN/CLAMP | 38 | 44 | 5703 | 0.0010399 | 8.023e-06 | 129.6136
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CABLE TERMINATOR | 23 | 37 | 4379 | 0.00079848 | 6.7467e-06 | 118.3514
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONN/CLAMP | 1 | 1 | 94 | 1.7018e-05 | 1.8105e-07 | 94
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | FUSE | 1 | 33 | 660 | 0.00011949 | 5.9745e-06 | 20
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | INSULATOR | 2 | 2 | 157 | 2.8424e-05 | 3.6209e-07 | 78.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 17 | 2206 | 0.00039939 | 3.0778e-06 | 129.7647
AEP Total | 2021 | 5523447 | PARTIAL POWER | F | CONDUCTOR UG | 1 | 1 | 1462 | 0.00026469 | 1.8105e-07 | 1462
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | NONE | 5 | 2993 | 320878 | 0.058094 | 0.00054187 | 107.2095
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 27 | 80 | 14588 | 0.00266 | 1.4587e-05 | 182.35
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | NONE | 249 | 3435 | 736871 | 0.13436 | 0.00062634 | 214.5185
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 40 | 566 | 77846 | 0.014195 | 0.00010321 | 137.5371
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | NONE | 3 | 4 | 776 | 0.0001415 | 7.2937e-07 | 194
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | INSULATOR | 5 | 6320 | 789141 | 0.14389 | 0.0011524 | 124.8641
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | ARRESTER | 2 | 45 | 2691 | 0.00049068 | 8.2054e-06 | 59.8
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | NONE | 19 | 2287 | 94663 | 0.017261 | 0.00041702 | 41.3918
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 14 | 43 | 6650 | 0.0012126 | 7.8407e-06 | 154.6512
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | REGULATOR | 1 | 581 | 5810 | 0.0010594 | 0.00010594 | 10
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 17 | 1938 | 46980 | 0.0085664 | 0.00035338 | 24.2415
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CUTOUT | 3 | 2668 | 352915 | 0.064351 | 0.00048649 | 132.277
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 9 | 30 | 3316 | 0.00060465 | 5.4703e-06 | 110.5333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 13 | 3071 | 0.00055997 | 2.3704e-06 | 236.2308
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 1 | 352 | 6.4184e-05 | 1.8234e-07 | 352
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | METERING | 3 | 16 | 206 | 3.7562e-05 | 2.9175e-06 | 12.875
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 243 | 17212 | 4188032 | 0.75415 | 0.0030994 | 243.3205
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | FUSE | 65 | 502 | 117512 | 0.021161 | 9.0396e-05 | 234.0876
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | FUSE | 15 | 166 | 108863 | 0.019603 | 2.9892e-05 | 655.8012
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | ARRESTER | 12 | 74 | 24258 | 0.0043682 | 1.3325e-05 | 327.8108
AEP Total | 2022 | 5553337 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 9 | 9 | 1233 | 0.00022203 | 1.6206e-06 | 137
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 12 | 1773 | 0.00031927 | 2.1609e-06 | 147.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | FUSE | 30 | 405 | 31569 | 0.0056619 | 7.2637e-05 | 77.9481
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR UG | 332 | 421 | 96261 | 0.017264 | 7.5506e-05 | 228.6485
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE | 11 | 824 | 461241 | 0.083057 | 0.00014838 | 559.7585
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CUTOUT | 6 | 156 | 9745 | 0.0017548 | 2.8091e-05 | 62.4679
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | ARRESTER | 42 | 2371 | 200216 | 0.035909 | 0.00042524 | 84.4437
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | POLE | 1 | 25 | 9886 | 0.0017605 | 4.452e-06 | 395.44
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 1 | 54 | 9.6163e-06 | 1.7808e-07 | 54
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 8 | 639 | 0.00011379 | 1.4246e-06 | 79.875
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 33 | 3051 | 0.00054332 | 5.8766e-06 | 92.4545
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 74 | 21386 | 0.0038719 | 1.3397e-05 | 289
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | SCO | NONE | 1 | 1179 | 17685 | 0.0032247 | 0.00021498 | 15
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | FUSE | 1 | 1 | 61 | 1.1044e-05 | 1.8105e-07 | 61
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 8 | 1448 | 0.00026216 | 1.4484e-06 | 181
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | PEDESTAL | 1 | 1 | 11 | 1.9808e-06 | 1.8007e-07 | 11
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 1 | 60 | 1.0941e-05 | 1.8234e-07 | 60
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 15 | 4490 | 0.00081872 | 2.7351e-06 | 299.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 1 | 28 | 5.1056e-06 | 1.8234e-07 | 28
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | CROSSARM | 2 | 2391 | 33474 | 0.005961 | 0.00042579 | 14
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | METERING | 1 | 1 | 159 | 2.8631e-05 | 1.8007e-07 | 159
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | METERING | 1 | 1 | 13 | 2.315e-06 | 1.7808e-07 | 13
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 13 | 468 | 8.3341e-05 | 2.315e-06 | 36
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 3 | 482 | 37203 | 0.0066251 | 8.5834e-05 | 77.1846
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | SPLICE, OH | 1 | 1 | 498 | 8.8684e-05 | 1.7808e-07 | 498
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 1 | 40 | 7.1232e-06 | 1.7808e-07 | 40
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | NONE | 3 | 3 | 425 | 7.5684e-05 | 5.3424e-07 | 141.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 1 | 814 | 0.00014496 | 1.7808e-07 | 814
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 5 | 68 | 5144 | 0.00091604 | 1.2109e-05 | 75.6471
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 1 | 2 | 180 | 3.2054e-05 | 3.5616e-07 | 90
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 225 | 4.0516e-05 | 1.8007e-07 | 225
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 1 | 142 | 2.5893e-05 | 1.8234e-07 | 142
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | POLE | 1 | 2 | 138 | 2.5163e-05 | 3.6468e-07 | 69
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 1 | 239 | 4.2561e-05 | 1.7808e-07 | 239
AEP Total | 2024 | 5615460 | PARTIAL POWER | UG | NONE | 2 | 2 | 622 | 0.00011077 | 3.5616e-07 | 311
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 2 | 378 | 6.7314e-05 | 3.5616e-07 | 189
AEP Total | 2024 | 5615460 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 1 | 203 | 3.615e-05 | 1.7808e-07 | 203
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 388 | 22730 | 0.004093 | 6.9868e-05 | 58.5825
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 14 | 2870 | 0.00051474 | 2.5109e-06 | 205
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | SCO | NONE | 1 | 1406 | 8436 | 0.0015191 | 0.00025318 | 6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 35 | 6090 | 0.0010966 | 6.3025e-06 | 174
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 2 | 11 | 2519 | 0.00045178 | 1.9729e-06 | 229
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 60 | 13593 | 0.0024379 | 1.0761e-05 | 226.55
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 46 | 8.2501e-06 | 1.7935e-07 | 46
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 12 | 3360 | 0.00060262 | 2.1522e-06 | 280
AEP Total | 2023 | 5575683 | PARTIAL POWER | OU | NONE | 1 | 0 | 0 | 0 | 0
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | INSULATOR | 4 | 6187 | 1624214 | 0.2913 | 0.0011096 | 262.5204
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | FUSE | 489 | 3276 | 287824 | 0.051256 | 0.00058339 | 87.8584
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 386 | 10531 | 1298807 | 0.23129 | 0.0018754 | 123.3318
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 27 | 27 | 2546 | 0.00045339 | 4.8082e-06 | 94.2963
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 57 | 9391 | 557298 | 0.099244 | 0.0016723 | 59.3438
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | FUSE | 224 | 3302 | 322019 | 0.057345 | 0.00058802 | 97.5224
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 166 | 724 | 50727 | 0.0090335 | 0.00012893 | 70.0649
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 3 | 8 | 1728 | 0.00030992 | 1.4348e-06 | 216
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | NONE | 3 | 14 | 4729 | 0.00084815 | 2.5109e-06 | 337.7857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | FUSE | 1 | 470 | 32430 | 0.0058163 | 8.4295e-05 | 69
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | METERING | 1 | 4 | 32 | 5.7392e-06 | 7.174e-07 | 8
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | U | NONE | 1 | 858 | 78936 | 0.014157 | 0.00015388 | 92
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 10 | 1530 | 0.00027441 | 1.7935e-06 | 153
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 9 | 93 | 17505 | 0.0031173 | 1.6561e-05 | 188.2258
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 3 | 18 | 2266 | 0.00040353 | 3.2054e-06 | 125.8889
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 1 | 343 | 6.1517e-05 | 1.7935e-07 | 343
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 2 | 2 | 590 | 0.00010624 | 3.6014e-07 | 295
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | METERING | 1 | 1 | 138 | 2.485e-05 | 1.8007e-07 | 138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | POLE | 4 | 68 | 11621 | 0.0020926 | 1.2245e-05 | 170.8971
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 185 | 1639 | 114740 | 0.020433 | 0.00029187 | 70.0061
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 449 | 3803 | 317821 | 0.056598 | 0.00067724 | 83.5711
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 30 | 2758 | 362227 | 0.064505 | 0.00049114 | 131.3368
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | NONE | 3 | 3 | 697 | 0.00012412 | 5.3424e-07 | 232.3333
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | NONE | 2 | 2 | 520 | 9.3262e-05 | 3.587e-07 | 260
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 250 | 4.4838e-05 | 1.7935e-07 | 250
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 4 | 1560 | 0.00027979 | 7.174e-07 | 390
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 1 | 303 | 5.4343e-05 | 1.7935e-07 | 303
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 6 | 1068 | 0.00019336 | 1.0863e-06 | 178
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | METERING | 3 | 3 | 266 | 4.8158e-05 | 5.4314e-07 | 88.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 2 | 124 | 2.245e-05 | 3.6209e-07 | 62
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | TRANSFORMER, GROUNDING | 1 | 24 | 5592 | 0.0010197 | 4.3762e-06 | 233
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | RELAY | 2 | 2672 | 350032 | 0.063826 | 0.00048722 | 131
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | FUSE | 1 | 1 | 131 | 2.3887e-05 | 1.8234e-07 | 131
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 10 | 1417 | 0.00025838 | 1.8234e-06 | 141.7
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | NONE | 1 | 1 | 133 | 2.4251e-05 | 1.8234e-07 | 133
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | CUTOUT | 2 | 2 | 333 | 6.072e-05 | 3.6468e-07 | 166.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 231 | 63756 | 0.011625 | 4.2121e-05 | 276
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 1 | 871 | 36582 | 0.006623 | 0.00015769 | 42
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | BREAKER | 5 | 4475 | 102979 | 0.018338 | 0.00079691 | 23.0121
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 6 | 9 | 805 | 0.00014335 | 1.6027e-06 | 89.4444
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, OH | 3 | 701 | 175794 | 0.031305 | 0.00012483 | 250.776
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | FUSE | 3 | 26 | 4144 | 0.00073796 | 4.6301e-06 | 159.3846
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | U | TRANSFORMER, STATION SERVICE | 1 | 436 | 71504 | 0.012733 | 7.7643e-05 | 164
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 10 | 2356 | 159804 | 0.028458 | 0.00041956 | 67.8285
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 2082 | 135354 | 0.024104 | 0.00037076 | 65.0115
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | FUSE | 2 | 463 | 21640 | 0.0038536 | 8.2451e-05 | 46.7387
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 4 | 42 | 7082 | 0.0012612 | 7.4794e-06 | 168.619
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | POLE | 1 | 859 | 136581 | 0.024496 | 0.00015406 | 159
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 3 | 511 | 45247 | 0.0080576 | 9.0999e-05 | 88.546
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 15 | 4410 | 0.00079093 | 2.6903e-06 | 294
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 2 | 239 | 22252 | 0.0039626 | 4.2561e-05 | 93.1046
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 65 | 4957 | 600390 | 0.10811 | 0.00089262 | 121.1196
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | FUSE | 35 | 263 | 27620 | 0.0049736 | 4.7359e-05 | 105.019
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | TR | NONE | 3 | 1973 | 279076 | 0.050526 | 0.0003572 | 141.4475
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | NONE | 5 | 6 | 978 | 0.00017706 | 1.0863e-06 | 163
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | INSULATOR | 3 | 1057 | 136571 | 0.024726 | 0.00019137 | 129.2062
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | INSULATOR | 2 | 2 | 220 | 3.983e-05 | 3.6209e-07 | 110
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 306 | 5.4492e-05 | 1.7808e-07 | 306
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 991 | 378160 | 0.067343 | 0.00017648 | 381.5943
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | BREAKER | 1 | 137 | 10412 | 0.0018749 | 2.467e-05 | 76
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 619 | 0.00011146 | 1.8007e-07 | 619
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 73 | 11023 | 0.001963 | 1.3e-05 | 151
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CUTOUT | 31 | 83 | 16273 | 0.0029186 | 1.4886e-05 | 196.0602
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | FUSE | 1 | 1 | 91 | 1.6387e-05 | 1.8007e-07 | 91
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 46 | 6432 | 0.0011582 | 8.2833e-06 | 139.8261
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 66 | 1.1949e-05 | 1.8105e-07 | 66
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 2 | 18 | 1906 | 0.00034507 | 3.2588e-06 | 105.8889
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 401 | 3703 | 498269 | 0.090855 | 0.00067521 | 134.5582
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CUTOUT | 59 | 135 | 26663 | 0.0048618 | 2.4616e-05 | 197.5037
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | NONE | 62 | 250 | 23129 | 0.0042174 | 4.5586e-05 | 92.516
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | ARRESTER | 8 | 3626 | 507491 | 0.092537 | 0.00066117 | 139.9589
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | BREAKER | 3 | 3703 | 1012695 | 0.18466 | 0.00067521 | 273.4796
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE | 68 | 6304 | 2633607 | 0.48022 | 0.0011495 | 417.7676
AEP Total | 2020 | 5484199 | PARTIAL POWER | UG | CONDUCTOR UG | 20 | 21 | 5385 | 0.00098191 | 3.8292e-06 | 256.4286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 35 | 521 | 216983 | 0.039565 | 9.5e-05 | 416.4741
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | FUSE | 15 | 412 | 44607 | 0.0081337 | 7.5125e-05 | 108.2694
AEP Total | 2020 | 5484199 | PARTIAL POWER | V | CONDUCTOR UG | 2 | 2 | 201 | 3.6651e-05 | 3.6468e-07 | 100.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | NONE | 15 | 51 | 17164 | 0.0031297 | 9.2994e-06 | 336.549
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 19 | 411 | 86692 | 0.015808 | 7.4943e-05 | 210.9294
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | CONN/CLAMP | 2 | 2 | 274 | 4.9962e-05 | 3.6468e-07 | 137
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CUTOUT | 9 | 85 | 26777 | 0.0048826 | 1.5499e-05 | 315.0235
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 12 | 5508 | 0.0010043 | 2.1881e-06 | 459
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | METERING | 3 | 3 | 631 | 0.00011506 | 5.4703e-07 | 210.3333
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | TRANSFORMER, UG | 1 | 1 | 66 | 1.2035e-05 | 1.8234e-07 | 66
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 19 | 696 | 0.00012691 | 3.4645e-06 | 36.6316
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 4 | 1144 | 0.0002086 | 7.2937e-07 | 286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 77 | 3056 | 348076 | 0.062428 | 0.00054809 | 113.8992
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | ERF | STATIC WIRE | 1 | 1663 | 108095 | 0.019465 | 0.00029946 | 65
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | FUSE | 24 | 79 | 7055 | 0.0012653 | 1.4169e-05 | 89.3038
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | NONE | 1 | 717 | 10755 | 0.0019367 | 0.00012911 | 15
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 2 | 684 | 266651 | 0.047485 | 0.00012181 | 389.8406
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 1 | 1 | 125 | 2.226e-05 | 1.7808e-07 | 125
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | GUY/ANCHOR | 1 | 7 | 1260 | 0.00022598 | 1.2555e-06 | 180
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | OTHER EQUIPMENT | 1 | 1 | 179 | 3.2104e-05 | 1.7935e-07 | 179
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 448 | 8.0672e-05 | 1.8007e-07 | 448
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | GUY/ANCHOR | 1 | 2 | 136 | 2.4219e-05 | 3.5616e-07 | 68
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 51 | 9.0821e-06 | 1.7808e-07 | 51
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 1 | 4 | 160 | 2.8493e-05 | 7.1232e-07 | 40
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 109 | 1.9875e-05 | 1.8234e-07 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 1 | 128 | 2.334e-05 | 1.8234e-07 | 128
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 1117 | 0.00020114 | 1.8007e-07 | 1117
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 324 | 4863 | 1612242 | 0.29189 | 0.00088043 | 331.5324
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 313 | 2403 | 792468 | 0.14347 | 0.00043505 | 329.7828
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | METERING | 4 | 4 | 776 | 0.00014049 | 7.2419e-07 | 194
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | NONE | 28 | 1280 | 32630 | 0.0059075 | 0.00023174 | 25.4922
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SPLICE, OH | 12 | 12 | 2340 | 0.00042365 | 2.1726e-06 | 195
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | ARRESTER | 20 | 69 | 22829 | 0.0041331 | 1.2492e-05 | 330.8551
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 1509 | 175521 | 0.031777 | 0.0002732 | 116.3161
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 7 | 7 | 1778 | 0.0003219 | 1.2673e-06 | 254
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | NONE | 3 | 285 | 17189 | 0.003112 | 5.1598e-05 | 60.3123
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | REGULATOR | 2 | 157 | 2307 | 0.00041767 | 2.8424e-05 | 14.6943
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CROSSARM | 3 | 692 | 127911 | 0.023158 | 0.00012528 | 184.8425
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CUTOUT | 8 | 101 | 17680 | 0.0032009 | 1.8286e-05 | 175.0495
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 1 | 290 | 5.2503e-05 | 1.8105e-07 | 290
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | JUMPER/RISER | 3 | 242 | 4021 | 0.00072799 | 4.3813e-05 | 16.6157
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | NONE | 6 | 85 | 5340 | 0.00096158 | 1.5306e-05 | 62.8235
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CUTOUT | 2 | 11 | 516 | 9.2545e-05 | 1.9729e-06 | 46.9091
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CROSSARM | 2 | 1909 | 101090 | 0.018131 | 0.00034238 | 52.9544
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 7 | 26 | 1551 | 0.00027817 | 4.6631e-06 | 59.6538
AEP Total | 2022 | 5553337 | PARTIAL POWER | UB | CONN/CLAMP | 2 | 11 | 1146 | 0.00020636 | 1.9808e-06 | 104.1818
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | METERING | 18 | 33 | 3090 | 0.00055419 | 5.9186e-06 | 93.6364
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | NONE | 129 | 6395 | 2158114 | 0.39072 | 0.0011578 | 337.469
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | NONE | 773 | 21509 | 3162218 | 0.57251 | 0.0038941 | 147.0184
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, OH | 3 | 1107 | 30820 | 0.0055798 | 0.00020042 | 27.841
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE | 70 | 6480 | 1975291 | 0.35762 | 0.0011732 | 304.8289
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 40 | 1375 | 354946 | 0.064262 | 0.00024894 | 258.1425
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CUTOUT | 9 | 531 | 22558 | 0.004084 | 9.6136e-05 | 42.4821
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 20 | 5660 | 0.0010247 | 3.6209e-06 | 283
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 43 | 1247 | 433210 | 0.078431 | 0.00022576 | 347.4018
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | INSULATOR | 3 | 3160 | 939416 | 0.17008 | 0.00057211 | 297.2835
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | FUSE | 20 | 230 | 30381 | 0.0055004 | 4.1641e-05 | 132.0913
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE | 10 | 934 | 371617 | 0.06728 | 0.0001691 | 397.8769
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | NONE | 2 | 3 | 2098 | 0.00037984 | 5.4314e-07 | 699.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 3 | 20 | 2121 | 0.000384 | 3.6209e-06 | 106.05
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 3 | 445 | 8.0566e-05 | 5.4314e-07 | 148.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 87 | 1.5751e-05 | 1.8105e-07 | 87
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 4 | 148 | 2.6795e-05 | 7.2419e-07 | 37
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 7 | 47 | 1549 | 0.00028044 | 8.5092e-06 | 32.9574
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | FUSE | 3 | 9 | 3227 | 0.00058424 | 1.6294e-06 | 358.5556
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | NONE | 4 | 27 | 2749 | 0.0004977 | 4.8883e-06 | 101.8148
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 2 | 2 | 803 | 0.00014538 | 3.6209e-07 | 401.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 4 | 17 | 7911 | 0.0014323 | 3.0778e-06 | 465.3529
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 3 | 642 | 0.00011623 | 5.4314e-07 | 214
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CUTOUT | 184 | 2135 | 146951 | 0.026462 | 0.00038445 | 68.8295
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | NONE | 107 | 916 | 129244 | 0.023273 | 0.00016495 | 141.0961
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | NONE | 6 | 18 | 3246 | 0.00058451 | 3.2413e-06 | 180.3333
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 7 | 595 | 0.00010714 | 1.2605e-06 | 85
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE | 14 | 303 | 360925 | 0.064992 | 5.4562e-05 | 1191.1716
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CUTOUT | 2 | 41 | 6953 | 0.001252 | 7.3829e-06 | 169.5854
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | ARRESTER | 9 | 190 | 16199 | 0.002917 | 3.4214e-05 | 85.2579
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 2 | 56 | 24776 | 0.0044121 | 9.9725e-06 | 442.4286
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CUTOUT | 1 | 2 | 190 | 3.3835e-05 | 3.5616e-07 | 95
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 5 | 12 | 590 | 0.00010507 | 2.137e-06 | 49.1667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | ARRESTER | 3 | 1608 | 66004 | 0.011754 | 0.00028635 | 41.0473
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 5 | 159 | 15303 | 0.0027252 | 2.8315e-05 | 96.2453
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CROSSARM | 1 | 706 | 7766 | 0.001383 | 0.00012572 | 11
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 3 | 583 | 0.00010382 | 5.3424e-07 | 194.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 12 | 120 | 2.137e-05 | 2.137e-06 | 10
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 2 | 16 | 3424 | 0.00060975 | 2.8493e-06 | 214
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 9 | 4483 | 369602 | 0.065819 | 0.00079833 | 82.4452
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 130 | 42846 | 0.00763 | 2.315e-05 | 329.5846
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 10 | 979 | 0.00017434 | 1.7808e-06 | 97.9
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, GROUNDING | 1 | 53 | 3657 | 0.00065588 | 9.5056e-06 | 69
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE | 6 | 2700 | 1199360 | 0.21358 | 0.00048082 | 444.2074
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 33 | 5.8766e-06 | 1.7808e-07 | 33
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 13 | 1053 | 0.00018752 | 2.315e-06 | 81
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 10 | 2020 | 0.00035972 | 1.7808e-06 | 202
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 7 | 4247 | 172030 | 0.030635 | 0.0007563 | 40.5062
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 5 | 977 | 0.00017398 | 8.904e-07 | 195.4
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 17 | 2788 | 0.00049649 | 3.0274e-06 | 164
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 14 | 2.4931e-06 | 1.7808e-07 | 14
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 1 | 1 | 1254 | 0.00022331 | 1.7808e-07 | 1254
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 5 | 155 | 2.7602e-05 | 8.904e-07 | 31
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | FUSE | 2 | 3 | 231 | 4.1597e-05 | 5.4022e-07 | 77
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | SWITCH, OH | 1 | 1 | 60 | 1.0941e-05 | 1.8234e-07 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | NETWORK TRANSFORMER | 1 | 13 | 611 | 0.00011002 | 2.3409e-06 | 47
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 6 | 6 | 610 | 0.00010984 | 1.0804e-06 | 101.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 60 | 11100 | 0.0019988 | 1.0804e-05 | 185
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | ARRESTER | 3 | 6 | 512 | 9.2197e-05 | 1.0804e-06 | 85.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 10 | 1680 | 0.00030252 | 1.8007e-06 | 168
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 465 | 365150 | 0.065753 | 8.3733e-05 | 785.2688
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | CONDUCTOR UG | 11 | 6134 | 793067 | 0.14281 | 0.0011046 | 129.2903
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 1 | 179 | 3.2104e-05 | 1.7935e-07 | 179
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | NONE | 1 | 1 | 402 | 7.2389e-05 | 1.8007e-07 | 402
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CABLE TERMINATOR | 1 | 1 | 67 | 1.2016e-05 | 1.7935e-07 | 67
AEP Total | 2024 | 5615460 | SUBTRANSMISSION LINE | ERF | NONE | 1 | 1319 | 94968 | 0.016912 | 0.00023489 | 72
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | FUSE | 1 | 1 | 119 | 2.1191e-05 | 1.7808e-07 | 119
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 9 | 1989 | 0.0003542 | 1.6027e-06 | 221
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 2 | 216 | 3.8465e-05 | 3.5616e-07 | 108
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | NONE | 3 | 3 | 284 | 5.0575e-05 | 5.3424e-07 | 94.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | SWITCH, OH | 2 | 552 | 74520 | 0.013271 | 9.83e-05 | 135
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 2 | 42 | 6188 | 0.0011143 | 7.563e-06 | 147.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CIRCUIT SWITCHER | 1 | 33 | 19635 | 0.0035357 | 5.9424e-06 | 595
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 10 | 3487 | 552627 | 0.098412 | 0.00062096 | 158.4821
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 939 | 0.00016722 | 1.7808e-07 | 939
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 2 | 295 | 5.3121e-05 | 3.6014e-07 | 147.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | CUTOUT | 1 | 1 | 118 | 2.1248e-05 | 1.8007e-07 | 118
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 1 | 103 | 1.8547e-05 | 1.8007e-07 | 103
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | FUSE | 1 | 5 | 3350 | 0.00060082 | 8.9675e-07 | 670
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR UG | 1 | 1 | 127 | 2.2616e-05 | 1.7808e-07 | 127
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE | 1 | 11 | 2372 | 0.00042241 | 1.9589e-06 | 215.6364
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 833 | 304599 | 0.054243 | 0.00014834 | 365.6651
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 1 | 311 | 8708 | 0.0015507 | 5.5383e-05 | 28
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | FUSE | 1 | 1 | 65 | 1.1575e-05 | 1.7808e-07 | 65
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 2 | 8 | 1945 | 0.00034637 | 1.4246e-06 | 243.125
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | RELAY | 1 | 1300 | 122200 | 0.022005 | 0.00023409 | 94
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | VA | STATIC WIRE | 6 | 4975 | 1305465 | 0.23804 | 0.00090715 | 262.405
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 1320 | 0.00024069 | 3.6468e-07 | 660
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONN/CLAMP | 1 | 403 | 29822 | 0.0053701 | 7.2569e-05 | 74
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 4 | 324 | 5.8343e-05 | 7.2029e-07 | 81
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 1 | 454 | 8.1753e-05 | 1.8007e-07 | 454
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 1540 | 53900 | 0.0098282 | 0.00028081 | 35
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 98 | 1.7576e-05 | 1.7935e-07 | 98
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | NONE | 1 | 4 | 4388 | 0.00080012 | 7.2937e-07 | 1097
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 7 | 155 | 12455 | 0.002218 | 2.7602e-05 | 80.3548
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 5 | 17 | 1896 | 0.00033764 | 3.0274e-06 | 111.5294
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 12 | 252 | 4.5196e-05 | 2.1522e-06 | 21
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 10 | 49 | 13450 | 0.0023952 | 8.7259e-06 | 274.4898
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 6 | 1801 | 129023 | 0.022976 | 0.00032072 | 71.6396
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 21 | 2074 | 557228 | 0.099231 | 0.00036934 | 268.6731
AEP Total | 2023 | 5575683 | PARTIAL POWER | FW | OTHER EQUIPMENT | 1 | 1 | 87 | 1.5603e-05 | 1.7935e-07 | 87
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 5 | 16 | 10822 | 0.0019409 | 2.8696e-06 | 676.375
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 1 | 68 | 1.2311e-05 | 1.8105e-07 | 68
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 55 | 189 | 18490 | 0.0032927 | 3.3657e-05 | 97.8307
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 7 | 157 | 14084 | 0.0025081 | 2.7959e-05 | 89.707
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 3 | 3 | 389 | 6.9273e-05 | 5.3424e-07 | 129.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 6 | 2368 | 428285 | 0.076269 | 0.00042169 | 180.8636
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 1 | 102 | 1.8294e-05 | 1.7935e-07 | 102
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 1 | 327 | 5.9202e-05 | 1.8105e-07 | 327
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 6 | 1374 | 0.00024876 | 1.0863e-06 | 229
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | WFS | NONE | 1 | 7 | 13832 | 0.0025042 | 1.2673e-06 | 1976
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | NONE | 2 | 15 | 936 | 0.00017067 | 2.7351e-06 | 62.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | PEDESTAL | 16 | 138 | 7201 | 0.001313 | 2.5163e-05 | 52.1812
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR UG | 2 | 2 | 454 | 8.2783e-05 | 3.6468e-07 | 227
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | SCO | NONE | 7 | 4603 | 63792 | 0.011632 | 0.00083932 | 13.8588
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 2 | 1422 | 0.00025929 | 3.6468e-07 | 711
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 48 | 13680 | 0.0024944 | 8.7524e-06 | 285
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 156 | 2.8445e-05 | 1.8234e-07 | 156
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 277 | 303869 | 0.055408 | 5.0509e-05 | 1097
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | METERING | 1 | 1 | 83 | 1.5134e-05 | 1.8234e-07 | 83
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 2 | 1619 | 0.00029311 | 3.6209e-07 | 809.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 2 | 146 | 2.6433e-05 | 3.6209e-07 | 73
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | RECLOSER, LINE/OCR/BR | 1 | 65 | 73060 | 0.013227 | 1.1768e-05 | 1124
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABI | NONE | 3 | 3389 | 406291 | 0.073162 | 0.00061026 | 119.8852
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 1 | 291 | 5.2401e-05 | 1.8007e-07 | 291
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 8 | 7136 | 0.0012919 | 1.4484e-06 | 892
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 13 | 10517 | 0.0019041 | 2.3536e-06 | 809
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | METERING | 1 | 1 | 67 | 1.2065e-05 | 1.8007e-07 | 67
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | NONE | 1 | 10 | 270 | 4.8082e-05 | 1.7808e-06 | 27
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 281 | 12557 | 0.0022361 | 5.004e-05 | 44.6868
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | NONE | 67 | 179 | 16292 | 0.0029013 | 3.1876e-05 | 91.0168
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 58 | 1.0402e-05 | 3.587e-07 | 29
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 4 | 392 | 6.9807e-05 | 7.1232e-07 | 98
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 41 | 5280 | 523584 | 0.09324 | 0.00094026 | 99.1636
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 3 | 330 | 5.9186e-05 | 5.3805e-07 | 110
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 1 | 1 | 68 | 1.2196e-05 | 1.7935e-07 | 68
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | ERF | CONDUCTOR OVERHEAD | 1 | 73 | 1752 | 0.00031422 | 1.3093e-05 | 24
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | NONE | 4 | 4 | 430 | 7.7431e-05 | 7.2029e-07 | 107.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 96 | 376 | 80911 | 0.014409 | 6.6958e-05 | 215.1888
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 133 | 4037 | 747301 | 0.13308 | 0.00071891 | 185.113
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE | 88 | 17605 | 2043233 | 0.36386 | 0.0031351 | 116.0598
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | NONE | 161 | 11920 | 690514 | 0.12297 | 0.0021227 | 57.929
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | FUSE | 71 | 1306 | 75124 | 0.013378 | 0.00023257 | 57.5222
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | SCO | NONE | 2 | 2687 | 34931 | 0.0063241 | 0.00048647 | 13
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | METERING | 15 | 15 | 1247 | 0.00022207 | 2.6712e-06 | 83.1333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 12 | 22 | 1736 | 0.00030915 | 3.9178e-06 | 78.9091
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 175 | 6825 | 0.0012154 | 3.1164e-05 | 39
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 1 | 102 | 1.8164e-05 | 1.7808e-07 | 102
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 87 | 5534 | 0.00099252 | 1.5603e-05 | 63.6092
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | FUSE | 1 | 1 | 53 | 9.5056e-06 | 1.7935e-07 | 53
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | EQF | CROSSARM | 2 | 1450 | 133474 | 0.024165 | 0.00026252 | 92.051
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | ARRESTER | 1 | 435 | 31320 | 0.005711 | 7.9319e-05 | 72
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 4 | 668 | 0.0001218 | 7.2937e-07 | 167
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | FUSE | 1 | 1 | 58 | 1.0576e-05 | 1.8234e-07 | 58
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | INSULATOR | 1 | 2 | 6044 | 0.0011021 | 3.6468e-07 | 3022
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | OTHER EQUIPMENT | 2 | 2 | 317 | 5.7802e-05 | 3.6468e-07 | 158.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 162 | 2.9539e-05 | 1.8234e-07 | 162
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | FUSE | 1 | 1 | 64 | 1.1587e-05 | 1.8105e-07 | 64
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | REGULATOR | 11 | 12602 | 1723643 | 0.31429 | 0.0022979 | 136.7754
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 2 | 57 | 24373 | 0.0043889 | 1.0264e-05 | 427.5965
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 3 | 855 | 0.00015396 | 5.4022e-07 | 285
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | METERING | 4 | 4 | 227 | 4.0713e-05 | 7.174e-07 | 56.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE | 5 | 158 | 29945 | 0.0053706 | 2.8337e-05 | 189.5253
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 4 | 204 | 3.6735e-05 | 7.2029e-07 | 51
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | POLE | 14 | 2385 | 192686 | 0.034558 | 0.00042775 | 80.7908
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 13 | 30160 | 0.005431 | 2.3409e-06 | 2320
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | PEDESTAL | 2 | 11 | 921 | 0.00016518 | 1.9729e-06 | 83.7273
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 7 | 1167 | 90337 | 0.016202 | 0.0002093 | 77.4096
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | NONE | 1 | 1 | 566 | 0.00010151 | 1.7935e-07 | 566
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | FUSE | 15 | 18 | 1547 | 0.00027745 | 3.2283e-06 | 85.9444
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | BREAKER | 1 | 1772 | 299468 | 0.05371 | 0.00031781 | 169
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | METERING | 10 | 24 | 1692 | 0.00030346 | 4.3044e-06 | 70.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CROSSARM | 3 | 170 | 6569 | 0.0011829 | 3.0612e-05 | 38.6412
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 14 | 1534 | 162072 | 0.029553 | 0.00027971 | 105.6532
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CROSSARM | 13 | 64 | 4074 | 0.00074286 | 1.167e-05 | 63.6562
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | NONE | 13 | 1044 | 201356 | 0.036716 | 0.00019037 | 192.8697
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | FUSE | 1 | 2 | 252 | 4.595e-05 | 3.6468e-07 | 126
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CROSSARM | 6 | 557 | 54363 | 0.0099127 | 0.00010156 | 97.5996
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | CE | INSULATOR | 1 | 1281 | 156387 | 0.028516 | 0.00023358 | 122.082
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, OH | 3 | 482 | 94467 | 0.017225 | 8.7889e-05 | 195.9896
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | FUSE | 55 | 195 | 18531 | 0.003379 | 3.5557e-05 | 95.0308
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | FUSE | 7 | 26 | 2093 | 0.00038164 | 4.7409e-06 | 80.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | SPLICE, OH | 1 | 1 | 134 | 2.4033e-05 | 1.7935e-07 | 134
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | NONE | 20 | 3773 | 2661377 | 0.47732 | 0.00067669 | 705.3742
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 3 | 185 | 3.318e-05 | 5.3805e-07 | 61.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 2 | 542 | 9.7208e-05 | 3.587e-07 | 271
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 6 | 2028 | 0.00036115 | 1.0685e-06 | 338
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | REGULATOR | 3 | 2265 | 189545 | 0.033754 | 0.00040335 | 83.6843
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 4 | 76 | 1.3534e-05 | 7.1232e-07 | 19
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 25 | 20775 | 0.0036996 | 4.452e-06 | 831
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 1 | 154 | 2.762e-05 | 1.7935e-07 | 154
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 1 | 185 | 49210 | 0.0087633 | 3.2945e-05 | 266
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CUTOUT | 1 | 1 | 48 | 8.5478e-06 | 1.7808e-07 | 48
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 6 | 2298 | 0.00041215 | 1.0761e-06 | 383
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 142 | 4954 | 0.0008885 | 2.5468e-05 | 34.8873
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | FUSE | 11 | 11 | 1240 | 0.00022082 | 1.9589e-06 | 112.7273
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CUTOUT | 3 | 223 | 15717 | 0.0027989 | 3.9712e-05 | 70.4798
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CROSSARM | 20 | 7183 | 2193762 | 0.40002 | 0.0013098 | 305.4103
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 91 | 5892 | 763304 | 0.13918 | 0.0010744 | 129.5492
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 132 | 7574 | 0.0013811 | 2.4069e-05 | 57.3788
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 28 | 149 | 39881 | 0.007272 | 2.7169e-05 | 267.6577
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 18 | 196 | 17996 | 0.0032814 | 3.5739e-05 | 91.8163
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 3 | 28 | 3633 | 0.00066245 | 5.1056e-06 | 129.75
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 25 | 3692 | 0.00067321 | 4.5586e-06 | 147.68
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | POLE | 2 | 7 | 3372 | 0.00061486 | 1.2764e-06 | 481.7143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 20 | 282 | 37818 | 0.0068958 | 5.142e-05 | 134.1064
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | ARRESTER | 7 | 1308 | 34687 | 0.0063249 | 0.0002385 | 26.5191
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 5 | 1156 | 205129 | 0.037404 | 0.00021079 | 177.4472
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | FUSE | 10 | 970 | 82671 | 0.015074 | 0.00017687 | 85.2278
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CUTOUT | 89 | 972 | 42509 | 0.0077512 | 0.00017724 | 43.7335
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | FUSE | 6 | 129 | 94798 | 0.017286 | 2.3522e-05 | 734.8682
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | POLE | 1 | 26 | 3666 | 0.00066847 | 4.7409e-06 | 141
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 5 | 965 | 0.00017596 | 9.1171e-07 | 193
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE | 7 | 140 | 29260 | 0.0053353 | 2.5528e-05 | 209
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 995 | 87560 | 0.015704 | 0.00017845 | 88
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 12 | 2142 | 0.00038417 | 2.1522e-06 | 178.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CUTOUT | 4 | 18 | 2559 | 0.00045896 | 3.2283e-06 | 142.1667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 20 | 266 | 35372 | 0.006299 | 4.7369e-05 | 132.9774
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 95 | 755 | 159405 | 0.028387 | 0.00013445 | 211.1325
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CIRCUIT SWITCHER | 1 | 137 | 32469 | 0.0058784 | 2.4803e-05 | 237
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | EQF | RELAY | 3 | 1968 | 495936 | 0.089787 | 0.0003563 | 252
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | NONE | 1757 | 14932 | 1264201 | 0.22765 | 0.0026888 | 84.6639
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | FUSE | 292 | 3606 | 377452 | 0.067969 | 0.00064934 | 104.6733
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | FUSE | 135 | 2974 | 530454 | 0.09552 | 0.00053553 | 178.3638
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | NONE | 86 | 6343 | 1110100 | 0.1999 | 0.0011422 | 175.0118
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | FUSE | 33 | 76 | 6084 | 0.0010956 | 1.3685e-05 | 80.0526
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 23 | 2352 | 0.00042353 | 4.1417e-06 | 102.2609
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | NONE | 38 | 608 | 82444 | 0.014846 | 0.00010948 | 135.5987
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | FUSE | 18 | 812 | 111067 | 0.02 | 0.00014622 | 136.782
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 157 | 2.8424e-05 | 1.8105e-07 | 157
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 597 | 0.00010808 | 1.8105e-07 | 597
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 105 | 1.901e-05 | 1.8105e-07 | 105
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 1 | 92 | 1.6656e-05 | 1.8105e-07 | 92
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 3 | 69 | 8214 | 0.0014871 | 1.2492e-05 | 119.0435
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | SWITCH, OH | 1 | 1 | 26 | 4.7072e-06 | 1.8105e-07 | 26
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | FUSE | 2 | 2 | 120 | 2.1726e-05 | 3.6209e-07 | 60
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | NONE | 367 | 18691 | 2372810 | 0.43266 | 0.0034082 | 126.9493
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR UG | 14 | 15 | 3256 | 0.00059371 | 2.7351e-06 | 217.0667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 12 | 500 | 144977 | 0.026435 | 9.1171e-05 | 289.954
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 696 | 62606 | 0.011274 | 0.00012533 | 89.9511
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | ARRESTER | 22 | 127 | 3364 | 0.00060576 | 2.2869e-05 | 26.4882
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 18 | 2694 | 0.00048511 | 3.2413e-06 | 149.6667
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | VA | POLE | 2 | 2681 | 522054 | 0.094007 | 0.00048277 | 194.7236
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CUTOUT | 6 | 47 | 55718 | 0.010033 | 8.4634e-06 | 1185.4894
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | POLE | 763 | 6019 | 774601 | 0.13892 | 0.0010795 | 128.6926
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | NONE | 53 | 122 | 13366 | 0.0023972 | 2.1881e-05 | 109.5574
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 11 | 757 | 0.00013631 | 1.9808e-06 | 68.8182
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 15 | 2475 | 0.00044568 | 2.7011e-06 | 165
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 8 | 3138 | 0.00056507 | 1.4406e-06 | 392.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | FUSE | 144 | 3521 | 258071 | 0.046285 | 0.00063149 | 73.2948
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CROSSARM | 42 | 11613 | 1365813 | 0.24496 | 0.0020828 | 117.6107
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 9 | 89 | 5279 | 0.00094008 | 1.5849e-05 | 59.3146
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | FUSE | 11 | 108 | 16642 | 0.0029636 | 1.9233e-05 | 154.0926
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 4 | 6 | 935 | 0.0001665 | 1.0685e-06 | 155.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | NONE | 8 | 109 | 20868 | 0.0037427 | 1.9549e-05 | 191.4495
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | NONE | 22 | 806 | 27037 | 0.0048147 | 0.00014353 | 33.5447
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | TRANSFORMER, OH | 1 | 1 | 500 | 8.9675e-05 | 1.7935e-07 | 500
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 4 | 23 | 4531 | 0.00082032 | 4.1641e-06 | 197
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 2 | 34 | 6542 | 0.0011844 | 6.1556e-06 | 192.4118
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | METERING | 3 | 3 | 427 | 7.7307e-05 | 5.4314e-07 | 142.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 560 | 0.00010139 | 3.6209e-07 | 280
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONN/CLAMP | 53 | 97 | 10477 | 0.0018866 | 1.7467e-05 | 108.0103
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | NONE | 1 | 1 | 19 | 3.4214e-06 | 1.8007e-07 | 19
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 59 | 15669 | 0.0028215 | 1.0624e-05 | 265.5763
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR UG | 21 | 21 | 5017 | 0.00090342 | 3.7815e-06 | 238.9048
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 5 | 266 | 9909 | 0.0017843 | 4.7899e-05 | 37.2519
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 1 | 4596 | 0.00082761 | 1.8007e-07 | 4596
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 50 | 9.0036e-06 | 1.8007e-07 | 50
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CUTOUT | 16 | 49 | 5663 | 0.0010197 | 8.8235e-06 | 115.5714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE HARDWARE | 3 | 52 | 10918 | 0.001966 | 9.3637e-06 | 209.9615
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 12 | 729 | 84829 | 0.015275 | 0.00013127 | 116.3635
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 6 | 110 | 10735 | 0.0019435 | 1.9915e-05 | 97.5909
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CAPACITOR | 5 | 2650 | 220350 | 0.039894 | 0.00047977 | 83.1509
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 172 | 3.114e-05 | 1.8105e-07 | 172
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | FUSE | 8 | 57 | 3263 | 0.00059075 | 1.032e-05 | 57.2456
AEP Total | 2021 | 5523447 | SUBTRANSMISSION LINE | ERF | NONE | 5 | 2396 | 102700 | 0.018593 | 0.00043379 | 42.8631
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 4 | 324 | 5.8659e-05 | 7.2419e-07 | 81
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 118 | 241 | 30903 | 0.0056349 | 4.3944e-05 | 128.2282
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 122 | 2982 | 343303 | 0.062599 | 0.00054374 | 115.1251
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE | 67 | 5043 | 1141790 | 0.2082 | 0.00091955 | 226.4109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | NONE | 3 | 2961 | 18050 | 0.0032913 | 0.00053991 | 6.0959
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE | 260 | 37015 | 6441138 | 1.1552 | 0.0066386 | 174.0143
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 6 | 60 | 5678 | 0.0010224 | 1.0804e-05 | 94.6333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | NONE | 86 | 432 | 43590 | 0.0078179 | 7.7479e-05 | 100.9028
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | NONE | 28 | 365 | 121090 | 0.021805 | 6.5726e-05 | 331.7534
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 877 | 133304 | 0.024004 | 0.00015792 | 152
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE | 44 | 2169 | 286441 | 0.051373 | 0.00038901 | 132.0613
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 2287 | 272158 | 0.049008 | 0.00041182 | 119.0022
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | FUSE | 58 | 867 | 120774 | 0.021661 | 0.0001555 | 139.301
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONN/CLAMP | 7 | 13 | 9726 | 0.0017514 | 2.3409e-06 | 748.1538
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONN/CLAMP | 3 | 5 | 355 | 6.3926e-05 | 9.0036e-07 | 71
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 19 | 54 | 15645 | 0.0028059 | 9.6849e-06 | 289.7222
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | NONE | 210 | 4991 | 1332961 | 0.23907 | 0.00089514 | 267.0729
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 9 | 2643 | 234128 | 0.042388 | 0.00047851 | 88.5842
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 5 | 7 | 362 | 6.5539e-05 | 1.2673e-06 | 51.7143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 7 | 65 | 7334 | 0.0013278 | 1.1768e-05 | 112.8308
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CUTOUT | 64 | 957 | 21610 | 0.0039124 | 0.00017326 | 22.581
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 4 | 133 | 60215 | 0.010902 | 2.4079e-05 | 452.7444
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 12 | 1240 | 330523 | 0.05984 | 0.0002245 | 266.5508
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 39 | 462 | 53600 | 0.0097041 | 8.3643e-05 | 116.0173
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 1 | 1178 | 0.00021327 | 1.8105e-07 | 1178
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CROSSARM | 37 | 18029 | 2195506 | 0.39749 | 0.0032641 | 121.7764
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 10 | 749 | 160564 | 0.02907 | 0.0001356 | 214.3712
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 11 | 112 | 69536 | 0.012589 | 2.0277e-05 | 620.8571
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE | 14 | 1965 | 1016662 | 0.18406 | 0.00035576 | 517.3852
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CABLE TERMINATOR | 26 | 26 | 3023 | 0.0005473 | 4.7072e-06 | 116.2692
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 93 | 1.6837e-05 | 1.8105e-07 | 93
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 1 | 53 | 9.5955e-06 | 1.8105e-07 | 53
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | POLE | 2 | 32 | 23116 | 0.0041851 | 5.7935e-06 | 722.375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CROSSARM | 18 | 8940 | 2276736 | 0.41219 | 0.0016186 | 254.6685
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR UG | 17 | 17 | 3499 | 0.00063348 | 3.0778e-06 | 205.8235
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | METERING | 11 | 19 | 1843 | 0.00033367 | 3.4399e-06 | 97
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | NONE | 72 | 119 | 11058 | 0.0019833 | 2.1343e-05 | 92.9244
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 19 | 1615 | 0.00028965 | 3.4077e-06 | 85
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | ARRESTER | 8 | 967 | 91294 | 0.016374 | 0.00017343 | 94.4095
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 2 | 34 | 1090 | 0.00019549 | 6.0979e-06 | 32.0588
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | NETWORK PROTECTOR | 1 | 3 | 279 | 5.024e-05 | 5.4022e-07 | 93
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 5 | 4390 | 139674 | 0.025151 | 0.00079052 | 31.8164
AEP Total | 2022 | 5553337 | SUBTRANSMISSION LINE | TOR | NONE | 1 | 958 | 189885 | 0.034193 | 0.00017251 | 198.2098
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 7 | 12 | 2874 | 0.00051545 | 2.1522e-06 | 239.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 11 | 156 | 12377 | 0.0022198 | 2.7979e-05 | 79.3397
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 4 | 821 | 0.00014864 | 7.2419e-07 | 205.25
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | BREAKER | 1 | 8 | 1216 | 0.00022015 | 1.4484e-06 | 152
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CUTOUT | 647 | 2302 | 100774 | 0.018147 | 0.00041453 | 43.7767
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE | 117 | 13618 | 4473111 | 0.80548 | 0.0024522 | 328.4705
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE | 4 | 1559 | 172563 | 0.031074 | 0.00028073 | 110.6883
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | CONN/CLAMP | 1 | 27 | 2277 | 0.00041224 | 4.8883e-06 | 84.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | NONE | 97 | 2081 | 2214708 | 0.40096 | 0.00037676 | 1064.2518
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 4 | 231 | 4.1822e-05 | 7.2419e-07 | 57.75
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | NONE | 3 | 3 | 245 | 4.4356e-05 | 5.4314e-07 | 81.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 57 | 19775 | 0.0035802 | 1.032e-05 | 346.9298
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 4 | 720 | 0.00013035 | 7.2419e-07 | 180
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 16 | 9118 | 0.0016626 | 2.9175e-06 | 569.875
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 29 | 52 | 13560 | 0.0024726 | 9.4818e-06 | 260.7692
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CUTOUT | 89 | 323 | 8118 | 0.001456 | 5.793e-05 | 25.1331
AEP Total | 2022 | 5553337 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 1 | 300 | 5.4022e-05 | 1.8007e-07 | 300
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 13 | 2912 | 0.00052227 | 2.3316e-06 | 224
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 4 | 1162 | 0.0002084 | 7.174e-07 | 290.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 16 | 1686 | 148933 | 0.026711 | 0.00030238 | 88.3351
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 30 | 1051 | 942229 | 0.16899 | 0.0001885 | 896.5071
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | FUSE | 234 | 865 | 147346 | 0.026676 | 0.00015661 | 170.3422
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | POLE | 2 | 23 | 14183 | 0.0025678 | 4.1641e-06 | 616.6522
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | NONE | 4 | 4 | 369 | 6.6806e-05 | 7.2419e-07 | 92.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 15 | 238 | 55045 | 0.0099657 | 4.3089e-05 | 231.2815
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | ARRESTER | 6 | 1389 | 51352 | 0.0092971 | 0.00025147 | 36.9705
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | FUSE | 13 | 191 | 24747 | 0.0044804 | 3.458e-05 | 129.5654
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | FUSE | 5 | 9 | 889 | 0.00016095 | 1.6294e-06 | 98.7778
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | METERING | 5 | 5 | 386 | 6.9884e-05 | 9.0523e-07 | 77.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | FUSE | 3 | 13 | 1934 | 0.00035014 | 2.3536e-06 | 148.7692
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 6 | 247 | 59564 | 0.010784 | 4.4718e-05 | 241.1498
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | FUSE | 8 | 82 | 8089 | 0.0014645 | 1.4846e-05 | 98.6463
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, OH | 26 | 530 | 42087 | 0.0075483 | 9.5056e-05 | 79.4094
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 30 | 64 | 36673 | 0.0065773 | 1.1478e-05 | 573.0156
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 4 | 512 | 9.1827e-05 | 7.174e-07 | 128
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | FUSE | 46 | 326 | 49887 | 0.0089472 | 5.8468e-05 | 153.0276
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 4 | 109 | 34959 | 0.0062699 | 1.9549e-05 | 320.7248
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | ARRESTER | 4 | 161 | 14000 | 0.002521 | 2.8992e-05 | 86.9565
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 4 | 25 | 2195 | 0.00039526 | 4.5018e-06 | 87.8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 2 | 280 | 5.042e-05 | 3.6014e-07 | 140
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | SPLICE, OH | 1 | 1 | 60 | 1.0804e-05 | 1.8007e-07 | 60
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 913 | 0.00016375 | 1.7935e-07 | 913
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CROSSARM | 13 | 126 | 11931 | 0.0021247 | 2.2438e-05 | 94.6905
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | INSULATOR | 4 | 1368 | 272028 | 0.049602 | 0.00024944 | 198.8509
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR UG | 10 | 30 | 5407 | 0.00098592 | 5.4703e-06 | 180.2333
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | RELAY | 1 | 45 | 9000 | 0.0016411 | 8.2054e-06 | 200
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CROSSARM | 33 | 10400 | 2259125 | 0.41193 | 0.0018964 | 217.2236
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | NONE | 10 | 574 | 100426 | 0.018312 | 0.00010466 | 174.9582
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 2154 | 242616 | 0.044239 | 0.00039276 | 112.6351
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CROSSARM | 3 | 235 | 74641 | 0.01361 | 4.285e-05 | 317.6213
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | INSULATOR | 2 | 22 | 3129 | 0.00057055 | 4.0115e-06 | 142.2273
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | UG | NONE | 1 | 486 | 128790 | 0.023484 | 8.8618e-05 | 265
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 1 | 11 | 2.0058e-06 | 1.8234e-07 | 11
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 166 | 54394 | 0.0099183 | 3.0269e-05 | 327.6747
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 161 | 4186 | 0.00076328 | 2.9357e-05 | 26
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 4 | 4296 | 0.00078334 | 7.2937e-07 | 1074
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 15 | 1328 | 0.00023818 | 2.6903e-06 | 88.5333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 1490 | 27447 | 0.0049226 | 0.00026723 | 18.4208
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | FUSE | 4 | 34 | 1677 | 0.00030361 | 6.1556e-06 | 49.3235
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | PEDESTAL | 1 | 5 | 155 | 2.8062e-05 | 9.0523e-07 | 31
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CROSSARM | 12 | 3674 | 763591 | 0.13825 | 0.00066516 | 207.8364
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 129 | 6679 | 1557375 | 0.28044 | 0.0012027 | 233.1749
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 226 | 2098 | 253554 | 0.045658 | 0.00037779 | 120.8551
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 42 | 258 | 480406 | 0.086976 | 4.671e-05 | 1862.0388
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 101 | 1.8286e-05 | 1.8105e-07 | 101
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 181 | 1380 | 400637 | 0.073053 | 0.00025163 | 290.3167
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CUTOUT | 475 | 19043 | 1766248 | 0.32206 | 0.0034723 | 92.7505
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | NONE | 227 | 18435 | 1712745 | 0.31231 | 0.0033615 | 92.9072
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | NONE | 467 | 9447 | 1399746 | 0.25523 | 0.0017226 | 148.1683
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | FUSE | 13 | 125 | 13784 | 0.0024821 | 2.2509e-05 | 110.272
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 121 | 3158 | 414374 | 0.074318 | 0.00056639 | 131.2141
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 161 | 18163 | 5968880 | 1.0629 | 0.0032345 | 328.6285
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 80 | 723 | 159426 | 0.028391 | 0.00012875 | 220.5062
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 16 | 189 | 62899 | 0.011201 | 3.3657e-05 | 332.7989
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 2 | 13 | 3582 | 0.00063788 | 2.315e-06 | 275.5385
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 2 | 230 | 4.1251e-05 | 3.587e-07 | 115
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | FUSE | 1 | 2 | 186 | 3.3675e-05 | 3.6209e-07 | 93
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 60 | 22260 | 0.0040301 | 1.0863e-05 | 371
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 154 | 3213 | 441716 | 0.078661 | 0.00057217 | 137.4777
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | NONE | 270 | 2832 | 392461 | 0.069889 | 0.00050432 | 138.5809
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | U | CONDUCTOR OVERHEAD | 2 | 17 | 4788 | 0.00085265 | 3.0274e-06 | 281.6471
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 3 | 32 | 3556 | 0.00063325 | 5.6986e-06 | 111.125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 2 | 495 | 13860 | 0.0024682 | 8.815e-05 | 28
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 57 | 5415 | 0.00097118 | 1.0223e-05 | 95
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONN/CLAMP | 1 | 1 | 111 | 1.9908e-05 | 1.7935e-07 | 111
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | POLE | 1 | 63 | 10311 | 0.0018493 | 1.1299e-05 | 163.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | NONE | 1 | 3 | 1110 | 0.00019908 | 5.3805e-07 | 370
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 2 | 314 | 5.6849e-05 | 3.6209e-07 | 157
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONN/CLAMP | 2 | 19 | 3558 | 0.00064877 | 3.4645e-06 | 187.2632
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | O | NONE | 3 | 38 | 6847 | 0.0012485 | 6.929e-06 | 180.1842
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | CONN/CLAMP | 3 | 3382 | 501928 | 0.089383 | 0.00060227 | 148.4116
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | NONE | 8 | 417 | 51568 | 0.0091832 | 7.4259e-05 | 123.6643
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 16 | 427 | 308575 | 0.055566 | 7.6891e-05 | 722.6581
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | POLE | 3 | 26 | 3739 | 0.00067329 | 4.6819e-06 | 143.8077
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | POLE HARDWARE | 2 | 88 | 3158 | 0.00056867 | 1.5846e-05 | 35.8864
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 6 | 620 | 0.00011164 | 1.0804e-06 | 103.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 2 | 170 | 3.0612e-05 | 3.6014e-07 | 85
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE | 3 | 52 | 39679 | 0.0071164 | 9.3262e-06 | 763.0577
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | METERING | 1 | 8 | 96 | 1.7218e-05 | 1.4348e-06 | 12
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 20 | 112 | 39236 | 0.0071544 | 2.0422e-05 | 350.3214
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | INSULATOR | 1 | 430 | 38279 | 0.0069799 | 7.8407e-05 | 89.0209
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | NONE | 8 | 695 | 136925 | 0.024967 | 0.00012673 | 197.0144
AEP Total | 2020 | 5484199 | SUBTRANSMISSION LINE | TOR | NONE | 1 | 490 | 126588 | 0.023082 | 8.9348e-05 | 258.3429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 6 | 91 | 16756 | 0.0030553 | 1.6593e-05 | 184.1319
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | FUSE | 6 | 20 | 1217 | 0.00022191 | 3.6468e-06 | 60.85
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | FUSE | 402 | 1890 | 247387 | 0.044055 | 0.00033657 | 130.8926
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONN/CLAMP | 7 | 11 | 1186 | 0.00021271 | 1.9729e-06 | 107.8182
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 2 | 468 | 8.3936e-05 | 3.587e-07 | 234
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | SWITCH, OH | 5 | 126 | 2242 | 0.0004021 | 2.2598e-05 | 17.7937
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | INSULATOR | 5 | 314 | 22108 | 0.003981 | 5.6543e-05 | 70.4076
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 398 | 4373 | 1075209 | 0.19147 | 0.00077874 | 245.8745
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 12 | 770 | 215344 | 0.038348 | 0.00013712 | 279.6675
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 149 | 4910 | 772383 | 0.13755 | 0.00087437 | 157.3081
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 56 | 4536 | 0.00080777 | 9.9725e-06 | 81
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | NONE | 183 | 17101 | 1750252 | 0.31168 | 0.0030453 | 102.3479
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE | 44 | 10421 | 2147661 | 0.38246 | 0.0018558 | 206.0897
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | NONE | 2 | 232 | 14648 | 0.0026085 | 4.1315e-05 | 63.1379
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | FUSE | 2 | 61 | 18318 | 0.0032621 | 1.0863e-05 | 300.2951
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 7 | 592 | 74594 | 0.013284 | 0.00010542 | 126.0034
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | POLE | 23 | 1789 | 325891 | 0.058035 | 0.00031858 | 182.1638
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 4 | 22 | 3890 | 0.00069273 | 3.9178e-06 | 176.8182
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | NONE | 1 | 1 | 53 | 9.4382e-06 | 1.7808e-07 | 53
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | METERING | 1 | 1 | 40 | 7.1232e-06 | 1.7808e-07 | 40
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 122 | 9062 | 0.0016253 | 2.1881e-05 | 74.2787
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | METERING | 2 | 4 | 799 | 0.0001433 | 7.174e-07 | 199.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 5 | 9 | 5587 | 0.00099493 | 1.6027e-06 | 620.7778
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 6 | 18 | 5250 | 0.00093492 | 3.2054e-06 | 291.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CROSSARM | 1 | 2 | 192 | 3.4191e-05 | 3.5616e-07 | 96
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 2 | 3 | 344 | 6.1259e-05 | 5.3424e-07 | 114.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 11 | 1690 | 174089 | 0.031002 | 0.00030095 | 103.0112
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 3 | 1181 | 52664 | 0.0093784 | 0.00021031 | 44.5927
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CUTOUT | 4 | 11 | 146 | 2.6e-05 | 1.9589e-06 | 13.2727
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 67 | 1.1931e-05 | 1.7808e-07 | 67
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | SCO | NONE | 1 | 2 | 520 | 9.2601e-05 | 3.5616e-07 | 260
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 16 | 320 | 5.6986e-05 | 2.8493e-06 | 20
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | NONE | 3 | 253 | 35549 | 0.0063306 | 4.5054e-05 | 140.5099
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | CONDUCTOR UG | 1 | 1 | 537 | 9.5629e-05 | 1.7808e-07 | 537
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | O | NONE | 3 | 2630 | 205625 | 0.037027 | 0.00047359 | 78.1844
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 272 | 4.8783e-05 | 1.7935e-07 | 272
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | NONE | 3 | 533 | 59694 | 0.01063 | 9.4917e-05 | 111.9962
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | FUSE | 7 | 20 | 15385 | 0.0027398 | 3.5616e-06 | 769.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 16 | 7920 | 0.0014205 | 2.8696e-06 | 495
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | SPLICE, OH | 1 | 617 | 45069 | 0.008218 | 0.00011251 | 73.0454
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | NONE | 6 | 152 | 34702 | 0.0061797 | 2.7068e-05 | 228.3026
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 1193 | 120984 | 0.021545 | 0.00021245 | 101.4116
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | NONE | 3 | 6 | 585 | 0.00010492 | 1.0761e-06 | 97.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 94 | 1.674e-05 | 1.7808e-07 | 94
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE | 9 | 382 | 152779 | 0.027207 | 6.8026e-05 | 399.945
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 2 | 8 | 8160 | 0.0014531 | 1.4246e-06 | 1020
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | SCO | REGULATOR | 1 | 1072 | 195104 | 0.034992 | 0.00019226 | 182
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 17 | 2890 | 0.00051832 | 3.049e-06 | 170
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | TOR | NONE | 6 | 3209 | 445340 | 0.080193 | 0.00057785 | 138.7784
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | NONE | 14 | 3072 | 841005 | 0.15144 | 0.00055318 | 273.7646
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 1 | 20 | 11880 | 0.0021393 | 3.6014e-06 | 594
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 9 | 84 | 55451 | 0.0098747 | 1.4959e-05 | 660.131
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 7 | 84 | 12123 | 0.0021589 | 1.4959e-05 | 144.3214
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 25 | 3535 | 1099262 | 0.19576 | 0.00062951 | 310.9652
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 44 | 2165 | 0.00038554 | 7.8355e-06 | 49.2045
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | TRANSFORMER, OH | 1 | 3 | 678 | 0.0001216 | 5.3805e-07 | 226
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | METERING | 1 | 2 | 682 | 0.00012347 | 3.6209e-07 | 341
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | METERING | 1 | 3 | 204 | 3.6933e-05 | 5.4314e-07 | 68
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | NONE | 1 | 905 | 83260 | 0.015182 | 0.00016502 | 92
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CUTOUT | 2 | 20 | 1488 | 0.00027132 | 3.6468e-06 | 74.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 6 | 1668 | 0.00030415 | 1.0941e-06 | 278
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 194 | 3.5123e-05 | 1.8105e-07 | 194
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 8 | 1872 | 0.00033892 | 1.4484e-06 | 234
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 1 | 25 | 4.5018e-06 | 1.8007e-07 | 25
AEP Total | 2022 | 5553337 | PARTIAL POWER | WFS | FUSE | 1 | 4 | 792 | 0.00014262 | 7.2029e-07 | 198
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE | 14 | 2398 | 252469 | 0.04496 | 0.00042704 | 105.2832
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | GUY/ANCHOR | 1 | 1 | 167 | 2.9739e-05 | 1.7808e-07 | 167
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 123 | 2.1904e-05 | 1.7808e-07 | 123
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | F | NONE | 1 | 2632 | 55272 | 0.0098428 | 0.00046871 | 21
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | NONE | 1 | 1 | 1357 | 0.00024165 | 1.7808e-07 | 1357
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 14 | 43 | 1764 | 0.00031937 | 7.785e-06 | 41.0233
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 124 | 440 | 50183 | 0.0090854 | 7.966e-05 | 114.0523
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 21 | 491 | 69713 | 0.012621 | 8.8894e-05 | 141.9817
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | POLE | 1 | 4 | 572 | 0.00010356 | 7.2419e-07 | 143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | FUSE | 1 | 1 | 525 | 9.5049e-05 | 1.8105e-07 | 525
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | FUSE | 5 | 15 | 1383 | 0.00025039 | 2.7157e-06 | 92.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | NONE | 363 | 12120 | 1493083 | 0.26886 | 0.0021825 | 123.1917
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 4 | 7 | 1060 | 0.00019088 | 1.2605e-06 | 151.4286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 139 | 6762 | 1059956 | 0.19087 | 0.0012176 | 156.7518
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | METERING | 3 | 3 | 301 | 5.4202e-05 | 5.4022e-07 | 100.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 10 | 2078 | 207009 | 0.037277 | 0.00037419 | 99.6193
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 2 | 2250 | 0.00040516 | 3.6014e-07 | 1125
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CUTOUT | 70 | 2210 | 187082 | 0.033688 | 0.00039796 | 84.6525
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 18 | 4320 | 0.0007693 | 3.2054e-06 | 240
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 17 | 70 | 11815 | 0.002104 | 1.2466e-05 | 168.7857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | POLE | 4 | 779 | 56901 | 0.010133 | 0.00013872 | 73.0436
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | NONE | 2 | 18 | 9216 | 0.0016412 | 3.2054e-06 | 512
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, STATION SERVICE | 1 | 1 | 299 | 5.3246e-05 | 1.7808e-07 | 299
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CUTOUT | 8 | 21 | 3851 | 0.00068579 | 3.7397e-06 | 183.381
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | O | NONE | 3 | 1612 | 154766 | 0.027561 | 0.00028706 | 96.0087
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 1 | 62 | 1.112e-05 | 1.7935e-07 | 62
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | SCO | INSULATOR | 1 | 147 | 5733 | 0.0010209 | 2.6178e-05 | 39
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | NONE | 1 | 1 | 121 | 2.1548e-05 | 1.7808e-07 | 121
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | POLE | 1 | 9 | 2565 | 0.00046003 | 1.6142e-06 | 285
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | METERING | 6 | 12 | 7478 | 0.0013317 | 2.137e-06 | 623.1667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 2 | 616 | 0.0001097 | 3.5616e-07 | 308
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | METERING | 1 | 1 | 75 | 1.3676e-05 | 1.8234e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 1 | 25 | 4.5018e-06 | 1.8007e-07 | 25
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 179 | 3.2104e-05 | 1.7935e-07 | 179
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | NONE | 1 | 1 | 168 | 3.0131e-05 | 1.7935e-07 | 168
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | FUSE | 2 | 5 | 664 | 0.00011909 | 8.9675e-07 | 132.8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | NONE | 1 | 209 | 33858 | 0.0060724 | 3.7484e-05 | 162
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | FUSE | 1 | 1 | 28 | 5.0218e-06 | 1.7935e-07 | 28
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 4 | 46 | 27644 | 0.0049228 | 8.1917e-06 | 600.9565
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 2 | 1172 | 38688 | 0.0068896 | 0.00020871 | 33.0102
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SO | NONE | 5 | 38 | 23084 | 0.0041108 | 6.767e-06 | 607.4737
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | NONE | 3 | 7 | 852 | 0.00015172 | 1.2466e-06 | 121.7143
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 1 | 79 | 1.4068e-05 | 1.7808e-07 | 79
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CUTOUT | 405 | 14294 | 1682203 | 0.3017 | 0.0025636 | 117.686
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 2 | 15 | 4529 | 0.00081228 | 2.6903e-06 | 301.9333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 26 | 1222 | 153705 | 0.027678 | 0.00022005 | 125.7815
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE | 130 | 6785 | 3627147 | 0.65053 | 0.0012169 | 534.5832
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | NONE | 4 | 668 | 66373 | 0.012017 | 0.00012094 | 99.3608
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | FUSE | 1 | 4 | 392 | 7.097e-05 | 7.2419e-07 | 98
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | FUSE | 303 | 1078 | 108273 | 0.019743 | 0.00019656 | 100.4388
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 116 | 4489 | 615599 | 0.11225 | 0.00081853 | 137.135
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | FUSE | 6 | 31 | 48408 | 0.0088268 | 5.6526e-06 | 1561.5484
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | NONE | 110 | 2359 | 280527 | 0.051152 | 0.00043014 | 118.9178
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONN/CLAMP | 1 | 1 | 237 | 4.3215e-05 | 1.8234e-07 | 237
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | TOR | NONE | 1 | 19 | 33991 | 0.006198 | 3.4645e-06 | 1789
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | POLE | 4 | 529 | 32151 | 0.0058625 | 9.6459e-05 | 60.7769
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 2 | 24 | 1028 | 0.00018745 | 4.3762e-06 | 42.8333
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CUTOUT | 1 | 4 | 572 | 0.0001043 | 7.2937e-07 | 143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 5 | 69 | 27877 | 0.0050831 | 1.2582e-05 | 404.0145
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABX | NONE | 1 | 355 | 62835 | 0.011457 | 6.4731e-05 | 177
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONN/CLAMP | 14 | 37 | 5543 | 0.00099814 | 6.6627e-06 | 149.8108
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | NONE | 18 | 805 | 194986 | 0.035112 | 0.00014496 | 242.2186
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 136 | 38188 | 0.0068766 | 2.449e-05 | 280.7941
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | SCO | NONE | 3 | 1581 | 85655 | 0.015424 | 0.00028469 | 54.1777
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | NONE | 33 | 829 | 129762 | 0.023273 | 0.00014868 | 156.5283
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | NONE | 22 | 259 | 26313 | 0.0047192 | 4.6452e-05 | 101.5946
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | F | NONE | 2 | 987 | 107970 | 0.019227 | 0.00017576 | 109.3921
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 1 | 239 | 12473 | 0.0022212 | 4.2561e-05 | 52.1883
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | ARRESTER | 1 | 9 | 990 | 0.00017827 | 1.6206e-06 | 110
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 26 | 3770 | 0.00068743 | 4.7409e-06 | 145
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TIR | NONE | 1 | 2 | 250 | 4.452e-05 | 3.5616e-07 | 125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SO | FUSE | 1 | 3 | 189 | 3.3657e-05 | 5.3424e-07 | 63
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | F | NONE | 2 | 929 | 19717 | 0.0035112 | 0.00016544 | 21.2239
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE | 1 | 3 | 567 | 0.00010097 | 5.3424e-07 | 189
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 3 | 561 | 9.9903e-05 | 5.3424e-07 | 187
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 2 | 470 | 8.3698e-05 | 3.5616e-07 | 235
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 430 | 39130 | 0.007018 | 7.7121e-05 | 91
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 1 | 307 | 5.5282e-05 | 1.8007e-07 | 307
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 320 | 6275 | 1140467 | 0.20648 | 0.0011361 | 181.7477
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | NONE | 307 | 20611 | 1762355 | 0.31907 | 0.0037315 | 85.5056
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | CIRCUIT SWITCHER | 1 | 3 | 57 | 1.032e-05 | 5.4314e-07 | 19
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | POLE | 7 | 105 | 102560 | 0.018568 | 1.901e-05 | 976.7619
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, OH | 7 | 38 | 7066 | 0.0012793 | 6.8798e-06 | 185.9474
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | NONE | 90 | 2038 | 186676 | 0.033797 | 0.00036897 | 91.5976
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | REGULATOR | 9 | 2380 | 199542 | 0.036126 | 0.00043089 | 83.8412
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 1 | 35 | 6825 | 0.0012356 | 6.3366e-06 | 195
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CUTOUT | 7 | 38 | 8122 | 0.0014705 | 6.8798e-06 | 213.7368
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | NONE | 6 | 30 | 17939 | 0.0032478 | 5.4314e-06 | 597.9667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE | 26 | 5618 | 1441905 | 0.26105 | 0.0010171 | 256.6581
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 12 | 1800 | 350258 | 0.063413 | 0.00032588 | 194.5878
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | NONE | 26 | 567 | 80835 | 0.014635 | 0.00010265 | 142.5661
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | SPLICE, OH | 1 | 246 | 79212 | 0.014341 | 4.4537e-05 | 322
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 7 | 105 | 22620 | 0.0040953 | 1.901e-05 | 215.4286
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 1 | 117 | 2.1182e-05 | 1.8105e-07 | 117
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CUTOUT | 5 | 115 | 16008 | 0.0028982 | 2.082e-05 | 139.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 1 | 71 | 1.2854e-05 | 1.8105e-07 | 71
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | FUSE | 3 | 176 | 54206 | 0.0098138 | 3.1864e-05 | 307.9886
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 30 | 414 | 587942 | 0.10587 | 7.455e-05 | 1420.1498
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | SPLICE, OH | 6 | 145 | 66180 | 0.011869 | 2.6006e-05 | 456.4138
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | ARRESTER | 3 | 71 | 33897 | 0.0060794 | 1.2734e-05 | 477.4225
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 9 | 9498 | 0.0017103 | 1.6206e-06 | 1055.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | METERING | 6 | 6 | 621 | 0.00011182 | 1.0804e-06 | 103.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 7 | 28 | 4821 | 0.00086465 | 5.0218e-06 | 172.1786
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONN/CLAMP | 4 | 12 | 531 | 9.5235e-05 | 2.1522e-06 | 44.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CUTOUT | 4 | 575 | 37124 | 0.006685 | 0.00010354 | 64.5635
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 5 | 706 | 182917 | 0.032938 | 0.00012713 | 259.0892
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | SWITCH, OH | 1 | 4 | 828 | 0.0001491 | 7.2029e-07 | 207
AEP Total | 2023 | 5575683 | PARTIAL POWER | WFS | CONDUCTOR OVERHEAD | 1 | 1 | 54 | 9.6849e-06 | 1.7935e-07 | 54
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 8 | 2106 | 0.00037771 | 1.4348e-06 | 263.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CUTOUT | 5 | 20 | 3026 | 0.00054271 | 3.587e-06 | 151.3
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CUTOUT | 5 | 15 | 3778 | 0.00067759 | 2.6903e-06 | 251.8667
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | POLE | 1 | 19 | 3116 | 0.00055886 | 3.4077e-06 | 164
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 5 | 115 | 33324 | 0.0059767 | 2.0625e-05 | 289.7739
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 11 | 36 | 14642 | 0.0026074 | 6.4109e-06 | 406.7222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 19 | 1436 | 197125 | 0.035104 | 0.00025572 | 137.2737
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 1 | 75 | 1.3356e-05 | 1.7808e-07 | 75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 9 | 1948 | 306922 | 0.054657 | 0.0003469 | 157.5575
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | POLE | 1 | 22 | 748 | 0.00013542 | 3.983e-06 | 34
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 72 | 632 | 219703 | 0.039125 | 0.00011255 | 347.6313
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 25 | 877 | 314361 | 0.055981 | 0.00015618 | 358.4504
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 36 | 78 | 6821 | 0.0012147 | 1.389e-05 | 87.4487
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | SCO | NONE | 2 | 1997 | 47746 | 0.0085026 | 0.00035563 | 23.9089
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 1 | 28 | 2268 | 0.00040388 | 4.9862e-06 | 81
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 15 | 5580 | 0.0010008 | 2.6903e-06 | 372
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | FUSE | 1 | 1 | 186 | 3.3916e-05 | 1.8234e-07 | 186
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | SCO | POLE | 1 | 17 | 391 | 7.1296e-05 | 3.0998e-06 | 23
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | FUSE | 2 | 5 | 578 | 0.00010539 | 9.1171e-07 | 115.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | INSULATOR | 1 | 42 | 3276 | 0.00059735 | 7.6584e-06 | 78
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 47 | 5730 | 0.0010374 | 8.5092e-06 | 121.9149
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | FUSE | 9 | 52 | 5335 | 0.00095006 | 9.2601e-06 | 102.5962
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 7 | 1554 | 354064 | 0.063052 | 0.00027674 | 227.8404
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 2 | 253 | 124533 | 0.022177 | 4.5054e-05 | 492.2253
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 2 | 13 | 813 | 0.00014478 | 2.315e-06 | 62.5385
AEP Total | 2024 | 5615460 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 7 | 728 | 0.00012964 | 1.2466e-06 | 104
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | NONE | 10 | 66 | 9223 | 0.0016424 | 1.1753e-05 | 139.7424
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | NONE | 3 | 276 | 9836 | 0.0017516 | 4.915e-05 | 35.6377
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 4 | 8 | 800 | 0.00014246 | 1.4246e-06 | 100
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 2 | 2080 | 0.00037041 | 3.5616e-07 | 1040
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | NONE | 1 | 1 | 65 | 1.1575e-05 | 1.7808e-07 | 65
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 397 | 7.0698e-05 | 3.5616e-07 | 198.5
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TOR | NONE | 11 | 7494 | 1801951 | 0.32089 | 0.0013345 | 240.4525
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 81 | 9153 | 0.00163 | 1.4424e-05 | 113
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | METERING | 2 | 4 | 1552 | 0.00027638 | 7.1232e-07 | 388
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 6 | 11 | 1809 | 0.00032751 | 1.9915e-06 | 164.4545
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 1 | 3 | 921 | 0.00016674 | 5.4314e-07 | 307
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | REGULATOR | 2 | 202 | 1530 | 0.000277 | 3.6571e-05 | 7.5743
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | FUSE | 257 | 3142 | 759608 | 0.13851 | 0.00057292 | 241.7594
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 122 | 3943 | 782823 | 0.14274 | 0.00071897 | 198.5349
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | POLE | 90 | 950 | 91839 | 0.016746 | 0.00017322 | 96.6726
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CUTOUT | 1 | 2 | 74 | 1.3493e-05 | 3.6468e-07 | 37
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | INSULATOR | 7 | 72 | 8027 | 0.0014637 | 1.3129e-05 | 111.4861
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | FUSE | 15 | 246 | 62308 | 0.011361 | 4.4856e-05 | 253.2846
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | FUSE | 1 | 2 | 234 | 4.2668e-05 | 3.6468e-07 | 117
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 17 | 1479 | 0.00026968 | 3.0998e-06 | 87
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | NONE | 75 | 8076 | 1534111 | 0.27625 | 0.0014543 | 189.9593
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | NONE | 170 | 12574 | 1101875 | 0.19842 | 0.0022642 | 87.6312
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SWITCH, OH | 8 | 636 | 56882 | 0.010243 | 0.00011453 | 89.4371
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 17 | 1644 | 817820 | 0.14727 | 0.00029604 | 497.4574
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE | 49 | 9053 | 1994580 | 0.35917 | 0.0016302 | 220.3225
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CROSSARM | 39 | 10157 | 3856194 | 0.69439 | 0.001829 | 379.6588
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 33 | 3300 | 0.00059424 | 5.9424e-06 | 100
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE | 8 | 111 | 71283 | 0.012836 | 1.9988e-05 | 642.1892
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | POLE | 90 | 1920 | 309065 | 0.055431 | 0.00034435 | 160.9714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | NONE | 192 | 1933 | 88025 | 0.015787 | 0.00034668 | 45.538
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | FUSE | 290 | 907 | 82233 | 0.014749 | 0.00016267 | 90.6648
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | FW | NONE | 1 | 335 | 2345 | 0.00042227 | 6.0324e-05 | 7
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 108 | 265 | 29009 | 0.0052028 | 4.7528e-05 | 109.4679
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 14 | 20 | 552 | 9.94e-05 | 3.6014e-06 | 27.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE | 48 | 7668 | 1263326 | 0.22658 | 0.0013753 | 164.753
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | VA | NONE | 4 | 2270 | 352798 | 0.062826 | 0.00040424 | 155.4176
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | CUTOUT | 1 | 2 | 50 | 8.904e-06 | 3.5616e-07 | 25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 5 | 2235 | 0.00039801 | 8.904e-07 | 447
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | FUSE | 2 | 7 | 658 | 0.00011718 | 1.2466e-06 | 94
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | POLE | 1 | 42 | 43048 | 0.007666 | 7.4794e-06 | 1024.9524
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WI | NONE | 1 | 603 | 97686 | 0.017812 | 0.00010995 | 162
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | FUSE | 1 | 4 | 456 | 8.2557e-05 | 7.2419e-07 | 114
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | NONE | 1 | 1 | 146 | 2.629e-05 | 1.8007e-07 | 146
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 9 | 334 | 6.0144e-05 | 1.6206e-06 | 37.1111
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | FUSE | 1 | 1 | 37 | 6.6627e-06 | 1.8007e-07 | 37
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | NONE | 1 | 1 | 253 | 4.5558e-05 | 1.8007e-07 | 253
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 224 | 42112 | 0.0075832 | 4.0336e-05 | 188
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | REGULATOR | 1 | 150 | 17250 | 0.0031062 | 2.7011e-05 | 115
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 1 | 97 | 1.7467e-05 | 1.8007e-07 | 97
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 2 | 10 | 5472 | 0.00098535 | 1.8007e-06 | 547.2
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | FUSE | 2 | 2 | 139 | 2.503e-05 | 3.6014e-07 | 69.5
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 1 | 1119 | 226038 | 0.040253 | 0.00019927 | 202
AEP Total | 2020 | 5484199 | PARTIAL POWER | UG | CONDUCTOR UG | 1 | 3 | 1407 | 0.00025656 | 5.4703e-07 | 469
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 34 | 1904 | 0.00033906 | 6.0547e-06 | 56
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 1 | 23 | 5474 | 0.00097481 | 4.0958e-06 | 238
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 11 | 979 | 0.00017851 | 2.0058e-06 | 89
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | FUSE | 7 | 26 | 80099 | 0.014502 | 4.7072e-06 | 3080.7308
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | FUSE | 109 | 634 | 63418 | 0.011374 | 0.00011371 | 100.0284
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | FUSE | 88 | 606 | 100621 | 0.018046 | 0.00010869 | 166.0413
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 6 | 18 | 1631 | 0.0002937 | 3.2413e-06 | 90.6111
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | NONE | 39 | 1593 | 243787 | 0.043723 | 0.0002857 | 153.0364
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 1 | 168 | 3.0252e-05 | 1.8007e-07 | 168
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 2 | 94 | 1.6927e-05 | 3.6014e-07 | 47
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | FUSE | 27 | 135 | 7644 | 0.001371 | 2.4212e-05 | 56.6222
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR UG | 12 | 14 | 3762 | 0.00067472 | 2.5109e-06 | 268.7143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 1 | 2 | 630 | 0.00011299 | 3.587e-07 | 315
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | POLE | 1 | 20 | 11920 | 0.0021379 | 3.587e-06 | 596
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | ARRESTER | 2 | 2 | 143 | 2.5647e-05 | 3.587e-07 | 71.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 228 | 4.1056e-05 | 1.8007e-07 | 228
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | NONE | 20 | 210 | 74112 | 0.013292 | 3.7664e-05 | 352.9143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 56 | 1977 | 435530 | 0.077559 | 0.00035206 | 220.2984
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 182 | 2159 | 350413 | 0.062401 | 0.00038447 | 162.3034
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 42 | 504 | 42631 | 0.0075917 | 8.9752e-05 | 84.5853
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | FUSE | 76 | 358 | 44132 | 0.007859 | 6.3753e-05 | 123.2737
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 50 | 10441 | 1946843 | 0.34669 | 0.0018593 | 186.4614
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | FUSE | 1 | 1 | 133 | 2.3854e-05 | 1.7935e-07 | 133
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | FUSE | 7 | 84 | 13303 | 0.002369 | 1.4959e-05 | 158.369
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | NONE | 3 | 3 | 151 | 2.7082e-05 | 5.3805e-07 | 50.3333
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | FUSE | 2 | 7 | 704 | 0.00012626 | 1.2555e-06 | 100.5714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | NONE | 2 | 6 | 196 | 3.5153e-05 | 1.0761e-06 | 32.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | FW | NONE | 1 | 2018 | 30270 | 0.0054289 | 0.00036193 | 15
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 30 | 1979 | 329096 | 0.058605 | 0.00035242 | 166.2941
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | METERING | 1 | 1 | 70 | 1.2466e-05 | 1.7808e-07 | 70
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 36 | 509 | 189418 | 0.033732 | 9.0643e-05 | 372.1375
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 8 | 23 | 9370 | 0.0016686 | 4.0958e-06 | 407.3913
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 1 | 83 | 1.4886e-05 | 1.7935e-07 | 83
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | TRANSFORMER, OH | 1 | 16 | 4288 | 0.00077215 | 2.8812e-06 | 268
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | NONE | 7 | 1852 | 242983 | 0.043991 | 0.0003353 | 131.2003
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | METERING | 1 | 1 | 116 | 2.1001e-05 | 1.8105e-07 | 116
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 7 | 978 | 215212 | 0.038963 | 0.00017706 | 220.0532
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | FUSE | 13 | 56 | 2327 | 0.00042129 | 1.0139e-05 | 41.5536
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE | 32 | 6109 | 1377964 | 0.24948 | 0.001106 | 225.5629
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | FUSE | 129 | 526 | 97287 | 0.017613 | 9.523e-05 | 184.9563
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONN/CLAMP | 1 | 3 | 393 | 7.1151e-05 | 5.4314e-07 | 131
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 35 | 332 | 104233 | 0.018871 | 6.0107e-05 | 313.9548
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | POLE | 4 | 226 | 165693 | 0.029998 | 4.0916e-05 | 733.1549
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CUTOUT | 9 | 209 | 27171 | 0.0049192 | 3.7839e-05 | 130.0048
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CROSSARM | 6 | 489 | 20599 | 0.0037294 | 8.8532e-05 | 42.1247
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 197 | 3.5666e-05 | 1.8105e-07 | 197
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | FUSE | 259 | 2735 | 524802 | 0.094502 | 0.0004925 | 191.8837
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | INSULATOR | 2 | 6 | 1165 | 0.00021092 | 1.0863e-06 | 194.1667
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | SPLICE, OH | 1 | 1 | 528 | 9.5592e-05 | 1.8105e-07 | 528
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 1 | 241 | 4.3632e-05 | 1.8105e-07 | 241
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONN/CLAMP | 6 | 49 | 4078 | 0.00073831 | 8.8713e-06 | 83.2245
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 600 | 66160 | 0.011978 | 0.00010863 | 110.2667
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | NONE | 2 | 5 | 1226 | 0.00022196 | 9.0523e-07 | 245.2
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | FUSE | 1203 | 7592 | 811353 | 0.14794 | 0.0013843 | 106.8695
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | NONE | 11 | 32 | 5290 | 0.00096459 | 5.8349e-06 | 165.3125
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | NONE | 5 | 18 | 24680 | 0.0045002 | 3.2822e-06 | 1371.1111
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CROSSARM | 17 | 2904 | 299275 | 0.05457 | 0.00052952 | 103.0561
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 320 | 5760 | 0.0010503 | 5.8349e-05 | 18
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 104 | 1.8964e-05 | 1.8234e-07 | 104
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | NONE | 19 | 405 | 88033 | 0.016052 | 7.3849e-05 | 217.3654
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CROSSARM | 8 | 77 | 6476 | 0.0011808 | 1.404e-05 | 84.1039
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | NONE | 58 | 1220 | 1192185 | 0.21468 | 0.00021969 | 977.2008
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 9 | 14 | 1630 | 0.00029352 | 2.521e-06 | 116.4286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | NONE | 55 | 7455 | 1135646 | 0.20368 | 0.0013371 | 152.3335
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | FUSE | 254 | 1048 | 156590 | 0.028084 | 0.00018796 | 149.4179
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, OH | 9 | 22 | 13034 | 0.0023471 | 3.9616e-06 | 592.4545
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE | 25 | 3002 | 505654 | 0.090689 | 0.00053841 | 168.439
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 4 | 152 | 19393 | 0.0034781 | 2.7261e-05 | 127.5855
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 1 | 239 | 4.3037e-05 | 1.8007e-07 | 239
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 7 | 533 | 55859 | 0.010018 | 9.5594e-05 | 104.8011
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | NONE | 3 | 11 | 2083 | 0.00037359 | 1.9729e-06 | 189.3636
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | ARRESTER | 2 | 8 | 141 | 2.539e-05 | 1.4406e-06 | 17.625
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 1 | 119 | 2.1429e-05 | 1.8007e-07 | 119
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 3 | 1068 | 0.00019155 | 5.3805e-07 | 356
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | ARRESTER | 4 | 3282 | 567725 | 0.10352 | 0.00059845 | 172.9814
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | ARRESTER | 2 | 11 | 640 | 0.0001167 | 2.0058e-06 | 58.1818
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | POLE | 1 | 907 | 18140 | 0.0033077 | 0.00016538 | 20
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | O | OTHER EQUIPMENT | 2 | 3254 | 292860 | 0.053401 | 0.00059334 | 90
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 26 | 4.7409e-06 | 1.8234e-07 | 26
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 8 | 976 | 0.00017797 | 1.4587e-06 | 122
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | FUSE | 3 | 14 | 3400 | 0.00061996 | 2.5528e-06 | 242.8571
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 9 | 37 | 3572 | 0.0006361 | 6.589e-06 | 96.5405
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | FUSE | 65 | 220 | 22714 | 0.0041417 | 4.0115e-05 | 103.2455
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | FUSE | 25 | 190 | 25662 | 0.0046793 | 3.4645e-05 | 135.0632
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | SCO | MOAB | 1 | 760 | 136040 | 0.024399 | 0.00013631 | 179
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | TOR | NONE | 3 | 2247 | 189944 | 0.034066 | 0.000403 | 84.5323
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 2 | 58 | 1.0402e-05 | 3.587e-07 | 29
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 2 | 7 | 494 | 8.8599e-05 | 1.2555e-06 | 70.5714
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | U | NONE | 2 | 2233 | 175896 | 0.031845 | 0.00040428 | 78.7712
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 74 | 845 | 112728 | 0.020075 | 0.00015048 | 133.4059
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 63 | 3327 | 712763 | 0.12693 | 0.00059247 | 214.2359
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 4 | 1435 | 233749 | 0.041626 | 0.00025554 | 162.8913
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | FUSE | 1 | 5 | 490 | 8.7259e-05 | 8.904e-07 | 98
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 27 | 332 | 74747 | 0.013311 | 5.9122e-05 | 225.1416
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 167 | 2.9739e-05 | 1.7808e-07 | 167
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONN/CLAMP | 3 | 81 | 3543 | 0.00063094 | 1.4424e-05 | 43.7407
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 3 | 1773 | 0.00031574 | 5.3424e-07 | 591
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 6 | 93 | 143419 | 0.02554 | 1.6561e-05 | 1542.1398
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | POLE | 8 | 297 | 70459 | 0.012547 | 5.289e-05 | 237.2357
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 8 | 50 | 11377 | 0.002026 | 8.904e-06 | 227.54
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | NONE | 1 | 11 | 1034 | 0.00018413 | 1.9589e-06 | 94
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, OH | 9 | 16 | 3515 | 0.00063042 | 2.8696e-06 | 219.6875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | ARRESTER | 2 | 5 | 1126 | 0.00020195 | 8.9675e-07 | 225.2
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | FUSE | 1 | 40 | 15680 | 0.0028122 | 7.174e-06 | 392
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | POLE | 5 | 1026 | 462169 | 0.08289 | 0.00018401 | 450.4571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 3 | 17 | 3111 | 0.00055796 | 3.049e-06 | 183
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | POLE | 1 | 7 | 3731 | 0.00066916 | 1.2555e-06 | 533
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | NONE | 63 | 10303 | 1322924 | 0.23559 | 0.0018348 | 128.4018
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | NONE | 22 | 86 | 5380 | 0.00095807 | 1.5315e-05 | 62.5581
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | FUSE | 24 | 200 | 9324 | 0.0016604 | 3.5616e-05 | 46.62
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 1 | 57 | 1.0223e-05 | 1.7935e-07 | 57
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, OH | 5 | 98 | 12239 | 0.0021795 | 1.7452e-05 | 124.8878
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 1 | 253 | 4.5376e-05 | 1.7935e-07 | 253
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 95 | 1.7107e-05 | 1.8007e-07 | 95
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 5 | 983 | 0.00017701 | 9.0036e-07 | 196.6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 726 | 0.00013073 | 5.4022e-07 | 242
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 32 | 187 | 15756 | 0.0028058 | 3.3301e-05 | 84.2567
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 1 | 67 | 1.2016e-05 | 1.7935e-07 | 67
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 394 | 22105 | 0.0039365 | 7.0163e-05 | 56.1041
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 74 | 1.3397e-05 | 1.8105e-07 | 74
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 132 | 17772 | 0.0032176 | 2.3898e-05 | 134.6364
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 3 | 2976 | 0.00053879 | 5.4314e-07 | 992
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | EQF | ARRESTER | 3 | 3555 | 1404207 | 0.25605 | 0.00064823 | 394.9949
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | POLE | 1 | 23 | 4692 | 0.00083555 | 4.0958e-06 | 204
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 63 | 1.1299e-05 | 1.7935e-07 | 63
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 62 | 42284 | 0.0076554 | 1.1225e-05 | 682
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | NONE | 1 | 39 | 5304 | 0.00096027 | 7.0608e-06 | 136
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 17 | 852 | 0.00015342 | 3.0612e-06 | 50.1176
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 5 | 874 | 0.00015937 | 9.1171e-07 | 174.8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONN/CLAMP | 3 | 260 | 15210 | 0.0027389 | 4.6819e-05 | 58.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | FUSE | 2 | 27 | 4890 | 0.00087081 | 4.8082e-06 | 181.1111
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 1 | 3161 | 0.00056291 | 1.7808e-07 | 3161
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 1598 | 362022 | 0.064469 | 0.00028457 | 226.5469
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | NONE | 4 | 56 | 11355 | 0.0020221 | 9.9725e-06 | 202.7679
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | SPLICE, OH | 1 | 1 | 130 | 2.315e-05 | 1.7808e-07 | 130
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | POLE | 1 | 52 | 10504 | 0.0018706 | 9.2601e-06 | 202
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 138 | 2.4575e-05 | 1.7808e-07 | 138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE | 2 | 143 | 15140 | 0.0027263 | 2.575e-05 | 105.8741
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 4 | 24 | 4462 | 0.00079459 | 4.2739e-06 | 185.9167
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 28 | 9116 | 0.0016234 | 4.9862e-06 | 325.5714
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 1 | 1399 | 283997 | 0.050574 | 0.00024913 | 203
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | FUSE | 2 | 5 | 443 | 7.8889e-05 | 8.904e-07 | 88.6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 6 | 13 | 350 | 6.2328e-05 | 2.315e-06 | 26.9231
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | SWITCH, OH | 3 | 2113 | 332095 | 0.060555 | 0.00038529 | 157.1675
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 101 | 27674 | 0.0050103 | 1.8286e-05 | 274
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | FW | NONE | 1 | 1042 | 20840 | 0.003773 | 0.00018865 | 20
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | INSULATOR | 6 | 6108 | 709224 | 0.1263 | 0.0010877 | 116.1139
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 15 | 118 | 11337 | 0.0020189 | 2.1013e-05 | 96.0763
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | NONE | 7 | 21 | 1269 | 0.00022598 | 3.7397e-06 | 60.4286
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 140 | 15447 | 0.0027508 | 2.4931e-05 | 110.3357
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 6 | 1230 | 0.00021904 | 1.0685e-06 | 205
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 2 | 50 | 8.904e-06 | 3.5616e-07 | 25
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | NONE | 1 | 1 | 112 | 1.9945e-05 | 1.7808e-07 | 112
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | CONDUCTOR UG | 1 | 1 | 315 | 5.6095e-05 | 1.7808e-07 | 315
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 1 | 75 | 1.3356e-05 | 1.7808e-07 | 75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 1 | 523 | 9.3136e-05 | 1.7808e-07 | 523
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | ERO | NONE | 3 | 1810 | 373225 | 0.066464 | 0.00032232 | 206.2017
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 9 | 6257 | 0.0011267 | 1.6206e-06 | 695.2222
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | REGULATOR | 1 | 930 | 191580 | 0.034933 | 0.00016958 | 206
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 2 | 484 | 8.7155e-05 | 3.6014e-07 | 242
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | NONE | 1 | 2 | 126 | 2.2975e-05 | 3.6468e-07 | 63
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | FUSE | 1 | 2 | 572 | 0.000103 | 3.6014e-07 | 286
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | ARRESTER | 1 | 3 | 552 | 9.94e-05 | 5.4022e-07 | 184
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 2 | 214 | 3.8109e-05 | 3.5616e-07 | 107
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 1 | 58 | 1.0329e-05 | 1.7808e-07 | 58
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CROSSARM | 3 | 25 | 1256 | 0.00022367 | 4.452e-06 | 50.24
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | NONE | 4 | 150 | 30208 | 0.0053794 | 2.6712e-05 | 201.3867
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 2 | 989 | 80654 | 0.014363 | 0.00017612 | 81.5511
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | FW | NONE | 1 | 3 | 816 | 0.00014531 | 5.3424e-07 | 272
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | POLE | 2 | 21 | 9483 | 0.0016887 | 3.7397e-06 | 451.5714
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 1 | 3 | 1923 | 0.00034245 | 5.3424e-07 | 641
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | NONE | 1 | 1 | 74 | 1.3178e-05 | 1.7808e-07 | 74
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | STATIC WIRE | 1 | 808 | 33128 | 0.0060406 | 0.00014733 | 41
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 2 | 254 | 4.5555e-05 | 3.587e-07 | 127
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 18 | 450 | 8.1032e-05 | 3.2413e-06 | 25
AEP Total | 2022 | 5553337 | PARTIAL POWER | WFS | POLE | 1 | 8 | 36600 | 0.0065906 | 1.4406e-06 | 4575
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 12 | 908 | 0.0001617 | 2.137e-06 | 75.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 2 | 5 | 555 | 9.8834e-05 | 8.904e-07 | 111
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 21 | 83 | 63904 | 0.01157 | 1.5027e-05 | 769.9277
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | METERING | 2 | 22 | 2170 | 0.00039287 | 3.983e-06 | 98.6364
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 123 | 9125 | 0.001652 | 2.2269e-05 | 74.187
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 113 | 3344 | 557703 | 0.10097 | 0.00060542 | 166.7772
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 11 | 2024 | 350442 | 0.063446 | 0.00036644 | 173.1433
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | FUSE | 10 | 105 | 15066 | 0.0027276 | 1.901e-05 | 143.4857
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | INSULATOR | 44 | 9509 | 1430600 | 0.259 | 0.0017216 | 150.4469
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CROSSARM | 17 | 1270 | 105597 | 0.019118 | 0.00022993 | 83.1472
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | FW | METERING | 1 | 777 | 13986 | 0.0025321 | 0.00014067 | 18
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | POLE | 1 | 118 | 31947 | 0.0057839 | 2.1363e-05 | 270.7373
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | FUSE | 1 | 1 | 556 | 0.00010066 | 1.8105e-07 | 556
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1247 | 50625 | 16768254 | 3.0195 | 0.0091161 | 331.2248
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 3 | 817 | 0.00014712 | 5.4022e-07 | 272.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 59 | 1.0582e-05 | 1.7935e-07 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CUTOUT | 2 | 5 | 11420 | 0.0020337 | 8.904e-07 | 2284
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 2 | 2 | 321 | 5.7571e-05 | 3.587e-07 | 160.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | TRANSFORMER, OH | 1 | 1 | 509 | 9.1289e-05 | 1.7935e-07 | 509
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | NONE | 1 | 5 | 815 | 0.00014617 | 8.9675e-07 | 163
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 261 | 4.7591e-05 | 1.8234e-07 | 261
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 1 | 194 | 3.5123e-05 | 1.8105e-07 | 194
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | RECLOSER, LINE/OCR/BR | 1 | 493 | 204825 | 0.036475 | 8.7793e-05 | 415.4665
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | FUSE | 1092 | 5748 | 694182 | 0.12568 | 0.0010407 | 120.7693
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 17 | 190 | 35118 | 0.006358 | 3.4399e-05 | 184.8316
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | NONE | 25 | 873 | 62610 | 0.011335 | 0.00015805 | 71.7182
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 79 | 4009 | 609767 | 0.1104 | 0.00072581 | 152.0995
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 9 | 299 | 54826 | 0.009926 | 5.4133e-05 | 183.3645
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 2 | 4 | 651 | 0.00011786 | 7.2419e-07 | 162.75
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONN/CLAMP | 2 | 6 | 321 | 5.8116e-05 | 1.0863e-06 | 53.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 60 | 9600 | 0.001738 | 1.0863e-05 | 160
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | ARRESTER | 7 | 495 | 70532 | 0.01277 | 8.9618e-05 | 142.4889
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 6 | 10 | 562 | 0.00010175 | 1.8105e-06 | 56.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CUTOUT | 3 | 10 | 33742 | 0.0061089 | 1.8105e-06 | 3374.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 5 | 14 | 2373 | 0.00042962 | 2.5346e-06 | 169.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CUTOUT | 1 | 11 | 2521 | 0.00045642 | 1.9915e-06 | 229.1818
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 5 | 151 | 2.7338e-05 | 9.0523e-07 | 30.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 1 | 2 | 30 | 5.4314e-06 | 3.6209e-07 | 15
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 86 | 3046 | 1063468 | 0.19391 | 0.00055541 | 349.1359
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 37 | 653 | 145258 | 0.026487 | 0.00011907 | 222.4472
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | O | NONE | 3 | 822 | 13257 | 0.0024001 | 0.00014882 | 16.1277
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | POLE | 7 | 114 | 16613 | 0.0030077 | 2.0639e-05 | 145.7281
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 6 | 15 | 1564 | 0.00028316 | 2.7157e-06 | 104.2667
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 1470 | 0.00026614 | 1.8105e-07 | 1470
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 197 | 47083 | 0.0085242 | 3.5666e-05 | 239
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | NONE | 4 | 90 | 20709 | 0.0037493 | 1.6294e-05 | 230.1
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | POLE | 81 | 2457 | 295705 | 0.053248 | 0.00044244 | 120.3521
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | NONE | 33 | 302 | 56045 | 0.010092 | 5.4382e-05 | 185.5795
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 2 | 517 | 68771 | 0.012384 | 9.3097e-05 | 133.0193
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | FUSE | 11 | 99 | 23404 | 0.0042144 | 1.7827e-05 | 236.404
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 9 | 3625 | 725198 | 0.13059 | 0.00065276 | 200.0546
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CUTOUT | 476 | 1559 | 113730 | 0.020398 | 0.00027961 | 72.9506
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | NONE | 773 | 14522 | 1519232 | 0.27247 | 0.0026045 | 104.6159
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | NONE | 9 | 11 | 1008 | 0.00018151 | 1.9808e-06 | 91.6364
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CUTOUT | 2 | 2 | 227 | 4.0876e-05 | 3.6014e-07 | 113.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CUTOUT | 11 | 222 | 48318 | 0.0086658 | 3.9816e-05 | 217.6486
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | NONE | 7 | 694 | 38268 | 0.0068634 | 0.00012447 | 55.1412
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 17 | 34 | 3820 | 0.00068512 | 6.0979e-06 | 112.3529
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | POLE | 6 | 424 | 117752 | 0.021119 | 7.6044e-05 | 277.717
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONN/CLAMP | 1 | 1 | 1562 | 0.00028127 | 1.8007e-07 | 1562
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 1 | 3 | 504 | 9.0756e-05 | 5.4022e-07 | 168
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 14 | 238 | 68348 | 0.012258 | 4.2685e-05 | 287.1765
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CUTOUT | 512 | 14198 | 1844520 | 0.33215 | 0.0025567 | 129.9141
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 50 | 1010 | 55542 | 0.010002 | 0.00018187 | 54.9921
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | NONE | 29 | 416 | 71441 | 0.012865 | 7.491e-05 | 171.7332
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 3 | 11 | 3002 | 0.00054058 | 1.9808e-06 | 272.9091
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | NONE | 16 | 92 | 7336 | 0.001321 | 1.6567e-05 | 79.7391
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | POLE | 1 | 5 | 185 | 3.3313e-05 | 9.0036e-07 | 37
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | METERING | 5 | 34 | 5255 | 0.00094628 | 6.1224e-06 | 154.5588
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CROSSARM | 21 | 758 | 111443 | 0.019987 | 0.00013595 | 147.0224
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 1 | 75 | 1.3505e-05 | 1.8007e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 5 | 24 | 2896 | 0.00052149 | 4.3217e-06 | 120.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | FUSE | 181 | 931 | 96140 | 0.017243 | 0.00016698 | 103.2653
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SWITCH, OH | 5 | 227 | 54492 | 0.0097732 | 4.0713e-05 | 240.0529
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 11 | 43 | 5117 | 0.00091774 | 7.7121e-06 | 119
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | ARRESTER | 40 | 2021 | 376317 | 0.067493 | 0.00036247 | 186.2034
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | TRANSFORMER, OH | 1 | 5 | 1708 | 0.00031144 | 9.1171e-07 | 341.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | FUSE | 2 | 4 | 124 | 2.261e-05 | 7.2937e-07 | 31
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 17 | 581 | 75451 | 0.013758 | 0.00010594 | 129.864
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 4 | 14 | 3475 | 0.00063364 | 2.5528e-06 | 248.2143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 30 | 3390 | 0.00061814 | 5.4703e-06 | 113
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 39 | 21762 | 0.0039399 | 7.0608e-06 | 558
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE | 113 | 7545 | 3380528 | 0.61641 | 0.0013758 | 448.0488
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CUTOUT | 467 | 1251 | 51577 | 0.0094047 | 0.00022811 | 41.2286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | METERING | 3 | 3 | 224 | 4.0845e-05 | 5.4703e-07 | 74.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 30 | 487 | 500672 | 0.091294 | 8.8801e-05 | 1028.0739
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | METERING | 3 | 3 | 419 | 7.6401e-05 | 5.4703e-07 | 139.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | NONE | 4 | 486 | 56294 | 0.010265 | 8.8618e-05 | 115.8313
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | ARRESTER | 48 | 1187 | 153445 | 0.027979 | 0.00021644 | 129.2713
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | NONE | 42 | 1244 | 138932 | 0.025333 | 0.00022683 | 111.6817
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE | 9 | 1591 | 416242 | 0.075898 | 0.00029011 | 261.6229
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE | 41 | 11210 | 1352879 | 0.24669 | 0.0020441 | 120.685
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | INSULATOR | 1 | 520 | 52520 | 0.0095766 | 9.4818e-05 | 101
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | NONE | 11 | 584 | 106542 | 0.019427 | 0.00010649 | 182.4349
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | FUSE | 2 | 95 | 9846 | 0.0017953 | 1.7322e-05 | 103.6421
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | SCO | NONE | 3 | 4006 | 43706 | 0.0079694 | 0.00073046 | 10.9101
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | FUSE | 11 | 88 | 7831 | 0.0014279 | 1.6046e-05 | 88.9886
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 2 | 558 | 86211 | 0.015524 | 0.00010048 | 154.5
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | JUMPER/RISER | 2 | 1160 | 23499 | 0.0042146 | 0.00020805 | 20.2578
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 13 | 355 | 111373 | 0.019975 | 6.3669e-05 | 313.7268
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 16 | 1626 | 0.00029649 | 2.9175e-06 | 101.625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CROSSARM | 24 | 5572 | 864042 | 0.15755 | 0.001016 | 155.0686
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 5 | 66 | 26738 | 0.0048755 | 1.2035e-05 | 405.1212
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 2 | 4 | 1608 | 0.00029321 | 7.2937e-07 | 402
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 58 | 9574 | 0.0017457 | 1.0576e-05 | 165.069
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | FUSE | 6 | 8 | 621 | 0.00011138 | 1.4348e-06 | 77.625
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 4 | 180 | 3.2413e-05 | 7.2029e-07 | 45
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 4 | 429 | 33179 | 0.0059507 | 7.6941e-05 | 77.3403
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 6 | 14 | 3022 | 0.00054418 | 2.521e-06 | 215.8571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | METERING | 3 | 4 | 288 | 5.1653e-05 | 7.174e-07 | 72
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | FUSE | 4 | 8 | 560 | 0.00010084 | 1.4406e-06 | 70
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONN/CLAMP | 3 | 5 | 647 | 0.00011604 | 8.9675e-07 | 129.4
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | F | NONE | 8 | 3177 | 340785 | 0.06112 | 0.0005698 | 107.2663
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 61 | 1.0984e-05 | 1.8007e-07 | 61
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | NONE | 8 | 1181 | 166472 | 0.029977 | 0.00021266 | 140.9585
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 5 | 3908 | 0.0007009 | 8.9675e-07 | 781.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 2 | 78 | 1.3989e-05 | 3.587e-07 | 39
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 2 | 35 | 2145 | 0.00038198 | 6.2328e-06 | 61.2857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 7 | 1674 | 62692 | 0.011164 | 0.00029811 | 37.4504
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 64 | 170 | 39537 | 0.0070407 | 3.0274e-05 | 232.5706
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 5 | 430 | 7.7121e-05 | 8.9675e-07 | 86
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | POLE | 73 | 2935 | 302995 | 0.053957 | 0.00052266 | 103.2351
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 5 | 515 | 9.1711e-05 | 8.904e-07 | 103
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 8 | 632 | 137988 | 0.024573 | 0.00011255 | 218.3354
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 216 | 3.8465e-05 | 1.7808e-07 | 216
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 41 | 651 | 44100 | 0.0078533 | 0.00011593 | 67.7419
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 6 | 51 | 8002 | 0.001425 | 9.0821e-06 | 156.902
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 12 | 23 | 508 | 9.0465e-05 | 4.0958e-06 | 22.087
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SO | NONE | 11 | 90 | 28055 | 0.004996 | 1.6027e-05 | 311.7222
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | POLE | 5 | 580 | 83858 | 0.01504 | 0.00010402 | 144.5828
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 3 | 145 | 2.5822e-05 | 5.3424e-07 | 48.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | NONE | 8 | 787 | 364293 | 0.064873 | 0.00014015 | 462.8882
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | ARRESTER | 2 | 24 | 246 | 4.412e-05 | 4.3044e-06 | 10.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 3 | 449 | 8.0528e-05 | 5.3805e-07 | 149.6667
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | FUSE | 2 | 2 | 176 | 3.1693e-05 | 3.6014e-07 | 88
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 2 | 8 | 2391 | 0.00043055 | 1.4406e-06 | 298.875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 2 | 1960 | 0.00035153 | 3.587e-07 | 980
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 7 | 3003 | 0.00053859 | 1.2555e-06 | 429
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | SCO | NONE | 1 | 1308 | 18108 | 0.0032477 | 0.00023459 | 13.844
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | ARRESTER | 2 | 2 | 937 | 0.00016805 | 3.587e-07 | 468.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 114 | 26690 | 0.0047869 | 2.0446e-05 | 234.1228
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 9 | 153 | 2.77e-05 | 1.6294e-06 | 17
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 2 | 900 | 0.00016411 | 3.6468e-07 | 450
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | METERING | 1 | 308 | 38192 | 0.006964 | 5.6161e-05 | 124
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | NONE | 16 | 230 | 340034 | 0.062002 | 4.1939e-05 | 1478.4087
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 148 | 8116 | 2081899 | 0.37074 | 0.0014453 | 256.5179
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 9 | 149 | 25783 | 0.0045914 | 2.6534e-05 | 173.0403
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | FUSE | 165 | 1215 | 199040 | 0.035445 | 0.00021637 | 163.8189
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | PEDESTAL | 1 | 5 | 175 | 3.1513e-05 | 9.0036e-07 | 35
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | METERING | 3 | 15 | 1275 | 0.00022959 | 2.7011e-06 | 85
AEP Total | 2024 | 5615460 | PARTIAL POWER | UG | CONDUCTOR UG | 1 | 2 | 664 | 0.00011824 | 3.5616e-07 | 332
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 58 | 435 | 81957 | 0.014595 | 7.7465e-05 | 188.4069
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 6 | 74 | 13085 | 0.0023302 | 1.3178e-05 | 176.8243
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 5 | 374 | 46543 | 0.0082884 | 6.6602e-05 | 124.4465
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 2 | 276 | 4.915e-05 | 3.5616e-07 | 138
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 3 | 10 | 2186 | 0.00038928 | 1.7808e-06 | 218.6
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | SCO | NONE | 3 | 183 | 26226 | 0.0046703 | 3.2589e-05 | 143.3115
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 4 | 387 | 6.8917e-05 | 7.1232e-07 | 96.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | FUSE | 5 | 14 | 1637 | 0.00029152 | 2.4931e-06 | 116.9286
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 8 | 117 | 2765 | 0.00049239 | 2.0835e-05 | 23.6325
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE | 2 | 45 | 38554 | 0.0069801 | 8.1471e-06 | 856.7556
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | METERING | 1 | 3 | 69 | 1.2288e-05 | 5.3424e-07 | 23
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | PEDESTAL | 2 | 23 | 3927 | 0.00069932 | 4.0958e-06 | 170.7391
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | SCO | NONE | 2 | 623 | 5242 | 0.00093349 | 0.00011094 | 8.4141
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 8 | 28 | 2445 | 0.00043541 | 4.9862e-06 | 87.3214
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 4 | 11 | 714 | 0.00012715 | 1.9589e-06 | 64.9091
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 13 | 6281 | 0.0011185 | 2.315e-06 | 483.1538
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 17 | 2227 | 0.00040319 | 3.0778e-06 | 131
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 1 | 1 | 52 | 9.4818e-06 | 1.8234e-07 | 52
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 3 | 219 | 3.9933e-05 | 5.4703e-07 | 73
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | CROSSARM | 1 | 698 | 57934 | 0.010432 | 0.00012569 | 83
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | POLE | 1 | 7 | 4445 | 0.00080042 | 1.2605e-06 | 635
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | SPLICE, OH | 1 | 4 | 552 | 9.94e-05 | 7.2029e-07 | 138
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 2 | 8 | 1262 | 0.00022474 | 1.4246e-06 | 157.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 2 | 415 | 95529 | 0.017012 | 7.3903e-05 | 230.1904
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | FUSE | 2 | 64 | 4950 | 0.0008815 | 1.1397e-05 | 77.3438
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | POLE | 1 | 1027 | 218914 | 0.038984 | 0.00018289 | 213.1587
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | INSULATOR | 1 | 229 | 39157 | 0.0070228 | 4.1071e-05 | 170.9913
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | SCO | NONE | 1 | 471 | 122540 | 0.021822 | 8.3876e-05 | 260.1699
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 2 | 36 | 6.4109e-06 | 3.5616e-07 | 18
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | JUMPER/RISER | 1 | 99 | 43893 | 0.0079039 | 1.7827e-05 | 443.3636
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | ARRESTER | 2 | 1435 | 324127 | 0.058682 | 0.0002598 | 225.8725
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | SPLICE, OH | 1 | 131 | 12090 | 0.0021683 | 2.3495e-05 | 92.2901
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | POLE | 2 | 46 | 15885 | 0.002849 | 8.2501e-06 | 345.3261
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 543 | 9.7387e-05 | 5.3805e-07 | 181
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 1891 | 697645 | 0.12721 | 0.00034481 | 368.9291
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 2 | 116 | 2.1152e-05 | 3.6468e-07 | 58
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | GUY/ANCHOR | 1 | 4 | 380 | 6.8798e-05 | 7.2419e-07 | 95
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | POLE | 2 | 116 | 86986 | 0.015861 | 2.1152e-05 | 749.8793
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CUTOUT | 8 | 20 | 6959 | 0.0012531 | 3.6014e-06 | 347.95
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | POLE | 223 | 5873 | 631190 | 0.1124 | 0.0010459 | 107.4732
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 5 | 119 | 44329 | 0.0078941 | 2.1191e-05 | 372.5126
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 9 | 49 | 7116 | 0.0012672 | 8.7259e-06 | 145.2245
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 12 | 206 | 45137 | 0.008038 | 3.6684e-05 | 219.1117
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 3 | 44 | 4744 | 0.00084481 | 7.8355e-06 | 107.8182
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | POLE | 2 | 737 | 179223 | 0.031916 | 0.00013124 | 243.1791
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 5 | 365 | 6.4999e-05 | 8.904e-07 | 73
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 3 | 429 | 7.6396e-05 | 5.3424e-07 | 143
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE | 1 | 18 | 30312 | 0.0054583 | 3.2413e-06 | 1684
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CROSSARM | 1 | 28 | 10052 | 0.0018329 | 5.1056e-06 | 359
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 1 | 286 | 5.1779e-05 | 1.8105e-07 | 286
AEP Total | 2022 | 5553337 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 1 | 5 | 380 | 6.8427e-05 | 9.0036e-07 | 76
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 1251 | 1502922 | 0.2721 | 0.00022649 | 1201.3765
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | NONE | 101 | 13795 | 1208918 | 0.21887 | 0.0024975 | 87.6345
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | FUSE | 43 | 98 | 8601 | 0.0015572 | 1.7743e-05 | 87.7653
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | METERING | 6 | 7 | 555 | 0.00010048 | 1.2673e-06 | 79.2857
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | NONE | 4 | 124 | 13791 | 0.0024968 | 2.245e-05 | 111.2177
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 22 | 7084 | 0.0012825 | 3.983e-06 | 322
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 6 | 224 | 141090 | 0.025544 | 4.0554e-05 | 629.8661
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | FUSE | 97 | 812 | 180384 | 0.032482 | 0.00014622 | 222.1478
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 113 | 336 | 31774 | 0.0057216 | 6.0504e-05 | 94.5655
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 2 | 224 | 4.0554e-05 | 3.6209e-07 | 112
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONN/CLAMP | 4 | 38 | 1273 | 0.00023047 | 6.8798e-06 | 33.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | NONE | 10 | 74 | 14426 | 0.0026118 | 1.3397e-05 | 194.9459
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR UG | 2 | 4 | 1566 | 0.00028352 | 7.2419e-07 | 391.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | FUSE | 1 | 15 | 2505 | 0.00045352 | 2.7157e-06 | 167
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 4 | 88 | 1241 | 0.00022468 | 1.5932e-05 | 14.1023
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | ARRESTER | 4 | 542 | 350814 | 0.063514 | 9.8127e-05 | 647.2583
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 2 | 206 | 3.7296e-05 | 3.6209e-07 | 103
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, OH | 5 | 1532 | 179500 | 0.03273 | 0.00027935 | 117.1671
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | NONE | 1 | 1 | 27 | 4.9232e-06 | 1.8234e-07 | 27
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | INSULATOR | 52 | 12008 | 1952423 | 0.35601 | 0.0021896 | 162.5935
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 41 | 68 | 20611 | 0.0037115 | 1.2245e-05 | 303.1029
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | FUSE | 56 | 485 | 66397 | 0.011956 | 8.7335e-05 | 136.901
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | TRANSFORMER, OH | 3 | 6 | 10216 | 0.0018396 | 1.0804e-06 | 1702.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 24 | 1050 | 354161 | 0.063774 | 0.00018908 | 337.2962
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, OH | 23 | 844 | 1090382 | 0.19635 | 0.00015198 | 1291.9218
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 12 | 27 | 4506 | 0.0008114 | 4.8619e-06 | 166.8889
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | FUSE | 12 | 49 | 19223 | 0.0034615 | 8.8235e-06 | 392.3061
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 914 | 42605 | 13641497 | 2.4466 | 0.0076412 | 320.1854
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 31 | 8246 | 0.0014849 | 5.5822e-06 | 266
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CROSSARM | 18 | 7627 | 1234563 | 0.22231 | 0.0013734 | 161.8674
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | BREAKER | 3 | 3195 | 1071661 | 0.19298 | 0.00057533 | 335.4182
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | FUSE | 182 | 2072 | 355237 | 0.063712 | 0.00037161 | 171.4464
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | FUSE | 59 | 673 | 144097 | 0.025844 | 0.0001207 | 214.1114
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 37 | 14282 | 0.0025718 | 6.6627e-06 | 386
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 17 | 642 | 314175 | 0.056574 | 0.00011561 | 489.3692
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 11 | 881 | 97018 | 0.0174 | 0.00015801 | 110.1226
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 2 | 52 | 10060 | 0.0018043 | 9.3262e-06 | 193.4615
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | EQF | MOAB | 2 | 113 | 1469 | 0.00026786 | 2.0605e-05 | 13
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 1269 | 87561 | 0.015593 | 0.00022598 | 69
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 7 | 3765 | 858828 | 0.15294 | 0.00067047 | 228.1084
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 2 | 6966 | 0.0012405 | 3.5616e-07 | 3483
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | U | NONE | 3 | 2626 | 52005 | 0.009261 | 0.00046764 | 19.8039
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 14 | 3710 | 0.00066068 | 2.4931e-06 | 265
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONN/CLAMP | 3 | 5 | 279 | 4.9684e-05 | 8.904e-07 | 55.8
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 1 | 2 | 456 | 8.2557e-05 | 3.6209e-07 | 228
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | RECLOSER, LINE/OCR/BR | 1 | 17 | 2108 | 0.00038438 | 3.0998e-06 | 124
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 43 | 8995 | 0.0016197 | 7.7431e-06 | 209.186
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | FUSE | 1 | 1 | 426 | 7.6711e-05 | 1.8007e-07 | 426
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABI | NONE | 2 | 1563 | 203705 | 0.036682 | 0.00028145 | 130.3295
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | JUMPER/RISER | 1 | 7 | 1351 | 0.0002423 | 1.2555e-06 | 193
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | FUSE | 1 | 27 | 1620 | 0.00028849 | 4.8082e-06 | 60
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 5 | 59 | 7207 | 0.0012834 | 1.0507e-05 | 122.1525
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | SPLICE, OH | 1 | 1 | 530 | 9.4382e-05 | 1.7808e-07 | 530
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | SPLICE, OH | 1 | 10 | 1550 | 0.00027911 | 1.8007e-06 | 155
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 3 | 7 | 1373 | 0.0002445 | 1.2466e-06 | 196.1429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | BE | CONDUCTOR OVERHEAD | 1 | 2 | 238 | 4.2383e-05 | 3.5616e-07 | 119
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | FUSE | 1 | 1 | 157 | 2.8628e-05 | 1.8234e-07 | 157
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 664 | 0.00011957 | 1.8007e-07 | 664
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | BREAKER | 1 | 2 | 194 | 3.5374e-05 | 3.6468e-07 | 97
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | FUSE | 2 | 6 | 754 | 0.00013523 | 1.0761e-06 | 125.6667
AEP Total | 2022 | 5553337 | PARTIAL POWER | WFS | CONDUCTOR OVERHEAD | 1 | 2 | 454 | 8.1753e-05 | 3.6014e-07 | 227
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 3 | 390 | 7.1113e-05 | 5.4703e-07 | 130
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | FUSE | 9 | 33 | 2627 | 0.00047901 | 6.0173e-06 | 79.6061
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | NONE | 3 | 74 | 17242 | 0.0031439 | 1.3493e-05 | 233
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 3 | 25 | 3157 | 0.00057565 | 4.5586e-06 | 126.28
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | ARRESTER | 5 | 25 | 4269 | 0.00077842 | 4.5586e-06 | 170.76
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 7 | 518 | 9.4453e-05 | 1.2764e-06 | 74
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | NONE | 1 | 1659 | 296961 | 0.054148 | 0.00030251 | 179
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | NONE | 738 | 12149 | 1522372 | 0.2711 | 0.0021635 | 125.3084
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | FUSE | 2 | 5 | 385 | 6.905e-05 | 8.9675e-07 | 77
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | NONE | 12 | 144 | 16229 | 0.0028901 | 2.5643e-05 | 112.7014
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 116 | 3398 | 552742 | 0.098432 | 0.00060512 | 162.6669
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | POLE | 1 | 10 | 2980 | 0.00053446 | 1.7935e-06 | 298
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 245 | 964 | 132796 | 0.023648 | 0.00017167 | 137.7552
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 89 | 50713 | 0.009031 | 1.5849e-05 | 569.809
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | NONE | 41 | 1704 | 839868 | 0.14956 | 0.00030345 | 492.8803
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 277 | 4.968e-05 | 1.7935e-07 | 277
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 2 | 863 | 0.00015478 | 3.587e-07 | 431.5
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AB | NONE | 2 | 1040 | 101920 | 0.018279 | 0.00018652 | 98
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | INSULATOR | 2 | 31 | 1975 | 0.00035171 | 5.5205e-06 | 63.7097
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 3 | 886 | 50600 | 0.0090108 | 0.00015778 | 57.1106
AEP Total | 2023 | 5575683 | SUBTRANSMISSION LINE | SCO | NONE | 3 | 12 | 632 | 0.00011335 | 2.1522e-06 | 52.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 8 | 17 | 607 | 0.0001093 | 3.0612e-06 | 35.7059
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 4 | 18 | 1044 | 0.00018724 | 3.2283e-06 | 58
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CUTOUT | 1 | 107 | 9416 | 0.0016768 | 1.9055e-05 | 88
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | SPLICE, OH | 1 | 6 | 792 | 0.00014339 | 1.0863e-06 | 132
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 541 | 9.6341e-05 | 1.7808e-07 | 541
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | FUSE | 252 | 3521 | 599454 | 0.10853 | 0.00063746 | 170.2511
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 16 | 1588 | 0.0002875 | 2.8967e-06 | 99.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | NONE | 12 | 164 | 31373 | 0.00568 | 2.9692e-05 | 191.2988
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CUTOUT | 52 | 126 | 3629 | 0.00065702 | 2.2812e-05 | 28.8016
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | FUSE | 6 | 12 | 858 | 0.00015534 | 2.1726e-06 | 71.5
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | U | FUSE | 1 | 2 | 108 | 1.9553e-05 | 3.6209e-07 | 54
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | NONE | 6 | 6 | 303 | 5.4857e-05 | 1.0863e-06 | 50.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 11 | 39 | 2616 | 0.00047362 | 7.0608e-06 | 67.0769
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | FUSE | 16 | 164 | 20995 | 0.0038011 | 2.9692e-05 | 128.0183
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | CUTOUT | 2 | 1106 | 193340 | 0.035004 | 0.00020024 | 174.8101
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 5 | 897 | 135007 | 0.024443 | 0.0001624 | 150.5095
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | FUSE | 9 | 160 | 26755 | 0.0048439 | 2.8967e-05 | 167.2188
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | FUSE | 22 | 160 | 47616 | 0.0085743 | 2.8812e-05 | 297.6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | FUSE | 9 | 43 | 6474 | 0.0011658 | 7.7431e-06 | 150.5581
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 16 | 1389 | 180525 | 0.032507 | 0.00025012 | 129.9676
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 28 | 3932 | 1354838 | 0.24397 | 0.00070804 | 344.5671
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 10 | 594 | 307514 | 0.055375 | 0.00010696 | 517.7003
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | NONE | 3 | 17 | 2526 | 0.00045486 | 3.0612e-06 | 148.5882
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, OH | 3 | 818 | 31367 | 0.0056483 | 0.0001473 | 38.346
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | INSULATOR | 48 | 16207 | 4333157 | 0.78028 | 0.0029184 | 267.3633
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WU | NONE | 6 | 3393 | 330691 | 0.059548 | 0.00061098 | 97.4627
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | REGULATOR | 5 | 1230 | 153399 | 0.027623 | 0.00022149 | 124.7146
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | FUSE | 7 | 34 | 3976 | 0.0007131 | 6.0979e-06 | 116.9412
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | NONE | 2 | 15 | 2178 | 0.0003922 | 2.7011e-06 | 145.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | FUSE | 1 | 8 | 1280 | 0.00023049 | 1.4406e-06 | 160
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | NONE | 2 | 1325 | 238526 | 0.043493 | 0.0002416 | 180.0196
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 276 | 5.0326e-05 | 3.6468e-07 | 138
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | POLE | 1 | 5 | 155 | 2.8263e-05 | 9.1171e-07 | 31
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 151 | 271347 | 0.049126 | 2.7338e-05 | 1797
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 2 | 404 | 7.2749e-05 | 3.6014e-07 | 202
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 1 | 936 | 59904 | 0.010668 | 0.00016668 | 64
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | FUSE | 1 | 2 | 118 | 2.1013e-05 | 3.5616e-07 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | NONE | 9 | 23 | 2282 | 0.00040638 | 4.0958e-06 | 99.2174
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 215 | 14530 | 0.0025875 | 3.8287e-05 | 67.5814
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | POLE | 7 | 1393 | 182417 | 0.032485 | 0.00024807 | 130.9526
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | FUSE | 5 | 9 | 736 | 0.00013107 | 1.6027e-06 | 81.7778
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 37 | 6413 | 0.001142 | 6.589e-06 | 173.3243
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 5 | 17 | 12130 | 0.0021601 | 3.0274e-06 | 713.5294
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 3 | 2086 | 115029 | 0.020484 | 0.00037147 | 55.1433
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | NONE | 6 | 8 | 843 | 0.00015012 | 1.4246e-06 | 105.375
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | POLE | 1 | 1 | 258 | 4.5945e-05 | 1.7808e-07 | 258
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | SCO | POLE | 1 | 324 | 1944 | 0.00034866 | 5.8109e-05 | 6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 230 | 23460 | 0.0041778 | 4.0958e-05 | 102
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | FW | NONE | 3 | 1711 | 22747 | 0.0040961 | 0.0003081 | 13.2946
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 44 | 44364 | 0.0079887 | 7.9232e-06 | 1008.2727
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 14 | 181 | 57981 | 0.010399 | 3.2462e-05 | 320.337
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 24 | 1227 | 285256 | 0.051367 | 0.00022095 | 232.4825
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 3 | 5 | 1803 | 0.00032337 | 8.9675e-07 | 360.6
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | NONE | 6 | 53 | 5051 | 0.00091447 | 9.5955e-06 | 95.3019
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 3 | 5 | 2304 | 0.00041713 | 9.0523e-07 | 460.8
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | REGULATOR | 1 | 42 | 127144 | 0.023019 | 7.6039e-06 | 3027.2381
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | NONE | 440 | 32239 | 7094411 | 1.2936 | 0.0058785 | 220.0568
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, OH | 29 | 520 | 90037 | 0.016418 | 9.4818e-05 | 173.1481
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | POLE | 503 | 9902 | 1790318 | 0.32645 | 0.0018056 | 180.8037
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | FUSE | 19 | 75 | 9926 | 0.0018099 | 1.3676e-05 | 132.3467
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 19 | 38 | 1462 | 0.00026658 | 6.929e-06 | 38.4737
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE | 5 | 29 | 5810 | 0.0010594 | 5.2879e-06 | 200.3448
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 47 | 108 | 10703 | 0.0019516 | 1.9693e-05 | 99.1019
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | RELAY | 2 | 3242 | 644255 | 0.11747 | 0.00059115 | 198.7215
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | NONE | 3 | 6 | 3109 | 0.0005669 | 1.0941e-06 | 518.1667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 6 | 29 | 10756 | 0.0019613 | 5.2879e-06 | 370.8966
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | NONE | 14 | 1917 | 176987 | 0.032272 | 0.00034955 | 92.325
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | U | NONE | 1 | 6 | 696 | 0.00012691 | 1.0941e-06 | 116
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 9 | 324 | 5.9079e-05 | 1.6411e-06 | 36
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | ARRESTER | 1 | 5 | 480 | 8.7524e-05 | 9.1171e-07 | 96
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | POLE | 1 | 1 | 615 | 0.00011214 | 1.8234e-07 | 615
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 53 | 2078 | 478742 | 0.085862 | 0.00037269 | 230.3859
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 2 | 11 | 3364 | 0.00060576 | 1.9808e-06 | 305.8182
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 625 | 126146 | 0.022715 | 0.00011254 | 201.8336
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 64 | 1.1525e-05 | 1.8007e-07 | 64
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 2 | 2 | 280 | 5.0218e-05 | 3.587e-07 | 140
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 14 | 5237 | 0.00094304 | 2.521e-06 | 374.0714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | CUTOUT | 2 | 2 | 1020 | 0.00018367 | 3.6014e-07 | 510
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 230 | 4.0958e-05 | 1.7808e-07 | 230
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE | 3 | 450 | 135399 | 0.024112 | 8.0136e-05 | 300.8867
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 17 | 815 | 0.00014514 | 3.0274e-06 | 47.9412
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 5 | 3255 | 0.00057965 | 8.904e-07 | 651
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 1 | 70 | 1.2555e-05 | 1.7935e-07 | 70
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 17 | 2550 | 0.00045734 | 3.049e-06 | 150
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 242 | 4.3403e-05 | 3.587e-07 | 121
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | GUY/ANCHOR | 2 | 218 | 29708 | 0.0052904 | 3.8821e-05 | 136.2752
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 1 | 1 | 263 | 4.7956e-05 | 1.8234e-07 | 263
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | CONDUCTOR OVERHEAD | 1 | 1 | 163 | 2.9352e-05 | 1.8007e-07 | 163
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE | 111 | 11519 | 5729931 | 1.0374 | 0.0020855 | 497.433
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 37 | 82 | 13110 | 0.0023735 | 1.4846e-05 | 159.878
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, OH | 6 | 2181 | 373149 | 0.067557 | 0.00039486 | 171.0908
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | FUSE | 91 | 1212 | 218725 | 0.039599 | 0.00021943 | 180.4662
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 15 | 2227 | 0.00040319 | 2.7157e-06 | 148.4667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 8 | 170 | 90175 | 0.016326 | 3.0778e-05 | 530.4412
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 36 | 78 | 21558 | 0.003903 | 1.4122e-05 | 276.3846
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | SWITCH, OH | 5 | 105 | 10087 | 0.0018262 | 1.901e-05 | 96.0667
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 3 | 6 | 1254 | 0.00022703 | 1.0863e-06 | 209
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WL | ARRESTER | 1 | 409 | 95706 | 0.017327 | 7.4048e-05 | 234
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | NONE | 7 | 733 | 140949 | 0.025518 | 0.00013271 | 192.2906
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | SECTIONALIZER | 1 | 22 | 2596 | 0.00047 | 3.983e-06 | 118
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | INSULATOR | 13 | 912 | 151119 | 0.02736 | 0.00016511 | 165.7007
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | FUSE | 1 | 1 | 90 | 1.6294e-05 | 1.8105e-07 | 90
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | NONE | 4 | 8 | 528 | 9.5592e-05 | 1.4484e-06 | 66
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 4 | 30 | 13504 | 0.0024219 | 5.3805e-06 | 450.1333
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | EQF | ARRESTER | 2 | 1481 | 367288 | 0.065873 | 0.00026562 | 248
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | FUSE | 6 | 17 | 2849 | 0.00051302 | 3.0612e-06 | 167.5882
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | NONE | 5 | 178 | 4775 | 0.0008564 | 3.1924e-05 | 26.8258
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | FUSE | 5 | 17 | 1606 | 0.00028804 | 3.049e-06 | 94.4706
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 481 | 16025 | 2138732 | 0.38086 | 0.0028537 | 133.4622
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 83 | 190 | 25094 | 0.0044687 | 3.3835e-05 | 132.0737
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 18 | 756 | 131500 | 0.023417 | 0.00013463 | 173.9418
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 59 | 10711 | 2680303 | 0.47731 | 0.0019074 | 250.2384
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 16 | 5733 | 522427 | 0.093034 | 0.0010209 | 91.1263
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 3 | 7 | 911 | 0.00016223 | 1.2466e-06 | 130.1429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 7 | 1157 | 0.00021097 | 1.2764e-06 | 165.2857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 4 | 220 | 3.9457e-05 | 7.174e-07 | 55
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 2 | 9 | 890 | 0.00015962 | 1.6142e-06 | 98.8889
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | REGULATOR | 5 | 641 | 26991 | 0.0048408 | 0.00011496 | 42.1076
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 34 | 14926 | 0.0027023 | 6.1556e-06 | 439
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | F | NONE | 2 | 1212 | 391563 | 0.070891 | 0.00021943 | 323.0718
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | FUSE | 5 | 49 | 6800 | 0.0012311 | 8.8713e-06 | 138.7755
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | CONDUCTOR UG | 2 | 2 | 598 | 0.00010827 | 3.6209e-07 | 299
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 2 | 124 | 2.245e-05 | 3.6209e-07 | 62
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 3 | 82 | 19552 | 0.0035398 | 1.4846e-05 | 238.439
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | FUSE | 62 | 747 | 143173 | 0.025781 | 0.00013451 | 191.664
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 8 | 142 | 2.5709e-05 | 1.4484e-06 | 17.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 2 | 488 | 178476 | 0.032312 | 8.8351e-05 | 365.7295
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 6 | 372 | 81655 | 0.014783 | 6.7349e-05 | 219.5027
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 2 | 279 | 108883 | 0.019713 | 5.0512e-05 | 390.2616
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 129 | 2.3355e-05 | 1.8105e-07 | 129
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 22 | 3344 | 0.00060542 | 3.983e-06 | 152
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONN/CLAMP | 89 | 228 | 25635 | 0.0046743 | 4.1574e-05 | 112.4342
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1097 | 51548 | 15899353 | 2.8991 | 0.0093994 | 308.4378
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | POLE | 13 | 615 | 125150 | 0.02282 | 0.00011214 | 203.4959
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | INSULATOR | 6 | 130 | 3311 | 0.00060373 | 2.3704e-05 | 25.4692
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | POLE | 3 | 20 | 75705 | 0.013804 | 3.6468e-06 | 3785.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | ARRESTER | 2 | 73 | 5431 | 0.0009903 | 1.3311e-05 | 74.3973
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 3 | 6 | 216 | 3.9386e-05 | 1.0941e-06 | 36
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 6 | 33 | 1649 | 0.00030068 | 6.0173e-06 | 49.9697
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 8 | 246 | 35494 | 0.006472 | 4.4856e-05 | 144.2846
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | NONE | 12 | 123 | 14151 | 0.0025803 | 2.2428e-05 | 115.0488
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | FUSE | 4 | 21 | 2726 | 0.00049706 | 3.8292e-06 | 129.8095
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | ARRESTER | 8 | 291 | 189421 | 0.034539 | 5.3062e-05 | 650.9313
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 4 | 75 | 16401 | 0.0029906 | 1.3676e-05 | 218.68
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | METERING | 2 | 3 | 486 | 8.8618e-05 | 5.4703e-07 | 162
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | NONE | 42 | 612 | 55285 | 0.010081 | 0.00011159 | 90.335
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 5 | 19 | 298 | 5.4338e-05 | 3.4645e-06 | 15.6842
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | NONE | 31 | 2404 | 362375 | 0.065254 | 0.00043289 | 150.7384
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | FUSE | 34 | 69 | 5839 | 0.0010514 | 1.2425e-05 | 84.6232
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | ARRESTER | 40 | 277 | 37882 | 0.0068215 | 4.988e-05 | 136.7581
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | POLE | 9 | 361 | 94357 | 0.016991 | 6.5006e-05 | 261.3767
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | U | NONE | 1 | 1007 | 187193 | 0.033708 | 0.00018133 | 185.8918
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | FUSE | 8 | 17 | 2722 | 0.00049016 | 3.0612e-06 | 160.1176
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 20 | 673 | 111831 | 0.020057 | 0.0001207 | 166.1679
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CROSSARM | 40 | 9932 | 2521497 | 0.45223 | 0.0017813 | 253.8761
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | ARRESTER | 2 | 5 | 1740 | 0.00031333 | 9.0036e-07 | 348
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 16 | 50 | 3807 | 0.00068553 | 9.0036e-06 | 76.14
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | FUSE | 13 | 196 | 10273 | 0.0018425 | 3.5153e-05 | 52.4133
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | ERF | NONE | 1 | 264 | 14256 | 0.0025671 | 4.7539e-05 | 54
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 12 | 3655 | 0.00065816 | 2.1609e-06 | 304.5833
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | NONE | 8 | 388 | 31253 | 0.0056278 | 6.9868e-05 | 80.549
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 2 | 8 | 498 | 8.9676e-05 | 1.4406e-06 | 62.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 1 | 1301 | 0.00023427 | 1.8007e-07 | 1301
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | NONE | 13 | 1427 | 109517 | 0.019642 | 0.00025593 | 76.7463
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 1 | 1 | 145 | 2.6006e-05 | 1.7935e-07 | 145
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | NONE | 10 | 2011 | 202614 | 0.036339 | 0.00036067 | 100.7529
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | NONE | 164 | 3381 | 139714 | 0.02488 | 0.00060209 | 41.3233
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 3 | 141 | 20991 | 0.0038003 | 2.5528e-05 | 148.8723
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONN/CLAMP | 2 | 5 | 6171 | 0.0011112 | 9.0036e-07 | 1234.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | POLE | 1 | 359 | 32310 | 0.0057538 | 6.3931e-05 | 90
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 7 | 9 | 2229 | 0.00039694 | 1.6027e-06 | 247.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | NONE | 1 | 2 | 60 | 1.0685e-05 | 3.5616e-07 | 30
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | NONE | 1 | 6 | 852 | 0.00015172 | 1.0685e-06 | 142
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 6 | 1165 | 102642 | 0.018278 | 0.00020746 | 88.1047
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 41 | 13606 | 0.002423 | 7.3013e-06 | 331.8537
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WFS | NONE | 1 | 45 | 21285 | 0.0038536 | 8.1471e-06 | 473
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | FUSE | 3 | 6 | 338 | 6.1194e-05 | 1.0863e-06 | 56.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | SPLICE, OH | 1 | 1 | 147 | 2.6614e-05 | 1.8105e-07 | 147
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 193 | 46804 | 0.0084281 | 3.4754e-05 | 242.5078
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 127 | 56535 | 0.01018 | 2.2869e-05 | 445.1575
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 24 | 4674 | 0.00083234 | 4.2739e-06 | 194.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 2 | 4 | 291 | 5.1821e-05 | 7.1232e-07 | 72.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | ARRESTER | 3 | 136 | 4618 | 0.00082237 | 2.4219e-05 | 33.9559
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 21 | 2205 | 0.00039267 | 3.7397e-06 | 105
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | FUSE | 2 | 2 | 229 | 4.078e-05 | 3.5616e-07 | 114.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SECTIONALIZER | 1 | 2 | 4246 | 0.00075613 | 3.5616e-07 | 2123
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 7 | 1301 | 223468 | 0.04024 | 0.00023427 | 171.7663
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 11 | 5412 | 0.00097455 | 1.9808e-06 | 492
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | FUSE | 6 | 120 | 17478 | 0.0031473 | 2.1609e-05 | 145.65
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 76 | 7112 | 0.0012807 | 1.3685e-05 | 93.5789
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 992 | 411562 | 0.073814 | 0.00017792 | 414.881
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 371 | 34841 | 6913189 | 1.2311 | 0.0062045 | 198.4211
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 15 | 25 | 3331 | 0.00059318 | 4.452e-06 | 133.24
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 95 | 10730 | 0.0019108 | 1.6918e-05 | 112.9474
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | FUSE | 27 | 70 | 8316 | 0.0014809 | 1.2466e-05 | 118.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CROSSARM | 10 | 223 | 24783 | 0.0044134 | 3.9712e-05 | 111.1345
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 39 | 2169 | 315502 | 0.056185 | 0.00038626 | 145.4597
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 9 | 25 | 5706 | 0.0010161 | 4.452e-06 | 228.24
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 2 | 2 | 21 | 3.7664e-06 | 3.587e-07 | 10.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 9 | 2574 | 0.00046165 | 1.6142e-06 | 286
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 6 | 173 | 45429 | 0.00809 | 3.0808e-05 | 262.5954
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CROSSARM | 2 | 289 | 192950 | 0.034745 | 5.2041e-05 | 667.6471
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 3 | 2991 | 0.0005386 | 5.4022e-07 | 997
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 1 | 562 | 0.00010175 | 1.8105e-07 | 562
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SWITCH, OH | 3 | 438 | 56918 | 0.010249 | 7.8871e-05 | 129.9498
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 108 | 33264 | 0.0059899 | 1.9448e-05 | 308
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 5 | 294 | 5.2941e-05 | 9.0036e-07 | 58.8
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | TRANSFORMER, STATION SERVICE | 2 | 1012 | 362814 | 0.066156 | 0.00018453 | 358.5119
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | SPLICE, OH | 2 | 3 | 497 | 9.0624e-05 | 5.4703e-07 | 165.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 129 | 2.3136e-05 | 1.7935e-07 | 129
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | NONE | 41 | 4444 | 525164 | 0.093521 | 0.00079139 | 118.1737
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 2 | 112 | 2.0168e-05 | 3.6014e-07 | 56
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | NONE | 1 | 1 | 270 | 4.8619e-05 | 1.8007e-07 | 270
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 236 | 2832 | 0.00050432 | 4.2027e-05 | 12
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | NONE | 1 | 3 | 195 | 3.4726e-05 | 5.3424e-07 | 65
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 1 | 1 | 164 | 2.9205e-05 | 1.7808e-07 | 164
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 20 | 3.5616e-06 | 1.7808e-07 | 20
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 1 | 9 | 1548 | 0.00027567 | 1.6027e-06 | 172
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | NONE | 3 | 7 | 2336 | 0.00042065 | 1.2605e-06 | 333.7143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | JUMPER/RISER | 1 | 9 | 387 | 6.9409e-05 | 1.6142e-06 | 43
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 37 | 9139 | 0.0016275 | 6.589e-06 | 247
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | FUSE | 54 | 229 | 38923 | 0.0070469 | 4.146e-05 | 169.9694
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CROSSARM | 31 | 4524 | 1300751 | 0.2355 | 0.00081905 | 287.5223
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | NONE | 56 | 2768 | 351430 | 0.063625 | 0.00050114 | 126.9617
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | FUSE | 55 | 173 | 18033 | 0.0032648 | 3.1321e-05 | 104.237
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR UG | 19 | 41 | 14866 | 0.0026914 | 7.4229e-06 | 362.5854
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | METERING | 2 | 3 | 128 | 2.3174e-05 | 5.4314e-07 | 42.6667
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SPLICE, OH | 9 | 20 | 3448 | 0.00062425 | 3.6209e-06 | 172.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | FUSE | 2 | 6 | 3393 | 0.00061429 | 1.0863e-06 | 565.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | ARRESTER | 1 | 1 | 1105 | 0.00020006 | 1.8105e-07 | 1105
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 1 | 2 | 960 | 0.00017096 | 3.5616e-07 | 480
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 5 | 103 | 47208 | 0.0084068 | 1.8342e-05 | 458.3301
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | FUSE | 3 | 16 | 907 | 0.00016152 | 2.8493e-06 | 56.6875
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 3 | 72 | 1.2822e-05 | 5.3424e-07 | 24
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | FUSE | 2 | 12 | 1533 | 0.000273 | 2.137e-06 | 127.75
AEP Total | 2024 | 5615460 | PARTIAL POWER | V | CONDUCTOR UG | 1 | 12 | 3504 | 0.00062399 | 2.137e-06 | 292
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | SPLICE, OH | 1 | 1 | 239 | 4.3037e-05 | 1.8007e-07 | 239
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | JUMPER/RISER | 1 | 7 | 931 | 0.00016765 | 1.2605e-06 | 133
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | METERING | 1 | 6 | 54 | 9.6163e-06 | 1.0685e-06 | 9
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 1 | 88 | 15400 | 0.0027424 | 1.5671e-05 | 175
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 5 | 7 | 536 | 9.5451e-05 | 1.2466e-06 | 76.5714
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 3 | 6 | 4662 | 0.00083021 | 1.0685e-06 | 777
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 20 | 3100 | 0.00055205 | 3.5616e-06 | 155
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | TIR | NONE | 1 | 924 | 71328 | 0.012844 | 0.00016639 | 77.1948
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | POLE | 1 | 1 | 513 | 9.2377e-05 | 1.8007e-07 | 513
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | CUTOUT | 1 | 57 | 4047 | 0.00072069 | 1.0151e-05 | 71
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 415 | 4150 | 0.00073903 | 7.3903e-05 | 10
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | CONN/CLAMP | 2 | 1144 | 174440 | 0.031064 | 0.00020372 | 152.4825
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | METERING | 1 | 3 | 45 | 8.0708e-06 | 5.3805e-07 | 15
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | NONE | 1 | 7 | 315 | 5.7438e-05 | 1.2764e-06 | 45
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | CONN/CLAMP | 1 | 33 | 10230 | 0.0018654 | 6.0173e-06 | 310
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | NONE | 277 | 23004 | 4997813 | 0.90484 | 0.0041648 | 217.2584
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | NONE | 37 | 6043 | 833401 | 0.15088 | 0.0010941 | 137.9118
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONN/CLAMP | 79 | 213 | 38089 | 0.0068959 | 3.8563e-05 | 178.8216
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 1 | 102 | 1.8467e-05 | 1.8105e-07 | 102
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | ARRESTER | 40 | 3101 | 508385 | 0.092041 | 0.00056142 | 163.9423
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CUTOUT | 365 | 916 | 21888 | 0.0039627 | 0.00016584 | 23.8952
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 378 | 60660 | 0.010982 | 6.8436e-05 | 160.4762
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 17 | 884 | 0.00016004 | 3.0778e-06 | 52
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | FUSE | 122 | 440 | 41215 | 0.0074618 | 7.966e-05 | 93.6705
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 2 | 9440 | 0.0017091 | 3.6209e-07 | 4720
AEP Total | 2021 | 5523447 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 2 | 2 | 242 | 4.3813e-05 | 3.6209e-07 | 121
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 5 | 47 | 10984 | 0.0019886 | 8.5092e-06 | 233.7021
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | CE | NONE | 1 | 785 | 143655 | 0.026008 | 0.00014212 | 183
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | ARRESTER | 2 | 3777 | 81266 | 0.014713 | 0.00068381 | 21.516
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 6 | 924 | 41130 | 0.0074997 | 0.00016848 | 44.513
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | SCO | OTHER EQUIPMENT | 1 | 3 | 1320 | 0.00023898 | 5.4314e-07 | 440
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | NONE | 3 | 348 | 9968 | 0.0018047 | 6.3004e-05 | 28.6437
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | FUSE | 1 | 2 | 48 | 8.6902e-06 | 3.6209e-07 | 24
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 2 | 436 | 7.8936e-05 | 3.6209e-07 | 218
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 1 | 2 | 298 | 5.3952e-05 | 3.6209e-07 | 149
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | FUSE | 150 | 1180 | 149560 | 0.026932 | 0.00021248 | 126.7458
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | FUSE | 331 | 1455 | 234755 | 0.042273 | 0.000262 | 161.3436
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CUTOUT | 21 | 137 | 85976 | 0.015482 | 2.467e-05 | 627.562
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 3 | 136 | 15007 | 0.0027023 | 2.449e-05 | 110.3456
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | FUSE | 15 | 203 | 47487 | 0.0085511 | 3.6555e-05 | 233.9261
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | NONE | 10 | 889 | 33739 | 0.0060754 | 0.00016008 | 37.9516
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 24 | 1445 | 421995 | 0.075989 | 0.0002602 | 292.0381
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CROSSARM | 9 | 364 | 28445 | 0.0051221 | 6.5546e-05 | 78.1456
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 56 | 1304 | 74932 | 0.013439 | 0.00023387 | 57.4632
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | POLE | 1 | 9 | 1942 | 0.0003497 | 1.6206e-06 | 215.7778
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONDUCTOR UG | 1 | 6 | 1326 | 0.00023878 | 1.0804e-06 | 221
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 6 | 19 | 1891 | 0.00034052 | 3.4214e-06 | 99.5263
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | NONE | 51 | 778 | 340528 | 0.062093 | 0.00014186 | 437.6967
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | NONE | 4 | 4 | 372 | 6.7831e-05 | 7.2937e-07 | 93
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | FUSE | 104 | 733 | 145984 | 0.026619 | 0.00013366 | 199.1596
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | FUSE | 40 | 164 | 16535 | 0.003015 | 2.9904e-05 | 100.8232
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | SWITCH, OH | 4 | 1388 | 29784 | 0.0054309 | 0.00025309 | 21.4582
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 31 | 1116 | 50394 | 0.0091889 | 0.00020349 | 45.1559
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CIRCUIT SWITCHER | 1 | 18 | 20412 | 0.003722 | 3.2822e-06 | 1134
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | NONE | 2 | 11 | 1449 | 0.00026421 | 2.0058e-06 | 131.7273
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE | 28 | 2036 | 1025075 | 0.18691 | 0.00037125 | 503.475
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 188 | 3.428e-05 | 1.8234e-07 | 188
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 8 | 40 | 3936 | 0.0007177 | 7.2937e-06 | 98.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 1 | 2601 | 0.00047427 | 1.8234e-07 | 2601
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | NONE | 1 | 3 | 360 | 6.5643e-05 | 5.4703e-07 | 120
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | FUSE | 6 | 19 | 1790 | 0.00032639 | 3.4645e-06 | 94.2105
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 87 | 1.5864e-05 | 1.8234e-07 | 87
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 3 | 26 | 4972 | 0.0009066 | 4.7409e-06 | 191.2308
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 21 | 588 | 74218 | 0.013311 | 0.00010546 | 126.2211
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | FUSE | 10 | 204 | 21365 | 0.0038318 | 3.6587e-05 | 104.7304
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | INSULATOR | 4 | 4285 | 528526 | 0.094791 | 0.00076852 | 123.3433
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | NONE | 10 | 1490 | 108758 | 0.019506 | 0.00026723 | 72.9919
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | FUSE | 25 | 72 | 5665 | 0.001016 | 1.2913e-05 | 78.6806
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | FUSE | 4 | 609 | 99844 | 0.017907 | 0.00010922 | 163.9475
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 9 | 872 | 152169 | 0.027292 | 0.00015639 | 174.5057
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | NONE | 8 | 276 | 43620 | 0.0078233 | 4.9501e-05 | 158.0435
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | POLE | 36 | 690 | 898890 | 0.16186 | 0.00012425 | 1302.7391
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 28 | 486 | 336134 | 0.060528 | 8.7515e-05 | 691.6337
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CROSSARM | 34 | 975 | 140901 | 0.025372 | 0.00017557 | 144.5138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | METERING | 1 | 3 | 126 | 2.2689e-05 | 5.4022e-07 | 42
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | PEDESTAL | 2 | 7 | 256 | 4.668e-05 | 1.2764e-06 | 36.5714
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 6 | 3916 | 0.00071405 | 1.0941e-06 | 652.6667
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CUTOUT | 14 | 24 | 3234 | 0.00058969 | 4.3762e-06 | 134.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 8 | 1576 | 0.00028737 | 1.4587e-06 | 197
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 26 | 5070 | 0.00092447 | 4.7409e-06 | 195
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | NONE | 11 | 450 | 64027 | 0.011675 | 8.2054e-05 | 142.2822
AEP Total | 2020 | 5484199 | PARTIAL POWER | OU | OTHER EQUIPMENT | 1 | 1 | 287 | 5.2332e-05 | 1.8234e-07 | 287
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | ARRESTER | 3 | 18 | 2122 | 0.00038693 | 3.2822e-06 | 117.8889
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | METERING | 2 | 8 | 871 | 0.00015882 | 1.4587e-06 | 108.875
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 7 | 98 | 9174 | 0.0016728 | 1.787e-05 | 93.6122
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CROSSARM | 22 | 5225 | 922465 | 0.16544 | 0.0009371 | 176.5483
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | NONE | 4 | 13 | 1326 | 0.00023782 | 2.3316e-06 | 102
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | FUSE | 14 | 111 | 55836 | 0.010014 | 1.9908e-05 | 503.027
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | FUSE | 12 | 13 | 925 | 0.0001659 | 2.3316e-06 | 71.1538
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | NONE | 26 | 341 | 133091 | 0.02387 | 6.1158e-05 | 390.2962
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | U | NONE | 9 | 7424 | 498735 | 0.089808 | 0.0013369 | 67.1787
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | INSULATOR | 13 | 1847 | 445013 | 0.079813 | 0.00033126 | 240.9383
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | SPLICE, OH | 2 | 91 | 19758 | 0.0035436 | 1.6321e-05 | 217.1209
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 5 | 18 | 974 | 0.00017469 | 3.2283e-06 | 54.1111
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 4 | 512 | 9.2197e-05 | 7.2029e-07 | 128
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 4 | 284 | 5.114e-05 | 7.2029e-07 | 71
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 2 | 144 | 2.593e-05 | 3.6014e-07 | 72
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 1 | 1 | 822 | 0.00014802 | 1.8007e-07 | 822
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | TRANSFORMER, UG | 2 | 43 | 19530 | 0.0035168 | 7.7431e-06 | 454.186
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 14 | 27 | 804 | 0.0001442 | 4.8425e-06 | 29.7778
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | NONE | 9 | 969 | 67369 | 0.012131 | 0.00017449 | 69.5243
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 37 | 23347 | 0.0041873 | 6.636e-06 | 631
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | ARRESTER | 3 | 27 | 6734 | 0.0012126 | 4.8619e-06 | 249.4074
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 8 | 1872 | 0.00033709 | 1.4406e-06 | 234
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | ERF | NONE | 4 | 3112 | 44531 | 0.0079866 | 0.00055814 | 14.3094
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | STATIC WIRE | 2 | 37 | 3849 | 0.0006931 | 6.6627e-06 | 104.027
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | F | POLE | 1 | 9 | 5837 | 0.0010469 | 1.6142e-06 | 648.5556
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | POLE | 1 | 94 | 16976 | 0.0030446 | 1.6859e-05 | 180.5957
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ERO | BREAKER | 1 | 1644 | 274548 | 0.04924 | 0.00029485 | 167
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CUTOUT | 309 | 1005 | 32896 | 0.0058581 | 0.00017897 | 32.7323
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | FUSE | 1 | 3 | 417 | 7.5496e-05 | 5.4314e-07 | 139
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 7 | 14 | 2376 | 0.00043324 | 2.5528e-06 | 169.7143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 1 | 210 | 3.8292e-05 | 1.8234e-07 | 210
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | POLE HARDWARE | 2 | 1032 | 155130 | 0.028287 | 0.00018818 | 150.3198
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 11 | 504 | 212674 | 0.038779 | 9.19e-05 | 421.9722
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | FUSE | 2 | 11 | 1160 | 0.00021001 | 1.9915e-06 | 105.4545
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | TRANSFORMER, OH | 1 | 1 | 40 | 7.2419e-06 | 1.8105e-07 | 40
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | ARRESTER | 1 | 4 | 120 | 2.1726e-05 | 7.2419e-07 | 30
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 7 | 1267 | 0.00022939 | 1.2673e-06 | 181
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 3 | 2494 | 0.00045476 | 5.4703e-07 | 831.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 3 | 551 | 9.922e-05 | 5.4022e-07 | 183.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 26 | 2342 | 490351 | 0.088298 | 0.00042173 | 209.3728
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CROSSARM | 1 | 2 | 3810 | 0.00068607 | 3.6014e-07 | 1905
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CABLE TERMINATOR | 3 | 4 | 471 | 8.4814e-05 | 7.2029e-07 | 117.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CUTOUT | 1 | 2 | 146 | 2.6e-05 | 3.5616e-07 | 73
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 1 | 4 | 3120 | 0.00055561 | 7.1232e-07 | 780
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | NONE | 15 | 1972 | 112882 | 0.020102 | 0.00035117 | 57.2424
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 5 | 77 | 14990 | 0.0026694 | 1.3712e-05 | 194.6753
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 11 | 251 | 14521 | 0.0025859 | 4.4698e-05 | 57.8526
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | EQF | REGULATOR | 2 | 1951 | 25363 | 0.0046247 | 0.00035575 | 13
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | OTHER EQUIPMENT | 1 | 1 | 207 | 3.7745e-05 | 1.8234e-07 | 207
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 3 | 690 | 0.00012582 | 5.4703e-07 | 230
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 3 | 7 | 2275 | 0.00040966 | 1.2605e-06 | 325
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONN/CLAMP | 4 | 6 | 434 | 7.8151e-05 | 1.0804e-06 | 72.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 811 | 61636 | 0.011099 | 0.00014604 | 76
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | NONE | 4 | 6 | 705 | 0.00012644 | 1.0761e-06 | 117.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 83 | 948 | 175632 | 0.031277 | 0.00016882 | 185.2658
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 13 | 473 | 169066 | 0.030107 | 8.4232e-05 | 357.4334
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 20 | 594 | 259289 | 0.046174 | 0.00010578 | 436.5135
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | CAPACITOR | 3 | 2314 | 13884 | 0.0025136 | 0.00041894 | 6
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 8 | 4417 | 870149 | 0.15496 | 0.00078658 | 197
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 2 | 1066 | 0.00018983 | 3.5616e-07 | 533
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 9 | 107 | 3295 | 0.00059096 | 1.919e-05 | 30.7944
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | FUSE | 1028 | 7378 | 947259 | 0.16869 | 0.0013139 | 128.3897
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 212 | 6328 | 447471 | 0.079686 | 0.0011269 | 70.7129
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 9 | 1611 | 0.00028893 | 1.6142e-06 | 179
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CUTOUT | 7 | 142 | 15444 | 0.0027699 | 2.5468e-05 | 108.7606
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONN/CLAMP | 2 | 6 | 1014 | 0.00018186 | 1.0761e-06 | 169
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | NONE | 7 | 435 | 39922 | 0.00716 | 7.8017e-05 | 91.7747
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 3 | 986 | 0.00017979 | 5.4703e-07 | 328.6667
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | FUSE | 1 | 4 | 588 | 0.00010722 | 7.2937e-07 | 147
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 2 | 944 | 140522 | 0.025623 | 0.00017213 | 148.8581
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 10 | 2169 | 0.0003955 | 1.8234e-06 | 216.9
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 3 | 582 | 0.00010537 | 5.4314e-07 | 194
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 3 | 537 | 9.7222e-05 | 5.4314e-07 | 179
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | ARRESTER | 1 | 23 | 1863 | 0.00033413 | 4.1251e-06 | 81
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 43 | 286 | 61770 | 0.011 | 5.0931e-05 | 215.979
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 3 | 734 | 209509 | 0.037309 | 0.00013071 | 285.4346
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | POLE | 1 | 1 | 145 | 2.5822e-05 | 1.7808e-07 | 145
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 85 | 1.5389e-05 | 1.8105e-07 | 85
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 20 | 65 | 6188 | 0.001102 | 1.1575e-05 | 95.2
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | FUSE | 39 | 134 | 10096 | 0.0017979 | 2.3863e-05 | 75.3433
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 399 | 19212 | 5250851 | 0.93507 | 0.0034213 | 273.311
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | FUSE | 1 | 41 | 1476 | 0.00026285 | 7.3013e-06 | 36
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | NONE | 37 | 927 | 54690 | 0.0097392 | 0.00016508 | 58.9968
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 15 | 462 | 117005 | 0.020836 | 8.2273e-05 | 253.2576
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 2 | 4 | 918 | 0.00016348 | 7.1232e-07 | 229.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 5 | 3026 | 0.00053887 | 8.904e-07 | 605.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 7 | 3863 | 0.00068792 | 1.2466e-06 | 551.8571
AEP Total | 2025 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 6 | 1734 | 0.00030879 | 1.0685e-06 | 289
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 1 | 474 | 8.441e-05 | 1.7808e-07 | 474
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | TOR | CONDUCTOR OVERHEAD | 1 | 44 | 28556 | 0.0051421 | 7.9232e-06 | 649
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 2 | 428 | 7.7071e-05 | 3.6014e-07 | 214
AEP Total | 2025 | 5615460 | PARTIAL POWER | O | NONE | 1 | 1 | 94 | 1.674e-05 | 1.7808e-07 | 94
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | FUSE | 3 | 32 | 2127 | 0.00037878 | 5.6986e-06 | 66.4688
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 3 | 5 | 977 | 0.00017398 | 8.904e-07 | 195.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 2 | 210 | 3.8292e-05 | 3.6468e-07 | 105
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 880 | 214360 | 0.038446 | 0.00015783 | 243.5909
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 1 | 607 | 0.00011068 | 1.8234e-07 | 607
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 1 | 1 | 948 | 0.00016882 | 1.7808e-07 | 948
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 1 | 1 | 76 | 1.3534e-05 | 1.7808e-07 | 76
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 8 | 1856 | 0.00033287 | 1.4348e-06 | 232
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | INSULATOR | 3 | 2260 | 205727 | 0.037046 | 0.00040696 | 91.0296
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | POLE | 1 | 5 | 1215 | 0.00021997 | 9.0523e-07 | 243
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CUTOUT | 452 | 12850 | 2282264 | 0.4132 | 0.0023264 | 177.6081
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 20 | 1036 | 105201 | 0.019046 | 0.00018756 | 101.5454
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 23 | 73 | 6692 | 0.0012116 | 1.3216e-05 | 91.6712
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 6 | 2922 | 0.00052902 | 1.0863e-06 | 487
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 4 | 20 | 3029 | 0.00054839 | 3.6209e-06 | 151.45
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | METERING | 6 | 6 | 514 | 9.3058e-05 | 1.0863e-06 | 85.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | NONE | 8 | 152 | 32276 | 0.0058435 | 2.7519e-05 | 212.3421
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 10 | 34 | 2127 | 0.00037878 | 6.0547e-06 | 62.5588
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 2 | 577 | 0.00010275 | 3.5616e-07 | 288.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 1 | 359 | 6.3931e-05 | 1.7808e-07 | 359
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CROSSARM | 11 | 259 | 15011 | 0.0026732 | 4.6123e-05 | 57.9575
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | CROSSARM | 3 | 1771 | 296081 | 0.052726 | 0.00031538 | 167.1829
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 2 | 344 | 6.1945e-05 | 3.6014e-07 | 172
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE | 1 | 16 | 3244 | 0.00058415 | 2.8812e-06 | 202.75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CUTOUT | 2 | 420 | 102044 | 0.018375 | 7.563e-05 | 242.9619
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | FUSE | 1 | 6 | 834 | 0.00015018 | 1.0804e-06 | 139
AEP Total | 2021 | 5523447 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 55 | 9.9576e-06 | 1.8105e-07 | 55
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 87 | 1.5603e-05 | 1.7935e-07 | 87
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 146 | 38544 | 0.0069129 | 2.6185e-05 | 264
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | U | CROSSARM | 1 | 379 | 70494 | 0.012643 | 6.7974e-05 | 186
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 90 | 2958 | 0.00052676 | 1.6027e-05 | 32.8667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 5 | 163 | 17944 | 0.0031955 | 2.9027e-05 | 110.0859
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | NONE | 5 | 12 | 4396 | 0.00078284 | 2.137e-06 | 366.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 16 | 1603 | 0.00028546 | 2.8493e-06 | 100.1875
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 3 | 429 | 7.6396e-05 | 5.3424e-07 | 143
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 4 | 4456 | 0.00079352 | 7.1232e-07 | 1114
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 7 | 11 | 2598 | 0.00046265 | 1.9589e-06 | 236.1818
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | NONE | 1 | 2 | 27 | 4.8082e-06 | 3.5616e-07 | 13.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 1 | 48 | 3504 | 0.00062399 | 8.5478e-06 | 73
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 156 | 20570 | 0.0036631 | 2.778e-05 | 131.859
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | POLE | 1 | 1 | 157 | 2.8271e-05 | 1.8007e-07 | 157
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 8 | 760 | 0.00013685 | 1.4406e-06 | 95
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 307 | 114511 | 0.02062 | 5.5282e-05 | 373
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 4 | 144 | 29947 | 0.005333 | 2.5643e-05 | 207.9653
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | NONE | 17 | 251 | 140632 | 0.025044 | 4.4698e-05 | 560.2869
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 569 | 108324 | 0.01929 | 0.00010133 | 190.3761
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | FUSE | 1 | 1 | 56 | 9.9725e-06 | 1.7808e-07 | 56
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 1 | 161 | 2.8671e-05 | 1.7808e-07 | 161
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 4 | 12 | 1263 | 0.00022866 | 2.1726e-06 | 105.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 5 | 12 | 2472 | 0.00044755 | 2.1726e-06 | 206
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 1 | 4465 | 0.00080837 | 1.8105e-07 | 4465
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | NONE | 1 | 1 | 40 | 7.2419e-06 | 1.8105e-07 | 40
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 57 | 1.032e-05 | 1.8105e-07 | 57
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | SPLICE, OH | 1 | 1 | 118 | 2.1363e-05 | 1.8105e-07 | 118
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 217 | 3.9287e-05 | 1.8105e-07 | 217
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 39 | 64 | 8219 | 0.00148 | 1.1525e-05 | 128.4219
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | FUSE | 229 | 946 | 86429 | 0.015563 | 0.00017035 | 91.3626
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | POLE | 1 | 163 | 58680 | 0.010624 | 2.9511e-05 | 360
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | NONE | 97 | 7227 | 1999486 | 0.36459 | 0.0013178 | 276.6689
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 5 | 923 | 239537 | 0.043678 | 0.0001683 | 259.52
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 99 | 230 | 18617 | 0.0033947 | 4.1939e-05 | 80.9435
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | NONE | 21 | 2017 | 327681 | 0.05975 | 0.00036778 | 162.4596
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 15 | 135 | 35668 | 0.0065038 | 2.4616e-05 | 264.2074
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 3 | 318 | 5.7985e-05 | 5.4703e-07 | 106
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 20 | 408 | 113551 | 0.020705 | 7.4396e-05 | 278.3113
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 1 | 83 | 1.5134e-05 | 1.8234e-07 | 83
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 2 | 60 | 1.0941e-05 | 3.6468e-07 | 30
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 19 | 2034 | 297827 | 0.054306 | 0.00037088 | 146.4243
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 1 | 4 | 460 | 8.3877e-05 | 7.2937e-07 | 115
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | FW | NONE | 1 | 12 | 3850 | 0.00070202 | 2.1881e-06 | 320.8333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | FUSE | 6 | 25 | 2442 | 0.00044528 | 4.5586e-06 | 97.68
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 30 | 32688 | 0.0059604 | 5.4703e-06 | 1089.6
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 36 | 5148 | 0.0009387 | 6.5643e-06 | 143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 33 | 6349 | 0.0011577 | 6.0173e-06 | 192.3939
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CUTOUT | 1 | 48 | 12393 | 0.0022598 | 8.7524e-06 | 258.1875
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | NONE | 109 | 2739 | 149821 | 0.026979 | 0.00049322 | 54.6992
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | POLE | 491 | 14721 | 2859585 | 0.51493 | 0.0026508 | 194.2521
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | SCO | NONE | 4 | 208 | 33141 | 0.0059678 | 3.7455e-05 | 159.3317
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 137 | 1635 | 236804 | 0.042471 | 0.00029324 | 144.8343
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONN/CLAMP | 88 | 221 | 20003 | 0.0035875 | 3.9636e-05 | 90.5113
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 8 | 768 | 0.0001383 | 1.4406e-06 | 96
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 14 | 1718 | 157651 | 0.028275 | 0.00030812 | 91.7643
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | METERING | 1 | 1 | 194 | 3.4934e-05 | 1.8007e-07 | 194
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 2 | 2 | 219 | 3.9278e-05 | 3.587e-07 | 109.5
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | CROSSARM | 4 | 2770 | 29038 | 0.005208 | 0.0004968 | 10.483
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 236 | 1260 | 154332 | 0.027483 | 0.00022438 | 122.4857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | FUSE | 2 | 6 | 345 | 6.1876e-05 | 1.0761e-06 | 57.5
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | SCO | NONE | 3 | 721 | 15358 | 0.0027545 | 0.00012931 | 21.301
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 8 | 6614 | 0.0011862 | 1.4348e-06 | 826.75
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, OH | 8 | 16 | 4274 | 0.00076654 | 2.8696e-06 | 267.125
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE | 5 | 58 | 47248 | 0.0084739 | 1.0402e-05 | 814.6207
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1274 | 59129 | 16328514 | 2.9078 | 0.01053 | 276.1507
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | NONE | 2 | 216 | 36300 | 0.0065104 | 3.874e-05 | 168.0556
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | NONE | 1 | 2 | 202 | 3.6833e-05 | 3.6468e-07 | 101
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | OTHER EQUIPMENT | 1 | 9 | 477 | 8.6977e-05 | 1.6411e-06 | 53
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CUTOUT | 2 | 10 | 1527 | 0.00027844 | 1.8234e-06 | 152.7
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | POLE HARDWARE | 1 | 185 | 16280 | 0.0029316 | 3.3313e-05 | 88
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 304 | 5.4742e-05 | 3.6014e-07 | 152
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | BREAKER | 1 | 260 | 2860 | 0.0005215 | 4.7409e-05 | 11
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | FUSE | 1 | 5 | 300 | 5.4703e-05 | 9.1171e-07 | 60
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 124 | 2.261e-05 | 1.8234e-07 | 124
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1 | 1 | 61 | 1.1123e-05 | 1.8234e-07 | 61
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | POLE | 461 | 18003 | 3129993 | 0.56667 | 0.0032594 | 173.8595
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | METERING | 2 | 2 | 169 | 3.0597e-05 | 3.6209e-07 | 84.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | POLE | 1 | 9 | 738 | 0.00013361 | 1.6294e-06 | 82
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | NONE | 3 | 11 | 8101 | 0.0014667 | 1.9915e-06 | 736.4545
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CUTOUT | 1 | 23 | 2257 | 0.00040862 | 4.1641e-06 | 98.1304
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | NONE | 2 | 36 | 8532 | 0.0015447 | 6.5177e-06 | 237
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONN/CLAMP | 5 | 8 | 1186 | 0.00021472 | 1.4484e-06 | 148.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 29 | 5394 | 0.00097656 | 5.2503e-06 | 186
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | FUSE | 176 | 1498 | 401772 | 0.07326 | 0.00027315 | 268.2056
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | FUSE | 145 | 1003 | 156325 | 0.028505 | 0.00018289 | 155.8574
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CUTOUT | 65 | 220 | 5311 | 0.00096842 | 4.0115e-05 | 24.1409
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 25 | 2167 | 0.00039514 | 4.5586e-06 | 86.68
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 11 | 31 | 2175 | 0.00039659 | 5.6526e-06 | 70.1613
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | NONE | 28 | 909 | 196481 | 0.035827 | 0.00016575 | 216.1507
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, OH | 18 | 41 | 3890 | 0.00070931 | 7.476e-06 | 94.878
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | REGULATOR | 2 | 186 | 1536 | 0.00028008 | 3.3916e-05 | 8.2581
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 4 | 212 | 3.8022e-05 | 7.174e-07 | 53
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 2 | 7 | 705 | 0.00012764 | 1.2673e-06 | 100.7143
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 3 | 3 | 618 | 0.00011269 | 5.4703e-07 | 206
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 2 | 9 | 606 | 0.0001105 | 1.6411e-06 | 67.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 2 | 532 | 9.7006e-05 | 3.6468e-07 | 266
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | OU | CONDUCTOR OVERHEAD | 1 | 20 | 21080 | 0.0038438 | 3.6468e-06 | 1054
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CROSSARM | 9 | 325 | 14729 | 0.0026416 | 5.8289e-05 | 45.32
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | FW | NONE | 7 | 3061 | 70593 | 0.012661 | 0.00054899 | 23.0621
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | SPLICE, OH | 3 | 1022 | 86943 | 0.015593 | 0.0001833 | 85.0714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | FUSE | 5 | 35 | 2831 | 0.00050978 | 6.3025e-06 | 80.8857
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CUTOUT | 4 | 332 | 56147 | 0.01011 | 5.9784e-05 | 169.1175
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | FUSE | 5 | 12 | 819 | 0.00014748 | 2.1609e-06 | 68.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | NONE | 2 | 7 | 760 | 0.00013685 | 1.2605e-06 | 108.5714
AEP Total | 2023 | 5575683 | TRANSMISSION STATION | SCO | NONE | 5 | 2853 | 191633 | 0.034369 | 0.00051169 | 67.1689
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 4 | 14 | 4174 | 0.00074331 | 2.4931e-06 | 298.1429
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 37 | 406 | 60734 | 0.010815 | 7.23e-05 | 149.5911
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 1 | 1 | 13 | 2.315e-06 | 1.7808e-07 | 13
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 1 | 27 | 13392 | 0.0024019 | 4.8425e-06 | 496
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 3 | 79 | 32294 | 0.0058152 | 1.4226e-05 | 408.7848
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 7 | 1302 | 0.00023572 | 1.2673e-06 | 186
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 65 | 23725 | 0.0042953 | 1.1768e-05 | 365
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | RECLOSER, LINE/OCR/BR | 1 | 73 | 2555 | 0.00046257 | 1.3216e-05 | 35
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 2 | 3 | 416 | 7.5854e-05 | 5.4703e-07 | 138.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 1 | 2825 | 0.0005087 | 1.8007e-07 | 2825
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | FUSE | 9 | 51 | 81144 | 0.014796 | 9.2994e-06 | 1591.0588
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 3 | 99 | 1.7827e-05 | 5.4022e-07 | 33
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | FUSE | 4 | 8 | 1208 | 0.00022027 | 1.4587e-06 | 151
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | FUSE | 1 | 1 | 28 | 5.1056e-06 | 1.8234e-07 | 28
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 299 | 92871 | 0.016814 | 5.4133e-05 | 310.6054
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | FUSE | 2 | 4 | 3289 | 0.00059546 | 7.2419e-07 | 822.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | POLE | 4 | 34 | 13848 | 0.0024936 | 6.1224e-06 | 407.2941
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 183 | 1760 | 352683 | 0.063508 | 0.00031693 | 200.3881
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 68 | 1340 | 660041 | 0.11885 | 0.0002413 | 492.5679
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | NONE | 53 | 4720 | 839247 | 0.15112 | 0.00084994 | 177.8066
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 13 | 93 | 17551 | 0.0031604 | 1.6747e-05 | 188.7204
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | FUSE | 41 | 117 | 10900 | 0.0019628 | 2.1068e-05 | 93.1624
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 120 | 3446 | 514923 | 0.092352 | 0.00061804 | 149.4263
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NONE | 290 | 31655 | 6331449 | 1.1355 | 0.0056773 | 200.0142
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 109 | 1.9875e-05 | 1.8234e-07 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | NONE | 1 | 243 | 60750 | 0.011077 | 4.4309e-05 | 250
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | METERING | 2 | 303 | 11284 | 0.0020575 | 5.525e-05 | 37.2409
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 2 | 731 | 97954 | 0.017861 | 0.00013329 | 134
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 254 | 2657 | 372705 | 0.066845 | 0.00047653 | 140.2729
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 21 | 948 | 182842 | 0.032793 | 0.00017002 | 192.8713
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | METERING | 8 | 8 | 879 | 0.00015765 | 1.4348e-06 | 109.875
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 24 | 43 | 11346 | 0.0020349 | 7.7121e-06 | 263.8605
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CUTOUT | 5 | 549 | 6294 | 0.0011288 | 9.8463e-05 | 11.4645
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, OH | 2 | 971 | 191586 | 0.034361 | 0.00017415 | 197.3079
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONN/CLAMP | 3 | 7 | 1787 | 0.0003205 | 1.2555e-06 | 255.2857
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | NONE | 58 | 4225 | 708725 | 0.12621 | 0.00075239 | 167.7456
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 37 | 178 | 15096 | 0.0026883 | 3.1698e-05 | 84.809
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 20 | 1163 | 287960 | 0.05128 | 0.00020711 | 247.601
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 54 | 3997 | 1455064 | 0.25912 | 0.00071178 | 364.039
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | NONE | 22 | 778 | 274829 | 0.048941 | 0.00013855 | 353.2506
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 6 | 91 | 36960 | 0.0065818 | 1.6205e-05 | 406.1538
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 701 | 82701 | 0.014892 | 0.00012623 | 117.9757
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | NONE | 7 | 274 | 91748 | 0.016338 | 4.8794e-05 | 334.8467
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 1 | 11 | 770 | 0.00013712 | 1.9589e-06 | 70
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 4 | 549 | 23652 | 0.0042119 | 9.7766e-05 | 43.082
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 1 | 86 | 1.5315e-05 | 1.7808e-07 | 86
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 6 | 445 | 195711 | 0.034852 | 7.9246e-05 | 439.8
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 4 | 34 | 8606 | 0.0015326 | 6.0547e-06 | 253.1176
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 6 | 336 | 66978 | 0.011927 | 5.9835e-05 | 199.3393
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 636 | 0.00011326 | 3.5616e-07 | 318
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | O | NONE | 2 | 118 | 10842 | 0.0019445 | 2.1163e-05 | 91.8814
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 3 | 10 | 1517 | 0.00027015 | 1.7808e-06 | 151.7
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | POLE | 2 | 276 | 117335 | 0.020895 | 4.915e-05 | 425.1268
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 8 | 1278 | 0.00022759 | 1.4246e-06 | 159.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | REGULATOR | 4 | 565 | 28827 | 0.0051335 | 0.00010062 | 51.0212
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | PEDESTAL | 1 | 12 | 840 | 0.00014959 | 2.137e-06 | 70
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 370 | 51800 | 0.0092245 | 6.589e-05 | 140
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 32 | 13616 | 0.0024247 | 5.6986e-06 | 425.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 5 | 790 | 0.00014068 | 8.904e-07 | 158
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | FW | NONE | 1 | 252 | 11018 | 0.0019621 | 4.4876e-05 | 43.7222
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | NONE | 1 | 5 | 995 | 0.00017917 | 9.0036e-07 | 199
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | POLE | 6 | 1008 | 116487 | 0.020744 | 0.0001795 | 115.5625
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 2 | 11 | 383 | 6.8691e-05 | 1.9729e-06 | 34.8182
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 2 | 21 | 3223 | 0.00058037 | 3.7815e-06 | 153.4762
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | CUTOUT | 1 | 1 | 172 | 3.0972e-05 | 1.8007e-07 | 172
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, OH | 11 | 13 | 1392 | 0.00025066 | 2.3409e-06 | 107.0769
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 4 | 130 | 26469 | 0.0047663 | 2.3409e-05 | 203.6077
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | FUSE | 11 | 103 | 10369 | 0.0018672 | 1.8547e-05 | 100.6699
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | REGULATOR | 4 | 1249 | 225246 | 0.04056 | 0.00022491 | 180.3411
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 1 | 11 | 1.9729e-06 | 1.7935e-07 | 11
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 4 | 4 | 1292 | 0.00023172 | 7.174e-07 | 323
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 25 | 316 | 276728 | 0.04928 | 5.6273e-05 | 875.7215
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | SCO | NONE | 1 | 24 | 2040 | 0.00036933 | 4.3451e-06 | 85
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | U | NONE | 2 | 847 | 58616 | 0.010688 | 0.00015444 | 69.2043
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 2 | 4 | 2302 | 0.00041975 | 7.2937e-07 | 575.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | REGULATOR | 3 | 1358 | 36289 | 0.006617 | 0.00024762 | 26.7224
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | POLE | 1 | 132 | 48444 | 0.0088334 | 2.4069e-05 | 367
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 153 | 2.7551e-05 | 1.8007e-07 | 153
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | FUSE | 8 | 9 | 694 | 0.00012359 | 1.6027e-06 | 77.1111
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 73 | 200 | 22197 | 0.0039528 | 3.5616e-05 | 110.985
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | POLE | 2 | 80 | 22076 | 0.0039593 | 1.4348e-05 | 275.95
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 1 | 119 | 2.1191e-05 | 1.7808e-07 | 119
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | NONE | 1 | 2 | 2256 | 0.00040175 | 3.5616e-07 | 1128
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 14 | 3134 | 0.00057146 | 2.5528e-06 | 223.8571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | FUSE | 1 | 8 | 7264 | 0.001308 | 1.4406e-06 | 908
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CUTOUT | 2 | 3 | 1181 | 0.00021181 | 5.3805e-07 | 393.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 311 | 5.5383e-05 | 1.7808e-07 | 311
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 2 | 1819 | 187439 | 0.033617 | 0.00032624 | 103.0451
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | NONE | 3 | 494 | 35388 | 0.0063019 | 8.7971e-05 | 71.6356
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 63 | 1209 | 193995 | 0.034547 | 0.0002153 | 160.4591
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 2 | 6 | 1510 | 0.0002689 | 1.0685e-06 | 251.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 13 | 4962 | 650816 | 0.1159 | 0.00088363 | 131.16
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 1 | 201 | 3.5794e-05 | 1.7808e-07 | 201
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 4 | 27 | 1520 | 0.00027068 | 4.8082e-06 | 56.2963
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 23 | 4002 | 0.00072973 | 4.1939e-06 | 174
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 111 | 2.0096e-05 | 1.8105e-07 | 111
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR UG | 6 | 12 | 2890 | 0.00052041 | 2.1609e-06 | 240.8333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 7 | 210 | 3.7815e-05 | 1.2605e-06 | 30
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 199 | 39203 | 0.0070311 | 3.5691e-05 | 197
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 7 | 310 | 162729 | 0.028979 | 5.5205e-05 | 524.9323
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE | 3 | 20 | 22425 | 0.0039934 | 3.5616e-06 | 1121.25
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | FUSE | 4 | 27 | 2867 | 0.00051055 | 4.8082e-06 | 106.1852
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 403 | 25792 | 0.004593 | 7.1766e-05 | 64
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 3 | 4 | 437 | 7.7821e-05 | 7.1232e-07 | 109.25
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 45 | 8.0136e-06 | 1.7808e-07 | 45
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 263 | 4.6835e-05 | 1.7808e-07 | 263
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | FUSE | 1 | 1 | 81 | 1.4424e-05 | 1.7808e-07 | 81
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | POLE | 1 | 151 | 12303 | 0.0021909 | 2.689e-05 | 81.4768
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 5 | 1535 | 0.00027335 | 8.904e-07 | 307
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 43 | 20683 | 0.0036832 | 7.6574e-06 | 481
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 204 | 32699 | 0.005823 | 3.6328e-05 | 160.2892
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 1 | 148 | 2.6651e-05 | 1.8007e-07 | 148
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 56 | 5880 | 0.0010588 | 1.0084e-05 | 105
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 37 | 6993 | 0.0012453 | 6.589e-06 | 189
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE | 1 | 8 | 796 | 0.00014175 | 1.4246e-06 | 99.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | PEDESTAL | 2 | 4 | 347 | 6.1794e-05 | 7.1232e-07 | 86.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | CUTOUT | 1 | 18 | 2712 | 0.00048295 | 3.2054e-06 | 150.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 5 | 2160 | 0.00038465 | 8.904e-07 | 432
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONN/CLAMP | 1 | 6 | 828 | 0.00014745 | 1.0685e-06 | 138
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 3 | 188 | 12471 | 0.0022208 | 3.3479e-05 | 66.3351
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 1 | 30 | 5.3424e-06 | 1.7808e-07 | 30
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | INSULATOR | 1 | 9 | 1998 | 0.00035834 | 1.6142e-06 | 222
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 2 | 30 | 5.4022e-06 | 3.6014e-07 | 15
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 1 | 63 | 1.1345e-05 | 1.8007e-07 | 63
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 1 | 1 | 92 | 1.6775e-05 | 1.8234e-07 | 92
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 1 | 2 | 312 | 5.5561e-05 | 3.5616e-07 | 156
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 2 | 144 | 2.5643e-05 | 3.5616e-07 | 72
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 2 | 3380 | 0.00060191 | 3.5616e-07 | 1690
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 386 | 50180 | 0.008936 | 6.8739e-05 | 130
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 81 | 2207 | 678903 | 0.12291 | 0.00039957 | 307.6135
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | POLE | 73 | 1191 | 117161 | 0.021212 | 0.00021563 | 98.372
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 597 | 19104 | 0.0034587 | 0.00010808 | 32
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | FUSE | 165 | 2106 | 441675 | 0.079964 | 0.00038128 | 209.7222
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 36 | 1845 | 496001 | 0.089799 | 0.00033403 | 268.8352
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 5 | 407 | 16209 | 0.0029346 | 7.3686e-05 | 39.8256
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CUTOUT | 7 | 55 | 8515 | 0.0015416 | 9.9576e-06 | 154.8182
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 65 | 1.1768e-05 | 1.8105e-07 | 65
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 16 | 64 | 6493 | 0.0011755 | 1.1587e-05 | 101.4531
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | POLE | 13 | 865 | 675523 | 0.1223 | 0.00015661 | 780.9514
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | INSULATOR | 1 | 41 | 1271 | 0.00023011 | 7.4229e-06 | 31
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 5 | 69 | 38796 | 0.0070239 | 1.2492e-05 | 562.2609
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | OU | NONE | 3 | 3984 | 913054 | 0.16531 | 0.00072129 | 229.1802
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 4 | 516 | 9.342e-05 | 7.2419e-07 | 129
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | NONE | 5 | 1591 | 57506 | 0.010411 | 0.00028804 | 36.1446
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 1 | 188 | 3.4037e-05 | 1.8105e-07 | 188
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | NONE | 1 | 1 | 533 | 9.6498e-05 | 1.8105e-07 | 533
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | OTHER EQUIPMENT | 1 | 3259 | 302447 | 0.054757 | 0.00059003 | 92.8036
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 4 | 684 | 0.00012384 | 7.2419e-07 | 171
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | O | NONE | 1 | 1038 | 90306 | 0.01635 | 0.00018793 | 87
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 4 | 17 | 11910 | 0.0021563 | 3.0778e-06 | 700.5882
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE | 47 | 7824 | 1321385 | 0.23794 | 0.0014089 | 168.8887
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | VIN | NONE | 3 | 2371 | 231789 | 0.041739 | 0.00042695 | 97.76
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 15 | 115 | 5780 | 0.0010408 | 2.0708e-05 | 50.2609
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 16 | 144 | 75103 | 0.013694 | 2.6257e-05 | 521.5486
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, OH | 5 | 16 | 3552 | 0.00064768 | 2.9175e-06 | 222
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | VA | NONE | 2 | 5 | 813 | 0.00014824 | 9.1171e-07 | 162.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | FUSE | 251 | 1006 | 151578 | 0.027639 | 0.00018344 | 150.674
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 6 | 27 | 1492 | 0.00027205 | 4.9232e-06 | 55.2593
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | NONE | 84 | 4943 | 1095159 | 0.19969 | 0.00090132 | 221.5576
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | JUMPER/RISER | 4 | 23 | 2013 | 0.00036705 | 4.1939e-06 | 87.5217
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | NONE | 14 | 1115 | 128441 | 0.02342 | 0.00020331 | 115.1937
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 2 | 2 | 438 | 7.9866e-05 | 3.6468e-07 | 219
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 57 | 5786 | 0.001055 | 1.0393e-05 | 101.5088
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 86 | 8278 | 0.0015094 | 1.5681e-05 | 96.2558
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CUTOUT | 2 | 13 | 338 | 6.1632e-05 | 2.3704e-06 | 26
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | METERING | 1 | 10 | 1140 | 0.00020787 | 1.8234e-06 | 114
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | NONE | 165 | 12630 | 1395172 | 0.25022 | 0.0022652 | 110.4649
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | POLE | 514 | 12070 | 2115294 | 0.37669 | 0.0021494 | 175.2522
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | NONE | 22 | 1330 | 259136 | 0.046476 | 0.00023854 | 194.8391
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | INSULATOR | 7 | 62 | 3771 | 0.00067633 | 1.112e-05 | 60.8226
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 216 | 3.874e-05 | 1.7935e-07 | 216
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 5 | 78 | 9800 | 0.0017576 | 1.3989e-05 | 125.641
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | ARRESTER | 2 | 8 | 138 | 2.475e-05 | 1.4348e-06 | 17.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | POLE | 3 | 13 | 943 | 0.00016913 | 2.3316e-06 | 72.5385
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 155 | 1526 | 377541 | 0.067232 | 0.00027175 | 247.4056
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | FUSE | 12 | 51 | 5555 | 0.00098923 | 9.0821e-06 | 108.9216
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | NONE | 1 | 1 | 126 | 2.2598e-05 | 1.7935e-07 | 126
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 56 | 1.0139e-05 | 1.8105e-07 | 56
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 79 | 1.4405e-05 | 1.8234e-07 | 79
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | METERING | 1 | 1 | 307 | 5.5979e-05 | 1.8234e-07 | 307
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 4 | 85 | 20154 | 0.0036749 | 1.5499e-05 | 237.1059
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | FUSE | 4 | 6 | 198 | 3.6104e-05 | 1.0941e-06 | 33
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CROSSARM | 1 | 789 | 85212 | 0.015538 | 0.00014387 | 108
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 9 | 1261 | 0.00022993 | 1.6411e-06 | 140.1111
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 1 | 65 | 1.1768e-05 | 1.8105e-07 | 65
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 1 | 1 | 112 | 2.0277e-05 | 1.8105e-07 | 112
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | FUSE | 12 | 185 | 5526 | 0.00099508 | 3.3313e-05 | 29.8703
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 7 | 720 | 0.00012913 | 1.2555e-06 | 102.8571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | FUSE | 3 | 15 | 2211 | 0.00039814 | 2.7011e-06 | 147.4
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 6 | 12 | 1649 | 0.00029694 | 2.1609e-06 | 137.4167
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 67 | 1.2016e-05 | 1.7935e-07 | 67
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | POLE | 4 | 1355 | 190449 | 0.034295 | 0.000244 | 140.5528
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 16 | 1360 | 0.0002449 | 2.8812e-06 | 85
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 3 | 11 | 367 | 6.6086e-05 | 1.9808e-06 | 33.3636
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | METERING | 1 | 2 | 218 | 3.9256e-05 | 3.6014e-07 | 109
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | FUSE | 9 | 173 | 13432 | 0.002409 | 3.1028e-05 | 77.6416
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 2 | 48 | 8.6088e-06 | 3.587e-07 | 24
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CUTOUT | 5 | 22 | 4499 | 0.00081014 | 3.9616e-06 | 204.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | FUSE | 1 | 1 | 68 | 1.2245e-05 | 1.8007e-07 | 68
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 17 | 608 | 0.00010904 | 3.049e-06 | 35.7647
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | REGULATOR | 1 | 110 | 67430 | 0.012094 | 1.9729e-05 | 613
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | NONE | 3 | 787 | 79038 | 0.014233 | 0.00014172 | 100.4295
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 32 | 178 | 59706 | 0.010632 | 3.1698e-05 | 335.427
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 22 | 355 | 79476 | 0.014153 | 6.3218e-05 | 223.8761
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 5 | 16 | 4286 | 0.00076325 | 2.8493e-06 | 267.875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 2 | 358 | 6.4207e-05 | 3.587e-07 | 179
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 15 | 1183 | 204457 | 0.03641 | 0.00021067 | 172.8292
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 109 | 1.9549e-05 | 1.7935e-07 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CROSSARM | 1 | 253 | 61985 | 0.011302 | 4.6133e-05 | 245
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 2 | 548 | 9.9923e-05 | 3.6468e-07 | 274
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | NONE | 1 | 1 | 26 | 4.6819e-06 | 1.8007e-07 | 26
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | NONE | 1 | 3 | 3528 | 0.00063529 | 5.4022e-07 | 1176
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | SPLICE, OH | 2 | 191 | 25679 | 0.0046241 | 3.4394e-05 | 134.445
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | INSULATOR | 1 | 375 | 61500 | 0.011074 | 6.7527e-05 | 164
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | FUSE | 2 | 5 | 626 | 0.00011148 | 8.904e-07 | 125.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 194 | 22189 | 0.0039514 | 3.4547e-05 | 114.3763
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONN/CLAMP | 2 | 14 | 4095 | 0.00072924 | 2.4931e-06 | 292.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | FUSE | 9 | 44 | 5570 | 0.0009919 | 7.8355e-06 | 126.5909
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 5 | 977 | 445878 | 0.079402 | 0.00017398 | 456.3746
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 3 | 3 | 556 | 9.9012e-05 | 5.3424e-07 | 185.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 10 | 11030 | 0.0019642 | 1.7808e-06 | 1103
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | POLE | 1 | 4 | 1612 | 0.00028706 | 7.1232e-07 | 403
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 182 | 3.295e-05 | 1.8105e-07 | 182
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 2 | 79 | 18339 | 0.0032658 | 1.4068e-05 | 232.1392
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 3 | 739 | 0.0001316 | 5.3424e-07 | 246.3333
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | WU | NONE | 1 | 414 | 31878 | 0.0056768 | 7.3725e-05 | 77
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | SCO | INSULATOR | 1 | 232 | 1740 | 0.00030986 | 4.1315e-05 | 7.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | CONN/CLAMP | 3 | 4 | 474 | 8.441e-05 | 7.1232e-07 | 118.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 8 | 3088 | 0.00054991 | 1.4246e-06 | 386
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 1 | 1 | 14 | 2.4931e-06 | 1.7808e-07 | 14
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | NONE | 6 | 486 | 76052 | 0.013543 | 8.6547e-05 | 156.4856
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | OTHER EQUIPMENT | 1 | 5 | 7375 | 0.0013133 | 8.904e-07 | 1475
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 40 | 7.1232e-06 | 1.7808e-07 | 40
AEP Total | 2025 | 5615460 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 53 | 9.4382e-06 | 1.7808e-07 | 53
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 5 | 75 | 1.3356e-05 | 8.904e-07 | 15
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | BE | FUSE | 1 | 6 | 630 | 0.00011345 | 1.0804e-06 | 105
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1089 | 49624 | 16589422 | 3.0035 | 0.0089842 | 334.3024
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 55 | 508 | 27773 | 0.0050282 | 9.1972e-05 | 54.6713
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 148 | 1364 | 288261 | 0.052189 | 0.00024695 | 211.335
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | FUSE | 215 | 784 | 82380 | 0.014915 | 0.00014194 | 105.0765
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE | 7 | 949 | 206329 | 0.037355 | 0.00017181 | 217.4173
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | SECTIONALIZER | 1 | 2 | 5604 | 0.0010146 | 3.6209e-07 | 2802
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 9 | 31968 | 0.0057877 | 1.6294e-06 | 3552
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | POLE | 5 | 94 | 46012 | 0.0083303 | 1.7018e-05 | 489.4894
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 1 | 69 | 1.2492e-05 | 1.8105e-07 | 69
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 11 | 1485 | 0.00026885 | 1.9915e-06 | 135
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WI | NONE | 1 | 804 | 101304 | 0.018341 | 0.00014556 | 126
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 1 | 3 | 3432 | 0.00062135 | 5.4314e-07 | 1144
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | NONE | 17 | 1061 | 107419 | 0.019448 | 0.00019209 | 101.2432
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 10 | 2680 | 0.0004852 | 1.8105e-06 | 268
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | POLE | 1 | 1 | 392 | 7.097e-05 | 1.8105e-07 | 392
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | SCO | NONE | 5 | 56 | 11418 | 0.0020672 | 1.0139e-05 | 203.8929
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 2245 | 641170 | 0.11608 | 0.00040645 | 285.5991
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 120 | 11423 | 1903174 | 0.34703 | 0.0020829 | 166.6089
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 2 | 352 | 6.4184e-05 | 3.6468e-07 | 176
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | POLE | 1 | 27 | 24246 | 0.0044211 | 4.9232e-06 | 898
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 389 | 8947 | 0.0016314 | 7.0931e-05 | 23
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | ARRESTER | 3 | 6 | 150 | 2.7351e-05 | 1.0941e-06 | 25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CUTOUT | 8 | 142 | 25091 | 0.0045751 | 2.5893e-05 | 176.6972
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 2 | 3 | 462 | 8.3643e-05 | 5.4314e-07 | 154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | FUSE | 1 | 26 | 728 | 0.0001318 | 4.7072e-06 | 28
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | RECLOSER, LINE/OCR/BR | 1 | 102 | 8058 | 0.0014589 | 1.8467e-05 | 79
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | NONE | 4 | 111 | 9148 | 0.0016562 | 2.0096e-05 | 82.4144
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | FUSE | 1031 | 7064 | 874953 | 0.15755 | 0.001272 | 123.8608
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | NONE | 348 | 40450 | 7330878 | 1.3201 | 0.0072839 | 181.2331
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | FUSE | 377 | 4708 | 1278716 | 0.23026 | 0.00084778 | 271.6049
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONN/CLAMP | 67 | 251 | 51662 | 0.0093029 | 4.5198e-05 | 205.8247
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 13 | 1150 | 252321 | 0.045436 | 0.00020708 | 219.4096
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 7 | 399 | 7.1849e-05 | 1.2605e-06 | 57
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | NONE | 22 | 321 | 13990 | 0.0025192 | 5.7803e-05 | 43.5826
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CUTOUT | 6 | 19 | 3022 | 0.00055104 | 3.4645e-06 | 159.0526
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CUTOUT | 1 | 302 | 27180 | 0.0049561 | 5.5067e-05 | 90
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 5 | 1120 | 0.00020422 | 9.1171e-07 | 224
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 229 | 7767 | 0.0014163 | 4.1756e-05 | 33.917
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 243 | 42007 | 0.0076596 | 4.4309e-05 | 172.8683
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 64 | 14115 | 0.0025738 | 1.167e-05 | 220.5469
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | FUSE | 267 | 2791 | 624969 | 0.11209 | 0.00050057 | 223.923
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | FUSE | 907 | 5619 | 684972 | 0.12285 | 0.0010078 | 121.9028
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | POLE | 464 | 11673 | 1846939 | 0.33125 | 0.0020936 | 158.2232
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | FUSE | 1 | 5 | 3880 | 0.00069588 | 8.9675e-07 | 776
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 10 | 6247 | 0.0011204 | 1.7935e-06 | 624.7
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | INSULATOR | 29 | 7033 | 787056 | 0.14116 | 0.0012614 | 111.909
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | WU | NONE | 11 | 9322 | 849703 | 0.15239 | 0.0016719 | 91.1503
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 23 | 1415 | 103958 | 0.018513 | 0.00025198 | 73.4686
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 4 | 76 | 4447 | 0.00080078 | 1.3685e-05 | 58.5132
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | POLE | 7 | 2441 | 125034 | 0.022515 | 0.00043956 | 51.2224
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 1 | 302 | 5.4382e-05 | 1.8007e-07 | 302
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 1 | 29 | 836 | 0.00015054 | 5.2221e-06 | 28.8276
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | FUSE | 4 | 25 | 3291 | 0.00059262 | 4.5018e-06 | 131.64
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | INSULATOR | 11 | 190 | 68180 | 0.012277 | 3.4214e-05 | 358.8421
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | METERING | 2 | 3 | 250 | 4.4838e-05 | 5.3805e-07 | 83.3333
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | NONE | 1 | 1 | 777 | 0.00013936 | 1.7935e-07 | 777
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 3 | 148 | 42898 | 0.0077247 | 2.6651e-05 | 289.8514
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | NONE | 1 | 1296 | 45360 | 0.0081681 | 0.00023337 | 35
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | SCO | NONE | 2 | 97 | 3766 | 0.0006867 | 1.7687e-05 | 38.8247
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | CONN/CLAMP | 6 | 3081 | 329667 | 0.059685 | 0.0005578 | 107
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 26 | 8660 | 0.0015679 | 4.7072e-06 | 333.0769
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | TRANSFORMER, OH | 1 | 6 | 816 | 0.00014694 | 1.0804e-06 | 136
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | RECLOSER, LINE/OCR/BR | 1 | 130 | 10010 | 0.0018025 | 2.3409e-05 | 77
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WH | NONE | 1 | 3 | 159 | 2.8631e-05 | 5.4022e-07 | 53
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 1 | 408 | 7.3175e-05 | 1.7935e-07 | 408
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | SWITCH, OH | 1 | 1237 | 139216 | 0.024968 | 0.00022186 | 112.5432
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CUTOUT | 38 | 260 | 11629 | 0.0020709 | 4.6301e-05 | 44.7269
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 2 | 35 | 4510 | 0.00080314 | 6.2328e-06 | 128.8571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 66 | 12355 | 0.0022159 | 1.1837e-05 | 187.197
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | FUSE | 10 | 110 | 12869 | 0.0022917 | 1.9589e-05 | 116.9909
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 1 | 14 | 3804 | 0.00068225 | 2.5109e-06 | 271.7143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 2 | 1164 | 0.00020876 | 3.587e-07 | 582
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 28 | 64 | 37491 | 0.0066764 | 1.1397e-05 | 585.7969
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | ARRESTER | 1 | 5 | 1308 | 0.00023293 | 8.904e-07 | 261.6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | NONE | 4 | 2811 | 357950 | 0.063744 | 0.00050058 | 127.339
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 45 | 3020 | 412022 | 0.073373 | 0.0005378 | 136.4311
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 128 | 10254 | 0.001826 | 2.2794e-05 | 80.1094
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | RECLOSER, LINE/OCR/BR | 1 | 22 | 7664 | 0.0013801 | 3.9616e-06 | 348.3636
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | POLE | 1 | 20 | 19800 | 0.0035654 | 3.6014e-06 | 990
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CUTOUT | 3 | 9 | 1894 | 0.00034106 | 1.6206e-06 | 210.4444
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 1 | 128 | 2.3049e-05 | 1.8007e-07 | 128
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CUTOUT | 124 | 354 | 7687 | 0.0013689 | 6.304e-05 | 21.7147
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 299 | 25769 | 0.0045889 | 5.3246e-05 | 86.1839
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 16 | 6011 | 670004 | 0.11931 | 0.0010704 | 111.463
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 46 | 9764 | 0.0017388 | 8.1917e-06 | 212.2609
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 1 | 239 | 53562 | 0.009645 | 4.3037e-05 | 224.1088
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | NONE | 1 | 297 | 4752 | 0.0008557 | 5.3481e-05 | 16
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | PEDESTAL | 1 | 5 | 1280 | 0.00023049 | 9.0036e-07 | 256
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 12 | 287 | 49445 | 0.0088052 | 5.1109e-05 | 172.2822
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 2 | 349 | 128552 | 0.022893 | 6.215e-05 | 368.3438
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 7 | 26 | 8880 | 0.0015813 | 4.6301e-06 | 341.5385
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | FUSE | 3 | 9 | 1559 | 0.00027763 | 1.6027e-06 | 173.2222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 4 | 11 | 2506 | 0.00044627 | 1.9589e-06 | 227.8182
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 8 | 272 | 4.8438e-05 | 1.4246e-06 | 34
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 25 | 8000 | 0.0014246 | 4.452e-06 | 320
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 2 | 183 | 17777 | 0.0031657 | 3.2589e-05 | 97.1421
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | U | NONE | 1 | 42 | 8904 | 0.0015856 | 7.4794e-06 | 212
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | SPLICE, OH | 1 | 1 | 199 | 3.5438e-05 | 1.7808e-07 | 199
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 3 | 136 | 2.4219e-05 | 5.3424e-07 | 45.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 1 | 96 | 1.7287e-05 | 1.8007e-07 | 96
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CROSSARM | 1 | 29 | 20909 | 0.0037235 | 5.1643e-06 | 721
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | FUSE | 1 | 1 | 99 | 1.763e-05 | 1.7808e-07 | 99
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | FUSE | 4 | 10 | 1338 | 0.00023827 | 1.7808e-06 | 133.8
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 100 | 1.7808e-05 | 1.7808e-07 | 100
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 356 | 6.4914e-05 | 3.6468e-07 | 178
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | SPLICE, OH | 1 | 3 | 2421 | 0.00044145 | 5.4703e-07 | 807
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 1 | 85 | 1.5137e-05 | 1.7808e-07 | 85
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CIRCUIT SWITCHER | 1 | 1618 | 140766 | 0.025668 | 0.00029503 | 87
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | FUSE | 1 | 10 | 1180 | 0.00021516 | 1.8234e-06 | 118
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | NONE | 2 | 2 | 100 | 1.7808e-05 | 3.5616e-07 | 50
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 17 | 16998 | 0.003027 | 3.0274e-06 | 999.8824
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR UG | 3 | 7182 | 473783 | 0.084371 | 0.001279 | 65.9681
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | R | OTHER EQUIPMENT | 1 | 4 | 708 | 0.00012749 | 7.2029e-07 | 177
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | POLE | 2 | 1299 | 109362 | 0.019941 | 0.00023686 | 84.1894
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1711 | 183077 | 0.032602 | 0.00030469 | 107
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 1 | 260 | 4.6301e-05 | 1.7808e-07 | 260
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 2 | 226 | 4.1209e-05 | 3.6468e-07 | 113
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 338 | 6.1194e-05 | 1.8105e-07 | 338
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 1 | 125 | 2.2631e-05 | 1.8105e-07 | 125
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 1 | 607 | 0.0001099 | 1.8105e-07 | 607
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | METERING | 1 | 2 | 290 | 5.2221e-05 | 3.6014e-07 | 145
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | JUMPER/RISER | 2 | 345 | 4165 | 0.00075 | 6.2125e-05 | 12.0725
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 709 | 53175 | 0.0095753 | 0.00012767 | 75
AEP Total | 2022 | 5553337 | PARTIAL POWER | V | NONE | 1 | 1 | 28 | 5.042e-06 | 1.8007e-07 | 28
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ERF | NONE | 3 | 2974 | 109776 | 0.019768 | 0.00053553 | 36.9119
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | POLE | 4 | 60 | 45470 | 0.0080973 | 1.0685e-05 | 757.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | RECLOSER, LINE/OCR/BR | 1 | 49 | 3332 | 0.00059759 | 8.7882e-06 | 68
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 6 | 39 | 2138 | 0.00038073 | 6.9451e-06 | 54.8205
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | NONE | 135 | 502 | 40020 | 0.0071268 | 8.9396e-05 | 79.7211
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 17 | 164 | 2169 | 0.00038626 | 2.9205e-05 | 13.2256
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 24 | 548 | 60457 | 0.010766 | 9.7588e-05 | 110.323
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 457 | 8.1963e-05 | 1.7935e-07 | 457
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | ARRESTER | 2 | 3 | 687 | 0.00012234 | 5.3424e-07 | 229
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | ARRESTER | 1 | 1 | 32 | 5.6986e-06 | 1.7808e-07 | 32
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | INSULATOR | 5 | 191 | 4161 | 0.00074099 | 3.4013e-05 | 21.7853
AEP Total | 2023 | 5575683 | PARTIAL POWER | V | METERING | 1 | 1 | 53 | 9.5056e-06 | 1.7935e-07 | 53
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CUTOUT | 4 | 47 | 28631 | 0.0051556 | 8.4634e-06 | 609.1702
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONN/CLAMP | 5 | 16 | 903 | 0.0001626 | 2.8812e-06 | 56.4375
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 1 | 231 | 4.1822e-05 | 1.8105e-07 | 231
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 4 | 21 | 5521 | 0.00099418 | 3.7815e-06 | 262.9048
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 24 | 5472 | 0.00098535 | 4.3217e-06 | 228
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 3 | 858 | 0.0001545 | 5.4022e-07 | 286
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CUTOUT | 1 | 2 | 180 | 3.2283e-05 | 3.587e-07 | 90
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | GUY/ANCHOR | 1 | 328 | 116112 | 0.020825 | 5.8827e-05 | 354
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | NONE | 611 | 27780 | 2727364 | 0.48569 | 0.0049471 | 98.1772
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 18 | 1099 | 115914 | 0.020642 | 0.00019571 | 105.4722
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 9 | 143 | 36930 | 0.0065765 | 2.5465e-05 | 258.2517
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 6 | 3518 | 350166 | 0.062357 | 0.00062648 | 99.5355
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | NONE | 10 | 3169 | 154695 | 0.027548 | 0.00056433 | 48.8151
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | TRANSFORMER, UG | 1 | 1 | 198 | 3.526e-05 | 1.7808e-07 | 198
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CUTOUT | 415 | 3154 | 74087 | 0.013193 | 0.00056166 | 23.4899
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 96 | 40314 | 0.0071791 | 1.7096e-05 | 419.9375
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 14 | 221 | 19928 | 0.0035488 | 3.9356e-05 | 90.1719
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | PEDESTAL | 6 | 22 | 1330 | 0.00023685 | 3.9178e-06 | 60.4545
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 13 | 1244 | 0.00022153 | 2.315e-06 | 95.6923
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 53 | 7381 | 0.0013291 | 9.5438e-06 | 139.2642
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | FUSE | 1 | 5 | 450 | 8.1471e-05 | 9.0523e-07 | 90
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | NONE | 10 | 615 | 157333 | 0.028018 | 0.00010952 | 255.826
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | INSULATOR | 1 | 3 | 276 | 4.915e-05 | 5.3424e-07 | 92
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 7 | 209 | 32587 | 0.0058031 | 3.7219e-05 | 155.9187
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CUTOUT | 1 | 1 | 60 | 1.0685e-05 | 1.7808e-07 | 60
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 4 | 28 | 5285 | 0.00094115 | 4.9862e-06 | 188.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 6 | 27 | 8625 | 0.0015359 | 4.8082e-06 | 319.4444
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | SPLICE, UG | 1 | 3 | 394 | 7.0163e-05 | 5.3424e-07 | 131.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 4 | 436 | 7.7643e-05 | 7.1232e-07 | 109
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | NONE | 1 | 1300 | 61100 | 0.010881 | 0.0002315 | 47
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | BREAKER | 2 | 2348 | 164954 | 0.029375 | 0.00041813 | 70.253
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 1 | 132 | 2.3507e-05 | 1.7808e-07 | 132
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | NONE | 4 | 4 | 230 | 4.0958e-05 | 7.1232e-07 | 57.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | CONDUCTOR UG | 1 | 11 | 4378 | 0.0007852 | 1.9729e-06 | 398
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 4 | 368 | 6.5533e-05 | 7.1232e-07 | 92
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | SWITCH, UG | 1 | 5 | 475 | 8.4588e-05 | 8.904e-07 | 95
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | POLE HARDWARE | 2 | 16 | 1399 | 0.00024913 | 2.8493e-06 | 87.4375
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 2500 | 430000 | 0.076574 | 0.0004452 | 172
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | NETWORK LIMITER | 1 | 6 | 516 | 9.1889e-05 | 1.0685e-06 | 86
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 42 | 17752 | 0.0031966 | 7.563e-06 | 422.6667
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CUTOUT | 1 | 1 | 79 | 1.4226e-05 | 1.8007e-07 | 79
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | NONE | 12 | 30 | 2655 | 0.0004728 | 5.3424e-06 | 88.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 3 | 3 | 738 | 0.00013142 | 5.3424e-07 | 246
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 1267 | 0.00022563 | 1.7808e-07 | 1267
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | SPLICE, OH | 2 | 3 | 1375 | 0.00024486 | 5.3424e-07 | 458.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 2542 | 231722 | 0.041952 | 0.00046022 | 91.1574
AEP Total | 2021 | 5523447 | PARTIAL POWER | V | NONE | 1 | 1 | 57 | 1.032e-05 | 1.8105e-07 | 57
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CUTOUT | 1 | 1 | 298 | 5.3952e-05 | 1.8105e-07 | 298
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | METERING | 47 | 291 | 49949 | 0.0089944 | 5.2401e-05 | 171.646
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | POLE | 5 | 5868 | 1211849 | 0.21822 | 0.0010567 | 206.5182
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CUTOUT | 56 | 143 | 20875 | 0.003759 | 2.575e-05 | 145.979
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | NONE | 5 | 656 | 61315 | 0.011041 | 0.00011813 | 93.468
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CUTOUT | 14 | 94 | 19930 | 0.0035888 | 1.6927e-05 | 212.0213
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 34 | 7582 | 0.0013653 | 6.1224e-06 | 223
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | NONE | 40 | 219 | 22817 | 0.0041087 | 3.9436e-05 | 104.1872
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | NONE | 10 | 15 | 2105 | 0.00037905 | 2.7011e-06 | 140.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CROSSARM | 3 | 3611 | 516976 | 0.093093 | 0.00065024 | 143.167
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONN/CLAMP | 9 | 10 | 2323 | 0.00042358 | 1.8234e-06 | 232.3
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 19 | 9994 | 0.0018223 | 3.4645e-06 | 526
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 14 | 2688 | 0.00049014 | 2.5528e-06 | 192
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | NONE | 13 | 8521 | 532300 | 0.097061 | 0.0015537 | 62.4692
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CROSSARM | 5 | 2636 | 388943 | 0.070921 | 0.00048065 | 147.5505
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | U | NONE | 4 | 2667 | 308717 | 0.056292 | 0.00048631 | 115.7544
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 2 | 42 | 7465 | 0.0013612 | 7.6584e-06 | 177.7381
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 653 | 46997 | 6167711 | 1.1062 | 0.0084289 | 131.2363
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 33 | 6167 | 1362030 | 0.24428 | 0.0011061 | 220.8578
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | FUSE | 115 | 2045 | 222103 | 0.039834 | 0.00036677 | 108.6078
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | NONE | 35 | 932 | 79184 | 0.014202 | 0.00016715 | 84.9614
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | NONE | 56 | 1217 | 81415 | 0.014602 | 0.00021827 | 66.8981
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CUTOUT | 13 | 269 | 33084 | 0.0059336 | 4.8245e-05 | 122.9888
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | ARRESTER | 2 | 3 | 772 | 0.00013846 | 5.3805e-07 | 257.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | ARRESTER | 6 | 410 | 103726 | 0.018603 | 7.3534e-05 | 252.9902
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CUTOUT | 43 | 126 | 17176 | 0.0030805 | 2.2598e-05 | 136.3175
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE | 16 | 1018 | 341330 | 0.061218 | 0.00018258 | 335.2947
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | NONE | 14 | 21 | 3117 | 0.00055903 | 3.7664e-06 | 148.4286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | ARRESTER | 54 | 211 | 5636 | 0.0010108 | 3.7843e-05 | 26.7109
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, OH | 31 | 56 | 9269 | 0.0016624 | 1.0044e-05 | 165.5179
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | POLE | 14 | 185 | 66654 | 0.011954 | 3.318e-05 | 360.2919
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | NONE | 7 | 3047 | 614162 | 0.11015 | 0.00054648 | 201.5628
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | METERING | 16 | 81 | 6610 | 0.0011855 | 1.4527e-05 | 81.6049
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 6 | 1824 | 0.00032713 | 1.0761e-06 | 304
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 3 | 9 | 559 | 0.00010026 | 1.6142e-06 | 62.1111
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | BREAKER | 6 | 7572 | 755386 | 0.13548 | 0.001358 | 99.7604
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | POLE HARDWARE | 1 | 12 | 350 | 6.2773e-05 | 2.1522e-06 | 29.1667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 14 | 5157 | 758650 | 0.13606 | 0.00092491 | 147.1107
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | NONE | 23 | 19140 | 849078 | 0.1529 | 0.0034466 | 44.3614
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 13 | 3674 | 1013404 | 0.18249 | 0.00066158 | 275.8312
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 18 | 186 | 29299 | 0.0052759 | 3.3493e-05 | 157.5215
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 27 | 56 | 9513 | 0.001713 | 1.0084e-05 | 169.875
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | SPLICE, UG | 2 | 2 | 252 | 4.5378e-05 | 3.6014e-07 | 126
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 2 | 224 | 4.0336e-05 | 3.6014e-07 | 112
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 5 | 6295 | 1593286 | 0.28691 | 0.0011336 | 253.1034
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 54 | 3078 | 0.00055426 | 9.7239e-06 | 57
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 258 | 61146 | 0.011011 | 4.6459e-05 | 237
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CUTOUT | 2 | 3 | 2299 | 0.00041233 | 5.3805e-07 | 766.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | OTHER EQUIPMENT | 1 | 582 | 155290 | 0.027963 | 0.0001048 | 266.8213
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | JUMPER/RISER | 3 | 3291 | 246902 | 0.044282 | 0.00059024 | 75.0234
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 82 | 1.4707e-05 | 1.7935e-07 | 82
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 1067 | 44814 | 0.0080697 | 0.00019214 | 42
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | OTHER EQUIPMENT | 1 | 1 | 95 | 1.7038e-05 | 1.7935e-07 | 95
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 4 | 20 | 3032 | 0.00054379 | 3.587e-06 | 151.6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | FUSE | 78 | 428 | 36885 | 0.0065685 | 7.6218e-05 | 86.1799
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONN/CLAMP | 1 | 2 | 252 | 4.5196e-05 | 3.587e-07 | 126
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | INSULATOR | 3 | 1509 | 379492 | 0.069197 | 0.00027515 | 251.4858
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 75 | 2850 | 0.00051967 | 1.3676e-05 | 38
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | NONE | 3 | 19 | 2271 | 0.0004141 | 3.4645e-06 | 119.5263
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | POLE HARDWARE | 2 | 17 | 6163 | 0.0011238 | 3.0998e-06 | 362.5294
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 2 | 306 | 5.5797e-05 | 3.6468e-07 | 153
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | CABLE TERMINATOR | 1 | 5 | 3230 | 0.00058478 | 9.0523e-07 | 646
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 24 | 4512 | 0.00081248 | 4.3217e-06 | 188
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | POLE | 3 | 9 | 3159 | 0.00056255 | 1.6027e-06 | 351
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 31 | 837 | 0.00014905 | 5.5205e-06 | 27
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 6 | 72 | 12149 | 0.0021635 | 1.2822e-05 | 168.7361
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | NONE | 18 | 631 | 32695 | 0.0058223 | 0.00011237 | 51.8146
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | FUSE | 1 | 103 | 2060 | 0.00036684 | 1.8342e-05 | 20
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | POLE HARDWARE | 2 | 22 | 4706 | 0.00083804 | 3.9178e-06 | 213.9091
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 3 | 6 | 1160 | 0.00020657 | 1.0685e-06 | 193.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 140 | 18620 | 0.0033158 | 2.4931e-05 | 133
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | CUTOUT | 1 | 4 | 396 | 7.052e-05 | 7.1232e-07 | 99
AEP Total | 2024 | 5615460 | PARTIAL POWER | V | CONDUCTOR UG | 2 | 6 | 901 | 0.00016045 | 1.0685e-06 | 150.1667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | SWITCH, UG | 1 | 2 | 250 | 4.5018e-05 | 3.6014e-07 | 125
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | SCO | SWITCH, OH | 3 | 1011 | 7077 | 0.0012603 | 0.00018004 | 7
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 5 | 38 | 6908 | 0.0012302 | 6.767e-06 | 181.7895
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 86 | 4872 | 0.0008676 | 1.5315e-05 | 56.6512
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 1 | 1 | 36 | 6.4109e-06 | 1.7808e-07 | 36
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 1 | 129 | 2.2972e-05 | 1.7808e-07 | 129
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 225 | 199309 | 0.035493 | 4.0068e-05 | 885.8178
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 68 | 1.2109e-05 | 1.7808e-07 | 68
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 794 | 222320 | 0.039591 | 0.0001414 | 280
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | POLE | 1 | 19 | 3135 | 0.00055828 | 3.3835e-06 | 165
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | REGULATOR | 1 | 51 | 3774 | 0.00067207 | 9.0821e-06 | 74
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | NETWORK PROTECTOR | 1 | 3 | 150 | 2.6712e-05 | 5.3424e-07 | 50
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | CROSSARM | 1 | 1 | 30 | 5.3424e-06 | 1.7808e-07 | 30
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | SPLICE, UG | 1 | 1 | 59 | 1.0507e-05 | 1.7808e-07 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 4 | 120 | 2.137e-05 | 7.1232e-07 | 30
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 1 | 150 | 2.6903e-05 | 1.7935e-07 | 150
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | SCO | OTHER EQUIPMENT | 2 | 1678 | 115782 | 0.021112 | 0.00030597 | 69
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 63 | 5670 | 0.0010339 | 1.1488e-05 | 90
AEP Total | 2023 | 5575683 | PARTIAL POWER | FW | PEDESTAL | 1 | 3 | 807 | 0.00014474 | 5.3805e-07 | 269
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 5 | 1135 | 0.00020696 | 9.1171e-07 | 227
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 74 | 1.3272e-05 | 1.7935e-07 | 74
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | METERING | 1 | 1 | 150 | 2.7351e-05 | 1.8234e-07 | 150
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SPLICE, OH | 20 | 21 | 2695 | 0.00048792 | 3.802e-06 | 128.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | METERING | 35 | 41 | 5188 | 0.00093927 | 7.4229e-06 | 126.5366
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | SWITCH, UG | 2 | 2 | 432 | 7.8212e-05 | 3.6209e-07 | 216
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 288 | 1934 | 212234 | 0.038424 | 0.00035014 | 109.7384
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | NONE | 61 | 145 | 25411 | 0.0046006 | 2.6252e-05 | 175.2483
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 1 | 155 | 2.8062e-05 | 1.8105e-07 | 155
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | RELAY | 20 | 7686 | 1117963 | 0.2024 | 0.0013915 | 145.4545
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | NONE | 61 | 8270 | 492434 | 0.089153 | 0.0014973 | 59.5446
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CROSSARM | 34 | 22257 | 2298097 | 0.41606 | 0.0040295 | 103.2528
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | POLE | 8 | 4314 | 576583 | 0.10439 | 0.00078103 | 133.6539
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | TOR | CONDUCTOR OVERHEAD | 1 | 1277 | 739383 | 0.13386 | 0.0002312 | 579
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 12 | 3396 | 0.00061483 | 2.1726e-06 | 283
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | JUMPER/RISER | 10 | 5264 | 508661 | 0.092091 | 0.00095303 | 96.6301
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | POLE HARDWARE | 2 | 216 | 33397 | 0.0060464 | 3.9106e-05 | 154.6157
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | METERING | 4 | 4 | 262 | 4.7434e-05 | 7.2419e-07 | 65.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CUTOUT | 22 | 380 | 90197 | 0.01633 | 6.8798e-05 | 237.3605
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | FUSE | 1 | 3 | 429 | 7.7669e-05 | 5.4314e-07 | 143
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | NONE | 171 | 943 | 114838 | 0.02094 | 0.00017195 | 121.7794
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | NONE | 3264 | 163181 | 12029056 | 2.1934 | 0.029755 | 73.716
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | NONE | 228 | 45087 | 4500446 | 0.82062 | 0.0082213 | 99.8169
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 363 | 2751 | 275061 | 0.050155 | 0.00050162 | 99.9858
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE | 510 | 113897 | 17473355 | 3.1861 | 0.020768 | 153.4137
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 47 | 169 | 55221 | 0.010069 | 3.0816e-05 | 326.7515
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | METERING | 27 | 37 | 2660 | 0.00048503 | 6.7467e-06 | 71.8919
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 244 | 390 | 96125 | 0.017528 | 7.1113e-05 | 246.4744
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | METERING | 24 | 93 | 5645 | 0.0010293 | 1.6958e-05 | 60.6989
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | NONE | 32 | 939 | 51994 | 0.0094807 | 0.00017122 | 55.3717
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 3 | 996 | 0.00018161 | 5.4703e-07 | 332
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | PEDESTAL | 5 | 540 | 44305 | 0.0080787 | 9.8465e-05 | 82.0463
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 22 | 4110 | 0.0007441 | 3.983e-06 | 186.8182
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 95 | 1.7199e-05 | 1.8105e-07 | 95
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CUTOUT | 2 | 11 | 2480 | 0.00045221 | 2.0058e-06 | 225.4545
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | BREAKER | 4 | 2858 | 661091 | 0.12054 | 0.00052113 | 231.3125
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 1448 | 0.00026403 | 1.8234e-07 | 1448
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | CONN/CLAMP | 1 | 986 | 122264 | 0.022294 | 0.00017979 | 124
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 18 | 3168 | 0.00057766 | 3.2822e-06 | 176
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | NONE | 3 | 31 | 13652 | 0.0024716 | 5.6124e-06 | 440.3871
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 17 | 2210 | 0.00040011 | 3.0778e-06 | 130
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 3 | 2424 | 267879 | 0.048499 | 0.00043886 | 110.5111
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | CUTOUT | 2 | 13 | 1726 | 0.00031249 | 2.3536e-06 | 132.7692
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | VA | CROSSARM | 3 | 2027 | 227024 | 0.041102 | 0.00036698 | 112
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 23 | 554 | 95386 | 0.017176 | 9.976e-05 | 172.1769
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 4 | 74 | 12225 | 0.0022014 | 1.3325e-05 | 165.2027
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 1 | 402 | 7.2389e-05 | 1.8007e-07 | 402
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 17 | 1200 | 303972 | 0.054737 | 0.00021609 | 253.31
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | POLE | 11 | 2680 | 162378 | 0.02924 | 0.00048259 | 60.5888
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE | 14 | 2557 | 856701 | 0.15427 | 0.00046044 | 335.0415
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CUTOUT | 7 | 319 | 78541 | 0.014143 | 5.7443e-05 | 246.21
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 1 | 13 | 2.3409e-06 | 1.8007e-07 | 13
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | REGULATOR | 14 | 6382 | 197131 | 0.035498 | 0.0011492 | 30.8886
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 5 | 15 | 4264 | 0.00076783 | 2.7011e-06 | 284.2667
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | NONE | 13 | 12982 | 1190850 | 0.21444 | 0.0023377 | 91.7309
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 3 | 25 | 2959 | 0.00053283 | 4.5018e-06 | 118.36
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | SPLICE, OH | 1 | 2 | 314 | 5.6543e-05 | 3.6014e-07 | 157
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 23 | 931 | 0.00016698 | 4.1251e-06 | 40.4783
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 7 | 2033 | 0.00036609 | 1.2605e-06 | 290.4286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 92 | 1.6567e-05 | 3.6014e-07 | 46
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 3 | 476 | 412714 | 0.07402 | 8.5371e-05 | 867.0462
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | ARRESTER | 1 | 19 | 1501 | 0.0002692 | 3.4077e-06 | 79
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | ARRESTER | 1 | 2 | 184 | 3.3e-05 | 3.587e-07 | 92
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 1 | 64 | 1.1525e-05 | 1.8007e-07 | 64
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | NONE | 13 | 53 | 11071 | 0.0019715 | 9.4382e-06 | 208.8868
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 70 | 1512 | 177558 | 0.031619 | 0.00026926 | 117.4325
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | FUSE | 32 | 85 | 8104 | 0.0014432 | 1.5137e-05 | 95.3412
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 10 | 970 | 0.00017274 | 1.7808e-06 | 97
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 129 | 26621 | 3204655 | 0.57068 | 0.0047407 | 120.3807
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | POLE | 7 | 3360 | 1102754 | 0.19638 | 0.00059835 | 328.2006
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 19 | 121 | 10724 | 0.0019097 | 2.1548e-05 | 88.6281
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 11 | 91 | 1365 | 0.00024308 | 1.6205e-05 | 15
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | NONE | 20 | 2893 | 721300 | 0.12845 | 0.00051518 | 249.326
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | ARRESTER | 6 | 6 | 178 | 3.1698e-05 | 1.0685e-06 | 29.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | NONE | 6 | 34 | 2204 | 0.00039529 | 6.0979e-06 | 64.8235
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | SPLICE, OH | 4 | 27 | 2078 | 0.00037269 | 4.8425e-06 | 76.963
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | POLE | 1 | 4 | 424 | 7.635e-05 | 7.2029e-07 | 106
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | REGULATOR | 1 | 1173 | 7038 | 0.0012742 | 0.00021237 | 6
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 4 | 2904 | 1883867 | 0.33923 | 0.00052293 | 648.7145
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | NONE | 451 | 8376 | 589030 | 0.10489 | 0.0014916 | 70.3235
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 92 | 10001 | 3042849 | 0.54187 | 0.001781 | 304.2545
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 10 | 2123 | 239117 | 0.042582 | 0.00037806 | 112.6317
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 44 | 53 | 8183 | 0.0014572 | 9.4382e-06 | 154.3962
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | NONE | 13 | 833 | 39159 | 0.0069734 | 0.00014834 | 47.0096
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE | 35 | 4010 | 1381464 | 0.24601 | 0.0007141 | 344.5047
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 41 | 13556 | 1799148 | 0.32039 | 0.002414 | 132.7197
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 9 | 3951 | 444986 | 0.079243 | 0.00070359 | 112.6262
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | INSULATOR | 2 | 969 | 115255 | 0.020754 | 0.00017449 | 118.9422
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 3 | 185 | 3.3313e-05 | 5.4022e-07 | 61.6667
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | NONE | 1 | 1 | 142 | 2.557e-05 | 1.8007e-07 | 142
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 99 | 1.7827e-05 | 1.8007e-07 | 99
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 4 | 889 | 359742 | 0.064779 | 0.00016008 | 404.6592
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | ARRESTER | 1 | 2 | 138 | 2.5163e-05 | 3.6468e-07 | 69
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | TRANSFORMER, UG | 1 | 1 | 396 | 7.1308e-05 | 1.8007e-07 | 396
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UB | NONE | 2 | 58 | 9353 | 0.0016842 | 1.0444e-05 | 161.2586
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 64 | 1.1478e-05 | 1.7935e-07 | 64
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | JUMPER/RISER | 3 | 2660 | 495041 | 0.088786 | 0.00047707 | 186.1056
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 1 | 1 | 354 | 6.3745e-05 | 1.8007e-07 | 354
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 18 | 1487 | 623313 | 0.11285 | 0.00026922 | 419.1748
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 5 | 21 | 889 | 0.00016095 | 3.802e-06 | 42.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 4 | 4 | 793 | 0.00014357 | 7.2419e-07 | 198.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 4 | 752 | 0.00013615 | 7.2419e-07 | 188
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 7 | 3423 | 577557 | 0.10456 | 0.00061972 | 168.7283
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | POLE | 7 | 1442 | 679412 | 0.12301 | 0.00026107 | 471.1595
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | METERING | 1 | 1 | 55 | 9.9576e-06 | 1.8105e-07 | 55
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | NONE | 7 | 19 | 1368 | 0.00024767 | 3.4399e-06 | 72
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 27 | 13893 | 0.0025153 | 4.8883e-06 | 514.5556
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CAPACITOR | 1 | 10 | 410 | 7.4229e-05 | 1.8105e-06 | 41
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 71 | 18350 | 0.0033222 | 1.2854e-05 | 258.4507
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CAPACITOR | 2 | 2442 | 271294 | 0.049117 | 0.00044212 | 111.095
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | GUY/ANCHOR | 1 | 1 | 93 | 1.6837e-05 | 1.8105e-07 | 93
AEP Total | 2021 | 5523447 | PARTIAL POWER | F | CONDUCTOR OVERHEAD | 1 | 1 | 88 | 1.5932e-05 | 1.8105e-07 | 88
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 750 | 3851 | 412806 | 0.074335 | 0.00069346 | 107.1945
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | METERING | 23 | 33 | 2858 | 0.00051465 | 5.9424e-06 | 86.6061
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE | 9 | 1272 | 197663 | 0.035594 | 0.00022905 | 155.3954
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 265 | 1246 | 188728 | 0.034413 | 0.0002272 | 151.4671
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2749 | 118817 | 28969148 | 5.2823 | 0.021665 | 243.8132
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | NONE | 129 | 932 | 111718 | 0.020371 | 0.00016994 | 119.8691
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | METERING | 35 | 45 | 6120 | 0.0011159 | 8.2054e-06 | 136
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | METERING | 52 | 319 | 26222 | 0.0047814 | 5.8167e-05 | 82.2006
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 13 | 323 | 46847 | 0.0085422 | 5.8896e-05 | 145.0372
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | NONE | 51 | 592 | 103009 | 0.018783 | 0.00010795 | 174.0017
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | POLE | 4 | 125 | 29985 | 0.0054675 | 2.2793e-05 | 239.88
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | NONE | 108 | 409 | 35596 | 0.0064906 | 7.4578e-05 | 87.0318
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | METERING | 2 | 12 | 942 | 0.00017177 | 2.1881e-06 | 78.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 9 | 156 | 8543 | 0.0015577 | 2.8445e-05 | 54.7628
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | NONE | 18 | 18399 | 1731838 | 0.31579 | 0.0033549 | 94.1267
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | ARRESTER | 19 | 16025 | 1821450 | 0.33213 | 0.002922 | 113.663
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | TRANSFORMER, UG | 1 | 1 | 697 | 0.00012709 | 1.8234e-07 | 697
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 863 | 25300 | 0.0046133 | 0.00015736 | 29.3163
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | ARRESTER | 9 | 33 | 7237 | 0.0013196 | 6.0173e-06 | 219.303
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | ARRESTER | 9 | 539 | 118186 | 0.02155 | 9.8282e-05 | 219.269
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | INSULATOR | 15 | 13564 | 1895281 | 0.34559 | 0.0024733 | 139.7288
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 9 | 657 | 0.0001198 | 1.6411e-06 | 73
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | REGULATOR | 3 | 2281 | 36561 | 0.0066666 | 0.00041592 | 16.0285
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 79 | 16128 | 0.0029408 | 1.4405e-05 | 204.1519
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 4 | 592 | 0.00010795 | 7.2937e-07 | 148
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 10 | 321 | 17781 | 0.0032422 | 5.8532e-05 | 55.3925
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | NONE | 291 | 12372 | 2062190 | 0.36985 | 0.0022189 | 166.682
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 4 | 102 | 13927 | 0.0024978 | 1.8294e-05 | 136.5392
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | NONE | 135 | 275 | 68425 | 0.012272 | 4.9321e-05 | 248.8182
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 238 | 615 | 96749 | 0.017352 | 0.0001103 | 157.3154
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CROSSARM | 71 | 25697 | 3626127 | 0.65035 | 0.0046088 | 141.1109
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | NONE | 11 | 63 | 10667 | 0.0019131 | 1.1299e-05 | 169.3175
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 43 | 2189 | 258282 | 0.046323 | 0.0003926 | 117.9909
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | ARRESTER | 14 | 2755 | 496798 | 0.089101 | 0.00049411 | 180.326
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CUTOUT | 5 | 2589 | 365052 | 0.065472 | 0.00046434 | 141.0012
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CUTOUT | 64 | 893 | 93355 | 0.016743 | 0.00016016 | 104.5409
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 21 | 1748 | 330399 | 0.058837 | 0.00031128 | 189.0154
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | NONE | 34 | 733 | 58242 | 0.010446 | 0.00013146 | 79.457
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | POLE | 3 | 2544 | 97574 | 0.0175 | 0.00045627 | 38.3546
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | ARRESTER | 1 | 1 | 218 | 3.9098e-05 | 1.7935e-07 | 218
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 3 | 20 | 1755 | 0.00031476 | 3.587e-06 | 87.75
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 4 | 20 | 2044 | 0.00036659 | 3.587e-06 | 102.2
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ERF | NONE | 9 | 7208 | 1123578 | 0.20151 | 0.0012928 | 155.8793
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | POLE | 2 | 7 | 104 | 1.8652e-05 | 1.2555e-06 | 14.8571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CUTOUT | 2 | 40 | 11620 | 0.002084 | 7.174e-06 | 290.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 244 | 69607 | 0.012484 | 4.3761e-05 | 285.2746
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 9 | 21 | 4835 | 0.00086102 | 3.7397e-06 | 230.2381
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 47 | 8.5092e-06 | 1.8105e-07 | 47
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | POLE | 1 | 12 | 9384 | 0.0017111 | 2.1881e-06 | 782
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 2 | 147 | 2.6804e-05 | 3.6468e-07 | 73.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | NONE | 2 | 2 | 178 | 3.2226e-05 | 3.6209e-07 | 89
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | NONE | 228 | 14283 | 3130315 | 0.55745 | 0.0025435 | 219.1637
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 52 | 339 | 55309 | 0.0098494 | 6.0369e-05 | 163.1534
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 118 | 1079 | 131972 | 0.023502 | 0.00019215 | 122.3095
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 25 | 38 | 4187 | 0.00074562 | 6.767e-06 | 110.1842
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | ARRESTER | 1 | 2 | 188 | 3.4037e-05 | 3.6209e-07 | 94
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 7 | 651 | 0.00011786 | 1.2673e-06 | 93
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONN/CLAMP | 4 | 4 | 413 | 7.437e-05 | 7.2029e-07 | 103.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 14 | 812 | 0.0001446 | 2.4931e-06 | 58
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 13 | 6559 | 507533 | 0.090381 | 0.001168 | 77.3796
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 5 | 17 | 4579 | 0.00081543 | 3.0274e-06 | 269.3529
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | ARRESTER | 5 | 23 | 2866 | 0.00051038 | 4.0958e-06 | 124.6087
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | NONE | 5 | 6 | 1140 | 0.00020301 | 1.0685e-06 | 190
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, GROUNDING | 4 | 5046 | 458813 | 0.083661 | 0.0009201 | 90.9261
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | CUTOUT | 1 | 7 | 140 | 2.521e-05 | 1.2605e-06 | 20
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | POLE | 2 | 119 | 19509 | 0.0034989 | 2.1343e-05 | 163.9412
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 338 | 71656 | 0.012903 | 6.0864e-05 | 212
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | NONE | 25 | 74 | 17875 | 0.0031832 | 1.3178e-05 | 241.5541
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 13 | 177 | 106328 | 0.018935 | 3.152e-05 | 600.7232
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 4 | 604 | 0.00010756 | 7.1232e-07 | 151
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 11 | 10643 | 1334414 | 0.23763 | 0.0018953 | 125.3795
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 8 | 2405 | 447451 | 0.079682 | 0.00042828 | 186.0503
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 589 | 267406 | 0.04762 | 0.00010489 | 454
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 1 | 112 | 1.9945e-05 | 1.7808e-07 | 112
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 2 | 66 | 5496 | 0.00097873 | 1.1753e-05 | 83.2727
AEP Total | 2024 | 5615460 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 7 | 3505 | 0.00062417 | 1.2466e-06 | 500.7143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 405 | 109404 | 0.019483 | 7.2122e-05 | 270.1333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 2 | 90 | 14270 | 0.0025412 | 1.6027e-05 | 158.5556
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 5 | 14500 | 0.0026006 | 8.9675e-07 | 2900
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CROSSARM | 1 | 56 | 2533 | 0.00045108 | 9.9725e-06 | 45.2321
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 14 | 692 | 0.00012323 | 2.4931e-06 | 49.4286
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | ARRESTER | 1 | 1 | 15 | 2.6712e-06 | 1.7808e-07 | 15
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | TRANSFORMER, STATION SERVICE | 2 | 1795 | 911855 | 0.1642 | 0.00032323 | 507.9972
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERO | CONDUCTOR UG | 1 | 4 | 536 | 9.6519e-05 | 7.2029e-07 | 134
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 5 | 995 | 0.00017719 | 8.904e-07 | 199
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE | 11 | 4431 | 1204189 | 0.21444 | 0.00078907 | 271.7646
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 2 | 9 | 9014 | 0.0016052 | 1.6027e-06 | 1001.5556
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 29 | 5220 | 0.00092958 | 5.1643e-06 | 180
AEP Total | 2025 | 5615460 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 27 | 4.8082e-06 | 1.7808e-07 | 27
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | SPLICE, OH | 2 | 2 | 213 | 3.7931e-05 | 3.5616e-07 | 106.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 2 | 1978 | 0.00035224 | 3.5616e-07 | 989
AEP Total | 2023 | 5575683 | PARTIAL POWER | UG | SPLICE, UG | 1 | 1 | 60 | 1.0761e-05 | 1.7935e-07 | 60
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | FUSE | 1 | 1 | 67 | 1.2016e-05 | 1.7935e-07 | 67
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 1 | 4 | 2560 | 0.00046098 | 7.2029e-07 | 640
AEP Total | 2021 | 5523447 | PARTIAL POWER | FW | CONN/CLAMP | 1 | 12 | 228 | 4.1279e-05 | 2.1726e-06 | 19
AEP Total | 2021 | 5523447 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 72 | 1.3035e-05 | 1.8105e-07 | 72
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | NONE | 2 | 15 | 4960 | 0.00090442 | 2.7351e-06 | 330.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CABLE TERMINATOR | 1 | 1 | 1374 | 0.00024643 | 1.7935e-07 | 1374
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | PEDESTAL | 1 | 14 | 1246 | 0.00022347 | 2.5109e-06 | 89
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | FUSE | 1 | 58 | 4176 | 0.00074897 | 1.0402e-05 | 72
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | SPLICE, UG | 1 | 1 | 399 | 7.2754e-05 | 1.8234e-07 | 399
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CAPACITOR | 1 | 4 | 784 | 0.00014296 | 7.2937e-07 | 196
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | O | NONE | 2 | 2289 | 319034 | 0.057219 | 0.00041053 | 139.377
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CABLE TERMINATOR | 1 | 1 | 156 | 2.7979e-05 | 1.7935e-07 | 156
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 4 | 1508 | 0.00026854 | 7.1232e-07 | 377
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CABLE TERMINATOR | 3 | 1933 | 202965 | 0.036548 | 0.00034808 | 105
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | ARRESTER | 1 | 2 | 150 | 2.7011e-05 | 3.6014e-07 | 75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | POLE | 4111 | 31918 | 4404847 | 0.79748 | 0.0057786 | 138.0051
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CUTOUT | 1432 | 10636 | 291379 | 0.052753 | 0.0019256 | 27.3955
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | METERING | 9 | 9 | 807 | 0.0001461 | 1.6294e-06 | 89.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONN/CLAMP | 32 | 270 | 43655 | 0.0079036 | 4.8883e-05 | 161.6852
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CUTOUT | 46 | 1663 | 137529 | 0.024899 | 0.00030108 | 82.6993
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 13 | 59 | 14329 | 0.0025942 | 1.0682e-05 | 242.8644
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | ARRESTER | 9 | 77 | 12866 | 0.0023293 | 1.3941e-05 | 167.0909
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 7 | 2232 | 317230 | 0.056895 | 0.00040031 | 142.1281
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | PEDESTAL | 4 | 19 | 1483 | 0.00026705 | 3.4214e-06 | 78.0526
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | POLE | 2 | 7 | 1289 | 0.00023118 | 1.2555e-06 | 184.1429
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 23 | 630 | 93211 | 0.016785 | 0.00011345 | 147.954
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | ARRESTER | 10 | 386 | 145917 | 0.026276 | 6.9508e-05 | 378.0233
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | BREAKER | 1 | 1 | 93 | 1.6747e-05 | 1.8007e-07 | 93
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | SCO | POLE | 2 | 22 | 3245 | 0.00058199 | 3.9457e-06 | 147.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | NONE | 2 | 3 | 653 | 0.00011712 | 5.3805e-07 | 217.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 21 | 2480 | 0.00044658 | 3.7815e-06 | 118.0952
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | PEDESTAL | 2 | 2 | 4187 | 0.00075396 | 3.6014e-07 | 2093.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | ARRESTER | 5 | 20 | 1831 | 0.00032971 | 3.6014e-06 | 91.55
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | NONE | 4 | 10 | 3092 | 0.00055678 | 1.8007e-06 | 309.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 12 | 2976 | 0.00053589 | 2.1609e-06 | 248
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 3 | 13 | 8279 | 0.0014908 | 2.3409e-06 | 636.8462
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | NONE | 4 | 22 | 503 | 9.0576e-05 | 3.9616e-06 | 22.8636
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | FUSE | 1 | 1 | 52 | 9.3637e-06 | 1.8007e-07 | 52
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 7 | 35 | 3980 | 0.00070876 | 6.2328e-06 | 113.7143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 23 | 310 | 44967 | 0.0080077 | 5.5205e-05 | 145.0548
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | NONE | 45 | 3255 | 113093 | 0.02014 | 0.00057965 | 34.7444
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | SCO | TRANSFORMER, POWER - NON LTC | 3 | 1014 | 167310 | 0.030007 | 0.00018186 | 165
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | NONE | 14 | 28 | 4981 | 0.00088702 | 4.9862e-06 | 177.8929
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | NONE | 3 | 40 | 4790 | 0.00085909 | 7.174e-06 | 119.75
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 3 | 4939 | 482757 | 0.087401 | 0.00089419 | 97.7439
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 227 | 69008 | 0.012583 | 4.1392e-05 | 304
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONN/CLAMP | 3 | 23 | 2001 | 0.00036487 | 4.1939e-06 | 87
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CUTOUT | 4 | 31 | 4720 | 0.00086065 | 5.6526e-06 | 152.2581
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 3 | 6 | 5418 | 0.00098793 | 1.0941e-06 | 903
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | METERING | 1 | 12 | 1536 | 0.00028008 | 2.1881e-06 | 128
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 2 | 760 | 0.0001376 | 3.6209e-07 | 380
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 25 | 2575 | 0.00046619 | 4.5262e-06 | 103
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR UG | 2 | 43 | 4838 | 0.00087119 | 7.7431e-06 | 112.5116
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 4 | 137 | 40375 | 0.0072704 | 2.467e-05 | 294.708
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 7 | 1255 | 0.00022599 | 1.2605e-06 | 179.2857
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 10 | 940 | 0.00017018 | 1.8105e-06 | 94
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | NONE | 32 | 2693 | 160065 | 0.028504 | 0.00047957 | 59.4374
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 95 | 3697 | 1395504 | 0.24851 | 0.00065836 | 377.4693
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 28 | 7899 | 1259719 | 0.22433 | 0.0014067 | 159.4783
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | VA | POLE | 1 | 9 | 5112 | 0.00091034 | 1.6027e-06 | 568
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 4 | 2612 | 130044 | 0.023158 | 0.00046514 | 49.7871
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | AF | NONE | 3 | 297 | 43092 | 0.0076738 | 5.289e-05 | 145.0909
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 1 | 162 | 2.9539e-05 | 1.8234e-07 | 162
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | INSULATOR | 1 | 1 | 534 | 9.6158e-05 | 1.8007e-07 | 534
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 2542 | 91512 | 0.016479 | 0.00045774 | 36
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | SCO | ARRESTER | 1 | 10 | 170 | 3.049e-05 | 1.7935e-06 | 17
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 2 | 1768 | 0.00032238 | 3.6468e-07 | 884
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 18 | 3078 | 0.00056125 | 3.2822e-06 | 171
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 2 | 16 | 2.8696e-06 | 3.587e-07 | 8
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | CUTOUT | 1 | 602 | 101738 | 0.01832 | 0.0001084 | 169
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | OTHER EQUIPMENT | 1 | 3 | 285 | 5.1598e-05 | 5.4314e-07 | 95
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | NONE | 1 | 1 | 103 | 1.8547e-05 | 1.8007e-07 | 103
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CROSSARM | 2 | 164 | 14113 | 0.0025312 | 2.9413e-05 | 86.0549
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | VA | POLE | 1 | 896 | 90496 | 0.01623 | 0.0001607 | 101
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 8 | 31 | 5926 | 0.0010553 | 5.5205e-06 | 191.1613
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 3 | 421 | 98812 | 0.017596 | 7.4972e-05 | 234.7078
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 49 | 2009 | 0.00036031 | 8.7882e-06 | 41
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | NONE | 7 | 13 | 952 | 0.00016953 | 2.315e-06 | 73.2308
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | FUSE | 2 | 49 | 5509 | 0.00098804 | 8.7882e-06 | 112.4286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CUTOUT | 2 | 1496 | 23936 | 0.0043102 | 0.00026939 | 16
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | TRANSFORMER, POWER - NON LTC | 1 | 41 | 13419 | 0.0024164 | 7.3829e-06 | 327.2927
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | CROSSARM | 2 | 72 | 2400 | 0.00043217 | 1.2965e-05 | 33.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | PEDESTAL | 1 | 4 | 836 | 0.00015135 | 7.2419e-07 | 209
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 601 | 328350 | 0.059447 | 0.00010881 | 546.3394
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | TRANSFORMER, GROUNDING | 1 | 316 | 15800 | 0.0028451 | 5.6903e-05 | 50
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | INSULATOR | 1 | 3 | 717 | 0.00012981 | 5.4314e-07 | 239
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 900 | 81999 | 0.014846 | 0.00016294 | 91.11
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 153 | 77509 | 0.014033 | 2.77e-05 | 506.5948
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | SWITCH, UG | 1 | 342 | 77648 | 0.014058 | 6.1918e-05 | 227.0409
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | POLE | 1 | 2 | 524 | 9.4868e-05 | 3.6209e-07 | 262
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | SWITCH, OH | 2 | 22 | 5483 | 0.00099268 | 3.983e-06 | 249.2273
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CUTOUT | 1700 | 61724 | 6725346 | 1.211 | 0.011115 | 108.9584
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | NONE | 2928 | 156438 | 14531546 | 2.6167 | 0.02817 | 92.8901
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 826 | 6805 | 1661008 | 0.2991 | 0.0012254 | 244.0864
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | FUSE | 129 | 1165 | 138482 | 0.024937 | 0.00020978 | 118.8687
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, OH | 39 | 3495 | 482098 | 0.086812 | 0.00062935 | 137.9393
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | REGULATOR | 12 | 18367 | 981966 | 0.17682 | 0.0033074 | 53.4636
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | NONE | 7 | 7190 | 778231 | 0.14014 | 0.0012947 | 108.238
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE | 7 | 155 | 110797 | 0.019951 | 2.7911e-05 | 714.8194
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | FUSE | 5 | 749 | 44987 | 0.0081009 | 0.00013487 | 60.0628
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 10 | 44 | 6308 | 0.0011359 | 7.9232e-06 | 143.3636
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | NONE | 10 | 32 | 3867 | 0.00069634 | 5.7623e-06 | 120.8438
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 93 | 6384 | 773175 | 0.13867 | 0.001145 | 121.1114
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 103 | 19434 | 2441629 | 0.43791 | 0.0034855 | 125.637
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | NONE | 3754 | 65599 | 4856093 | 0.87094 | 0.011765 | 74.0269
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | FUSE | 3 | 14 | 1450 | 0.0002611 | 2.521e-06 | 103.5714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | OTHER EQUIPMENT | 1 | 4 | 1492 | 0.00026867 | 7.2029e-07 | 373
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | NONE | 54 | 8550 | 615406 | 0.11037 | 0.0015334 | 71.9773
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | INSULATOR | 2 | 165 | 5608 | 0.0010226 | 3.0086e-05 | 33.9879
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | SCO | NONE | 16 | 9994 | 804183 | 0.14664 | 0.0018223 | 80.4666
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | FUSE | 1 | 1 | 143 | 2.6075e-05 | 1.8234e-07 | 143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | NONE | 5 | 1281 | 11637 | 0.0021219 | 0.00023358 | 9.0843
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 10 | 1026 | 71224 | 0.012774 | 0.00018401 | 69.4191
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 13 | 3874 | 0.0006948 | 2.3316e-06 | 298
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | GUY/ANCHOR | 3 | 51 | 5764 | 0.0010338 | 9.1469e-06 | 113.0196
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | METERING | 17 | 24 | 1892 | 0.00033933 | 4.3044e-06 | 78.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | SPLICE, OH | 1 | 794 | 135774 | 0.024351 | 0.0001424 | 171
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CUTOUT | 2 | 3 | 312 | 5.5957e-05 | 5.3805e-07 | 104
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CUTOUT | 2 | 3 | 204 | 3.6587e-05 | 5.3805e-07 | 68
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 26 | 709 | 448701 | 0.080475 | 0.00012716 | 632.8646
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | FUSE | 1 | 3 | 558 | 9.9369e-05 | 5.3424e-07 | 186
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 7 | 43 | 2924 | 0.00052071 | 7.6574e-06 | 68
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | FUSE | 4 | 71 | 13809 | 0.0024591 | 1.2644e-05 | 194.493
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 110 | 19111 | 0.0034033 | 1.9589e-05 | 173.7364
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 12 | 2713 | 0.00048313 | 2.137e-06 | 226.0833
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 8 | 134 | 29865 | 0.0053184 | 2.3863e-05 | 222.8731
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CUTOUT | 1 | 3 | 576 | 0.00010257 | 5.3424e-07 | 192
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | POLE | 5 | 318 | 39778 | 0.0070837 | 5.6629e-05 | 125.0881
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 4 | 102 | 1.8164e-05 | 7.1232e-07 | 25.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 455 | 2730 | 0.00048616 | 8.1026e-05 | 6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 3 | 2459 | 199483 | 0.035524 | 0.0004379 | 81.1236
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 67 | 1.2065e-05 | 1.8007e-07 | 67
AEP Total | 2023 | 5575683 | PARTIAL POWER | AF | CONN/CLAMP | 1 | 1 | 79 | 1.4169e-05 | 1.7935e-07 | 79
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 1 | 2 | 150 | 2.6903e-05 | 3.587e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | SWITCH, OH | 2 | 3970 | 369210 | 0.066484 | 0.00071489 | 93
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | POLE | 3 | 788 | 16460 | 0.0029312 | 0.00014033 | 20.8883
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 136 | 2.4219e-05 | 3.5616e-07 | 68
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | NONE | 40 | 2645 | 503948 | 0.089743 | 0.00047102 | 190.5285
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AF | INSULATOR | 1 | 6 | 1170 | 0.00020835 | 1.0685e-06 | 195
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 4 | 8 | 529 | 9.4204e-05 | 1.4246e-06 | 66.125
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 1 | 321 | 5.7571e-05 | 1.7935e-07 | 321
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | BE | NONE | 1 | 2 | 108 | 1.9233e-05 | 3.5616e-07 | 54
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 103 | 5974 | 0.0010638 | 1.8342e-05 | 58
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 5 | 610 | 0.00010984 | 9.0036e-07 | 122
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 1 | 3 | 843 | 0.0001518 | 5.4022e-07 | 281
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 16 | 1731 | 851731 | 0.15168 | 0.00030826 | 492.0456
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 805 | 0.00014335 | 3.5616e-07 | 402.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | INSULATOR | 1 | 32 | 8576 | 0.0015272 | 5.6986e-06 | 268
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 190 | 126347 | 0.02266 | 3.4077e-05 | 664.9842
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | FUSE | 2 | 2 | 877 | 0.00015729 | 3.587e-07 | 438.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 65 | 1.1705e-05 | 1.8007e-07 | 65
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | TRANSFORMER, UG | 1 | 5 | 375 | 6.8378e-05 | 9.1171e-07 | 75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | REGULATOR | 1 | 412 | 16068 | 0.0028818 | 7.3892e-05 | 39
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 83 | 3735 | 0.00068105 | 1.5134e-05 | 45
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | JUMPER/RISER | 1 | 235 | 10105 | 0.0018295 | 4.2546e-05 | 43
AEP Total | 2022 | 5553337 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 68 | 1.2245e-05 | 1.8007e-07 | 68
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR UG | 584 | 1283 | 316537 | 0.057308 | 0.00023228 | 246.7163
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | OTHER EQUIPMENT | 1 | 26 | 20748 | 0.0037563 | 4.7072e-06 | 798
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 51 | 2093 | 291683 | 0.052808 | 0.00037893 | 139.3612
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 11 | 307 | 78662 | 0.014241 | 5.5581e-05 | 256.228
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | INSULATOR | 10 | 791 | 116349 | 0.021065 | 0.00014321 | 147.091
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 24 | 9271 | 465896 | 0.084349 | 0.0016785 | 50.253
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | NONE | 6 | 6554 | 834586 | 0.1511 | 0.0011866 | 127.3399
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 4 | 104 | 1.8829e-05 | 7.2419e-07 | 26
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | NONE | 30 | 3137 | 227435 | 0.041176 | 0.00056794 | 72.5008
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 14 | 231 | 15264 | 0.0027635 | 4.1822e-05 | 66.0779
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | FUSE | 11 | 111 | 15550 | 0.0028153 | 2.0096e-05 | 140.0901
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | FUSE | 2 | 3 | 285 | 5.1598e-05 | 5.4314e-07 | 95
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | SWITCH, OH | 6 | 4067 | 867649 | 0.15708 | 0.00073632 | 213.3388
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | NONE | 3419 | 63278 | 4428570 | 0.80751 | 0.011538 | 69.9859
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | INSULATOR | 173 | 49328 | 5861912 | 1.0689 | 0.0089946 | 118.8354
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 58 | 9971 | 0.0018181 | 1.0576e-05 | 171.9138
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 145 | 14135 | 1806335 | 0.32937 | 0.0025774 | 127.7917
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE | 206 | 18825 | 5745755 | 1.0477 | 0.0034326 | 305.2194
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 4 | 1256 | 0.00022902 | 7.2937e-07 | 314
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 6 | 1430 | 0.00026075 | 1.0941e-06 | 238.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 15 | 3464 | 900823 | 0.16426 | 0.00063163 | 260.0528
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 3 | 10 | 2259 | 0.00041191 | 1.8234e-06 | 225.9
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 8 | 84 | 35495 | 0.0063209 | 1.4959e-05 | 422.5595
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CUTOUT | 315 | 13010 | 205717 | 0.036634 | 0.0023168 | 15.8122
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR UG | 2 | 2 | 489 | 8.8532e-05 | 3.6209e-07 | 244.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 93 | 1.6958e-05 | 1.8234e-07 | 93
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 3 | 4680 | 767730 | 0.13999 | 0.00085336 | 164.0449
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | NONE | 2 | 9 | 889 | 0.0001621 | 1.6411e-06 | 98.7778
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 8 | 8131 | 1130944 | 0.20622 | 0.0014826 | 139.0904
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 3 | 63 | 1.1299e-05 | 5.3805e-07 | 21
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 4 | 256 | 4.5588e-05 | 7.1232e-07 | 64
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 251 | 20971 | 10138167 | 1.8054 | 0.0037345 | 483.4375
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 202 | 3298 | 406387 | 0.072369 | 0.00058731 | 123.2223
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 36 | 1495 | 493310 | 0.087849 | 0.00026623 | 329.9732
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | NONE | 63 | 1189 | 77290 | 0.013764 | 0.00021174 | 65.0042
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 85 | 13216 | 685510 | 0.12208 | 0.0023535 | 51.8697
AEP Total | 2023 | 5575683 | PARTIAL POWER | SCO | CONDUCTOR UG | 1 | 8 | 560 | 0.00010044 | 1.4348e-06 | 70
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | METERING | 2 | 2 | 218 | 3.9098e-05 | 3.587e-07 | 109
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | METERING | 18 | 28 | 5592 | 0.00099582 | 4.9862e-06 | 199.7143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 8 | 63 | 5867 | 0.0010448 | 1.1219e-05 | 93.127
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | FUSE | 2 | 2 | 104 | 1.8652e-05 | 3.587e-07 | 52
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 17 | 11905 | 801103 | 0.14266 | 0.00212 | 67.2913
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | POLE | 1 | 12 | 16848 | 0.0030003 | 2.137e-06 | 1404
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 7 | 462 | 8.286e-05 | 1.2555e-06 | 66
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 4 | 29 | 3303 | 0.0005882 | 5.1643e-06 | 113.8966
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 36 | 218 | 36602 | 0.0065181 | 3.8821e-05 | 167.8991
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | FUSE | 4 | 9 | 819 | 0.00014585 | 1.6027e-06 | 91
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | CONDUCTOR UG | 1 | 2 | 1130 | 0.00020267 | 3.587e-07 | 565
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ERF | INSULATOR | 2 | 201 | 42161 | 0.0076331 | 3.639e-05 | 209.7562
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | SPLICE, UG | 1 | 1 | 463 | 8.4424e-05 | 1.8234e-07 | 463
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 2 | 194 | 3.5374e-05 | 3.6468e-07 | 97
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | ARRESTER | 2 | 3 | 363 | 6.5366e-05 | 5.4022e-07 | 121
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 32 | 3488 | 0.00062809 | 5.7623e-06 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 7 | 1064 | 0.00019401 | 1.2764e-06 | 152
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 86 | 8256 | 0.0015054 | 1.5681e-05 | 96
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | V | TRANSFORMER, POWER - NON LTC | 2 | 1748 | 176216 | 0.031732 | 0.00031477 | 100.8101
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 98 | 1.787e-05 | 1.8234e-07 | 98
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 382 | 27270 | 0.0049725 | 6.9655e-05 | 71.3874
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONN/CLAMP | 5 | 8 | 990 | 0.00017924 | 1.4484e-06 | 123.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 280 | 29446 | 0.0053311 | 5.0693e-05 | 105.1643
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | ARRESTER | 41 | 3538 | 281385 | 0.051308 | 0.00064513 | 79.5322
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 51 | 1249 | 284452 | 0.051868 | 0.00022775 | 227.7438
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 27 | 2390 | 274140 | 0.049987 | 0.0004358 | 114.7029
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CUTOUT | 42 | 400 | 30753 | 0.0056076 | 7.2937e-05 | 76.8825
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 129 | 2.3522e-05 | 3.6468e-07 | 64.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 12 | 2364 | 286109 | 0.05217 | 0.00043106 | 121.0275
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | NONE | 10 | 86 | 3007 | 0.0005483 | 1.5681e-05 | 34.9651
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | NONE | 11 | 52 | 1853 | 0.00033788 | 9.4818e-06 | 35.6346
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 4 | 4 | 295 | 5.3791e-05 | 7.2937e-07 | 73.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 4 | 240 | 19608 | 0.0035754 | 4.3762e-05 | 81.7
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CROSSARM | 1 | 211 | 14457 | 0.0026361 | 3.8474e-05 | 68.5166
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 2 | 3 | 1444 | 0.0002633 | 5.4703e-07 | 481.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | ARRESTER | 13 | 1400 | 116508 | 0.021244 | 0.00025528 | 83.22
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | NONE | 5 | 84 | 10761 | 0.0019622 | 1.5317e-05 | 128.1071
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 4 | 349 | 6.3637e-05 | 7.2937e-07 | 87.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 2 | 22 | 275 | 5.0144e-05 | 4.0115e-06 | 12.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 4 | 3972 | 0.00072426 | 7.2937e-07 | 993
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 3 | 611 | 0.00011141 | 5.4703e-07 | 203.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 410 | 2054 | 214990 | 0.038559 | 0.00036839 | 104.6689
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | FUSE | 57 | 1556 | 384036 | 0.069154 | 0.00028019 | 246.8098
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE | 187 | 18720 | 6857647 | 1.2349 | 0.0033709 | 366.3273
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 7 | 1591 | 0.00028649 | 1.2605e-06 | 227.2857
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 11 | 1582 | 401995 | 0.072388 | 0.00028487 | 254.1056
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 15 | 318 | 74807 | 0.013471 | 5.7263e-05 | 235.2421
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | NONE | 10 | 21 | 7517 | 0.0013536 | 3.7815e-06 | 357.9524
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | ARRESTER | 86 | 281 | 6462 | 0.0011636 | 5.06e-05 | 22.9964
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CUTOUT | 831 | 6887 | 322080 | 0.057765 | 0.0012352 | 46.7664
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 161 | 4724 | 1491624 | 0.26752 | 0.00084725 | 315.7544
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 7 | 52 | 18563 | 0.0033427 | 9.3637e-06 | 356.9808
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 12 | 3709 | 0.00066521 | 2.1522e-06 | 309.0833
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CROSSARM | 1 | 64 | 3904 | 0.000703 | 1.1525e-05 | 61
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | JUMPER/RISER | 7 | 9 | 1305 | 0.00023405 | 1.6142e-06 | 145
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONN/CLAMP | 3 | 3 | 210 | 3.7815e-05 | 5.4022e-07 | 70
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SO | NONE | 6 | 65 | 1838 | 0.00033097 | 1.1705e-05 | 28.2769
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONN/CLAMP | 41 | 633 | 72969 | 0.013087 | 0.00011353 | 115.2749
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 11 | 43 | 4387 | 0.00078681 | 7.7121e-06 | 102.0233
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 12 | 1329 | 86047 | 0.015433 | 0.00023836 | 64.7457
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | CUTOUT | 3 | 86 | 9542 | 0.0017114 | 1.5424e-05 | 110.9535
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | NONE | 9 | 563 | 122849 | 0.022033 | 0.00010097 | 218.2043
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CUTOUT | 1 | 1 | 192 | 3.4435e-05 | 1.7935e-07 | 192
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | FUSE | 21 | 53 | 10887 | 0.0019526 | 9.5056e-06 | 205.4151
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 6 | 59 | 13687 | 0.0024646 | 1.0624e-05 | 231.9831
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 165 | 34299 | 0.0061515 | 2.9593e-05 | 207.8727
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | INSULATOR | 4 | 2778 | 258519 | 0.046365 | 0.00049823 | 93.0594
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | POLE | 3602 | 24533 | 3050880 | 0.5433 | 0.0043688 | 124.3582
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | NONE | 3212 | 116095 | 11385509 | 2.0275 | 0.020674 | 98.0706
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | FUSE | 14 | 666 | 12478 | 0.0022221 | 0.0001186 | 18.7357
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | SPLICE, OH | 13 | 37 | 6527 | 0.0011706 | 6.636e-06 | 176.4054
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | NONE | 4 | 23 | 1288 | 0.000231 | 4.1251e-06 | 56
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | SECTIONALIZER | 2 | 23 | 345 | 6.1876e-05 | 4.1251e-06 | 15
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, UG | 4 | 5 | 958 | 0.00017182 | 8.9675e-07 | 191.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | BREAKER | 1 | 1 | 469 | 8.4115e-05 | 1.7935e-07 | 469
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CROSSARM | 4 | 4160 | 1717649 | 0.30806 | 0.0007461 | 412.8964
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | INSULATOR | 7 | 8028 | 1643758 | 0.29481 | 0.0014398 | 204.7531
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 2 | 392 | 7.0305e-05 | 3.587e-07 | 196
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | POLE | 2 | 29 | 8704 | 0.0015611 | 5.2012e-06 | 300.1379
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | BREAKER | 1 | 6 | 1872 | 0.00033574 | 1.0761e-06 | 312
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WL | INSULATOR | 1 | 1558 | 267976 | 0.048062 | 0.00027943 | 172
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 44 | 6424 | 0.001144 | 7.8355e-06 | 146
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | TRANSFORMER, UG | 1 | 4 | 1432 | 0.00025683 | 7.174e-07 | 358
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | NONE | 3 | 1441 | 141218 | 0.02575 | 0.00026275 | 98
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 2 | 329 | 5.9991e-05 | 3.6468e-07 | 164.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | PEDESTAL | 1 | 1 | 104 | 1.852e-05 | 1.7808e-07 | 104
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 11 | 1485 | 0.00026741 | 1.9808e-06 | 135
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | METERING | 7 | 8 | 825 | 0.00014692 | 1.4246e-06 | 103.125
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 64 | 6336 | 0.0011283 | 1.1397e-05 | 99
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 3 | 6 | 679 | 0.00012092 | 1.0685e-06 | 113.1667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 2 | 5 | 4334 | 0.0007718 | 8.904e-07 | 866.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SWITCH, UG | 1 | 1355 | 860719 | 0.15328 | 0.0002413 | 635.217
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 66 | 6996 | 0.0012458 | 1.1753e-05 | 106
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CUTOUT | 2 | 73 | 20005 | 0.0035625 | 1.3e-05 | 274.0411
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 108 | 1.9233e-05 | 1.7808e-07 | 108
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | NONE | 1 | 1104 | 141312 | 0.025165 | 0.0001966 | 128
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | NONE | 1 | 21 | 5103 | 0.00093049 | 3.8292e-06 | 243
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 1074 | 82698 | 0.015079 | 0.00019584 | 77
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WI | NONE | 2 | 506 | 149008 | 0.026832 | 9.1116e-05 | 294.4822
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | SPLICE, OH | 1 | 314 | 28260 | 0.0050888 | 5.6543e-05 | 90
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 1667 | 17460 | 1744953 | 0.31592 | 0.0031611 | 99.94
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | NONE | 178 | 6111 | 461614 | 0.083574 | 0.0011064 | 75.5382
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE | 606 | 156162 | 25879704 | 4.6854 | 0.028273 | 165.7234
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 677 | 14125 | 1392144 | 0.25204 | 0.0025573 | 98.5589
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | NONE | 368 | 23931 | 3511374 | 0.63572 | 0.0043326 | 146.7291
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE | 237 | 18740 | 6045243 | 1.0945 | 0.0033928 | 322.585
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 24 | 726 | 120578 | 0.02183 | 0.00013144 | 166.0854
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 6 | 5139 | 203183 | 0.036786 | 0.0009304 | 39.5375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONN/CLAMP | 4 | 41 | 5670 | 0.0010265 | 7.4229e-06 | 138.2927
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 18 | 787 | 88489 | 0.016021 | 0.00014248 | 112.4384
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 1 | 1 | 30 | 5.4314e-06 | 1.8105e-07 | 30
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONDUCTOR UG | 3 | 7 | 1131 | 0.00020476 | 1.2673e-06 | 161.5714
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 53 | 6254 | 0.0011137 | 9.4382e-06 | 118
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 4 | 896 | 0.00016222 | 7.2419e-07 | 224
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 2 | 2186 | 0.00039577 | 3.6209e-07 | 1093
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | POLE | 4 | 443 | 51753 | 0.0093193 | 7.9772e-05 | 116.8239
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 3 | 1113 | 120923 | 0.021775 | 0.00020042 | 108.646
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 2438 | 241220 | 0.043437 | 0.00043902 | 98.9418
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, GROUNDING | 1 | 27 | 1026 | 0.00018475 | 4.8619e-06 | 38
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CONDUCTOR UG | 1 | 1 | 225 | 4.1027e-05 | 1.8234e-07 | 225
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 18 | 1162 | 0.0002084 | 3.2283e-06 | 64.5556
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 16 | 5131 | 0.00092025 | 2.8696e-06 | 320.6875
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 4 | 12 | 392 | 6.9807e-05 | 2.137e-06 | 32.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 49 | 3973 | 0.00070751 | 8.7259e-06 | 81.0816
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | POLE | 1 | 7 | 2856 | 0.0005086 | 1.2466e-06 | 408
AEP Total | 2024 | 5615460 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 92 | 1.6383e-05 | 1.7808e-07 | 92
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 10 | 160 | 57187 | 0.010184 | 2.8493e-05 | 357.4187
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AB | INSULATOR | 9 | 14704 | 967314 | 0.17226 | 0.0026185 | 65.7858
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 2 | 2 | 1377 | 0.00024522 | 3.5616e-07 | 688.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CAPACITOR | 1 | 741 | 54834 | 0.0097648 | 0.00013196 | 74
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 1 | 290 | 5.1643e-05 | 1.7808e-07 | 290
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 241 | 36391 | 0.0064805 | 4.2917e-05 | 151
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 1 | 120 | 2.1609e-05 | 1.8007e-07 | 120
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 1 | 59 | 1.0624e-05 | 1.8007e-07 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | NONE | 11 | 1288 | 119587 | 0.021296 | 0.00022937 | 92.847
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CROSSARM | 1 | 300 | 19500 | 0.0034726 | 5.3424e-05 | 65
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 7 | 938 | 0.00016704 | 1.2466e-06 | 134
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CUTOUT | 1 | 1 | 224 | 3.989e-05 | 1.7808e-07 | 224
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | METERING | 1 | 1271 | 234676 | 0.041791 | 0.00022634 | 184.6389
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 23 | 40 | 6077 | 0.0011002 | 7.2419e-06 | 151.925
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CUTOUT | 3 | 36 | 3284 | 0.00059456 | 6.5177e-06 | 91.2222
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | JUMPER/RISER | 1 | 2 | 1052 | 0.00019046 | 3.6209e-07 | 526
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | POLE | 1 | 1 | 103 | 1.8648e-05 | 1.8105e-07 | 103
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | ARRESTER | 1 | 2 | 436 | 7.8936e-05 | 3.6209e-07 | 218
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | METERING | 3 | 7 | 489 | 8.8532e-05 | 1.2673e-06 | 69.8571
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CUTOUT | 10 | 1309 | 101811 | 0.018433 | 0.00023699 | 77.7777
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 4 | 937 | 0.00016964 | 7.2419e-07 | 234.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 448 | 28672 | 0.005191 | 8.1109e-05 | 64
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 11 | 605 | 0.00010953 | 1.9915e-06 | 55
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 2 | 74 | 1.3272e-05 | 3.587e-07 | 37
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | POLE | 2 | 179 | 49985 | 0.0089648 | 3.2104e-05 | 279.2458
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 37 | 1464 | 539106 | 0.096004 | 0.00026071 | 368.2418
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | FUSE | 14 | 51 | 3963 | 0.00070573 | 9.0821e-06 | 77.7059
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 47 | 7157 | 1165939 | 0.20763 | 0.0012745 | 162.9089
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 7 | 119 | 13577 | 0.0024178 | 2.1191e-05 | 114.0924
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 40 | 1045 | 448115 | 0.080693 | 0.00018818 | 428.8182
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 2 | 258 | 4.671e-05 | 3.6209e-07 | 129
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 16 | 212 | 108190 | 0.019266 | 3.7753e-05 | 510.3302
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 2 | 508 | 95780 | 0.017056 | 9.0465e-05 | 188.5433
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONN/CLAMP | 1 | 1 | 88 | 1.5932e-05 | 1.8105e-07 | 88
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | POLE HARDWARE | 1 | 101 | 29492 | 0.0053107 | 1.8187e-05 | 292
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 8 | 3610 | 0.00064287 | 1.4246e-06 | 451.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 4 | 79 | 20337 | 0.0036216 | 1.4068e-05 | 257.4304
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 237 | 780 | 120581 | 0.021473 | 0.0001389 | 154.591
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 3405 | 156302 | 32957009 | 5.869 | 0.027834 | 210.8547
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | NONE | 122 | 244 | 46665 | 0.0083101 | 4.3451e-05 | 191.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1691 | 67109 | 19714920 | 3.5108 | 0.011951 | 293.7746
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 186 | 354 | 65284 | 0.011626 | 6.304e-05 | 184.4181
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 16 | 493 | 318430 | 0.056706 | 8.7793e-05 | 645.9026
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 61 | 5700 | 1786054 | 0.31806 | 0.0010151 | 313.3428
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 777 | 34960 | 5542727 | 0.98705 | 0.0062257 | 158.5448
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CROSSARM | 136 | 4916 | 304340 | 0.054197 | 0.00087544 | 61.9081
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CROSSARM | 3 | 3729 | 688520 | 0.12261 | 0.00066406 | 184.6393
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | SPLICE, OH | 2 | 2 | 1216 | 0.00021655 | 3.5616e-07 | 608
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SECTIONALIZER | 1 | 103 | 145745 | 0.025954 | 1.8342e-05 | 1415
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CUTOUT | 9 | 45 | 46764 | 0.0083871 | 8.0708e-06 | 1039.2
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 4 | 16 | 2679 | 0.00048048 | 2.8696e-06 | 167.4375
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 1 | 10 | 1.7935e-06 | 1.7935e-07 | 10
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 1 | 121 | 2.1701e-05 | 1.7935e-07 | 121
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | POLE | 6 | 38 | 18673 | 0.003349 | 6.8153e-06 | 491.3947
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 4 | 634 | 0.00011371 | 7.174e-07 | 158.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 2 | 216 | 3.9106e-05 | 3.6209e-07 | 108
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 151 | 44092 | 0.0080398 | 2.7534e-05 | 292
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 1 | 731 | 0.00013329 | 1.8234e-07 | 731
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | METERING | 1 | 1 | 192 | 3.501e-05 | 1.8234e-07 | 192
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | SPLICE, UG | 4 | 31 | 6512 | 0.0011597 | 5.5205e-06 | 210.0645
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 21 | 90 | 13371 | 0.0023811 | 1.6027e-05 | 148.5667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 4 | 1151 | 154747 | 0.027557 | 0.00020497 | 134.4457
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 29 | 10306 | 0.0018484 | 5.2012e-06 | 355.3793
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | CONN/CLAMP | 7 | 20 | 5822 | 0.0010368 | 3.5616e-06 | 291.1
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | NONE | 28 | 969 | 92950 | 0.016553 | 0.00017256 | 95.9236
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 14 | 255 | 56536 | 0.010068 | 4.541e-05 | 221.7098
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | REGULATOR | 1 | 412 | 4120 | 0.00073892 | 7.3892e-05 | 10
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, GROUNDING | 1 | 9 | 63 | 1.1299e-05 | 1.6142e-06 | 7
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CIRCUIT SWITCHER | 1 | 4 | 512 | 9.1827e-05 | 7.174e-07 | 128
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 2 | 182 | 3.2642e-05 | 3.587e-07 | 91
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 3 | 3712 | 1028410 | 0.18314 | 0.00066103 | 277.0501
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 4 | 48 | 10305 | 0.0018351 | 8.5478e-06 | 214.6875
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 6 | 1510 | 0.00027191 | 1.0804e-06 | 251.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 55 | 6197 | 766883 | 0.13657 | 0.0011036 | 123.7507
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 2 | 149 | 2.6534e-05 | 3.5616e-07 | 74.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 32 | 1829 | 295216 | 0.052572 | 0.00032571 | 161.4084
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 4 | 106 | 14214 | 0.0025312 | 1.8876e-05 | 134.0943
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 95 | 11115 | 0.0020015 | 1.7107e-05 | 117
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CROSSARM | 1 | 2 | 80 | 1.4406e-05 | 3.6014e-07 | 40
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | SWITCH, OH | 3 | 3581 | 96785 | 0.017428 | 0.00064484 | 27.0274
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABX | INSULATOR | 1 | 901 | 153170 | 0.027276 | 0.00016045 | 170
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CABLE TERMINATOR | 2 | 164 | 18345 | 0.0032669 | 2.9205e-05 | 111.8598
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | POLE | 6 | 150 | 47972 | 0.0085428 | 2.6712e-05 | 319.8133
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 9 | 647 | 94702 | 0.016865 | 0.00011522 | 146.3709
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 92 | 4886 | 0.0008701 | 1.6383e-05 | 53.1087
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | V | NONE | 8 | 9843 | 935153 | 0.16653 | 0.0017528 | 95.0069
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 895 | 275710 | 0.049098 | 0.00015938 | 308.0559
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 7 | 21 | 9124 | 0.001643 | 3.7815e-06 | 434.4762
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 2 | 20 | 3.6014e-06 | 3.6014e-07 | 10
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SPLICE, OH | 1 | 1 | 29 | 5.2221e-06 | 1.8007e-07 | 29
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SWITCH, OH | 8 | 162 | 5070 | 0.00091296 | 2.9172e-05 | 31.2963
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 9 | 405 | 7.2929e-05 | 1.6206e-06 | 45
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | CONN/CLAMP | 4 | 5 | 525 | 9.4538e-05 | 9.0036e-07 | 105
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | JUMPER/RISER | 5 | 5 | 665 | 0.00011975 | 9.0036e-07 | 133
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 14 | 1062 | 51035 | 0.0091531 | 0.00019047 | 48.0556
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 4 | 3795 | 1339615 | 0.24026 | 0.00068063 | 352.9947
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | POLE | 3 | 14 | 3704 | 0.00066699 | 2.521e-06 | 264.5714
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | NONE | 6 | 20 | 3459 | 0.00062037 | 3.587e-06 | 172.95
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 3 | 6 | 652 | 0.00011694 | 1.0761e-06 | 108.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | SPLICE, UG | 3 | 23 | 4568 | 0.00081927 | 4.1251e-06 | 198.6087
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 14 | 1243 | 0.00022293 | 2.5109e-06 | 88.7857
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 1 | 321 | 65484 | 0.011745 | 5.7571e-05 | 204
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 1 | 126 | 2.2598e-05 | 1.7935e-07 | 126
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | CONN/CLAMP | 1 | 22 | 1870 | 0.00033538 | 3.9457e-06 | 85
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | BREAKER | 4 | 2166 | 221561 | 0.039737 | 0.00038847 | 102.2904
AEP Total | 2023 | 5575683 | PARTIAL POWER | UG | CONN/CLAMP | 3 | 3 | 361 | 6.4745e-05 | 5.3805e-07 | 120.3333
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 25 | 44 | 6615 | 0.001178 | 7.8355e-06 | 150.3409
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 159 | 2.8517e-05 | 1.7935e-07 | 159
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AB | INSULATOR | 1 | 1470 | 99960 | 0.017928 | 0.00026364 | 68
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | METERING | 1 | 2 | 226 | 4.0533e-05 | 3.587e-07 | 113
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 33 | 6471 | 0.0011716 | 5.9745e-06 | 196.0909
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 1 | 64 | 1.167e-05 | 1.8234e-07 | 64
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 13 | 3932 | 0.00071697 | 2.3704e-06 | 302.4615
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 2 | 9 | 1260 | 0.00022975 | 1.6411e-06 | 140
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | METERING | 3 | 3 | 164 | 2.9904e-05 | 5.4703e-07 | 54.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | PEDESTAL | 1 | 1 | 47 | 8.5701e-06 | 1.8234e-07 | 47
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 13 | 1131 | 0.00020623 | 2.3704e-06 | 87
AEP Total | 2020 | 5484199 | PARTIAL POWER | F | CONDUCTOR OVERHEAD | 1 | 8 | 1232 | 0.00022465 | 1.4587e-06 | 154
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 2551 | 157652 | 0.028747 | 0.00046515 | 61.8001
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 185 | 20350 | 0.0036843 | 3.3494e-05 | 110
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 1 | 188 | 3.4037e-05 | 1.8105e-07 | 188
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | POLE | 1 | 1 | 178 | 3.2226e-05 | 1.8105e-07 | 178
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | VA | POLE | 2 | 463 | 6945 | 0.0012506 | 8.3373e-05 | 15
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 11 | 319 | 5.7443e-05 | 1.9808e-06 | 29
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 41 | 2591 | 0.00046657 | 7.3829e-06 | 63.1951
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 1 | 308 | 5.524e-05 | 1.7935e-07 | 308
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 1074 | 115713 | 0.020753 | 0.00019262 | 107.7402
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 94 | 16699 | 0.003007 | 1.6927e-05 | 177.6489
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 2 | 179 | 3.2104e-05 | 3.587e-07 | 89.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 3 | 3 | 1297 | 0.00023262 | 5.3805e-07 | 432.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 18 | 2034 | 0.0003648 | 3.2283e-06 | 113
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | TRANSFORMER, GROUNDING | 2 | 2 | 224 | 4.0336e-05 | 3.6014e-07 | 112
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | POLE | 1 | 29 | 3799 | 0.00068409 | 5.2221e-06 | 131
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | BREAKER | 1 | 1 | 91 | 1.6387e-05 | 1.8007e-07 | 91
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 3860 | 546855 | 0.097384 | 0.00068739 | 141.6723
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 63 | 1049 | 511594 | 0.091105 | 0.00018681 | 487.6969
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | NONE | 26 | 297 | 7325 | 0.0013044 | 5.289e-05 | 24.6633
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 7 | 1657 | 477356 | 0.085007 | 0.00029508 | 288.0845
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 2 | 14 | 2336 | 0.00041599 | 2.4931e-06 | 166.8571
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 20 | 16083 | 1271197 | 0.22637 | 0.0028641 | 79.0398
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 15 | 385 | 61452 | 0.010943 | 6.8561e-05 | 159.6156
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 45 | 11295 | 0.0020114 | 8.0136e-06 | 251
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | CUTOUT | 1 | 5 | 5960 | 0.0010689 | 8.9675e-07 | 1192
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | ARRESTER | 3 | 1467 | 116740 | 0.020789 | 0.00026124 | 79.5774
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | METERING | 1 | 1 | 282 | 5.142e-05 | 1.8234e-07 | 282
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | POLE | 1 | 1 | 155 | 2.8263e-05 | 1.8234e-07 | 155
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | OU | NONE | 1 | 672 | 50400 | 0.00919 | 0.00012253 | 75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CIRCUIT SWITCHER | 1 | 217 | 5642 | 0.0010288 | 3.9568e-05 | 26
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | JUMPER/RISER | 1 | 5 | 1200 | 0.00021609 | 9.0036e-07 | 240
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 3 | 420 | 7.5327e-05 | 5.3805e-07 | 140
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | POLE | 2 | 2 | 994 | 0.00017827 | 3.587e-07 | 497
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | JUMPER/RISER | 4 | 201 | 22568 | 0.0041151 | 3.6651e-05 | 112.2786
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 2 | 36 | 15575 | 0.00284 | 6.5643e-06 | 432.6389
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | NONE | 2 | 2 | 156 | 2.8445e-05 | 3.6468e-07 | 78
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CUTOUT | 1 | 4 | 364 | 6.6373e-05 | 7.2937e-07 | 91
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONDUCTOR UG | 3 | 31 | 916 | 0.00016703 | 5.6526e-06 | 29.5484
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 2857 | 523762 | 0.095504 | 0.00052095 | 183.3259
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 367 | 6.692e-05 | 1.8234e-07 | 367
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 1 | 269 | 4.905e-05 | 1.8234e-07 | 269
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | METERING | 1 | 1 | 71 | 1.2946e-05 | 1.8234e-07 | 71
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR UG | 3 | 28 | 3416 | 0.00062288 | 5.1056e-06 | 122
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | NONE | 78 | 5969 | 328803 | 0.058971 | 0.0010705 | 55.0851
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | NONE | 93 | 2104 | 191206 | 0.034293 | 0.00037735 | 90.8774
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 47 | 5209 | 0.00093424 | 8.4295e-06 | 110.8298
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, OH | 46 | 7467 | 716204 | 0.12845 | 0.0013392 | 95.9159
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 6 | 10 | 7098 | 0.001273 | 1.7935e-06 | 709.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 777 | 11215 | 1827562 | 0.32545 | 0.0019972 | 162.9569
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | INSULATOR | 135 | 33803 | 3831340 | 0.68715 | 0.0060626 | 113.3432
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 9 | 32 | 3302 | 0.00058802 | 5.6986e-06 | 103.1875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 19 | 770 | 312911 | 0.056121 | 0.0001381 | 406.3779
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 30 | 1742 | 0.00031243 | 5.3805e-06 | 58.0667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 9 | 2836 | 0.00050864 | 1.6142e-06 | 315.1111
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONN/CLAMP | 4 | 33 | 3655 | 0.00065553 | 5.9186e-06 | 110.7576
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | FUSE | 7 | 200 | 39708 | 0.0071216 | 3.587e-05 | 198.54
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | FUSE | 26 | 94 | 8673 | 0.0015555 | 1.6859e-05 | 92.266
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | SPLICE, OH | 3 | 5 | 549 | 9.8463e-05 | 8.9675e-07 | 109.8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 11 | 893 | 0.00016016 | 1.9729e-06 | 81.1818
AEP Total | 2021 | 5523447 | PARTIAL POWER | FW | METERING | 1 | 1 | 25 | 4.5262e-06 | 1.8105e-07 | 25
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | CONDUCTOR UG | 2 | 2 | 417 | 7.5496e-05 | 3.6209e-07 | 208.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CROSSARM | 57 | 20454 | 5444859 | 0.98047 | 0.0036832 | 266.2002
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 171 | 31077 | 3376973 | 0.6081 | 0.0055961 | 108.6647
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | TRANSFORMER, POWER - NON LTC | 5 | 3966 | 408323 | 0.073528 | 0.00071417 | 102.9559
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 439 | 3386 | 377580 | 0.067992 | 0.00060972 | 111.5121
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CROSSARM | 1 | 293 | 70661 | 0.012724 | 5.2761e-05 | 241.1638
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 13 | 4499 | 308433 | 0.05554 | 0.00081014 | 68.5559
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | INSULATOR | 117 | 27610 | 3657820 | 0.65867 | 0.0049718 | 132.4817
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | NONE | 16 | 34 | 8900 | 0.0016026 | 6.1224e-06 | 261.7647
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | SPLICE, OH | 4 | 5 | 578 | 0.00010539 | 9.1171e-07 | 115.6
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | NONE | 5 | 175 | 12741 | 0.0023232 | 3.191e-05 | 72.8057
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | NONE | 767 | 9991 | 760365 | 0.13865 | 0.0018218 | 76.105
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | ARRESTER | 16 | 2133 | 255098 | 0.046515 | 0.00038894 | 119.5959
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 29 | 4084 | 383146 | 0.069864 | 0.00074468 | 93.8164
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 5 | 1285 | 0.00023431 | 9.1171e-07 | 257
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 25 | 442 | 11401 | 0.0020789 | 8.0595e-05 | 25.7941
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | REGULATOR | 11 | 4942 | 191560 | 0.034929 | 0.00090113 | 38.7616
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | ARRESTER | 3 | 12 | 2065 | 0.00037654 | 2.1881e-06 | 172.0833
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 6 | 4875 | 956425 | 0.1744 | 0.00088892 | 196.1897
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 7 | 262 | 107261 | 0.019558 | 4.7774e-05 | 409.3931
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | NONE | 12 | 91 | 20943 | 0.0038188 | 1.6593e-05 | 230.1429
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | NONE | 2 | 7 | 600 | 0.00010941 | 1.2764e-06 | 85.7143
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, UG | 7 | 11 | 3528 | 0.0006433 | 2.0058e-06 | 320.7273
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 1623 | 31838 | 0.0057102 | 0.00029109 | 19.6168
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | SPLICE, OH | 8 | 25 | 10163 | 0.0018227 | 4.4838e-06 | 406.52
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 4 | 9 | 1056 | 0.00019016 | 1.6206e-06 | 117.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 25 | 3078 | 0.00055426 | 4.5018e-06 | 123.12
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | POLE | 7 | 1480 | 456306 | 0.081839 | 0.00026544 | 308.3149
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | REGULATOR | 6 | 1097 | 218165 | 0.039128 | 0.00019675 | 198.8742
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | TRANSFORMER, UG | 1 | 2 | 1140 | 0.00020446 | 3.587e-07 | 570
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | NONE | 17 | 35 | 7050 | 0.0012644 | 6.2773e-06 | 201.4286
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | METERING | 4 | 7 | 1096 | 0.00019736 | 1.2605e-06 | 156.5714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 1740 | 700544 | 0.12615 | 0.00031333 | 402.6115
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 34 | 456 | 53599 | 0.009613 | 8.1784e-05 | 117.5417
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CUTOUT | 7 | 16 | 4061 | 0.00072834 | 2.8696e-06 | 253.8125
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 4 | 308 | 5.524e-05 | 7.174e-07 | 77
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 4 | 4104 | 56276 | 0.010093 | 0.00073605 | 13.7125
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CUTOUT | 2 | 740 | 20061 | 0.003632 | 0.00013397 | 27.1095
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | NONE | 2 | 4 | 522 | 9.4506e-05 | 7.2419e-07 | 130.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 1 | 100 | 1.8105e-05 | 1.8105e-07 | 100
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CUTOUT | 1686 | 74695 | 7645510 | 1.3941 | 0.01362 | 102.3564
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 90 | 34905 | 3940359 | 0.71849 | 0.0063646 | 112.8881
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | INSULATOR | 9 | 4140 | 642038 | 0.11707 | 0.0007549 | 155.0816
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 7 | 14 | 1175 | 0.00021425 | 2.5528e-06 | 83.9286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | NONE | 494 | 43225 | 5401031 | 0.98483 | 0.0078817 | 124.9516
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | REGULATOR | 2 | 230 | 2034 | 0.00037088 | 4.1939e-05 | 8.8435
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | NONE | 46 | 4766 | 136938 | 0.02497 | 0.00086904 | 28.7323
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | SWITCH, OH | 12 | 900 | 31253 | 0.0056987 | 0.00016411 | 34.7256
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | NONE | 8 | 20 | 5026 | 0.00090994 | 3.6209e-06 | 251.3
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 2922 | 516102 | 0.093438 | 0.00052902 | 176.6263
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | ARRESTER | 1 | 1 | 288 | 5.2141e-05 | 1.8105e-07 | 288
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 6 | 882 | 0.00015968 | 1.0863e-06 | 147
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | POLE | 3 | 74 | 15803 | 0.0028816 | 1.3493e-05 | 213.5541
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | NONE | 82 | 6873 | 449214 | 0.081911 | 0.0012532 | 65.3592
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 35 | 19950 | 1802458 | 0.32866 | 0.0036377 | 90.3488
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | POLE | 3 | 184 | 162278 | 0.02938 | 3.3313e-05 | 881.9457
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONN/CLAMP | 15 | 18 | 2416 | 0.00043741 | 3.2588e-06 | 134.2222
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | NONE | 11 | 700 | 28697 | 0.0051955 | 0.00012673 | 40.9957
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | BREAKER | 5 | 9598 | 1137509 | 0.20594 | 0.0017377 | 118.5152
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 354 | 30447 | 0.0055123 | 6.409e-05 | 86.0085
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABI | ARRESTER | 1 | 1210 | 224405 | 0.040628 | 0.00021907 | 185.4587
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | POLE | 2 | 304 | 75765 | 0.013717 | 5.5038e-05 | 249.227
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | POLE | 1 | 82 | 7708 | 0.0013955 | 1.4846e-05 | 94
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONN/CLAMP | 3 | 6 | 4895 | 0.00088622 | 1.0863e-06 | 815.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | SWITCH, OH | 1 | 506 | 71122 | 0.012876 | 9.1609e-05 | 140.5573
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 677 | 6770 | 0.0012257 | 0.00012257 | 10
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 1 | 241 | 4.3632e-05 | 1.8105e-07 | 241
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 4 | 15 | 2493 | 0.00045135 | 2.7157e-06 | 166.2
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABI | NONE | 1 | 885 | 245097 | 0.044374 | 0.00016023 | 276.9458
AEP Total | 2021 | 5523447 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 15 | 2.7157e-06 | 1.8105e-07 | 15
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 4 | 13 | 4409 | 0.00079823 | 2.3536e-06 | 339.1538
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 4 | 297 | 176126 | 0.031887 | 5.3771e-05 | 593.0168
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | NONE | 2346 | 132221 | 24602941 | 4.4303 | 0.023809 | 186.0744
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | NONE | 3660 | 66883 | 5597111 | 1.0079 | 0.012044 | 83.6851
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | NONE | 88 | 364 | 51478 | 0.0092697 | 6.5546e-05 | 141.4231
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 49 | 13387 | 1735582 | 0.31253 | 0.0024106 | 129.6468
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | NONE | 17 | 62 | 11612 | 0.002091 | 1.1164e-05 | 187.2903
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | METERING | 9 | 14 | 954 | 0.00017179 | 2.521e-06 | 68.1429
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | NONE | 7 | 119 | 11041 | 0.0019882 | 2.1429e-05 | 92.7815
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 12 | 1365 | 138158 | 0.024878 | 0.0002458 | 101.2147
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 29 | 1536 | 213120 | 0.038377 | 0.00027659 | 138.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 3 | 5 | 1093 | 0.00019603 | 8.9675e-07 | 218.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 8 | 577 | 109854 | 0.019702 | 0.00010349 | 190.3882
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | NONE | 6 | 26 | 10005 | 0.0017944 | 4.6631e-06 | 384.8077
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 37 | 8351 | 0.0015038 | 6.6627e-06 | 225.7027
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 4 | 39 | 2166 | 0.00039004 | 7.0228e-06 | 55.5385
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE | 135 | 16818 | 2790950 | 0.50056 | 0.0030163 | 165.9502
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | SPLICE, UG | 2 | 4 | 818 | 0.0001473 | 7.2029e-07 | 204.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CROSSARM | 243 | 9928 | 348947 | 0.062584 | 0.0017806 | 35.1478
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 11 | 116 | 17712 | 0.0031767 | 2.0805e-05 | 152.6897
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 25 | 1748 | 175390 | 0.031456 | 0.0003135 | 100.3375
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | NONE | 2 | 136 | 18662 | 0.0033787 | 2.4622e-05 | 137.2206
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 178 | 3.2226e-05 | 1.8105e-07 | 178
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 948 | 6041 | 1420236 | 0.25897 | 0.0011015 | 235.0995
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 836 | 4878 | 459776 | 0.083836 | 0.00088946 | 94.255
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 346 | 6.309e-05 | 1.8234e-07 | 346
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | NONE | 158 | 6552 | 1476621 | 0.26925 | 0.0011947 | 225.3695
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 1 | 514 | 9.3724e-05 | 1.8234e-07 | 514
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 345 | 6.2908e-05 | 3.6468e-07 | 172.5
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | REGULATOR | 11 | 13794 | 953338 | 0.17383 | 0.0025152 | 69.1125
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 3 | 931 | 0.00016976 | 5.4703e-07 | 310.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 6 | 140 | 339330 | 0.060428 | 2.4931e-05 | 2423.7857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 3691 | 422144 | 0.075175 | 0.00065729 | 114.3712
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | METERING | 4 | 24 | 9271 | 0.001651 | 4.2739e-06 | 386.2917
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 12 | 176 | 19600 | 0.0034904 | 3.1342e-05 | 111.3636
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CUTOUT | 9 | 2234 | 212292 | 0.037805 | 0.00039783 | 95.0278
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 3 | 13 | 590 | 0.00010507 | 2.315e-06 | 45.3846
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONN/CLAMP | 6 | 148 | 14755 | 0.0026276 | 2.6356e-05 | 99.6959
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 4 | 705 | 0.00012555 | 7.1232e-07 | 176.25
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 1945 | 529830 | 0.094352 | 0.00034637 | 272.4062
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 305 | 31110 | 0.0055401 | 5.4314e-05 | 102
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | SPLICE, OH | 1 | 6 | 642 | 0.00011433 | 1.0685e-06 | 107
AEP Total | 2024 | 5615460 | PARTIAL POWER | CE | OTHER EQUIPMENT | 1 | 1 | 1370 | 0.00024397 | 1.7808e-07 | 1370
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 71 | 55664 | 0.0099126 | 1.2644e-05 | 784
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 3 | 11 | 1688 | 0.00030274 | 1.9729e-06 | 153.4545
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | POLE | 2 | 912 | 245532 | 0.043724 | 0.00016241 | 269.2237
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | ARRESTER | 2 | 2 | 958 | 0.0001706 | 3.5616e-07 | 479
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 2927 | 571087 | 0.1017 | 0.00052124 | 195.11
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | NETWORK LIMITER | 1 | 1 | 99 | 1.763e-05 | 1.7808e-07 | 99
AEP Total | 2025 | 5615460 | PARTIAL POWER | UG | CONDUCTOR UG | 10 | 12 | 4203 | 0.00074847 | 2.137e-06 | 350.25
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | ARRESTER | 1 | 4 | 96 | 1.7096e-05 | 7.1232e-07 | 24
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 718 | 9991 | 0.0017792 | 0.00012786 | 13.915
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CABLE TERMINATOR | 1 | 35 | 2240 | 0.0003989 | 6.2328e-06 | 64
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 5 | 300 | 5.3805e-05 | 8.9675e-07 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | POLE | 1 | 18 | 9738 | 0.0017535 | 3.2413e-06 | 541
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 1 | 36 | 6.4826e-06 | 1.8007e-07 | 36
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 15 | 5205 | 0.00092691 | 2.6712e-06 | 347
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 5 | 1250 | 0.0002226 | 8.904e-07 | 250
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 3 | 780 | 0.0001389 | 5.3424e-07 | 260
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 1 | 1 | 183 | 3.2589e-05 | 1.7808e-07 | 183
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 2 | 1078 | 0.00019197 | 3.5616e-07 | 539
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 5 | 245 | 313096 | 0.055756 | 4.363e-05 | 1277.9429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 313 | 114177 | 0.020333 | 5.5739e-05 | 364.7827
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 9 | 3978 | 0.0007084 | 1.6027e-06 | 442
AEP Total | 2025 | 5615460 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 57 | 1.0151e-05 | 1.7808e-07 | 57
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 1 | 2 | 156 | 2.778e-05 | 3.5616e-07 | 78
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 2 | 316 | 11540 | 0.002055 | 5.6273e-05 | 36.519
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 247 | 51376 | 0.009149 | 4.3986e-05 | 208
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 2 | 142 | 2.5287e-05 | 3.5616e-07 | 71
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 211 | 3.8474e-05 | 1.8234e-07 | 211
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 2 | 28 | 4004 | 0.0007301 | 5.1056e-06 | 143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 6 | 552 | 9.9001e-05 | 1.0761e-06 | 92
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | SPLICE, OH | 1 | 1 | 117 | 2.1068e-05 | 1.8007e-07 | 117
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CUTOUT | 1 | 2 | 146 | 2.629e-05 | 3.6014e-07 | 73
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | NONE | 1 | 13 | 936 | 0.00016787 | 2.3316e-06 | 72
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | REGULATOR | 1 | 112 | 9408 | 0.0016873 | 2.0087e-05 | 84
AEP Total | 2021 | 5523447 | PARTIAL POWER | OU | CUTOUT | 1 | 3 | 186 | 3.3675e-05 | 5.4314e-07 | 62
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CROSSARM | 59 | 14104 | 3309159 | 0.59911 | 0.0025535 | 234.6256
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | NONE | 1846 | 35031 | 2953785 | 0.53477 | 0.0063422 | 84.3192
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | NONE | 8 | 8 | 1393 | 0.0002522 | 1.4484e-06 | 174.125
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | INSULATOR | 4 | 55 | 10125 | 0.0018331 | 9.9576e-06 | 184.0909
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CUTOUT | 12 | 67 | 8837 | 0.0015999 | 1.213e-05 | 131.8955
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 13 | 328 | 58848 | 0.010654 | 5.9383e-05 | 179.4146
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | METERING | 19 | 20 | 2393 | 0.00043324 | 3.6209e-06 | 119.65
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | INSULATOR | 14 | 2029 | 159149 | 0.028813 | 0.00036734 | 78.4372
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | REGULATOR | 8 | 2453 | 85530 | 0.015485 | 0.00044411 | 34.8675
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 6 | 4940 | 513530 | 0.092973 | 0.00089437 | 103.9534
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE | 6 | 142 | 30978 | 0.0056085 | 2.5709e-05 | 218.1549
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 6 | 9 | 4804 | 0.00086975 | 1.6294e-06 | 533.7778
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 63 | 1.1406e-05 | 1.8105e-07 | 63
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | FUSE | 4 | 56 | 8792 | 0.0015918 | 1.0139e-05 | 157
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 577 | 91646 | 0.016592 | 0.00010446 | 158.8319
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | POLE | 1 | 30 | 1050 | 0.0001901 | 5.4314e-06 | 35
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 833 | 165376 | 0.029941 | 0.00015081 | 198.5306
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CUTOUT | 2 | 15 | 2463 | 0.00044592 | 2.7157e-06 | 164.2
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 266 | 4.8158e-05 | 1.8105e-07 | 266
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | POLE | 1 | 9 | 3150 | 0.00057438 | 1.6411e-06 | 350
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 31 | 21876 | 0.0039393 | 5.5822e-06 | 705.6774
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONN/CLAMP | 2 | 2 | 154 | 2.7731e-05 | 3.6014e-07 | 77
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 234 | 25974 | 0.0047025 | 4.2365e-05 | 111
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 5 | 600 | 0.00010804 | 9.0036e-07 | 120
AEP Total | 2023 | 5575683 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 186 | 3.3359e-05 | 1.7935e-07 | 186
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 6 | 522 | 9.3621e-05 | 1.0761e-06 | 87
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | POLE | 1733 | 11818 | 1546315 | 0.27537 | 0.0021045 | 130.8441
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 954 | 47550 | 8775136 | 1.5627 | 0.0084677 | 184.5454
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 298 | 9305 | 1609165 | 0.28656 | 0.001657 | 172.9355
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 69 | 179 | 32958 | 0.0058692 | 3.1876e-05 | 184.1229
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 17 | 482 | 240407 | 0.042812 | 8.5834e-05 | 498.7697
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 5 | 27 | 4262 | 0.00075898 | 4.8082e-06 | 157.8519
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | NONE | 39 | 600 | 333654 | 0.060082 | 0.00010804 | 556.09
AEP Total | 2022 | 5553337 | PARTIAL POWER | WFS | SPLICE, OH | 1 | 1 | 133 | 2.395e-05 | 1.8007e-07 | 133
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | SPLICE, UG | 1 | 46 | 7724 | 0.0013909 | 8.2833e-06 | 167.913
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 3 | 435 | 7.8331e-05 | 5.4022e-07 | 145
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | WU | NONE | 1 | 3 | 870 | 0.00015493 | 5.3424e-07 | 290
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | FUSE | 1 | 1 | 26 | 4.6301e-06 | 1.7808e-07 | 26
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 6 | 1693 | 0.00030149 | 1.0685e-06 | 282.1667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 4 | 11 | 441 | 7.8533e-05 | 1.9589e-06 | 40.0909
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 2 | 112 | 2375 | 0.00042294 | 1.9945e-05 | 21.2054
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 43 | 5504 | 0.00098015 | 7.6574e-06 | 128
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 6116 | 1139405 | 0.20291 | 0.0010891 | 186.2991
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 1 | 452 | 8.0492e-05 | 1.7808e-07 | 452
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | TRANSFORMER, OH | 1 | 1 | 105 | 1.9146e-05 | 1.8234e-07 | 105
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 108 | 1.9233e-05 | 1.7808e-07 | 108
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 199 | 3.5438e-05 | 1.7808e-07 | 199
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 82 | 1.4603e-05 | 1.7808e-07 | 82
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONN/CLAMP | 1 | 1 | 47 | 8.4634e-06 | 1.8007e-07 | 47
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 20 | 9781 | 0.0017835 | 3.6468e-06 | 489.05
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 8 | 1560 | 0.00028091 | 1.4406e-06 | 195
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | FUSE | 1 | 1 | 68 | 1.2196e-05 | 1.7935e-07 | 68
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | R | NONE | 2 | 4461 | 729939 | 0.12999 | 0.00079441 | 163.6268
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 2 | 62 | 1.1041e-05 | 3.5616e-07 | 31
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | INSULATOR | 1 | 6 | 432 | 7.693e-05 | 1.0685e-06 | 72
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | JUMPER/RISER | 1 | 580 | 114840 | 0.020451 | 0.00010329 | 198
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | POLE | 1 | 61 | 7808 | 0.0013904 | 1.0863e-05 | 128
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | NONE | 3682 | 72725 | 5482082 | 0.99251 | 0.013167 | 75.381
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 701 | 41321 | 7737003 | 1.4008 | 0.007481 | 187.2414
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | METERING | 56 | 74 | 6537 | 0.0011835 | 1.3397e-05 | 88.3378
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 764 | 3668 | 334021 | 0.060473 | 0.00066408 | 91.0635
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | NONE | 1032 | 19924 | 1749370 | 0.31672 | 0.0036072 | 87.8021
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CROSSARM | 90 | 39132 | 4761174 | 0.86199 | 0.0070847 | 121.6696
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | NONE | 121 | 751 | 69418 | 0.012568 | 0.00013597 | 92.4341
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE | 11 | 855 | 332197 | 0.060143 | 0.00015479 | 388.5345
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 5 | 416 | 7.5315e-05 | 9.0523e-07 | 83.2
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | OTHER EQUIPMENT | 1 | 10 | 350 | 6.3366e-05 | 1.8105e-06 | 35
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CABLE TERMINATOR | 8 | 10 | 1046 | 0.00018937 | 1.8105e-06 | 104.6
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | NONE | 3 | 3 | 309 | 5.5943e-05 | 5.4314e-07 | 103
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | ARRESTER | 4 | 250 | 18281 | 0.0033097 | 4.5262e-05 | 73.124
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 7 | 7 | 1036 | 0.00018756 | 1.2673e-06 | 148
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CUTOUT | 4 | 24 | 1045 | 0.00018919 | 4.3451e-06 | 43.5417
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CROSSARM | 2 | 572 | 74876 | 0.013556 | 0.00010356 | 130.9021
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | POLE | 1 | 45 | 5325 | 0.00096407 | 8.1471e-06 | 118.3333
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 2 | 572 | 0.000103 | 3.6014e-07 | 286
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | NONE | 1 | 1 | 94 | 1.7018e-05 | 1.8105e-07 | 94
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | CONN/CLAMP | 1 | 3 | 90 | 1.6206e-05 | 5.4022e-07 | 30
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, STATION SERVICE | 1 | 1 | 65 | 1.1768e-05 | 1.8105e-07 | 65
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | SPLICE, OH | 1 | 8 | 15688 | 0.0027937 | 1.4246e-06 | 1961
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 40 | 989 | 108874 | 0.019388 | 0.00017612 | 110.0849
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | ARRESTER | 43 | 196 | 4886 | 0.0008701 | 3.4904e-05 | 24.9286
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 7 | 466 | 89166 | 0.015879 | 8.2985e-05 | 191.3433
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 2 | 3709 | 314618 | 0.056427 | 0.00066521 | 84.8256
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | NETWORK TRANSFORMER | 1 | 4 | 344 | 6.2726e-05 | 7.2937e-07 | 86
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | METERING | 2 | 38 | 1050 | 0.00019146 | 6.929e-06 | 27.6316
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 6 | 546 | 9.9559e-05 | 1.0941e-06 | 91
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 6 | 612 | 0.00011159 | 1.0941e-06 | 102
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | FUSE | 1 | 25 | 2000 | 0.00036468 | 4.5586e-06 | 80
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | POLE | 2 | 16 | 3076 | 0.00056088 | 2.9175e-06 | 192.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CAPACITOR | 1 | 9 | 2655 | 0.00048412 | 1.6411e-06 | 295
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | NONE | 1 | 6 | 540 | 9.7765e-05 | 1.0863e-06 | 90
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 31 | 2418 | 0.00043541 | 5.5822e-06 | 78
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | NONE | 835 | 11699 | 837869 | 0.14921 | 0.0020834 | 71.6189
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 480 | 19903 | 2122541 | 0.37798 | 0.0035443 | 106.6443
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 255 | 15698 | 1726833 | 0.30751 | 0.0027955 | 110.0034
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 174 | 16356 | 0.0029127 | 3.0986e-05 | 94
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 8 | 72 | 18593 | 0.003311 | 1.2822e-05 | 258.2361
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 1807 | 137794 | 0.024538 | 0.00032179 | 76.2557
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 53 | 16483 | 0.0029842 | 9.5955e-06 | 311
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | METERING | 5 | 5 | 420 | 7.563e-05 | 9.0036e-07 | 84
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | INSULATOR | 2 | 116 | 8508 | 0.0015321 | 2.0888e-05 | 73.3448
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 96 | 1.7287e-05 | 1.8007e-07 | 96
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CUTOUT | 1 | 2 | 230 | 4.1641e-05 | 3.6209e-07 | 115
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 6 | 6 | 652 | 0.00011611 | 1.0685e-06 | 108.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 1111 | 76337 | 0.013594 | 0.00019785 | 68.7102
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | SWITCH, OH | 1 | 1 | 191 | 3.4013e-05 | 1.7808e-07 | 191
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 14 | 854 | 0.00015572 | 2.5528e-06 | 61
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 10 | 3040 | 0.00055432 | 1.8234e-06 | 304
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 1177 | 15675 | 0.0028582 | 0.00021462 | 13.3178
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 259 | 4.7227e-05 | 1.8234e-07 | 259
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | SPLICE, UG | 3 | 3 | 1183 | 0.00021571 | 5.4703e-07 | 394.3333
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | NONE | 1 | 1 | 204 | 3.7198e-05 | 1.8234e-07 | 204
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | TRANSFORMER, OH | 1 | 3 | 360 | 6.5177e-05 | 5.4314e-07 | 120
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | CONN/CLAMP | 1 | 1 | 104 | 1.8829e-05 | 1.8105e-07 | 104
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CABLE TERMINATOR | 2 | 2 | 390 | 7.0228e-05 | 3.6014e-07 | 195
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | FUSE | 1 | 14 | 784 | 0.00014296 | 2.5528e-06 | 56
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 3 | 486 | 8.7515e-05 | 5.4022e-07 | 162
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SPLICE, UG | 2 | 5 | 63 | 1.1345e-05 | 9.0036e-07 | 12.6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 7 | 1223 | 0.00022023 | 1.2605e-06 | 174.7143
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | METERING | 33 | 71 | 2503 | 0.00044573 | 1.2644e-05 | 35.2535
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, UG | 7 | 217 | 29256 | 0.0052099 | 3.8643e-05 | 134.8203
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 3 | 28 | 5145 | 0.00091622 | 4.9862e-06 | 183.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 1 | 102 | 2040 | 0.00036328 | 1.8164e-05 | 20
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CUTOUT | 1 | 1 | 206 | 3.6684e-05 | 1.7808e-07 | 206
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 2 | 25 | 489 | 8.7081e-05 | 4.452e-06 | 19.56
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 15 | 416 | 7.4081e-05 | 2.6712e-06 | 27.7333
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABI | NONE | 1 | 556 | 120940 | 0.021778 | 0.00010012 | 217.518
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | TRANSFORMER, OH | 2 | 3 | 541 | 9.7419e-05 | 5.4022e-07 | 180.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 5 | 354 | 111645 | 0.020024 | 6.349e-05 | 315.3814
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 101 | 24528 | 3358147 | 0.59802 | 0.0043679 | 136.9108
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | NONE | 149 | 377 | 45086 | 0.0080289 | 6.7136e-05 | 119.5915
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AF | NONE | 1 | 695 | 49345 | 0.0087873 | 0.00012377 | 71
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 19 | 203 | 32903 | 0.0058594 | 3.615e-05 | 162.0837
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 4 | 235 | 40532 | 0.0072179 | 4.1849e-05 | 172.4766
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | METERING | 10 | 12 | 2252 | 0.00040104 | 2.137e-06 | 187.6667
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | FUSE | 2 | 4 | 368 | 6.5533e-05 | 7.1232e-07 | 92
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | INSULATOR | 1 | 501 | 171843 | 0.03082 | 8.9854e-05 | 343
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | POLE | 1 | 6 | 1578 | 0.00028301 | 1.0761e-06 | 263
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 30 | 5340 | 0.00095773 | 5.3805e-06 | 178
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 49 | 99225 | 0.017796 | 8.7882e-06 | 2025
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 450 | 8.0708e-05 | 1.7935e-07 | 450
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONN/CLAMP | 9 | 45 | 1665 | 0.00029982 | 8.1032e-06 | 37
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERO | NONE | 1 | 1 | 318 | 5.7573e-05 | 1.8105e-07 | 318
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 2 | 2 | 753 | 0.00013633 | 3.6209e-07 | 376.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | TRANSFORMER, UG | 1 | 20 | 580 | 0.00010501 | 3.6209e-06 | 29
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | CONN/CLAMP | 2 | 6 | 590 | 0.00010682 | 1.0863e-06 | 98.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ERF | NONE | 11 | 7470 | 543676 | 0.098431 | 0.0013524 | 72.7813
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 1452 | 86412 | 0.015645 | 0.00026288 | 59.5124
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | TRANSFORMER, OH | 1 | 3 | 345 | 6.2461e-05 | 5.4314e-07 | 115
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | ARRESTER | 1 | 6 | 1986 | 0.00035956 | 1.0863e-06 | 331
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 16 | 1664 | 0.00030126 | 2.8967e-06 | 104
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 655 | 24848 | 3312528 | 0.59649 | 0.0044744 | 133.3117
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | SWITCH, OH | 5 | 8398 | 448874 | 0.08083 | 0.0015122 | 53.4501
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | NONE | 68 | 2378 | 1553229 | 0.27969 | 0.00042821 | 653.1661
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | U | NONE | 4 | 4599 | 416347 | 0.075378 | 0.00083263 | 90.5299
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 4 | 12 | 682 | 0.00012347 | 2.1726e-06 | 56.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SPLICE, OH | 4 | 7 | 602 | 0.00010899 | 1.2673e-06 | 86
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | BREAKER | 1 | 1106 | 27650 | 0.0050059 | 0.00020024 | 25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | NONE | 2117 | 110119 | 17671849 | 3.2223 | 0.020079 | 160.4796
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CROSSARM | 27 | 13474 | 1849814 | 0.3373 | 0.0024569 | 137.2877
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 4 | 30 | 2838 | 0.00051749 | 5.4703e-06 | 94.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | POLE | 3 | 48 | 2677 | 0.00048813 | 8.7524e-06 | 55.7708
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, OH | 40 | 191 | 52617 | 0.0095943 | 3.4827e-05 | 275.4817
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CROSSARM | 57 | 12064 | 3693728 | 0.67352 | 0.0021998 | 306.1777
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CUTOUT | 4 | 12 | 1293 | 0.00023577 | 2.1881e-06 | 107.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE | 6 | 239 | 81710 | 0.014899 | 4.358e-05 | 341.8828
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 22 | 7892 | 0.001439 | 4.0115e-06 | 358.7273
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, OH | 19 | 22 | 2618 | 0.00047737 | 4.0115e-06 | 119
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 5 | 6 | 600 | 0.00010941 | 1.0941e-06 | 100
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 12 | 228 | 22555 | 0.0041127 | 4.1574e-05 | 98.9254
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | INSULATOR | 2 | 694 | 38910 | 0.0070949 | 0.00012655 | 56.0663
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE HARDWARE | 7 | 758 | 70238 | 0.012807 | 0.00013822 | 92.6623
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 16 | 90 | 11963 | 0.0021814 | 1.6411e-05 | 132.9222
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CAPACITOR | 5 | 16 | 1179 | 0.00021498 | 2.9175e-06 | 73.6875
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | FO | NONE | 1 | 952 | 59024 | 0.010763 | 0.00017359 | 62
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONN/CLAMP | 57 | 148 | 20485 | 0.0036888 | 2.6651e-05 | 138.4122
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 17 | 1993 | 595193 | 0.10718 | 0.00035888 | 298.6417
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | POLE | 10 | 318 | 105013 | 0.01891 | 5.7263e-05 | 330.2296
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 90 | 1.6206e-05 | 1.8007e-07 | 90
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR UG | 499 | 828 | 161246 | 0.02892 | 0.0001485 | 194.7415
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE | 220 | 27148 | 11290437 | 2.0249 | 0.004869 | 415.8847
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 303 | 1440 | 184605 | 0.033109 | 0.00025826 | 128.1979
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SPLICE, OH | 11 | 42 | 1889 | 0.00034016 | 7.563e-06 | 44.9762
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONN/CLAMP | 35 | 590 | 72772 | 0.013104 | 0.00010624 | 123.3424
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR UG | 22 | 41 | 7365 | 0.0013262 | 7.3829e-06 | 179.6341
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | FUSE | 5 | 23 | 3296 | 0.00059352 | 4.1417e-06 | 143.3043
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 17 | 3559 | 379712 | 0.068375 | 0.00064088 | 106.6906
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WU | NONE | 2 | 1573 | 429810 | 0.077397 | 0.00028325 | 273.2422
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, OH | 16 | 9492 | 1336734 | 0.24071 | 0.0017092 | 140.8274
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SPLICE, OH | 7 | 12 | 1932 | 0.0003479 | 2.1609e-06 | 161
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CUTOUT | 1 | 1 | 72 | 1.2965e-05 | 1.8007e-07 | 72
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 13 | 1020 | 0.00018367 | 2.3409e-06 | 78.4615
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE | 7 | 123 | 75849 | 0.013604 | 2.206e-05 | 616.6585
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | FUSE | 11 | 100 | 25527 | 0.0045783 | 1.7935e-05 | 255.27
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | NONE | 27 | 843 | 37920 | 0.006801 | 0.00015119 | 44.9822
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | INSULATOR | 9 | 618 | 113113 | 0.020287 | 0.00011084 | 183.0307
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | JUMPER/RISER | 2 | 3 | 911 | 0.00016405 | 5.4022e-07 | 303.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 350 | 77445 | 0.013946 | 6.3025e-05 | 221.2714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 14 | 161 | 40508 | 0.0072651 | 2.8875e-05 | 251.6025
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 13 | 70 | 17374 | 0.003094 | 1.2466e-05 | 248.2
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | NONE | 10 | 12 | 2089 | 0.00037466 | 2.1522e-06 | 174.0833
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | NONE | 2222 | 32402 | 3116125 | 0.55492 | 0.0057701 | 96.1708
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CROSSARM | 1 | 237 | 48822 | 0.0087562 | 4.2506e-05 | 206
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 26 | 85 | 18114 | 0.0032487 | 1.5245e-05 | 213.1059
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 4 | 13 | 968 | 0.00017361 | 2.3316e-06 | 74.4615
AEP Total | 2023 | 5575683 | PARTIAL POWER | FW | NONE | 1 | 10 | 2870 | 0.00051474 | 1.7935e-06 | 287
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONN/CLAMP | 9 | 9 | 975 | 0.00017487 | 1.6142e-06 | 108.3333
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | PEDESTAL | 1 | 5 | 880 | 0.00015783 | 8.9675e-07 | 176
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | NONE | 6 | 35 | 3641 | 0.00065301 | 6.2773e-06 | 104.0286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 7 | 126 | 7501 | 0.0013453 | 2.2598e-05 | 59.5317
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 1 | 509 | 140484 | 0.025017 | 9.0643e-05 | 276
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 2 | 2 | 851 | 0.00015155 | 3.5616e-07 | 425.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | OTHER EQUIPMENT | 1 | 5 | 615 | 0.00010952 | 8.904e-07 | 123
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 2906 | 241198 | 0.042952 | 0.0005175 | 83
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 17 | 1309 | 0.00023311 | 3.0274e-06 | 77
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 355 | 6.3926e-05 | 1.8007e-07 | 355
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | SPLICE, OH | 1 | 1 | 60 | 1.0685e-05 | 1.7808e-07 | 60
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 18 | 1134 | 0.00020194 | 3.2054e-06 | 63
AEP Total | 2024 | 5615460 | PARTIAL POWER | FW | NONE | 1 | 1 | 57 | 1.0151e-05 | 1.7808e-07 | 57
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 37 | 6.589e-06 | 1.7808e-07 | 37
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 37 | 6179 | 0.0011004 | 6.589e-06 | 167
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CAPACITOR | 1 | 1 | 511 | 9.2017e-05 | 1.8007e-07 | 511
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RELAY | 1 | 631 | 77613 | 0.013976 | 0.00011363 | 123
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | METERING | 1 | 1 | 64 | 1.1587e-05 | 1.8105e-07 | 64
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | INSULATOR | 122 | 31497 | 3819331 | 0.69148 | 0.0057024 | 121.2602
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | FUSE | 76 | 1456 | 150621 | 0.027269 | 0.0002636 | 103.4485
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE HARDWARE | 5 | 1042 | 42007 | 0.0076052 | 0.00018865 | 40.3138
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 3 | 20 | 47697 | 0.0086354 | 3.6209e-06 | 2384.85
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | METERING | 17 | 134 | 14207 | 0.0025721 | 2.426e-05 | 106.0224
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CUTOUT | 36 | 542 | 200385 | 0.036279 | 9.8127e-05 | 369.714
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONN/CLAMP | 8 | 1002 | 36901 | 0.0066808 | 0.00018141 | 36.8273
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | NONE | 3 | 11 | 14209 | 0.0025725 | 1.9915e-06 | 1291.7273
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | FUSE | 35 | 797 | 71411 | 0.012929 | 0.00014429 | 89.5997
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | NONE | 2 | 47 | 4782 | 0.00086576 | 8.5092e-06 | 101.7447
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CROSSARM | 4 | 42 | 6697 | 0.0012125 | 7.6039e-06 | 159.4524
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | NONE | 26 | 16221 | 496392 | 0.08987 | 0.0029368 | 30.6018
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | SWITCH, OH | 3 | 1761 | 137122 | 0.024825 | 0.00031882 | 77.866
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 6 | 55 | 4720 | 0.00085454 | 9.9576e-06 | 85.8182
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | NONE | 3 | 153 | 81192 | 0.01462 | 2.7551e-05 | 530.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 3 | 165 | 2.9593e-05 | 5.3805e-07 | 55
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | FUSE | 5 | 11 | 1666 | 0.0003 | 1.9808e-06 | 151.4545
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CABLE TERMINATOR | 7 | 10 | 1503 | 0.00026956 | 1.7935e-06 | 150.3
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CABLE TERMINATOR | 1 | 42 | 4494 | 0.000806 | 7.5327e-06 | 107
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 12 | 1087 | 0.00019495 | 2.1522e-06 | 90.5833
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | SPLICE, OH | 1 | 1 | 81 | 1.4527e-05 | 1.7935e-07 | 81
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | BREAKER | 1 | 3 | 321 | 5.7803e-05 | 5.4022e-07 | 107
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | SPLICE, OH | 1 | 1 | 174 | 3.1333e-05 | 1.8007e-07 | 174
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 14 | 7934 | 930352 | 0.16686 | 0.001423 | 117.2614
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 273 | 3330 | 276326 | 0.049208 | 0.00059301 | 82.9808
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 3 | 14 | 17063 | 0.0030386 | 2.4931e-06 | 1218.7857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 14 | 1315 | 401139 | 0.071435 | 0.00023417 | 305.0487
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SWITCH, UG | 5 | 16 | 4572 | 0.00081999 | 2.8696e-06 | 285.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | NONE | 43 | 2180 | 261616 | 0.046589 | 0.00038821 | 120.0073
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | NONE | 54 | 817 | 98856 | 0.017604 | 0.00014549 | 120.9988
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 33 | 1406 | 161541 | 0.028767 | 0.00025038 | 114.894
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 27 | 6827 | 839238 | 0.14945 | 0.0012158 | 122.9293
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | FUSE | 1 | 6 | 2208 | 0.00039601 | 1.0761e-06 | 368
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 8 | 175 | 32263 | 0.0057454 | 3.1164e-05 | 184.36
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | NONE | 36 | 70 | 5635 | 0.0010035 | 1.2466e-05 | 80.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 36 | 6.5643e-06 | 1.8234e-07 | 36
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABI | NONE | 11 | 10271 | 1214787 | 0.22151 | 0.0018728 | 118.2735
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 307 | 5.5061e-05 | 1.7935e-07 | 307
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | INSULATOR | 1 | 132 | 17688 | 0.0031723 | 2.3674e-05 | 134
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | TRANSFORMER, OH | 1 | 1 | 173 | 3.1028e-05 | 1.7935e-07 | 173
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AB | NONE | 3 | 2422 | 280753 | 0.050353 | 0.00043439 | 115.9178
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SPLICE, OH | 2 | 4 | 88 | 1.5783e-05 | 7.174e-07 | 22
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 1 | 93 | 1.668e-05 | 1.7935e-07 | 93
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR UG | 3 | 4 | 662 | 0.00011985 | 7.2419e-07 | 165.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 80 | 1.4348e-05 | 1.7935e-07 | 80
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE | 6 | 337 | 88955 | 0.015841 | 6.0013e-05 | 263.9614
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 213 | 75330 | 0.013415 | 3.7931e-05 | 353.662
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 2 | 421 | 7.5506e-05 | 3.587e-07 | 210.5
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | FW | NONE | 1 | 1863 | 11178 | 0.0020048 | 0.00033413 | 6
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, UG | 7 | 12 | 2500 | 0.00045018 | 2.1609e-06 | 208.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | BREAKER | 1 | 2 | 148 | 2.6544e-05 | 3.587e-07 | 74
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 223 | 22831 | 0.0040947 | 3.9995e-05 | 102.3812
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 146 | 2.6e-05 | 1.7808e-07 | 146
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 11 | 74 | 7240 | 0.0012893 | 1.3178e-05 | 97.8378
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | JUMPER/RISER | 3 | 46 | 7458 | 0.0013281 | 8.1917e-06 | 162.1304
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SO | NONE | 1 | 6 | 738 | 0.00013142 | 1.0685e-06 | 123
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 1 | 5 | 5870 | 0.0010453 | 8.904e-07 | 1174
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | OL | TRANSFORMER, STATION SERVICE | 7 | 9858 | 740522 | 0.13335 | 0.0017751 | 75.1189
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WL | INSULATOR | 4 | 1723 | 850096 | 0.15501 | 0.00031418 | 493.3813
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 4 | 668 | 0.0001218 | 7.2937e-07 | 167
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 4 | 906 | 0.00016315 | 7.2029e-07 | 226.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | METERING | 3 | 4 | 217 | 3.9568e-05 | 7.2937e-07 | 54.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 109 | 29321 | 0.0053465 | 1.9875e-05 | 269
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 6 | 1458 | 0.00026254 | 1.0804e-06 | 243
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 167 | 3.0072e-05 | 1.8007e-07 | 167
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CABLE TERMINATOR | 1 | 2 | 138 | 2.475e-05 | 3.587e-07 | 69
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | NONE | 11 | 1916 | 192887 | 0.034734 | 0.00034502 | 100.6717
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | FUSE | 8 | 23 | 14367 | 0.0025871 | 4.1417e-06 | 624.6522
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | R | NONE | 3 | 1429 | 192718 | 0.034703 | 0.00025732 | 134.8621
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | FUSE | 11 | 48 | 3303 | 0.00059239 | 8.6088e-06 | 68.8125
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | JUMPER/RISER | 1 | 670 | 41540 | 0.0074802 | 0.00012065 | 62
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE HARDWARE | 2 | 1174 | 137340 | 0.024731 | 0.0002114 | 116.9847
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONN/CLAMP | 4 | 16 | 1348 | 0.00024405 | 2.8967e-06 | 84.25
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | R | RELAY | 5 | 4888 | 419209 | 0.075896 | 0.00088495 | 85.7629
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 8 | 39 | 3024 | 0.00054748 | 7.0608e-06 | 77.5385
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CABLE TERMINATOR | 4 | 6 | 794 | 0.00014375 | 1.0863e-06 | 132.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | NETWORK LIMITER | 1 | 9 | 1521 | 0.00027537 | 1.6294e-06 | 169
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 18 | 4538 | 0.00082159 | 3.2588e-06 | 252.1111
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | CONN/CLAMP | 2 | 4 | 2555 | 0.00046257 | 7.2419e-07 | 638.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | FUSE | 7 | 145 | 13966 | 0.0025285 | 2.6252e-05 | 96.3172
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CROSSARM | 1 | 26 | 2080 | 0.00037658 | 4.7072e-06 | 80
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 2 | 3 | 1388 | 0.00025129 | 5.4314e-07 | 462.6667
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONN/CLAMP | 88 | 188 | 19706 | 0.0035932 | 3.428e-05 | 104.8191
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 794 | 35003 | 3673162 | 0.66977 | 0.0063825 | 104.9385
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CROSSARM | 246 | 9004 | 766544 | 0.13977 | 0.0016418 | 85.1337
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CUTOUT | 35 | 2096 | 144443 | 0.026338 | 0.00038219 | 68.9136
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | NONE | 123 | 15759 | 749559 | 0.13668 | 0.0028735 | 47.5639
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | NONE | 46 | 111 | 10653 | 0.0019425 | 2.024e-05 | 95.973
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 4 | 27 | 3303 | 0.00060228 | 4.9232e-06 | 122.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 22 | 4620 | 0.00084242 | 4.0115e-06 | 210
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 28 | 3824 | 293434 | 0.053505 | 0.00069728 | 76.7348
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | POLE | 2 | 909 | 172606 | 0.031473 | 0.00016575 | 189.8856
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 1 | 14 | 19390 | 0.0035356 | 2.5528e-06 | 1385
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | POLE | 3 | 298 | 98348 | 0.017933 | 5.4338e-05 | 330.0268
AEP Total | 2020 | 5484199 | PARTIAL POWER | UG | NONE | 3 | 3 | 798 | 0.00014551 | 5.4703e-07 | 266
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | JUMPER/RISER | 9 | 56 | 5070 | 0.00092447 | 1.0211e-05 | 90.5357
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 22 | 1156 | 0.00021079 | 4.0115e-06 | 52.5455
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, UG | 2 | 3 | 437 | 7.9683e-05 | 5.4703e-07 | 145.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 9 | 26 | 3659 | 0.00066719 | 4.7409e-06 | 140.7308
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 191 | 53237 | 0.0097073 | 3.4827e-05 | 278.7277
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 4 | 436 | 7.9501e-05 | 7.2937e-07 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | WU | NONE | 2 | 882 | 257544 | 0.046961 | 0.00016083 | 292
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONN/CLAMP | 5 | 68 | 96753 | 0.017353 | 1.2196e-05 | 1422.8382
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 2 | 457 | 8.1963e-05 | 3.587e-07 | 228.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | INSULATOR | 11 | 134 | 4637 | 0.00083165 | 2.4033e-05 | 34.6045
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | NONE | 15 | 60 | 11901 | 0.0021344 | 1.0761e-05 | 198.35
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 155 | 8370 | 0.0015072 | 2.7911e-05 | 54
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | METERING | 4 | 9 | 831 | 0.00014964 | 1.6206e-06 | 92.3333
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | POLE | 1 | 1 | 192 | 3.4574e-05 | 1.8007e-07 | 192
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | METERING | 1 | 21 | 210 | 3.7664e-05 | 3.7664e-06 | 10
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 3 | 1773 | 0.00031799 | 5.3805e-07 | 591
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 4 | 777 | 0.00013992 | 7.2029e-07 | 194.25
AEP Total | 2025 | 5615460 | PARTIAL POWER | WL | NONE | 1 | 1 | 195 | 3.4726e-05 | 1.7808e-07 | 195
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 496 | 8.8328e-05 | 3.5616e-07 | 248
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 902 | 15858 | 2313759 | 0.4189 | 0.002871 | 145.9048
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 266 | 385 | 84314 | 0.015265 | 6.9703e-05 | 218.9974
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 37 | 410 | 65963 | 0.011942 | 7.4229e-05 | 160.8854
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 116 | 1887 | 589909 | 0.1068 | 0.00034163 | 312.6174
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | NONE | 24 | 14322 | 1335282 | 0.24175 | 0.0025929 | 93.2329
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CROSSARM | 335 | 11334 | 798335 | 0.14454 | 0.002052 | 70.4372
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | NONE | 14 | 2105 | 247593 | 0.044826 | 0.0003811 | 117.6214
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | ARRESTER | 172 | 9875 | 1029969 | 0.18647 | 0.0017878 | 104.3007
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | NONE | 39 | 2338 | 386470 | 0.069969 | 0.00042329 | 165.2994
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 3 | 258 | 4.671e-05 | 5.4314e-07 | 86
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | POLE | 2 | 3 | 394 | 7.1332e-05 | 5.4314e-07 | 131.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CUTOUT | 7 | 64 | 11355 | 0.0020558 | 1.1587e-05 | 177.4219
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 29 | 23646 | 0.004281 | 5.2503e-06 | 815.3793
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | NONE | 43 | 4017 | 1328031 | 0.24044 | 0.00072726 | 330.6027
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | OL | NONE | 9 | 8817 | 635607 | 0.11445 | 0.0015877 | 72.0888
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 96 | 16636 | 1591318 | 0.28655 | 0.0029957 | 95.6551
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CUTOUT | 72 | 1290 | 168871 | 0.030409 | 0.00023229 | 130.9078
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE | 502 | 91853 | 16569099 | 2.9836 | 0.01654 | 180.3871
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | POLE | 3 | 117 | 43007 | 0.0077444 | 2.1068e-05 | 367.5812
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CROSSARM | 18 | 7962 | 697766 | 0.12565 | 0.0014337 | 87.637
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | NONE | 42 | 3935 | 340673 | 0.061346 | 0.00070858 | 86.5751
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | NONE | 82 | 19683 | 923111 | 0.16623 | 0.0035444 | 46.8989
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | FUSE | 44 | 383 | 29915 | 0.0053869 | 6.8968e-05 | 78.107
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 9 | 27 | 5111 | 0.00092035 | 4.8619e-06 | 189.2963
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CUTOUT | 6 | 36 | 8389 | 0.0015106 | 6.4826e-06 | 233.0278
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 27 | 5916 | 814835 | 0.14673 | 0.0010653 | 137.7341
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | POLE | 4 | 4072 | 622757 | 0.11214 | 0.00073325 | 152.9364
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | METERING | 32 | 41 | 7066 | 0.0012724 | 7.3829e-06 | 172.3415
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | POLE | 2903 | 24428 | 3480290 | 0.62419 | 0.0043812 | 142.4713
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONN/CLAMP | 675 | 2045 | 248578 | 0.044583 | 0.00036677 | 121.554
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | NONE | 2532 | 98463 | 9835583 | 1.764 | 0.017659 | 99.8912
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | ARRESTER | 132 | 13100 | 1048672 | 0.18808 | 0.0023495 | 80.0513
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, UG | 6 | 3551 | 307397 | 0.055132 | 0.00063687 | 86.5663
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 207 | 1666 | 132497 | 0.023763 | 0.0002988 | 79.53
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONN/CLAMP | 4 | 39 | 3457 | 0.00063036 | 7.1113e-06 | 88.641
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 5 | 550 | 0.00010029 | 9.1171e-07 | 110
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 10 | 965 | 0.00017596 | 1.8234e-06 | 96.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 2 | 2438 | 0.00044455 | 3.6468e-07 | 1219
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 2 | 1796 | 371392 | 0.06772 | 0.00032749 | 206.7884
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONN/CLAMP | 4 | 30 | 2751 | 0.00050162 | 5.4703e-06 | 91.7
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | SPLICE, OH | 1 | 1 | 94 | 1.714e-05 | 1.8234e-07 | 94
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERO | CONDUCTOR UG | 1 | 1 | 132 | 2.3898e-05 | 1.8105e-07 | 132
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 1 | 1 | 193 | 3.4942e-05 | 1.8105e-07 | 193
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 33 | 4704 | 0.00085164 | 5.9745e-06 | 142.5455
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CUTOUT | 2 | 6 | 1448 | 0.00026216 | 1.0863e-06 | 241.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONDUCTOR UG | 1 | 5 | 540 | 9.7765e-05 | 9.0523e-07 | 108
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 2 | 212 | 3.8657e-05 | 3.6468e-07 | 106
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CUTOUT | 2 | 100 | 10095 | 0.0017977 | 1.7808e-05 | 100.95
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 10 | 59 | 52829 | 0.0094078 | 1.0507e-05 | 895.4068
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 116 | 1187 | 209554 | 0.037317 | 0.00021138 | 176.5409
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | FUSE | 3 | 7 | 5292 | 0.00095294 | 1.2605e-06 | 756
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 5 | 3566 | 0.00064214 | 9.0036e-07 | 713.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 9 | 32 | 10354 | 0.0018438 | 5.6986e-06 | 323.5625
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AB | NONE | 20 | 14003 | 1505753 | 0.26814 | 0.0024937 | 107.5307
AEP Total | 2024 | 5615460 | PARTIAL POWER | UG | NONE | 14 | 35 | 5659 | 0.0010078 | 6.2328e-06 | 161.6857
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | SCO | REGULATOR | 2 | 2418 | 31434 | 0.0055978 | 0.0004306 | 13
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 8 | 7323 | 805885 | 0.14351 | 0.0013041 | 110.0485
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 7 | 43 | 47236 | 0.0084118 | 7.6574e-06 | 1098.5116
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | SPLICE, OH | 1 | 1 | 61 | 1.0863e-05 | 1.7808e-07 | 61
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | POLE | 1 | 2 | 478 | 8.5122e-05 | 3.5616e-07 | 239
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | METERING | 1 | 1 | 343 | 6.1081e-05 | 1.7808e-07 | 343
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | REGULATOR | 1 | 106 | 2968 | 0.00052854 | 1.8876e-05 | 28
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | FUSE | 9 | 25 | 1590 | 0.00028315 | 4.452e-06 | 63.6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, GROUNDING | 1 | 265 | 50155 | 0.0089316 | 4.7191e-05 | 189.2642
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 10 | 6010 | 0.0010779 | 1.7935e-06 | 601
AEP Total | 2024 | 5615460 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 1 | 1 | 129 | 2.2972e-05 | 1.7808e-07 | 129
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | SPLICE, OH | 1 | 1 | 1001 | 0.00017826 | 1.7808e-07 | 1001
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 1 | 36 | 6.4109e-06 | 1.7808e-07 | 36
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | POLE | 1 | 149 | 21456 | 0.0038209 | 2.6534e-05 | 144
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | PEDESTAL | 1 | 9 | 342 | 6.0903e-05 | 1.6027e-06 | 38
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 5 | 98 | 24800 | 0.0044164 | 1.7452e-05 | 253.0612
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | CUTOUT | 2 | 388 | 58497 | 0.010417 | 6.9095e-05 | 150.7655
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1 | 40 | 7.1232e-06 | 1.7808e-07 | 40
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 33 | 547 | 9.741e-05 | 5.8766e-06 | 16.5758
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, OH | 2 | 11 | 583 | 0.00010382 | 1.9589e-06 | 53
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 1 | 646 | 0.00011504 | 1.7808e-07 | 646
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 3 | 239 | 62015 | 0.011044 | 4.2561e-05 | 259.477
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 34 | 7140 | 0.0012715 | 6.0547e-06 | 210
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | FUSE | 1 | 8 | 1232 | 0.00021939 | 1.4246e-06 | 154
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | POLE | 1 | 1 | 27 | 4.8082e-06 | 1.7808e-07 | 27
AEP Total | 2025 | 5615460 | PARTIAL POWER | VA | POLE | 1 | 15 | 1425 | 0.00025376 | 2.6712e-06 | 95
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 1 | 279 | 5.0873e-05 | 1.8234e-07 | 279
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 28 | 3308 | 0.00060319 | 5.1056e-06 | 118.1429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 1 | 240 | 4.3762e-05 | 1.8234e-07 | 240
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 1697 | 130669 | 0.02353 | 0.00030558 | 77
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 1 | 368 | 6.7102e-05 | 1.8234e-07 | 368
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | ARRESTER | 1 | 1 | 85 | 1.5499e-05 | 1.8234e-07 | 85
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | CROSSARM | 1 | 674 | 217826 | 0.039719 | 0.0001229 | 323.184
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 200 | 3.6014e-05 | 1.8007e-07 | 200
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | FUSE | 1 | 4 | 452 | 8.1833e-05 | 7.2419e-07 | 113
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | JUMPER/RISER | 3 | 6264 | 1401965 | 0.25564 | 0.0011422 | 223.8131
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CUTOUT | 8 | 116 | 13943 | 0.0025424 | 2.1152e-05 | 120.1983
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | METERING | 4 | 10 | 1453 | 0.00026494 | 1.8234e-06 | 145.3
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | POLE | 3 | 7 | 2570 | 0.00046862 | 1.2764e-06 | 367.1429
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | POLE | 1 | 188 | 226164 | 0.040563 | 3.3718e-05 | 1203
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE HARDWARE | 9 | 737 | 157045 | 0.028166 | 0.00013218 | 213.0868
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 6 | 5845 | 3803444 | 0.68215 | 0.0010483 | 650.7175
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 5 | 115 | 31277 | 0.0056095 | 2.0625e-05 | 271.9739
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | INSULATOR | 3 | 2075 | 292217 | 0.052409 | 0.00037215 | 140.8275
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 10 | 1330 | 0.00023854 | 1.7935e-06 | 133
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | SPLICE, UG | 2 | 3 | 1200 | 0.00021522 | 5.3805e-07 | 400
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | FUSE | 2 | 24 | 2497 | 0.00044784 | 4.3044e-06 | 104.0417
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | METERING | 33 | 49 | 4979 | 0.00088666 | 8.7259e-06 | 101.6122
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE | 484 | 75491 | 14740408 | 2.625 | 0.013443 | 195.2605
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 193 | 3314 | 650333 | 0.11581 | 0.00059016 | 196.2381
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 34 | 421 | 100645 | 0.017923 | 7.4972e-05 | 239.0618
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 151 | 1288 | 100373 | 0.017874 | 0.00022937 | 77.9293
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 150 | 6496 | 800344 | 0.14253 | 0.0011568 | 123.2057
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 1 | 203 | 3.6408e-05 | 1.7935e-07 | 203
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ERF | TRANSFORMER, GROUNDING | 3 | 2501 | 323376 | 0.057587 | 0.00044538 | 129.2987
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 4 | 396 | 60864 | 0.010839 | 7.052e-05 | 153.697
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | OTHER EQUIPMENT | 1 | 53 | 30793 | 0.0055227 | 9.5056e-06 | 581
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 1 | 2 | 352 | 6.3131e-05 | 3.587e-07 | 176
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 11 | 1984 | 54311 | 0.0096717 | 0.00035331 | 27.3745
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | METERING | 5 | 5 | 351 | 6.2952e-05 | 8.9675e-07 | 70.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 93 | 1.6561e-05 | 1.7808e-07 | 93
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | ARRESTER | 3 | 2082 | 282143 | 0.051081 | 0.00037694 | 135.5154
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | METERING | 4 | 256 | 19223 | 0.0034615 | 4.6098e-05 | 75.0898
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 274 | 439 | 77041 | 0.013719 | 7.8177e-05 | 175.492
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CROSSARM | 174 | 3310 | 298326 | 0.053126 | 0.00058944 | 90.1287
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 610 | 0.0001094 | 1.7935e-07 | 610
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 5 | 23 | 2705 | 0.00048514 | 4.1251e-06 | 117.6087
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | METERING | 1 | 2 | 143 | 2.5465e-05 | 3.5616e-07 | 71.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 1 | 120 | 2.1726e-05 | 1.8105e-07 | 120
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 36 | 7289 | 0.0013291 | 6.5643e-06 | 202.4722
AEP Total | 2024 | 5615460 | PARTIAL POWER | FW | CONDUCTOR UG | 1 | 1 | 73 | 1.3e-05 | 1.7808e-07 | 73
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 2 | 162 | 2.8849e-05 | 3.5616e-07 | 81
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CUTOUT | 1 | 5 | 15120 | 0.0026926 | 8.904e-07 | 3024
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 30 | 75 | 20098 | 0.0036387 | 1.3578e-05 | 267.9733
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CUTOUT | 2 | 69 | 3849 | 0.00069685 | 1.2492e-05 | 55.7826
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, OH | 33 | 5870 | 728412 | 0.13188 | 0.0010627 | 124.0906
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | NONE | 5 | 16 | 968 | 0.00017525 | 2.8967e-06 | 60.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CUTOUT | 11 | 876 | 138516 | 0.025078 | 0.0001586 | 158.1233
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 17 | 138 | 15276 | 0.0027657 | 2.4984e-05 | 110.6957
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 6 | 529 | 9.5774e-05 | 1.0863e-06 | 88.1667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | INSULATOR | 4 | 2201 | 220095 | 0.039847 | 0.00039848 | 99.9977
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 2 | 6 | 96 | 1.738e-05 | 1.0863e-06 | 16
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 2 | 196 | 3.5485e-05 | 3.6209e-07 | 98
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 13 | 6361 | 0.0011516 | 2.3536e-06 | 489.3077
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | FUSE | 10 | 2645 | 79265 | 0.014351 | 0.00047887 | 29.9679
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 1773 | 19947 | 2180606 | 0.39267 | 0.0035919 | 109.32
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | NONE | 1775 | 27092 | 2432058 | 0.43795 | 0.0048785 | 89.7703
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | POLE | 5 | 1136 | 1205449 | 0.21824 | 0.00020567 | 1061.1347
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 1 | 1 | 123 | 2.2269e-05 | 1.8105e-07 | 123
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 4 | 3572 | 0.0006467 | 7.2419e-07 | 893
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | NONE | 1449 | 35311 | 2739307 | 0.49949 | 0.0064387 | 77.5766
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONN/CLAMP | 813 | 2202 | 270970 | 0.049409 | 0.00040152 | 123.0563
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 825 | 60326 | 9908170 | 1.8067 | 0.011 | 164.2438
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | FUSE | 526 | 4140 | 411521 | 0.075038 | 0.0007549 | 99.4012
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONN/CLAMP | 28 | 548 | 44622 | 0.0081365 | 9.9923e-05 | 81.427
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 927 | 75602 | 0.013785 | 0.00016903 | 81.5556
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | NONE | 352 | 8970 | 1247386 | 0.22745 | 0.0016356 | 139.062
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | POLE | 23 | 1472 | 624065 | 0.11379 | 0.00026841 | 423.9572
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | FUSE | 22 | 515 | 84791 | 0.015268 | 9.2737e-05 | 164.6427
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 16 | 396 | 99362 | 0.017892 | 7.1308e-05 | 250.9141
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | ARRESTER | 2 | 15 | 1076 | 0.00019376 | 2.7011e-06 | 71.7333
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | NONE | 10 | 17 | 2018 | 0.00036339 | 3.0612e-06 | 118.7059
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 25 | 130 | 30315 | 0.0054589 | 2.3409e-05 | 233.1923
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 9 | 4936 | 162172 | 0.029203 | 0.00088883 | 32.8549
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | NONE | 459 | 23867 | 3706435 | 0.66475 | 0.0042806 | 155.2954
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 22 | 3238 | 0.00058307 | 3.9616e-06 | 147.1818
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 27 | 112 | 36541 | 0.0065536 | 2.0087e-05 | 326.2589
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | PEDESTAL | 18 | 95 | 8634 | 0.0015547 | 1.7107e-05 | 90.8842
AEP Total | 2023 | 5575683 | PARTIAL POWER | UG | NONE | 26 | 59 | 11434 | 0.0020507 | 1.0582e-05 | 193.7966
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | SPLICE, OH | 4 | 4 | 379 | 6.8247e-05 | 7.2029e-07 | 94.75
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 5 | 5 | 608 | 0.00010948 | 9.0036e-07 | 121.6
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR UG | 6 | 6 | 1812 | 0.00032629 | 1.0804e-06 | 302
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 13 | 6623 | 1844216 | 0.33209 | 0.0011926 | 278.4563
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 11 | 27 | 2785 | 0.00049949 | 4.8425e-06 | 103.1481
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | NONE | 44 | 87 | 7004 | 0.0012562 | 1.5603e-05 | 80.5057
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 4 | 560 | 24636 | 0.0044185 | 0.00010044 | 43.9929
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | NONE | 3 | 11 | 2028 | 0.00036519 | 1.9808e-06 | 184.3636
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 15 | 476 | 88077 | 0.015797 | 8.5371e-05 | 185.0357
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | OTHER EQUIPMENT | 1 | 1369 | 157435 | 0.02835 | 0.00024652 | 115
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 6 | 399 | 61505 | 0.011031 | 7.1561e-05 | 154.1479
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 13 | 937 | 311597 | 0.055885 | 0.00016805 | 332.5475
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CAPACITOR | 6 | 5367 | 189174 | 0.034494 | 0.00097863 | 35.2476
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | NONE | 77 | 739 | 82532 | 0.015049 | 0.00013475 | 111.6806
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 25 | 333 | 38144 | 0.0069553 | 6.072e-05 | 114.5465
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 86 | 2222 | 0.00040516 | 1.5681e-05 | 25.8372
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | NONE | 12 | 3461 | 760045 | 0.13859 | 0.00063109 | 219.6027
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 6990 | 150838 | 0.027504 | 0.0012746 | 21.5791
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CUTOUT | 1 | 3 | 396 | 7.2207e-05 | 5.4703e-07 | 132
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CUTOUT | 8 | 91 | 7274 | 0.0013264 | 1.6593e-05 | 79.9341
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 75 | 1.3356e-05 | 1.7808e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE | 2 | 25 | 12688 | 0.0022848 | 4.5018e-06 | 507.52
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | PEDESTAL | 1 | 5 | 475 | 8.6612e-05 | 9.1171e-07 | 95
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | OTHER EQUIPMENT | 1 | 589 | 114058 | 0.020456 | 0.00010564 | 193.6469
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | ARRESTER | 2 | 3 | 364 | 6.5283e-05 | 5.3805e-07 | 121.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 1 | 381 | 6.8332e-05 | 1.7935e-07 | 381
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | FUSE | 1 | 96 | 11136 | 0.0019831 | 1.7096e-05 | 116
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | NONE | 1 | 35 | 5040 | 0.00089752 | 6.2328e-06 | 144
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | PEDESTAL | 1 | 26 | 2470 | 0.00044478 | 4.6819e-06 | 95
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | FUSE | 2 | 514 | 28784 | 0.0051832 | 9.2557e-05 | 56
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONN/CLAMP | 1 | 1 | 101 | 1.8417e-05 | 1.8234e-07 | 101
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONN/CLAMP | 2 | 2 | 209 | 3.7484e-05 | 3.587e-07 | 104.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 9 | 270 | 4.8425e-05 | 1.6142e-06 | 30
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 17 | 23153 | 0.0041525 | 3.049e-06 | 1361.9412
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 972 | 0.00017309 | 3.5616e-07 | 486
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 3 | 231 | 4.1136e-05 | 5.3424e-07 | 77
AEP Total | 2024 | 5615460 | PARTIAL POWER | CE | NONE | 1 | 2 | 84 | 1.4959e-05 | 3.5616e-07 | 42
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WL | BREAKER | 1 | 1527 | 241266 | 0.042965 | 0.00027193 | 158
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | SPLICE, OH | 2 | 2 | 323 | 5.752e-05 | 3.5616e-07 | 161.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR UG | 1 | 1 | 129 | 2.3229e-05 | 1.8007e-07 | 129
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | BREAKER | 1 | 905 | 199100 | 0.035852 | 0.00016297 | 220
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | FUSE | 4 | 30 | 691 | 0.00012305 | 5.3424e-06 | 23.0333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | SPLICE, OH | 5 | 14 | 10111 | 0.0018006 | 2.4931e-06 | 722.2143
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 1232 | 141202 | 0.025145 | 0.00021939 | 114.612
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 3 | 12 | 4679 | 0.00083324 | 2.137e-06 | 389.9167
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | NONE | 1 | 2 | 290 | 5.1643e-05 | 3.5616e-07 | 145
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 2 | 774 | 13147 | 0.0023412 | 0.00013783 | 16.9858
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 1 | 94 | 1.674e-05 | 1.7808e-07 | 94
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 1 | 232 | 4.1609e-05 | 1.7935e-07 | 232
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 2 | 228 | 4.1056e-05 | 3.6014e-07 | 114
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 75 | 1.3356e-05 | 1.7808e-07 | 75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | GUY/ANCHOR | 1 | 450 | 46220 | 0.0082308 | 8.0136e-05 | 102.7111
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 13 | 912 | 0.00016357 | 2.3316e-06 | 70.1538
AEP Total | 2023 | 5575683 | PARTIAL POWER | V | CONN/CLAMP | 2 | 2 | 176 | 3.1566e-05 | 3.587e-07 | 88
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | POLE | 4 | 4 | 1642 | 0.00029568 | 7.2029e-07 | 410.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | FUSE | 1 | 11 | 1386 | 0.00025093 | 1.9915e-06 | 126
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | UG | NONE | 1 | 7 | 1092 | 0.00019585 | 1.2555e-06 | 156
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 1 | 2 | 2480 | 0.00044899 | 3.6209e-07 | 1240
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 2 | 4 | 1978 | 0.00036067 | 7.2937e-07 | 494.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 40 | 4400 | 0.0008023 | 7.2937e-06 | 110
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 354 | 97470 | 0.017773 | 6.4549e-05 | 275.339
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | TRANSFORMER, GROUNDING | 1 | 153 | 1071 | 0.00019529 | 2.7898e-05 | 7
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 28 | 5.0693e-06 | 1.8105e-07 | 28
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 182 | 729 | 69095 | 0.012304 | 0.00012982 | 94.7805
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 269 | 594 | 62351 | 0.011103 | 0.00010578 | 104.968
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 5 | 14 | 4547 | 0.00080973 | 2.4931e-06 | 324.7857
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | NONE | 24 | 87 | 11449 | 0.0020388 | 1.5493e-05 | 131.5977
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 6 | 23 | 4636 | 0.00083481 | 4.1417e-06 | 201.5652
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 4 | 5 | 6072 | 0.0010934 | 9.0036e-07 | 1214.4
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 12 | 251 | 15183 | 0.0027038 | 4.4698e-05 | 60.49
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | U | NONE | 10 | 5331 | 826183 | 0.14713 | 0.00094934 | 154.9771
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 5 | 3020 | 423022 | 0.075332 | 0.0005378 | 140.0735
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 80 | 4880 | 0.00086903 | 1.4246e-05 | 61
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | TRANSFORMER, OH | 1 | 3859 | 1134349 | 0.202 | 0.00068721 | 293.949
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | PEDESTAL | 4 | 1680 | 184461 | 0.032849 | 0.00029917 | 109.7982
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CUTOUT | 3 | 96 | 2032 | 0.00036186 | 1.7096e-05 | 21.1667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | SPLICE, UG | 1 | 7 | 105 | 1.901e-05 | 1.2673e-06 | 15
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1345 | 181501 | 0.032322 | 0.00023952 | 134.945
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | SWITCH, UG | 1 | 1159 | 158783 | 0.028276 | 0.00020639 | 137
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CUTOUT | 4 | 3440 | 633620 | 0.1141 | 0.00061945 | 184.1919
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 4 | 404 | 7.2749e-05 | 7.2029e-07 | 101
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | PEDESTAL | 1 | 1 | 76 | 1.3685e-05 | 1.8007e-07 | 76
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | REGULATOR | 11 | 2683 | 222759 | 0.04033 | 0.00048575 | 83.0261
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 733 | 63345 | 8580708 | 1.5535 | 0.011468 | 135.4599
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 13 | 6433 | 368351 | 0.066689 | 0.0011647 | 57.2596
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 47 | 3437 | 823143 | 0.14903 | 0.00062226 | 239.4946
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 29 | 739 | 162853 | 0.029484 | 0.00013379 | 220.3694
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 3 | 11 | 1273 | 0.00023047 | 1.9915e-06 | 115.7273
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | FUSE | 2 | 16 | 2015 | 0.00036481 | 2.8967e-06 | 125.9375
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | JUMPER/RISER | 6 | 63 | 12450 | 0.002254 | 1.1406e-05 | 197.619
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 17 | 384 | 113545 | 0.020557 | 6.9522e-05 | 295.6901
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | NONE | 9 | 9377 | 1162023 | 0.21038 | 0.0016977 | 123.9227
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | SPLICE, OH | 8 | 15 | 2050 | 0.00036767 | 2.6903e-06 | 136.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | POLE | 8 | 438 | 67522 | 0.01211 | 7.8555e-05 | 154.1598
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | FUSE | 9 | 32 | 3261 | 0.00058486 | 5.7392e-06 | 101.9062
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1184 | 105304 | 0.018886 | 0.00021235 | 88.9392
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 1 | 279 | 5.024e-05 | 1.8007e-07 | 279
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 697 | 43653 | 5940537 | 1.0579 | 0.0077737 | 136.0854
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | NONE | 571 | 44069 | 7105247 | 1.2653 | 0.0078478 | 161.23
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 74 | 6803 | 750914 | 0.13372 | 0.0012115 | 110.3798
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 6 | 16 | 6227 | 0.0011089 | 2.8493e-06 | 389.1875
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 20 | 3010 | 339397 | 0.06044 | 0.00053602 | 112.7565
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE | 19 | 3854 | 1945454 | 0.34645 | 0.00068632 | 504.7883
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 90 | 1.6142e-05 | 1.7935e-07 | 90
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 1 | 1020 | 0.00018294 | 1.7935e-07 | 1020
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 2 | 134 | 2.4033e-05 | 3.587e-07 | 67
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | METERING | 2 | 2 | 158 | 2.8337e-05 | 3.587e-07 | 79
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | METERING | 1 | 1 | 41 | 7.3534e-06 | 1.7935e-07 | 41
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | JUMPER/RISER | 1 | 449 | 2694 | 0.00048317 | 8.0528e-05 | 6
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | SPLICE, OH | 1 | 0 | 0 | 0 | 0
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | PEDESTAL | 22 | 104 | 8055 | 0.0014344 | 1.852e-05 | 77.4519
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 753 | 166479 | 0.029647 | 0.00013409 | 221.0876
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 61 | 1233 | 805523 | 0.14345 | 0.00021957 | 653.3033
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 22 | 1547 | 0.00027549 | 3.9178e-06 | 70.3182
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | SCO | REGULATOR | 1 | 1900 | 62700 | 0.011166 | 0.00033835 | 33
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | NONE | 26 | 252 | 39037 | 0.0069517 | 4.4876e-05 | 154.9087
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 72 | 1.2913e-05 | 1.7935e-07 | 72
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | NONE | 3 | 13 | 2414 | 0.00042988 | 2.315e-06 | 185.6923
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 6 | 17 | 16831 | 0.0029973 | 3.0274e-06 | 990.0588
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | INSULATOR | 4 | 212 | 52760 | 0.0093955 | 3.7753e-05 | 248.8679
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | FUSE | 3 | 4 | 291 | 5.1821e-05 | 7.1232e-07 | 72.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | ARRESTER | 2 | 13 | 1573 | 0.00028212 | 2.3316e-06 | 121
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 245 | 1960 | 0.00035485 | 4.4356e-05 | 8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | SPLICE, UG | 1 | 10 | 3430 | 0.00061517 | 1.7935e-06 | 343
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | TRANSFORMER, OH | 1 | 1 | 312 | 5.5957e-05 | 1.7935e-07 | 312
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 98 | 1.787e-05 | 1.8234e-07 | 98
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, UG | 2 | 1987 | 429054 | 0.078235 | 0.00036231 | 215.9305
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 57 | 47475 | 0.0086567 | 1.0393e-05 | 832.8947
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | SWITCH, OH | 2 | 3454 | 209044 | 0.038118 | 0.00062981 | 60.5223
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 31 | 5.6124e-06 | 1.8105e-07 | 31
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | CONDUCTOR UG | 1 | 1 | 176 | 3.1693e-05 | 1.8007e-07 | 176
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | FW | NONE | 2 | 1732 | 137493 | 0.024485 | 0.00030843 | 79.3839
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 11 | 219 | 26783 | 0.0047695 | 3.8999e-05 | 122.2968
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 14 | 98 | 40100 | 0.007141 | 1.7452e-05 | 409.1837
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 51 | 4887 | 697922 | 0.12429 | 0.00087028 | 142.812
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | FUSE | 11 | 79 | 10139 | 0.0018056 | 1.4068e-05 | 128.3418
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | SWITCH, OH | 2 | 955 | 72170 | 0.012852 | 0.00017007 | 75.5707
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | SCO | NONE | 18 | 11172 | 2011795 | 0.35826 | 0.0019895 | 180.0747
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | NETWORK TRANSFORMER | 1 | 2 | 169 | 3.0095e-05 | 3.5616e-07 | 84.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 2 | 142 | 2.5287e-05 | 3.5616e-07 | 71
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | POLE | 1 | 3 | 1176 | 0.00020942 | 5.3424e-07 | 392
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | POLE | 5 | 519 | 35071 | 0.0062454 | 9.2423e-05 | 67.5742
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 5 | 18 | 8254 | 0.0014699 | 3.2054e-06 | 458.5556
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 118 | 2.1013e-05 | 3.5616e-07 | 59
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CABLE TERMINATOR | 2 | 4 | 412 | 7.3369e-05 | 7.1232e-07 | 103
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 1 | 131 | 2.3328e-05 | 1.7808e-07 | 131
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UG | NONE | 9 | 666 | 209565 | 0.037319 | 0.0001186 | 314.6622
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | FO | NONE | 4 | 3696 | 2071972 | 0.36898 | 0.00065818 | 560.5985
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 1 | 5 | 385 | 6.8561e-05 | 8.904e-07 | 77
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 2521 | 249159 | 0.04437 | 0.00044894 | 98.8334
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | INSULATOR | 3 | 501 | 110533 | 0.019684 | 8.9218e-05 | 220.6248
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CROSSARM | 4 | 1436 | 396106 | 0.071714 | 0.00025998 | 275.8398
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | CUTOUT | 1 | 9 | 909 | 0.00016457 | 1.6294e-06 | 101
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | POLE | 2 | 794 | 459488 | 0.083189 | 0.00014375 | 578.7003
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CIRCUIT SWITCHER | 1 | 11 | 1232 | 0.00022305 | 1.9915e-06 | 112
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | NETWORK TRANSFORMER | 3 | 18 | 1192 | 0.00021465 | 3.2413e-06 | 66.2222
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | METERING | 23 | 93 | 10620 | 0.0019124 | 1.6747e-05 | 114.1935
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CROSSARM | 1 | 9 | 1242 | 0.00022365 | 1.6206e-06 | 138
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CROSSARM | 26 | 12071 | 1312012 | 0.23531 | 0.0021649 | 108.6912
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | FUSE | 20 | 103 | 12331 | 0.0022205 | 1.8547e-05 | 119.7184
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | FUSE | 457 | 4847 | 501706 | 0.089981 | 0.00086931 | 103.5086
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | BREAKER | 6 | 5113 | 703070 | 0.1266 | 0.00092071 | 137.5064
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | FUSE | 7 | 81 | 11853 | 0.0021344 | 1.4586e-05 | 146.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | FUSE | 233 | 4135 | 343415 | 0.061592 | 0.00074161 | 83.0508
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CABLE TERMINATOR | 1 | 3 | 105 | 1.8908e-05 | 5.4022e-07 | 35
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CROSSARM | 65 | 14585 | 4345786 | 0.77942 | 0.0026158 | 297.9627
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | FUSE | 4 | 13 | 1702 | 0.00030648 | 2.3409e-06 | 130.9231
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | METERING | 29 | 37 | 3407 | 0.00061105 | 6.636e-06 | 92.0811
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 5 | 43 | 4815 | 0.00086357 | 7.7121e-06 | 111.9767
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CROSSARM | 101 | 37540 | 3766233 | 0.68674 | 0.0068451 | 100.3259
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 10 | 32 | 4093 | 0.00074633 | 5.8349e-06 | 127.9062
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | PEDESTAL | 39 | 208 | 16142 | 0.0029434 | 3.7927e-05 | 77.6058
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 33 | 470 | 31025 | 0.0056572 | 8.5701e-05 | 66.0106
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 2097 | 18549 | 1850011 | 0.33733 | 0.0033823 | 99.7364
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR UG | 532 | 922 | 204034 | 0.037204 | 0.00016812 | 221.295
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | INSULATOR | 2 | 1056 | 205644 | 0.037498 | 0.00019255 | 194.7386
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | POLE | 5 | 488 | 121401 | 0.022137 | 8.8983e-05 | 248.7725
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 20 | 2086 | 150323 | 0.02741 | 0.00038037 | 72.0628
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 13 | 387 | 50581 | 0.009223 | 7.0566e-05 | 130.7003
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 78 | 4914 | 0.00089603 | 1.4223e-05 | 63
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CUTOUT | 37 | 2107 | 399827 | 0.072905 | 0.00038419 | 189.7613
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | METERING | 10 | 15 | 1171 | 0.00021352 | 2.7351e-06 | 78.0667
AEP Total | 2020 | 5484199 | PARTIAL POWER | V | CIRCUIT SWITCHER | 1 | 1 | 114 | 2.0787e-05 | 1.8234e-07 | 114
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CUTOUT | 11 | 213 | 31576 | 0.0057576 | 3.8839e-05 | 148.2441
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | NONE | 15 | 66 | 18624 | 0.0033959 | 1.2035e-05 | 282.1818
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 5 | 26 | 3783 | 0.0006898 | 4.7409e-06 | 145.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | FUSE | 1 | 1 | 104 | 1.8964e-05 | 1.8234e-07 | 104
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CUTOUT | 10 | 671 | 53668 | 0.0097859 | 0.00012235 | 79.9821
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | NONE | 16 | 91 | 9460 | 0.001725 | 1.6593e-05 | 103.956
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 12 | 159 | 83716 | 0.015265 | 2.8992e-05 | 526.5157
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 735 | 171255 | 0.031227 | 0.00013402 | 233
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 120 | 14352 | 0.002617 | 2.1881e-05 | 119.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 4 | 26 | 3323 | 0.00060592 | 4.7409e-06 | 127.8077
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | ARRESTER | 1 | 1 | 19 | 3.4077e-06 | 1.7935e-07 | 19
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | METERING | 1 | 81 | 6318 | 0.0011331 | 1.4527e-05 | 78
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | ARRESTER | 10 | 760 | 58965 | 0.010618 | 0.00013685 | 77.5855
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SPLICE, UG | 1 | 1 | 15 | 2.7011e-06 | 1.8007e-07 | 15
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 2626 | 123587 | 0.022165 | 0.00047097 | 47.0628
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | SCO | NONE | 28 | 9844 | 953867 | 0.17108 | 0.0017655 | 96.8983
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 5 | 18 | 2862 | 0.0005133 | 3.2283e-06 | 159
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 831 | 34018 | 3260866 | 0.58069 | 0.0060579 | 95.8571
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 674 | 1999 | 244989 | 0.043628 | 0.00035598 | 122.5558
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | GUY/ANCHOR | 3 | 2922 | 322944 | 0.05751 | 0.00052035 | 110.5216
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 423 | 6177 | 602098 | 0.10722 | 0.0011 | 97.4742
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 146 | 800 | 69594 | 0.012393 | 0.00014246 | 86.9925
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | POLE | 9 | 1472 | 289094 | 0.051482 | 0.00026213 | 196.3954
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | FUSE | 3 | 2206 | 246363 | 0.044922 | 0.00040225 | 111.6786
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 1 | 106 | 1.9328e-05 | 1.8234e-07 | 106
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 15 | 671 | 62913 | 0.011472 | 0.00012235 | 93.7601
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | NONE | 9 | 46 | 20394 | 0.0037187 | 8.3877e-06 | 443.3478
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | NONE | 10 | 380 | 22367 | 0.0040784 | 6.929e-05 | 58.8605
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 13 | 2759 | 969911 | 0.17686 | 0.00050308 | 351.5444
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | SWITCH, OH | 1 | 946 | 232338 | 0.042365 | 0.0001725 | 245.6004
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 2 | 166 | 3.0269e-05 | 3.6468e-07 | 83
AEP Total | 2024 | 5615460 | PARTIAL POWER | UG | CONDUCTOR UG | 68 | 141 | 22659 | 0.0040351 | 2.5109e-05 | 160.7021
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CAPACITOR | 1 | 2510 | 238450 | 0.042766 | 0.00045017 | 95
AEP Total | 2023 | 5575683 | PARTIAL POWER | OU | NONE | 1 | 1 | 115 | 2.0625e-05 | 1.7935e-07 | 115
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 13 | 930 | 122631 | 0.021994 | 0.0001668 | 131.8613
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, UG | 6 | 10 | 3190 | 0.00057213 | 1.7935e-06 | 319
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 454 | 81534 | 0.014682 | 8.1753e-05 | 179.5903
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | NONE | 1 | 1 | 2380 | 0.00043089 | 1.8105e-07 | 2380
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | POLE | 4 | 346 | 27962 | 0.0050624 | 6.2642e-05 | 80.815
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | PEDESTAL | 3 | 64 | 12106 | 0.0021917 | 1.1587e-05 | 189.1562
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 1 | 91 | 1.6475e-05 | 1.8105e-07 | 91
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 1 | 75 | 1.3578e-05 | 1.8105e-07 | 75
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 111 | 2.0096e-05 | 1.8105e-07 | 111
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | FO | NONE | 2 | 200 | 63200 | 0.011442 | 3.6209e-05 | 316
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | SWITCH, OH | 2 | 273 | 34761 | 0.0062934 | 4.9426e-05 | 127.3297
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CUTOUT | 1189 | 7621 | 235453 | 0.042398 | 0.0013723 | 30.8953
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | NONE | 172 | 10167 | 1053267 | 0.18966 | 0.0018308 | 103.5966
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 269 | 526 | 125163 | 0.022538 | 9.4718e-05 | 237.9525
AEP Total | 2022 | 5553337 | PARTIAL POWER | OU | CONDUCTOR UG | 2 | 3 | 1162 | 0.00020924 | 5.4022e-07 | 387.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 16 | 391 | 72704 | 0.013092 | 7.0408e-05 | 185.9437
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 54 | 4103 | 1626826 | 0.29295 | 0.00073884 | 396.4967
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | NONE | 45 | 1498 | 167514 | 0.030165 | 0.00026975 | 111.8251
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | POLE HARDWARE | 2 | 2 | 430 | 7.785e-05 | 3.6209e-07 | 215
AEP Total | 2021 | 5523447 | PARTIAL POWER | OU | SPLICE, OH | 1 | 4 | 224 | 4.0554e-05 | 7.2419e-07 | 56
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | INSULATOR | 9 | 4266 | 210631 | 0.038134 | 0.00077234 | 49.3744
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | POLE | 3 | 703 | 155311 | 0.028118 | 0.00012728 | 220.926
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 979 | 7832 | 0.001418 | 0.00017724 | 8
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | POLE | 2 | 1570 | 307800 | 0.055726 | 0.00028424 | 196.051
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | NONE | 6 | 99 | 18158 | 0.0032697 | 1.7827e-05 | 183.4141
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 7 | 611 | 66560 | 0.011986 | 0.00011002 | 108.9362
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE | 148 | 18218 | 3457857 | 0.62266 | 0.0032806 | 189.8044
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 225 | 507 | 88197 | 0.015818 | 9.0931e-05 | 173.9586
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NONE | 2923 | 138032 | 28034018 | 5.0279 | 0.024756 | 203.098
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | METERING | 39 | 72 | 5625 | 0.0010088 | 1.2913e-05 | 78.125
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | NONE | 68 | 2917 | 573360 | 0.10283 | 0.00052316 | 196.5581
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 150 | 3043 | 0.00054796 | 2.7011e-05 | 20.2867
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE | 426 | 96761 | 16845496 | 3.0212 | 0.017354 | 174.0939
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | FUSE | 24 | 493 | 44429 | 0.0079684 | 8.842e-05 | 90.1197
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 2 | 58 | 1.0444e-05 | 3.6014e-07 | 29
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | NONE | 139 | 362 | 42549 | 0.0076312 | 6.4925e-05 | 117.5387
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SWITCH, OH | 1 | 711 | 21330 | 0.0038409 | 0.00012803 | 30
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, OH | 27 | 79 | 23881 | 0.0042831 | 1.4169e-05 | 302.2911
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 3 | 636 | 0.00011407 | 5.3805e-07 | 212
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | NONE | 2 | 5 | 348 | 6.2665e-05 | 9.0036e-07 | 69.6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 4 | 19 | 1582 | 0.00028487 | 3.4214e-06 | 83.2632
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | METERING | 2 | 643 | 129215 | 0.023268 | 0.00011579 | 200.9565
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | NONE | 205 | 3238 | 623784 | 0.11188 | 0.00058074 | 192.6448
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR UG | 23 | 48 | 9069 | 0.0016265 | 8.6088e-06 | 188.9375
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | FUSE | 23 | 69 | 5360 | 0.00096132 | 1.2375e-05 | 77.6812
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 14 | 1231 | 207450 | 0.037206 | 0.00022078 | 168.5215
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 38 | 259 | 79264 | 0.014216 | 4.6452e-05 | 306.0386
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 7 | 8567 | 1037957 | 0.18691 | 0.0015427 | 121.1576
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 33 | 244 | 59808 | 0.010727 | 4.3761e-05 | 245.1148
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 17 | 6980 | 833088 | 0.14941 | 0.0012519 | 119.3536
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CUTOUT | 9 | 105 | 8680 | 0.0015568 | 1.8832e-05 | 82.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | JUMPER/RISER | 1 | 3 | 462 | 8.286e-05 | 5.3805e-07 | 154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | FUSE | 2 | 4 | 244 | 4.4175e-05 | 7.2419e-07 | 61
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 12 | 7367 | 1174569 | 0.21151 | 0.0013266 | 159.4365
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | FUSE | 52 | 2723 | 251353 | 0.045262 | 0.00049034 | 92.3074
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | NONE | 44 | 3453 | 152585 | 0.027476 | 0.00062179 | 44.1891
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | NONE | 288 | 7303 | 973386 | 0.17528 | 0.0013151 | 133.2858
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | FUSE | 3 | 4 | 441 | 7.9412e-05 | 7.2029e-07 | 110.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | FUSE | 214 | 7457 | 493150 | 0.088802 | 0.0013428 | 66.1325
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | POLE | 1 | 3 | 792 | 0.00014262 | 5.4022e-07 | 264
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 21 | 93 | 23066 | 0.0041535 | 1.6747e-05 | 248.0215
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | SWITCH, OH | 1 | 2 | 566 | 0.00010192 | 3.6014e-07 | 283
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | NONE | 45 | 478 | 88964 | 0.01602 | 8.6074e-05 | 186.1172
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 467 | 91301 | 0.016441 | 8.4094e-05 | 195.5054
AEP Total | 2022 | 5553337 | PARTIAL POWER | UG | CONDUCTOR UG | 69 | 188 | 30646 | 0.0055185 | 3.3854e-05 | 163.0106
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | SPLICE, OH | 3 | 16 | 8116 | 0.0014615 | 2.8812e-06 | 507.25
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | SPLICE, OH | 10 | 19 | 1929 | 0.00034736 | 3.4214e-06 | 101.5263
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | POLE | 1 | 261 | 54810 | 0.0097606 | 4.6479e-05 | 210
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 6 | 136 | 51233 | 0.0091236 | 2.4219e-05 | 376.7132
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 89 | 38804 | 0.0069102 | 1.5849e-05 | 436
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 1 | 774 | 0.00013783 | 1.7808e-07 | 774
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 2 | 1006 | 100153 | 0.017835 | 0.00017915 | 99.5557
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | OTHER EQUIPMENT | 1 | 104 | 39936 | 0.0071118 | 1.852e-05 | 384
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 165 | 57807 | 0.010294 | 2.9383e-05 | 350.3455
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | WU | NONE | 2 | 4639 | 652567 | 0.11621 | 0.00082611 | 140.6698
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 1 | 84 | 1.4959e-05 | 1.7808e-07 | 84
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | FUSE | 1 | 1 | 64 | 1.1397e-05 | 1.7808e-07 | 64
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 266 | 49476 | 0.0088107 | 4.7369e-05 | 186
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | POLE | 1 | 23 | 16606 | 0.0029572 | 4.0958e-06 | 722
AEP Total | 2020 | 5484199 | PARTIAL POWER | WFS | CONDUCTOR OVERHEAD | 1 | 1 | 119 | 2.1699e-05 | 1.8234e-07 | 119
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 484 | 8.6806e-05 | 1.7935e-07 | 484
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | METERING | 1 | 1 | 64 | 1.1478e-05 | 1.7935e-07 | 64
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | OTHER EQUIPMENT | 1 | 1 | 210 | 3.7664e-05 | 1.7935e-07 | 210
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | JUMPER/RISER | 1 | 1 | 120 | 2.1881e-05 | 1.8234e-07 | 120
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 149 | 2.6831e-05 | 1.8007e-07 | 149
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | SWITCH, OH | 2 | 2278 | 609226 | 0.10926 | 0.00040856 | 267.439
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | POLE | 5 | 82 | 133836 | 0.0241 | 1.4766e-05 | 1632.1463
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | NONE | 1 | 3 | 414 | 7.455e-05 | 5.4022e-07 | 138
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 2 | 38 | 7646 | 0.0013616 | 6.767e-06 | 201.2105
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | V | OTHER EQUIPMENT | 1 | 100 | 900 | 0.00016027 | 1.7808e-05 | 9
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 268 | 1101 | 212996 | 0.038562 | 0.00019933 | 193.4569
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 248 | 18519 | 0.0033528 | 4.4899e-05 | 74.6734
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | NONE | 7 | 13 | 2543 | 0.0004604 | 2.3536e-06 | 195.6154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 2 | 184 | 3.3313e-05 | 3.6209e-07 | 92
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | NONE | 42 | 2017 | 66319 | 0.012007 | 0.00036517 | 32.88
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | NONE | 23 | 300 | 65721 | 0.011899 | 5.4314e-05 | 219.07
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 10 | 2237 | 208855 | 0.037812 | 0.000405 | 93.3639
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | METERING | 3 | 22 | 2127 | 0.00038509 | 3.983e-06 | 96.6818
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | POLE | 3 | 1278 | 118814 | 0.021511 | 0.00023138 | 92.9687
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | NONE | 4 | 4299 | 354162 | 0.06412 | 0.00077832 | 82.3824
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 11 | 19 | 2805 | 0.00050784 | 3.4399e-06 | 147.6316
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SPLICE, OH | 7 | 24 | 4719 | 0.00085436 | 4.3451e-06 | 196.625
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 580 | 88160 | 0.015961 | 0.00010501 | 152
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | POLE | 3333 | 25788 | 3907378 | 0.70361 | 0.0046437 | 151.5192
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 640 | 40884 | 8009430 | 1.4423 | 0.0073621 | 195.9062
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 7 | 4872 | 0.00087731 | 1.2605e-06 | 696
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 3739 | 123387 | 0.022219 | 0.00067329 | 33
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 2 | 74 | 12084 | 0.0021673 | 1.3272e-05 | 163.2973
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 1 | 57 | 1.0264e-05 | 1.8007e-07 | 57
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 867 | 201874 | 0.036206 | 0.0001555 | 232.842
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 164 | 2.9413e-05 | 1.7935e-07 | 164
AEP Total | 2023 | 5575683 | PARTIAL POWER | UB | METERING | 1 | 1 | 67 | 1.2016e-05 | 1.7935e-07 | 67
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 2 | 734 | 0.00013164 | 3.587e-07 | 367
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 95 | 1.7038e-05 | 1.7935e-07 | 95
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 3 | 485 | 8.8436e-05 | 5.4703e-07 | 161.6667
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 2 | 328 | 5.9064e-05 | 3.6014e-07 | 164
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | FUSE | 1 | 1 | 113 | 2.0267e-05 | 1.7935e-07 | 113
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | OTHER EQUIPMENT | 2 | 84 | 27401 | 0.0049342 | 1.5126e-05 | 326.2024
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 266 | 4.7369e-05 | 1.7808e-07 | 266
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | POLE | 1 | 200 | 7896 | 0.0014061 | 3.5616e-05 | 39.48
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 92 | 2576 | 0.00045873 | 1.6383e-05 | 28
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 4 | 2371 | 837786 | 0.14919 | 0.00042223 | 353.3471
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | NONE | 362 | 12016 | 1510090 | 0.2734 | 0.0021755 | 125.6733
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 18 | 312 | 23102 | 0.0041825 | 5.6486e-05 | 74.0449
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | FUSE | 68 | 1748 | 141284 | 0.025579 | 0.00031647 | 80.8261
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | NONE | 124 | 446 | 54031 | 0.0097821 | 8.0747e-05 | 121.1457
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | METERING | 2 | 2 | 82 | 1.4846e-05 | 3.6209e-07 | 41
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | PEDESTAL | 24 | 303 | 44875 | 0.0081245 | 5.4857e-05 | 148.1023
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CUTOUT | 48 | 149 | 13855 | 0.0025084 | 2.6976e-05 | 92.9866
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | POLE | 2 | 1880 | 98040 | 0.01775 | 0.00034037 | 52.1489
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, UG | 6 | 1290 | 182602 | 0.033059 | 0.00023355 | 141.5519
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | CONDUCTOR OVERHEAD | 1 | 6 | 1686 | 0.00030524 | 1.0863e-06 | 281
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | NONE | 1 | 1 | 97 | 1.7561e-05 | 1.8105e-07 | 97
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 2 | 47 | 1214 | 0.00021979 | 8.5092e-06 | 25.8298
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | INSULATOR | 3 | 2861 | 710643 | 0.12866 | 0.00051797 | 248.3897
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | CF | NONE | 6 | 1175 | 157315 | 0.028685 | 0.00021425 | 133.8851
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 1924 | 21164 | 0.003811 | 0.00034646 | 11
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 2 | 6 | 1027 | 0.00018727 | 1.0941e-06 | 171.1667
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | OTHER EQUIPMENT | 3 | 3341 | 779052 | 0.14029 | 0.00060162 | 233.1793
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CAPACITOR | 1 | 30 | 1800 | 0.00032822 | 5.4703e-06 | 60
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 2 | 2 | 238 | 4.2857e-05 | 3.6014e-07 | 119
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 2 | 3 | 230 | 4.1939e-05 | 5.4703e-07 | 76.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 3 | 12 | 2627 | 0.00046782 | 2.137e-06 | 218.9167
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 11 | 214 | 20081 | 0.003576 | 3.8109e-05 | 93.8364
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 3 | 756 | 101686 | 0.018108 | 0.00013463 | 134.5053
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 1 | 25 | 4.452e-06 | 1.7808e-07 | 25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | TRANSFORMER, UG | 1 | 3 | 1050 | 0.00018698 | 5.3424e-07 | 350
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | POLE | 1 | 876 | 299904 | 0.053407 | 0.000156 | 342.3562
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CONN/CLAMP | 2 | 18 | 4553 | 0.0008108 | 3.2054e-06 | 252.9444
AEP Total | 2023 | 5575683 | PARTIAL POWER | AF | CONDUCTOR OVERHEAD | 1 | 1 | 1872 | 0.00033574 | 1.7935e-07 | 1872
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | METERING | 1 | 1 | 141 | 2.5109e-05 | 1.7808e-07 | 141
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CUTOUT | 1 | 1 | 93 | 1.6561e-05 | 1.7808e-07 | 93
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 6 | 1110 | 0.00019767 | 1.0685e-06 | 185
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | POLE | 2 | 97 | 24531 | 0.0044173 | 1.7467e-05 | 252.8969
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 713 | 65596 | 0.011812 | 0.00012839 | 92
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | FUSE | 2 | 3 | 339 | 6.1044e-05 | 5.4022e-07 | 113
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | METERING | 2 | 12 | 1964 | 0.00035366 | 2.1609e-06 | 163.6667
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 485 | 8.7335e-05 | 1.8007e-07 | 485
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 28 | 4.9862e-06 | 1.7808e-07 | 28
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 3 | 16 | 3251 | 0.00057894 | 2.8493e-06 | 203.1875
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 1 | 71 | 1.2644e-05 | 1.7808e-07 | 71
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 13 | 7735 | 0.0013774 | 2.315e-06 | 595
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 1 | 8 | 1104 | 0.0001966 | 1.4246e-06 | 138
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 2 | 314 | 5.5917e-05 | 3.5616e-07 | 157
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 95 | 1.6918e-05 | 1.7808e-07 | 95
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | SWITCH, UG | 3 | 145 | 24393 | 0.0044479 | 2.644e-05 | 168.2276
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | METERING | 1 | 1 | 388 | 7.0246e-05 | 1.8105e-07 | 388
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 51 | 26268 | 0.0046778 | 9.0821e-06 | 515.0588
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | FUSE | 1 | 5 | 185 | 3.3494e-05 | 9.0523e-07 | 37
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | FUSE | 2 | 3 | 655 | 0.00011859 | 5.4314e-07 | 218.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | FW | NONE | 2 | 848 | 5093 | 0.00091711 | 0.0001527 | 6.0059
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 4 | 39 | 8742 | 0.0015568 | 6.9451e-06 | 224.1538
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | NONE | 19 | 1205 | 55200 | 0.00983 | 0.00021459 | 45.8091
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | NONE | 1 | 1464 | 642346 | 0.11439 | 0.00026071 | 438.7609
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CUTOUT | 7 | 242 | 43909 | 0.0078193 | 4.3095e-05 | 181.4421
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 2140 | 427386 | 0.076109 | 0.00038109 | 199.7131
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 16 | 44 | 10697 | 0.0019049 | 7.8355e-06 | 243.1136
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 4 | 640 | 0.00011397 | 7.1232e-07 | 160
AEP Total | 2024 | 5615460 | PARTIAL POWER | WT | CONN/CLAMP | 1 | 1 | 130 | 2.315e-05 | 1.7808e-07 | 130
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 6 | 45 | 5672 | 0.0010101 | 8.0136e-06 | 126.0444
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CUTOUT | 3 | 1730 | 115626 | 0.020591 | 0.00030808 | 66.8358
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | R | JUMPER/RISER | 1 | 1432 | 351056 | 0.062516 | 0.00025501 | 245.1508
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONN/CLAMP | 1 | 1 | 118 | 2.1013e-05 | 1.7808e-07 | 118
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 1 | 87 | 1.5493e-05 | 1.7808e-07 | 87
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 1 | 20 | 5475 | 0.00097499 | 3.5616e-06 | 273.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 1 | 125 | 2.226e-05 | 1.7808e-07 | 125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 14 | 9573 | 0.0017048 | 2.4931e-06 | 683.7857
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | ARRESTER | 1 | 1 | 142 | 2.557e-05 | 1.8007e-07 | 142
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 2342 | 221710 | 0.039924 | 0.00042173 | 94.667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CUTOUT | 1 | 3 | 126 | 2.2689e-05 | 5.4022e-07 | 42
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | SWITCH, OH | 2 | 1854 | 111322 | 0.020046 | 0.00033385 | 60.0442
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | ARRESTER | 1 | 979 | 39160 | 0.0070898 | 0.00017724 | 40
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 109 | 31937 | 0.005751 | 1.9628e-05 | 293
AEP Total | 2024 | 5615460 | PARTIAL POWER | V | METERING | 2 | 5 | 428 | 7.6218e-05 | 8.904e-07 | 85.6
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | F | REGULATOR | 1 | 1 | 93 | 1.6561e-05 | 1.7808e-07 | 93
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 145 | 2024 | 147800 | 0.02632 | 0.00036043 | 73.0237
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 8 | 41 | 7790 | 0.0013872 | 7.3013e-06 | 190
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 38 | 13486 | 4278103 | 0.76184 | 0.0024016 | 317.2255
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 6 | 291 | 11039 | 0.0019658 | 5.1821e-05 | 37.9347
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 1 | 14 | 1582 | 0.00028487 | 2.521e-06 | 113
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 24 | 936 | 0.00016855 | 4.3217e-06 | 39
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | FUSE | 1 | 1 | 12 | 2.1609e-06 | 1.8007e-07 | 12
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 26 | 3163 | 97696 | 0.017398 | 0.00056327 | 30.8871
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 60 | 1795 | 223511 | 0.039803 | 0.00031965 | 124.5187
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 27 | 563 | 78350 | 0.013953 | 0.00010026 | 139.1652
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 5 | 12 | 869 | 0.00015475 | 2.137e-06 | 72.4167
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 2 | 6 | 2452 | 0.00043665 | 1.0685e-06 | 408.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CROSSARM | 1 | 13 | 1914 | 0.00034084 | 2.315e-06 | 147.2308
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 5 | 6 | 499 | 8.8862e-05 | 1.0685e-06 | 83.1667
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | FUSE | 2 | 920 | 276025 | 0.049154 | 0.00016383 | 300.0272
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | SPLICE, OH | 10 | 22 | 3401 | 0.00060565 | 3.9178e-06 | 154.5909
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | TRANSFORMER, UG | 2 | 208 | 23920 | 0.0042597 | 3.7041e-05 | 115
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 463 | 57875 | 0.010306 | 8.2451e-05 | 125
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | U | NONE | 7 | 1374 | 101012 | 0.017988 | 0.00024468 | 73.5167
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 3 | 13 | 696 | 0.00012394 | 2.315e-06 | 53.5385
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | SPLICE, UG | 1 | 4 | 143 | 2.5465e-05 | 7.1232e-07 | 35.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 3 | 3475 | 0.00061883 | 5.3424e-07 | 1158.3333
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 10 | 31 | 3667 | 0.00065302 | 5.5205e-06 | 118.2903
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AF | BREAKER | 1 | 715 | 50050 | 0.0089129 | 0.00012733 | 70
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | NONE | 5 | 1076 | 43160 | 0.0077408 | 0.00019298 | 40.1115
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 5 | 549 | 356688 | 0.063972 | 9.8463e-05 | 649.7049
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WU | NONE | 9 | 12190 | 1658182 | 0.2974 | 0.0021863 | 136.0281
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | NETWORK TRANSFORMER | 1 | 75 | 7875 | 0.0014181 | 1.3505e-05 | 105
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | PEDESTAL | 1 | 1 | 98 | 1.7647e-05 | 1.8007e-07 | 98
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 2 | 5 | 453 | 8.1246e-05 | 8.9675e-07 | 90.6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 20 | 87 | 64423 | 0.011472 | 1.5493e-05 | 740.4943
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 5 | 3737 | 604156 | 0.10836 | 0.00067023 | 161.6687
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 7 | 59 | 41065 | 0.0073128 | 1.0507e-05 | 696.0169
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 41 | 1862 | 605668 | 0.10786 | 0.00033158 | 325.2782
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UB | NONE | 1 | 310 | 25572 | 0.0045863 | 5.5599e-05 | 82.4903
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 22 | 734 | 187089 | 0.033317 | 0.00013071 | 254.8896
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 10 | 594 | 32636 | 0.0058118 | 0.00010578 | 54.9428
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | FUSE | 1 | 1 | 121 | 2.1701e-05 | 1.7935e-07 | 121
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | INSULATOR | 6 | 102 | 11576 | 0.0020615 | 1.8164e-05 | 113.4902
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 46 | 4942 | 432836 | 0.077079 | 0.00088007 | 87.5832
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 9 | 147 | 5206 | 0.00092708 | 2.6178e-05 | 35.415
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | GUY/ANCHOR | 2 | 152 | 11831 | 0.002142 | 2.7519e-05 | 77.8355
AEP Total | 2021 | 5523447 | PARTIAL POWER | SCO | CONDUCTOR OVERHEAD | 1 | 1 | 490 | 8.8713e-05 | 1.8105e-07 | 490
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | ARRESTER | 1 | 7 | 105 | 1.901e-05 | 1.2673e-06 | 15
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CROSSARM | 3 | 340 | 273718 | 0.049556 | 6.1556e-05 | 805.0529
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 6 | 876 | 0.0001586 | 1.0863e-06 | 146
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 1 | 9 | 3123 | 0.00056541 | 1.6294e-06 | 347
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | ARRESTER | 1 | 1403 | 106628 | 0.019443 | 0.00025583 | 76
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 5 | 1150 | 0.00020969 | 9.1171e-07 | 230
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SPLICE, OH | 3 | 6 | 838 | 0.0001528 | 1.0941e-06 | 139.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | CONDUCTOR UG | 3 | 3484 | 1232461 | 0.22473 | 0.00063528 | 353.7489
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 135 | 2.4616e-05 | 1.8234e-07 | 135
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 3 | 70 | 48204 | 0.0087896 | 1.2764e-05 | 688.6286
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 465 | 130665 | 0.023826 | 8.4789e-05 | 281
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 3 | 3719 | 507163 | 0.092477 | 0.00067813 | 136.3708
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CUTOUT | 1 | 1 | 31 | 5.6124e-06 | 1.8105e-07 | 31
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | POLE | 3 | 547 | 256281 | 0.045638 | 9.741e-05 | 468.521
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | REGULATOR | 1 | 1138 | 199544 | 0.035535 | 0.00020265 | 175.3462
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | METERING | 1 | 1 | 53 | 9.5955e-06 | 1.8105e-07 | 53
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | NONE | 9 | 40 | 9311 | 0.0016978 | 7.2937e-06 | 232.775
AEP Total | 2020 | 5484199 | PARTIAL POWER | V | NONE | 3 | 3 | 197 | 3.5921e-05 | 5.4703e-07 | 65.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CAPACITOR | 1 | 1970 | 120170 | 0.021912 | 0.00035921 | 61
AEP Total | 2020 | 5484199 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 2 | 2 | 203 | 3.7015e-05 | 3.6468e-07 | 101.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | SWITCH, UG | 2 | 49 | 4512 | 0.00082273 | 8.9348e-06 | 92.0816
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 19 | 1074 | 126864 | 0.023133 | 0.00019584 | 118.1229
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 51 | 440 | 34935 | 0.0063701 | 8.023e-05 | 79.3977
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 205 | 9250 | 1659862 | 0.29889 | 0.0016657 | 179.4445
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | ARRESTER | 153 | 12592 | 1238497 | 0.22302 | 0.0022675 | 98.3559
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | FUSE | 568 | 9210 | 693786 | 0.12493 | 0.0016585 | 75.3296
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, UG | 309 | 3104 | 213914 | 0.03852 | 0.00055894 | 68.9156
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CROSSARM | 100 | 35907 | 4425609 | 0.79693 | 0.0064658 | 123.252
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 18 | 16424 | 1605103 | 0.28903 | 0.0029575 | 97.7291
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | JUMPER/RISER | 3 | 22 | 2618 | 0.00047143 | 3.9616e-06 | 119
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | NONE | 50 | 26219 | 2986293 | 0.53775 | 0.0047213 | 113.8981
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONN/CLAMP | 11 | 25 | 4168 | 0.00075054 | 4.5018e-06 | 166.72
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | OTHER EQUIPMENT | 52 | 538 | 37829 | 0.0068119 | 9.6879e-05 | 70.3141
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONDUCTOR UG | 13 | 28 | 4606 | 0.00082609 | 5.0218e-06 | 164.5
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | INSULATOR | 2 | 787 | 163187 | 0.029385 | 0.00014172 | 207.3532
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 14 | 665 | 99417 | 0.017902 | 0.00011975 | 149.4992
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CUTOUT | 25 | 472 | 50664 | 0.0091232 | 8.4994e-05 | 107.339
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WU | CONDUCTOR OVERHEAD | 1 | 210 | 24360 | 0.0043866 | 3.7815e-05 | 116
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | PEDESTAL | 21 | 123 | 10448 | 0.0018739 | 2.206e-05 | 84.9431
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 6 | 267 | 15838 | 0.002852 | 4.8079e-05 | 59.3184
AEP Total | 2023 | 5575683 | PARTIAL POWER | UG | CONDUCTOR UG | 71 | 125 | 18029 | 0.0032335 | 2.2419e-05 | 144.232
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | SCO | REGULATOR | 5 | 3353 | 261904 | 0.046973 | 0.00060136 | 78.1103
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 18 | 3655 | 185192 | 0.033348 | 0.00065816 | 50.6681
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | ARRESTER | 6 | 9019 | 1181222 | 0.21185 | 0.0016176 | 130.9704
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 9 | 1591 | 0.00028649 | 1.6206e-06 | 176.7778
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | INSULATOR | 3 | 53 | 15485 | 0.0027772 | 9.5056e-06 | 292.1698
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 29 | 515 | 210049 | 0.037672 | 9.2365e-05 | 407.8621
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 7 | 155 | 23013 | 0.004144 | 2.7911e-05 | 148.471
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | NONE | 5 | 37 | 4752 | 0.0008557 | 6.6627e-06 | 128.4324
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | ARRESTER | 8 | 3682 | 635094 | 0.11436 | 0.00066302 | 172.4861
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 20 | 1045 | 196360 | 0.035217 | 0.00018742 | 187.9043
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 1 | 1 | 190 | 3.4214e-05 | 1.8007e-07 | 190
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CUTOUT | 9 | 26 | 2508 | 0.00044981 | 4.6631e-06 | 96.4615
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 4 | 67 | 20083 | 0.0036019 | 1.2016e-05 | 299.7463
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 2 | 318 | 5.7033e-05 | 3.587e-07 | 159
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | FUSE | 16 | 216 | 36478 | 0.0065423 | 3.874e-05 | 168.8796
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | FUSE | 11 | 62 | 13007 | 0.0023328 | 1.112e-05 | 209.7903
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | POLE | 7 | 149 | 78112 | 0.014009 | 2.6723e-05 | 524.2416
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 23 | 1601 | 147050 | 0.026813 | 0.00029193 | 91.8488
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | NONE | 13 | 7436 | 505356 | 0.092148 | 0.0013559 | 67.9607
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 23 | 212 | 92419 | 0.016852 | 3.8657e-05 | 435.9387
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, OH | 18 | 45 | 8110 | 0.0014788 | 8.2054e-06 | 180.2222
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | CONN/CLAMP | 1 | 2 | 162 | 2.9539e-05 | 3.6468e-07 | 81
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 38 | 8546 | 0.0015583 | 6.929e-06 | 224.8947
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONN/CLAMP | 5 | 44 | 4839 | 0.00088235 | 8.023e-06 | 109.9773
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE | 4 | 216 | 324603 | 0.059189 | 3.9386e-05 | 1502.7917
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | POLE HARDWARE | 2 | 15 | 1254 | 0.00022866 | 2.7351e-06 | 83.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1201 | 174544 | 0.031827 | 0.00021899 | 145.3322
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | NONE | 4 | 38 | 17519 | 0.0031945 | 6.929e-06 | 461.0263
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | U | NONE | 12 | 7049 | 870320 | 0.15609 | 0.0012642 | 123.4672
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 193 | 45350 | 0.0081335 | 3.4615e-05 | 234.9741
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 1007 | 14908 | 923569 | 0.16447 | 0.0026548 | 61.9512
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 167 | 5931 | 1405060 | 0.25021 | 0.0010562 | 236.901
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | FUSE | 4 | 55 | 7244 | 0.0013115 | 9.9576e-06 | 131.7091
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 3 | 1023 | 60971 | 0.011118 | 0.00018654 | 59.6002
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ERF | TRANSFORMER, POWER - NON LTC | 2 | 2634 | 322415 | 0.05879 | 0.00048029 | 122.4051
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | NONE | 31 | 34716 | 3837099 | 0.69966 | 0.0063302 | 110.5283
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | CONDUCTOR UG | 3 | 7 | 873 | 0.00015918 | 1.2764e-06 | 124.7143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 52 | 24804 | 0.0044486 | 9.3262e-06 | 477
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CUTOUT | 5 | 1145 | 199572 | 0.035793 | 0.00020536 | 174.2987
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONN/CLAMP | 5 | 35 | 1691 | 0.00030328 | 6.2773e-06 | 48.3143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | FUSE | 2 | 15 | 1570 | 0.00028158 | 2.6903e-06 | 104.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 3 | 51 | 9.1469e-06 | 5.3805e-07 | 17
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | SECTIONALIZER | 1 | 1 | 103 | 1.8473e-05 | 1.7935e-07 | 103
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 342 | 2722 | 322980 | 0.057516 | 0.00048473 | 118.6554
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | NONE | 172 | 1772 | 236186 | 0.04236 | 0.00031781 | 133.2878
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 16 | 4614 | 0.00082752 | 2.8696e-06 | 288.375
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | FUSE | 9 | 175 | 57309 | 0.010278 | 3.1386e-05 | 327.48
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CUTOUT | 42 | 1461 | 395956 | 0.071015 | 0.00026203 | 271.0171
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | NONE | 33 | 13466 | 902128 | 0.1618 | 0.0024151 | 66.993
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 19 | 520 | 93075 | 0.016693 | 9.3262e-05 | 178.9904
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | REGULATOR | 10 | 3532 | 90728 | 0.016272 | 0.00063346 | 25.6874
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 6 | 3445 | 772123 | 0.13848 | 0.00061786 | 224.1286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | METERING | 5 | 9 | 1063 | 0.00019065 | 1.6142e-06 | 118.1111
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 3880 | 35690 | 0.006401 | 0.00069588 | 9.1985
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 3 | 7194 | 0.0012954 | 5.4022e-07 | 2398
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | ARRESTER | 7 | 51 | 9900 | 0.0017756 | 9.1469e-06 | 194.1176
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CUTOUT | 10 | 63 | 3683 | 0.00066055 | 1.1299e-05 | 58.4603
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CROSSARM | 3 | 4976 | 517584 | 0.093202 | 0.00089604 | 104.0161
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | CONN/CLAMP | 2 | 2 | 266 | 4.7707e-05 | 3.587e-07 | 133
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | NONE | 4506 | 58762 | 4689039 | 0.83502 | 0.010464 | 79.7971
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 67 | 1430 | 150776 | 0.02685 | 0.00025465 | 105.4378
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, OH | 372 | 2012 | 184091 | 0.032783 | 0.0003583 | 91.4965
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 38 | 155 | 36069 | 0.0064232 | 2.7602e-05 | 232.7032
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ERF | NONE | 2 | 3657 | 259229 | 0.046163 | 0.00065124 | 70.8857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | POLE | 5 | 595 | 67113 | 0.011951 | 0.00010596 | 112.795
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 139 | 5847 | 1315648 | 0.23429 | 0.0010412 | 225.0125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 48 | 896 | 267211 | 0.047585 | 0.00015956 | 298.2266
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE | 21 | 1683 | 1384175 | 0.24649 | 0.00029971 | 822.445
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 85 | 26879 | 8026214 | 1.4293 | 0.0047866 | 298.6054
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | FUSE | 53 | 481 | 54244 | 0.0096598 | 8.5656e-05 | 112.7734
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | NONE | 9 | 3324 | 1822763 | 0.3246 | 0.00059194 | 548.3643
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 6 | 15 | 8854 | 0.0015767 | 2.6712e-06 | 590.2667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | ARRESTER | 20 | 331 | 3124 | 0.00055632 | 5.8944e-05 | 9.4381
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | NONE | 6 | 6 | 1706 | 0.0003038 | 1.0685e-06 | 284.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NETWORK PROTECTOR | 1 | 95 | 42105 | 0.0075515 | 1.7038e-05 | 443.2105
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | POLE | 2 | 3 | 403 | 7.2278e-05 | 5.3805e-07 | 134.3333
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | FUSE | 2 | 2 | 212 | 3.7753e-05 | 3.5616e-07 | 106
AEP Total | 2023 | 5575683 | PARTIAL POWER | AF | REGULATOR | 1 | 1 | 264 | 4.7348e-05 | 1.7935e-07 | 264
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 269 | 4.7903e-05 | 1.7808e-07 | 269
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | POLE | 5 | 1155 | 57333 | 0.010283 | 0.00020715 | 49.639
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | NONE | 51 | 5387 | 599736 | 0.10858 | 0.0009753 | 111.3302
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 8 | 6712 | 1493622 | 0.27041 | 0.0012152 | 222.5301
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 49 | 201 | 55779 | 0.010099 | 3.639e-05 | 277.5075
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | POLE | 3 | 10 | 1602 | 0.00029004 | 1.8105e-06 | 160.2
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | NONE | 42 | 86 | 8718 | 0.0015784 | 1.557e-05 | 101.3721
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | POLE | 3 | 35 | 3280 | 0.00059383 | 6.3366e-06 | 93.7143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 74 | 23464 | 2190251 | 0.39654 | 0.0042481 | 93.3452
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 7 | 14 | 2438 | 0.00044139 | 2.5346e-06 | 174.1429
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | BREAKER | 13 | 12884 | 1593239 | 0.28845 | 0.0023326 | 123.6603
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | NONE | 25 | 1054 | 159146 | 0.028813 | 0.00019082 | 150.9924
AEP Total | 2021 | 5523447 | PARTIAL POWER | FW | CONDUCTOR UG | 1 | 1 | 218 | 3.9468e-05 | 1.8105e-07 | 218
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 8 | 1430 | 0.0002589 | 1.4484e-06 | 178.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 2 | 184 | 3.3313e-05 | 3.6209e-07 | 92
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 2 | 2364 | 242682 | 0.043937 | 0.00042799 | 102.6574
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 6 | 272 | 46242 | 0.0083719 | 4.9245e-05 | 170.0074
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | NONE | 541 | 26917 | 4835405 | 0.87072 | 0.004847 | 179.6413
AEP Total | 2021 | 5523447 | PARTIAL POWER | FW | NONE | 1 | 1 | 71 | 1.2854e-05 | 1.8105e-07 | 71
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 1 | 49 | 8.8713e-06 | 1.8105e-07 | 49
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 29 | 2871 | 0.00051978 | 5.2503e-06 | 99
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CUTOUT | 1 | 309 | 14523 | 0.0026293 | 5.5943e-05 | 47
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | NONE | 3 | 147 | 12480 | 0.0022595 | 2.6614e-05 | 84.898
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CUTOUT | 1226 | 8019 | 286686 | 0.052275 | 0.0014622 | 35.7508
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 144 | 8205 | 999158 | 0.18219 | 0.0014961 | 121.7743
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 4 | 455 | 64797 | 0.011815 | 8.2966e-05 | 142.411
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE | 124 | 22535 | 4027788 | 0.73444 | 0.0041091 | 178.7348
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | NONE | 54 | 4462 | 639988 | 0.1167 | 0.00081361 | 143.4307
AEP Total | 2020 | 5484199 | PARTIAL POWER | UG | CONDUCTOR UG | 45 | 55 | 10133 | 0.0018477 | 1.0029e-05 | 184.2364
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | FUSE | 35 | 87 | 11519 | 0.0021004 | 1.5864e-05 | 132.4023
AEP Total | 2020 | 5484199 | PARTIAL POWER | WFS | CONDUCTOR UG | 1 | 1 | 383 | 6.9837e-05 | 1.8234e-07 | 383
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 437 | 119907 | 0.021864 | 7.9683e-05 | 274.3867
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | FUSE | 1 | 58 | 5452 | 0.00099413 | 1.0576e-05 | 94
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 11 | 41 | 3683 | 0.00067157 | 7.476e-06 | 89.8293
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CROSSARM | 281 | 7047 | 446283 | 0.080363 | 0.001269 | 63.3295
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | ARRESTER | 45 | 2455 | 372151 | 0.067014 | 0.00044208 | 151.589
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | NONE | 63 | 798 | 94444 | 0.017007 | 0.0001437 | 118.3509
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 136 | 5660 | 1189333 | 0.21417 | 0.0010192 | 210.1295
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | NONE | 138 | 513 | 53272 | 0.0095928 | 9.2377e-05 | 103.8441
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 43 | 791 | 119763 | 0.021566 | 0.00014244 | 151.4071
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | FUSE | 11 | 146 | 30716 | 0.0055311 | 2.629e-05 | 210.3836
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CUTOUT | 1395 | 49667 | 5715032 | 1.025 | 0.0089078 | 115.067
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 1410 | 52110 | 15044526 | 2.6982 | 0.0093459 | 288.7071
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | NONE | 2886 | 47635 | 4671920 | 0.83791 | 0.0085433 | 98.0775
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 125 | 12318 | 1354424 | 0.24292 | 0.0022092 | 109.9549
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 3730 | 289258 | 0.051878 | 0.00066898 | 77.5491
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 47 | 8022 | 0.0014286 | 8.3698e-06 | 170.6809
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | SPLICE, UG | 1 | 49 | 14847 | 0.002688 | 8.8713e-06 | 303
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | INSULATOR | 1 | 1793 | 272528 | 0.04934 | 0.00032462 | 151.9955
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 1 | 35 | 6.3366e-06 | 1.8105e-07 | 35
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 3 | 321 | 5.8116e-05 | 5.4314e-07 | 107
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | FUSE | 2 | 26 | 1800 | 0.00032413 | 4.6819e-06 | 69.2308
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 882 | 123480 | 0.022235 | 0.00015882 | 140
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | INSULATOR | 3 | 2033 | 575179 | 0.10357 | 0.00036609 | 282.9213
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 59 | 9381 | 0.0016893 | 1.0624e-05 | 159
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | FUSE | 1 | 93 | 5580 | 0.0010008 | 1.668e-05 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | SECTIONALIZER | 1 | 1 | 138 | 2.485e-05 | 1.8007e-07 | 138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 3 | 669 | 0.00012047 | 5.4022e-07 | 223
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 4 | 284 | 5.0935e-05 | 7.174e-07 | 71
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 263 | 4.7169e-05 | 1.7935e-07 | 263
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 89 | 8291 | 0.0014765 | 1.5849e-05 | 93.1573
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 96 | 15360 | 0.0027353 | 1.7096e-05 | 160
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 689 | 64638 | 0.011639 | 0.00012407 | 93.8142
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABX | BREAKER | 1 | 2443 | 254072 | 0.045751 | 0.00043992 | 104
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | SPLICE, UG | 1 | 1707 | 287247 | 0.051725 | 0.00030738 | 168.2759
AEP Total | 2025 | 5615460 | PARTIAL POWER | UG | NONE | 2 | 5 | 441 | 7.8533e-05 | 8.904e-07 | 88.2
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 9 | 657 | 0.000117 | 1.6027e-06 | 73
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | O | NONE | 1 | 282 | 42018 | 0.0074826 | 5.0219e-05 | 149
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 16 | 2472 | 0.00044021 | 2.8493e-06 | 154.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 3 | 180 | 3.2054e-05 | 5.3424e-07 | 60
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | FUSE | 1 | 5 | 535 | 9.5273e-05 | 8.904e-07 | 107
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 5 | 1940 | 0.00034547 | 8.904e-07 | 388
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 1 | 1 | 56 | 9.9725e-06 | 1.7808e-07 | 56
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 25 | 7175 | 0.0012777 | 4.452e-06 | 287
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 557 | 9.919e-05 | 1.7808e-07 | 557
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | OL | NONE | 9 | 16096 | 2589727 | 0.46118 | 0.0028664 | 160.8926
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 1 | 244 | 4.3451e-05 | 1.7808e-07 | 244
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | ARRESTER | 1 | 10 | 5072 | 0.00090322 | 1.7808e-06 | 507.2
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 2 | 29 | 6474 | 0.0011529 | 5.1643e-06 | 223.2414
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 140 | 2.5528e-05 | 1.8234e-07 | 140
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CIRCUIT SWITCHER | 1 | 1 | 102 | 1.8599e-05 | 1.8234e-07 | 102
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONN/CLAMP | 1 | 4 | 32 | 5.6986e-06 | 7.1232e-07 | 8
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | CUTOUT | 1 | 15 | 15525 | 0.0027647 | 2.6712e-06 | 1035
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 36 | 1224 | 0.00021797 | 6.4109e-06 | 34
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | METERING | 2 | 2 | 93 | 1.6561e-05 | 3.5616e-07 | 46.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | VA | NONE | 1 | 2 | 52 | 9.2601e-06 | 3.5616e-07 | 26
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 16 | 24880 | 0.0044306 | 2.8493e-06 | 1555
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 66 | 5280 | 0.00096277 | 1.2035e-05 | 80
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 2 | 226 | 4.1209e-05 | 3.6468e-07 | 113
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | FUSE | 579 | 6997 | 759977 | 0.13759 | 0.0012668 | 108.6147
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | FUSE | 1 | 37 | 5205 | 0.00093727 | 6.6627e-06 | 140.6757
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | NONE | 754 | 12425 | 980449 | 0.17584 | 0.0022284 | 78.9094
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 2 | 9 | 3574 | 0.00064358 | 1.6206e-06 | 397.1111
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 232 | 6032 | 0.0010862 | 4.1777e-05 | 26
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 1 | 147 | 2.6178e-05 | 1.7808e-07 | 147
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 6 | 29 | 4608 | 0.00082059 | 5.1643e-06 | 158.8966
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | SWITCH, OH | 4 | 291 | 41028 | 0.0073063 | 5.1821e-05 | 140.9897
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 17 | 31 | 5404 | 0.00096234 | 5.5205e-06 | 174.3226
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | NONE | 41 | 1725 | 247684 | 0.044108 | 0.00030719 | 143.5849
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 13 | 127 | 16361 | 0.0029136 | 2.2616e-05 | 128.8268
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 15 | 94 | 16871 | 0.0030044 | 1.674e-05 | 179.4787
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 6 | 3365 | 339088 | 0.060385 | 0.00059924 | 100.7691
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 1 | 489 | 8.7702e-05 | 1.7935e-07 | 489
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CABLE TERMINATOR | 1 | 3 | 594 | 0.00010653 | 5.3805e-07 | 198
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | POLE | 1 | 6 | 378 | 6.7794e-05 | 1.0761e-06 | 63
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 126 | 40194 | 0.0072088 | 2.2598e-05 | 319
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 3 | 172 | 13843 | 0.0024827 | 3.0848e-05 | 80.4826
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 1 | 151 | 2.7082e-05 | 1.7935e-07 | 151
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | SPLICE, OH | 3 | 7 | 682 | 0.00012232 | 1.2555e-06 | 97.4286
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CROSSARM | 4 | 3334 | 364092 | 0.065918 | 0.00060361 | 109.2058
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 2 | 1935 | 104781 | 0.01897 | 0.00035032 | 54.1504
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, GROUNDING | 1 | 3 | 4077 | 0.00073813 | 5.4314e-07 | 1359
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 6 | 33 | 2088 | 0.00038073 | 6.0173e-06 | 63.2727
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | POLE | 5 | 906 | 59612 | 0.01087 | 0.0001652 | 65.7969
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 33 | 16498 | 0.0030083 | 6.0173e-06 | 499.9394
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 269 | 4.905e-05 | 1.8234e-07 | 269
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 168 | 20901 | 0.0038111 | 3.0633e-05 | 124.4107
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | NONE | 13 | 836 | 140283 | 0.024982 | 0.00014887 | 167.8026
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 5 | 182 | 58574 | 0.010431 | 3.2411e-05 | 321.8352
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | TRANSFORMER, UG | 1 | 5 | 2105 | 0.0003811 | 9.0523e-07 | 421
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 2 | 546 | 9.8851e-05 | 3.6209e-07 | 273
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 5 | 1031 | 0.0001836 | 8.904e-07 | 206.2
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | ARRESTER | 6 | 5031 | 526218 | 0.093709 | 0.00089592 | 104.5951
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | SWITCH, OH | 6 | 5353 | 305260 | 0.054361 | 0.00095326 | 57.026
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 6 | 1146 | 0.00020408 | 1.0685e-06 | 191
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 6 | 23 | 866 | 0.00015422 | 4.0958e-06 | 37.6522
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 8 | 1274 | 129150 | 0.022999 | 0.00022687 | 101.3736
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | METERING | 8 | 8 | 675 | 0.0001202 | 1.4246e-06 | 84.375
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 1643 | 0.00029259 | 1.7808e-07 | 1643
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | REGULATOR | 8 | 10715 | 635972 | 0.11325 | 0.0019081 | 59.3534
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONN/CLAMP | 3 | 10 | 590 | 0.00010507 | 1.7808e-06 | 59
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 556 | 48824 | 0.0086946 | 9.9012e-05 | 87.8129
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | NONE | 7 | 5404 | 206070 | 0.036697 | 0.00096234 | 38.1329
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | CONN/CLAMP | 3 | 29 | 2651 | 0.00047209 | 5.1643e-06 | 91.4138
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | FUSE | 2 | 2 | 183 | 3.2589e-05 | 3.5616e-07 | 91.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 4 | 19 | 4974 | 0.00088577 | 3.3835e-06 | 261.7895
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | R | NONE | 2 | 478 | 79635 | 0.014181 | 8.5122e-05 | 166.6004
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | SCO | SWITCH, OH | 1 | 1 | 425 | 7.5684e-05 | 1.7808e-07 | 425
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | ARRESTER | 8 | 6994 | 818126 | 0.14569 | 0.0012455 | 116.9754
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 7 | 1121 | 0.00019963 | 1.2466e-06 | 160.1429
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | TRANSFORMER, STATION SERVICE | 1 | 1 | 193 | 3.4369e-05 | 1.7808e-07 | 193
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 1382 | 235133 | 0.041872 | 0.00024611 | 170.1397
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | U | NONE | 17 | 16990 | 2480438 | 0.44666 | 0.0030594 | 145.994
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | NONE | 3 | 7993 | 849797 | 0.15302 | 0.0014393 | 106.3177
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 264 | 795 | 148206 | 0.026688 | 0.00014316 | 186.4226
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | SPLICE, OH | 1 | 1 | 149 | 2.6976e-05 | 1.8105e-07 | 149
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 24 | 1901 | 0.00034417 | 4.3451e-06 | 79.2083
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 852 | 0.00015425 | 1.8105e-07 | 852
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 4 | 156 | 20030 | 0.0036264 | 2.8243e-05 | 128.3974
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | FUSE | 1 | 1 | 56 | 1.0139e-05 | 1.8105e-07 | 56
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 324 | 3029 | 464512 | 0.0847 | 0.00055231 | 153.3549
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CUTOUT | 3 | 3249 | 287711 | 0.052462 | 0.00059243 | 88.5537
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CUTOUT | 8 | 310 | 75341 | 0.013738 | 5.6526e-05 | 243.0355
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 55 | 9154 | 1183899 | 0.21587 | 0.0016692 | 129.3313
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CROSSARM | 4 | 370 | 93263 | 0.017006 | 6.7467e-05 | 252.0622
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CABLE TERMINATOR | 9 | 58 | 17258 | 0.0031469 | 1.0576e-05 | 297.5517
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 3 | 526 | 33478 | 0.0061044 | 9.5912e-05 | 63.6464
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | JUMPER/RISER | 10 | 497 | 51653 | 0.0094185 | 9.0624e-05 | 103.9296
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | POLE HARDWARE | 1 | 100 | 25419 | 0.0045266 | 1.7808e-05 | 254.19
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | NONE | 2 | 2166 | 69822 | 0.012434 | 0.00038572 | 32.2355
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 1732 | 156604 | 0.027888 | 0.00030843 | 90.418
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 589 | 0.00010489 | 1.7808e-07 | 589
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | POLE | 1 | 33 | 1290 | 0.00023522 | 6.0173e-06 | 39.0909
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | POLE | 1 | 1 | 65 | 1.1705e-05 | 1.8007e-07 | 65
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | OTHER EQUIPMENT | 1 | 3 | 2544 | 0.0004581 | 5.4022e-07 | 848
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 38 | 1298 | 1231864 | 0.22302 | 0.000235 | 949.0478
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | NONE | 910 | 37951 | 1920488 | 0.3477 | 0.0068709 | 50.6044
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2606 | 115212 | 29911665 | 5.4154 | 0.020859 | 259.6228
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | METERING | 1 | 2 | 124 | 2.245e-05 | 3.6209e-07 | 62
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | NONE | 91 | 11517 | 557845 | 0.101 | 0.0020851 | 48.4367
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | METERING | 3 | 3 | 1234 | 0.00022341 | 5.4314e-07 | 411.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | UG | CONDUCTOR UG | 50 | 88 | 15271 | 0.0027648 | 1.5932e-05 | 173.5341
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 10 | 3014 | 86608 | 0.01568 | 0.00054567 | 28.7352
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | SWITCH, OH | 6 | 2931 | 314365 | 0.056915 | 0.00053065 | 107.2552
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 32 | 11766 | 554220 | 0.10034 | 0.0021302 | 47.1035
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONN/CLAMP | 40 | 118 | 10903 | 0.0019739 | 2.1363e-05 | 92.3983
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | FUSE | 31 | 317 | 16750 | 0.0030325 | 5.7392e-05 | 52.8391
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 3 | 24 | 4841 | 0.00087645 | 4.3451e-06 | 201.7083
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CAPACITOR | 11 | 6422 | 525819 | 0.095198 | 0.0011627 | 81.8778
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | ARRESTER | 1 | 82 | 9102 | 0.0016479 | 1.4846e-05 | 111
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | NONE | 26 | 388 | 72216 | 0.013074 | 7.0246e-05 | 186.1237
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 2 | 12 | 2.1726e-06 | 3.6209e-07 | 6
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | V | BREAKER | 3 | 993 | 12909 | 0.0023371 | 0.00017978 | 13
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CAPACITOR | 2 | 299 | 44512 | 0.0080587 | 5.4133e-05 | 148.8696
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 7 | 805 | 52783 | 0.0095562 | 0.00014574 | 65.5689
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 22 | 135 | 56017 | 0.010142 | 2.4441e-05 | 414.9407
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | NONE | 5 | 30 | 5443 | 0.00098544 | 5.4314e-06 | 181.4333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | ARRESTER | 3 | 343 | 33937 | 0.0061442 | 6.2099e-05 | 98.9417
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | FUSE | 7 | 537 | 42340 | 0.0076655 | 9.7222e-05 | 78.8454
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | TRANSFORMER, UG | 1 | 4 | 1364 | 0.00024695 | 7.2419e-07 | 341
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | FUSE | 2 | 19 | 1374 | 0.00024742 | 3.4214e-06 | 72.3158
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CABLE TERMINATOR | 10 | 23 | 3811 | 0.00068625 | 4.1417e-06 | 165.6957
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 5 | 934 | 154345 | 0.027682 | 0.00016751 | 165.2516
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 4 | 12 | 4435 | 0.00079862 | 2.1609e-06 | 369.5833
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | JUMPER/RISER | 4 | 368 | 50888 | 0.0091268 | 6.6001e-05 | 138.2826
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | FUSE | 1 | 2 | 368 | 6.6001e-05 | 3.587e-07 | 184
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | INSULATOR | 3 | 663 | 129758 | 0.023366 | 0.00011939 | 195.7134
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | PEDESTAL | 1 | 1 | 1737 | 0.00031278 | 1.8007e-07 | 1737
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONDUCTOR OVERHEAD | 5 | 219 | 46670 | 0.008404 | 3.9436e-05 | 213.105
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 5 | 1124 | 201134 | 0.036219 | 0.0002024 | 178.9448
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 4 | 19 | 4380 | 0.00078555 | 3.4077e-06 | 230.5263
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CUTOUT | 6 | 1583 | 175730 | 0.031517 | 0.00028391 | 111.0107
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 6 | 909 | 0.00016303 | 1.0761e-06 | 151.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | METERING | 2 | 1376 | 107376 | 0.019258 | 0.00024679 | 78.0349
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 1372 | 50907 | 5357361 | 0.95404 | 0.0090655 | 105.2382
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 5 | 2075 | 0.00036952 | 8.904e-07 | 415
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 103 | 28789 | 4079833 | 0.72654 | 0.0051267 | 141.715
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | NONE | 56 | 2722 | 1081110 | 0.19252 | 0.00048473 | 397.1749
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | NONE | 6 | 35 | 6136 | 0.0011005 | 6.2773e-06 | 175.3143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 78 | 4836 | 0.00086119 | 1.389e-05 | 62
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 14 | 27 | 2139 | 0.00038091 | 4.8082e-06 | 79.2222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 10 | 3489 | 153948 | 0.027415 | 0.00062132 | 44.1238
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | OTHER EQUIPMENT | 1 | 1 | 81 | 1.4527e-05 | 1.7935e-07 | 81
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | INSULATOR | 2 | 61 | 20839 | 0.0037375 | 1.094e-05 | 341.623
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 5 | 7 | 739 | 0.00013254 | 1.2555e-06 | 105.5714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 8 | 7232 | 0.0012971 | 1.4348e-06 | 904
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONN/CLAMP | 4 | 58 | 6571 | 0.0011702 | 1.0329e-05 | 113.2931
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE HARDWARE | 2 | 37 | 8698 | 0.0015489 | 6.589e-06 | 235.0811
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | NONE | 7 | 46 | 4377 | 0.00077946 | 8.1917e-06 | 95.1522
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | FUSE | 2 | 6 | 1185 | 0.00021253 | 1.0761e-06 | 197.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 30 | 61 | 7721 | 0.001375 | 1.0863e-05 | 126.5738
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 8 | 465 | 40885 | 0.0072808 | 8.2807e-05 | 87.9247
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 5 | 211 | 38364 | 0.0069083 | 3.7995e-05 | 181.8199
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UG | CONN/CLAMP | 2 | 18 | 954 | 0.00017179 | 3.2413e-06 | 53
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 624 | 27141 | 5177949 | 0.92867 | 0.0048677 | 190.7796
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 187 | 7494 | 1063814 | 0.1908 | 0.0013441 | 141.9554
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 677 | 3978 | 1032320 | 0.18515 | 0.00071346 | 259.5073
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 19 | 1043 | 218014 | 0.038824 | 0.00018574 | 209.0259
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 1 | 9 | 684 | 0.00012181 | 1.6027e-06 | 76
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 3 | 2295 | 0.00040869 | 5.3424e-07 | 765
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 5 | 2101 | 348348 | 0.062034 | 0.00037415 | 165.801
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UG | CUTOUT | 2 | 5 | 1007 | 0.00017933 | 8.904e-07 | 201.4
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | NONE | 6 | 10 | 1343 | 0.00023916 | 1.7808e-06 | 134.3
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | NONE | 2 | 5 | 639 | 0.00011379 | 8.904e-07 | 127.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | OTHER EQUIPMENT | 1 | 5 | 3950 | 0.00070342 | 8.904e-07 | 790
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | BREAKER | 4 | 3830 | 46978 | 0.0083658 | 0.00068205 | 12.2658
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 1 | 8 | 1.4246e-06 | 1.7808e-07 | 8
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | TRANSFORMER, UG | 1 | 8 | 752 | 0.00013392 | 1.4246e-06 | 94
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 3 | 1092 | 0.00019446 | 5.3424e-07 | 364
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CUTOUT | 4 | 13 | 1645 | 0.00029294 | 2.315e-06 | 126.5385
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | ARRESTER | 5 | 50 | 6313 | 0.0011368 | 9.0036e-06 | 126.26
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UB | CONN/CLAMP | 2 | 2 | 307 | 5.5282e-05 | 3.6014e-07 | 153.5
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | FUSE | 3 | 1179 | 70740 | 0.012687 | 0.00021145 | 60
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | POLE | 1 | 4 | 1696 | 0.00030418 | 7.174e-07 | 424
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | INSULATOR | 1 | 727 | 26899 | 0.0048243 | 0.00013039 | 37
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 54 | 3240 | 0.00058343 | 9.7239e-06 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 4 | 468 | 8.4274e-05 | 7.2029e-07 | 117
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 31 | 2393 | 0.00042614 | 5.5205e-06 | 77.1935
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 1472 | 217417 | 0.038718 | 0.00026213 | 147.7018
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | ERF | NONE | 2 | 1490 | 116220 | 0.020696 | 0.00026534 | 78
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | U | NONE | 1 | 15 | 1110 | 0.00019767 | 2.6712e-06 | 74
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 9 | 51 | 13467 | 0.0023982 | 9.0821e-06 | 264.0588
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SCO | REGULATOR | 6 | 3926 | 546105 | 0.098338 | 0.00070696 | 139.0996
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 3 | 8 | 2046 | 0.00037042 | 1.4484e-06 | 255.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | FUSE | 1 | 3 | 408 | 7.3867e-05 | 5.4314e-07 | 136
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | ARRESTER | 172 | 24910 | 2712286 | 0.49456 | 0.0045421 | 108.8834
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | NONE | 79 | 10557 | 858729 | 0.15658 | 0.001925 | 81.3421
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR UG | 20 | 30 | 5129 | 0.00093523 | 5.4703e-06 | 170.9667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 150 | 8289 | 2165284 | 0.39482 | 0.0015114 | 261.2238
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | INSULATOR | 2 | 2674 | 281238 | 0.051282 | 0.00048758 | 105.175
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | FUSE | 20 | 217 | 7266 | 0.0013249 | 3.9568e-05 | 33.4839
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 26 | 31 | 4661 | 0.0008499 | 5.6526e-06 | 150.3548
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 2 | 2622 | 78226 | 0.014264 | 0.0004781 | 29.8345
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | POLE | 10 | 3434 | 158618 | 0.028923 | 0.00062616 | 46.1904
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 61 | 1.1123e-05 | 1.8234e-07 | 61
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | REGULATOR | 16 | 10048 | 664599 | 0.12118 | 0.0018322 | 66.1424
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | CONDUCTOR UG | 3 | 4 | 2866 | 0.00052259 | 7.2937e-07 | 716.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | NONE | 10 | 80 | 11008 | 0.0020072 | 1.4587e-05 | 137.6
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 4 | 7 | 1579 | 0.00028792 | 1.2764e-06 | 225.5714
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONN/CLAMP | 52 | 148 | 20569 | 0.0036891 | 2.6544e-05 | 138.9797
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | REGULATOR | 7 | 4680 | 972609 | 0.17514 | 0.00084274 | 207.8224
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CUTOUT | 3 | 14 | 13080 | 0.0023553 | 2.521e-06 | 934.2857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 17 | 91 | 19334 | 0.0034676 | 1.6321e-05 | 212.4615
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONN/CLAMP | 2 | 6 | 2686 | 0.00048367 | 1.0804e-06 | 447.6667
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 7 | 768 | 0.0001383 | 1.2605e-06 | 109.7143
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CONN/CLAMP | 2 | 2 | 207 | 3.7275e-05 | 3.6014e-07 | 103.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 42 | 481 | 123625 | 0.022261 | 8.6615e-05 | 257.0166
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 8 | 339 | 25672 | 0.0046228 | 6.1044e-05 | 75.7286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 5 | 380 | 17318 | 0.0031185 | 6.8427e-05 | 45.5737
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | SPLICE, UG | 2 | 1705 | 28985 | 0.0051616 | 0.00030363 | 17
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1 | 111 | 1.9767e-05 | 1.7808e-07 | 111
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 1 | 41 | 7.3013e-06 | 1.7808e-07 | 41
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 70 | 1.2466e-05 | 1.7808e-07 | 70
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 11 | 1848 | 0.00033144 | 1.9729e-06 | 168
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 20 | 3540 | 0.0006349 | 3.587e-06 | 177
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 1 | 10 | 1.8234e-06 | 1.8234e-07 | 10
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 4605 | 2055304 | 0.36862 | 0.00082591 | 446.3201
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 19 | 52 | 7112 | 0.0012665 | 9.2601e-06 | 136.7692
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 1 | 79 | 1.4169e-05 | 1.7935e-07 | 79
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 13 | 5217 | 451749 | 0.080447 | 0.00092904 | 86.5917
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | CROSSARM | 1 | 1 | 237 | 4.2506e-05 | 1.7935e-07 | 237
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 8 | 480 | 8.6088e-05 | 1.4348e-06 | 60
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NETWORK LIMITER | 1 | 3 | 2244 | 0.00040246 | 5.3805e-07 | 748
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | TRANSFORMER, GROUNDING | 6 | 44 | 2636 | 0.00047467 | 7.9232e-06 | 59.9091
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | SCO | TRANSFORMER, POWER - LTC | 3 | 1027 | 7688 | 0.0013919 | 0.00018593 | 7.4859
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 326 | 4313 | 428184 | 0.076251 | 0.00076806 | 99.2775
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 10 | 344 | 29288 | 0.0052156 | 6.1259e-05 | 85.1395
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | JUMPER/RISER | 1 | 105 | 66390 | 0.011907 | 1.8832e-05 | 632.2857
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABX | BREAKER | 1 | 902 | 83886 | 0.015045 | 0.00016177 | 93
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CROSSARM | 5 | 4355 | 1006603 | 0.18224 | 0.00078846 | 231.1373
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 1 | 571 | 0.00010338 | 1.8105e-07 | 571
AEP Total | 2021 | 5523447 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 2 | 6 | 200 | 3.6209e-05 | 1.0863e-06 | 33.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 10 | 85 | 15987 | 0.0029151 | 1.5499e-05 | 188.0824
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 1 | 203 | 3.7015e-05 | 1.8234e-07 | 203
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 38 | 13298 | 0.0024248 | 6.929e-06 | 349.9474
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CUTOUT | 3 | 7 | 442 | 8.0595e-05 | 1.2764e-06 | 63.1429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 176 | 13751 | 0.0025074 | 3.2092e-05 | 78.1307
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 2 | 14 | 1126 | 0.00020532 | 2.5528e-06 | 80.4286
AEP Total | 2020 | 5484199 | PARTIAL POWER | FW | CONN/CLAMP | 1 | 5 | 200 | 3.6468e-05 | 9.1171e-07 | 40
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 936 | 0.00016946 | 1.8105e-07 | 936
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | ARRESTER | 5 | 134 | 12016 | 0.0021755 | 2.426e-05 | 89.6716
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 3 | 180 | 3.2822e-05 | 5.4703e-07 | 60
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | POLE HARDWARE | 2 | 60 | 1932 | 0.00034978 | 1.0863e-05 | 32.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CUTOUT | 2 | 13 | 6177 | 0.0011123 | 2.3409e-06 | 475.1538
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 6 | 67 | 6627 | 0.0011801 | 1.1931e-05 | 98.9104
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 20 | 272 | 44338 | 0.0078957 | 4.8438e-05 | 163.0074
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | V | OTHER EQUIPMENT | 10 | 8971 | 1209814 | 0.21544 | 0.0015976 | 134.8583
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 3101 | 0.00055223 | 1.7808e-07 | 3101
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | RELAY | 1 | 1345 | 182593 | 0.032516 | 0.00023952 | 135.7569
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | NONE | 148 | 6637 | 1132110 | 0.20496 | 0.0012016 | 170.5756
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONDUCTOR UG | 417 | 3287 | 426075 | 0.077139 | 0.0005951 | 129.6243
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | POLE HARDWARE | 23 | 136 | 16041 | 0.0029042 | 2.4622e-05 | 117.9485
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | ARRESTER | 46 | 1357 | 178515 | 0.032319 | 0.00024568 | 131.5512
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1201 | 69702 | 0.012619 | 0.00021744 | 58.0366
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | REGULATOR | 8 | 8095 | 451113 | 0.081672 | 0.0014656 | 55.7274
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, OH | 33 | 132 | 25982 | 0.0047039 | 2.3898e-05 | 196.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | NONE | 53 | 4274 | 303631 | 0.054971 | 0.00077379 | 71.0414
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | INSULATOR | 2 | 49 | 5579 | 0.0010101 | 8.8713e-06 | 113.8571
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 43 | 2184 | 313398 | 0.05674 | 0.00039541 | 143.4973
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 1882 | 707632 | 0.12811 | 0.00034073 | 376
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 90 | 1.6294e-05 | 1.8105e-07 | 90
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 3 | 115 | 49616 | 0.0089828 | 2.082e-05 | 431.4435
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | NONE | 2 | 8 | 1096 | 0.00019843 | 1.4484e-06 | 137
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | INSULATOR | 7 | 351 | 82486 | 0.014934 | 6.3547e-05 | 235.0028
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | METERING | 2 | 2 | 338 | 6.1194e-05 | 3.6209e-07 | 169
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CIRCUIT SWITCHER | 2 | 2 | 275 | 4.9788e-05 | 3.6209e-07 | 137.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CONN/CLAMP | 1 | 1 | 33 | 5.9745e-06 | 1.8105e-07 | 33
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 1806 | 138411 | 0.025059 | 0.00032697 | 76.6395
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | FUSE | 4 | 22 | 2856 | 0.00051429 | 3.9616e-06 | 129.8182
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | NONE | 149 | 1230 | 228798 | 0.0412 | 0.00022149 | 186.0146
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 802 | 66337 | 9535206 | 1.717 | 0.011945 | 143.7389
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 20 | 483 | 15394 | 0.002772 | 8.6975e-05 | 31.8716
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE | 9 | 771 | 221902 | 0.039958 | 0.00013884 | 287.8106
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | NONE | 114 | 369 | 31795 | 0.0057254 | 6.6447e-05 | 86.1653
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONN/CLAMP | 5 | 17 | 1782 | 0.00032089 | 3.0612e-06 | 104.8235
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CUTOUT | 38 | 1429 | 453902 | 0.081735 | 0.00025732 | 317.6361
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | FUSE | 67 | 1288 | 74778 | 0.013465 | 0.00023193 | 58.0575
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, OH | 26 | 33 | 4646 | 0.00083661 | 5.9424e-06 | 140.7879
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | POLE HARDWARE | 2 | 1326 | 29172 | 0.0052531 | 0.00023878 | 22
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 28 | 1470 | 141331 | 0.02545 | 0.00026471 | 96.1435
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CAPACITOR | 1 | 753 | 18072 | 0.0032412 | 0.00013505 | 24
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 5143 | 241546 | 0.043496 | 0.00092611 | 46.966
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | FUSE | 5 | 253 | 15825 | 0.0028382 | 4.5376e-05 | 62.5494
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE | 9 | 920 | 430622 | 0.07852 | 0.00016775 | 468.0674
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 19 | 308 | 34250 | 0.0062452 | 5.6161e-05 | 111.2013
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CUTOUT | 7 | 424 | 10402 | 0.0018967 | 7.7313e-05 | 24.533
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 9 | 24 | 3172 | 0.00057839 | 4.3762e-06 | 132.1667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 19 | 163 | 6167 | 0.0011245 | 2.9722e-05 | 37.8344
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RELAY | 1 | 186 | 42036 | 0.0076649 | 3.3916e-05 | 226
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SWITCH, OH | 3 | 943 | 157426 | 0.028705 | 0.00017195 | 166.9417
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 3 | 3273 | 0.00059681 | 5.4703e-07 | 1091
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 102 | 11824 | 0.002156 | 1.8599e-05 | 115.9216
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | SWITCH, UG | 1 | 12 | 3156 | 0.00057547 | 2.1881e-06 | 263
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 1 | 5 | 275 | 5.0144e-05 | 9.1171e-07 | 55
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | SWITCH, OH | 5 | 324 | 52331 | 0.0093856 | 5.8109e-05 | 161.5154
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONN/CLAMP | 4 | 14 | 1474 | 0.00026436 | 2.5109e-06 | 105.2857
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | NONE | 5 | 23 | 2207 | 0.00039583 | 4.1251e-06 | 95.9565
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CAPACITOR | 5 | 3443 | 481683 | 0.08639 | 0.0006175 | 139.9021
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | POLE | 1 | 2 | 20 | 3.587e-06 | 3.587e-07 | 10
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 7 | 17 | 1644 | 0.00029485 | 3.049e-06 | 96.7059
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 541 | 1053 | 183065 | 0.0326 | 0.00018752 | 173.8509
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | NONE | 60 | 5231 | 387891 | 0.069076 | 0.00093154 | 74.1524
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 7 | 4401 | 427449 | 0.07612 | 0.00078373 | 97.1254
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CABLE TERMINATOR | 1 | 1 | 114 | 2.0301e-05 | 1.7808e-07 | 114
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CROSSARM | 3 | 7 | 406 | 7.23e-05 | 1.2466e-06 | 58
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WU | NONE | 8 | 8640 | 582825 | 0.10379 | 0.0015386 | 67.4566
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WU | BREAKER | 1 | 3148 | 199416 | 0.035512 | 0.0005606 | 63.3469
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 34 | 3430 | 0.00061081 | 6.0547e-06 | 100.8824
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | POLE | 1 | 1 | 150 | 2.6712e-05 | 1.7808e-07 | 150
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | NONE | 1 | 1 | 58 | 1.0329e-05 | 1.7808e-07 | 58
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 67 | 1.1931e-05 | 1.7808e-07 | 67
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 10 | 1257 | 0.00022385 | 1.7808e-06 | 125.7
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 444 | 70170 | 0.012496 | 7.9067e-05 | 158.0405
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 4 | 426 | 41866 | 0.0074555 | 7.5862e-05 | 98.277
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 5 | 1420 | 0.00025287 | 8.904e-07 | 284
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 5 | 76 | 17273 | 0.003076 | 1.3534e-05 | 227.2763
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 3 | 7 | 426 | 7.5862e-05 | 1.2466e-06 | 60.8571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 3113 | 662245 | 0.11925 | 0.00056056 | 212.7353
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | CF | ARRESTER | 1 | 2180 | 303536 | 0.054658 | 0.00039256 | 139.2367
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | ARRESTER | 2 | 2 | 201 | 3.6194e-05 | 3.6014e-07 | 100.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 9 | 357 | 13809 | 0.0024591 | 6.3574e-05 | 38.6807
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 68 | 7574 | 0.0013488 | 1.2109e-05 | 111.3824
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 1883 | 30128 | 0.0053652 | 0.00033532 | 16
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | FUSE | 2 | 91 | 16561 | 0.0029492 | 1.6205e-05 | 181.989
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | METERING | 1 | 1 | 51 | 9.0821e-06 | 1.7808e-07 | 51
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | BREAKER | 1 | 1 | 52 | 9.2601e-06 | 1.7808e-07 | 52
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 228 | 4.0602e-05 | 1.7808e-07 | 228
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 92 | 1.6775e-05 | 1.8234e-07 | 92
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 2 | 7 | 1895 | 0.00034124 | 1.2605e-06 | 270.7143
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 2 | 4808 | 263000 | 0.047359 | 0.00086579 | 54.7005
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 8 | 2256 | 0.00040624 | 1.4406e-06 | 282
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | INSULATOR | 1 | 941 | 251545 | 0.045867 | 0.00017158 | 267.3167
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | SWITCH, UG | 2 | 1605 | 275726 | 0.049452 | 0.00028786 | 171.7919
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 117 | 2.1068e-05 | 1.8007e-07 | 117
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 61 | 1.094e-05 | 1.7935e-07 | 61
AEP Total | 2023 | 5575683 | PARTIAL POWER | AF | CONDUCTOR UG | 1 | 2 | 402 | 7.2099e-05 | 3.587e-07 | 201
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | SCO | REGULATOR | 3 | 288 | 17881 | 0.0031842 | 5.1287e-05 | 62.0868
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | FUSE | 2 | 3 | 348 | 6.1972e-05 | 5.3424e-07 | 116
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CIRCUIT SWITCHER | 1 | 1 | 183 | 3.3369e-05 | 1.8234e-07 | 183
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 1 | 1 | 240 | 4.3044e-05 | 1.7935e-07 | 240
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | SPLICE, OH | 1 | 1 | 50 | 9.1171e-06 | 1.8234e-07 | 50
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 22 | 1914 | 0.00034328 | 3.9457e-06 | 87
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 2 | 2 | 275 | 4.9321e-05 | 3.587e-07 | 137.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | RECLOSER, LINE/OCR/BR | 3 | 43 | 984 | 0.00017648 | 7.7121e-06 | 22.8837
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | NONE | 81 | 4831 | 412606 | 0.075235 | 0.00088089 | 85.408
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | NONE | 26 | 1079 | 23881 | 0.0043545 | 0.00019675 | 22.1325
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | METERING | 4 | 115 | 122339 | 0.02203 | 2.0708e-05 | 1063.8174
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CUTOUT | 7 | 232 | 22860 | 0.0041164 | 4.1777e-05 | 98.5345
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, UG | 13 | 54 | 19321 | 0.0034792 | 9.7239e-06 | 357.7963
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 5 | 67 | 8123 | 0.0014627 | 1.2065e-05 | 121.2388
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | JUMPER/RISER | 2 | 76 | 13946 | 0.0025113 | 1.3685e-05 | 183.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SCO | CONDUCTOR OVERHEAD | 581 | 7381 | 788178 | 0.14136 | 0.0013238 | 106.7847
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | NONE | 273 | 25950 | 2136404 | 0.38316 | 0.0046541 | 82.3277
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | ARRESTER | 39 | 890 | 176524 | 0.03166 | 0.00015962 | 198.3416
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | V | NONE | 5 | 2268 | 723340 | 0.13025 | 0.0004084 | 318.933
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | POLE | 4 | 66 | 14785 | 0.0026624 | 1.1885e-05 | 224.0152
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 8 | 2140 | 182886 | 0.032933 | 0.00038535 | 85.4607
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | NONE | 83 | 3526 | 368060 | 0.066012 | 0.00063239 | 104.3846
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 67 | 19162 | 0.0034505 | 1.2065e-05 | 286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 699 | 15467 | 1958613 | 0.35128 | 0.002774 | 126.6317
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 40 | 182 | 53569 | 0.0095396 | 3.2411e-05 | 294.3352
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 73 | 3059 | 386164 | 0.068768 | 0.00054475 | 126.2386
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 7 | 2914 | 769956 | 0.13711 | 0.00051892 | 264.2265
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 18 | 234 | 4.1968e-05 | 3.2283e-06 | 13
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CUTOUT | 1 | 28 | 5264 | 0.0009479 | 5.042e-06 | 188
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 120 | 21048 | 0.0037902 | 2.1609e-05 | 175.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | FUSE | 3 | 318 | 17232 | 0.0031198 | 5.7573e-05 | 54.1887
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | SCO | NONE | 6 | 4645 | 66471 | 0.011837 | 0.00082718 | 14.3102
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 615 | 20376 | 6664014 | 1.1867 | 0.0036286 | 327.0521
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE | 193 | 35280 | 6836461 | 1.2174 | 0.0062827 | 193.7772
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 76 | 4843 | 1371557 | 0.24425 | 0.00086244 | 283.204
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | NONE | 74 | 1274 | 230160 | 0.040987 | 0.00022687 | 180.6593
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 2 | 211 | 167769 | 0.03021 | 3.7995e-05 | 795.1137
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 9 | 2070 | 0.00037275 | 1.6206e-06 | 230
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | TRANSFORMER, OH | 2 | 3 | 584 | 0.000104 | 5.3424e-07 | 194.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | OTHER EQUIPMENT | 1 | 1 | 279 | 4.9684e-05 | 1.7808e-07 | 279
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 3 | 3 | 1191 | 0.00021209 | 5.3424e-07 | 397
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 57 | 57342 | 0.010211 | 1.0151e-05 | 1006
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | POLE | 1 | 4 | 11344 | 0.0020201 | 7.1232e-07 | 2836
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | TRANSFORMER, GROUNDING | 1 | 2 | 102 | 1.8294e-05 | 3.587e-07 | 51
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 2 | 9 | 1542 | 0.00027656 | 1.6142e-06 | 171.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | FUSE | 3 | 18 | 2338 | 0.00042632 | 3.2822e-06 | 129.8889
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 2 | 72 | 104719 | 0.019095 | 1.3129e-05 | 1454.4306
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 23 | 1863 | 0.0003397 | 4.1939e-06 | 81
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SO | CONDUCTOR OVERHEAD | 1 | 1 | 317 | 5.7802e-05 | 1.8234e-07 | 317
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | INSULATOR | 1 | 1 | 226 | 4.1209e-05 | 1.8234e-07 | 226
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 1 | 59 | 43719 | 0.0079718 | 1.0758e-05 | 741
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | JUMPER/RISER | 1 | 1 | 139 | 2.5165e-05 | 1.8105e-07 | 139
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 2 | 30 | 5804 | 0.0010508 | 5.4314e-06 | 193.4667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | NONE | 8 | 159 | 17899 | 0.0031875 | 2.8315e-05 | 112.5723
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | ARRESTER | 6 | 930 | 147111 | 0.026197 | 0.00016561 | 158.1839
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | NONE | 22 | 13429 | 1116755 | 0.19887 | 0.0023914 | 83.16
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | SCO | REGULATOR | 3 | 892 | 17424 | 0.0031029 | 0.00015885 | 19.5336
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | CONDUCTOR UG | 4 | 6 | 571 | 0.00010168 | 1.0685e-06 | 95.1667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CUTOUT | 12 | 1471 | 186252 | 0.033539 | 0.00026489 | 126.6159
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | NONE | 1 | 10 | 4640 | 0.00083553 | 1.8007e-06 | 464
AEP Total | 2022 | 5553337 | PARTIAL POWER | OU | NONE | 1 | 1 | 143 | 2.575e-05 | 1.8007e-07 | 143
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 11 | 140 | 22890 | 0.0041218 | 2.521e-05 | 163.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | FUSE | 48 | 876 | 174842 | 0.031358 | 0.00015711 | 199.5913
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CUTOUT | 13 | 162 | 21146 | 0.0038078 | 2.9172e-05 | 130.5309
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | NETWORK TRANSFORMER | 1 | 1 | 2774 | 0.00049752 | 1.7935e-07 | 2774
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | FUSE | 27 | 1122 | 151423 | 0.027158 | 0.00020123 | 134.9581
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | RELAY | 15 | 6135 | 311139 | 0.055803 | 0.0011003 | 50.7154
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | SWITCH, UG | 1 | 199 | 61690 | 0.011064 | 3.5691e-05 | 310
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 35 | 1017 | 188842 | 0.033869 | 0.0001824 | 185.6853
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 2080 | 147680 | 0.026593 | 0.00037455 | 71
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | NONE | 15 | 2323 | 221022 | 0.03964 | 0.00041663 | 95.1451
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CUTOUT | 1 | 1 | 118 | 2.1248e-05 | 1.8007e-07 | 118
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | ARRESTER | 75 | 623 | 75996 | 0.013759 | 0.00011279 | 121.9839
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR UG | 36 | 121 | 43884 | 0.007945 | 2.1907e-05 | 362.6777
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 10 | 155 | 35911 | 0.0065016 | 2.8062e-05 | 231.6839
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CUTOUT | 13 | 279 | 42169 | 0.0076345 | 5.0512e-05 | 151.1434
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 913 | 228250 | 0.041324 | 0.0001653 | 250
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 118 | 2987 | 831433 | 0.15053 | 0.00054079 | 278.3505
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONN/CLAMP | 718 | 2033 | 262107 | 0.047454 | 0.00036807 | 128.9262
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 5 | 4976 | 287177 | 0.051992 | 0.00090089 | 57.7124
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 4 | 592 | 104291 | 0.01878 | 0.0001066 | 176.1672
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | SCO | INSULATOR | 10 | 1121 | 18305 | 0.0032962 | 0.00020186 | 16.3292
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | POLE | 7 | 4100 | 239190 | 0.043071 | 0.00073829 | 58.339
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 101 | 1.8187e-05 | 1.8007e-07 | 101
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 2 | 20 | 1723 | 0.00031026 | 3.6014e-06 | 86.15
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | NONE | 5 | 4846 | 723097 | 0.12969 | 0.00086913 | 149.2152
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | ABI | NONE | 1 | 892 | 243516 | 0.04385 | 0.00016062 | 273
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | GUY/ANCHOR | 1 | 2 | 48 | 8.6435e-06 | 3.6014e-07 | 24
AEP Total | 2023 | 5575683 | PARTIAL POWER | V | CONDUCTOR OVERHEAD | 5 | 9 | 743 | 0.00013326 | 1.6142e-06 | 82.5556
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | METERING | 1 | 1 | 100 | 1.8007e-05 | 1.8007e-07 | 100
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CROSSARM | 2 | 3 | 536 | 9.6519e-05 | 5.4022e-07 | 178.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, UG | 7 | 14 | 3555 | 0.00063759 | 2.5109e-06 | 253.9286
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONN/CLAMP | 8 | 8 | 3056 | 0.00054809 | 1.4348e-06 | 382
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONN/CLAMP | 5 | 1631 | 54006 | 0.009686 | 0.00029252 | 33.1122
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | NONE | 5 | 6 | 881 | 0.00015801 | 1.0761e-06 | 146.8333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 162 | 17526 | 3159365 | 0.56262 | 0.003121 | 180.2673
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | NONE | 261 | 27707 | 3466290 | 0.61728 | 0.0049341 | 125.1052
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CUTOUT | 4 | 2259 | 130033 | 0.02371 | 0.00041191 | 57.5622
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 9 | 9850 | 2861631 | 0.5218 | 0.0017961 | 290.5209
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 4 | 57 | 3618 | 0.00065971 | 1.0393e-05 | 63.4737
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | GUY/ANCHOR | 10 | 38 | 896 | 0.00016338 | 6.929e-06 | 23.5789
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 25 | 71 | 26324 | 0.0048 | 1.2946e-05 | 370.7606
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 12 | 36 | 11897 | 0.0021693 | 6.5643e-06 | 330.4722
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | R | NONE | 6 | 1507 | 244091 | 0.044508 | 0.00027479 | 161.9715
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | POLE | 1 | 50 | 5150 | 0.00093906 | 9.1171e-06 | 103
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | NONE | 1 | 2 | 274 | 4.9962e-05 | 3.6468e-07 | 137
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 11 | 6408 | 0.0011684 | 2.0058e-06 | 582.5455
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | SCO | REGULATOR | 4 | 2620 | 950995 | 0.17341 | 0.00047774 | 362.9752
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | SWITCH, UG | 4 | 980 | 110087 | 0.020073 | 0.0001787 | 112.3337
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | NONE | 211 | 5900 | 1031121 | 0.18362 | 0.0010507 | 174.7663
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 3 | 703 | 0.00012519 | 5.3424e-07 | 234.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | SO | TRANSFORMER, OH | 1 | 6 | 900 | 0.00016142 | 1.0761e-06 | 150
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | NONE | 4 | 5 | 401 | 7.1919e-05 | 8.9675e-07 | 80.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 10 | 108 | 12924 | 0.0023015 | 1.9233e-05 | 119.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | NONE | 738 | 10630 | 729194 | 0.13131 | 0.0019142 | 68.5977
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR UG | 568 | 1003 | 214380 | 0.038604 | 0.00018061 | 213.7388
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 53 | 1387 | 252019 | 0.045382 | 0.00024976 | 181.7008
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 121 | 2638 | 695773 | 0.12529 | 0.00047503 | 263.7502
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | FUSE | 22 | 53 | 6257 | 0.0011267 | 9.5438e-06 | 118.0566
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | NONE | 48 | 2087 | 160715 | 0.02894 | 0.00037581 | 77.0077
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | NONE | 159 | 22332 | 3126867 | 0.56306 | 0.0040214 | 140.0173
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 58 | 2174 | 400968 | 0.072203 | 0.00039148 | 184.4379
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | JUMPER/RISER | 8 | 5932 | 790784 | 0.1424 | 0.0010682 | 133.3082
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CUTOUT | 2 | 10 | 33816 | 0.0061223 | 1.8105e-06 | 3381.6
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 767 | 24920 | 0.0045117 | 0.00013886 | 32.4902
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 9 | 378 | 6.8436e-05 | 1.6294e-06 | 42
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABI | OTHER EQUIPMENT | 1 | 1377 | 247860 | 0.044874 | 0.0002493 | 180
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 40 | 4600 | 0.00083281 | 7.2419e-06 | 115
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | POLE HARDWARE | 1 | 1 | 248 | 4.4899e-05 | 1.8105e-07 | 248
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CAPACITOR | 2 | 1375 | 79482 | 0.01439 | 0.00024894 | 57.8051
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 597 | 86188 | 0.015604 | 0.00010808 | 144.3685
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | JUMPER/RISER | 1 | 1 | 25 | 4.5262e-06 | 1.8105e-07 | 25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | CONDUCTOR UG | 1 | 1 | 191 | 3.458e-05 | 1.8105e-07 | 191
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 657 | 31496 | 5946962 | 1.0844 | 0.005743 | 188.8164
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 49 | 1101 | 237362 | 0.043281 | 0.00020076 | 215.5876
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | INSULATOR | 15 | 164 | 7625 | 0.0013904 | 2.9904e-05 | 46.4939
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 1112 | 49727 | 0.0090029 | 0.00020132 | 44.7185
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 2463 | 115554 | 28744089 | 5.176 | 0.020808 | 248.7503
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONN/CLAMP | 765 | 1909 | 238235 | 0.042899 | 0.00034376 | 124.7957
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | NONE | 55 | 2680 | 247736 | 0.04461 | 0.00048259 | 92.4388
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CUTOUT | 10 | 31 | 3420 | 0.00061585 | 5.5822e-06 | 110.3226
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, OH | 31 | 111 | 39910 | 0.0071867 | 1.9988e-05 | 359.5495
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | FUSE | 20 | 516 | 52759 | 0.0095004 | 9.2917e-05 | 102.2461
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CUTOUT | 4 | 6 | 1682 | 0.00030452 | 1.0863e-06 | 280.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | R | POLE | 1 | 782 | 4692 | 0.00084947 | 0.00014158 | 6
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CROSSARM | 1 | 7 | 1288 | 0.00023319 | 1.2673e-06 | 184
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | FUSE | 5 | 36 | 6997 | 0.0012668 | 6.5177e-06 | 194.3611
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONN/CLAMP | 1 | 10 | 1040 | 0.00018829 | 1.8105e-06 | 104
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | POLE | 3126 | 23155 | 2871197 | 0.52354 | 0.0042221 | 123.999
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | SCO | ARRESTER | 82 | 424 | 11639 | 0.0021223 | 7.7313e-05 | 27.4505
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 103 | 2938 | 790920 | 0.14422 | 0.00053572 | 269.2035
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 615 | 84605 | 0.015427 | 0.00011214 | 137.5691
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | CONN/CLAMP | 1 | 1 | 274 | 4.934e-05 | 1.8007e-07 | 274
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | INSULATOR | 9 | 2483 | 333624 | 0.060076 | 0.00044712 | 134.3633
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | NONE | 108 | 19025 | 720798 | 0.12928 | 0.0034121 | 37.8869
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | NONE | 46 | 324 | 27542 | 0.0049595 | 5.8343e-05 | 85.0062
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | FUSE | 15 | 64 | 5862 | 0.0010556 | 1.1525e-05 | 91.5938
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 4 | 491 | 106314 | 0.019144 | 8.8415e-05 | 216.5255
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UG | NONE | 67 | 1922 | 183610 | 0.03293 | 0.00034471 | 95.5307
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | NONE | 7 | 10 | 2534 | 0.0004563 | 1.8007e-06 | 253.4
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | NONE | 129 | 854 | 80341 | 0.014409 | 0.00015317 | 94.0761
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 16 | 2629 | 0.00047341 | 2.8812e-06 | 164.3125
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | REGULATOR | 2 | 711 | 25994 | 0.0046808 | 0.00012803 | 36.5598
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 2 | 218 | 3.9256e-05 | 3.6014e-07 | 109
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | NONE | 9 | 40 | 2733 | 0.00049214 | 7.2029e-06 | 68.325
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CUTOUT | 1748 | 72502 | 7172660 | 1.2986 | 0.013126 | 98.9305
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | POLE | 3 | 41 | 4837 | 0.00087572 | 7.4229e-06 | 117.9756
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 4 | 113 | 20391 | 0.0036917 | 2.0458e-05 | 180.4513
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | CONN/CLAMP | 35 | 336 | 16495 | 0.0029864 | 6.0832e-05 | 49.0923
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 2 | 308 | 5.5762e-05 | 3.6209e-07 | 154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE | 10 | 294 | 118750 | 0.021499 | 5.3228e-05 | 403.9116
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 12 | 255 | 4.6167e-05 | 2.1726e-06 | 21.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 12 | 5651 | 679470 | 0.12302 | 0.0010231 | 120.2389
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 8 | 91 | 11773 | 0.0021315 | 1.6475e-05 | 129.3736
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 15 | 390 | 7.0608e-05 | 2.7157e-06 | 26
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 21 | 289 | 60824 | 0.011012 | 5.2322e-05 | 210.4637
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 147 | 14831 | 2298111 | 0.41606 | 0.0026851 | 154.9532
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 41 | 1875 | 580263 | 0.10505 | 0.00033946 | 309.4736
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 37 | 19272 | 2652490 | 0.48022 | 0.0034891 | 137.6344
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 9 | 4060 | 318912 | 0.057738 | 0.00073505 | 78.5498
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE | 124 | 23280 | 4447968 | 0.80529 | 0.0042148 | 191.0639
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | NONE | 163 | 22992 | 2947654 | 0.53366 | 0.0041626 | 128.2035
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | NONE | 1957 | 93951 | 15779365 | 2.8568 | 0.017009 | 167.9531
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UG | CONDUCTOR UG | 164 | 12521 | 1234146 | 0.22344 | 0.0022669 | 98.5661
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | NONE | 3319 | 188038 | 15725983 | 2.8471 | 0.034044 | 83.6319
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 5 | 11 | 2461 | 0.00044556 | 1.9915e-06 | 223.7273
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | R | NONE | 9 | 13721 | 1115636 | 0.20198 | 0.0024841 | 81.3087
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 4 | 48 | 8.6902e-06 | 7.2419e-07 | 12
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | SCO | TRANSFORMER, POWER - LTC | 1 | 2 | 282 | 5.1055e-05 | 3.6209e-07 | 141
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | NETWORK PROTECTOR | 1 | 4 | 1644 | 0.00029764 | 7.2419e-07 | 411
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 3 | 48 | 5321 | 0.00096335 | 8.6902e-06 | 110.8542
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 10 | 1366 | 183202 | 0.033168 | 0.00024731 | 134.1157
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 1761 | 417219 | 0.075536 | 0.00031882 | 236.9216
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | ARRESTER | 7 | 4109 | 489674 | 0.088654 | 0.00074392 | 119.1711
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | POLE | 8 | 305 | 25261 | 0.0045734 | 5.5219e-05 | 82.823
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, OH | 23 | 15803 | 1326500 | 0.24016 | 0.0028611 | 83.9398
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 22 | 2084 | 71891 | 0.013016 | 0.0003773 | 34.4966
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | ARRESTER | 8 | 39 | 3917 | 0.00070916 | 7.0608e-06 | 100.4359
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | NONE | 60 | 5524 | 454613 | 0.082306 | 0.0010001 | 82.2978
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | FUSE | 1 | 36 | 7308 | 0.0013231 | 6.5177e-06 | 203
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | TRANSFORMER, OH | 1 | 2 | 128 | 2.334e-05 | 3.6468e-07 | 64
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | NONE | 1 | 1 | 53 | 9.6641e-06 | 1.8234e-07 | 53
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | POLE | 1 | 4 | 228 | 4.0892e-05 | 7.174e-07 | 57
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 91 | 1.6593e-05 | 1.8234e-07 | 91
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 2 | 134 | 2.4434e-05 | 3.6468e-07 | 67
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 4 | 43 | 7063 | 0.0012668 | 7.7121e-06 | 164.2558
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | NONE | 5 | 2723 | 254144 | 0.045581 | 0.00048837 | 93.3324
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | FW | NONE | 14 | 4259 | 185079 | 0.032959 | 0.00075844 | 43.456
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 131 | 265 | 27951 | 0.0049775 | 4.7191e-05 | 105.4755
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 129 | 2679 | 602241 | 0.10725 | 0.00047708 | 224.8007
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | NONE | 22 | 1385 | 607268 | 0.10814 | 0.00024664 | 438.4606
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 76 | 5456 | 1364968 | 0.24307 | 0.0009716 | 250.1774
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 47 | 64 | 6877 | 0.0012247 | 1.1397e-05 | 107.4531
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | NONE | 85 | 240 | 17391 | 0.003097 | 4.2739e-05 | 72.4625
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | ARRESTER | 3 | 1809 | 164316 | 0.02947 | 0.00032444 | 90.8325
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | POLE | 1 | 725 | 30450 | 0.0054612 | 0.00013003 | 42
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | NONE | 20 | 21 | 1909 | 0.00033995 | 3.7397e-06 | 90.9048
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 280 | 24634 | 0.0043868 | 4.9862e-05 | 87.9786
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | NONE | 10 | 824 | 58823 | 0.010475 | 0.00014674 | 71.3871
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 10 | 43 | 2838 | 0.00050539 | 7.6574e-06 | 66
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | GUY/ANCHOR | 2 | 73 | 5402 | 0.00096885 | 1.3093e-05 | 74
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 1 | 71 | 1.2854e-05 | 1.8105e-07 | 71
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 14 | 13898 | 925484 | 0.16665 | 0.0025026 | 66.5912
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 5 | 635 | 0.00011435 | 9.0036e-07 | 127
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | NONE | 1 | 1 | 136 | 2.4799e-05 | 1.8234e-07 | 136
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 1 | 43 | 7.7431e-06 | 1.8007e-07 | 43
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | WI | NONE | 4 | 3248 | 25984 | 0.0046602 | 0.00058253 | 8
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 85 | 1.5137e-05 | 1.7808e-07 | 85
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | FW | NONE | 2 | 1716 | 72072 | 0.012835 | 0.00030558 | 42
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 176 | 10544 | 0.0018777 | 3.1342e-05 | 59.9091
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 11 | 261 | 80656 | 0.014363 | 4.6479e-05 | 309.0268
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | ARRESTER | 9 | 6978 | 610323 | 0.10869 | 0.0012426 | 87.4639
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | U | NONE | 7 | 2555 | 31170 | 0.0055507 | 0.00045499 | 12.1996
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 3 | 33 | 1422 | 0.00025323 | 5.8766e-06 | 43.0909
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 2 | 7 | 611 | 0.00010881 | 1.2466e-06 | 87.2857
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 52 | 4638 | 544801 | 0.097018 | 0.00082593 | 117.4646
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | FUSE | 3 | 4 | 281 | 5.004e-05 | 7.1232e-07 | 70.25
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 7 | 1332 | 79814 | 0.014213 | 0.0002372 | 59.9204
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | INSULATOR | 7 | 1202 | 162726 | 0.028978 | 0.00021405 | 135.3794
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | SPLICE, OH | 1 | 4 | 296 | 5.3301e-05 | 7.2029e-07 | 74
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 2 | 2 | 140 | 2.5346e-05 | 3.6209e-07 | 70
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 43 | 8716 | 0.0015521 | 7.6574e-06 | 202.6977
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 5 | 2027 | 345476 | 0.061522 | 0.00036097 | 170.4371
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 2 | 3 | 341 | 6.0725e-05 | 5.3424e-07 | 113.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | FUSE | 1 | 2 | 42 | 7.4794e-06 | 3.5616e-07 | 21
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | METERING | 2 | 2 | 155 | 2.7602e-05 | 3.5616e-07 | 77.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 2 | 2 | 160 | 2.8493e-05 | 3.5616e-07 | 80
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | U | RELAY | 13 | 7134 | 56467 | 0.010056 | 0.0012704 | 7.9152
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | FW | NONE | 4 | 963 | 131974 | 0.023502 | 0.00017149 | 137.0447
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CUTOUT | 1 | 2 | 108 | 1.9233e-05 | 3.5616e-07 | 54
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | FO | NONE | 1 | 1663 | 84769 | 0.015096 | 0.00029615 | 50.9735
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 1 | 2 | 94 | 1.674e-05 | 3.5616e-07 | 47
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | BREAKER | 1 | 140 | 10362 | 0.0018453 | 2.4931e-05 | 74.0143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 16 | 1382 | 0.00024611 | 2.8493e-06 | 86.375
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 36 | 10431 | 0.0018576 | 6.4109e-06 | 289.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 3 | 535 | 9.5273e-05 | 5.3424e-07 | 178.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | REGULATOR | 1 | 314 | 4082 | 0.00072692 | 5.5917e-05 | 13
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WU | NONE | 2 | 1604 | 235660 | 0.041966 | 0.00028564 | 146.9202
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | WL | POLE | 1 | 168 | 8400 | 0.0014959 | 2.9917e-05 | 50
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 8 | 10 | 1574 | 0.0002803 | 1.7808e-06 | 157.4
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 31 | 6415 | 0.0011424 | 5.5205e-06 | 206.9355
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 223 | 3.9712e-05 | 1.7808e-07 | 223
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | FUSE | 1 | 1 | 33 | 5.8766e-06 | 1.7808e-07 | 33
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 7 | 31 | 4262 | 0.00075898 | 5.5205e-06 | 137.4839
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | A | NONE | 5 | 575 | 32435 | 0.0058172 | 0.00010313 | 56.4087
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WL | CROSSARM | 2 | 596 | 48766 | 0.0087814 | 0.00010732 | 81.8221
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CUTOUT | 1 | 2 | 30 | 5.4703e-06 | 3.6468e-07 | 15
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 5 | 545 | 9.7746e-05 | 8.9675e-07 | 109
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CONDUCTOR UG | 1 | 1 | 285 | 5.0753e-05 | 1.7808e-07 | 285
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 142 | 3428 | 334553 | 0.061003 | 0.00062507 | 97.5942
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, OH | 27 | 94 | 20536 | 0.0037446 | 1.714e-05 | 218.4681
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | NONE | 54 | 8939 | 231917 | 0.042288 | 0.00163 | 25.9444
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | NONE | 6 | 54 | 6179 | 0.0011267 | 9.8465e-06 | 114.4259
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONN/CLAMP | 3 | 4 | 274 | 4.9962e-05 | 7.2937e-07 | 68.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 52 | 2804 | 0.00051129 | 9.4818e-06 | 53.9231
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | ARRESTER | 6 | 131 | 7871 | 0.0014352 | 2.3887e-05 | 60.084
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | FUSE | 2 | 556 | 48892 | 0.0088517 | 0.00010066 | 87.9353
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABX | NONE | 3 | 4 | 301 | 5.4495e-05 | 7.2419e-07 | 75.25
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 1 | 91 | 1.6475e-05 | 1.8105e-07 | 91
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 5 | 15 | 1774 | 0.00032118 | 2.7157e-06 | 118.2667
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WT | NONE | 11 | 7338 | 1157520 | 0.20956 | 0.0013285 | 157.7433
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | FUSE | 28 | 59 | 5209 | 0.00093799 | 1.0624e-05 | 88.2881
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CROSSARM | 180 | 18425 | 1875784 | 0.33778 | 0.0033178 | 101.8065
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | NONE | 71 | 555 | 62590 | 0.011271 | 9.994e-05 | 112.7748
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | CUTOUT | 2 | 3 | 190 | 3.4214e-05 | 5.4022e-07 | 63.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | METERING | 51 | 655 | 70357 | 0.012669 | 0.00011795 | 107.4153
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | NONE | 48 | 438 | 56793 | 0.010227 | 7.8871e-05 | 129.6644
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | POLE | 1 | 1 | 125 | 2.2793e-05 | 1.8234e-07 | 125
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 5 | 890 | 0.00016228 | 9.1171e-07 | 178
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | NONE | 1 | 1 | 31 | 5.6526e-06 | 1.8234e-07 | 31
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | ARRESTER | 1 | 1113 | 170289 | 0.031051 | 0.00020295 | 153
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 2 | 272 | 4.9597e-05 | 3.6468e-07 | 136
AEP Total | 2020 | 5484199 | PARTIAL POWER | WFS | CONDUCTOR UG | 1 | 1 | 76 | 1.3858e-05 | 1.8234e-07 | 76
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | METERING | 25 | 26 | 3066 | 0.00054989 | 4.6631e-06 | 117.9231
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | FUSE | 22 | 250 | 42457 | 0.0076147 | 4.4838e-05 | 169.828
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | FUSE | 20 | 36 | 3837 | 0.00068817 | 6.4566e-06 | 106.5833
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | POLE | 61 | 10333 | 2143916 | 0.38451 | 0.0018532 | 207.4824
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CROSSARM | 3 | 35 | 10883 | 0.0019519 | 6.2773e-06 | 310.9429
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | METERING | 1 | 2 | 58 | 1.0402e-05 | 3.587e-07 | 29
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | NONE | 17 | 34 | 4513 | 0.00080941 | 6.0979e-06 | 132.7353
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONN/CLAMP | 5 | 5 | 879 | 0.00015765 | 8.9675e-07 | 175.8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR UG | 12 | 52 | 7024 | 0.0012598 | 9.3262e-06 | 135.0769
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | FUSE | 8 | 50 | 2780 | 0.00049859 | 8.9675e-06 | 55.6
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | POLE | 2 | 3 | 90 | 1.6142e-05 | 5.3805e-07 | 30
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 3 | 19 | 6131 | 0.0010996 | 3.4077e-06 | 322.6842
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 4 | 12 | 435 | 7.8017e-05 | 2.1522e-06 | 36.25
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | NONE | 1 | 2 | 442 | 7.9273e-05 | 3.587e-07 | 221
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CUTOUT | 11 | 90 | 8023 | 0.0014447 | 1.6206e-05 | 89.1444
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | BREAKER | 6 | 3147 | 39328 | 0.0070819 | 0.00056669 | 12.497
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, OH | 14 | 52 | 5170 | 0.00093097 | 9.3637e-06 | 99.4231
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CROSSARM | 34 | 4218 | 240676 | 0.043339 | 0.00075954 | 57.0593
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | POLE | 25 | 375 | 18312 | 0.0032975 | 6.7527e-05 | 48.832
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 53 | 13313 | 0.0023973 | 9.5438e-06 | 251.1887
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CROSSARM | 3 | 4 | 363 | 6.5366e-05 | 7.2029e-07 | 90.75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 9 | 44 | 6842 | 0.0012321 | 7.9232e-06 | 155.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | NONE | 9 | 57 | 17381 | 0.0031298 | 1.0264e-05 | 304.9298
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABX | NONE | 4 | 13 | 826 | 0.00014874 | 2.3409e-06 | 63.5385
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | METERING | 17 | 18 | 1417 | 0.00025516 | 3.2413e-06 | 78.7222
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 4 | 5 | 456 | 8.1784e-05 | 8.9675e-07 | 91.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | SWITCH, OH | 1 | 1 | 106 | 1.9088e-05 | 1.8007e-07 | 106
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | NONE | 1 | 6 | 180 | 3.2413e-05 | 1.0804e-06 | 30
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | POLE HARDWARE | 2 | 4 | 282 | 5.078e-05 | 7.2029e-07 | 70.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 4 | 556 | 0.00010012 | 7.2029e-07 | 139
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 10 | 3420 | 0.00061338 | 1.7935e-06 | 342
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CABLE TERMINATOR | 1 | 1 | 60 | 1.0941e-05 | 1.8234e-07 | 60
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | FUSE | 2 | 3 | 97 | 1.7687e-05 | 5.4703e-07 | 32.3333
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | ERF | GUY/ANCHOR | 1 | 213 | 159111 | 0.028806 | 3.8563e-05 | 747
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | BREAKER | 2 | 9 | 1330 | 0.00024079 | 1.6294e-06 | 147.7778
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | JUMPER/RISER | 4 | 5 | 386 | 6.9508e-05 | 9.0036e-07 | 77.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | ARRESTER | 1 | 3 | 66 | 1.1885e-05 | 5.4022e-07 | 22
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 4 | 15 | 641 | 0.00011543 | 2.7011e-06 | 42.7333
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | ABI | NONE | 2 | 270 | 20815 | 0.0037332 | 4.8425e-05 | 77.0926
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 1941 | 214279 | 0.038431 | 0.00034812 | 110.3962
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | TRANSFORMER, OH | 1 | 1 | 62 | 1.1225e-05 | 1.8105e-07 | 62
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 35 | 6.3025e-06 | 1.8007e-07 | 35
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | ARRESTER | 3 | 2332 | 216744 | 0.03903 | 0.00041993 | 92.9434
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 1 | 57 | 1.0264e-05 | 1.8007e-07 | 57
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 2 | 21 | 2586 | 0.00046567 | 3.7815e-06 | 123.1429
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 150 | 2.7011e-05 | 1.8007e-07 | 150
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE HARDWARE | 1 | 1 | 115 | 2.0708e-05 | 1.8007e-07 | 115
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 4 | 40 | 9280 | 0.0016526 | 7.1232e-06 | 232
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 21 | 180 | 10416 | 0.0018549 | 3.2054e-05 | 57.8667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | ARRESTER | 1 | 1 | 36 | 6.4109e-06 | 1.7808e-07 | 36
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 2 | 2 | 138 | 2.4575e-05 | 3.5616e-07 | 69
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | FUSE | 14 | 22 | 2274 | 0.00040495 | 3.9178e-06 | 103.3636
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 7 | 29 | 3758 | 0.00066922 | 5.1643e-06 | 129.5862
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | RELAY | 1 | 339 | 6780 | 0.0012074 | 6.0369e-05 | 20
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | WL | NONE | 4 | 1734 | 50517 | 0.0089961 | 0.00030879 | 29.1332
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CROSSARM | 2 | 10 | 704 | 0.00012537 | 1.7808e-06 | 70.4
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | JUMPER/RISER | 4 | 4 | 354 | 6.304e-05 | 7.1232e-07 | 88.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | INSULATOR | 1 | 6 | 876 | 0.000156 | 1.0685e-06 | 146
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 1 | 88 | 1.5671e-05 | 1.7808e-07 | 88
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 1 | 219 | 3.9278e-05 | 1.7935e-07 | 219
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 13 | 1838 | 0.00032731 | 2.315e-06 | 141.3846
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 5 | 29 | 1708 | 0.00030416 | 5.1643e-06 | 58.8966
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 9 | 58 | 5665 | 0.0010088 | 1.0329e-05 | 97.6724
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 5 | 28 | 3605 | 0.00064198 | 4.9862e-06 | 128.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 3 | 37 | 2107 | 0.00037521 | 6.589e-06 | 56.9459
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | CONN/CLAMP | 1 | 1 | 58 | 1.0329e-05 | 1.7808e-07 | 58
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 2 | 8 | 967 | 0.0001722 | 1.4246e-06 | 120.875
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 77 | 1.3712e-05 | 1.7808e-07 | 77
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 220 | 3.9178e-05 | 1.7808e-07 | 220
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | FUSE | 3 | 5 | 393 | 6.9985e-05 | 8.904e-07 | 78.6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CUTOUT | 1 | 1 | 56 | 9.9725e-06 | 1.7808e-07 | 56
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 51 | 41055 | 0.0073111 | 9.0821e-06 | 805
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 1 | 76 | 1.3534e-05 | 1.7808e-07 | 76
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 4 | 141 | 2.539e-05 | 7.2029e-07 | 35.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | NETWORK TRANSFORMER | 1 | 6 | 780 | 0.00014046 | 1.0804e-06 | 130
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | WI | CONDUCTOR OVERHEAD | 3 | 809 | 140482 | 0.025616 | 0.00014751 | 173.6489
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CROSSARM | 1 | 2 | 84 | 1.5126e-05 | 3.6014e-07 | 42
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 417 | 56955 | 0.010256 | 7.509e-05 | 136.5827
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | NONE | 1 | 1 | 91 | 1.6593e-05 | 1.8234e-07 | 91
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONDUCTOR UG | 1 | 1 | 103 | 1.8648e-05 | 1.8105e-07 | 103
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CABLE TERMINATOR | 1 | 1 | 138 | 2.485e-05 | 1.8007e-07 | 138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 1085 | 54250 | 0.0097689 | 0.00019538 | 50
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 5741 | 300074 | 0.054327 | 0.0010394 | 52.2686
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR UG | 293 | 477 | 77900 | 0.014104 | 8.6359e-05 | 163.3124
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | ARRESTER | 149 | 11324 | 1329085 | 0.24063 | 0.0020502 | 117.3689
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | NONE | 33 | 1394 | 132289 | 0.02395 | 0.00025238 | 94.8989
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CUTOUT | 26 | 870 | 120327 | 0.021785 | 0.00015751 | 138.3069
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CUTOUT | 16 | 272 | 20811 | 0.0037678 | 4.9245e-05 | 76.511
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 72 | 461 | 74131 | 0.013421 | 8.3462e-05 | 160.8048
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | CONN/CLAMP | 1 | 3 | 249 | 4.5081e-05 | 5.4314e-07 | 83
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 12 | 520 | 9.4144e-05 | 2.1726e-06 | 43.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | FUSE | 7 | 24 | 1522 | 0.00027555 | 4.3451e-06 | 63.4167
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 2 | 193 | 3.4942e-05 | 3.6209e-07 | 96.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | PEDESTAL | 1 | 1 | 264 | 4.7796e-05 | 1.8105e-07 | 264
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CAPACITOR | 1 | 1147 | 10323 | 0.0018689 | 0.00020766 | 9
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 2 | 12 | 2.1726e-06 | 3.6209e-07 | 6
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | NONE | 6 | 10 | 739 | 0.00013379 | 1.8105e-06 | 73.9
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | SWITCH, UG | 1 | 2 | 428 | 7.7488e-05 | 3.6209e-07 | 214
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 1 | 457 | 8.2738e-05 | 1.8105e-07 | 457
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 6 | 456 | 8.2557e-05 | 1.0863e-06 | 76
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 482 | 12632 | 1405688 | 0.25632 | 0.0023033 | 111.2799
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | FUSE | 3 | 23 | 1768 | 0.00032238 | 4.1939e-06 | 76.8696
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 9 | 13 | 881 | 0.00016064 | 2.3704e-06 | 67.7692
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 44 | 3502 | 635240 | 0.11583 | 0.00063856 | 181.3935
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | JUMPER/RISER | 19 | 47 | 7497 | 0.001367 | 8.5701e-06 | 159.5106
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CABLE TERMINATOR | 1 | 1 | 344 | 6.2726e-05 | 1.8234e-07 | 344
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | FUSE | 4 | 69 | 1921 | 0.00035028 | 1.2582e-05 | 27.8406
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | RELAY | 4 | 3631 | 114733 | 0.020921 | 0.00066208 | 31.5982
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | NONE | 28 | 39 | 2827 | 0.00051548 | 7.1113e-06 | 72.4872
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | FUSE | 5 | 452 | 59348 | 0.010822 | 8.2419e-05 | 131.3009
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONN/CLAMP | 3 | 23 | 2536 | 0.00046242 | 4.1939e-06 | 110.2609
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 2 | 17 | 1575 | 0.00028719 | 3.0998e-06 | 92.6471
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | NONE | 112 | 245 | 17848 | 0.003201 | 4.3941e-05 | 72.849
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE | 171 | 10884 | 2212190 | 0.39676 | 0.001952 | 203.2516
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | ARRESTER | 145 | 6095 | 506737 | 0.090883 | 0.0010931 | 83.1398
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONN/CLAMP | 5 | 8 | 775 | 0.000139 | 1.4348e-06 | 96.875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 1 | 118 | 2.1163e-05 | 1.7935e-07 | 118
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 4 | 1831 | 13302 | 0.0023857 | 0.00032839 | 7.2649
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | PEDESTAL | 1 | 31 | 2666 | 0.00047815 | 5.5599e-06 | 86
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | POLE | 1 | 2 | 30 | 5.3805e-06 | 3.587e-07 | 15
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | U | NONE | 33 | 33612 | 1392927 | 0.24982 | 0.0060283 | 41.4414
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | NONE | 7 | 219 | 12579 | 0.002256 | 3.9278e-05 | 57.4384
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 29 | 5.2012e-06 | 1.7935e-07 | 29
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | INSULATOR | 12 | 1818 | 234743 | 0.042101 | 0.00032606 | 129.1216
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 259 | 4.6452e-05 | 1.7935e-07 | 259
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 19 | 1265 | 0.00022688 | 3.4077e-06 | 66.5789
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 5 | 25 | 2089 | 0.00037466 | 4.4838e-06 | 83.56
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | JUMPER/RISER | 18 | 19670 | 2678562 | 0.48841 | 0.0035867 | 136.175
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | TRANSFORMER, POWER - LTC | 4 | 2637 | 124420 | 0.022687 | 0.00048084 | 47.1824
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | CROSSARM | 3 | 1398 | 41940 | 0.0076474 | 0.00025491 | 30
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONN/CLAMP | 3 | 5 | 1746 | 0.00031837 | 9.1171e-07 | 349.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 23 | 2484 | 0.00044972 | 4.1641e-06 | 108
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | U | BREAKER | 1 | 552 | 56304 | 0.010194 | 9.9938e-05 | 102
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | SPLICE, OH | 2 | 5 | 279 | 5.0512e-05 | 9.0523e-07 | 55.8
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 43 | 7.785e-06 | 1.8105e-07 | 43
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABI | NONE | 5 | 2434 | 144366 | 0.025996 | 0.0004383 | 59.3122
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CUTOUT | 11 | 18 | 2343 | 0.00042191 | 3.2413e-06 | 130.1667
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 12 | 2761 | 345005 | 0.062126 | 0.00049718 | 124.9565
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 29 | 5786 | 379120 | 0.068269 | 0.0010419 | 65.5237
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 39 | 7.0228e-06 | 1.8007e-07 | 39
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 1 | 97 | 1.7467e-05 | 1.8007e-07 | 97
AEP Total | 2022 | 5553337 | PARTIAL POWER | WFS | NONE | 3 | 4 | 294 | 5.2941e-05 | 7.2029e-07 | 73.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | ARRESTER | 2 | 2 | 101 | 1.8187e-05 | 3.6014e-07 | 50.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 2 | 282 | 5.078e-05 | 3.6014e-07 | 141
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | SPLICE, OH | 1 | 1 | 57 | 1.0223e-05 | 1.7935e-07 | 57
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | NONE | 6 | 254 | 70090 | 0.012621 | 4.5738e-05 | 275.9449
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 10 | 6568 | 947403 | 0.16992 | 0.001178 | 144.2453
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 2 | 5 | 455 | 8.1604e-05 | 8.9675e-07 | 91
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WU | NONE | 7 | 4628 | 487889 | 0.087503 | 0.00083003 | 105.4211
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 3 | 4 | 947 | 0.00017053 | 7.2029e-07 | 236.75
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | NONE | 1 | 1 | 120 | 2.1522e-05 | 1.7935e-07 | 120
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | NONE | 2 | 306 | 18336 | 0.0032886 | 5.4881e-05 | 59.9216
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | ARRESTER | 4 | 282 | 32550 | 0.0058613 | 5.078e-05 | 115.4255
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 1 | 1241 | 165282 | 0.029763 | 0.00022347 | 133.1845
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | REGULATOR | 2 | 781 | 15158 | 0.0027186 | 0.00014007 | 19.4085
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | NONE | 1 | 2 | 84 | 1.5065e-05 | 3.587e-07 | 42
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | ARRESTER | 1 | 1 | 47 | 8.4295e-06 | 1.7935e-07 | 47
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | FUSE | 18 | 31 | 1362 | 0.00024254 | 5.5205e-06 | 43.9355
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 11 | 8539 | 1076526 | 0.19308 | 0.0015315 | 126.0717
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 2 | 7 | 438 | 7.7999e-05 | 1.2466e-06 | 62.5714
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | ARRESTER | 1 | 1 | 75 | 1.3451e-05 | 1.7935e-07 | 75
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WW | NONE | 2 | 2922 | 49348 | 0.0089343 | 0.00052902 | 16.8884
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 90 | 120 | 16741 | 0.0029812 | 2.137e-05 | 139.5083
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 80 | 7168 | 550603 | 0.098051 | 0.0012765 | 76.814
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | METERING | 4 | 14 | 922 | 0.00016419 | 2.4931e-06 | 65.8571
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | GC | NONE | 7 | 1201 | 404947 | 0.072113 | 0.00021387 | 337.1749
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | NONE | 56 | 1216 | 71706 | 0.012769 | 0.00021655 | 58.9688
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | NONE | 7 | 1481 | 95742 | 0.01705 | 0.00026374 | 64.6469
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 79 | 1.4068e-05 | 1.7808e-07 | 79
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 3 | 864 | 0.00015386 | 5.3424e-07 | 288
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 48 | 2160 | 0.00038896 | 8.6435e-06 | 45
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 45 | 16484 | 0.0029683 | 8.1032e-06 | 366.3111
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | TRANSFORMER, UG | 1 | 5 | 1990 | 0.00035834 | 9.0036e-07 | 398
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 95 | 1017 | 82081 | 0.014617 | 0.00018111 | 80.7089
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 9 | 10 | 1424 | 0.00025359 | 1.7808e-06 | 142.4
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 3 | 562 | 49897 | 0.0088856 | 0.00010008 | 88.7847
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | WU | NONE | 4 | 693 | 45721 | 0.008142 | 0.00012341 | 65.9755
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 4 | 61 | 3177 | 0.00056576 | 1.0863e-05 | 52.082
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | FUSE | 2 | 2 | 155 | 2.7602e-05 | 3.5616e-07 | 77.5
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | FO | NONE | 1 | 770 | 25410 | 0.004525 | 0.00013712 | 33
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1918 | 157276 | 0.028008 | 0.00034156 | 82
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | OTHER EQUIPMENT | 1 | 31 | 2263 | 0.00040299 | 5.5205e-06 | 73
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 1 | 21 | 3.7397e-06 | 1.7808e-07 | 21
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CABLE TERMINATOR | 1 | 2 | 198 | 3.6104e-05 | 3.6468e-07 | 99
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 1620 | 167990 | 0.030632 | 0.00029539 | 103.6975
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1302 | 114021 | 0.020791 | 0.00023741 | 87.5737
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | O | NONE | 4 | 1292 | 84248 | 0.015362 | 0.00023559 | 65.2074
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | JUMPER/RISER | 1 | 1 | 192 | 3.501e-05 | 1.8234e-07 | 192
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 1 | 822 | 0.00014743 | 1.7935e-07 | 822
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | INSULATOR | 1 | 37 | 2109 | 0.00037825 | 6.636e-06 | 57
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | FW | BREAKER | 1 | 1625 | 149500 | 0.02726 | 0.00029631 | 92
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 65 | 1.1852e-05 | 1.8234e-07 | 65
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 1 | 1 | 65 | 1.1575e-05 | 1.7808e-07 | 65
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WI | POLE | 9 | 1588 | 154146 | 0.027757 | 0.00028595 | 97.0693
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | SPLICE, OH | 1 | 1 | 16 | 2.8812e-06 | 1.8007e-07 | 16
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONN/CLAMP | 344 | 658 | 43857 | 0.0079402 | 0.00011913 | 66.652
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, OH | 20 | 38 | 7847 | 0.0014207 | 6.8798e-06 | 206.5
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | MOAB | 2 | 692 | 90652 | 0.016412 | 0.00012528 | 131
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | NONE | 38 | 1683 | 84172 | 0.015239 | 0.0003047 | 50.0131
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 3 | 10 | 554 | 0.0001003 | 1.8105e-06 | 55.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | REGULATOR | 10 | 6555 | 348182 | 0.063037 | 0.0011868 | 53.117
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, OH | 17 | 1233 | 138695 | 0.02511 | 0.00022323 | 112.4858
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CUTOUT | 19 | 39 | 5309 | 0.00096118 | 7.0608e-06 | 136.1282
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 11 | 24 | 2087 | 0.00037784 | 4.3451e-06 | 86.9583
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 28 | 64 | 6123 | 0.0011085 | 1.1587e-05 | 95.6719
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 2 | 682 | 23452 | 0.0042459 | 0.00012347 | 34.3871
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONN/CLAMP | 5 | 5 | 594 | 0.00010754 | 9.0523e-07 | 118.8
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | NONE | 3 | 3 | 215 | 3.8925e-05 | 5.4314e-07 | 71.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | WU | NONE | 11 | 2747 | 325506 | 0.058932 | 0.00049733 | 118.4951
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 68 | 7276 | 0.0013173 | 1.2311e-05 | 107
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 12 | 492 | 8.9075e-05 | 2.1726e-06 | 41
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | BREAKER | 2 | 2161 | 103593 | 0.018755 | 0.00039124 | 47.9375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | RECLOSER, LINE/OCR/BR | 1 | 1206 | 207832 | 0.037627 | 0.00021834 | 172.3317
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | V | CIRCUIT SWITCHER | 2 | 1500 | 34320 | 0.0062135 | 0.00027157 | 22.88
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 10 | 17 | 1110 | 0.00020096 | 3.0778e-06 | 65.2941
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CROSSARM | 1 | 126 | 41832 | 0.0075735 | 2.2812e-05 | 332
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | JUMPER/RISER | 2 | 2 | 155 | 2.8062e-05 | 3.6209e-07 | 77.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CROSSARM | 7 | 791 | 86512 | 0.015663 | 0.00014321 | 109.3704
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONN/CLAMP | 1 | 1 | 28 | 5.0693e-06 | 1.8105e-07 | 28
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | ARRESTER | 2 | 3 | 227 | 4.1098e-05 | 5.4314e-07 | 75.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 225 | 13624 | 1374802 | 0.24756 | 0.0024533 | 100.9103
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE | 22 | 1071 | 255339 | 0.045979 | 0.00019286 | 238.4118
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | NONE | 117 | 5028 | 656760 | 0.11826 | 0.0009054 | 130.6205
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE | 31 | 5396 | 1040086 | 0.18729 | 0.00097167 | 192.7513
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 3 | 295 | 5.3121e-05 | 5.4022e-07 | 98.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 1 | 39 | 7.0228e-06 | 1.8007e-07 | 39
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | METERING | 4 | 5 | 396 | 7.1308e-05 | 9.0036e-07 | 79.2
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 3 | 312 | 5.6182e-05 | 5.4022e-07 | 104
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | NONE | 5 | 27 | 947 | 0.00017268 | 4.9232e-06 | 35.0741
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 134 | 2677 | 519523 | 0.094731 | 0.00048813 | 194.0691
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CROSSARM | 132 | 11679 | 1228218 | 0.22396 | 0.0021296 | 105.1647
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | FUSE | 20 | 33 | 2645 | 0.00048229 | 6.0173e-06 | 80.1515
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 5 | 228 | 4.1056e-05 | 9.0036e-07 | 45.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 3 | 1020 | 0.00018294 | 5.3805e-07 | 340
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | POLE | 2 | 12 | 2042 | 0.00036771 | 2.1609e-06 | 170.1667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 159 | 6768 | 740037 | 0.13179 | 0.0012052 | 109.3435
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 5 | 545 | 9.9376e-05 | 9.1171e-07 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 2 | 56 | 1.0211e-05 | 3.6468e-07 | 28
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 115 | 2.0708e-05 | 3.6014e-07 | 57.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 1 | 1 | 141 | 2.571e-05 | 1.8234e-07 | 141
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 37 | 238 | 20186 | 0.0035947 | 4.2383e-05 | 84.8151
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | SWITCH, OH | 1 | 2 | 564 | 0.00010115 | 3.587e-07 | 282
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 2 | 33 | 3818 | 0.00067991 | 5.8766e-06 | 115.697
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | FUSE | 1 | 1 | 60 | 1.0761e-05 | 1.7935e-07 | 60
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | METERING | 3 | 3 | 165 | 2.9383e-05 | 5.3424e-07 | 55
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 188 | 5284 | 546691 | 0.097355 | 0.00094097 | 103.4616
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 31 | 61 | 6508 | 0.0011589 | 1.0863e-05 | 106.6885
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | NONE | 145 | 9469 | 788571 | 0.14043 | 0.0016862 | 83.2792
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE HARDWARE | 3 | 688 | 155383 | 0.027671 | 0.00012252 | 225.8474
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 81 | 972 | 76400 | 0.013605 | 0.00017309 | 78.6008
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 6 | 24 | 1030 | 0.00018547 | 4.3217e-06 | 42.9167
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | SWITCH, OH | 1 | 30 | 7020 | 0.0012709 | 5.4314e-06 | 234
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 5 | 72 | 9128 | 0.0016255 | 1.2822e-05 | 126.7778
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AB | NONE | 5 | 2676 | 332897 | 0.059282 | 0.00047654 | 124.401
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | BREAKER | 7 | 1623 | 137231 | 0.024438 | 0.00028902 | 84.5539
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 14 | 4823 | 0.00085888 | 2.4931e-06 | 344.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 11 | 1045 | 0.00018818 | 1.9808e-06 | 95
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 7 | 308 | 5.5462e-05 | 1.2605e-06 | 44
AEP Total | 2022 | 5553337 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 22 | 3.9616e-06 | 1.8007e-07 | 22
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 2 | 82 | 46704 | 0.0083764 | 1.4707e-05 | 569.561
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 1322 | 64961 | 0.011698 | 0.00023806 | 49.1384
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 732 | 90228 | 0.016068 | 0.00013035 | 123.2623
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 2098 | 98951 | 0.017621 | 0.00037361 | 47.1644
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 1 | 57 | 1.0151e-05 | 1.7808e-07 | 57
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONN/CLAMP | 3 | 3 | 211 | 3.7575e-05 | 5.3424e-07 | 70.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1 | 26 | 4.6301e-06 | 1.7808e-07 | 26
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 1 | 1312 | 76096 | 0.013551 | 0.00023364 | 58
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | V | OTHER EQUIPMENT | 4 | 4836 | 618921 | 0.11145 | 0.00087083 | 127.982
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 1 | 11 | 2948 | 0.00053085 | 1.9808e-06 | 268
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 3 | 4 | 717 | 0.00012768 | 7.1232e-07 | 179.25
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 1 | 104 | 1.852e-05 | 1.7808e-07 | 104
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 5 | 388 | 41162 | 0.0073301 | 6.9095e-05 | 106.0876
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 1 | 624 | 88008 | 0.015672 | 0.00011112 | 141.0385
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 2 | 4 | 1470 | 0.00026178 | 7.1232e-07 | 367.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 2 | 2 | 133 | 2.3685e-05 | 3.5616e-07 | 66.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 229 | 4.078e-05 | 3.5616e-07 | 114.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 25 | 4.452e-06 | 1.7808e-07 | 25
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | CONN/CLAMP | 1 | 182 | 24388 | 0.004343 | 3.2411e-05 | 134
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 1 | 12 | 3684 | 0.00065605 | 2.137e-06 | 307
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 383 | 45194 | 0.0080481 | 6.8205e-05 | 118
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 57 | 17556 | 0.0031264 | 1.0151e-05 | 308
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 403 | 7.3484e-05 | 1.8234e-07 | 403
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | FUSE | 1 | 6 | 894 | 0.00016098 | 1.0804e-06 | 149
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 1 | 52 | 9.3262e-06 | 1.7935e-07 | 52
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | NONE | 1 | 1 | 72 | 1.3129e-05 | 1.8234e-07 | 72
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 1 | 20 | 3.6209e-06 | 1.8105e-07 | 20
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | NONE | 4 | 1190 | 103504 | 0.018432 | 0.00021191 | 86.9782
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 2 | 152 | 2.7068e-05 | 3.5616e-07 | 76
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 5 | 12 | 3341 | 0.00059496 | 2.137e-06 | 278.4167
AEP Total | 2024 | 5615460 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 127 | 2.2616e-05 | 1.7808e-07 | 127
AEP Total | 2024 | 5615460 | PARTIAL POWER | UB | NONE | 1 | 1 | 353 | 6.2862e-05 | 1.7808e-07 | 353
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 4 | 8 | 3371 | 0.00060031 | 1.4246e-06 | 421.375
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | WU | NONE | 4 | 1925 | 78926 | 0.014155 | 0.00034525 | 41.0005
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | CROSSARM | 4 | 1143 | 144544 | 0.02574 | 0.00020355 | 126.4602
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 36 | 6.4109e-06 | 1.7808e-07 | 36
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | EQF | TRANSFORMER, POWER - LTC | 2 | 1171 | 47719 | 0.0084978 | 0.00020853 | 40.7506
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 2 | 8 | 357 | 6.3574e-05 | 1.4246e-06 | 44.625
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 3 | 14 | 2287 | 0.00040727 | 2.4931e-06 | 163.3571
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 14 | 1106 | 0.00019696 | 2.4931e-06 | 79
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SWITCH, OH | 1 | 1 | 219 | 3.8999e-05 | 1.7808e-07 | 219
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 1 | 117 | 2.0835e-05 | 1.7808e-07 | 117
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 531 | 63159 | 0.011247 | 9.456e-05 | 118.9435
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 1 | 3 | 1293 | 0.00023026 | 5.3424e-07 | 431
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | ABI | ARRESTER | 2 | 2744 | 268912 | 0.047888 | 0.00048865 | 98
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | FUSE | 1 | 1 | 62 | 1.1225e-05 | 1.8105e-07 | 62
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | NONE | 155 | 5800 | 853356 | 0.15367 | 0.0010444 | 147.1303
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 261 | 2319 | 458293 | 0.082526 | 0.00041759 | 197.6253
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE | 161 | 14086 | 1882867 | 0.33905 | 0.0025365 | 133.6694
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | FUSE | 101 | 1058 | 66391 | 0.011955 | 0.00019052 | 62.7514
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 10 | 1.8007e-06 | 1.8007e-07 | 10
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | NONE | 23 | 239 | 25572 | 0.0046048 | 4.3037e-05 | 106.9958
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | NONE | 76 | 593 | 57139 | 0.010289 | 0.00010678 | 96.3558
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE | 17 | 259 | 71168 | 0.012815 | 4.6639e-05 | 274.7799
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CUTOUT | 32 | 2302 | 301836 | 0.054352 | 0.00041453 | 131.119
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CROSSARM | 19 | 3486 | 560875 | 0.101 | 0.00062773 | 160.8936
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, OH | 13 | 24 | 5390 | 0.00097059 | 4.3217e-06 | 224.5833
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 2 | 7 | 985 | 0.00017737 | 1.2605e-06 | 140.7143
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | PEDESTAL | 10 | 38 | 2685 | 0.00048349 | 6.8427e-06 | 70.6579
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 8 | 126 | 13373 | 0.0024081 | 2.2689e-05 | 106.1349
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE | 9 | 1730 | 239672 | 0.043158 | 0.00031152 | 138.5387
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | NONE | 43 | 599 | 32496 | 0.0058516 | 0.00010786 | 54.2504
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | INSULATOR | 12 | 1760 | 160995 | 0.028991 | 0.00031693 | 91.4744
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CUTOUT | 9 | 320 | 27629 | 0.0049752 | 5.7623e-05 | 86.3406
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 3 | 614 | 0.00011056 | 5.4022e-07 | 204.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | JUMPER/RISER | 4 | 310 | 13129 | 0.0023642 | 5.5822e-05 | 42.3516
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | NONE | 86 | 265 | 43654 | 0.0078294 | 4.7528e-05 | 164.7321
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | POLE | 5 | 1796 | 101102 | 0.018435 | 0.00032749 | 56.2929
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | POLE | 2 | 8 | 315 | 5.7438e-05 | 1.4587e-06 | 39.375
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 5 | 18 | 3444 | 0.00062799 | 3.2822e-06 | 191.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 913 | 21346 | 0.0038923 | 0.00016648 | 23.3801
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 9 | 328 | 5.9808e-05 | 1.6411e-06 | 36.4444
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WL | NONE | 8 | 4210 | 332431 | 0.060616 | 0.00076766 | 78.9622
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | FUSE | 2 | 54 | 2619 | 0.00047755 | 9.8465e-06 | 48.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | POLE | 1 | 1 | 126 | 2.2975e-05 | 1.8234e-07 | 126
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | BREAKER | 5 | 3167 | 380160 | 0.069319 | 0.00057748 | 120.0379
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | NONE | 49 | 7204 | 137875 | 0.024728 | 0.001292 | 19.1387
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | V | NONE | 10 | 7013 | 266115 | 0.047728 | 0.0012578 | 37.946
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | TRANSFORMER, OH | 2 | 4 | 160 | 2.8696e-05 | 7.174e-07 | 40
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | WW | NONE | 10 | 2274 | 351970 | 0.063126 | 0.00040784 | 154.7801
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | NONE | 31 | 239 | 18136 | 0.0032527 | 4.2865e-05 | 75.8828
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | POLE HARDWARE | 3 | 1428 | 32536 | 0.0058353 | 0.00025611 | 22.7843
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | POLE | 3 | 395 | 202166 | 0.036259 | 7.0843e-05 | 511.8127
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONN/CLAMP | 4 | 24 | 8390 | 0.0015047 | 4.3044e-06 | 349.5833
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | LS | NONE | 38 | 41727 | 4996627 | 0.89615 | 0.0074837 | 119.7457
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | METERING | 4 | 4 | 783 | 0.00014043 | 7.174e-07 | 195.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CROSSARM | 3 | 208 | 31971 | 0.005734 | 3.7305e-05 | 153.7067
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 12 | 3132 | 0.00056172 | 2.1522e-06 | 261
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 3 | 13 | 1049 | 0.00018814 | 2.3316e-06 | 80.6923
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 1 | 55 | 9.8643e-06 | 1.7935e-07 | 55
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | CROSSARM | 5 | 1170 | 192905 | 0.034598 | 0.00020984 | 164.8761
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | WW | POLE | 5 | 1894 | 951872 | 0.17072 | 0.00033969 | 502.5723
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR UG | 3 | 46 | 2798 | 0.00050384 | 8.2833e-06 | 60.8261
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | PEDESTAL | 1 | 3 | 552 | 9.94e-05 | 5.4022e-07 | 184
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 25 | 12565 | 0.0022626 | 4.5018e-06 | 502.6
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | NONE | 20 | 27 | 1709 | 0.00030774 | 4.8619e-06 | 63.2963
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 8 | 8705 | 373774 | 0.067306 | 0.0015675 | 42.9379
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | OTHER EQUIPMENT | 1 | 409 | 184459 | 0.033083 | 7.3354e-05 | 451
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | JUMPER/RISER | 8 | 154 | 21993 | 0.0039444 | 2.762e-05 | 142.8117
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | FW | TRANSFORMER, OH | 1 | 6 | 1572 | 0.00028307 | 1.0804e-06 | 262
AEP Total | 2022 | 5553337 | TRANSMISSION STATION | R | NONE | 2 | 3078 | 36936 | 0.0066511 | 0.00055426 | 12
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, OH | 24 | 78 | 17100 | 0.0030669 | 1.3989e-05 | 219.2308
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | FUSE | 3 | 53 | 3306 | 0.00059532 | 9.5438e-06 | 62.3774
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | OL | BREAKER | 1 | 287 | 25543 | 0.0045996 | 5.1681e-05 | 89
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 88 | 745 | 132778 | 0.023814 | 0.00013362 | 178.2255
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | U | NONE | 15 | 13506 | 661690 | 0.11915 | 0.0024321 | 48.9923
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | PEDESTAL | 1 | 4 | 1216 | 0.00021897 | 7.2029e-07 | 304
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 591 | 25853 | 0.0046367 | 0.000106 | 43.7445
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 3 | 3897 | 77756 | 0.013946 | 0.00069893 | 19.9528
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | ARRESTER | 14 | 20 | 2325 | 0.00041699 | 3.587e-06 | 116.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CUTOUT | 2 | 2 | 522 | 9.3621e-05 | 3.587e-07 | 261
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 740 | 17609 | 2721046 | 0.48456 | 0.0031358 | 154.5259
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | TRANSFORMER, UG | 1 | 12 | 228 | 4.0892e-05 | 2.1522e-06 | 19
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 9 | 12 | 3071 | 0.00055078 | 2.1522e-06 | 255.9167
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR UG | 1 | 1 | 83 | 1.4886e-05 | 1.7935e-07 | 83
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 5 | 5 | 1296 | 0.00023244 | 8.9675e-07 | 259.2
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | WL | NONE | 26 | 5351 | 389507 | 0.069858 | 0.0009597 | 72.7914
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | SWITCH, OH | 3 | 960 | 29974 | 0.0053758 | 0.00017218 | 31.2229
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONN/CLAMP | 10 | 43 | 1450 | 0.00026006 | 7.7121e-06 | 33.7209
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | PEDESTAL | 1 | 1 | 43 | 7.7121e-06 | 1.7935e-07 | 43
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | TRANSFORMER, OH | 1 | 4 | 8772 | 0.0015733 | 7.174e-07 | 2193
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | NONE | 1633 | 38520 | 4561230 | 0.81226 | 0.0068596 | 118.412
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 374 | 7887 | 1415615 | 0.25209 | 0.0014045 | 179.4871
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | JUMPER/RISER | 1 | 13 | 2470 | 0.00045038 | 2.3704e-06 | 190
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | OL | FUSE | 2 | 519 | 51729 | 0.0094324 | 9.4636e-05 | 99.6705
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | OL | NONE | 4 | 518 | 61642 | 0.01124 | 9.4453e-05 | 119
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | FW | CUTOUT | 1 | 6 | 1254 | 0.00022581 | 1.0804e-06 | 209
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 238 | 4.2685e-05 | 3.587e-07 | 119
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 1 | 133 | 2.395e-05 | 1.8007e-07 | 133
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | NONE | 43 | 4109 | 233550 | 0.041591 | 0.00073173 | 56.8386
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 69 | 10163 | 0.0018098 | 1.2288e-05 | 147.2899
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | JUMPER/RISER | 3 | 10 | 1405 | 0.0002502 | 1.7808e-06 | 140.5
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | CUTOUT | 5 | 2221 | 275679 | 0.049093 | 0.00039552 | 124.1238
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CROSSARM | 1 | 22 | 2772 | 0.00049716 | 3.9457e-06 | 126
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | FUSE | 1 | 2 | 182 | 3.2642e-05 | 3.587e-07 | 91
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | WL | NONE | 24 | 14823 | 726613 | 0.1294 | 0.0026397 | 49.0193
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | ARRESTER | 1 | 3 | 345 | 6.1438e-05 | 5.3424e-07 | 115
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | RELAY | 1 | 377 | 3393 | 0.00060854 | 6.7615e-05 | 9
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 3 | 66 | 1.1885e-05 | 5.4022e-07 | 22
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONN/CLAMP | 1 | 1 | 34 | 6.1556e-06 | 1.8105e-07 | 34
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 4 | 276 | 4.9969e-05 | 7.2419e-07 | 69
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | U | RECLOSER, LINE/OCR/BR | 1 | 182 | 3640 | 0.00065901 | 3.295e-05 | 20
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 1 | 27 | 4.9232e-06 | 1.8234e-07 | 27
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | FUSE | 1 | 1 | 100 | 1.8007e-05 | 1.8007e-07 | 100
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 2 | 28 | 5.042e-06 | 3.6014e-07 | 14
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | POLE HARDWARE | 2 | 57 | 4322 | 0.00078808 | 1.0393e-05 | 75.8246
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 265 | 40952 | 0.0073743 | 4.7719e-05 | 154.5358
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 2 | 250 | 4.5586e-05 | 3.6468e-07 | 125
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | ARRESTER | 4 | 154 | 12278 | 0.0022109 | 2.7731e-05 | 79.7273
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 2 | 362 | 6.5539e-05 | 3.6209e-07 | 181
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 4 | 78 | 11722 | 0.0020875 | 1.389e-05 | 150.2821
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | FUSE | 5 | 27 | 4446 | 0.00079174 | 4.8082e-06 | 164.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 44 | 1127 | 77372 | 0.013778 | 0.0002007 | 68.6531
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WI | NONE | 4 | 5780 | 1161780 | 0.2092 | 0.0010408 | 201
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 2 | 2 | 80 | 1.4246e-05 | 3.5616e-07 | 40
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | FUSE | 1 | 3 | 264 | 4.7013e-05 | 5.3424e-07 | 88
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | CONN/CLAMP | 3 | 13 | 1915 | 0.00034102 | 2.315e-06 | 147.3077
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 69 | 1.2288e-05 | 1.7808e-07 | 69
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 3 | 51 | 1342 | 0.00023898 | 9.0821e-06 | 26.3137
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | JUMPER/RISER | 16 | 15561 | 1833942 | 0.32659 | 0.0027711 | 117.855
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | ERF | NONE | 2 | 324 | 2592 | 0.00046158 | 5.7698e-05 | 8
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | FO | NONE | 9 | 3401 | 144657 | 0.02576 | 0.00060565 | 42.5337
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 4 | 424 | 7.5506e-05 | 7.1232e-07 | 106
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | PEDESTAL | 2 | 2 | 115 | 2.0625e-05 | 3.587e-07 | 57.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 249 | 48651 | 0.0086638 | 4.4342e-05 | 195.3855
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 11 | 23 | 1896 | 0.00034572 | 4.1939e-06 | 82.4348
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | ARRESTER | 3 | 3 | 131 | 2.3887e-05 | 5.4703e-07 | 43.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | SPLICE, OH | 2 | 36 | 869 | 0.00015846 | 6.5643e-06 | 24.1389
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 162 | 16668 | 0.0030393 | 2.9539e-05 | 102.8889
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | TRANSFORMER, UG | 1 | 8 | 848 | 0.00015463 | 1.4587e-06 | 106
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | INSULATOR | 1 | 133 | 11451 | 0.002088 | 2.4251e-05 | 86.0977
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 477 | 16096 | 2048462 | 0.36739 | 0.0028868 | 127.2653
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 13 | 822 | 31224 | 0.0056 | 0.00014743 | 37.9854
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | NONE | 38 | 98 | 6160 | 0.0011048 | 1.7576e-05 | 62.8571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 92 | 7645 | 1699821 | 0.30486 | 0.0013711 | 222.3441
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 253 | 69575 | 0.01239 | 4.5054e-05 | 275
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 2 | 862 | 0.0001535 | 3.5616e-07 | 431
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | JUMPER/RISER | 1 | 746 | 8206 | 0.0014613 | 0.00013285 | 11
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | CONDUCTOR UG | 2 | 2460 | 20369 | 0.0036273 | 0.00043808 | 8.2801
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | SPLICE, UG | 1 | 1 | 40 | 7.1232e-06 | 1.7808e-07 | 40
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 158 | 30020 | 0.005346 | 2.8137e-05 | 190
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 6 | 696 | 0.00012394 | 1.0685e-06 | 116
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, GROUNDING | 1 | 4 | 192 | 3.4191e-05 | 7.1232e-07 | 48
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | GUY/ANCHOR | 1 | 829 | 283551 | 0.050495 | 0.00014763 | 342.0398
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | BREAKER | 1 | 504 | 31248 | 0.0056978 | 9.19e-05 | 62
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | CF | INSULATOR | 1 | 204 | 25500 | 0.0046497 | 3.7198e-05 | 125
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | A | CONDUCTOR OVERHEAD | 1 | 99 | 10593 | 0.0019315 | 1.8052e-05 | 107
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 2 | 22 | 3.9616e-06 | 3.6014e-07 | 11
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 178 | 8108 | 523286 | 0.094739 | 0.0014679 | 64.5395
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | NONE | 226 | 3220 | 117446 | 0.021263 | 0.00058297 | 36.4739
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | FUSE | 80 | 835 | 55050 | 0.0099666 | 0.00015117 | 65.9281
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CUTOUT | 276 | 10156 | 680953 | 0.12328 | 0.0018387 | 67.0493
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | FUSE | 13 | 168 | 47234 | 0.0085515 | 3.0416e-05 | 281.1548
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 2 | 376 | 6.8073e-05 | 3.6209e-07 | 188
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CROSSARM | 12 | 269 | 11726 | 0.0021229 | 4.8701e-05 | 43.5911
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | ERF | NONE | 8 | 6369 | 140118 | 0.025368 | 0.0011531 | 22
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 63 | 8644 | 0.001565 | 1.1406e-05 | 137.2063
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 4 | 29 | 1886 | 0.00034145 | 5.2503e-06 | 65.0345
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | NONE | 51 | 13498 | 582249 | 0.10541 | 0.0024438 | 43.1359
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 1 | 1 | 72 | 1.3035e-05 | 1.8105e-07 | 72
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | JUMPER/RISER | 1 | 1 | 12 | 2.1726e-06 | 1.8105e-07 | 12
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 8 | 449 | 66864 | 0.012105 | 8.129e-05 | 148.9176
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 3 | 21 | 2152 | 0.00038961 | 3.802e-06 | 102.4762
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 15 | 935 | 0.00016928 | 2.7157e-06 | 62.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | CONDUCTOR UG | 2 | 467 | 4673 | 0.00084603 | 8.4549e-05 | 10.0064
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 61 | 5622 | 0.0010178 | 1.1044e-05 | 92.1639
AEP Total | 2021 | 5523447 | PARTIAL POWER | AF | CONDUCTOR UG | 1 | 1 | 76 | 1.376e-05 | 1.8105e-07 | 76
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 3 | 2414 | 101388 | 0.018356 | 0.00043705 | 42
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | NONE | 4 | 4 | 268 | 4.852e-05 | 7.2419e-07 | 67
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | NONE | 1666 | 31523 | 3335117 | 0.60813 | 0.005748 | 105.7995
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | NONE | 34 | 6210 | 133473 | 0.024338 | 0.0011323 | 21.4932
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 23 | 113 | 9016 | 0.001644 | 2.0605e-05 | 79.7876
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | POLE | 4 | 18 | 6349 | 0.0011577 | 3.2822e-06 | 352.7222
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 55 | 254 | 16229 | 0.0029592 | 4.6315e-05 | 63.8937
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 16 | 123 | 14409 | 0.0026274 | 2.2428e-05 | 117.1463
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 6 | 24 | 2642 | 0.00048175 | 4.3762e-06 | 110.0833
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | POLE HARDWARE | 1 | 18 | 810 | 0.0001477 | 3.2822e-06 | 45
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | NONE | 6 | 3254 | 181542 | 0.033103 | 0.00059334 | 55.7904
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 4 | 773 | 38560 | 0.0070311 | 0.00014095 | 49.8836
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | NONE | 5 | 20 | 1446 | 0.00026367 | 3.6468e-06 | 72.3
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 237 | 14301 | 0.0026077 | 4.3215e-05 | 60.3418
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | ARRESTER | 2 | 704 | 212272 | 0.038431 | 0.00012746 | 301.5227
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 87 | 1914 | 0.00034652 | 1.5751e-05 | 22
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 99 | 1.7827e-05 | 1.8007e-07 | 99
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | FUSE | 79 | 1112 | 107419 | 0.019266 | 0.00019944 | 96.5998
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | JUMPER/RISER | 15 | 219 | 31986 | 0.0057367 | 3.9278e-05 | 146.0548
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | TIR | NONE | 2 | 607 | 159570 | 0.028734 | 0.0001093 | 262.883
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | METERING | 1 | 1 | 207 | 3.7275e-05 | 1.8007e-07 | 207
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | NONE | 80 | 5047 | 849596 | 0.15238 | 0.00090518 | 168.3368
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | ARRESTER | 1 | 1 | 101 | 1.8286e-05 | 1.8105e-07 | 101
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | ARRESTER | 2 | 2 | 209 | 3.7839e-05 | 3.6209e-07 | 104.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CABLE TERMINATOR | 1 | 1 | 9 | 1.6206e-06 | 1.8007e-07 | 9
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 289 | 11560 | 0.0020816 | 5.2041e-05 | 40
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 171 | 12312 | 0.002217 | 3.0792e-05 | 72
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 2 | 140 | 2.521e-05 | 3.6014e-07 | 70
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | INSULATOR | 2 | 408 | 26724 | 0.0048729 | 7.4396e-05 | 65.5
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | ERF | NONE | 1 | 299 | 9568 | 0.0017229 | 5.3842e-05 | 32
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CUTOUT | 3 | 633 | 141516 | 0.025483 | 0.00011399 | 223.564
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | NONE | 1 | 3 | 138 | 2.485e-05 | 5.4022e-07 | 46
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 1 | 1 | 75 | 1.3356e-05 | 1.7808e-07 | 75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | CONDUCTOR UG | 1 | 54 | 5346 | 0.00095201 | 9.6163e-06 | 99
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | V | NONE | 2 | 1769 | 86681 | 0.015546 | 0.00031727 | 49
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | RELAY | 4 | 1596 | 22198 | 0.003953 | 0.00028422 | 13.9085
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 3 | 1353 | 99222 | 0.017669 | 0.00024094 | 73.3348
AEP Total | 2024 | 5615460 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 1 | 1 | 58 | 1.0329e-05 | 1.7808e-07 | 58
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | A | OTHER EQUIPMENT | 1 | 7 | 441 | 7.8533e-05 | 1.2466e-06 | 63
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABX | BREAKER | 1 | 1 | 151 | 2.689e-05 | 1.7808e-07 | 151
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | TRANSFORMER, OH | 1 | 1 | 218 | 3.9256e-05 | 1.8007e-07 | 218
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 104 | 1.8727e-05 | 3.6014e-07 | 52
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 1 | 23 | 1495 | 0.00026921 | 4.1417e-06 | 65
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | GUY/ANCHOR | 1 | 1 | 8 | 1.4406e-06 | 1.8007e-07 | 8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | SECTIONALIZER | 1 | 14 | 1008 | 0.00018151 | 2.521e-06 | 72
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 9 | 11 | 985 | 0.00017541 | 1.9589e-06 | 89.5455
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | F | NONE | 3 | 1074 | 74106 | 0.013197 | 0.00019126 | 69
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 1 | 1 | 188 | 3.3479e-05 | 1.7808e-07 | 188
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | WW | NONE | 11 | 3149 | 994187 | 0.17704 | 0.00056077 | 315.7151
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 16 | 1648 | 0.00029348 | 2.8493e-06 | 103
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | METERING | 1 | 1 | 25 | 4.452e-06 | 1.7808e-07 | 25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 3 | 390 | 7.0608e-05 | 5.4314e-07 | 130
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 2 | 8 | 1636 | 0.00029619 | 1.4484e-06 | 204.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WH | NONE | 1 | 2 | 70 | 1.2673e-05 | 3.6209e-07 | 35
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | PEDESTAL | 3 | 7 | 333 | 6.0288e-05 | 1.2673e-06 | 47.5714
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 441 | 34839 | 0.0063075 | 7.9841e-05 | 79
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | JUMPER/RISER | 2 | 201 | 4146 | 0.00075062 | 3.639e-05 | 20.6269
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | BREAKER | 1 | 2213 | 480585 | 0.087008 | 0.00040066 | 217.1645
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | NONE | 1 | 1 | 394 | 7.1332e-05 | 1.8105e-07 | 394
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | WW | NONE | 4 | 679 | 99731 | 0.018056 | 0.00012293 | 146.8792
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | NONE | 1923 | 66216 | 3639030 | 0.65529 | 0.011924 | 54.957
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 36 | 2119 | 333493 | 0.060053 | 0.00038157 | 157.3823
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | CF | NONE | 7 | 45 | 3094 | 0.00056016 | 8.1471e-06 | 68.7556
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | SPLICE, OH | 1 | 2 | 208 | 3.7658e-05 | 3.6209e-07 | 104
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 4 | 676 | 0.00012239 | 7.2419e-07 | 169
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 362 | 20872 | 2603293 | 0.47469 | 0.0038058 | 124.7266
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | NONE | 116 | 263 | 16945 | 0.0030898 | 4.7956e-05 | 64.4297
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | STATIC WIRE | 7 | 2528 | 158758 | 0.028948 | 0.00046096 | 62.7998
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | NONE | 22 | 203 | 16169 | 0.0029483 | 3.7015e-05 | 79.6502
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 22 | 2207 | 483207 | 0.088109 | 0.00040243 | 218.9429
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | NONE | 15 | 19 | 1712 | 0.00031217 | 3.4645e-06 | 90.1053
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 3 | 234 | 4.2668e-05 | 5.4703e-07 | 78
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | POLE | 2 | 8 | 1478 | 0.0002695 | 1.4587e-06 | 184.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | NONE | 32 | 2563 | 117298 | 0.021388 | 0.00046734 | 45.7659
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | ARRESTER | 14 | 25 | 1890 | 0.00034463 | 4.5586e-06 | 75.6
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | CROSSARM | 9 | 9995 | 678865 | 0.12379 | 0.0018225 | 67.9205
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | NONE | 93 | 295 | 22750 | 0.0041483 | 5.3791e-05 | 77.1186
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | TRANSFORMER, OH | 2 | 2 | 133 | 2.4251e-05 | 3.6468e-07 | 66.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | BREAKER | 5 | 3758 | 151577 | 0.027639 | 0.00068524 | 40.3345
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE | 12 | 431 | 266074 | 0.048516 | 7.8589e-05 | 617.3411
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 4 | 40 | 7.2937e-06 | 7.2937e-07 | 10
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 12 | 23 | 932 | 0.00016994 | 4.1939e-06 | 40.5217
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | NONE | 45 | 992 | 137992 | 0.025162 | 0.00018088 | 139.1048
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONDUCTOR UG | 4 | 4 | 424 | 7.7313e-05 | 7.2937e-07 | 106
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | FUSE | 7 | 153 | 18679 | 0.003406 | 2.7898e-05 | 122.085
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 1 | 8 | 1.4587e-06 | 1.8234e-07 | 8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | CROSSARM | 3 | 27 | 6693 | 0.0011919 | 4.8082e-06 | 247.8889
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONN/CLAMP | 2 | 8 | 318 | 5.6629e-05 | 1.4246e-06 | 39.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | SPLICE, OH | 2 | 2 | 183 | 3.2589e-05 | 3.5616e-07 | 91.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 87 | 1479 | 0.00026633 | 1.5666e-05 | 17
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 11 | 2542 | 309543 | 0.055123 | 0.00045268 | 121.7714
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | WL | NONE | 3 | 1009 | 91419 | 0.01628 | 0.00017968 | 90.6036
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 3 | 19 | 11606 | 0.0020668 | 3.3835e-06 | 610.8421
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 1 | 21 | 3.7397e-06 | 1.7808e-07 | 21
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | GUY/ANCHOR | 1 | 2 | 40 | 7.1232e-06 | 3.5616e-07 | 20
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | TRANSFORMER, UG | 1 | 36 | 14180 | 0.0025252 | 6.4109e-06 | 393.8889
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 50 | 5850 | 0.0010418 | 8.904e-06 | 117
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 2 | 484 | 8.6191e-05 | 3.5616e-07 | 242
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CUTOUT | 1 | 2 | 182 | 3.2411e-05 | 3.5616e-07 | 91
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 1 | 1 | 104 | 1.852e-05 | 1.7808e-07 | 104
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CROSSARM | 2 | 1218 | 127708 | 0.022742 | 0.0002169 | 104.8506
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 2 | 148 | 2.6987e-05 | 3.6468e-07 | 74
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | EQF | POLE | 5 | 3591 | 53496 | 0.0095945 | 0.00064405 | 14.8972
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 33 | 5982 | 0.0010729 | 5.9186e-06 | 181.2727
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CAPACITOR | 1 | 360 | 42120 | 0.0075007 | 6.4109e-05 | 117
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CAPACITOR | 2 | 2432 | 194374 | 0.034614 | 0.00043309 | 79.9235
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 2 | 94 | 1.674e-05 | 3.5616e-07 | 47
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 1 | 1235 | 0.00022519 | 1.8234e-07 | 1235
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WL | SWITCH, OH | 1 | 5 | 2020 | 0.00036833 | 9.1171e-07 | 404
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | CONDUCTOR OVERHEAD | 1 | 1 | 24 | 4.3762e-06 | 1.8234e-07 | 24
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | OTHER EQUIPMENT | 1 | 1 | 77 | 1.3941e-05 | 1.8105e-07 | 77
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 8 | 26 | 2086 | 0.00037766 | 4.7072e-06 | 80.2308
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR UG | 49 | 69 | 10762 | 0.0019484 | 1.2492e-05 | 155.971
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 8 | 19 | 1880 | 0.00034037 | 3.4399e-06 | 98.9474
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE | 17 | 1037 | 245842 | 0.044509 | 0.00018775 | 237.0704
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | METERING | 11 | 11 | 1089 | 0.00019716 | 1.9915e-06 | 99
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | FW | NONE | 4 | 1446 | 52546 | 0.0095133 | 0.00026179 | 36.3389
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | NONE | 150 | 328 | 31706 | 0.0057403 | 5.9383e-05 | 96.6646
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OU | NONE | 7 | 1823 | 226630 | 0.041031 | 0.00033005 | 124.3171
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE | 9 | 3401 | 575207 | 0.10414 | 0.00061574 | 169.1288
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CONN/CLAMP | 8 | 240 | 34811 | 0.0063024 | 4.3451e-05 | 145.0458
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | POLE HARDWARE | 1 | 1115 | 91430 | 0.016553 | 0.00020187 | 82
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 12 | 61 | 8273 | 0.0014978 | 1.1044e-05 | 135.623
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | WI | NONE | 4 | 2136 | 646094 | 0.11697 | 0.00038672 | 302.4785
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | TRANSFORMER, POWER - LTC | 1 | 5 | 3285 | 0.00059474 | 9.0523e-07 | 657
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 3 | 104 | 1.8829e-05 | 5.4314e-07 | 34.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 1 | 73 | 1.3216e-05 | 1.8105e-07 | 73
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | V | BREAKER | 1 | 802 | 5614 | 0.0010164 | 0.0001452 | 7
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | FUSE | 3 | 4 | 278 | 5.0331e-05 | 7.2419e-07 | 69.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 8 | 2432 | 0.0004403 | 1.4484e-06 | 304
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | NONE | 14 | 84 | 16440 | 0.0029764 | 1.5208e-05 | 195.7143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE | 29 | 5668 | 1467552 | 0.26134 | 0.0010094 | 258.9188
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 13 | 151 | 58713 | 0.010456 | 2.689e-05 | 388.8278
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE | 10 | 886 | 92704 | 0.016509 | 0.00015778 | 104.6321
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE | 15 | 2447 | 850201 | 0.1514 | 0.00043576 | 347.4463
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | FW | NONE | 6 | 1820 | 36941 | 0.006688 | 0.0003295 | 20.2973
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 3 | 730 | 130568 | 0.023252 | 0.00013 | 178.8603
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 95 | 158 | 11703 | 0.0020841 | 2.8137e-05 | 74.0696
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | NONE | 171 | 13324 | 1415203 | 0.25202 | 0.0023727 | 106.2146
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 2 | 8 | 900 | 0.00016027 | 1.4246e-06 | 112.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 73 | 7041 | 0.0012539 | 1.3e-05 | 96.4521
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | SWITCH, UG | 1 | 775 | 62415 | 0.011239 | 0.00013956 | 80.5355
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 72 | 28368 | 0.0051359 | 1.3035e-05 | 394
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 5 | 641 | 0.00011605 | 9.0523e-07 | 128.2
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | POLE | 1 | 8 | 344 | 6.228e-05 | 1.4484e-06 | 43
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 2 | 132 | 2.3898e-05 | 3.6209e-07 | 66
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 1 | 67 | 2479 | 0.00044881 | 1.213e-05 | 37
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 2 | 4 | 322 | 5.7342e-05 | 7.1232e-07 | 80.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | NONE | 20 | 32 | 1942 | 0.00034583 | 5.6986e-06 | 60.6875
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 10 | 707 | 38515 | 0.0068587 | 0.0001259 | 54.4767
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 1 | 9 | 900 | 0.00016411 | 1.6411e-06 | 100
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | NETWORK TRANSFORMER | 1 | 1 | 71 | 1.2946e-05 | 1.8234e-07 | 71
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | OU | NONE | 8 | 3440 | 489343 | 0.089228 | 0.00062726 | 142.2509
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 17 | 2089 | 0.00037821 | 3.0778e-06 | 122.8824
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | PEDESTAL | 4 | 15 | 442 | 7.8711e-05 | 2.6712e-06 | 29.4667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 23 | 41 | 3038 | 0.00054101 | 7.3013e-06 | 74.0976
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 24 | 1879 | 367197 | 0.06539 | 0.00033461 | 195.4215
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CUTOUT | 1 | 1 | 311 | 5.5778e-05 | 1.7935e-07 | 311
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 6 | 975 | 125100 | 0.022278 | 0.00017363 | 128.3077
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 29 | 5858 | 0.0010506 | 5.2012e-06 | 202
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 35 | 3239 | 396440 | 0.070598 | 0.0005768 | 122.3958
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 290 | 15080 | 0.0027497 | 5.2879e-05 | 52
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | JUMPER/RISER | 6 | 51 | 13696 | 0.0024974 | 9.2994e-06 | 268.549
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 7 | 560 | 0.00010211 | 1.2764e-06 | 80
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 1795 | 315078 | 0.057452 | 0.0003273 | 175.5309
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 209 | 91989 | 0.016773 | 3.8109e-05 | 440.1388
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CUTOUT | 1 | 4 | 88 | 1.5932e-05 | 7.2419e-07 | 22
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | V | NONE | 1 | 795 | 27825 | 0.0050737 | 0.00014496 | 35
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | POLE | 4 | 1812 | 703063 | 0.1282 | 0.0003304 | 388.0039
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | JUMPER/RISER | 4 | 578 | 45664 | 0.0082228 | 0.00010408 | 79.0035
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 1 | 10 | 1150 | 0.00020708 | 1.8007e-06 | 115
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 109 | 1.9628e-05 | 1.8007e-07 | 109
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONN/CLAMP | 9 | 40 | 1145 | 0.00020618 | 7.2029e-06 | 28.625
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CUTOUT | 1 | 2 | 108 | 1.9448e-05 | 3.6014e-07 | 54
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | FUSE | 1 | 3 | 183 | 3.2821e-05 | 5.3805e-07 | 61
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 4 | 1309 | 0.00023477 | 7.174e-07 | 327.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 269 | 3288 | 457197 | 0.081418 | 0.00058553 | 139.0502
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | NONE | 207 | 23177 | 2960190 | 0.52715 | 0.0041274 | 127.721
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 114 | 6533 | 969767 | 0.1727 | 0.0011634 | 148.4413
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 10 | 247 | 41705 | 0.0074268 | 4.3986e-05 | 168.8462
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 40 | 2267 | 574674 | 0.10234 | 0.00040371 | 253.4954
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 15 | 63 | 7483 | 0.0013326 | 1.1219e-05 | 118.7778
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | NONE | 24 | 144 | 9455 | 0.0016837 | 2.5643e-05 | 65.6597
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 100 | 672 | 158419 | 0.028211 | 0.00011967 | 235.7426
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | POLE | 11 | 82 | 16739 | 0.0029809 | 1.4603e-05 | 204.1341
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 2 | 172 | 3.0848e-05 | 3.587e-07 | 86
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 18 | 23 | 1472 | 0.00026213 | 4.0958e-06 | 64
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 9 | 1495 | 0.00026921 | 1.6206e-06 | 166.1111
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | FUSE | 1 | 1 | 218 | 3.9751e-05 | 1.8234e-07 | 218
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 3 | 138 | 2.5163e-05 | 5.4703e-07 | 46
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONN/CLAMP | 3 | 13 | 1066 | 0.00019196 | 2.3409e-06 | 82
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 3 | 1097 | 13164 | 0.0023705 | 0.00019754 | 12
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | NONE | 521 | 2955 | 175619 | 0.031274 | 0.00052623 | 59.4311
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 3 | 1108 | 103117 | 0.018363 | 0.00019731 | 93.0659
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CROSSARM | 12 | 1037 | 23779 | 0.0042346 | 0.00018467 | 22.9306
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE | 16 | 1337 | 166497 | 0.02965 | 0.00023809 | 124.5303
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 125 | 1045 | 193689 | 0.034492 | 0.00018609 | 185.3483
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | R | NONE | 2 | 1921 | 21194 | 0.0037742 | 0.00034209 | 11.0328
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 1 | 246 | 4.412e-05 | 1.7935e-07 | 246
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | POLE | 1 | 2 | 70 | 1.2605e-05 | 3.6014e-07 | 35
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, POWER - LTC | 1 | 4 | 652 | 0.00011611 | 7.1232e-07 | 163
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | FUSE | 1 | 2 | 118 | 2.1013e-05 | 3.5616e-07 | 59
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 4 | 35 | 3656 | 0.00065106 | 6.2328e-06 | 104.4571
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 2 | 3186 | 957405 | 0.17049 | 0.00056736 | 300.5038
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONN/CLAMP | 3 | 3 | 242 | 4.3095e-05 | 5.3424e-07 | 80.6667
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | TRANSFORMER, OH | 3 | 15 | 1760 | 0.00031342 | 2.6712e-06 | 117.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, STATION SERVICE | 2 | 3 | 115 | 2.0479e-05 | 5.3424e-07 | 38.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CABLE TERMINATOR | 1 | 32 | 2624 | 0.00047507 | 5.7935e-06 | 82
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 3 | 692 | 14052 | 0.0025024 | 0.00012323 | 20.3064
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | RECLOSER, LINE/OCR/BR | 4 | 826 | 114493 | 0.020389 | 0.00014709 | 138.6114
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | BREAKER | 4 | 1702 | 529658 | 0.094321 | 0.00030309 | 311.1974
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 63 | 1.1219e-05 | 1.7808e-07 | 63
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 3 | 2562 | 160154 | 0.02852 | 0.00045624 | 62.5113
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 43 | 10392 | 0.0018506 | 7.6574e-06 | 241.6744
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ERF | NONE | 3 | 2881 | 386237 | 0.070427 | 0.00052533 | 134.0635
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | JUMPER/RISER | 5 | 65 | 11358 | 0.002071 | 1.1852e-05 | 174.7385
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 13 | 955 | 0.00017414 | 2.3704e-06 | 73.4615
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 1465 | 42525 | 0.0077541 | 0.00026713 | 29.0273
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 10 | 10 | 1021 | 0.00018617 | 1.8234e-06 | 102.1
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WL | BREAKER | 1 | 200 | 26600 | 0.0048503 | 3.6468e-05 | 133
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 119 | 2.1699e-05 | 1.8234e-07 | 119
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | JUMPER/RISER | 6 | 56 | 6082 | 0.001109 | 1.0211e-05 | 108.6071
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | FUSE | 23 | 162 | 11337 | 0.0020333 | 2.9055e-05 | 69.9815
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CUTOUT | 33 | 1484 | 312618 | 0.056068 | 0.00026616 | 210.659
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | NONE | 53 | 331 | 39564 | 0.0070958 | 5.9365e-05 | 119.5287
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | POLE | 10 | 1015 | 108966 | 0.019543 | 0.00018204 | 107.3557
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 824 | 97145 | 0.017423 | 0.00014778 | 117.8944
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | NONE | 17 | 717 | 12714 | 0.0022803 | 0.00012859 | 17.7322
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | R | NONE | 13 | 2971 | 238909 | 0.042848 | 0.00053285 | 80.4137
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | FUSE | 17 | 303 | 54912 | 0.0098485 | 5.4343e-05 | 181.2277
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | NONE | 15 | 848 | 208841 | 0.037456 | 0.00015209 | 246.2748
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 12 | 2916 | 0.00052299 | 2.1522e-06 | 243
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CROSSARM | 4 | 1954 | 293941 | 0.052718 | 0.00035045 | 150.4304
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | U | NONE | 18 | 14750 | 1321851 | 0.23707 | 0.0026454 | 89.617
AEP Total | 2023 | 5575683 | PARTIAL POWER | WH | NONE | 1 | 1 | 42 | 7.5327e-06 | 1.7935e-07 | 42
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | GUY/ANCHOR | 2 | 6 | 610 | 0.00011044 | 1.0863e-06 | 101.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | NONE | 1778 | 36456 | 3347470 | 0.60279 | 0.0065647 | 91.8222
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | NONE | 366 | 6412 | 393276 | 0.070818 | 0.0011546 | 61.3344
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | NONE | 384 | 30556 | 2792253 | 0.50281 | 0.0055023 | 91.3815
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CUTOUT | 319 | 7907 | 914366 | 0.16465 | 0.0014238 | 115.6401
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | NONE | 13 | 472 | 44555 | 0.0080231 | 8.4994e-05 | 94.3962
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 10 | 54 | 13061 | 0.0023519 | 9.7239e-06 | 241.8704
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WW | NONE | 15 | 3323 | 381753 | 0.068743 | 0.00059838 | 114.882
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE | 7 | 48 | 7762 | 0.0013977 | 8.6435e-06 | 161.7083
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | FUSE | 23 | 393 | 27381 | 0.0049305 | 7.0768e-05 | 69.6718
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | FUSE | 6 | 32 | 1699 | 0.00030594 | 5.7623e-06 | 53.0938
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | PEDESTAL | 15 | 64 | 4783 | 0.00085783 | 1.1478e-05 | 74.7344
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | BREAKER | 1 | 1147 | 25234 | 0.0046012 | 0.00020915 | 22
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 16 | 2627 | 0.00047901 | 2.9175e-06 | 164.1875
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | PEDESTAL | 1 | 8 | 328 | 5.9808e-05 | 1.4587e-06 | 41
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 34 | 4862 | 0.00088655 | 6.1996e-06 | 143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 6 | 1255 | 0.00022884 | 1.0941e-06 | 209.1667
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 2 | 254 | 4.5555e-05 | 3.587e-07 | 127
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 5 | 202 | 7642 | 0.0013706 | 3.6229e-05 | 37.8317
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CUTOUT | 13 | 203 | 22495 | 0.0040345 | 3.6408e-05 | 110.8128
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABX | FUSE | 3 | 22 | 1028 | 0.00018511 | 3.9616e-06 | 46.7273
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | METERING | 2 | 5 | 487 | 8.7695e-05 | 9.0036e-07 | 97.4
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, OH | 6 | 6 | 423 | 7.5865e-05 | 1.0761e-06 | 70.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | NONE | 3 | 1416 | 82173 | 0.014738 | 0.00025396 | 58.0318
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | JUMPER/RISER | 4 | 170 | 15048 | 0.0026989 | 3.049e-05 | 88.5176
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | INSULATOR | 1 | 5 | 755 | 0.00013595 | 9.0036e-07 | 151
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONN/CLAMP | 2 | 10 | 742 | 0.00013308 | 1.7935e-06 | 74.2
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | OTHER EQUIPMENT | 1 | 2 | 130 | 2.3316e-05 | 3.587e-07 | 65
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE HARDWARE | 2 | 302 | 79611 | 0.014336 | 5.4382e-05 | 263.6126
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | BREAKER | 7 | 5893 | 557332 | 0.099958 | 0.0010569 | 94.5753
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 38 | 992 | 26935 | 0.0047966 | 0.00017666 | 27.1522
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | NONE | 96 | 444 | 36945 | 0.0065792 | 7.9067e-05 | 83.2095
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | METERING | 21 | 23 | 1940 | 0.00034547 | 4.0958e-06 | 84.3478
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 2 | 1143 | 21965 | 0.0039394 | 0.000205 | 19.217
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 31 | 8109 | 0.0014544 | 5.5599e-06 | 261.5806
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 2 | 10 | 2064 | 0.00037018 | 1.7935e-06 | 206.4
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 2 | 3 | 212 | 3.8022e-05 | 5.3805e-07 | 70.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 1 | 1 | 255 | 4.5734e-05 | 1.7935e-07 | 255
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | ARRESTER | 1 | 9 | 1377 | 0.00024697 | 1.6142e-06 | 153
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | ARRESTER | 2 | 20 | 2989 | 0.00053608 | 3.587e-06 | 149.45
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | MOAB | 1 | 180 | 10800 | 0.0019553 | 3.2588e-05 | 60
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 8 | 872 | 0.000159 | 1.4587e-06 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CONN/CLAMP | 2 | 2 | 139 | 2.5346e-05 | 3.6468e-07 | 69.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 38 | 187 | 24070 | 0.0043578 | 3.3856e-05 | 128.7166
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | ARRESTER | 2 | 37 | 1930 | 0.00034942 | 6.6987e-06 | 52.1622
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 1 | 30 | 5.4314e-06 | 1.8105e-07 | 30
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | ARRESTER | 35 | 2762 | 227656 | 0.041216 | 0.00050005 | 82.4243
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 2 | 21 | 1829 | 0.00033113 | 3.802e-06 | 87.0952
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 9 | 339 | 118048 | 0.021372 | 6.1375e-05 | 348.2242
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 11 | 30 | 2923 | 0.0005292 | 5.4314e-06 | 97.4333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 2 | 42 | 9149 | 0.0016564 | 7.6039e-06 | 217.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 200 | 15218 | 0.0027552 | 3.6209e-05 | 76.09
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | INSULATOR | 1 | 3 | 183 | 3.3131e-05 | 5.4314e-07 | 61
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | A | NONE | 9 | 1683 | 76422 | 0.013836 | 0.0003047 | 45.4082
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | INSULATOR | 57 | 8608 | 799551 | 0.14579 | 0.0015696 | 92.8846
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | NONE | 255 | 9918 | 993806 | 0.18121 | 0.0018085 | 100.2023
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | INSULATOR | 8 | 451 | 53260 | 0.0097115 | 8.2236e-05 | 118.0931
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CROSSARM | 7 | 705 | 180740 | 0.032956 | 0.00012855 | 256.3688
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CROSSARM | 6 | 71 | 11825 | 0.0021562 | 1.2946e-05 | 166.5493
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE | 111 | 7160 | 1063674 | 0.19395 | 0.0013056 | 148.5578
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | BREAKER | 1 | 23 | 4531 | 0.00082032 | 4.1641e-06 | 197
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 8 | 264 | 4.7796e-05 | 1.4484e-06 | 33
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | TRANSFORMER, UG | 1 | 10 | 4680 | 0.0008473 | 1.8105e-06 | 468
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | BREAKER | 1 | 587 | 90504 | 0.016385 | 0.00010627 | 154.1806
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | POLE | 4 | 22 | 1300 | 0.00023536 | 3.983e-06 | 59.0909
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 1 | 63 | 1.1406e-05 | 1.8105e-07 | 63
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | JUMPER/RISER | 6 | 28 | 4972 | 0.00090016 | 5.0693e-06 | 177.5714
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | METERING | 2 | 6 | 346 | 6.2642e-05 | 1.0863e-06 | 57.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 4 | 116 | 16048 | 0.0029054 | 2.1001e-05 | 138.3448
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | POLE | 1 | 3 | 1020 | 0.00018367 | 5.4022e-07 | 340
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WL | NONE | 21 | 19756 | 1513256 | 0.27249 | 0.0035575 | 76.5973
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 162 | 2669 | 458182 | 0.082506 | 0.00048061 | 171.668
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | FUSE | 9 | 17 | 1158 | 0.00020852 | 3.0612e-06 | 68.1176
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 30 | 2329 | 565151 | 0.10177 | 0.00041939 | 242.6582
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CIRCUIT SWITCHER | 5 | 4178 | 183260 | 0.033 | 0.00075234 | 43.8631
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 11 | 191 | 11251 | 0.002026 | 3.4394e-05 | 58.9058
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 295 | 6577 | 1260855 | 0.22613 | 0.0011796 | 191.7067
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | JUMPER/RISER | 28 | 193 | 12772 | 0.0022999 | 3.4754e-05 | 66.1762
AEP Total | 2022 | 5553337 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 2 | 152 | 2.7371e-05 | 3.6014e-07 | 76
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | NONE | 28 | 52 | 3012 | 0.0005402 | 9.3262e-06 | 57.9231
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WT | NONE | 5 | 3422 | 402206 | 0.072426 | 0.00061621 | 117.5354
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | INSULATOR | 57 | 10012 | 943028 | 0.16913 | 0.0017957 | 94.1898
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | FUSE | 1 | 3 | 219 | 3.9436e-05 | 5.4022e-07 | 73
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 5 | 6 | 522 | 9.3998e-05 | 1.0804e-06 | 87
AEP Total | 2022 | 5553337 | PARTIAL POWER | OU | CONDUCTOR UG | 6 | 6 | 1082 | 0.00019484 | 1.0804e-06 | 180.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | FUSE | 23 | 157 | 9877 | 0.001801 | 2.8628e-05 | 62.9108
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 51 | 2945 | 375396 | 0.06845 | 0.000537 | 127.4689
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 70 | 239 | 43991 | 0.0080214 | 4.358e-05 | 184.0628
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | NONE | 75 | 143 | 11753 | 0.0021431 | 2.6075e-05 | 82.1888
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | FUSE | 183 | 2271 | 106658 | 0.019448 | 0.0004141 | 46.9652
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR UG | 7 | 122 | 21443 | 0.00391 | 2.2246e-05 | 175.7623
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CABLE TERMINATOR | 3 | 3 | 575 | 0.00010485 | 5.4703e-07 | 191.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | POLE | 1 | 1 | 279 | 5.0873e-05 | 1.8234e-07 | 279
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | NONE | 2 | 52 | 4167 | 0.00075982 | 9.4818e-06 | 80.1346
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | FUSE | 2 | 3 | 245 | 4.4674e-05 | 5.4703e-07 | 81.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 8 | 283 | 37826 | 0.0068973 | 5.1603e-05 | 133.6608
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 5 | 11 | 632 | 0.00011524 | 2.0058e-06 | 57.4545
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | NONE | 2 | 4 | 180 | 3.2588e-05 | 7.2419e-07 | 45
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | BREAKER | 1 | 858 | 6864 | 0.0012427 | 0.00015534 | 8
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 7 | 657 | 0.00011895 | 1.2673e-06 | 93.8571
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | R | RELAY | 4 | 3909 | 141296 | 0.025581 | 0.00070771 | 36.1463
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | FUSE | 8 | 14 | 991 | 0.00017942 | 2.5346e-06 | 70.7857
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CROSSARM | 1 | 469 | 21574 | 0.0039059 | 8.4911e-05 | 46
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CUTOUT | 1 | 1 | 31 | 5.6124e-06 | 1.8105e-07 | 31
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | CONDUCTOR OVERHEAD | 6 | 2428 | 189134 | 0.034487 | 0.00044273 | 77.897
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | ERF | NONE | 3 | 1802 | 16218 | 0.0029572 | 0.00032858 | 9
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, OH | 1 | 1 | 126 | 2.2975e-05 | 1.8234e-07 | 126
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | SWITCH, UG | 1 | 1 | 372 | 6.6246e-05 | 1.7808e-07 | 372
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | FUSE | 3 | 87 | 73410 | 0.013073 | 1.5493e-05 | 843.7931
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 31 | 29450 | 0.0052445 | 5.5205e-06 | 950
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 7 | 638 | 0.00011361 | 1.2466e-06 | 91.1429
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | V | TRANSFORMER, GROUNDING | 4 | 5212 | 181139 | 0.032618 | 0.00093853 | 34.7542
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE | 49 | 5781 | 1080416 | 0.1924 | 0.0010295 | 186.8908
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CROSSARM | 6 | 54 | 2062 | 0.0003672 | 9.6163e-06 | 38.1852
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 4 | 19 | 1508 | 0.00026854 | 3.3835e-06 | 79.3684
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | OU | NONE | 5 | 1303 | 66453 | 0.011834 | 0.00023204 | 51
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONN/CLAMP | 2 | 2 | 131 | 2.3328e-05 | 3.5616e-07 | 65.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | CONN/CLAMP | 3 | 4 | 515 | 9.1711e-05 | 7.1232e-07 | 128.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | POLE | 2 | 2 | 719 | 0.00012804 | 3.5616e-07 | 359.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | JUMPER/RISER | 2 | 2 | 344 | 6.1259e-05 | 3.5616e-07 | 172
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | FUSE | 1 | 1 | 97 | 1.7274e-05 | 1.7808e-07 | 97
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | BREAKER | 1 | 1 | 233 | 4.1493e-05 | 1.7808e-07 | 233
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | NONE | 1 | 2 | 150 | 2.7011e-05 | 3.6014e-07 | 75
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | CONN/CLAMP | 1 | 30 | 2940 | 0.00052941 | 5.4022e-06 | 98
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | TRANSFORMER, OH | 2 | 13 | 1418 | 0.00025432 | 2.3316e-06 | 109.0769
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 927 | 108466 | 0.019453 | 0.00016626 | 117.0076
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | WU | NONE | 4 | 3102 | 118554 | 0.021112 | 0.0005524 | 38.2186
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 933 | 10263 | 0.0018276 | 0.00016615 | 11
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | NONE | 1 | 1 | 69 | 1.2375e-05 | 1.7935e-07 | 69
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | TOR | NONE | 1 | 1026 | 42066 | 0.0076704 | 0.00018708 | 41
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 1 | 2 | 246 | 4.4856e-05 | 3.6468e-07 | 123
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 49 | 40229 | 0.0072151 | 8.7882e-06 | 821
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 1 | 761 | 0.00013552 | 1.7808e-07 | 761
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | FUSE | 170 | 1003 | 57370 | 0.010387 | 0.00018159 | 57.1984
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 14 | 116 | 10259 | 0.0018574 | 2.1001e-05 | 88.4397
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | NONE | 42 | 2661 | 213980 | 0.03874 | 0.00048176 | 80.4134
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | NONE | 127 | 435 | 23242 | 0.0042079 | 7.8755e-05 | 53.4299
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | FUSE | 74 | 1380 | 194485 | 0.035211 | 0.00024984 | 140.9312
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 7 | 4841 | 1044399 | 0.18908 | 0.00087645 | 215.7403
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 10 | 1334 | 0.00024152 | 1.8105e-06 | 133.4
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | PEDESTAL | 2 | 27 | 694 | 0.00012359 | 4.8082e-06 | 25.7037
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | METERING | 4 | 4 | 238 | 4.2383e-05 | 7.1232e-07 | 59.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 150 | 13870 | 0.00247 | 2.6712e-05 | 92.4667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | SWITCH, OH | 1 | 9 | 549 | 9.7766e-05 | 1.6027e-06 | 61
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 29 | 5.1643e-06 | 1.7808e-07 | 29
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | JUMPER/RISER | 1 | 1 | 17 | 3.0274e-06 | 1.7808e-07 | 17
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 10 | 1889 | 0.00033639 | 1.7808e-06 | 188.9
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 9 | 1977 | 54687 | 0.0097387 | 0.00035206 | 27.6616
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | POLE | 1 | 1 | 140 | 2.521e-05 | 1.8007e-07 | 140
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | REGULATOR | 1 | 296 | 28712 | 0.0051495 | 5.3088e-05 | 97
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | ABI | NONE | 2 | 1512 | 89606 | 0.015957 | 0.00026926 | 59.2632
AEP Total | 2025 | 5615460 | PARTIAL POWER | VIN | FUSE | 1 | 1 | 93 | 1.6561e-05 | 1.7808e-07 | 93
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 266 | 21014 | 0.0037422 | 4.7369e-05 | 79
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 5 | 6537 | 839659 | 0.14953 | 0.0011641 | 128.4471
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CUTOUT | 4 | 13 | 329 | 5.8588e-05 | 2.315e-06 | 25.3077
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 1 | 1 | 98 | 1.7452e-05 | 1.7808e-07 | 98
AEP Total | 2025 | 5615460 | PARTIAL POWER | WL | NONE | 6 | 10 | 1118 | 0.00019909 | 1.7808e-06 | 111.8
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 8 | 1800 | 0.00032054 | 1.4246e-06 | 225
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 16 | 3562 | 0.00063432 | 2.8493e-06 | 222.625
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 2 | 5 | 857 | 0.00015261 | 8.904e-07 | 171.4
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | METERING | 1 | 1 | 91 | 1.6205e-05 | 1.7808e-07 | 91
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 1 | 57 | 4748 | 0.00084552 | 1.0151e-05 | 83.2982
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | WU | NONE | 1 | 255 | 14806 | 0.0026366 | 4.541e-05 | 58.0627
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | ERF | NONE | 1 | 832 | 16640 | 0.0029632 | 0.00014816 | 20
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 77 | 3542 | 0.00064586 | 1.404e-05 | 46
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | CONDUCTOR UG | 1 | 458 | 20610 | 0.0037581 | 8.3513e-05 | 45
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | POLE | 1 | 2 | 44 | 7.8355e-06 | 3.5616e-07 | 22
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | INSULATOR | 1 | 33 | 5181 | 0.00093295 | 5.9424e-06 | 157
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WU | POLE | 1 | 2 | 430 | 7.785e-05 | 3.6209e-07 | 215
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 3 | 69 | 1.2425e-05 | 5.4022e-07 | 23
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 558 | 18388 | 1996345 | 0.36143 | 0.0033291 | 108.5678
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 321 | 1645 | 244303 | 0.043505 | 0.00029294 | 148.5125
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE | 23 | 461 | 178960 | 0.032097 | 8.268e-05 | 388.1996
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | NONE | 1 | 1 | 60 | 1.0761e-05 | 1.7935e-07 | 60
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | METERING | 2 | 2 | 185 | 3.318e-05 | 3.587e-07 | 92.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 29 | 463 | 8.3039e-05 | 5.2012e-06 | 15.9655
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 445 | 4171 | 413352 | 0.07361 | 0.00074277 | 99.1014
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 248 | 1824 | 107815 | 0.0192 | 0.00032482 | 59.1091
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 3 | 703 | 54191 | 0.0097192 | 0.00012608 | 77.0853
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | METERING | 1 | 1 | 58 | 1.0501e-05 | 1.8105e-07 | 58
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 1 | 1 | 65 | 1.1852e-05 | 1.8234e-07 | 65
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | U | CIRCUIT SWITCHER | 1 | 1007 | 7049 | 0.0012853 | 0.00018362 | 7
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | SPLICE, OH | 1 | 1 | 14 | 2.5528e-06 | 1.8234e-07 | 14
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 165 | 3.0086e-05 | 3.6468e-07 | 82.5
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 6 | 2037 | 272305 | 0.049653 | 0.00037143 | 133.6794
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 2360 | 103256 | 0.018828 | 0.00043033 | 43.7525
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 1 | 1 | 106 | 1.9328e-05 | 1.8234e-07 | 106
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 845 | 5123 | 0.00093414 | 0.00015408 | 6.0627
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 35 | 196 | 32718 | 0.0059659 | 3.5739e-05 | 166.9286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 2 | 224 | 4.0845e-05 | 3.6468e-07 | 112
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 253 | 4.5805e-05 | 1.8105e-07 | 253
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 371 | 32298 | 0.0057927 | 6.6539e-05 | 87.0566
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | U | NONE | 17 | 16327 | 748886 | 0.13336 | 0.0029075 | 45.8679
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | WW | NONE | 20 | 16272 | 761523 | 0.13561 | 0.0028977 | 46.7996
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 10 | 42 | 2471 | 0.00044004 | 7.4794e-06 | 58.8333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | NONE | 20 | 229 | 15329 | 0.0027298 | 4.078e-05 | 66.9389
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 14 | 25 | 2884 | 0.00051358 | 4.452e-06 | 115.36
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 6 | 118 | 8966 | 0.0015967 | 2.1013e-05 | 75.9831
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CABLE TERMINATOR | 2 | 28 | 3107 | 0.00055724 | 5.0218e-06 | 110.9643
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 35 | 814 | 176970 | 0.031515 | 0.00014496 | 217.4079
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | FUSE | 23 | 48 | 4173 | 0.00074313 | 8.5478e-06 | 86.9375
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 7 | 13 | 793 | 0.00014122 | 2.315e-06 | 61
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | POLE HARDWARE | 2 | 2 | 208 | 3.7658e-05 | 3.6209e-07 | 104
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | FUSE | 4 | 191 | 21161 | 0.0038105 | 3.4394e-05 | 110.7906
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 139 | 2.503e-05 | 1.8007e-07 | 139
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 6 | 306 | 5.5102e-05 | 1.0804e-06 | 51
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WL | NONE | 2 | 2 | 103 | 1.8547e-05 | 3.6014e-07 | 51.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 43 | 8208 | 0.001478 | 7.7431e-06 | 190.8837
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 3 | 355 | 6.3218e-05 | 5.3424e-07 | 118.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 48 | 690 | 143678 | 0.025586 | 0.00012288 | 208.229
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 19 | 200 | 24491 | 0.0043614 | 3.5616e-05 | 122.455
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 19 | 3960 | 111196 | 0.019802 | 0.0007052 | 28.0798
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 2 | 9 | 1278 | 0.00022759 | 1.6027e-06 | 142
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | SPLICE, UG | 1 | 1 | 119 | 2.1191e-05 | 1.7808e-07 | 119
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 1 | 70 | 1.2466e-05 | 1.7808e-07 | 70
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 6 | 6 | 555 | 9.8834e-05 | 1.0685e-06 | 92.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 1 | 275 | 4.8972e-05 | 1.7808e-07 | 275
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE HARDWARE | 2 | 724 | 120761 | 0.021505 | 0.00012893 | 166.797
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 1 | 65 | 1.1575e-05 | 1.7808e-07 | 65
AEP Total | 2024 | 5615460 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 1 | 185 | 3.2945e-05 | 1.7808e-07 | 185
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 12 | 980 | 33209 | 0.0059139 | 0.00017452 | 33.8867
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | INSULATOR | 3 | 396 | 41580 | 0.0074046 | 7.052e-05 | 105
AEP Total | 2024 | 5615460 | PARTIAL POWER | CE | NONE | 1 | 2 | 288 | 5.1287e-05 | 3.5616e-07 | 144
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | FUSE | 3 | 12 | 996 | 0.00017737 | 2.137e-06 | 83
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 3 | 71 | 2571 | 0.00045784 | 1.2644e-05 | 36.2113
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | METERING | 1 | 1 | 50 | 8.904e-06 | 1.7808e-07 | 50
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | OTHER EQUIPMENT | 3 | 3162 | 146864 | 0.026154 | 0.00056309 | 46.4466
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 5 | 59 | 5455 | 0.00099468 | 1.0758e-05 | 92.4576
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | R | BREAKER | 1 | 341 | 65472 | 0.011938 | 6.2179e-05 | 192
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 71 | 1.2946e-05 | 1.8234e-07 | 71
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | FO | CROSSARM | 1 | 211 | 42608 | 0.0076725 | 3.7995e-05 | 201.9336
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 2 | 421 | 68765 | 0.012246 | 7.4972e-05 | 163.3373
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CUTOUT | 5 | 15 | 2694 | 0.00047975 | 2.6712e-06 | 179.6
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | WW | REGULATOR | 3 | 710 | 93010 | 0.016563 | 0.00012644 | 131
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | SWITCH, OH | 5 | 1212 | 474274 | 0.084459 | 0.00021583 | 391.3152
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | NONE | 25 | 35 | 2348 | 0.00042814 | 6.382e-06 | 67.0857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CUTOUT | 5 | 15 | 1648 | 0.00029557 | 2.6903e-06 | 109.8667
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | U | NONE | 5 | 1151 | 88843 | 0.015934 | 0.00020643 | 77.1877
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | NONE | 2 | 11 | 907 | 0.00016267 | 1.9729e-06 | 82.4545
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | TRANSFORMER, UG | 3 | 3 | 453 | 8.1246e-05 | 5.3805e-07 | 151
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 3 | 67 | 16190 | 0.0029037 | 1.2016e-05 | 241.6418
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABX | NONE | 1 | 726 | 42834 | 0.0076823 | 0.00013021 | 59
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | ERF | NONE | 3 | 626 | 4530 | 0.00081246 | 0.00011227 | 7.2364
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | NONE | 6 | 5726 | 724887 | 0.12909 | 0.0010197 | 126.5957
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 3 | 3 | 293 | 5.2177e-05 | 5.3424e-07 | 97.6667
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 4 | 7 | 1556 | 0.00027709 | 1.2466e-06 | 222.2857
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 4 | 85 | 20190 | 0.0036553 | 1.5389e-05 | 237.5294
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | FUSE | 1 | 15 | 4875 | 0.0008826 | 2.7157e-06 | 325
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 2 | 273 | 11537 | 0.0020775 | 4.916e-05 | 42.2601
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | SPLICE, OH | 9 | 156 | 9997 | 0.0018002 | 2.8091e-05 | 64.0833
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 3 | 114 | 2.0528e-05 | 5.4022e-07 | 38
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | FUSE | 1 | 1 | 11 | 1.9808e-06 | 1.8007e-07 | 11
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | FUSE | 57 | 796 | 51039 | 0.009089 | 0.00014175 | 64.1193
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | NONE | 456 | 9514 | 915178 | 0.16297 | 0.0016943 | 96.1928
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 88 | 2177 | 545496 | 0.097142 | 0.00038768 | 250.5723
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | U | NONE | 4 | 4836 | 100466 | 0.017891 | 0.00086119 | 20.7746
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 41 | 189 | 29649 | 0.0052799 | 3.3657e-05 | 156.873
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 50 | 470 | 77567 | 0.013813 | 8.3698e-05 | 165.0362
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | POLE | 5 | 156 | 18741 | 0.0033374 | 2.778e-05 | 120.1346
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 3 | 252 | 4.5378e-05 | 5.4022e-07 | 84
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | NONE | 2 | 2 | 333 | 5.9964e-05 | 3.6014e-07 | 166.5
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | AF | CROSSARM | 1 | 257 | 15163 | 0.0027304 | 4.6278e-05 | 59
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | FUSE | 3 | 5 | 355 | 6.3218e-05 | 8.904e-07 | 71
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | NONE | 1 | 1396 | 15356 | 0.0027346 | 0.0002486 | 11
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | INSULATOR | 4 | 2120 | 209394 | 0.037289 | 0.00037753 | 98.7708
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 2 | 98 | 1.7452e-05 | 3.5616e-07 | 49
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | BREAKER | 2 | 51 | 17442 | 0.0031061 | 9.0821e-06 | 342
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | TRANSFORMER, UG | 1 | 2 | 130 | 2.3704e-05 | 3.6468e-07 | 65
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | PEDESTAL | 11 | 86 | 3321 | 0.00060556 | 1.5681e-05 | 38.6163
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | FUSE | 5 | 6 | 726 | 0.00013238 | 1.0941e-06 | 121
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | METERING | 5 | 17 | 1523 | 0.00027771 | 3.0998e-06 | 89.5882
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 3 | 4 | 451 | 8.2236e-05 | 7.2937e-07 | 112.75
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | F | POLE | 1 | 185 | 50320 | 0.0091755 | 3.3733e-05 | 272
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | POLE | 2 | 10 | 3143 | 0.0005731 | 1.8234e-06 | 314.3
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONDUCTOR UG | 3 | 3 | 286 | 5.215e-05 | 5.4703e-07 | 95.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 2 | 66 | 1.2035e-05 | 3.6468e-07 | 33
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | FUSE | 2 | 2 | 215 | 3.9204e-05 | 3.6468e-07 | 107.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 8 | 408 | 7.4396e-05 | 1.4587e-06 | 51
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 12 | 660 | 0.00011885 | 2.1609e-06 | 55
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | RELAY | 3 | 2147 | 47234 | 0.0085055 | 0.00038661 | 22
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CE | CABLE TERMINATOR | 1 | 42 | 8148 | 0.0014672 | 7.563e-06 | 194
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 3 | 12 | 135 | 2.431e-05 | 2.1609e-06 | 11.25
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR UG | 398 | 623 | 81886 | 0.014686 | 0.00011174 | 131.4382
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 152 | 3001 | 618861 | 0.11099 | 0.00053823 | 206.2183
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | METERING | 1 | 1 | 148 | 2.6651e-05 | 1.8007e-07 | 148
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 8 | 1040 | 0.00018727 | 1.4406e-06 | 130
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | FUSE | 1 | 1 | 64 | 1.1525e-05 | 1.8007e-07 | 64
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | NONE | 22 | 4356 | 385366 | 0.069115 | 0.00078125 | 88.4679
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | ARRESTER | 8 | 367 | 65922 | 0.011871 | 6.6086e-05 | 179.624
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 2 | 114 | 2.0528e-05 | 3.6014e-07 | 57
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | TOR | NONE | 1 | 102 | 11424 | 0.0020571 | 1.8367e-05 | 112
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 1 | 147 | 2.6364e-05 | 1.7935e-07 | 147
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | GUY/ANCHOR | 1 | 1 | 168 | 3.0252e-05 | 1.8007e-07 | 168
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CROSSARM | 4 | 29 | 5362 | 0.00096555 | 5.2221e-06 | 184.8966
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | FUSE | 1 | 211 | 47686 | 0.0085869 | 3.7995e-05 | 226
AEP Total | 2023 | 5575683 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 1 | 108 | 1.937e-05 | 1.7935e-07 | 108
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | SPLICE, OH | 6 | 7 | 1440 | 0.00025826 | 1.2555e-06 | 205.7143
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | SPLICE, OH | 1 | 1 | 73 | 1.3093e-05 | 1.7935e-07 | 73
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | PEDESTAL | 4 | 5 | 550 | 9.8643e-05 | 8.9675e-07 | 110
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CABLE TERMINATOR | 1 | 2 | 152 | 2.7716e-05 | 3.6468e-07 | 76
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | NONE | 2 | 2 | 165 | 3.0086e-05 | 3.6468e-07 | 82.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 29 | 3043 | 0.00055487 | 5.2879e-06 | 104.931
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | POLE | 7 | 263 | 134871 | 0.024593 | 4.7956e-05 | 512.8175
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 2 | 5 | 220 | 4.0115e-05 | 9.1171e-07 | 44
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 6 | 883 | 0.00016101 | 1.0941e-06 | 147.1667
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | EQF | OTHER EQUIPMENT | 1 | 278 | 12510 | 0.0022811 | 5.0691e-05 | 45
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 6 | 25 | 3546 | 0.00063598 | 4.4838e-06 | 141.84
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 3 | 183 | 3.2953e-05 | 5.4022e-07 | 61
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | FUSE | 2 | 2 | 135 | 2.431e-05 | 3.6014e-07 | 67.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 5 | 13 | 2405 | 0.00043134 | 2.3316e-06 | 185
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | FUSE | 2 | 2 | 245 | 4.4118e-05 | 3.6014e-07 | 122.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | FUSE | 2 | 8 | 350 | 6.2773e-05 | 1.4348e-06 | 43.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | NONE | 33 | 1382 | 123337 | 0.022121 | 0.00024786 | 89.2453
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 6 | 6 | 537 | 9.6311e-05 | 1.0761e-06 | 89.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 55 | 16667 | 0.0030013 | 9.904e-06 | 303.0364
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | FUSE | 2 | 12 | 1869 | 0.00033521 | 2.1522e-06 | 155.75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 62 | 1.1164e-05 | 1.8007e-07 | 62
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | CIRCUIT SWITCHER | 1 | 408 | 28152 | 0.0050133 | 7.2657e-05 | 69
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 728 | 184184 | 0.032799 | 0.00012964 | 253
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 6 | 90 | 1.6206e-05 | 1.0804e-06 | 15
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | F | POLE | 1 | 46 | 14966 | 0.0027095 | 8.3281e-06 | 325.3478
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 3 | 3665 | 101709 | 0.018546 | 0.00066828 | 27.7514
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | FO | NONE | 1 | 28 | 3948 | 0.00071989 | 5.1056e-06 | 141
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 1 | 508 | 9.263e-05 | 1.8234e-07 | 508
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | NONE | 3 | 46 | 2156 | 0.00038394 | 8.1917e-06 | 46.8696
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | RELAY | 1 | 1945 | 33065 | 0.0058882 | 0.00034637 | 17
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | NONE | 1 | 1 | 50 | 8.904e-06 | 1.7808e-07 | 50
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 13 | 1092 | 0.00019446 | 2.315e-06 | 84
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 74 | 1.3493e-05 | 1.8234e-07 | 74
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CUTOUT | 1 | 2 | 152 | 2.7519e-05 | 3.6209e-07 | 76
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | NONE | 245 | 10076 | 2726079 | 0.49355 | 0.0018242 | 270.5517
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 156 | 17334 | 0.0031383 | 2.8243e-05 | 111.1154
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 48 | 8.6902e-06 | 1.8105e-07 | 48
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE HARDWARE | 2 | 3 | 1040 | 0.00018829 | 5.4314e-07 | 346.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | METERING | 8 | 8 | 576 | 0.00010428 | 1.4484e-06 | 72
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | FUSE | 3 | 71 | 10490 | 0.0018992 | 1.2854e-05 | 147.7465
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | FUSE | 2 | 7 | 537 | 9.7222e-05 | 1.2673e-06 | 76.7143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 1 | 546 | 9.8851e-05 | 1.8105e-07 | 546
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 528 | 35070 | 3423416 | 0.61646 | 0.0063151 | 97.6167
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR UG | 316 | 463 | 59586 | 0.01073 | 8.3373e-05 | 128.6955
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | FUSE | 7 | 18 | 1385 | 0.0002494 | 3.2413e-06 | 76.9444
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | TRANSFORMER, POWER - LTC | 1 | 3 | 33 | 5.9745e-06 | 5.4314e-07 | 11
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | ARRESTER | 5 | 1377 | 273587 | 0.049532 | 0.0002493 | 198.6834
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | V | CIRCUIT SWITCHER | 5 | 6545 | 92960 | 0.01683 | 0.0011849 | 14.2032
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | TRANSFORMER, OH | 1 | 1 | 33 | 5.9745e-06 | 1.8105e-07 | 33
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | PEDESTAL | 4 | 22 | 516 | 9.342e-05 | 3.983e-06 | 23.4545
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | NONE | 2 | 8 | 280 | 5.0693e-05 | 1.4484e-06 | 35
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | NONE | 2991 | 23863 | 1408432 | 0.25682 | 0.0043512 | 59.0216
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | NONE | 281 | 10362 | 1094377 | 0.19955 | 0.0018894 | 105.6145
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR UG | 36 | 95 | 14425 | 0.0026303 | 1.7322e-05 | 151.8421
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | INSULATOR | 2 | 791 | 158602 | 0.02892 | 0.00014423 | 200.5082
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | F | NONE | 1 | 19 | 1178 | 0.00021127 | 3.4077e-06 | 62
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 41 | 1834 | 278283 | 0.049557 | 0.0003266 | 151.7356
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 7 | 145 | 64138 | 0.011422 | 2.5822e-05 | 442.331
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | FUSE | 12 | 39 | 3514 | 0.00063024 | 6.9947e-06 | 90.1026
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 124 | 7589 | 585877 | 0.10433 | 0.0013514 | 77.2008
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 29 | 1587 | 50136 | 0.0089282 | 0.00028261 | 31.5917
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 3654 | 245294 | 0.043682 | 0.0006507 | 67.1303
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | FUSE | 2 | 417 | 82364 | 0.014772 | 7.4789e-05 | 197.5156
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | NONE | 44 | 3438 | 93270 | 0.01661 | 0.00061224 | 27.1291
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | NONE | 6 | 17 | 3519 | 0.00064166 | 3.0998e-06 | 207
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 38 | 2888 | 0.0005266 | 6.929e-06 | 76
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | WU | NONE | 13 | 2664 | 418402 | 0.076292 | 0.00048576 | 157.0578
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CROSSARM | 1 | 17 | 4216 | 0.00075078 | 3.0274e-06 | 248
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | WU | NONE | 5 | 1873 | 211776 | 0.037713 | 0.00033354 | 113.0678
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 8 | 651 | 0.00011593 | 1.4246e-06 | 81.375
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | TRANSFORMER, OH | 1 | 5 | 535 | 9.5273e-05 | 8.904e-07 | 107
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | BREAKER | 1 | 145 | 12325 | 0.0021948 | 2.5822e-05 | 85
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 7 | 32 | 7354 | 0.0013096 | 5.6986e-06 | 229.8125
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 232 | 4.1315e-05 | 1.7808e-07 | 232
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | POLE | 2 | 4 | 1210 | 0.00021548 | 7.1232e-07 | 302.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 5 | 1051 | 11610 | 0.0020675 | 0.00018716 | 11.0466
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | ARRESTER | 1 | 389 | 8491 | 0.0015121 | 6.9273e-05 | 21.8278
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 19 | 209 | 3.7219e-05 | 3.3835e-06 | 11
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | SPLICE, OH | 1 | 1 | 20 | 3.5616e-06 | 1.7808e-07 | 20
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 3 | 24 | 4712 | 0.00083911 | 4.2739e-06 | 196.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 2 | 220 | 3.9178e-05 | 3.5616e-07 | 110
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | ARRESTER | 2 | 386 | 97274 | 0.017323 | 6.8739e-05 | 252.0052
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | INSULATOR | 3 | 2053 | 411764 | 0.073327 | 0.0003656 | 200.567
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | OTHER EQUIPMENT | 1 | 1 | 8 | 1.4246e-06 | 1.7808e-07 | 8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | OTHER EQUIPMENT | 1 | 3 | 186 | 3.3123e-05 | 5.3424e-07 | 62
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONN/CLAMP | 3 | 3 | 289 | 5.1465e-05 | 5.3424e-07 | 96.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | BREAKER | 1 | 362 | 39096 | 0.0069622 | 6.4465e-05 | 108
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, GROUNDING | 1 | 1 | 36 | 6.4826e-06 | 1.8007e-07 | 36
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 17 | 3995 | 0.00071939 | 3.0612e-06 | 235
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CROSSARM | 1 | 6 | 1536 | 0.00027659 | 1.0804e-06 | 256
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | O | NONE | 1 | 1 | 84 | 1.5317e-05 | 1.8234e-07 | 84
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | NONE | 3 | 3 | 135 | 2.431e-05 | 5.4022e-07 | 45
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WU | CONDUCTOR OVERHEAD | 2 | 284 | 63808 | 0.01149 | 5.114e-05 | 224.6761
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | INSULATOR | 1 | 5 | 370 | 6.6627e-05 | 9.0036e-07 | 74
AEP Total | 2022 | 5553337 | PARTIAL POWER | FW | NONE | 1 | 5 | 1040 | 0.00018727 | 9.0036e-07 | 208
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | FUSE | 2 | 3 | 166 | 2.9892e-05 | 5.4022e-07 | 55.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 9 | 101 | 5876 | 0.0010464 | 1.7986e-05 | 58.1782
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 133 | 13832 | 0.0024908 | 2.395e-05 | 104
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | V | NONE | 3 | 3104 | 181974 | 0.032768 | 0.00055894 | 58.6256
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, GROUNDING | 1 | 1 | 206 | 3.6684e-05 | 1.7808e-07 | 206
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 369 | 6.5711e-05 | 5.3424e-07 | 123
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 7 | 29 | 3136 | 0.00055846 | 5.1643e-06 | 108.1379
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 2 | 2 | 384 | 6.8383e-05 | 3.5616e-07 | 192
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 540 | 127604 | 0.022724 | 9.6163e-05 | 236.3037
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 1 | 39 | 1053 | 0.00018752 | 6.9451e-06 | 27
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 1 | 51 | 9.0821e-06 | 1.7808e-07 | 51
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 49 | 8.7259e-06 | 1.7808e-07 | 49
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 687 | 18824 | 2564095 | 0.45987 | 0.0033761 | 136.2141
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CUTOUT | 284 | 6019 | 615701 | 0.11043 | 0.0010795 | 102.2929
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | FUSE | 188 | 2346 | 169688 | 0.030434 | 0.00042076 | 72.3308
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | A | NONE | 3 | 1286 | 81695 | 0.014711 | 0.00023157 | 63.5264
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WW | CONDUCTOR OVERHEAD | 3 | 382 | 35080 | 0.0063169 | 6.8787e-05 | 91.8325
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | NONE | 409 | 21401 | 2094026 | 0.37556 | 0.0038383 | 97.8471
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 15 | 6778 | 0.0012205 | 2.7011e-06 | 451.8667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | OTHER EQUIPMENT | 1 | 1 | 20 | 3.6014e-06 | 1.8007e-07 | 20
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CROSSARM | 19 | 252 | 12546 | 0.0022501 | 4.5196e-05 | 49.7857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 16 | 17 | 1404 | 0.00025181 | 3.049e-06 | 82.5882
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | POLE | 2 | 54 | 4476 | 0.00080277 | 9.6849e-06 | 82.8889
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 24 | 3024 | 532038 | 0.095805 | 0.00054454 | 175.9385
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 6 | 662 | 14823 | 0.0026692 | 0.00011921 | 22.3912
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | FUSE | 9 | 27 | 2165 | 0.00038829 | 4.8425e-06 | 80.1852
AEP Total | 2021 | 5523447 | GENERATION | G | NONE | 9 | 11637 | 675443 | 0.12229 | 0.0021068 | 58.0427
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | OL | NONE | 2 | 1789 | 375347 | 0.067955 | 0.00032389 | 209.8083
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | INSULATOR | 1 | 46 | 15180 | 0.0027483 | 8.3281e-06 | 330
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | INSULATOR | 1 | 3 | 162 | 2.933e-05 | 5.4314e-07 | 54
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | V | NONE | 14 | 15848 | 559888 | 0.10209 | 0.0028898 | 35.3286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | FUSE | 100 | 1593 | 114344 | 0.02085 | 0.00029047 | 71.779
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | PEDESTAL | 1 | 3 | 75 | 1.3676e-05 | 5.4703e-07 | 25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CROSSARM | 1 | 8 | 1976 | 0.00036031 | 1.4587e-06 | 247
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 8 | 21 | 1112 | 0.00020276 | 3.8292e-06 | 52.9524
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE | 12 | 459 | 72730 | 0.013262 | 8.3695e-05 | 158.4532
AEP Total | 2024 | 5615460 | PARTIAL POWER | OU | CONDUCTOR UG | 1 | 3 | 189 | 3.3657e-05 | 5.3424e-07 | 63
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 16 | 752 | 0.00013541 | 2.8812e-06 | 47
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | FUSE | 2 | 7 | 580 | 0.00010329 | 1.2466e-06 | 82.8571
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | POLE | 5 | 95 | 30829 | 0.00549 | 1.6918e-05 | 324.5158
AEP Total | 2025 | 5615460 | TRANSMISSION STATION | ERF | NONE | 2 | 331 | 5958 | 0.001061 | 5.8944e-05 | 18
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | PEDESTAL | 1 | 1 | 50 | 8.904e-06 | 1.7808e-07 | 50
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 71 | 11519 | 0.0020513 | 1.2644e-05 | 162.2394
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 2 | 103 | 1.8342e-05 | 3.5616e-07 | 51.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 55 | 9.7944e-06 | 1.7808e-07 | 55
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 33 | 33330 | 0.0059354 | 5.8766e-06 | 1010
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 97 | 1.7467e-05 | 1.8007e-07 | 97
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 1 | 229 | 4.1756e-05 | 1.8234e-07 | 229
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 84 | 7392 | 0.0013479 | 1.5317e-05 | 88
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | NONE | 2 | 4804 | 337124 | 0.060707 | 0.00086507 | 70.1757
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | SWITCH, UG | 1 | 457 | 61633 | 0.011238 | 8.333e-05 | 134.8643
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | SPLICE, OH | 1 | 8 | 1687 | 0.00030761 | 1.4587e-06 | 210.875
AEP Total | 2020 | 5484199 | PARTIAL POWER | WI | NONE | 2 | 4 | 563 | 0.00010266 | 7.2937e-07 | 140.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 15 | 2775 | 0.0004977 | 2.6903e-06 | 185
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 46 | 9108 | 0.0016608 | 8.3877e-06 | 198
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | OU | NONE | 1 | 181 | 15396 | 0.0028073 | 3.3004e-05 | 85.0608
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | SWITCH, OH | 1 | 2674 | 236176 | 0.043065 | 0.00048758 | 88.3231
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | CONDUCTOR UG | 1 | 1 | 107 | 1.9372e-05 | 1.8105e-07 | 107
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | JUMPER/RISER | 4 | 3006 | 1029477 | 0.18333 | 0.00053531 | 342.4741
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | A | NONE | 5 | 1770 | 149337 | 0.026594 | 0.0003152 | 84.3712
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 34 | 2235 | 0.00039801 | 6.0547e-06 | 65.7353
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, STATION SERVICE | 1 | 1 | 61 | 1.0863e-05 | 1.7808e-07 | 61
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 21 | 2730 | 0.00048616 | 3.7397e-06 | 130
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 2 | 216 | 3.8465e-05 | 3.5616e-07 | 108
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | NONE | 1 | 1 | 166 | 2.9561e-05 | 1.7808e-07 | 166
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | NONE | 89 | 935 | 88974 | 0.016108 | 0.00016928 | 95.1594
AEP Total | 2021 | 5523447 | TRANSMISSION STATION | AB | NONE | 3 | 39 | 2714 | 0.00049136 | 7.0608e-06 | 69.5897
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | FUSE | 4 | 7 | 693 | 0.00012547 | 1.2673e-06 | 99
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | POLE | 1 | 408 | 95072 | 0.017212 | 7.3867e-05 | 233.0196
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE | 104 | 7994 | 1581986 | 0.28641 | 0.0014473 | 197.8967
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 5 | 1350 | 0.00024441 | 9.0523e-07 | 270
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 4 | 2052 | 0.00037151 | 7.2419e-07 | 513
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | INSULATOR | 10 | 2301 | 225020 | 0.040739 | 0.00041659 | 97.7923
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 2 | 84 | 1.5208e-05 | 3.6209e-07 | 42
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | POLE HARDWARE | 2 | 1218 | 112901 | 0.02044 | 0.00022051 | 92.6938
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CUTOUT | 1 | 1 | 114 | 2.0639e-05 | 1.8105e-07 | 114
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 83 | 1.5027e-05 | 1.8105e-07 | 83
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | CABLE TERMINATOR | 3 | 958 | 68038 | 0.012318 | 0.00017344 | 71.0209
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | NONE | 2956 | 23167 | 1382955 | 0.24903 | 0.0041717 | 59.695
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | NONE | 103 | 273 | 23761 | 0.0042787 | 4.916e-05 | 87.0366
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CROSSARM | 10 | 1496 | 171257 | 0.030839 | 0.00026939 | 114.4766
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | FUSE | 249 | 2169 | 161381 | 0.02906 | 0.00039058 | 74.4034
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 6 | 800 | 0.00014406 | 1.0804e-06 | 133.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CUTOUT | 1 | 2 | 162 | 2.9172e-05 | 3.6014e-07 | 81
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | NONE | 7 | 609 | 6219 | 0.0011199 | 0.00010966 | 10.2118
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | INSULATOR | 70 | 8978 | 1308331 | 0.23559 | 0.0016167 | 145.7263
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | NONE | 57 | 14007 | 771042 | 0.13884 | 0.0025223 | 55.0469
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 9 | 46 | 2204 | 0.00039688 | 8.2833e-06 | 47.913
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | FUSE | 1 | 1 | 98 | 1.7743e-05 | 1.8105e-07 | 98
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, STATION SERVICE | 1 | 42 | 8232 | 0.0014904 | 7.6039e-06 | 196
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CABLE TERMINATOR | 1 | 3 | 60 | 1.0863e-05 | 5.4314e-07 | 20
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | WU | ARRESTER | 1 | 122 | 2318 | 0.00041967 | 2.2088e-05 | 19
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | U | NONE | 3 | 3004 | 161825 | 0.029507 | 0.00054776 | 53.8698
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | ARRESTER | 1 | 13 | 1963 | 0.00035794 | 2.3704e-06 | 151
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONN/CLAMP | 1 | 1 | 181 | 3.2593e-05 | 1.8007e-07 | 181
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 6 | 21 | 3950 | 0.00070342 | 3.7397e-06 | 188.0952
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | BREAKER | 2 | 2587 | 345683 | 0.061559 | 0.00046069 | 133.6231
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, STATION SERVICE | 2 | 7 | 277 | 4.9328e-05 | 1.2466e-06 | 39.5714
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | NONE | 4 | 290 | 29635 | 0.0052774 | 5.1643e-05 | 102.1897
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | NONE | 1 | 1 | 39 | 6.9451e-06 | 1.7808e-07 | 39
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONN/CLAMP | 7 | 10 | 1130 | 0.00020348 | 1.8007e-06 | 113
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 77 | 317 | 59656 | 0.010742 | 5.7083e-05 | 188.1893
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WU | FUSE | 1 | 246 | 21156 | 0.0038096 | 4.4298e-05 | 86
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | NONE | 1608 | 68910 | 2684190 | 0.48141 | 0.012359 | 38.9521
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 9 | 1246 | 0.00022437 | 1.6206e-06 | 138.4444
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WU | NONE | 13 | 9405 | 507522 | 0.09139 | 0.0016936 | 53.963
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | FUSE | 188 | 2550 | 226432 | 0.040611 | 0.00045734 | 88.7969
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WU | NONE | 5 | 2922 | 297061 | 0.053492 | 0.00052617 | 101.6636
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CUTOUT | 2 | 5 | 828 | 0.0001491 | 9.0036e-07 | 165.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | NONE | 24 | 159 | 13786 | 0.0024725 | 2.8517e-05 | 86.7044
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 12 | 150 | 12792 | 0.0022942 | 2.6903e-05 | 85.28
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 7 | 35 | 7725 | 0.0013911 | 6.3025e-06 | 220.7143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 30 | 174 | 6732 | 0.0012074 | 3.1207e-05 | 38.6897
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | NONE | 6 | 24 | 1529 | 0.00027533 | 4.3217e-06 | 63.7083
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE | 3 | 79 | 16830 | 0.0030185 | 1.4169e-05 | 213.038
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | CUTOUT | 5 | 88 | 15476 | 0.0027756 | 1.5783e-05 | 175.8636
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 71 | 819 | 186979 | 0.034094 | 0.00014934 | 228.3016
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WW | NONE | 8 | 7922 | 440431 | 0.080309 | 0.0014445 | 55.5959
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 7 | 967 | 65360 | 0.011918 | 0.00017632 | 67.5905
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 28 | 1707 | 127463 | 0.023242 | 0.00031126 | 74.6708
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CUTOUT | 4 | 44 | 5642 | 0.0010288 | 8.023e-06 | 128.2273
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | O | SPLICE, OH | 1 | 1 | 107 | 1.9511e-05 | 1.8234e-07 | 107
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 7 | 42 | 7.6584e-06 | 1.2764e-06 | 6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | INSULATOR | 1 | 6 | 150 | 2.7351e-05 | 1.0941e-06 | 25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 2 | 117 | 12010 | 0.0021899 | 2.1334e-05 | 102.6496
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | NONE | 82 | 9466 | 1043045 | 0.19019 | 0.001726 | 110.1886
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CROSSARM | 8 | 71 | 2646 | 0.00048248 | 1.2946e-05 | 37.2676
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 6 | 546 | 9.9559e-05 | 1.0941e-06 | 91
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 2 | 365 | 5110 | 0.00093177 | 6.6555e-05 | 14
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, UG | 4 | 56 | 4275 | 0.00077951 | 1.0211e-05 | 76.3393
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 868 | 64787 | 0.011813 | 0.00015827 | 74.6394
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 2 | 3 | 179 | 3.2639e-05 | 5.4703e-07 | 59.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 3 | 731 | 21428 | 0.0039072 | 0.00013329 | 29.3133
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | U | NONE | 8 | 3794 | 95840 | 0.017476 | 0.00069181 | 25.2609
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | SPLICE, OH | 1 | 4 | 160 | 2.9175e-05 | 7.2937e-07 | 40
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | NONE | 8 | 18 | 1933 | 0.00034668 | 3.2283e-06 | 107.3889
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | FUSE | 9 | 24 | 1642 | 0.00029449 | 4.3044e-06 | 68.4167
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 3 | 357 | 6.4028e-05 | 5.3805e-07 | 119
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 1103 | 103916 | 0.018637 | 0.00019782 | 94.2121
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | NONE | 601 | 38874 | 4157988 | 0.74045 | 0.0069227 | 106.9606
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 49 | 9335 | 321553 | 0.057262 | 0.0016624 | 34.446
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | FUSE | 251 | 1951 | 125193 | 0.022294 | 0.00034743 | 64.1686
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 473 | 47420 | 0.0085048 | 8.4833e-05 | 100.2537
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 27 | 463 | 34813 | 0.0061995 | 8.2451e-05 | 75.1901
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | NONE | 57 | 83 | 9526 | 0.0016964 | 1.4781e-05 | 114.7711
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 30 | 650 | 102423 | 0.018239 | 0.00011575 | 157.5738
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 14 | 206 | 43919 | 0.0078211 | 3.6684e-05 | 213.199
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 112 | 1648 | 132345 | 0.023568 | 0.00029348 | 80.3064
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | ABI | NONE | 4 | 6460 | 54241 | 0.0096592 | 0.0011504 | 8.3964
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 39 | 5927 | 525816 | 0.093637 | 0.0010555 | 88.7154
AEP Total | 2023 | 5575683 | PARTIAL POWER | V | CONN/CLAMP | 1 | 1 | 34 | 6.0979e-06 | 1.7935e-07 | 34
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | POLE | 2 | 3 | 391 | 7.0126e-05 | 5.3805e-07 | 130.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | TRANSFORMER, OH | 1 | 359 | 75390 | 0.013576 | 6.4646e-05 | 210
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | JUMPER/RISER | 1 | 1 | 92 | 1.6656e-05 | 1.8105e-07 | 92
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | NONE | 233 | 15304 | 719187 | 0.12807 | 0.0027253 | 46.9934
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 26 | 3540 | 275290 | 0.049024 | 0.0006304 | 77.7655
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 1 | 28 | 5.0218e-06 | 1.7935e-07 | 28
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 14 | 1224 | 0.00021952 | 2.5109e-06 | 87.4286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONN/CLAMP | 4 | 4 | 319 | 5.7213e-05 | 7.174e-07 | 79.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CROSSARM | 1 | 7 | 2590 | 0.00046452 | 1.2555e-06 | 370
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | INSULATOR | 1 | 1 | 34 | 6.1996e-06 | 1.8234e-07 | 34
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, OH | 5 | 1334 | 62087 | 0.011321 | 0.00024324 | 46.542
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 3 | 14 | 1403 | 0.00025583 | 2.5528e-06 | 100.2143
AEP Total | 2024 | 5615460 | PARTIAL POWER | WT | NONE | 1 | 1 | 123 | 2.1904e-05 | 1.7808e-07 | 123
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | SPLICE, OH | 2 | 28 | 2408 | 0.00043596 | 5.0693e-06 | 86
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 1 | 156 | 2.8243e-05 | 1.8105e-07 | 156
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | INSULATOR | 1 | 252 | 26964 | 0.004836 | 4.5196e-05 | 107
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | NONE | 1 | 1 | 80 | 1.4348e-05 | 1.7935e-07 | 80
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 4 | 844 | 0.00015137 | 7.174e-07 | 211
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CUTOUT | 1 | 1 | 212 | 3.8022e-05 | 1.7935e-07 | 212
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | SPLICE, OH | 1 | 1 | 49 | 8.7882e-06 | 1.7935e-07 | 49
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | POLE | 2 | 11 | 1894 | 0.0003429 | 1.9915e-06 | 172.1818
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | JUMPER/RISER | 1 | 441 | 26901 | 0.0049052 | 8.0413e-05 | 61
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | POLE | 1 | 159 | 10010 | 0.0018123 | 2.8786e-05 | 62.956
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 305 | 5.5219e-05 | 1.8105e-07 | 305
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 2 | 5 | 465 | 8.4187e-05 | 9.0523e-07 | 93
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | NONE | 1 | 1 | 104 | 1.8829e-05 | 1.8105e-07 | 104
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | INSULATOR | 2 | 956 | 81724 | 0.014902 | 0.00017432 | 85.4854
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 101 | 12928 | 0.0023406 | 1.8286e-05 | 128
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | TRANSFORMER, OH | 1 | 2 | 174 | 3.1333e-05 | 3.6014e-07 | 87
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 106 | 397 | 62952 | 0.01121 | 7.0698e-05 | 158.5693
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 2 | 14 | 1669 | 0.00030054 | 2.521e-06 | 119.2143
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | CONDUCTOR UG | 4 | 618 | 119224 | 0.021469 | 0.00011128 | 192.9191
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | SWITCH, UG | 2 | 881 | 110356 | 0.01998 | 0.0001595 | 125.2622
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | POLE | 23 | 205 | 28088 | 0.0050019 | 3.6506e-05 | 137.0146
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 14 | 1203 | 253963 | 0.045226 | 0.00021423 | 211.1081
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 38 | 883 | 196342 | 0.034965 | 0.00015724 | 222.3579
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | AO | NONE | 3 | 2423 | 103597 | 0.018449 | 0.00043149 | 42.7557
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | RELAY | 1 | 772 | 15440 | 0.0027496 | 0.00013748 | 20
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 4 | 4 | 733 | 0.00013053 | 7.1232e-07 | 183.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 6 | 28 | 1362 | 0.00024254 | 4.9862e-06 | 48.6429
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 10 | 60 | 1.0685e-05 | 1.7808e-06 | 6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | NONE | 4 | 11 | 896 | 0.00015956 | 1.9589e-06 | 81.4545
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | AB | ARRESTER | 1 | 1177 | 40018 | 0.0071264 | 0.0002096 | 34
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 5 | 730 | 0.00013 | 8.904e-07 | 146
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 1 | 423 | 62528 | 0.011135 | 7.5328e-05 | 147.8203
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 2 | 5735 | 91760 | 0.016613 | 0.0010383 | 16
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | R | NONE | 3 | 2287 | 130294 | 0.023462 | 0.00041182 | 56.9716
AEP Total | 2020 | 5484199 | PARTIAL POWER | WI | CONDUCTOR UG | 1 | 1 | 131 | 2.3887e-05 | 1.8234e-07 | 131
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | POLE | 1 | 8 | 288 | 5.2515e-05 | 1.4587e-06 | 36
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 3 | 761 | 117214 | 0.021107 | 0.00013703 | 154.0263
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | WL | POLE | 1 | 568 | 57368 | 0.01033 | 0.00010228 | 101
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CUTOUT | 1 | 30 | 990 | 0.00018052 | 5.4703e-06 | 33
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 1 | 1 | 133 | 2.3854e-05 | 1.7935e-07 | 133
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 2 | 220 | 3.9457e-05 | 3.587e-07 | 110
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 6 | 22 | 941 | 0.00016757 | 3.9178e-06 | 42.7727
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | WW | POLE | 1 | 615 | 153135 | 0.02727 | 0.00010952 | 249
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 1 | 186 | 3.3123e-05 | 1.7808e-07 | 186
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 1 | 62 | 1.1041e-05 | 1.7808e-07 | 62
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | POLE HARDWARE | 1 | 2 | 158 | 2.8137e-05 | 3.5616e-07 | 79
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 340 | 131580 | 0.023822 | 6.1556e-05 | 387
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 4 | 356 | 6.4453e-05 | 7.2419e-07 | 89
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CUTOUT | 3 | 12 | 1163 | 0.00021056 | 2.1726e-06 | 96.9167
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR UG | 6 | 7 | 1237 | 0.00022395 | 1.2673e-06 | 176.7143
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 1 | 17 | 3.0778e-06 | 1.8105e-07 | 17
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 2 | 35 | 10502 | 0.0019013 | 6.3366e-06 | 300.0571
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | FUSE | 1 | 28 | 3080 | 0.00055762 | 5.0693e-06 | 110
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | FO | NONE | 4 | 538 | 69106 | 0.012511 | 9.7403e-05 | 128.4498
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ERF | CONDUCTOR OVERHEAD | 2 | 700 | 117382 | 0.021252 | 0.00012673 | 167.6886
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | METERING | 2 | 2 | 75 | 1.3578e-05 | 3.6209e-07 | 37.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CIRCUIT SWITCHER | 1 | 1344 | 33600 | 0.0060832 | 0.00024333 | 25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CUTOUT | 2 | 4 | 311 | 5.6305e-05 | 7.2419e-07 | 77.75
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | NONE | 1 | 2 | 52 | 9.4144e-06 | 3.6209e-07 | 26
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR UG | 293 | 434 | 66626 | 0.012149 | 7.9136e-05 | 153.5161
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONN/CLAMP | 109 | 409 | 20159 | 0.0036758 | 7.4578e-05 | 49.2885
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CROSSARM | 3 | 332 | 23029 | 0.0041992 | 6.0538e-05 | 69.3645
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | FUSE | 4 | 40 | 1397 | 0.00025473 | 7.2937e-06 | 34.925
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONN/CLAMP | 295 | 515 | 37499 | 0.0067525 | 9.2737e-05 | 72.8136
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 88 | 3616 | 395894 | 0.070501 | 0.00064394 | 109.484
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 5 | 1636 | 147035 | 0.026184 | 0.00029134 | 89.8747
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | NONE | 4 | 28 | 1835 | 0.00032678 | 4.9862e-06 | 65.5357
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 10 | 2562 | 337115 | 0.060033 | 0.00045624 | 131.5827
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | CONN/CLAMP | 1 | 3 | 57 | 1.032e-05 | 5.4314e-07 | 19
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | ARRESTER | 2 | 510 | 67681 | 0.012053 | 9.0821e-05 | 132.7078
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | NONE | 14 | 19 | 2145 | 0.00038198 | 3.3835e-06 | 112.8947
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 19 | 41 | 2996 | 0.00053353 | 7.3013e-06 | 73.0732
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 6 | 1795 | 432878 | 0.077087 | 0.00031965 | 241.1577
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | FUSE | 1 | 13 | 975 | 0.00017363 | 2.315e-06 | 75
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | ARRESTER | 1 | 20 | 1200 | 0.0002137 | 3.5616e-06 | 60
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | NONE | 12 | 14 | 2355 | 0.00041938 | 2.4931e-06 | 168.2143
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | NONE | 6 | 8 | 2138 | 0.00038073 | 1.4246e-06 | 267.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONN/CLAMP | 2 | 2 | 119 | 2.1191e-05 | 3.5616e-07 | 59.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | NONE | 2 | 89 | 3861 | 0.00068757 | 1.5849e-05 | 43.382
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONN/CLAMP | 3 | 18 | 508 | 9.0465e-05 | 3.2054e-06 | 28.2222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | METERING | 1 | 20 | 1920 | 0.00034191 | 3.5616e-06 | 96
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | NONE | 2 | 29 | 2807 | 0.00049987 | 5.1643e-06 | 96.7931
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 114 | 2.0446e-05 | 1.7935e-07 | 114
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | SWITCH, OH | 5 | 1187 | 35802 | 0.0063756 | 0.00021138 | 30.1618
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 72 | 1.2913e-05 | 1.7935e-07 | 72
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 3 | 380 | 6.767e-05 | 5.3424e-07 | 126.6667
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | FUSE | 3 | 35 | 12963 | 0.0023084 | 6.2328e-06 | 370.3714
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 180 | 3.2054e-05 | 5.3424e-07 | 60
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | A | NONE | 1 | 1274 | 21658 | 0.0038569 | 0.00022687 | 17
AEP Total | 2020 | 5484199 | PARTIAL POWER | WI | CONN/CLAMP | 3 | 6 | 1220 | 0.00022246 | 1.0941e-06 | 203.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | OU | CONDUCTOR OVERHEAD | 1 | 1 | 38 | 6.8798e-06 | 1.8105e-07 | 38
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 57 | 1.032e-05 | 1.8105e-07 | 57
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | FO | NONE | 1 | 246 | 34932 | 0.0063696 | 4.4856e-05 | 142
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 4 | 5 | 439 | 7.9052e-05 | 9.0036e-07 | 87.8
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 17 | 2221 | 0.00039552 | 3.0274e-06 | 130.6471
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 7 | 477 | 95889 | 0.017076 | 8.4944e-05 | 201.0252
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 18 | 212 | 71143 | 0.012669 | 3.7753e-05 | 335.5802
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 64 | 16930 | 0.0030149 | 1.1397e-05 | 264.5312
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 23 | 1737 | 163331 | 0.029086 | 0.00030932 | 94.0305
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, POWER - LTC | 1 | 1 | 78 | 1.389e-05 | 1.7808e-07 | 78
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | U | NONE | 13 | 2155 | 453364 | 0.080735 | 0.00038376 | 210.3777
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 19 | 2755 | 0.00049061 | 3.3835e-06 | 145
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CABLE TERMINATOR | 1 | 24 | 22968 | 0.0040901 | 4.2739e-06 | 957
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 16 | 2336 | 0.00041896 | 2.8696e-06 | 146
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 1 | 225 | 4.0516e-05 | 1.8007e-07 | 225
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | PEDESTAL | 1 | 3 | 465 | 8.4789e-05 | 5.4703e-07 | 155
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | SWITCH, OH | 1 | 366 | 40352 | 0.0072663 | 6.5906e-05 | 110.2514
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | BREAKER | 1 | 306 | 26928 | 0.0049101 | 5.5797e-05 | 88
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | JUMPER/RISER | 1 | 1 | 116 | 2.1152e-05 | 1.8234e-07 | 116
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | EQF | POLE | 6 | 1629 | 1043578 | 0.18584 | 0.00029009 | 640.6249
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | PEDESTAL | 1 | 3 | 768 | 0.00013677 | 5.3424e-07 | 256
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 1 | 148 | 2.6356e-05 | 1.7808e-07 | 148
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 6 | 624 | 0.00011112 | 1.0685e-06 | 104
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | POLE HARDWARE | 1 | 3 | 579 | 0.00010311 | 5.3424e-07 | 193
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 40 | 6630 | 0.0012089 | 7.2937e-06 | 165.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 332 | 4591 | 336309 | 0.060888 | 0.00083118 | 73.254
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 5 | 151 | 2.7338e-05 | 9.0523e-07 | 30.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | NONE | 231 | 3316 | 291159 | 0.052713 | 0.00060035 | 87.8043
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CROSSARM | 17 | 2704 | 161987 | 0.029327 | 0.00048955 | 59.9064
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 82 | 1768 | 238584 | 0.043195 | 0.00032009 | 134.9457
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, OH | 11 | 5886 | 536744 | 0.097176 | 0.0010656 | 91.1899
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 8 | 193 | 35605 | 0.0064462 | 3.4942e-05 | 184.4819
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | NONE | 7 | 4850 | 259747 | 0.047026 | 0.00087807 | 53.5561
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | JUMPER/RISER | 7 | 182 | 16821 | 0.0030454 | 3.295e-05 | 92.4231
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | FUSE | 15 | 230 | 14828 | 0.0026846 | 4.1641e-05 | 64.4696
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | NONE | 18 | 84 | 10630 | 0.0019245 | 1.5208e-05 | 126.5476
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CROSSARM | 3 | 55 | 36299 | 0.0065718 | 9.9576e-06 | 659.9818
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | V | NONE | 1 | 58 | 2692 | 0.00048281 | 1.0402e-05 | 46.4138
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 10 | 18 | 3399 | 0.00061978 | 3.2822e-06 | 188.8333
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | NONE | 4 | 4 | 391 | 7.1296e-05 | 7.2937e-07 | 97.75
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 166 | 3.0269e-05 | 1.8234e-07 | 166
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 3 | 68 | 1.2399e-05 | 5.4703e-07 | 22.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 6 | 408 | 7.4396e-05 | 1.0941e-06 | 68
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | WW | NONE | 1 | 248 | 99696 | 0.018179 | 4.5221e-05 | 402
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 3 | 1398 | 143179 | 0.025679 | 0.00025073 | 102.417
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 302 | 5.378e-05 | 1.7808e-07 | 302
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | NONE | 1721 | 89016 | 3548114 | 0.63185 | 0.015852 | 39.8593
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | SPLICE, UG | 1 | 1 | 126 | 2.2598e-05 | 1.7935e-07 | 126
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 11 | 1043 | 0.00018706 | 1.9729e-06 | 94.8182
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | FUSE | 2 | 9 | 985 | 0.00017666 | 1.6142e-06 | 109.4444
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 4 | 24 | 2541 | 0.00045573 | 4.3044e-06 | 105.875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 3011 | 310553 | 0.055698 | 0.00054002 | 103.1395
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 6 | 30 | 1248 | 0.00022473 | 5.4022e-06 | 41.6
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | NONE | 7 | 30 | 5743 | 0.00103 | 5.3805e-06 | 191.4333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 3 | 639 | 0.00011507 | 5.4022e-07 | 213
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | ARRESTER | 4 | 271 | 23725 | 0.0042551 | 4.8604e-05 | 87.5461
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 5 | 685 | 0.00012285 | 8.9675e-07 | 137
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 8 | 1194 | 36709 | 0.0065838 | 0.00021414 | 30.7446
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | ARRESTER | 1 | 2 | 92 | 1.6567e-05 | 3.6014e-07 | 46
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 4 | 4628 | 0.00083003 | 7.174e-07 | 1157
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | NONE | 45 | 7702 | 392189 | 0.069841 | 0.0013716 | 50.9204
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 12 | 201 | 12873 | 0.0022924 | 3.5794e-05 | 64.0448
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 7 | 89 | 10085 | 0.0017959 | 1.5849e-05 | 113.3146
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 17 | 465 | 8.2807e-05 | 3.0274e-06 | 27.3529
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | CONDUCTOR UG | 1 | 20 | 18440 | 0.0033072 | 3.587e-06 | 922
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 1 | 68 | 1.2109e-05 | 1.7808e-07 | 68
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | OTHER EQUIPMENT | 1 | 558 | 96839 | 0.017368 | 0.00010008 | 173.5466
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 8 | 606 | 101982 | 0.018161 | 0.00010792 | 168.2871
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 3 | 16 | 6910 | 0.0012305 | 2.8493e-06 | 431.875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 1 | 35 | 5635 | 0.0010106 | 6.2773e-06 | 161
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 15 | 219 | 20859 | 0.0037146 | 3.8999e-05 | 95.2466
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 36 | 10422 | 0.0018692 | 6.4566e-06 | 289.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | CUTOUT | 3 | 3 | 378 | 6.7794e-05 | 5.3805e-07 | 126
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 3 | 44 | 4931 | 0.00088438 | 7.8914e-06 | 112.0682
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | JUMPER/RISER | 2 | 36 | 1782 | 0.00032089 | 6.4826e-06 | 49.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 439 | 666 | 96992 | 0.017272 | 0.0001186 | 145.6336
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 285 | 8212 | 805955 | 0.14352 | 0.0014624 | 98.1436
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 431 | 16085 | 1861320 | 0.33146 | 0.0028644 | 115.7177
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 160 | 28044 | 2834518 | 0.50477 | 0.0049941 | 101.074
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | F | NONE | 26 | 26616 | 12675312 | 2.2733 | 0.0047736 | 476.229
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | POLE | 16 | 1409 | 218015 | 0.039101 | 0.0002527 | 154.7303
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 440 | 64575 | 0.0115 | 7.8355e-05 | 146.7614
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | NONE | 23 | 283 | 33113 | 0.0058968 | 5.0397e-05 | 117.0071
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 20 | 33 | 3137 | 0.00055864 | 5.8766e-06 | 95.0606
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 18 | 340 | 74470 | 0.013262 | 6.0547e-05 | 219.0294
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | NONE | 6 | 437 | 191079 | 0.034027 | 7.7821e-05 | 437.2517
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | WW | NONE | 5 | 1296 | 91983 | 0.01638 | 0.00023079 | 70.9745
AEP Total | 2023 | 5575683 | PARTIAL POWER | WI | FUSE | 1 | 1 | 245 | 4.3941e-05 | 1.7935e-07 | 245
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | NONE | 3 | 6 | 1107 | 0.00019713 | 1.0685e-06 | 184.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 5 | 2429 | 0.00043256 | 8.904e-07 | 485.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | POLE | 9 | 1609 | 1042949 | 0.18573 | 0.00028653 | 648.197
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AB | NONE | 4 | 3852 | 200550 | 0.035969 | 0.00069086 | 52.0639
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | JUMPER/RISER | 8 | 119 | 22507 | 0.0040529 | 2.1429e-05 | 189.1345
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 15 | 1860 | 0.00033916 | 2.7351e-06 | 124
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 36 | 3868 | 0.00069373 | 6.4566e-06 | 107.4444
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 7 | 2096 | 0.00037592 | 1.2555e-06 | 299.4286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 57 | 2565 | 0.00046003 | 1.0223e-05 | 45
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 48 | 3888 | 0.00069731 | 8.6088e-06 | 81
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | FUSE | 4 | 21 | 954 | 0.00017272 | 3.802e-06 | 45.4286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | ARRESTER | 1 | 6 | 636 | 0.00011597 | 1.0941e-06 | 106
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | INSULATOR | 3 | 20 | 2911 | 0.0005308 | 3.6468e-06 | 145.55
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | METERING | 1 | 2 | 112 | 2.0422e-05 | 3.6468e-07 | 56
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CROSSARM | 8 | 918 | 187341 | 0.033735 | 0.00016531 | 204.0752
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | NONE | 6 | 28 | 7057 | 0.0012708 | 5.042e-06 | 252.0357
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 361 | 93909 | 0.01691 | 6.5006e-05 | 260.1357
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CONDUCTOR UG | 10 | 37 | 3405 | 0.00061314 | 6.6627e-06 | 92.027
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CROSSARM | 179 | 18321 | 1920333 | 0.34441 | 0.0032859 | 104.8159
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | POLE | 43 | 811 | 150006 | 0.026904 | 0.00014545 | 184.9642
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CUTOUT | 4 | 18 | 355 | 6.3926e-05 | 3.2413e-06 | 19.7222
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | JUMPER/RISER | 4 | 41 | 11029 | 0.001986 | 7.3829e-06 | 269
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE | 9 | 3039 | 662624 | 0.11932 | 0.00054724 | 218.0401
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | FUSE | 11 | 157 | 18891 | 0.0034017 | 2.8271e-05 | 120.3248
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | FUSE | 4 | 22 | 1258 | 0.00022653 | 3.9616e-06 | 57.1818
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | OU | NONE | 3 | 1540 | 148088 | 0.026666 | 0.00027731 | 96.161
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | NONE | 2 | 1963 | 62816 | 0.011266 | 0.00035206 | 32
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | NONE | 4 | 127 | 16614 | 0.0029797 | 2.2777e-05 | 130.8189
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | REGULATOR | 9 | 3876 | 327794 | 0.059026 | 0.00069796 | 84.5702
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | NONE | 85 | 180 | 10488 | 0.001881 | 3.2283e-05 | 58.2667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | METERING | 7 | 9 | 859 | 0.00015406 | 1.6142e-06 | 95.4444
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | R | CABLE TERMINATOR | 1 | 2093 | 210327 | 0.037722 | 0.00037538 | 100.4907
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | JUMPER/RISER | 2 | 2 | 212 | 3.8022e-05 | 3.587e-07 | 106
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 1 | 1110 | 83250 | 0.014931 | 0.00019908 | 75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 1 | 18 | 3.2283e-06 | 1.7935e-07 | 18
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | WU | NONE | 37 | 6147 | 511273 | 0.091697 | 0.0011025 | 83.1744
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | FUSE | 11 | 103 | 12140 | 0.0021979 | 1.8648e-05 | 117.8641
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | FO | RECLOSER, LINE/OCR/BR | 1 | 445 | 72535 | 0.013132 | 8.0566e-05 | 163
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | FUSE | 2 | 4 | 320 | 5.7935e-05 | 7.2419e-07 | 80
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | CONDUCTOR UG | 1 | 14 | 882 | 0.00015968 | 2.5346e-06 | 63
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONN/CLAMP | 334 | 542 | 44088 | 0.0080391 | 9.8829e-05 | 81.3432
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | ARRESTER | 143 | 6803 | 485012 | 0.088438 | 0.0012405 | 71.2938
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | FUSE | 13 | 21 | 1273 | 0.00023212 | 3.8292e-06 | 60.619
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | NONE | 7 | 2211 | 464458 | 0.08469 | 0.00040316 | 210.0669
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 46 | 50 | 5425 | 0.00098921 | 9.1171e-06 | 108.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | FUSE | 1 | 1 | 120 | 2.1881e-05 | 1.8234e-07 | 120
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | FUSE | 2 | 4 | 256 | 4.668e-05 | 7.2937e-07 | 64
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | ARRESTER | 4 | 52 | 10026 | 0.0018282 | 9.4818e-06 | 192.8077
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 9 | 5999 | 878528 | 0.16019 | 0.0010939 | 146.4457
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | METERING | 2 | 2 | 176 | 3.2092e-05 | 3.6468e-07 | 88
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | METERING | 3 | 4 | 278 | 5.0691e-05 | 7.2937e-07 | 69.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CUTOUT | 20 | 62 | 4736 | 0.00086357 | 1.1305e-05 | 76.3871
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 6 | 327 | 5.9626e-05 | 1.0941e-06 | 54.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 77 | 1.404e-05 | 1.8234e-07 | 77
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | WL | NONE | 4 | 785 | 128308 | 0.023396 | 0.00014314 | 163.4497
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | FUSE | 1 | 1 | 48 | 8.7524e-06 | 1.8234e-07 | 48
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 2 | 2512 | 203472 | 0.037101 | 0.00045804 | 81
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONN/CLAMP | 4 | 12 | 4384 | 0.00079939 | 2.1881e-06 | 365.3333
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 3 | 1150 | 50615 | 0.0092292 | 0.00020969 | 44.013
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | SPLICE, UG | 1 | 1 | 240 | 4.3762e-05 | 1.8234e-07 | 240
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WL | CIRCUIT SWITCHER | 4 | 1545 | 23123 | 0.0042163 | 0.00028172 | 14.9663
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | INSULATOR | 3 | 161 | 60267 | 0.010989 | 2.9357e-05 | 374.3292
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | SPLICE, OH | 1 | 1 | 104 | 1.8964e-05 | 1.8234e-07 | 104
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 11 | 897 | 0.00016152 | 1.9808e-06 | 81.5455
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | F | FUSE | 3 | 14 | 799 | 0.0001433 | 2.5109e-06 | 57.0714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 2 | 172 | 3.0972e-05 | 3.6014e-07 | 86
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | FUSE | 7 | 8 | 572 | 0.000103 | 1.4406e-06 | 71.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR UG | 4 | 4 | 576 | 0.00010372 | 7.2029e-07 | 144
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 9 | 903 | 111330 | 0.019967 | 0.00016195 | 123.289
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 819 | 55427 | 0.0099808 | 0.00014748 | 67.6764
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | NONE | 7 | 7 | 445 | 7.9811e-05 | 1.2555e-06 | 63.5714
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 3 | 203 | 3.6555e-05 | 5.4022e-07 | 67.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 168 | 399 | 30508 | 0.0054716 | 7.1561e-05 | 76.4612
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 6 | 564 | 0.00010156 | 1.0804e-06 | 94
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | NONE | 46 | 1349 | 165882 | 0.030247 | 0.00024598 | 122.9666
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | METERING | 66 | 142 | 14385 | 0.002623 | 2.5893e-05 | 101.3028
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | FUSE | 24 | 74 | 5195 | 0.00094727 | 1.3493e-05 | 70.2027
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CUTOUT | 3 | 5 | 771 | 0.00014059 | 9.1171e-07 | 154.2
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | WU | CROSSARM | 2 | 521 | 34924 | 0.0063681 | 9.5e-05 | 67.0326
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | TRANSFORMER, STATION SERVICE | 1 | 5 | 225 | 4.0068e-05 | 8.904e-07 | 45
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | NONE | 1556 | 26451 | 4062969 | 0.73559 | 0.0047889 | 153.6036
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 149 | 5326 | 738747 | 0.13375 | 0.00096425 | 138.7058
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | METERING | 52 | 57 | 4952 | 0.00089654 | 1.032e-05 | 86.8772
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 67 | 4748 | 713889 | 0.12925 | 0.00085961 | 150.3557
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | INSULATOR | 43 | 5550 | 485477 | 0.087894 | 0.0010048 | 87.4733
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | FUSE | 1 | 63 | 6139 | 0.0011114 | 1.1406e-05 | 97.4444
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 31 | 5558 | 0.0010063 | 5.6124e-06 | 179.2903
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | V | NONE | 11 | 13023 | 253082 | 0.04582 | 0.0023578 | 19.4335
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WU | NONE | 7 | 2787 | 172444 | 0.03122 | 0.00050458 | 61.8744
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 448 | 2058 | 314494 | 0.056632 | 0.00037059 | 152.8154
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONN/CLAMP | 5 | 274 | 54323 | 0.009782 | 4.934e-05 | 198.2591
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | NONE | 16 | 31 | 2923 | 0.00052635 | 5.5822e-06 | 94.2903
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | ARRESTER | 17 | 29 | 2401 | 0.00043235 | 5.2221e-06 | 82.7931
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 1907 | 74672 | 0.013519 | 0.00034526 | 39.1568
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | INSULATOR | 4 | 1389 | 118074 | 0.021377 | 0.00025147 | 85.0065
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | WL | POLE | 1 | 279 | 96534 | 0.017477 | 5.0512e-05 | 346
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 33 | 5709 | 0.0010336 | 5.9745e-06 | 173
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 67 | 452 | 75880 | 0.013664 | 8.1393e-05 | 167.8761
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | OTHER EQUIPMENT | 1 | 2 | 140 | 2.4931e-05 | 3.5616e-07 | 70
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 1 | 3 | 117 | 2.0835e-05 | 5.3424e-07 | 39
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | U | POLE | 1 | 1128 | 203040 | 0.037023 | 0.00020568 | 180
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 2 | 262 | 4.7179e-05 | 3.6014e-07 | 131
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | ERF | NONE | 1 | 937 | 91826 | 0.016352 | 0.00016686 | 98
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 1 | 15 | 2025 | 0.00036061 | 2.6712e-06 | 135
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 53 | 11872 | 0.0021292 | 9.5056e-06 | 224
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 2 | 1224 | 0.00022319 | 3.6468e-07 | 612
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 458 | 8.3513e-05 | 1.8234e-07 | 458
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 744 | 9672 | 0.0017347 | 0.00013344 | 13
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | METERING | 1 | 1 | 43 | 7.8407e-06 | 1.8234e-07 | 43
AEP Total | 2020 | 5484199 | PARTIAL POWER | FW | TRANSFORMER, OH | 1 | 6 | 198 | 3.6104e-05 | 1.0941e-06 | 33
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | TRANSFORMER, GROUNDING | 1 | 1 | 20 | 3.6468e-06 | 1.8234e-07 | 20
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | JUMPER/RISER | 1 | 1 | 188 | 3.3854e-05 | 1.8007e-07 | 188
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | OU | NONE | 1 | 205 | 9840 | 0.0017942 | 3.738e-05 | 48
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | ERF | NONE | 3 | 893 | 102946 | 0.018333 | 0.00015903 | 115.2811
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | NONE | 1742 | 65969 | 2901650 | 0.52533 | 0.011943 | 43.9851
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 365 | 2169 | 298997 | 0.054132 | 0.00039269 | 137.8502
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 444 | 29234 | 3403313 | 0.61616 | 0.0052927 | 116.4163
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | METERING | 1 | 1 | 217 | 3.9287e-05 | 1.8105e-07 | 217
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 28 | 4646 | 505123 | 0.091451 | 0.00084114 | 108.7221
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | FUSE | 5 | 9 | 901 | 0.00016312 | 1.6294e-06 | 100.1111
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | NONE | 41 | 8639 | 653275 | 0.11827 | 0.0015641 | 75.6193
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | NONE | 25 | 226 | 15486 | 0.0028037 | 4.0916e-05 | 68.5221
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 263 | 4.7615e-05 | 1.8105e-07 | 263
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, UG | 6 | 1286 | 182571 | 0.033054 | 0.00023283 | 141.9681
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | FUSE | 3 | 3 | 225 | 4.0735e-05 | 5.4314e-07 | 75
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | FUSE | 3 | 3 | 255 | 4.6167e-05 | 5.4314e-07 | 85
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | NONE | 63 | 2690 | 303944 | 0.055028 | 0.00048701 | 112.9903
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | ARRESTER | 1 | 5 | 315 | 5.703e-05 | 9.0523e-07 | 63
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | NONE | 2 | 5 | 327 | 5.9202e-05 | 9.0523e-07 | 65.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | PEDESTAL | 2 | 5 | 248 | 4.4899e-05 | 9.0523e-07 | 49.6
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 97 | 12020 | 0.0021762 | 1.7561e-05 | 123.9175
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | POLE | 1 | 2 | 420 | 7.6039e-05 | 3.6209e-07 | 210
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | METERING | 5 | 100 | 8018 | 0.0014516 | 1.8105e-05 | 80.18
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 651 | 23259 | 3072157 | 0.55321 | 0.0041883 | 132.0847
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONN/CLAMP | 76 | 208 | 16908 | 0.0030447 | 3.7455e-05 | 81.2885
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | V | NONE | 3 | 2272 | 199318 | 0.035892 | 0.00040912 | 87.728
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | POLE | 5 | 117 | 18486 | 0.0033288 | 2.1068e-05 | 158
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | NONE | 24 | 19464 | 1389271 | 0.25017 | 0.0035049 | 71.3764
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | NONE | 4 | 5 | 544 | 9.7959e-05 | 9.0036e-07 | 108.8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NONE | 334 | 12252 | 1704470 | 0.3057 | 0.0021974 | 139.1177
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 6 | 17 | 749 | 0.00013487 | 3.0612e-06 | 44.0588
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 7 | 806 | 7913 | 0.0014249 | 0.00014514 | 9.8176
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | NONE | 1 | 1 | 146 | 2.6e-05 | 1.7808e-07 | 146
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | POLE | 10 | 580 | 33682 | 0.0059981 | 0.00010329 | 58.0724
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 13 | 150 | 36468 | 0.0064942 | 2.6712e-05 | 243.12
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 1 | 1 | 56 | 9.9725e-06 | 1.7808e-07 | 56
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 3 | 12 | 3609 | 0.00064269 | 2.137e-06 | 300.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 5 | 19 | 802 | 0.00014282 | 3.3835e-06 | 42.2105
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 67 | 1570 | 307056 | 0.05468 | 0.00027959 | 195.5771
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 14 | 144 | 11866 | 0.0021131 | 2.5643e-05 | 82.4028
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | SPLICE, UG | 1 | 107 | 4988 | 0.0008982 | 1.9268e-05 | 46.6168
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 9 | 1099 | 0.00019897 | 1.6294e-06 | 122.1111
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 240 | 5492 | 731874 | 0.13033 | 0.00097801 | 133.2618
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | FUSE | 153 | 846 | 45212 | 0.0080513 | 0.00015066 | 53.4421
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | U | NONE | 6 | 5740 | 253855 | 0.045206 | 0.0010222 | 44.2256
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 1 | 354 | 6.4549e-05 | 1.8234e-07 | 354
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | ARRESTER | 1 | 3 | 141 | 2.571e-05 | 5.4703e-07 | 47
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 8 | 1952 | 0.00035593 | 1.4587e-06 | 244
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | OL | JUMPER/RISER | 1 | 1910 | 91580 | 0.016699 | 0.00034827 | 47.9476
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 3 | 30 | 5.4314e-06 | 5.4314e-07 | 10
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | WI | NONE | 1 | 246 | 10578 | 0.0019288 | 4.4856e-05 | 43
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 1 | 88 | 1.5932e-05 | 1.8105e-07 | 88
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | NETWORK TRANSFORMER | 1 | 7 | 826 | 0.00014954 | 1.2673e-06 | 118
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WU | NONE | 5 | 1539 | 130936 | 0.023578 | 0.00027713 | 85.0786
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 12 | 21 | 1497 | 0.00026659 | 3.7397e-06 | 71.2857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 16 | 239 | 28873 | 0.0051417 | 4.2561e-05 | 120.8075
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | R | BREAKER | 5 | 5897 | 218763 | 0.038957 | 0.0010501 | 37.0973
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | OTHER EQUIPMENT | 1 | 1 | 52 | 9.2601e-06 | 1.7808e-07 | 52
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, UG | 2 | 44 | 8249 | 0.001469 | 7.8355e-06 | 187.4773
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 8 | 111 | 8198 | 0.0014599 | 1.9767e-05 | 73.8559
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 4 | 54 | 6114 | 0.0010888 | 9.6163e-06 | 113.2222
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 4 | 107 | 15083 | 0.002686 | 1.9055e-05 | 140.9626
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | JUMPER/RISER | 6 | 74 | 9848 | 0.0017537 | 1.3178e-05 | 133.0811
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 17 | 135 | 17294 | 0.0030797 | 2.4041e-05 | 128.1037
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 3 | 3 | 143 | 2.5465e-05 | 5.3424e-07 | 47.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 2 | 2 | 255 | 4.541e-05 | 3.5616e-07 | 127.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 6 | 5826 | 0.0010375 | 1.0685e-06 | 971
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | EQF | TRANSFORMER, STATION SERVICE | 3 | 479 | 37841 | 0.0067387 | 8.53e-05 | 79
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CONN/CLAMP | 1 | 9 | 837 | 0.00014905 | 1.6027e-06 | 93
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 8 | 4680 | 0.00083341 | 1.4246e-06 | 585
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | CONDUCTOR UG | 2 | 847 | 71939 | 0.012811 | 0.00015083 | 84.9339
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | POLE | 1 | 12 | 1812 | 0.00032268 | 2.137e-06 | 151
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONN/CLAMP | 1 | 1 | 49 | 8.7259e-06 | 1.7808e-07 | 49
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | BREAKER | 2 | 288 | 45216 | 0.0080521 | 5.1287e-05 | 157
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 1 | 26 | 988 | 0.00017594 | 4.6301e-06 | 38
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | POLE | 1 | 20 | 8520 | 0.0015342 | 3.6014e-06 | 426
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 4 | 19 | 1554 | 0.00027674 | 3.3835e-06 | 81.7895
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ERF | NONE | 6 | 7503 | 61257 | 0.011031 | 0.0013511 | 8.1643
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | FUSE | 1 | 1 | 75 | 1.3505e-05 | 1.8007e-07 | 75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | POLE | 2 | 17 | 1153 | 0.00020679 | 3.049e-06 | 67.8235
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 122 | 2.1881e-05 | 1.7935e-07 | 122
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | V | NONE | 7 | 14 | 1376 | 0.00024504 | 2.4931e-06 | 98.2857
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 2 | 15 | 2718 | 0.00048402 | 2.6712e-06 | 181.2
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | JUMPER/RISER | 5 | 70 | 16097 | 0.0028666 | 1.2466e-05 | 229.9571
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | CUTOUT | 1 | 30 | 7560 | 0.0013463 | 5.3424e-06 | 252
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OU | FUSE | 2 | 35 | 1960 | 0.00034904 | 6.2328e-06 | 56
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | CUTOUT | 1 | 1 | 161 | 2.8671e-05 | 1.7808e-07 | 161
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | NONE | 2 | 24 | 5175 | 0.00092156 | 4.2739e-06 | 215.625
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 7 | 132 | 25129 | 0.004475 | 2.3507e-05 | 190.3712
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | RECLOSER, LINE/OCR/BR | 1 | 832 | 49088 | 0.0087416 | 0.00014816 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | SWITCH, OH | 2 | 1227 | 14724 | 0.002622 | 0.0002185 | 12
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 74 | 5402 | 0.00096199 | 1.3178e-05 | 73
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | AO | NONE | 2 | 563 | 30812 | 0.005487 | 0.00010026 | 54.7282
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | FW | CROSSARM | 2 | 525 | 8925 | 0.0016274 | 9.573e-05 | 17
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | ABI | NONE | 1 | 1916 | 30656 | 0.0055203 | 0.00034502 | 16
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | NONE | 2 | 29 | 4466 | 0.00081434 | 5.2879e-06 | 154
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CROSSARM | 4 | 459 | 141154 | 0.025738 | 8.3695e-05 | 307.5251
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONN/CLAMP | 2 | 673 | 38398 | 0.0070016 | 0.00012272 | 57.055
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | JUMPER/RISER | 4 | 4 | 241 | 4.3944e-05 | 7.2937e-07 | 60.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 1 | 179 | 3.2639e-05 | 1.8234e-07 | 179
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CUTOUT | 3 | 4 | 187 | 3.4098e-05 | 7.2937e-07 | 46.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OU | POLE | 1 | 3 | 132 | 2.4069e-05 | 5.4703e-07 | 44
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | CROSSARM | 1 | 6 | 90 | 1.6411e-05 | 1.0941e-06 | 15
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 1 | 45 | 8.2054e-06 | 1.8234e-07 | 45
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 4 | 56 | 9701 | 0.0017689 | 1.0211e-05 | 173.2321
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 3073 | 216875 | 0.039545 | 0.00056034 | 70.5744
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CAPACITOR | 2 | 242 | 6411 | 0.001169 | 4.4127e-05 | 26.4917
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WL | NONE | 2 | 401 | 54268 | 0.0098953 | 7.3119e-05 | 135.3317
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | FUSE | 1 | 14 | 3136 | 0.00057182 | 2.5528e-06 | 224
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 8 | 58 | 16952 | 0.0030403 | 1.0402e-05 | 292.2759
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 30 | 2870 | 302735 | 0.054296 | 0.00051474 | 105.4826
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 11 | 2151 | 0.00038578 | 1.9729e-06 | 195.5455
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 31 | 3360 | 783187 | 0.14046 | 0.00060262 | 233.0914
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | FUSE | 13 | 79 | 22633 | 0.0040592 | 1.4169e-05 | 286.4937
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 4 | 4 | 889 | 0.00015944 | 7.174e-07 | 222.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 8 | 1344 | 0.00024105 | 1.4348e-06 | 168
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | TRANSFORMER, OH | 5 | 17 | 502 | 9.0034e-05 | 3.049e-06 | 29.5294
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | OTHER EQUIPMENT | 1 | 522 | 8352 | 0.001504 | 9.3998e-05 | 16
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | FUSE | 3 | 21 | 1408 | 0.00025074 | 3.7397e-06 | 67.0476
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 29 | 4067 | 290435 | 0.051721 | 0.00072425 | 71.4126
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | JUMPER/RISER | 3 | 138 | 3331 | 0.00059742 | 2.475e-05 | 24.1377
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | NONE | 7 | 52 | 2662 | 0.00048539 | 9.4818e-06 | 51.1923
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 28 | 3878 | 0.00070712 | 5.1056e-06 | 138.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CUTOUT | 1 | 1 | 78 | 1.3989e-05 | 1.7935e-07 | 78
AEP Total | 2023 | 5575683 | PARTIAL POWER | FW | NONE | 1 | 1 | 229 | 4.1071e-05 | 1.7935e-07 | 229
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 4 | 260 | 4.6631e-05 | 7.174e-07 | 65
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | SWITCH, OH | 2 | 2413 | 116106 | 0.020676 | 0.00042971 | 48.1169
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 2 | 31 | 6310 | 0.0011237 | 5.5205e-06 | 203.5484
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | NONE | 9 | 2080 | 90200 | 0.016063 | 0.00037041 | 43.3654
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 2 | 2 | 109 | 1.9628e-05 | 3.6014e-07 | 54.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | NONE | 3 | 156 | 13968 | 0.0025152 | 2.8091e-05 | 89.5385
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | FUSE | 1 | 7 | 322 | 5.7342e-05 | 1.2466e-06 | 46
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | OU | NONE | 5 | 8859 | 371439 | 0.066146 | 0.0015776 | 41.9279
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | CUTOUT | 3 | 14 | 1231 | 0.00021922 | 2.4931e-06 | 87.9286
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 5 | 52 | 9135 | 0.0016268 | 9.2601e-06 | 175.6731
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | FUSE | 1 | 7 | 336 | 5.9835e-05 | 1.2466e-06 | 48
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 2 | 10 | 2612 | 0.00046514 | 1.7808e-06 | 261.2
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | OU | NONE | 5 | 1990 | 194063 | 0.034559 | 0.00035438 | 97.5191
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 163 | 12877 | 0.0022931 | 2.9027e-05 | 79
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | FUSE | 2 | 11 | 560 | 9.9725e-05 | 1.9589e-06 | 50.9091
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | NONE | 4 | 5 | 293 | 5.2177e-05 | 8.904e-07 | 58.6
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | GUY/ANCHOR | 2 | 10 | 316 | 5.6273e-05 | 1.7808e-06 | 31.6
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | ERF | NONE | 1 | 205 | 10660 | 0.00193 | 3.7115e-05 | 52
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | WU | NONE | 9 | 4215 | 498928 | 0.090976 | 0.00076857 | 118.3696
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | CONN/CLAMP | 1 | 2 | 246 | 4.4856e-05 | 3.6468e-07 | 123
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | TRANSFORMER, OH | 1 | 1 | 78 | 1.4223e-05 | 1.8234e-07 | 78
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | METERING | 2 | 2 | 102 | 1.8599e-05 | 3.6468e-07 | 51
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | POLE | 1 | 16 | 4025 | 0.00072871 | 2.8967e-06 | 251.5625
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | CROSSARM | 1 | 16 | 1667 | 0.0003018 | 2.8967e-06 | 104.1875
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | RECLOSER, LINE/OCR/BR | 4 | 1501 | 193941 | 0.035364 | 0.0002737 | 129.2079
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 3 | 1326 | 0.00023878 | 5.4022e-07 | 442
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | OTHER EQUIPMENT | 1 | 1 | 82 | 1.4766e-05 | 1.8007e-07 | 82
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 9 | 2742 | 0.00049376 | 1.6206e-06 | 304.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 3 | 35 | 1382 | 0.00024886 | 6.3025e-06 | 39.4857
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | V | NONE | 3 | 4609 | 153208 | 0.027283 | 0.00082077 | 33.2411
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 3 | 2025 | 0.00036061 | 5.3424e-07 | 675
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 2 | 594 | 0.00010578 | 3.5616e-07 | 297
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, GROUNDING | 2 | 6 | 742 | 0.00013214 | 1.0685e-06 | 123.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 124 | 26846 | 0.0047807 | 2.2082e-05 | 216.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | FW | CONN/CLAMP | 1 | 1 | 43 | 7.6574e-06 | 1.7808e-07 | 43
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | FUSE | 5 | 59 | 3398 | 0.0006196 | 1.0758e-05 | 57.5932
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 3 | 271 | 4.9415e-05 | 5.4703e-07 | 90.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 1 | 38 | 6.929e-06 | 1.8234e-07 | 38
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 19 | 32 | 2212 | 0.00039832 | 5.7623e-06 | 69.125
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | NONE | 34 | 168 | 12887 | 0.0023206 | 3.0252e-05 | 76.7083
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | NONE | 312 | 10838 | 555953 | 0.10011 | 0.0019516 | 51.2966
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | ARRESTER | 50 | 5177 | 561879 | 0.10118 | 0.00093223 | 108.5337
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | ARRESTER | 2 | 5 | 388 | 6.9868e-05 | 9.0036e-07 | 77.6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | ARRESTER | 181 | 7599 | 715854 | 0.12891 | 0.0013684 | 94.2037
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | JUMPER/RISER | 26 | 2196 | 142549 | 0.025669 | 0.00039544 | 64.913
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR UG | 41 | 48 | 4840 | 0.00087155 | 8.6435e-06 | 100.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | FUSE | 397 | 2585 | 157034 | 0.028164 | 0.00046362 | 60.7482
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | NONE | 1971 | 43108 | 6281655 | 1.1266 | 0.0077314 | 145.719
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 22 | 128 | 22103 | 0.0039642 | 2.2957e-05 | 172.6797
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | FUSE | 7 | 23 | 3206 | 0.00057731 | 4.1417e-06 | 139.3913
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 45 | 69 | 5039 | 0.00090738 | 1.2425e-05 | 73.029
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 22 | 4221 | 117495 | 0.021158 | 0.00076008 | 27.8358
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | OU | POLE | 2 | 605 | 443976 | 0.079627 | 0.00010851 | 733.8446
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 4 | 312 | 5.6182e-05 | 7.2029e-07 | 78
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | FUSE | 4 | 30 | 1785 | 0.00032143 | 5.4022e-06 | 59.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | METERING | 59 | 87 | 7083 | 0.0012703 | 1.5603e-05 | 81.4138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | METERING | 12 | 24 | 1363 | 0.00024544 | 4.3217e-06 | 56.7917
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | NONE | 7 | 192 | 35430 | 0.0063799 | 3.4574e-05 | 184.5312
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | FUSE | 5 | 45 | 2767 | 0.00049826 | 8.1032e-06 | 61.4889
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | FUSE | 7 | 43 | 6722 | 0.0012056 | 7.7121e-06 | 156.3256
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | FUSE | 4 | 9 | 493 | 8.842e-05 | 1.6142e-06 | 54.7778
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | FUSE | 4 | 527 | 6093 | 0.0010972 | 9.4898e-05 | 11.5617
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 569 | 75108 | 0.013525 | 0.00010246 | 132
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | OU | NONE | 9 | 5726 | 274637 | 0.049256 | 0.001027 | 47.9632
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CUTOUT | 8 | 28 | 5842 | 0.0010478 | 5.0218e-06 | 208.6429
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CROSSARM | 9 | 1570 | 191220 | 0.034295 | 0.00028158 | 121.7962
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 10 | 1472 | 152579 | 0.027365 | 0.000264 | 103.6542
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE HARDWARE | 2 | 312 | 96492 | 0.017375 | 5.6182e-05 | 309.2692
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 6 | 1554 | 0.00027871 | 1.0761e-06 | 259
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | TRANSFORMER, UG | 3 | 22 | 795 | 0.00014258 | 3.9457e-06 | 36.1364
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 1 | 10 | 4930 | 0.00087793 | 1.7808e-06 | 493
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | NONE | 3690 | 34910 | 2055911 | 0.36612 | 0.0062168 | 58.8918
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WL | CONDUCTOR UG | 1 | 90 | 53460 | 0.0095881 | 1.6142e-05 | 594
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 1 | 100 | 1.7935e-05 | 1.7935e-07 | 100
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 4 | 257 | 4.6093e-05 | 7.174e-07 | 64.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | NONE | 4 | 24 | 5123 | 0.0009123 | 4.2739e-06 | 213.4583
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 7 | 146 | 11701 | 0.0020837 | 2.6e-05 | 80.1438
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | SPLICE, UG | 1 | 1 | 452 | 8.2419e-05 | 1.8234e-07 | 452
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | ERF | CONDUCTOR OVERHEAD | 1 | 460 | 8740 | 0.0015937 | 8.3877e-05 | 19
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | NONE | 18 | 2952 | 333672 | 0.060842 | 0.00053827 | 113.0325
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | NONE | 2 | 2 | 262 | 4.7774e-05 | 3.6468e-07 | 131
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 3 | 525 | 9.573e-05 | 5.4703e-07 | 175
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | NONE | 31 | 3377 | 279950 | 0.050411 | 0.0006081 | 82.899
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | CROSSARM | 4 | 1099 | 74220 | 0.013365 | 0.0001979 | 67.5341
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 17 | 118 | 18042 | 0.0032489 | 2.1248e-05 | 152.8983
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | JUMPER/RISER | 9 | 125 | 44136 | 0.0079477 | 2.2509e-05 | 353.088
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CUTOUT | 11 | 44 | 3507 | 0.00062898 | 7.8914e-06 | 79.7045
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 169 | 6326 | 559022 | 0.10026 | 0.0011346 | 88.369
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | NONE | 5 | 19 | 786 | 0.00014154 | 3.4214e-06 | 41.3684
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | POLE | 3 | 2697 | 490338 | 0.087942 | 0.00048371 | 181.8087
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CROSSARM | 8 | 607 | 243007 | 0.043759 | 0.0001093 | 400.341
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 9 | 54 | 9.7239e-06 | 1.6206e-06 | 6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 1506 | 82351 | 0.01477 | 0.0002701 | 54.6819
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 771 | 43947 | 0.0079136 | 0.00013884 | 57
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | CONDUCTOR UG | 1 | 4 | 484 | 8.7155e-05 | 7.2029e-07 | 121
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CROSSARM | 9 | 676 | 202893 | 0.036389 | 0.00012124 | 300.1376
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 3 | 9 | 2730 | 0.0004916 | 1.6206e-06 | 303.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | V | CONDUCTOR OVERHEAD | 4 | 9 | 435 | 7.8331e-05 | 1.6206e-06 | 48.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 11 | 677 | 0.00012345 | 2.0058e-06 | 61.5455
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 8 | 1664 | 0.00029632 | 1.4246e-06 | 208
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | O | TRANSFORMER, POWER - NON LTC | 1 | 256 | 122624 | 0.021837 | 4.5588e-05 | 479
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 1 | 100 | 1.7808e-05 | 1.7808e-07 | 100
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | FUSE | 1 | 49 | 6174 | 0.0010995 | 8.7259e-06 | 126
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | FW | NONE | 1 | 146 | 2774 | 0.00050222 | 2.6433e-05 | 19
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | METERING | 1 | 1 | 53 | 9.5955e-06 | 1.8105e-07 | 53
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | BE | NONE | 1 | 44 | 1540 | 0.00027881 | 7.966e-06 | 35
AEP Total | 2020 | 5484199 | PARTIAL POWER | V | CONN/CLAMP | 1 | 1 | 36 | 6.5643e-06 | 1.8234e-07 | 36
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | ARRESTER | 1 | 1 | 149 | 2.6831e-05 | 1.8007e-07 | 149
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | WL | NONE | 1 | 499 | 52395 | 0.0095538 | 9.0989e-05 | 105
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | BREAKER | 1 | 276 | 61795 | 0.011268 | 5.0326e-05 | 223.8949
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | UB | NONE | 2 | 31 | 317 | 5.6854e-05 | 5.5599e-06 | 10.2258
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | SPLICE, OH | 1 | 2 | 24 | 4.3044e-06 | 3.587e-07 | 12
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 854 | 36724 | 0.006613 | 0.00015378 | 43.0023
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WL | ARRESTER | 1 | 800 | 89485 | 0.016049 | 0.00014348 | 111.8563
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | WL | NONE | 4 | 3492 | 58147 | 0.010429 | 0.00062629 | 16.6515
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 2 | 14 | 2.4931e-06 | 3.5616e-07 | 7
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 2 | 16 | 5052 | 0.00089966 | 2.8493e-06 | 315.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 28 | 5036 | 0.00089681 | 4.9862e-06 | 179.8571
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | POLE | 10 | 592 | 86832 | 0.015463 | 0.00010542 | 146.6757
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 4 | 63 | 12314 | 0.0021929 | 1.1219e-05 | 195.4603
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | CONDUCTOR UG | 2 | 3 | 290 | 5.1643e-05 | 5.3424e-07 | 96.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | NONE | 2 | 1379 | 341951 | 0.060895 | 0.00024557 | 247.9703
AEP Total | 2025 | 5615460 | PARTIAL POWER | ABI | NONE | 1 | 1 | 53 | 9.4382e-06 | 1.7808e-07 | 53
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 3 | 231 | 4.1136e-05 | 5.3424e-07 | 77
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FW | ARRESTER | 1 | 29 | 406 | 7.23e-05 | 5.1643e-06 | 14
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 4 | 583 | 0.00010382 | 7.1232e-07 | 145.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | NONE | 3 | 52 | 1878 | 0.00033443 | 9.2601e-06 | 36.1154
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | WU | NONE | 2 | 2533 | 443275 | 0.080828 | 0.00046187 | 175
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 53 | 12561 | 0.0022528 | 9.5056e-06 | 237
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 9 | 1314 | 0.00023789 | 1.6294e-06 | 146
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | R | BREAKER | 1 | 587 | 75723 | 0.013636 | 0.0001057 | 129
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SPLICE, UG | 1 | 9 | 237 | 4.2677e-05 | 1.6206e-06 | 26.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | NONE | 31 | 109 | 11248 | 0.0020364 | 1.9734e-05 | 103.1927
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 30 | 3610 | 599446 | 0.10853 | 0.00065358 | 166.0515
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONN/CLAMP | 101 | 191 | 11953 | 0.002164 | 3.458e-05 | 62.5812
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | NONE | 5 | 2718 | 695009 | 0.12583 | 0.00049208 | 255.706
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CROSSARM | 153 | 19094 | 2537491 | 0.4594 | 0.0034569 | 132.8947
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | NONE | 10 | 2534 | 71717 | 0.012984 | 0.00045877 | 28.3019
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CROSSARM | 7 | 187 | 36816 | 0.0066654 | 3.3856e-05 | 196.877
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | JUMPER/RISER | 15 | 64 | 11356 | 0.002056 | 1.1587e-05 | 177.4375
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, OH | 6 | 13 | 2676 | 0.00048448 | 2.3536e-06 | 205.8462
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WL | NONE | 5 | 15 | 2194 | 0.00039722 | 2.7157e-06 | 146.2667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 15 | 1312 | 0.00023753 | 2.7157e-06 | 87.4667
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | NONE | 7 | 15 | 903 | 0.00016348 | 2.7157e-06 | 60.2
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 2 | 230 | 4.1641e-05 | 3.6209e-07 | 115
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WI | NONE | 9 | 8189 | 1633280 | 0.2957 | 0.0014826 | 199.448
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 10 | 1340 | 0.0002426 | 1.8105e-06 | 134
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | FW | POLE | 3 | 528 | 110398 | 0.019987 | 9.5592e-05 | 209.0871
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 1 | 48 | 3552 | 0.00064308 | 8.6902e-06 | 74
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | CONDUCTOR OVERHEAD | 5 | 700 | 220292 | 0.039883 | 0.00012673 | 314.7029
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | POLE | 2 | 68 | 7704 | 0.0013948 | 1.2311e-05 | 113.2941
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CUTOUT | 3 | 81 | 11926 | 0.0021592 | 1.4665e-05 | 147.2346
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 1 | 58 | 1.0501e-05 | 1.8105e-07 | 58
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 89 | 6675 | 0.0012085 | 1.6113e-05 | 75
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | EQF | SWITCH, OH | 3 | 2166 | 1647389 | 0.29825 | 0.00039215 | 760.5674
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 2 | 22 | 3984 | 0.00072129 | 3.983e-06 | 181.0909
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | METERING | 1 | 1 | 154 | 2.7881e-05 | 1.8105e-07 | 154
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | ARRESTER | 46 | 789 | 84122 | 0.015339 | 0.00014387 | 106.6185
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | NONE | 14 | 38 | 2282 | 0.0004161 | 6.929e-06 | 60.0526
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 25 | 54 | 4182 | 0.00076255 | 9.8465e-06 | 77.4444
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 104 | 226 | 29458 | 0.0053714 | 4.1209e-05 | 130.3451
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | NONE | 39 | 885 | 43820 | 0.0079902 | 0.00016137 | 49.5141
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CE | NONE | 37 | 203 | 11607 | 0.0021164 | 3.7015e-05 | 57.1773
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | R | NONE | 5 | 3879 | 158452 | 0.028687 | 0.00070228 | 40.8487
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | WL | NONE | 12 | 66 | 7628 | 0.001381 | 1.1949e-05 | 115.5758
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | U | NONE | 40 | 20874 | 2800662 | 0.50705 | 0.0037792 | 134.1699
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 14 | 42 | 7664 | 0.0013875 | 7.6039e-06 | 182.4762
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CUTOUT | 2 | 5 | 257 | 4.6529e-05 | 9.0523e-07 | 51.4
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WU | NONE | 3 | 36 | 360 | 6.5177e-05 | 6.5177e-06 | 10
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | NONE | 7 | 2792 | 99460 | 0.018007 | 0.00050548 | 35.6232
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 3099 | 257991 | 0.046708 | 0.00056106 | 83.2498
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CROSSARM | 2 | 116 | 54644 | 0.0098931 | 2.1001e-05 | 471.069
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 2 | 15 | 3042 | 0.00055074 | 2.7157e-06 | 202.8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | FUSE | 203 | 2319 | 211311 | 0.038051 | 0.00041759 | 91.1216
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 3 | 8 | 770 | 0.00013941 | 1.4484e-06 | 96.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | SWITCH, UG | 1 | 345 | 5175 | 0.00093691 | 6.2461e-05 | 15
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CUTOUT | 1 | 1 | 97 | 1.7561e-05 | 1.8105e-07 | 97
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RELAY | 2 | 834 | 5004 | 0.00090596 | 0.00015099 | 6
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 21 | 3422 | 0.00061954 | 3.802e-06 | 162.9524
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 2 | 351 | 6.3547e-05 | 3.6209e-07 | 175.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR UG | 3 | 8 | 515 | 9.3239e-05 | 1.4484e-06 | 64.375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 2 | 306 | 5.54e-05 | 3.6209e-07 | 153
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | NONE | 210 | 2496 | 118426 | 0.021594 | 0.00045513 | 47.4463
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 397 | 5413 | 815222 | 0.14865 | 0.00098702 | 150.6045
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | POLE | 38 | 264 | 38353 | 0.0069934 | 4.8138e-05 | 145.2765
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | TRANSFORMER, OH | 3 | 4 | 783 | 0.00014277 | 7.2937e-07 | 195.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 4 | 27 | 4045 | 0.00073757 | 4.9232e-06 | 149.8148
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | METERING | 4 | 4 | 477 | 8.6977e-05 | 7.2937e-07 | 119.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 6 | 1430 | 0.00026075 | 1.0941e-06 | 238.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE | 6 | 288 | 58019 | 0.010579 | 5.2515e-05 | 201.4549
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | TRANSFORMER, UG | 1 | 2 | 536 | 9.7735e-05 | 3.6468e-07 | 268
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | PEDESTAL | 2 | 10 | 564 | 0.00010284 | 1.8234e-06 | 56.4
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | METERING | 4 | 4 | 192 | 3.501e-05 | 7.2937e-07 | 48
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 2 | 8 | 539 | 9.7059e-05 | 1.4406e-06 | 67.375
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | NONE | 55 | 17924 | 417323 | 0.075148 | 0.0032276 | 23.2829
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 3 | 3 | 167 | 3.0072e-05 | 5.4022e-07 | 55.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ERF | RELAY | 2 | 2736 | 49248 | 0.0088682 | 0.00049268 | 18
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 13 | 559 | 0.0001012 | 2.3536e-06 | 43
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CROSSARM | 4 | 122 | 6168 | 0.0011247 | 2.2246e-05 | 50.5574
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 1 | 88 | 1.6046e-05 | 1.8234e-07 | 88
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | FO | NONE | 3 | 2331 | 144522 | 0.026352 | 0.00042504 | 62
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 146 | 2.6622e-05 | 1.8234e-07 | 146
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | POLE | 5 | 15 | 2242 | 0.00040881 | 2.7351e-06 | 149.4667
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | PEDESTAL | 1 | 2 | 140 | 2.5528e-05 | 3.6468e-07 | 70
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 3 | 2571 | 394679 | 0.071967 | 0.0004688 | 153.5119
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 643 | 48947 | 0.0087165 | 0.00011451 | 76.1229
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | FUSE | 11 | 17 | 1003 | 0.00017861 | 3.0274e-06 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 10 | 27 | 1711 | 0.00030469 | 4.8082e-06 | 63.3704
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | INSULATOR | 6 | 3334 | 289983 | 0.05164 | 0.00059372 | 86.9775
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | NONE | 4 | 17 | 2214 | 0.00039427 | 3.0274e-06 | 130.2353
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | METERING | 1 | 1 | 39 | 6.9451e-06 | 1.7808e-07 | 39
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 4 | 723 | 0.00012875 | 7.1232e-07 | 180.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 3 | 6 | 451 | 8.0314e-05 | 1.0685e-06 | 75.1667
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | ARRESTER | 1 | 1 | 126 | 2.2438e-05 | 1.7808e-07 | 126
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | F | CONDUCTOR OVERHEAD | 4 | 23 | 3171 | 0.00056469 | 4.0958e-06 | 137.8696
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | INSULATOR | 2 | 20 | 715 | 0.00012733 | 3.5616e-06 | 35.75
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | FUSE | 8 | 9 | 451 | 8.0314e-05 | 1.6027e-06 | 50.1111
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | CONN/CLAMP | 1 | 19 | 1254 | 0.00022331 | 3.3835e-06 | 66
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 2 | 2 | 505 | 8.993e-05 | 3.5616e-07 | 252.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 40 | 13316 | 0.0023713 | 7.1232e-06 | 332.9
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | EQF | CROSSARM | 9 | 1557 | 120954 | 0.021539 | 0.00027727 | 77.684
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | INSULATOR | 2 | 191 | 25441 | 0.0045628 | 3.4256e-05 | 133.199
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | CONN/CLAMP | 4 | 4 | 381 | 6.7848e-05 | 7.1232e-07 | 95.25
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | WI | NONE | 2 | 1080 | 104760 | 0.018656 | 0.00019233 | 97
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WL | FUSE | 1 | 563 | 156783 | 0.02792 | 0.00010026 | 278.4778
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 390 | 6.9451e-05 | 1.7808e-07 | 390
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | V | NONE | 1 | 827 | 16540 | 0.0029454 | 0.00014727 | 20
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | A | NONE | 8 | 909 | 88568 | 0.01615 | 0.00016575 | 97.4345
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 4 | 252 | 4.595e-05 | 7.2937e-07 | 63
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | NONE | 6 | 12 | 826 | 0.00014874 | 2.1609e-06 | 68.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 34 | 671 | 117524 | 0.021078 | 0.00012034 | 175.1475
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONN/CLAMP | 2 | 10 | 235 | 4.2317e-05 | 1.8007e-06 | 23.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 10 | 58 | 6358 | 0.0011449 | 1.0444e-05 | 109.6207
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | JUMPER/RISER | 4 | 4 | 464 | 8.3553e-05 | 7.2029e-07 | 116
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONN/CLAMP | 1 | 1 | 100 | 1.8007e-05 | 1.8007e-07 | 100
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONN/CLAMP | 3 | 329 | 43536 | 0.0078082 | 5.9006e-05 | 132.3283
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | NONE | 284 | 2963 | 265431 | 0.047605 | 0.00053141 | 89.5818
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE | 12 | 956 | 176332 | 0.031625 | 0.00017146 | 184.4477
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | NONE | 5 | 75 | 9691 | 0.0017451 | 1.3505e-05 | 129.2133
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | ARRESTER | 45 | 1294 | 161270 | 0.028924 | 0.00023208 | 124.6291
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 56 | 6274 | 0.0011298 | 1.0084e-05 | 112.0357
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | PEDESTAL | 1 | 7 | 1512 | 0.00027118 | 1.2555e-06 | 216
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 279 | 29450 | 0.0052819 | 5.0039e-05 | 105.5556
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 7 | 415 | 40681 | 0.0072961 | 7.443e-05 | 98.0265
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 6 | 7 | 601 | 0.00010779 | 1.2555e-06 | 85.8571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CUTOUT | 4 | 88 | 6028 | 0.0010855 | 1.5846e-05 | 68.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CE | ARRESTER | 1 | 44 | 3124 | 0.00056029 | 7.8914e-06 | 71
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 509 | 21422 | 2950362 | 0.5254 | 0.0038148 | 137.7258
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | METERING | 6 | 66 | 3778 | 0.00067279 | 1.1753e-05 | 57.2424
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | U | NONE | 6 | 2009 | 173675 | 0.030928 | 0.00035776 | 86.4485
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | NONE | 39 | 1278 | 179953 | 0.032046 | 0.00022759 | 140.8083
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 350 | 3539 | 228132 | 0.040626 | 0.00063022 | 64.4623
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 5 | 251 | 47656 | 0.0084866 | 4.4698e-05 | 189.8645
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 62 | 220 | 12589 | 0.0022418 | 3.9178e-05 | 57.2227
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 39 | 3931 | 0.00070503 | 6.9947e-06 | 100.7949
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 9 | 1540 | 0.0002762 | 1.6142e-06 | 171.1111
AEP Total | 2023 | 5575683 | PARTIAL POWER | CE | CONN/CLAMP | 1 | 5 | 290 | 5.2012e-05 | 8.9675e-07 | 58
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 2 | 163 | 2.9234e-05 | 3.587e-07 | 81.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 281 | 55937 | 0.0099612 | 5.004e-05 | 199.0641
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | WL | NONE | 1 | 871 | 215137 | 0.038312 | 0.00015511 | 247
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 811 | 50282 | 0.0090181 | 0.00014545 | 62
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | FUSE | 2 | 18 | 1833 | 0.00032642 | 3.2054e-06 | 101.8333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | NONE | 9 | 615 | 54435 | 0.0096938 | 0.00010952 | 88.5122
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | FUSE | 2 | 37 | 1396 | 0.00025037 | 6.636e-06 | 37.7297
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 1 | 99 | 1.7924e-05 | 1.8105e-07 | 99
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 6 | 206 | 20574 | 0.0037048 | 3.7095e-05 | 99.8738
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WU | POLE | 1 | 114 | 7068 | 0.0012727 | 2.0528e-05 | 62
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | NETWORK TRANSFORMER | 1 | 4 | 116 | 2.1001e-05 | 7.2419e-07 | 29
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | POLE | 2 | 1311 | 67801 | 0.012209 | 0.00023607 | 51.717
AEP Total | 2022 | 5553337 | PARTIAL POWER | OU | METERING | 1 | 1 | 109 | 1.9628e-05 | 1.8007e-07 | 109
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | CONDUCTOR UG | 1 | 1 | 59 | 1.0682e-05 | 1.8105e-07 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 98 | 5418 | 478670 | 0.085241 | 0.00096484 | 88.3481
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CE | NONE | 5 | 16 | 682 | 0.00012145 | 2.8493e-06 | 42.625
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 4 | 303 | 5.3958e-05 | 7.1232e-07 | 75.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 6 | 60 | 12241 | 0.0021799 | 1.0685e-05 | 204.0167
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 3 | 3 | 222 | 3.9816e-05 | 5.3805e-07 | 74
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 4 | 249 | 4.4658e-05 | 7.174e-07 | 62.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 5 | 165 | 2.9383e-05 | 8.904e-07 | 33
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 1 | 16 | 5889 | 0.0010562 | 2.8696e-06 | 368.0625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 43 | 12206 | 0.0022257 | 7.8407e-06 | 283.8605
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CROSSARM | 1 | 1 | 366 | 6.5906e-05 | 1.8007e-07 | 366
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | NONE | 262 | 19572 | 1251155 | 0.22652 | 0.0035434 | 63.9258
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | FUSE | 205 | 2135 | 148804 | 0.02694 | 0.00038653 | 69.6974
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 38 | 9362 | 1164435 | 0.21082 | 0.001695 | 124.3789
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 43 | 51 | 12865 | 0.0023292 | 9.2334e-06 | 252.2549
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | U | NONE | 10 | 9769 | 450990 | 0.08165 | 0.0017686 | 46.1654
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | F | POLE | 7 | 167 | 28164 | 0.005099 | 3.0235e-05 | 168.6467
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | POLE HARDWARE | 1 | 180 | 35504 | 0.0064279 | 3.2588e-05 | 197.2444
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | ARRESTER | 24 | 204 | 12573 | 0.0022763 | 3.6933e-05 | 61.6324
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 26 | 2636 | 299322 | 0.054191 | 0.00047724 | 113.5516
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | NONE | 112 | 6932 | 1203074 | 0.21781 | 0.001255 | 173.5537
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | BREAKER | 1 | 43 | 4644 | 0.000827 | 7.6574e-06 | 108
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONN/CLAMP | 1 | 1 | 87 | 1.5493e-05 | 1.7808e-07 | 87
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 24 | 1268 | 0.00022833 | 4.3217e-06 | 52.8333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | TRANSFORMER, OH | 1 | 3 | 372 | 6.7831e-05 | 5.4703e-07 | 124
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | SWITCH, OH | 1 | 180 | 6048 | 0.0010891 | 3.2413e-05 | 33.6
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | RELAY | 7 | 9679 | 269819 | 0.048587 | 0.0017429 | 27.8767
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 1 | 583 | 81037 | 0.014592 | 0.00010498 | 139
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | FW | CUTOUT | 1 | 3 | 165 | 2.9712e-05 | 5.4022e-07 | 55
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 2 | 1748 | 0.00031477 | 3.6014e-07 | 874
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONN/CLAMP | 1 | 1 | 34 | 6.0979e-06 | 1.7935e-07 | 34
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | CONDUCTOR UG | 1 | 1 | 97 | 1.7467e-05 | 1.8007e-07 | 97
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 1 | 70 | 1.2605e-05 | 1.8007e-07 | 70
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | POLE HARDWARE | 1 | 1 | 24 | 4.3044e-06 | 1.7935e-07 | 24
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | NONE | 2 | 3 | 142 | 2.5287e-05 | 5.3424e-07 | 47.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 10 | 4100 | 0.00073829 | 1.8007e-06 | 410
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | NONE | 1 | 4 | 440 | 7.9232e-05 | 7.2029e-07 | 110
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WL | CUTOUT | 1 | 1 | 33 | 5.9424e-06 | 1.8007e-07 | 33
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 111 | 1.9767e-05 | 1.7808e-07 | 111
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | POLE HARDWARE | 1 | 28 | 7756 | 0.0013812 | 4.9862e-06 | 277
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 72 | 1.2822e-05 | 1.7808e-07 | 72
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONN/CLAMP | 1 | 1 | 121 | 2.1701e-05 | 1.7935e-07 | 121
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONN/CLAMP | 1 | 8 | 72 | 1.3129e-05 | 1.4587e-06 | 9
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | FW | BREAKER | 1 | 671 | 61732 | 0.011256 | 0.00012235 | 92
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | TIR | FUSE | 1 | 6 | 870 | 0.00015666 | 1.0804e-06 | 145
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | R | NONE | 5 | 5859 | 52867 | 0.0094145 | 0.0010434 | 9.0232
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 2 | 139 | 20989 | 0.0037377 | 2.4753e-05 | 151
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 1 | 3 | 507 | 9.1791e-05 | 5.4314e-07 | 169
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | F | POLE | 1 | 240 | 47040 | 0.0085164 | 4.3451e-05 | 196
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 32 | 3568 | 0.00064597 | 5.7935e-06 | 111.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | V | TRANSFORMER, OH | 1 | 4 | 388 | 7.0246e-05 | 7.2419e-07 | 97
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WL | FUSE | 2 | 2 | 479 | 8.6721e-05 | 3.6209e-07 | 239.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 2 | 163 | 2.9511e-05 | 3.6209e-07 | 81.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 38 | 6319 | 0.001144 | 6.8798e-06 | 166.2895
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | NONE | 324 | 11595 | 1129570 | 0.2034 | 0.0020879 | 97.4187
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 377 | 5213 | 368532 | 0.066362 | 0.00093871 | 70.6948
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 36 | 4959 | 468396 | 0.084345 | 0.00089298 | 94.4537
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | FUSE | 106 | 1231 | 102793 | 0.01851 | 0.00022167 | 83.5037
AEP Total | 2022 | 5553337 | PARTIAL POWER | CE | FUSE | 1 | 2 | 120 | 2.1609e-05 | 3.6014e-07 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, UG | 4 | 1480 | 99474 | 0.017912 | 0.00026651 | 67.2122
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 9 | 43 | 6151 | 0.0011076 | 7.7431e-06 | 143.0465
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | NONE | 11 | 24 | 1107 | 0.00019934 | 4.3217e-06 | 46.125
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | NETWORK PROTECTOR | 1 | 2 | 60 | 1.0804e-05 | 3.6014e-07 | 30
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONN/CLAMP | 366 | 646 | 53834 | 0.0096551 | 0.00011586 | 83.3344
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | NONE | 285 | 19222 | 4523004 | 0.8112 | 0.0034475 | 235.3035
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 45 | 87 | 14827 | 0.0026592 | 1.5603e-05 | 170.4253
AEP Total | 2021 | 5523447 | TRANSMISSION LINE | WL | NONE | 18 | 8128 | 759801 | 0.13756 | 0.0014715 | 93.4795
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 4 | 4 | 210 | 3.802e-05 | 7.2419e-07 | 52.5
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABI | MOAB | 4 | 1533 | 22995 | 0.0041632 | 0.00027754 | 15
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 88 | 10317 | 0.0018679 | 1.5932e-05 | 117.2386
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | NONE | 2 | 2 | 51 | 9.2334e-06 | 3.6209e-07 | 25.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 197 | 1528 | 399944 | 0.072927 | 0.00027862 | 261.7435
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | FUSE | 113 | 1638 | 102724 | 0.018731 | 0.00029868 | 62.7131
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONN/CLAMP | 90 | 159 | 12317 | 0.0022459 | 2.8992e-05 | 77.4654
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | FUSE | 180 | 989 | 50480 | 0.0092046 | 0.00018034 | 51.0415
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CUTOUT | 24 | 2313 | 354754 | 0.064687 | 0.00042176 | 153.374
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | NONE | 256 | 927 | 59968 | 0.010935 | 0.00016903 | 64.6904
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | TRANSFORMER, UG | 1 | 29 | 4958 | 0.00090405 | 5.2879e-06 | 170.9655
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 37 | 199 | 34105 | 0.0062188 | 3.6286e-05 | 171.3819
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 2 | 232 | 4.2303e-05 | 3.6468e-07 | 116
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CUTOUT | 14 | 465 | 66403 | 0.012108 | 8.4789e-05 | 142.8022
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE | 28 | 3431 | 1074733 | 0.19597 | 0.00062562 | 313.2419
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 12 | 1160 | 0.00021152 | 2.1881e-06 | 96.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | F | CONDUCTOR UG | 3 | 10 | 1424 | 0.00025966 | 1.8234e-06 | 142.4
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | R | ARRESTER | 2 | 560 | 67564 | 0.01232 | 0.00010211 | 120.65
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | PEDESTAL | 1 | 4 | 152 | 2.7519e-05 | 7.2419e-07 | 38
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | FUSE | 2 | 34 | 1871 | 0.00033874 | 6.1556e-06 | 55.0294
AEP Total | 2024 | 5615460 | PARTIAL POWER | FW | CONDUCTOR UG | 1 | 11 | 1254 | 0.00022331 | 1.9589e-06 | 114
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | F | POLE | 3 | 24 | 7463 | 0.001329 | 4.2739e-06 | 310.9583
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 6 | 6 | 440 | 7.8355e-05 | 1.0685e-06 | 73.3333
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | PEDESTAL | 1 | 7 | 441 | 7.8533e-05 | 1.2466e-06 | 63
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 3 | 452 | 41769 | 0.0074382 | 8.0492e-05 | 92.4093
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | OTHER EQUIPMENT | 5 | 912 | 58055 | 0.010338 | 0.00016241 | 63.6568
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | SPLICE, OH | 1 | 1 | 113 | 2.0123e-05 | 1.7808e-07 | 113
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 1 | 5 | 745 | 0.00013267 | 8.904e-07 | 149
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 141 | 2.539e-05 | 3.6014e-07 | 70.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 3 | 7 | 517 | 9.2067e-05 | 1.2466e-06 | 73.8571
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 6 | 63 | 5146 | 0.0009164 | 1.1219e-05 | 81.6825
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 12 | 226 | 21157 | 0.0037676 | 4.0246e-05 | 93.615
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CROSSARM | 1 | 1 | 377 | 6.7136e-05 | 1.7808e-07 | 377
AEP Total | 2025 | 5615460 | PARTIAL POWER | WL | FUSE | 3 | 10 | 419 | 7.4615e-05 | 1.7808e-06 | 41.9
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | WW | NONE | 2 | 381 | 192717 | 0.034319 | 6.7848e-05 | 505.8189
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 4 | 130 | 11888 | 0.002117 | 2.315e-05 | 91.4462
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 4 | 1251 | 109305 | 0.019465 | 0.00022278 | 87.3741
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | METERING | 1 | 1 | 60 | 1.0804e-05 | 1.8007e-07 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | INSULATOR | 1 | 611 | 116701 | 0.021015 | 0.00011002 | 191
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | NONE | 9 | 127 | 8205 | 0.0014716 | 2.2777e-05 | 64.6063
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | METERING | 1 | 1 | 86 | 1.5486e-05 | 1.8007e-07 | 86
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | BREAKER | 3 | 595 | 54460 | 0.0098067 | 0.00010714 | 91.5294
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 124 | 25930 | 0.0046176 | 2.2082e-05 | 209.1129
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | TRANSFORMER, UG | 1 | 1 | 331 | 5.9604e-05 | 1.8007e-07 | 331
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 5 | 3229 | 571138 | 0.10243 | 0.00057912 | 176.8777
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | R | NONE | 1 | 1 | 65 | 1.1852e-05 | 1.8234e-07 | 65
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 103 | 29896 | 0.0053619 | 1.8473e-05 | 290.2524
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | JUMPER/RISER | 3 | 1774 | 145717 | 0.02657 | 0.00032347 | 82.1404
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | TRANSFORMER, GROUNDING | 1 | 9 | 333 | 5.9724e-05 | 1.6142e-06 | 37
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | SPLICE, UG | 1 | 19 | 1254 | 0.00022703 | 3.4399e-06 | 66
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 51 | 4437 | 0.00079014 | 9.0821e-06 | 87
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 963 | 88608 | 0.015779 | 0.00017149 | 92.0125
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR UG | 3 | 3 | 313 | 5.6668e-05 | 5.4314e-07 | 104.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | POLE | 31 | 789 | 75059 | 0.013589 | 0.00014285 | 95.1318
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | NONE | 63 | 2632 | 137746 | 0.024938 | 0.00047651 | 52.3351
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONN/CLAMP | 71 | 212 | 17258 | 0.0031245 | 3.8382e-05 | 81.4057
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CUTOUT | 9 | 220 | 14966 | 0.0027095 | 3.983e-05 | 68.0273
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | JUMPER/RISER | 13 | 103 | 14268 | 0.0025832 | 1.8648e-05 | 138.5243
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | FUSE | 11 | 227 | 27923 | 0.0050554 | 4.1098e-05 | 123.0088
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 38 | 292 | 42328 | 0.0076633 | 5.2866e-05 | 144.9589
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | POLE | 2 | 6 | 648 | 0.00011732 | 1.0863e-06 | 108
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | ARRESTER | 4 | 18 | 955 | 0.0001729 | 3.2588e-06 | 53.0556
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | METERING | 19 | 21 | 1466 | 0.00026541 | 3.802e-06 | 69.8095
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | U | NONE | 8 | 1766 | 86779 | 0.015711 | 0.00031973 | 49.1387
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | NONE | 3 | 106 | 3542 | 0.00064127 | 1.9191e-05 | 33.4151
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 2 | 86 | 1.5486e-05 | 3.6014e-07 | 43
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 10 | 900 | 0.00016294 | 1.8105e-06 | 90
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 1779 | 153696 | 0.027676 | 0.00032035 | 86.3946
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 6 | 715 | 78835 | 0.014039 | 0.00012733 | 110.2587
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 7 | 873 | 133590 | 0.02379 | 0.00015546 | 153.0241
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 4 | 6 | 551 | 9.8122e-05 | 1.0685e-06 | 91.8333
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 4 | 4 | 504 | 8.9752e-05 | 7.1232e-07 | 126
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 32 | 241 | 29635 | 0.0052774 | 4.2917e-05 | 122.9668
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 5 | 6 | 917 | 0.0001633 | 1.0685e-06 | 152.8333
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 18 | 1166 | 0.00020764 | 3.2054e-06 | 64.7778
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CUTOUT | 1 | 7 | 210 | 3.802e-05 | 1.2673e-06 | 30
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 561 | 9.9903e-05 | 3.5616e-07 | 280.5
AEP Total | 2024 | 5615460 | GENERATION | G | NONE | 15 | 9275 | 814031 | 0.14496 | 0.0016517 | 87.7661
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CE | CONDUCTOR OVERHEAD | 1 | 1 | 35 | 6.2328e-06 | 1.7808e-07 | 35
AEP Total | 2024 | 5615460 | PARTIAL POWER | WT | CONDUCTOR OVERHEAD | 1 | 1 | 156 | 2.778e-05 | 1.7808e-07 | 156
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CROSSARM | 1 | 2 | 178 | 3.1698e-05 | 3.5616e-07 | 89
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 1 | 89 | 1.5849e-05 | 1.7808e-07 | 89
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | ARRESTER | 2 | 10 | 404 | 7.2457e-05 | 1.7935e-06 | 40.4
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 6 | 253 | 44378 | 0.0079028 | 4.5054e-05 | 175.4071
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 16 | 63 | 5577 | 0.00099315 | 1.1219e-05 | 88.5238
AEP Total | 2024 | 5615460 | TRANSMISSION LINE | LS | NONE | 11 | 10962 | 792234 | 0.14108 | 0.0019521 | 72.2709
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | POLE HARDWARE | 4 | 124 | 13767 | 0.0024516 | 2.2082e-05 | 111.0242
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | POLE | 1 | 51 | 7065 | 0.0012671 | 9.1469e-06 | 138.5294
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 3 | 1378 | 290008 | 0.051645 | 0.00024539 | 210.4557
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR UG | 2 | 2 | 502 | 8.9396e-05 | 3.5616e-07 | 251
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 2 | 14 | 2325 | 0.00041404 | 2.4931e-06 | 166.0714
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | BREAKER | 1 | 558 | 81468 | 0.014611 | 0.00010008 | 146
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 198 | 2955 | 245428 | 0.043706 | 0.00052623 | 83.0552
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 4 | 27 | 1844 | 0.00032838 | 4.8082e-06 | 68.2963
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 44 | 424 | 85030 | 0.015142 | 7.5506e-05 | 200.5425
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 831 | 138350 | 0.024913 | 0.00014964 | 166.4862
AEP Total | 2025 | 5615460 | TRANSMISSION LINE | EQF | RELAY | 1 | 576 | 51248 | 0.0091262 | 0.00010257 | 88.9722
AEP Total | 2024 | 5615460 | TRANSMISSION STATION | AB | NONE | 16 | 15373 | 869687 | 0.15487 | 0.0027376 | 56.5724
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CROSSARM | 3 | 6 | 690 | 0.00012288 | 1.0685e-06 | 115
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 9 | 263 | 24704 | 0.0043993 | 4.6835e-05 | 93.9316
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 5 | 689 | 321448 | 0.057652 | 0.00012357 | 466.5428
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CE | POLE | 1 | 5 | 965 | 0.00017471 | 9.0523e-07 | 193
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 5 | 685 | 0.0001249 | 9.1171e-07 | 137
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 846 | 201657 | 0.036771 | 0.00015426 | 238.3652
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | CONDUCTOR OVERHEAD | 1 | 1 | 60 | 1.0863e-05 | 1.8105e-07 | 60
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | POLE | 1 | 7 | 686 | 0.00012509 | 1.2764e-06 | 98
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | O | CONDUCTOR OVERHEAD | 1 | 11 | 352 | 6.3728e-05 | 1.9915e-06 | 32
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 181 | 3.2769e-05 | 1.8105e-07 | 181
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | FUSE | 1 | 1 | 80 | 1.4406e-05 | 1.8007e-07 | 80
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | JUMPER/RISER | 5 | 89 | 6244 | 0.0011385 | 1.6228e-05 | 70.1573
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | JUMPER/RISER | 5 | 42 | 4099 | 0.00072995 | 7.4794e-06 | 97.5952
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 7 | 1756 | 63819 | 0.011365 | 0.00031271 | 36.3434
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CROSSARM | 1 | 12 | 558 | 9.9369e-05 | 2.137e-06 | 46.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CROSSARM | 11 | 2855 | 709220 | 0.1272 | 0.00051204 | 248.4133
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | NONE | 55 | 539 | 52756 | 0.0096196 | 9.8282e-05 | 97.8776
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 41 | 105 | 7128 | 0.0012997 | 1.9146e-05 | 67.8857
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | NONE | 164 | 8855 | 1236452 | 0.22546 | 0.0016146 | 139.6332
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 29 | 2594 | 212023 | 0.038661 | 0.000473 | 81.7359
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 12 | 821 | 0.0001497 | 2.1881e-06 | 68.4167
AEP Total | 2020 | 5484199 | PARTIAL POWER | V | NONE | 1 | 1 | 57 | 1.0393e-05 | 1.8234e-07 | 57
AEP Total | 2020 | 5484199 | PARTIAL POWER | CE | CONN/CLAMP | 2 | 6 | 90 | 1.6411e-05 | 1.0941e-06 | 15
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 551 | 77231 | 0.014082 | 0.00010047 | 140.1652
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | BREAKER | 1 | 581 | 8134 | 0.0014832 | 0.00010594 | 14
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | U | NONE | 9 | 2877 | 92921 | 0.016943 | 0.0005246 | 32.2979
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 320 | 629 | 54661 | 0.009734 | 0.00011201 | 86.9014
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 56 | 78 | 9035 | 0.001609 | 1.389e-05 | 115.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 170 | 22181 | 0.0039782 | 3.049e-05 | 130.4765
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | A | CUTOUT | 1 | 5 | 690 | 0.00012425 | 9.0036e-07 | 138
AEP Total | 2023 | 5575683 | TRANSMISSION LINE | ERF | NONE | 1 | 43 | 11051 | 0.001982 | 7.7121e-06 | 257
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 131 | 15476 | 3127450 | 0.55694 | 0.002756 | 202.0839
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 61 | 1381 | 176851 | 0.031494 | 0.00024593 | 128.0601
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 13 | 731 | 163567 | 0.029128 | 0.00013018 | 223.7579
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 9 | 76 | 11765 | 0.0020951 | 1.3534e-05 | 154.8026
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | V | METERING | 9 | 10 | 624 | 0.00011112 | 1.7808e-06 | 62.4
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | FUSE | 1 | 14 | 1190 | 0.00021343 | 2.5109e-06 | 85
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | FUSE | 3 | 36 | 5788 | 0.0010479 | 6.5177e-06 | 160.7778
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | F | METERING | 1 | 2 | 116 | 2.0888e-05 | 3.6014e-07 | 58
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 56 | 5223 | 452209 | 0.080529 | 0.00093011 | 86.5803
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 22 | 260 | 43299 | 0.0077107 | 4.6301e-05 | 166.5346
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CROSSARM | 1 | 24 | 4992 | 0.00089532 | 4.3044e-06 | 208
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | ABI | JUMPER/RISER | 1 | 881 | 54622 | 0.0099599 | 0.00016064 | 62
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 35 | 4270 | 0.0007786 | 6.382e-06 | 122
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 1982 | 151356 | 0.027599 | 0.0003614 | 76.3653
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | CO | NONE | 1 | 408 | 7344 | 0.0013391 | 7.4396e-05 | 18
AEP Total | 2020 | 5484199 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 3 | 25 | 1627 | 0.00029667 | 4.5586e-06 | 65.08
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | REGULATOR | 1 | 74 | 6068 | 0.0010986 | 1.3397e-05 | 82
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 1 | 58 | 1.0501e-05 | 1.8105e-07 | 58
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 4 | 484 | 8.7626e-05 | 7.2419e-07 | 121
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | NONE | 72 | 163 | 16425 | 0.0029577 | 2.9352e-05 | 100.7669
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WW | NONE | 5 | 883 | 157776 | 0.028411 | 0.000159 | 178.6818
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, OH | 14 | 4952 | 497245 | 0.08954 | 0.00089172 | 100.413
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 131 | 399 | 39765 | 0.0071606 | 7.1849e-05 | 99.6617
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | FUSE | 14 | 1188 | 70427 | 0.012682 | 0.00021393 | 59.282
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONN/CLAMP | 92 | 170 | 10097 | 0.0018182 | 3.0612e-05 | 59.3941
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 68 | 346 | 34762 | 0.0062597 | 6.2305e-05 | 100.4682
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 2 | 86 | 1.5486e-05 | 3.6014e-07 | 43
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 54 | 3085 | 314316 | 0.056599 | 0.00055552 | 101.8853
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | ARRESTER | 2 | 7 | 651 | 0.00011786 | 1.2673e-06 | 93
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CUTOUT | 3 | 140 | 28792 | 0.0052127 | 2.5346e-05 | 205.6571
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 19 | 884 | 145334 | 0.026312 | 0.00016004 | 164.405
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 8 | 2241 | 0.00040572 | 1.4484e-06 | 280.125
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 2 | 51 | 13890 | 0.0025147 | 9.2334e-06 | 272.3529
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 2 | 2 | 180 | 3.2588e-05 | 3.6209e-07 | 90
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | WU | BREAKER | 2 | 649 | 97283 | 0.017613 | 0.0001175 | 149.8968
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 81 | 1.4665e-05 | 1.8105e-07 | 81
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 8 | 1593 | 0.00028841 | 1.4484e-06 | 199.125
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CABLE TERMINATOR | 1 | 1 | 239 | 4.327e-05 | 1.8105e-07 | 239
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | METERING | 5 | 7 | 914 | 0.00016548 | 1.2673e-06 | 130.5714
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 3 | 1302 | 0.00023572 | 5.4314e-07 | 434
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SWITCH, UG | 1 | 111 | 19827 | 0.0035896 | 2.0096e-05 | 178.6216
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 282 | 3847 | 276706 | 0.050455 | 0.00070147 | 71.9277
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 34 | 3072 | 261540 | 0.04769 | 0.00056015 | 85.1367
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CUTOUT | 268 | 5457 | 635141 | 0.11581 | 0.00099504 | 116.3901
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | ERF | NONE | 10 | 3960 | 245113 | 0.044694 | 0.00072207 | 61.8972
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | NONE | 8 | 16 | 723 | 0.00013019 | 2.8812e-06 | 45.1875
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONN/CLAMP | 2 | 2 | 238 | 4.2857e-05 | 3.6014e-07 | 119
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | V | CONDUCTOR UG | 5 | 6 | 667 | 0.00011963 | 1.0761e-06 | 111.1667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 419 | 3371 | 337951 | 0.060612 | 0.00060459 | 100.2524
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 2 | 401 | 7.2209e-05 | 3.6014e-07 | 200.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | FUSE | 222 | 2470 | 354881 | 0.063648 | 0.000443 | 143.6765
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | POLE | 1 | 14 | 1708 | 0.00030756 | 2.521e-06 | 122
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | REGULATOR | 1 | 213 | 38979 | 0.0069909 | 3.8202e-05 | 183
AEP Total | 2023 | 5575683 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 1 | 13 | 609 | 0.00010922 | 2.3316e-06 | 46.8462
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | U | NONE | 7 | 2477 | 165417 | 0.029787 | 0.00044604 | 66.7812
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | PEDESTAL | 6 | 23 | 895 | 0.00016116 | 4.1417e-06 | 38.913
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FW | INSULATOR | 4 | 19 | 297 | 5.3481e-05 | 3.4214e-06 | 15.6316
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | POLE | 3 | 1079 | 65815 | 0.011851 | 0.0001943 | 60.9963
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | ARRESTER | 3 | 4 | 49 | 8.7882e-06 | 7.174e-07 | 12.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR UG | 4 | 7 | 1971 | 0.00035492 | 1.2605e-06 | 281.5714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CAPACITOR | 2 | 184 | 8104 | 0.0014535 | 3.3e-05 | 44.0435
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | CE | ARRESTER | 4 | 2771 | 189509 | 0.034125 | 0.00049898 | 68.3901
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 18 | 514 | 98453 | 0.017658 | 9.2186e-05 | 191.5428
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | FW | NONE | 1 | 2 | 102 | 1.8367e-05 | 3.6014e-07 | 51
AEP Total | 2022 | 5553337 | PARTIAL POWER | FW | CONDUCTOR UG | 1 | 1 | 71 | 1.2785e-05 | 1.8007e-07 | 71
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | ARRESTER | 12 | 1818 | 145851 | 0.026595 | 0.0003315 | 80.2261
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | FUSE | 2 | 6 | 244 | 4.4491e-05 | 1.0941e-06 | 40.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | NONE | 1 | 32 | 352 | 6.4184e-05 | 5.8349e-06 | 11
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | TRANSFORMER, STATION SERVICE | 2 | 510 | 25500 | 0.0046497 | 9.2994e-05 | 50
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 1 | 312 | 5.6891e-05 | 1.8234e-07 | 312
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | OTHER EQUIPMENT | 1 | 3 | 72 | 1.3129e-05 | 5.4703e-07 | 24
AEP Total | 2020 | 5484199 | TRANSMISSION LINE | EQF | SWITCH, OH | 1 | 799 | 10387 | 0.001894 | 0.00014569 | 13
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | V | METERING | 8 | 8 | 736 | 0.0001342 | 1.4587e-06 | 92
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 11 | 40 | 3370 | 0.00061449 | 7.2937e-06 | 84.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, OH | 13 | 69 | 8143 | 0.0014848 | 1.2582e-05 | 118.0145
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | POLE | 2 | 2601 | 1183546 | 0.21581 | 0.00047427 | 455.035
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | NONE | 11 | 11119 | 523211 | 0.095403 | 0.0020275 | 47.0556
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | NONE | 5 | 822 | 39000 | 0.0071113 | 0.00014989 | 47.4453
AEP Total | 2020 | 5484199 | TRANSMISSION STATION | EQF | BREAKER | 5 | 2803 | 57805 | 0.01054 | 0.0005111 | 20.6225
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CROSSARM | 3 | 12 | 1863 | 0.0003397 | 2.1881e-06 | 155.25
AEP Total | 2020 | 5484199 | PARTIAL POWER | FW | CONDUCTOR OVERHEAD | 2 | 6 | 1181 | 0.00021535 | 1.0941e-06 | 196.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 12 | 1398 | 0.0002531 | 2.1726e-06 | 116.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 145 | 20445 | 0.0037015 | 2.6252e-05 | 141
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | METERING | 3 | 3 | 176 | 3.1864e-05 | 5.4314e-07 | 58.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 2 | 88 | 11030 | 0.0019969 | 1.5932e-05 | 125.3409
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 6 | 166 | 14409 | 0.0026087 | 3.0054e-05 | 86.8012
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | O | NONE | 5 | 6405 | 366667 | 0.066384 | 0.0011596 | 57.247
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | POLE | 2 | 616 | 83905 | 0.015191 | 0.00011152 | 136.2094
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | ARRESTER | 2 | 1818 | 182878 | 0.033109 | 0.00032914 | 100.593
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | NONE | 8 | 18 | 1111 | 0.00020114 | 3.2588e-06 | 61.7222
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, UG | 9 | 214 | 20733 | 0.0037536 | 3.8744e-05 | 96.8832
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 236 | 5212 | 867718 | 0.1571 | 0.00094361 | 166.4847
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | NONE | 11 | 41 | 4749 | 0.00085979 | 7.4229e-06 | 115.8293
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 31 | 817 | 94053 | 0.017028 | 0.00014791 | 115.12
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 124 | 325 | 36444 | 0.0065981 | 5.884e-05 | 112.1354
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | OTHER EQUIPMENT | 2 | 2 | 66 | 1.1949e-05 | 3.6209e-07 | 33
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | NONE | 2965 | 27922 | 1588263 | 0.28755 | 0.0050552 | 56.8821
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 1 | 87 | 1.5751e-05 | 1.8105e-07 | 87
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 1299 | 87762 | 0.015889 | 0.00023518 | 67.5612
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | NONE | 2 | 3 | 271 | 4.9064e-05 | 5.4314e-07 | 90.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | POLE | 35 | 6051 | 1565674 | 0.28346 | 0.0010955 | 258.7463
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | RELAY | 15 | 4436 | 390698 | 0.070734 | 0.00080312 | 88.0744
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | NONE | 7 | 7 | 906 | 0.00016403 | 1.2673e-06 | 129.4286
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 19 | 312 | 8233 | 0.0014906 | 5.6486e-05 | 26.3878
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | ARRESTER | 5 | 1493 | 136039 | 0.024629 | 0.0002703 | 91.1179
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE | 11 | 646 | 187793 | 0.033999 | 0.00011696 | 290.7012
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | NONE | 62 | 99 | 8920 | 0.0016149 | 1.7924e-05 | 90.101
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | FUSE | 23 | 171 | 13647 | 0.0024707 | 3.0959e-05 | 79.807
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | NONE | 109 | 8892 | 1481583 | 0.26824 | 0.0016099 | 166.6198
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | NONE | 26 | 1707 | 88572 | 0.016036 | 0.00030905 | 51.8875
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 87 | 609 | 0.00011026 | 1.5751e-05 | 7
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | EQF | CROSSARM | 4 | 1047 | 92983 | 0.016834 | 0.00018956 | 88.809
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | NONE | 113 | 237 | 13747 | 0.0024754 | 4.2677e-05 | 58.0042
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 62 | 4721 | 519130 | 0.093481 | 0.00085012 | 109.9619
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | FUSE | 11 | 155 | 9188 | 0.0016545 | 2.7911e-05 | 59.2774
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OU | CONDUCTOR OVERHEAD | 1 | 1 | 80 | 1.4406e-05 | 1.8007e-07 | 80
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 373 | 135026 | 0.024446 | 6.753e-05 | 362
AEP Total | 2021 | 5523447 | PARTIAL POWER | CE | ARRESTER | 1 | 2 | 128 | 2.3174e-05 | 3.6209e-07 | 64
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | V | NONE | 2 | 1589 | 26232 | 0.0047492 | 0.00028768 | 16.5085
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | NONE | 1893 | 75322 | 2970099 | 0.54157 | 0.013734 | 39.432
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | NONE | 2348 | 22419 | 1543063 | 0.27675 | 0.0040209 | 68.8284
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 369 | 2160 | 355181 | 0.063702 | 0.0003874 | 164.4356
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE HARDWARE | 4 | 1540 | 98587 | 0.017753 | 0.00027731 | 64.0175
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | METERING | 10 | 10 | 2229 | 0.00040138 | 1.8007e-06 | 222.9
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 3 | 183 | 3.2953e-05 | 5.4022e-07 | 61
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | SWITCH, OH | 4 | 4340 | 284330 | 0.0512 | 0.00078151 | 65.5138
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 23 | 1200 | 166340 | 0.029833 | 0.00021522 | 138.6167
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 4 | 32 | 1159 | 0.0002087 | 5.7623e-06 | 36.2188
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, UG | 9 | 1823 | 99237 | 0.017798 | 0.00032696 | 54.4361
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | U | NONE | 30 | 20352 | 2086852 | 0.37578 | 0.0036648 | 102.5379
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, OH | 9 | 5592 | 225487 | 0.040441 | 0.0010029 | 40.3231
AEP Total | 2022 | 5553337 | TRANSMISSION LINE | EQF | CROSSARM | 3 | 1720 | 230561 | 0.041518 | 0.00030972 | 134.0471
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FW | NONE | 152 | 6590 | 288775 | 0.051792 | 0.0011819 | 43.8202
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | CONN/CLAMP | 1 | 182 | 27482 | 0.0049289 | 3.2642e-05 | 151
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 3161 | 342212 | 0.061376 | 0.00056693 | 108.2607
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 1 | 1 | 79 | 1.4169e-05 | 1.7935e-07 | 79
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 15 | 3390 | 0.000608 | 2.6903e-06 | 226
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OU | FUSE | 1 | 12 | 288 | 5.1653e-05 | 2.1522e-06 | 24
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | JUMPER/RISER | 10 | 13 | 2233 | 0.00040049 | 2.3316e-06 | 171.7692
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | FUSE | 767 | 4670 | 314945 | 0.056085 | 0.00083163 | 67.44
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FW | NONE | 182 | 3975 | 152918 | 0.027232 | 0.00070787 | 38.4699
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | METERING | 30 | 34 | 3731 | 0.00068032 | 6.1996e-06 | 109.7353
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FW | CONDUCTOR OVERHEAD | 17 | 817 | 15061 | 0.0027463 | 0.00014897 | 18.4345
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | ARRESTER | 8 | 6253 | 1138103 | 0.20752 | 0.0011402 | 182.0091
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 5 | 42 | 5964 | 0.0010798 | 7.6039e-06 | 142
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | NONE | 513 | 34918 | 4374391 | 0.79197 | 0.0063218 | 125.2761
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 2 | 242 | 4.3813e-05 | 3.6209e-07 | 121
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 11 | 1156 | 105765 | 0.019148 | 0.00020929 | 91.4922
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 209 | 3.7839e-05 | 1.8105e-07 | 209
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CUTOUT | 27 | 1596 | 127408 | 0.023067 | 0.00028895 | 79.8296
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CROSSARM | 4 | 534 | 262455 | 0.047517 | 9.6679e-05 | 491.4888
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CUTOUT | 7 | 35 | 7151 | 0.0012947 | 6.3366e-06 | 204.3143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 14 | 69 | 27766 | 0.0050269 | 1.2492e-05 | 402.4058
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | FUSE | 3 | 85 | 4142 | 0.00074989 | 1.5389e-05 | 48.7294
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CUTOUT | 104 | 3602 | 532360 | 0.096382 | 0.00065213 | 147.7957
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | ARRESTER | 56 | 985 | 102820 | 0.018615 | 0.00017833 | 104.3858
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | FUSE | 81 | 1872 | 121997 | 0.022087 | 0.00033892 | 65.1693
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | SWITCH, OH | 2 | 3 | 226 | 4.0916e-05 | 5.4314e-07 | 75.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 26 | 133 | 28555 | 0.0051698 | 2.4079e-05 | 214.6992
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | ARRESTER | 8 | 28 | 2531 | 0.00045823 | 5.0693e-06 | 90.3929
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 1 | 91 | 36309 | 0.0065736 | 1.6475e-05 | 399
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WL | ARRESTER | 1 | 9 | 1395 | 0.00025256 | 1.6294e-06 | 155
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | NONE | 64 | 305 | 44205 | 0.0080032 | 5.5219e-05 | 144.9344
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | NONE | 18 | 26 | 1955 | 0.00035395 | 4.7072e-06 | 75.1923
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONN/CLAMP | 42 | 91 | 13339 | 0.002415 | 1.6475e-05 | 146.5824
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 24 | 2751 | 309866 | 0.0561 | 0.00049806 | 112.6376
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | NONE | 83 | 3036 | 337150 | 0.06104 | 0.00054966 | 111.0507
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONN/CLAMP | 18 | 533 | 78039 | 0.014129 | 9.6498e-05 | 146.4146
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | NONE | 20 | 59 | 5832 | 0.0010559 | 1.0682e-05 | 98.8475
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | NONE | 124 | 6328 | 638249 | 0.11555 | 0.0011457 | 100.8611
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | JUMPER/RISER | 11 | 825 | 182904 | 0.033114 | 0.00014936 | 221.7018
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | NONE | 549 | 8564 | 1236846 | 0.22272 | 0.0015421 | 144.4239
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | NONE | 165 | 9191 | 2556977 | 0.46044 | 0.001655 | 278.2044
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 60 | 2749 | 494745 | 0.08909 | 0.00049502 | 179.9727
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 42 | 1185 | 153589 | 0.027657 | 0.00021339 | 129.611
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | NONE | 108 | 14281 | 2125792 | 0.3828 | 0.0025716 | 148.8546
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 33 | 142 | 30651 | 0.0055194 | 2.557e-05 | 215.8521
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 33 | 5.9424e-06 | 1.8007e-07 | 33
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 18 | 6163 | 0.0011098 | 3.2413e-06 | 342.3889
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 5 | 57 | 16982 | 0.0030745 | 1.032e-05 | 297.9298
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | ARRESTER | 6 | 489 | 49218 | 0.0089107 | 8.8532e-05 | 100.6503
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WU | NONE | 5 | 2766 | 409706 | 0.074176 | 0.00050077 | 148.1222
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | SPLICE, OH | 1 | 8 | 184 | 3.3313e-05 | 1.4484e-06 | 23
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | SWITCH, OH | 2 | 115 | 13748 | 0.002489 | 2.082e-05 | 119.5478
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | NONE | 606 | 30767 | 6215600 | 1.1334 | 0.0056101 | 202.0216
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | NONE | 38 | 2435 | 614800 | 0.1121 | 0.000444 | 252.4846
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 99 | 6878 | 867263 | 0.15814 | 0.0012541 | 126.0923
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | ARRESTER | 18 | 386 | 38676 | 0.0070523 | 7.0384e-05 | 100.1969
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | NONE | 4617 | 211528 | 30835958 | 5.5304 | 0.037938 | 145.7772
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | NONE | 57 | 2536 | 1212510 | 0.21746 | 0.00045483 | 478.1191
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 68 | 1730 | 505665 | 0.090691 | 0.00031028 | 292.2919
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | FUSE | 3 | 220 | 33408 | 0.0059917 | 3.9457e-05 | 151.8545
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 15 | 756 | 89411 | 0.0161 | 0.00013613 | 118.2685
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 6 | 1311 | 0.00023607 | 1.0804e-06 | 218.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | NONE | 34 | 136 | 11533 | 0.0020684 | 2.4392e-05 | 84.8015
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 11 | 1081 | 0.00019466 | 1.9808e-06 | 98.2727
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CROSSARM | 48 | 8844 | 1832775 | 0.32871 | 0.0015862 | 207.2337
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 7 | 931 | 116900 | 0.02105 | 0.00016765 | 125.5639
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 14 | 359 | 69383 | 0.012444 | 6.4387e-05 | 193.2674
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | FUSE | 1 | 1 | 74 | 1.3325e-05 | 1.8007e-07 | 74
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | JUMPER/RISER | 1 | 8 | 696 | 0.00012533 | 1.4406e-06 | 87
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | TRANSFORMER, OH | 1 | 3 | 2409 | 0.00043379 | 5.4022e-07 | 803
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SWITCH, OH | 10 | 1399 | 121904 | 0.021951 | 0.00025192 | 87.1365
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | FUSE | 1 | 1 | 138 | 2.4575e-05 | 1.7808e-07 | 138
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 13 | 429 | 7.6396e-05 | 2.315e-06 | 33
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 179 | 9892 | 1882402 | 0.33522 | 0.0017616 | 190.2954
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CROSSARM | 2 | 113 | 15432 | 0.0028139 | 2.0605e-05 | 136.5664
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | INSULATOR | 1 | 48 | 11376 | 0.0020596 | 8.6902e-06 | 237
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | BREAKER | 6 | 4647 | 341219 | 0.061776 | 0.00084132 | 73.4278
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | NONE | 4823 | 221264 | 35308218 | 6.358 | 0.039843 | 159.5751
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | NONE | 839 | 77615 | 10109218 | 1.8204 | 0.013976 | 130.2483
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE | 62 | 6991 | 1499464 | 0.27001 | 0.0012589 | 214.4849
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 3 | 630 | 0.00011345 | 5.4022e-07 | 210
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | FUSE | 1 | 2 | 90 | 1.6206e-05 | 3.6014e-07 | 45
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 8 | 1112 | 0.00020132 | 1.4484e-06 | 139
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 3 | 638 | 374876 | 0.06787 | 0.00011551 | 587.5799
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | METERING | 9 | 13 | 1655 | 0.00029963 | 2.3536e-06 | 127.3077
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 6 | 1186 | 0.00021472 | 1.0863e-06 | 197.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 4 | 1499 | 485730 | 0.08794 | 0.00027139 | 324.036
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 121 | 980 | 223704 | 0.040791 | 0.0001787 | 228.2694
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 169 | 76082 | 0.0137 | 3.0432e-05 | 450.1893
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NONE | 881 | 58759 | 8980562 | 1.6107 | 0.010538 | 152.8372
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | JUMPER/RISER | 15 | 296 | 46252 | 0.0083287 | 5.3301e-05 | 156.2568
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR UG | 9 | 25 | 6565 | 0.0011822 | 4.5018e-06 | 262.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 21 | 1092 | 138970 | 0.024924 | 0.00019585 | 127.2619
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | POLE | 11 | 197 | 56250 | 0.010088 | 3.5332e-05 | 285.533
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 121 | 6905 | 1370684 | 0.24583 | 0.0012384 | 198.506
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 25 | 91 | 11920 | 0.0021379 | 1.6321e-05 | 130.989
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | NONE | 52 | 201 | 25770 | 0.0046219 | 3.6049e-05 | 128.209
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CROSSARM | 3 | 545 | 59493 | 0.01067 | 9.7746e-05 | 109.1615
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 623 | 44981 | 0.0080998 | 0.00011218 | 72.2006
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | FUSE | 97 | 1426 | 194780 | 0.034934 | 0.00025575 | 136.5919
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | NONE | 4 | 9 | 814 | 0.00014599 | 1.6142e-06 | 90.4444
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | NONE | 81 | 1466 | 228596 | 0.040999 | 0.00026293 | 155.9318
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CUTOUT | 12 | 13 | 1186 | 0.00021271 | 2.3316e-06 | 91.2308
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 5 | 970 | 0.00017397 | 8.9675e-07 | 194
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 1 | 2 | 276 | 4.97e-05 | 3.6014e-07 | 138
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | SWITCH, UG | 1 | 1 | 201 | 3.6194e-05 | 1.8007e-07 | 201
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | JUMPER/RISER | 6 | 296 | 15216 | 0.0027745 | 5.3973e-05 | 51.4054
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | ARRESTER | 5 | 8 | 2519 | 0.00045932 | 1.4587e-06 | 314.875
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABI | NONE | 2 | 1899 | 153819 | 0.028048 | 0.00034627 | 81
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 51 | 32487 | 0.0059237 | 9.2994e-06 | 637
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 7 | 1449 | 0.00025988 | 1.2555e-06 | 207
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | ARRESTER | 4 | 36 | 2476 | 0.00044407 | 6.4566e-06 | 68.7778
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 15 | 142 | 22324 | 0.0039755 | 2.5287e-05 | 157.2113
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 3 | 1179 | 0.00021145 | 5.3805e-07 | 393
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 4 | 38 | 5632 | 0.0010029 | 6.767e-06 | 148.2105
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | ARRESTER | 1 | 4 | 336 | 6.0262e-05 | 7.174e-07 | 84
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | NONE | 1 | 138 | 1242 | 0.00022275 | 2.475e-05 | 9
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 10 | 497 | 48660 | 0.0086654 | 8.8506e-05 | 97.9074
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | FUSE | 2 | 9 | 401 | 7.26e-05 | 1.6294e-06 | 44.5556
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 36 | 90 | 10421 | 0.0018558 | 1.6027e-05 | 115.7889
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | SWITCH, OH | 2 | 6 | 822 | 0.00014882 | 1.0863e-06 | 137
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 36 | 1854 | 0.00033016 | 6.4109e-06 | 51.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 3 | 4 | 390 | 6.9451e-05 | 7.1232e-07 | 97.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 58 | 8642 | 0.0015499 | 1.0402e-05 | 149
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 250 | 22764 | 0.0040827 | 4.4838e-05 | 91.056
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 3 | 348 | 6.3004e-05 | 5.4314e-07 | 116
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONN/CLAMP | 3 | 13 | 1875 | 0.00033946 | 2.3536e-06 | 144.2308
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 298 | 187144 | 0.034124 | 5.4338e-05 | 628
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 273 | 19383 | 0.0035343 | 4.9779e-05 | 71
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | NONE | 5 | 5 | 855 | 0.0001559 | 9.1171e-07 | 171
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 47 | 8.5092e-06 | 1.8105e-07 | 47
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 14 | 4928 | 0.00089858 | 2.5528e-06 | 352
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | NONE | 15 | 1749 | 243287 | 0.044361 | 0.00031892 | 139.1006
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 5 | 2123 | 0.00038076 | 8.9675e-07 | 424.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, OH | 15 | 665 | 59942 | 0.010751 | 0.00011927 | 90.1383
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | FUSE | 3 | 40 | 3054 | 0.00054774 | 7.174e-06 | 76.35
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | NONE | 1 | 101 | 13231 | 0.0023825 | 1.8187e-05 | 131
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 6 | 57 | 45302 | 0.0082605 | 1.0393e-05 | 794.7719
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 7 | 608 | 331501 | 0.060447 | 0.00011086 | 545.2319
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | ARRESTER | 5 | 9 | 788 | 0.00014369 | 1.6411e-06 | 87.5556
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 225 | 109350 | 0.019939 | 4.1027e-05 | 486
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 5 | 10 | 1337 | 0.00024379 | 1.8234e-06 | 133.7
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | FUSE | 1 | 2 | 104 | 1.8964e-05 | 3.6468e-07 | 52
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | FUSE | 5 | 91 | 25175 | 0.0045905 | 1.6593e-05 | 276.6484
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | POLE | 9 | 1143 | 193631 | 0.035307 | 0.00020842 | 169.4059
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 2 | 328 | 5.9808e-05 | 3.6468e-07 | 164
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | NONE | 2459 | 33823 | 2786921 | 0.49629 | 0.0060232 | 82.3972
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 8 | 1648 | 0.00029557 | 1.4348e-06 | 206
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 66 | 170 | 43241 | 0.0077003 | 3.0274e-05 | 254.3588
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CROSSARM | 4 | 1387 | 186660 | 0.033478 | 0.00024876 | 134.5782
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 7 | 19 | 5627 | 0.0010092 | 3.4077e-06 | 296.1579
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 27 | 4401 | 0.00078932 | 4.8425e-06 | 163
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 557 | 60547 | 0.010859 | 9.9898e-05 | 108.702
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 2 | 578 | 0.00010366 | 3.587e-07 | 289
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 5 | 72 | 35096 | 0.0062945 | 1.2913e-05 | 487.4444
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | NONE | 4 | 11 | 780 | 0.00013989 | 1.9729e-06 | 70.9091
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 187 | 5566 | 567768 | 0.10111 | 0.00099119 | 102.0065
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 376 | 27096 | 4194787 | 0.74701 | 0.0048253 | 154.812
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 16 | 2195 | 106167 | 0.018906 | 0.00039089 | 48.3677
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | FUSE | 1 | 1 | 75 | 1.3451e-05 | 1.7935e-07 | 75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 75 | 5811 | 0.0010348 | 1.3356e-05 | 77.48
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 9 | 68 | 19274 | 0.0034323 | 1.2109e-05 | 283.4412
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 10 | 720 | 0.00012913 | 1.7935e-06 | 72
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CROSSARM | 1 | 119 | 15103 | 0.0027087 | 2.1343e-05 | 126.916
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 4 | 9 | 1064 | 0.00018948 | 1.6027e-06 | 118.2222
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 435 | 130284 | 0.023366 | 7.8017e-05 | 299.5034
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 2 | 39 | 2431 | 0.00044012 | 7.0608e-06 | 62.3333
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CABLE TERMINATOR | 1 | 1 | 52 | 9.3637e-06 | 1.8007e-07 | 52
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | NONE | 148 | 7854 | 1196210 | 0.21302 | 0.0013986 | 152.3058
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 20 | 209 | 24385 | 0.0043425 | 3.7219e-05 | 116.6746
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CUTOUT | 1 | 7 | 301 | 5.4202e-05 | 1.2605e-06 | 43
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | TRANSFORMER, OH | 1 | 7 | 1687 | 0.00030256 | 1.2555e-06 | 241
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | RECLOSER, LINE/OCR/BR | 1 | 697 | 36244 | 0.0065618 | 0.00012619 | 52
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | FUSE | 9 | 53 | 10330 | 0.0018836 | 9.6641e-06 | 194.9057
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 4 | 1912 | 0.00034864 | 7.2937e-07 | 478
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | SWITCH, OH | 5 | 3678 | 305274 | 0.055664 | 0.00067065 | 83
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 21 | 4686 | 0.00085445 | 3.8292e-06 | 223.1429
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 5 | 3208 | 407546 | 0.074313 | 0.00058495 | 127.0405
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CUTOUT | 1 | 16 | 1280 | 0.0002334 | 2.9175e-06 | 80
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 4 | 13 | 1878 | 0.00033443 | 2.315e-06 | 144.4615
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | NONE | 17 | 33 | 15061 | 0.0026821 | 5.8766e-06 | 456.3939
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 4 | 399 | 7.1054e-05 | 7.1232e-07 | 99.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, STATION SERVICE | 1 | 1 | 50 | 8.904e-06 | 1.7808e-07 | 50
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 14 | 44 | 20491 | 0.003649 | 7.8355e-06 | 465.7045
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | NONE | 2 | 8 | 3809 | 0.00067831 | 1.4246e-06 | 476.125
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | U | NONE | 1 | 912 | 9537 | 0.0016983 | 0.00016241 | 10.4572
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | TRANSFORMER, OH | 1 | 2 | 296 | 5.3301e-05 | 3.6014e-07 | 148
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 3 | 441 | 7.8533e-05 | 5.3424e-07 | 147
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | JUMPER/RISER | 4 | 208 | 78378 | 0.013958 | 3.7041e-05 | 376.8173
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 4 | 30 | 3422 | 0.00060939 | 5.3424e-06 | 114.0667
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | PEDESTAL | 1 | 1 | 165 | 2.9383e-05 | 1.7808e-07 | 165
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE | 2 | 8 | 1704 | 0.00030684 | 1.4406e-06 | 213
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | SWITCH, OH | 1 | 1 | 123 | 2.2269e-05 | 1.8105e-07 | 123
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | TRANSFORMER, OH | 1 | 8 | 1432 | 0.00026111 | 1.4587e-06 | 179
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CUTOUT | 1 | 75 | 5625 | 0.0010129 | 1.3505e-05 | 75
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 2 | 6 | 652 | 0.00011611 | 1.0685e-06 | 108.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 629 | 46546 | 0.0082889 | 0.00011201 | 74
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 2 | 1107 | 29889 | 0.0053226 | 0.00019713 | 27
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 464 | 14848 | 0.0026441 | 8.2629e-05 | 32
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | FUSE | 3 | 9 | 958 | 0.00017344 | 1.6294e-06 | 106.4444
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | FUSE | 60 | 601 | 48201 | 0.0087266 | 0.00010881 | 80.2013
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 1 | 97 | 1.7561e-05 | 1.8105e-07 | 97
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 2 | 38 | 24296 | 0.0043987 | 6.8798e-06 | 639.3684
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONN/CLAMP | 7 | 64 | 9884 | 0.0017895 | 1.1587e-05 | 154.4375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | FUSE | 79 | 1157 | 117954 | 0.021355 | 0.00020947 | 101.9481
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | NONE | 11 | 1214 | 503526 | 0.091162 | 0.00021979 | 414.7661
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | FUSE | 31 | 288 | 24984 | 0.0045233 | 5.2141e-05 | 86.75
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | NONE | 25 | 92 | 9116 | 0.0016504 | 1.6656e-05 | 99.087
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, OH | 13 | 38 | 15152 | 0.0027432 | 6.8798e-06 | 398.7368
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 7 | 6433 | 0.0011647 | 1.2673e-06 | 919
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 2914 | 327822 | 0.059776 | 0.00053134 | 112.499
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 1 | 8 | 312 | 5.6891e-05 | 1.4587e-06 | 39
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | SPLICE, OH | 1 | 3 | 468 | 8.4274e-05 | 5.4022e-07 | 156
AEP Total | 2022 | 5553337 | PARTIAL POWER | WI | NONE | 1 | 1 | 53 | 9.5438e-06 | 1.8007e-07 | 53
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 11 | 21 | 2212 | 0.00039391 | 3.7397e-06 | 105.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | SWITCH, OH | 9 | 603 | 74049 | 0.013187 | 0.00010738 | 122.801
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 52 | 4471 | 0.00079619 | 9.2601e-06 | 85.9808
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | ARRESTER | 10 | 32 | 2744 | 0.00048865 | 5.6986e-06 | 85.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 12 | 2173 | 531612 | 0.094669 | 0.00038697 | 244.6443
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 67 | 15007 | 0.0026724 | 1.1931e-05 | 223.9851
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 2 | 2 | 99 | 1.763e-05 | 3.5616e-07 | 49.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | POLE | 1 | 10 | 4300 | 0.0007785 | 1.8105e-06 | 430
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 12 | 838 | 0.00014923 | 2.137e-06 | 69.8333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | JUMPER/RISER | 1 | 4 | 612 | 0.00010898 | 7.1232e-07 | 153
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | U | NONE | 3 | 3267 | 476982 | 0.084941 | 0.00058179 | 146
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | SWITCH, OH | 4 | 122 | 9877 | 0.0017589 | 2.1726e-05 | 80.959
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | POLE | 2 | 49 | 10544 | 0.0018777 | 8.7259e-06 | 215.1837
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | NONE | 1 | 1 | 42 | 7.4794e-06 | 1.7808e-07 | 42
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | PEDESTAL | 1 | 1 | 174 | 3.0986e-05 | 1.7808e-07 | 174
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | SWITCH, OH | 1 | 3 | 795 | 0.00014157 | 5.3424e-07 | 265
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 4 | 561 | 9.9903e-05 | 7.1232e-07 | 140.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 2 | 7 | 2538 | 0.00046278 | 1.2764e-06 | 362.5714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1 | 49 | 8.8235e-06 | 1.8007e-07 | 49
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 1 | 98 | 1.7647e-05 | 1.8007e-07 | 98
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 4 | 428 | 7.6762e-05 | 7.174e-07 | 107
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 1 | 17 | 6970 | 0.0012551 | 3.0612e-06 | 410
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 687 | 57013 | 0.010266 | 0.00012371 | 82.9884
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 12 | 3501 | 0.00062346 | 2.137e-06 | 291.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 105 | 19845 | 0.003534 | 1.8698e-05 | 189
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 74 | 1.3325e-05 | 1.8007e-07 | 74
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 37 | 8066 | 0.0014525 | 6.6627e-06 | 218
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 3 | 321 | 5.7803e-05 | 5.4022e-07 | 107
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 3 | 1125 | 0.00020034 | 5.3424e-07 | 375
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 6 | 1046 | 138676 | 0.024695 | 0.00018627 | 132.5774
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 4 | 14 | 14856 | 0.0026456 | 2.4931e-06 | 1061.1429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 45 | 9558 | 0.0017021 | 8.0136e-06 | 212.4
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | OTHER EQUIPMENT | 1 | 5 | 295 | 5.2534e-05 | 8.904e-07 | 59
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | ARRESTER | 1 | 6 | 792 | 0.00014262 | 1.0804e-06 | 132
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CAPACITOR | 1 | 1 | 90 | 1.6411e-05 | 1.8234e-07 | 90
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | SWITCH, OH | 1 | 3 | 96 | 1.738e-05 | 5.4314e-07 | 32
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 1 | 251 | 4.5768e-05 | 1.8234e-07 | 251
AEP Total | 2025 | 5615460 | PARTIAL POWER | WL | METERING | 1 | 2 | 230 | 4.0958e-05 | 3.5616e-07 | 115
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1 | 7 | 553 | 9.9181e-05 | 1.2555e-06 | 79
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | JUMPER/RISER | 1 | 1 | 159 | 2.8786e-05 | 1.8105e-07 | 159
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 796 | 125760 | 0.022768 | 0.00014411 | 157.9899
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | FUSE | 2 | 7 | 610 | 0.00011044 | 1.2673e-06 | 87.1429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | JUMPER/RISER | 2 | 158 | 12405 | 0.0022459 | 2.8605e-05 | 78.5127
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | NONE | 2127 | 58849 | 9610193 | 1.7305 | 0.010597 | 163.3026
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | POLE | 6 | 388 | 140891 | 0.025371 | 6.9868e-05 | 363.1211
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | NONE | 2388 | 63228 | 7409625 | 1.3289 | 0.01134 | 117.189
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | NONE | 764 | 38458 | 3324613 | 0.59627 | 0.0068975 | 86.4479
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | NONE | 16 | 50 | 7466 | 0.0013444 | 9.0036e-06 | 149.32
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 6 | 348 | 6.2665e-05 | 1.0804e-06 | 58
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 4 | 120 | 78411 | 0.01412 | 2.1609e-05 | 653.425
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | TIR | NONE | 4 | 921 | 50542 | 0.0091012 | 0.00016585 | 54.8773
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | ARRESTER | 6 | 12 | 965 | 0.00017377 | 2.1609e-06 | 80.4167
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | NONE | 4 | 351 | 12508 | 0.0022645 | 6.3547e-05 | 35.6353
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 6 | 336 | 6.0832e-05 | 1.0863e-06 | 56
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 447 | 123757 | 0.022406 | 8.0928e-05 | 276.8613
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | SWITCH, UG | 1 | 29 | 1740 | 0.00031502 | 5.2503e-06 | 60
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | FUSE | 1 | 8 | 968 | 0.00017525 | 1.4484e-06 | 121
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | NONE | 1974 | 29522 | 1935053 | 0.35284 | 0.0053831 | 65.5461
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONN/CLAMP | 24 | 48 | 3747 | 0.00068324 | 8.7524e-06 | 78.0625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 38 | 1765 | 525099 | 0.095748 | 0.00032183 | 297.5065
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | SWITCH, OH | 5 | 388 | 50466 | 0.0092021 | 7.0749e-05 | 130.067
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | TRANSFORMER, OH | 9 | 23 | 3531 | 0.00064385 | 4.1939e-06 | 153.5217
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 49 | 5045 | 476401 | 0.086868 | 0.00091992 | 94.4303
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 20 | 85 | 12157 | 0.0022167 | 1.5499e-05 | 143.0235
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 3850 | 308134 | 0.056186 | 0.00070202 | 80.0348
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 5 | 87 | 28375 | 0.005174 | 1.5864e-05 | 326.1494
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | NONE | 17 | 49 | 8213 | 0.0014976 | 8.9348e-06 | 167.6122
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 4 | 14 | 3173 | 0.00057857 | 2.5528e-06 | 226.6429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | SWITCH, OH | 2 | 92 | 18064 | 0.0032938 | 1.6775e-05 | 196.3478
AEP Total | 2020 | 5484199 | PARTIAL POWER | WI | NONE | 1 | 1 | 47 | 8.5701e-06 | 1.8234e-07 | 47
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 3 | 8 | 896 | 0.00016338 | 1.4587e-06 | 112
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | JUMPER/RISER | 2 | 4 | 533 | 9.7188e-05 | 7.2937e-07 | 133.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 3 | 89 | 50334 | 0.009178 | 1.6228e-05 | 565.5506
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 3 | 5 | 1005 | 0.00018325 | 9.1171e-07 | 201
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 39 | 3144 | 536272 | 0.096181 | 0.00056388 | 170.57
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 853 | 26689 | 0.0047867 | 0.00015299 | 31.2884
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 1 | 6 | 1200 | 0.00021609 | 1.0804e-06 | 200
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 13 | 820 | 128992 | 0.023135 | 0.00014707 | 157.3073
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | FUSE | 83 | 714 | 66850 | 0.01199 | 0.00012806 | 93.6275
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 21 | 5203 | 795189 | 0.14262 | 0.00093316 | 152.8328
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 5 | 2260 | 0.00040696 | 9.0036e-07 | 452
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | SWITCH, OH | 2 | 64 | 5208 | 0.00093781 | 1.1525e-05 | 81.375
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, POWER - NON LTC | 1 | 10 | 2040 | 0.00036735 | 1.8007e-06 | 204
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 1 | 425 | 7.6224e-05 | 1.7935e-07 | 425
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 906 | 151438 | 0.02727 | 0.00016315 | 167.1501
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CUTOUT | 5 | 126 | 27511 | 0.0049341 | 2.2598e-05 | 218.3413
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | NONE | 83 | 6406 | 538167 | 0.095837 | 0.0011408 | 84.0098
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 3 | 696 | 166116 | 0.029582 | 0.00012394 | 238.6724
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 226 | 6984 | 1117359 | 0.19898 | 0.0012437 | 159.9884
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 50 | 1196 | 287577 | 0.051212 | 0.00021298 | 240.449
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | NONE | 42 | 249 | 35530 | 0.0063272 | 4.4342e-05 | 142.6908
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONN/CLAMP | 10 | 26 | 1941 | 0.00034565 | 4.6301e-06 | 74.6538
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 18 | 2509 | 0.00044999 | 3.2283e-06 | 139.3889
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 2 | 4 | 2396 | 0.00042668 | 7.1232e-07 | 599
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 139 | 934 | 238491 | 0.04247 | 0.00016633 | 255.3437
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 210 | 3.7664e-05 | 1.7935e-07 | 210
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 17 | 668 | 81017 | 0.014427 | 0.00011896 | 121.2829
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | NONE | 15 | 41 | 4635 | 0.0008254 | 7.3013e-06 | 113.0488
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 10 | 1000 | 130663 | 0.023268 | 0.00017808 | 130.663
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | POLE | 8 | 1209 | 113536 | 0.020218 | 0.0002153 | 93.909
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 22 | 735 | 40158 | 0.0071513 | 0.00013089 | 54.6367
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 4 | 33 | 5105 | 0.00091558 | 5.9186e-06 | 154.697
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | TRANSFORMER, POWER - LTC | 1 | 22 | 6448 | 0.0011565 | 3.9457e-06 | 293.0909
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | U | NONE | 7 | 4109 | 196192 | 0.03552 | 0.00074392 | 47.7469
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 3 | 33 | 5.9745e-06 | 5.4314e-07 | 11
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 31 | 561 | 43199 | 0.0076929 | 9.9903e-05 | 77.0036
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 125 | 2126 | 288016 | 0.05129 | 0.0003786 | 135.4732
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 7 | 1401 | 35480 | 0.0063183 | 0.00024949 | 25.3248
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 31 | 2301 | 293904 | 0.052338 | 0.00040976 | 127.7288
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 8 | 8188 | 0.0014685 | 1.4348e-06 | 1023.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 1 | 365 | 6.5463e-05 | 1.7935e-07 | 365
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | METERING | 1 | 1 | 122 | 2.1881e-05 | 1.7935e-07 | 122
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | CO | SWITCH, OH | 4 | 4055 | 621383 | 0.1125 | 0.00073414 | 153.2387
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CUTOUT | 2 | 239 | 25685 | 0.0046502 | 4.327e-05 | 107.4686
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 141 | 1542 | 356424 | 0.064529 | 0.00027917 | 231.144
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 15 | 217 | 55765 | 0.010096 | 3.9287e-05 | 256.9816
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 3 | 234 | 4.2365e-05 | 5.4314e-07 | 78
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | NONE | 3 | 11 | 1162 | 0.00021038 | 1.9915e-06 | 105.6364
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | FUSE | 4 | 5 | 266 | 4.8158e-05 | 9.0523e-07 | 53.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SWITCH, OH | 4 | 81 | 11223 | 0.0020319 | 1.4665e-05 | 138.5556
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | NONE | 10 | 10222 | 1467674 | 0.26572 | 0.0018507 | 143.5799
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | BREAKER | 5 | 1624 | 83611 | 0.015137 | 0.00029402 | 51.4846
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 21 | 193 | 30239 | 0.0054747 | 3.4942e-05 | 156.6788
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | NONE | 3 | 459 | 70686 | 0.012797 | 8.31e-05 | 154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 9 | 2003 | 332248 | 0.060152 | 0.00036264 | 165.8752
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | POLE | 3 | 5 | 1624 | 0.00029402 | 9.0523e-07 | 324.8
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CUTOUT | 5 | 85 | 19494 | 0.0035293 | 1.5389e-05 | 229.3412
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 2 | 404 | 7.3143e-05 | 3.6209e-07 | 202
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | TRANSFORMER, OH | 8 | 36 | 6902 | 0.0012496 | 6.5177e-06 | 191.7222
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | REGULATOR | 2 | 270 | 46691 | 0.0084532 | 4.8883e-05 | 172.9296
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 7 | 117 | 14181 | 0.0025674 | 2.1182e-05 | 121.2051
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONN/CLAMP | 1 | 1 | 40 | 7.2419e-06 | 1.8105e-07 | 40
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 32 | 5384 | 0.00097475 | 5.7935e-06 | 168.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 80 | 5280 | 0.00095592 | 1.4484e-05 | 66
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 1761 | 10566 | 0.0019129 | 0.00031882 | 6
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 13 | 1233 | 0.00022323 | 2.3536e-06 | 94.8462
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | TRANSFORMER, OH | 1 | 4 | 1696 | 0.00030705 | 7.2419e-07 | 424
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | POLE | 3 | 46 | 2722 | 0.00049281 | 8.3281e-06 | 59.1739
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 5 | 674 | 0.00012203 | 9.0523e-07 | 134.8
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 23 | 78 | 10006 | 0.0018245 | 1.4223e-05 | 128.2821
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 37 | 1820 | 627999 | 0.11451 | 0.00033186 | 345.0544
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | CONDUCTOR UG | 1 | 1 | 227 | 4.1392e-05 | 1.8234e-07 | 227
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | FUSE | 33 | 280 | 30176 | 0.0055024 | 5.1056e-05 | 107.7714
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | ARRESTER | 7 | 7 | 388 | 7.0749e-05 | 1.2764e-06 | 55.4286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 10 | 105 | 42604 | 0.0077685 | 1.9146e-05 | 405.7524
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | ARRESTER | 22 | 282 | 58457 | 0.010659 | 5.142e-05 | 207.2943
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 3 | 108 | 1.9693e-05 | 5.4703e-07 | 36
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 1 | 226 | 42712 | 0.0077882 | 4.1209e-05 | 188.9912
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 215 | 14269 | 1722135 | 0.31011 | 0.0025694 | 120.6907
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 16 | 2128 | 341486 | 0.061492 | 0.00038319 | 160.4727
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 7 | 545 | 128022 | 0.023053 | 9.8139e-05 | 234.9028
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, UG | 6 | 1402 | 40184 | 0.007236 | 0.00025246 | 28.6619
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR UG | 4 | 84 | 15627 | 0.0028292 | 1.5208e-05 | 186.0357
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 286 | 21201 | 0.0038658 | 5.215e-05 | 74.1294
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 12 | 780 | 0.00014223 | 2.1881e-06 | 65
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 2 | 106 | 1.9191e-05 | 3.6209e-07 | 53
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | POLE | 1 | 1 | 161 | 2.9148e-05 | 1.8105e-07 | 161
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | SWITCH, OH | 3 | 1310 | 173686 | 0.031276 | 0.00023589 | 132.5847
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | FUSE | 1 | 1 | 104 | 1.852e-05 | 1.7808e-07 | 104
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 14 | 2386 | 275006 | 0.048973 | 0.0004249 | 115.2582
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AB | NONE | 6 | 4267 | 503426 | 0.08965 | 0.00075987 | 117.9813
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 8 | 3316 | 0.00059051 | 1.4246e-06 | 414.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 1 | 109 | 1.9411e-05 | 1.7808e-07 | 109
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 4 | 10 | 5013 | 0.00089271 | 1.7808e-06 | 501.3
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | SWITCH, UG | 1 | 39 | 1716 | 0.00030558 | 6.9451e-06 | 44
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 3 | 37 | 10058 | 0.0017911 | 6.589e-06 | 271.8378
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | TRANSFORMER, OH | 4 | 18 | 3236 | 0.00057627 | 3.2054e-06 | 179.7778
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | JUMPER/RISER | 3 | 61 | 4719 | 0.00084036 | 1.0863e-05 | 77.3607
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | BREAKER | 2 | 62 | 1283 | 0.00022848 | 1.1041e-05 | 20.6935
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 30 | 1893 | 93112 | 0.016581 | 0.00033711 | 49.1875
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | METERING | 3 | 148 | 17918 | 0.0031908 | 2.6356e-05 | 121.0676
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 294 | 324209 | 0.057735 | 5.2355e-05 | 1102.7517
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 120 | 39360 | 0.0070092 | 2.137e-05 | 328
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 8 | 2064 | 0.00036756 | 1.4246e-06 | 258
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 102 | 1.8164e-05 | 1.7808e-07 | 102
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 2 | 263 | 4.6835e-05 | 3.5616e-07 | 131.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | ARRESTER | 1 | 45 | 1845 | 0.00032856 | 8.0136e-06 | 41
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 9 | 492 | 8.7615e-05 | 1.6027e-06 | 54.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 69 | 8625 | 0.0015615 | 1.2492e-05 | 125
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CUTOUT | 1 | 2 | 224 | 4.0554e-05 | 3.6209e-07 | 112
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | FUSE | 1 | 1 | 55 | 9.9576e-06 | 1.8105e-07 | 55
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | ARRESTER | 1 | 2 | 80 | 1.4484e-05 | 3.6209e-07 | 40
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | EQF | POLE | 1 | 2 | 810 | 0.00014586 | 3.6014e-07 | 405
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WU | NONE | 1 | 1 | 105 | 1.8908e-05 | 1.8007e-07 | 105
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CABLE TERMINATOR | 1 | 116 | 17671 | 0.0031468 | 2.0657e-05 | 152.3362
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 1 | 73 | 1.3e-05 | 1.7808e-07 | 73
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | NONE | 2 | 539 | 61113 | 0.010883 | 9.5985e-05 | 113.3822
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 120 | 9480 | 0.0016882 | 2.137e-05 | 79
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE | 3 | 5 | 1628 | 0.00028991 | 8.904e-07 | 325.6
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | NONE | 3 | 32 | 4088 | 0.00072799 | 5.6986e-06 | 127.75
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONN/CLAMP | 1 | 3 | 237 | 4.3215e-05 | 5.4703e-07 | 79
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | STATIC WIRE | 4 | 132 | 6060 | 0.0010792 | 2.3507e-05 | 45.9091
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 3 | 258 | 4.5945e-05 | 5.3424e-07 | 86
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 1 | 8 | 1344 | 0.00023934 | 1.4246e-06 | 168
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CONN/CLAMP | 1 | 2 | 544 | 9.7959e-05 | 3.6014e-07 | 272
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | POLE | 2 | 2 | 428 | 7.8042e-05 | 3.6468e-07 | 214
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 1 | 57 | 1.0264e-05 | 1.8007e-07 | 57
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONN/CLAMP | 8 | 82 | 14521 | 0.002629 | 1.4846e-05 | 177.0854
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 1 | 108 | 1.9553e-05 | 1.8105e-07 | 108
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | NONE | 11 | 956 | 170370 | 0.030845 | 0.00017308 | 178.2113
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 2 | 33 | 10104 | 0.0018293 | 5.9745e-06 | 306.1818
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 44 | 113 | 16202 | 0.0029333 | 2.0458e-05 | 143.3805
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 367 | 6.6444e-05 | 1.8105e-07 | 367
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 2 | 7 | 1090 | 0.00019734 | 1.2673e-06 | 155.7143
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | BREAKER | 7 | 2535 | 105488 | 0.019098 | 0.00045895 | 41.6126
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | NONE | 2 | 6 | 1351 | 0.00024459 | 1.0863e-06 | 225.1667
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | POLE | 1 | 5 | 1195 | 0.00021635 | 9.0523e-07 | 239
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONN/CLAMP | 2 | 5 | 2002 | 0.00036245 | 9.0523e-07 | 400.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | METERING | 2 | 5 | 1158 | 0.00020965 | 9.0523e-07 | 231.6
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | ARRESTER | 1 | 4 | 558 | 0.00010102 | 7.2419e-07 | 139.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 1 | 813 | 0.00014719 | 1.8105e-07 | 813
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 6 | 351 | 6.4002e-05 | 1.0941e-06 | 58.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | NONE | 371 | 18322 | 2574919 | 0.46952 | 0.0033409 | 140.537
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONN/CLAMP | 28 | 114 | 11703 | 0.0021339 | 2.0787e-05 | 102.6579
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | NONE | 48 | 128 | 16266 | 0.002966 | 2.334e-05 | 127.0781
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | NONE | 50 | 2868 | 237517 | 0.043309 | 0.00052296 | 82.8162
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | NONE | 84 | 180 | 22859 | 0.0041682 | 3.2822e-05 | 126.9944
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | ARRESTER | 69 | 3792 | 313220 | 0.057113 | 0.00069144 | 82.6002
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | FUSE | 101 | 1701 | 297105 | 0.054175 | 0.00031016 | 174.6649
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 13 | 1592 | 102969 | 0.018776 | 0.00029029 | 64.679
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | FUSE | 29 | 285 | 71008 | 0.012787 | 5.132e-05 | 249.1509
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 148 | 2354 | 455733 | 0.082065 | 0.00042389 | 193.5994
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | NONE | 66 | 4107 | 527123 | 0.09492 | 0.00073956 | 128.3475
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | NONE | 1782 | 18506 | 1433797 | 0.25715 | 0.0033191 | 77.4774
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABI | NONE | 3 | 2894 | 343269 | 0.061813 | 0.00052113 | 118.614
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 20 | 2981 | 400470 | 0.072113 | 0.00053679 | 134.3408
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CUTOUT | 8 | 64 | 13015 | 0.0023436 | 1.1525e-05 | 203.3594
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | FUSE | 14 | 46 | 4179 | 0.0007495 | 8.2501e-06 | 90.8478
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | NONE | 551 | 6835 | 1230506 | 0.22069 | 0.0012259 | 180.0301
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | NONE | 7 | 15 | 1797 | 0.00032359 | 2.7011e-06 | 119.8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE | 44 | 3076 | 740617 | 0.13283 | 0.00055168 | 240.7728
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 1327 | 97470 | 0.017552 | 0.00023896 | 73.4514
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | NONE | 23 | 58 | 7073 | 0.0012685 | 1.0402e-05 | 121.9483
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | NONE | 12 | 2587 | 543806 | 0.097924 | 0.00046585 | 210.2072
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CUTOUT | 12 | 187 | 30817 | 0.005527 | 3.3538e-05 | 164.7968
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 82 | 18040 | 0.0032485 | 1.4766e-05 | 220
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 1700 | 222700 | 0.039941 | 0.0003049 | 131
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 28 | 1265 | 203950 | 0.036578 | 0.00022688 | 161.2253
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CAPACITOR | 1 | 2 | 28 | 5.042e-06 | 3.6014e-07 | 14
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR UG | 3 | 19 | 5523 | 0.00099055 | 3.4077e-06 | 290.6842
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 5 | 30 | 4378 | 0.0007852 | 5.3805e-06 | 145.9333
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | FUSE | 2 | 20 | 2440 | 0.00043761 | 3.587e-06 | 122
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | FUSE | 1 | 1 | 53 | 9.5056e-06 | 1.7935e-07 | 53
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | NONE | 654 | 35392 | 3836770 | 0.68325 | 0.0063026 | 108.4078
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | NONE | 14 | 55 | 8689 | 0.0015473 | 9.7944e-06 | 157.9818
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 26 | 2298 | 458223 | 0.0816 | 0.00040923 | 199.4008
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 9 | 13 | 2708 | 0.00048224 | 2.315e-06 | 208.3077
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 12 | 2357 | 183667 | 0.032707 | 0.00041973 | 77.9241
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 7 | 78 | 21325 | 0.0037976 | 1.389e-05 | 273.3974
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SWITCH, OH | 2 | 24 | 2005 | 0.00035705 | 4.2739e-06 | 83.5417
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | TRANSFORMER, OH | 2 | 11 | 2215 | 0.00039445 | 1.9589e-06 | 201.3636
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | OTHER EQUIPMENT | 1 | 11 | 1749 | 0.00031368 | 1.9729e-06 | 159
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 4 | 420 | 7.5327e-05 | 7.174e-07 | 105
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 3 | 7 | 771 | 0.00013959 | 1.2673e-06 | 110.1429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 16 | 1680 | 0.00030633 | 2.9175e-06 | 105
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | JUMPER/RISER | 9 | 1950 | 191186 | 0.034861 | 0.00035557 | 98.0441
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | SECTIONALIZER | 1 | 8 | 8968 | 0.0016352 | 1.4587e-06 | 1121
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | TRANSFORMER, OH | 7 | 35 | 8413 | 0.0015149 | 6.3025e-06 | 240.3714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | FUSE | 17 | 503 | 57043 | 0.010272 | 9.0576e-05 | 113.4056
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 12 | 129 | 92009 | 0.016568 | 2.3229e-05 | 713.2481
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONN/CLAMP | 49 | 137 | 11966 | 0.0021547 | 2.467e-05 | 87.3431
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 3 | 71 | 21361 | 0.0038465 | 1.2785e-05 | 300.8592
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | METERING | 6 | 10 | 721 | 0.00012983 | 1.8007e-06 | 72.1
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | JUMPER/RISER | 5 | 42 | 6967 | 0.0012546 | 7.563e-06 | 165.881
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | INSULATOR | 3 | 234 | 36793 | 0.0066254 | 4.2137e-05 | 157.235
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | SPLICE, OH | 2 | 9 | 2439 | 0.0004392 | 1.6206e-06 | 271
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 64 | 10513 | 0.0018931 | 1.1525e-05 | 164.2656
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, UG | 1 | 4 | 1496 | 0.00026939 | 7.2029e-07 | 374
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 5 | 15 | 2936 | 0.00052657 | 2.6903e-06 | 195.7333
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 46 | 8.2501e-06 | 1.7935e-07 | 46
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WU | CONDUCTOR OVERHEAD | 1 | 14 | 4704 | 0.00084706 | 2.521e-06 | 336
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 16 | 2509 | 0.00044999 | 2.8696e-06 | 156.8125
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONN/CLAMP | 1 | 5 | 340 | 6.1996e-05 | 9.1171e-07 | 68
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | FUSE | 4 | 42 | 2589 | 0.00047208 | 7.6584e-06 | 61.6429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 1 | 22 | 3960 | 0.00072207 | 4.0115e-06 | 180
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE | 7 | 959 | 60213 | 0.010979 | 0.00017487 | 62.7873
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | FUSE | 4 | 11 | 1511 | 0.00027552 | 2.0058e-06 | 137.3636
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | SWITCH, UG | 1 | 3 | 297 | 5.4156e-05 | 5.4703e-07 | 99
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ERF | NONE | 5 | 4247 | 227534 | 0.041489 | 0.00077441 | 53.5752
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 7 | 1252 | 0.00022829 | 1.2764e-06 | 178.8571
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | SWITCH, UG | 1 | 17 | 2295 | 0.00041847 | 3.0998e-06 | 135
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 5 | 12 | 2121 | 0.00038675 | 2.1881e-06 | 176.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 5 | 14 | 2581 | 0.0004629 | 2.5109e-06 | 184.3571
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 716 | 42170 | 5272696 | 0.93896 | 0.0075096 | 125.0343
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 12 | 148 | 60090 | 0.010777 | 2.6544e-05 | 406.0135
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | FUSE | 1 | 15 | 2160 | 0.0003874 | 2.6903e-06 | 144
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 4 | 4 | 540 | 9.6849e-05 | 7.174e-07 | 135
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | FUSE | 2 | 19 | 10723 | 0.0019309 | 3.4214e-06 | 564.3684
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 6 | 370 | 6.636e-05 | 1.0761e-06 | 61.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 10 | 458 | 8.2142e-05 | 1.7935e-06 | 45.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 63 | 3429 | 662016 | 0.11789 | 0.00061064 | 193.0639
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | NONE | 104 | 5300 | 569073 | 0.10134 | 0.00094382 | 107.3723
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | ARRESTER | 6 | 83 | 14399 | 0.0026255 | 1.5134e-05 | 173.4819
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 818 | 15542 | 0.002834 | 0.00014916 | 19
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, POWER - LTC | 1 | 2 | 424 | 7.6044e-05 | 3.587e-07 | 212
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 542 | 35530 | 0.0063723 | 9.7208e-05 | 65.5535
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | BREAKER | 1 | 1 | 165 | 2.9593e-05 | 1.7935e-07 | 165
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 6 | 900 | 0.00016206 | 1.0804e-06 | 150
AEP Total | 2021 | 5523447 | DISTRIBUTION SOURCE | AF | NONE | 1 | 53 | 3869 | 0.00070047 | 9.5955e-06 | 73
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 42 | 6031 | 256992 | 0.045765 | 0.001074 | 42.6118
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 78 | 5004 | 858410 | 0.15287 | 0.00089111 | 171.5448
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 54 | 1116 | 174259 | 0.031032 | 0.00019874 | 156.1461
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 5 | 27 | 1865 | 0.00033212 | 4.8082e-06 | 69.0741
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 2 | 21 | 906 | 0.00016134 | 3.7397e-06 | 43.1429
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 12 | 35 | 6560 | 0.0011682 | 6.2328e-06 | 187.4286
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 22 | 10144 | 0.0018064 | 3.9178e-06 | 461.0909
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 4 | 524 | 9.3314e-05 | 7.1232e-07 | 131
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | FUSE | 12 | 74 | 5154 | 0.00091782 | 1.3178e-05 | 69.6486
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | FUSE | 12 | 166 | 13852 | 0.0024668 | 2.9561e-05 | 83.4458
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 6 | 70 | 9618 | 0.0017128 | 1.2466e-05 | 137.4
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 3 | 44 | 10498 | 0.0018695 | 7.8355e-06 | 238.5909
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CUTOUT | 1 | 3 | 687 | 0.00012321 | 5.3805e-07 | 229
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 4 | 936 | 136497 | 0.024307 | 0.00016668 | 145.8301
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 1824 | 224368 | 0.04024 | 0.00032713 | 123.0088
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | NONE | 5 | 14 | 776 | 0.0001415 | 2.5528e-06 | 55.4286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | NONE | 15 | 402 | 354186 | 0.064583 | 7.3301e-05 | 881.0597
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CAPACITOR | 1 | 51 | 62016 | 0.011228 | 9.2334e-06 | 1216
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 728 | 98472 | 0.017536 | 0.00012964 | 135.2637
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONN/CLAMP | 8 | 60 | 4139 | 0.00073707 | 1.0685e-05 | 68.9833
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | NONE | 2 | 1423 | 751017 | 0.13374 | 0.00025341 | 527.7702
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 8 | 400 | 7.1232e-05 | 1.4246e-06 | 50
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 124 | 21232 | 0.003781 | 2.2082e-05 | 171.2258
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | NONE | 2 | 3 | 222 | 3.9534e-05 | 5.3424e-07 | 74
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | METERING | 1 | 5 | 540 | 9.6163e-05 | 8.904e-07 | 108
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | FUSE | 1 | 1 | 234 | 4.1671e-05 | 1.7808e-07 | 234
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | ARRESTER | 1 | 8 | 432 | 7.693e-05 | 1.4246e-06 | 54
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | BREAKER | 3 | 1102 | 65133 | 0.011599 | 0.00019624 | 59.1044
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | POLE | 1 | 122 | 18666 | 0.0033612 | 2.1969e-05 | 153
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 1915 | 78515 | 0.013982 | 0.00034102 | 41
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 3 | 70 | 10193 | 0.0018152 | 1.2466e-05 | 145.6143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | POLE | 4 | 43 | 5832 | 0.0010386 | 7.6574e-06 | 135.6279
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | SWITCH, OH | 3 | 2036 | 245947 | 0.044111 | 0.00036516 | 120.7991
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 4 | 164 | 2.9205e-05 | 7.1232e-07 | 41
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, UG | 2 | 15 | 8239 | 0.0014777 | 2.6903e-06 | 549.2667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 10 | 178 | 47869 | 0.0085245 | 3.1698e-05 | 268.927
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 12 | 194 | 60200 | 0.01072 | 3.4547e-05 | 310.3093
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | TRANSFORMER, OH | 1 | 1 | 318 | 5.7033e-05 | 1.7935e-07 | 318
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CABLE TERMINATOR | 1 | 4 | 388 | 6.9868e-05 | 7.2029e-07 | 97
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CUTOUT | 3 | 942 | 65953 | 0.011941 | 0.00017055 | 70.0138
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | NONE | 369 | 5903 | 709591 | 0.12636 | 0.0010512 | 120.2085
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | FUSE | 1 | 1 | 120 | 2.1881e-05 | 1.8234e-07 | 120
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | NONE | 5 | 1317 | 207428 | 0.037823 | 0.00024014 | 157.5004
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 4 | 48 | 13885 | 0.0025318 | 8.7524e-06 | 289.2708
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 267 | 2937 | 0.00053554 | 4.8685e-05 | 11
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 4 | 652 | 0.00011804 | 7.2419e-07 | 163
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 316 | 74576 | 0.013502 | 5.7211e-05 | 236
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 154 | 11242 | 0.0020499 | 2.8081e-05 | 73
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 1 | 9 | 2259 | 0.00040678 | 1.6206e-06 | 251
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1475 | 185029 | 0.033499 | 0.00026704 | 125.4434
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 1 | 191 | 3.4013e-05 | 1.7808e-07 | 191
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 11 | 501 | 58434 | 0.010406 | 8.9218e-05 | 116.6347
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 15 | 65 | 15693 | 0.0027946 | 1.1575e-05 | 241.4308
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR UG | 2 | 4 | 412 | 7.3369e-05 | 7.1232e-07 | 103
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | NONE | 6 | 34 | 2165 | 0.00038554 | 6.0547e-06 | 63.6765
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 94 | 19620 | 0.0034939 | 1.674e-05 | 208.7234
AEP Total | 2024 | 5615460 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 5 | 2920 | 0.00051999 | 8.904e-07 | 584
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 4 | 10 | 632 | 0.00011255 | 1.7808e-06 | 63.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 4 | 380 | 6.767e-05 | 7.1232e-07 | 95
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 1 | 65 | 1.1575e-05 | 1.7808e-07 | 65
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 2 | 6 | 1938 | 0.00034512 | 1.0685e-06 | 323
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 4 | 603 | 45137 | 0.008038 | 0.00010738 | 74.8541
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 4 | 16 | 1029 | 0.00018324 | 2.8493e-06 | 64.3125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | JUMPER/RISER | 2 | 480 | 74804 | 0.013321 | 8.5478e-05 | 155.8417
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | NONE | 3 | 984 | 25749 | 0.0045854 | 0.00017523 | 26.1677
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | POLE HARDWARE | 1 | 9 | 729 | 0.00012982 | 1.6027e-06 | 81
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1 | 160 | 2.8812e-05 | 1.8007e-07 | 160
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | SWITCH, OH | 2 | 3 | 275 | 4.952e-05 | 5.4022e-07 | 91.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WU | NONE | 1 | 52 | 2600 | 0.00046819 | 9.3637e-06 | 50
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | TRANSFORMER, OH | 1 | 1 | 754 | 0.00013577 | 1.8007e-07 | 754
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | FUSE | 1 | 1 | 1157 | 0.00020751 | 1.7935e-07 | 1157
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 20 | 3900 | 0.00069947 | 3.587e-06 | 195
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | NETWORK LIMITER | 1 | 13 | 11609 | 0.0020905 | 2.3409e-06 | 893
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 2 | 210 | 42860 | 0.0076325 | 3.7397e-05 | 204.0952
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | ARRESTER | 1 | 3 | 162 | 2.8849e-05 | 5.3424e-07 | 54
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 2 | 7 | 3003 | 0.00053477 | 1.2466e-06 | 429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 270 | 4.8082e-05 | 1.7808e-07 | 270
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | SWITCH, OH | 2 | 1484 | 437170 | 0.077851 | 0.00026427 | 294.5889
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 23 | 2536 | 0.00045161 | 4.0958e-06 | 110.2609
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 31 | 6262 | 0.0011151 | 5.5205e-06 | 202
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SWITCH, OH | 1 | 5 | 875 | 0.00015582 | 8.904e-07 | 175
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 1 | 2 | 206 | 3.6684e-05 | 3.5616e-07 | 103
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 55 | 9.8643e-06 | 1.7935e-07 | 55
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 6 | 1554 | 0.00027871 | 1.0761e-06 | 259
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CAPACITOR | 1 | 68 | 5712 | 0.0010244 | 1.2196e-05 | 84
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 92 | 8556 | 0.001549 | 1.6656e-05 | 93
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | GUY/ANCHOR | 1 | 2 | 316 | 5.6273e-05 | 3.5616e-07 | 158
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | JUMPER/RISER | 1 | 39 | 2964 | 0.00052783 | 6.9451e-06 | 76
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | ARRESTER | 1 | 2 | 96 | 1.7096e-05 | 3.5616e-07 | 48
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | NONE | 3822 | 184101 | 25616800 | 4.6378 | 0.033331 | 139.1454
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | NONE | 111 | 10955 | 1337173 | 0.24209 | 0.0019834 | 122.0605
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 285 | 11399 | 2820138 | 0.51058 | 0.0020637 | 247.4022
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 10 | 1275 | 165123 | 0.029895 | 0.00023083 | 129.5082
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE | 47 | 2931 | 1803965 | 0.3266 | 0.00053065 | 615.4777
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CUTOUT | 13 | 277 | 51133 | 0.0092574 | 5.015e-05 | 184.5957
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CUTOUT | 2 | 2 | 511 | 9.2515e-05 | 3.6209e-07 | 255.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | FUSE | 19 | 268 | 21932 | 0.0039707 | 4.852e-05 | 81.8358
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SWITCH, OH | 5 | 32 | 2761 | 0.00049987 | 5.7935e-06 | 86.2812
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 9 | 3291 | 0.00059582 | 1.6294e-06 | 365.6667
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 2 | 20 | 2626 | 0.00047543 | 3.6209e-06 | 131.3
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | NONE | 148 | 16846 | 2151591 | 0.38744 | 0.0030335 | 127.7212
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | ARRESTER | 9 | 323 | 25609 | 0.0046115 | 5.8163e-05 | 79.2848
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE | 136 | 11452 | 1925337 | 0.3467 | 0.0020622 | 168.1223
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | TRANSFORMER, OH | 2 | 4 | 1062 | 0.00019227 | 7.2419e-07 | 265.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | JUMPER/RISER | 1 | 358 | 43318 | 0.0078426 | 6.4815e-05 | 121
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | ARRESTER | 3 | 8 | 1352 | 0.00024477 | 1.4484e-06 | 169
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | POLE HARDWARE | 1 | 24 | 2952 | 0.00053445 | 4.3451e-06 | 123
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, STATION SERVICE | 1 | 4 | 376 | 6.8073e-05 | 7.2419e-07 | 94
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONN/CLAMP | 4 | 22 | 4009 | 0.00072191 | 3.9616e-06 | 182.2273
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 18 | 1944 | 0.00034619 | 3.2054e-06 | 108
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | TOR | NONE | 1 | 469 | 62846 | 0.011271 | 8.4115e-05 | 134
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | ARRESTER | 3 | 427 | 126329 | 0.022657 | 7.6583e-05 | 295.8525
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 5 | 875 | 0.00015693 | 8.9675e-07 | 175
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | SWITCH, OH | 1 | 6 | 318 | 5.7033e-05 | 1.0761e-06 | 53
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | METERING | 1 | 1 | 185 | 3.318e-05 | 1.7935e-07 | 185
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 1 | 46 | 8.3877e-06 | 1.8234e-07 | 46
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | ARRESTER | 1 | 5 | 295 | 5.3121e-05 | 9.0036e-07 | 59
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | SWITCH, OH | 1 | 2 | 230 | 4.1417e-05 | 3.6014e-07 | 115
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 111 | 9879 | 0.0017593 | 1.9767e-05 | 89
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 7 | 1897 | 0.00033782 | 1.2466e-06 | 271
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 104 | 5821 | 1064263 | 0.19268 | 0.0010539 | 182.8316
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | ARRESTER | 109 | 9483 | 651459 | 0.11794 | 0.0017169 | 68.6976
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CUTOUT | 9 | 20 | 5179 | 0.00093764 | 3.6209e-06 | 258.95
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 3 | 113 | 47493 | 0.0085984 | 2.0458e-05 | 420.292
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | POLE | 3 | 44 | 24044 | 0.0043531 | 7.966e-06 | 546.4545
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | FUSE | 2 | 4 | 122 | 2.2088e-05 | 7.2419e-07 | 30.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | SWITCH, OH | 1 | 4 | 464 | 8.4006e-05 | 7.2419e-07 | 116
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | FUSE | 6 | 130 | 12837 | 0.0023241 | 2.3536e-05 | 98.7462
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 2 | 203 | 3.6752e-05 | 3.6209e-07 | 101.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CABLE TERMINATOR | 1 | 1 | 165 | 2.9873e-05 | 1.8105e-07 | 165
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 1 | 137 | 2.4803e-05 | 1.8105e-07 | 137
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | NONE | 4223 | 163514 | 24773603 | 4.5173 | 0.029815 | 151.5075
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 197 | 8648 | 2597035 | 0.46765 | 0.0015573 | 300.3047
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | ARRESTER | 128 | 5980 | 793567 | 0.1429 | 0.0010768 | 132.7035
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE | 37 | 2473 | 769783 | 0.13862 | 0.00044532 | 311.275
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | NONE | 16 | 1277 | 1392309 | 0.25072 | 0.00022995 | 1090.2968
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | NONE | 19 | 70 | 10076 | 0.0018144 | 1.2605e-05 | 143.9429
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | FUSE | 100 | 1134 | 121227 | 0.02183 | 0.0002042 | 106.9021
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | NONE | 28 | 113 | 10486 | 0.0018882 | 2.0348e-05 | 92.7965
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONN/CLAMP | 3 | 10 | 890 | 0.00016026 | 1.8007e-06 | 89
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 5 | 1658 | 0.00029856 | 9.0036e-07 | 331.6
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | METERING | 7 | 15 | 1106 | 0.00019916 | 2.7011e-06 | 73.7333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 4 | 142 | 13206 | 0.002378 | 2.557e-05 | 93
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 19 | 3021 | 0.000544 | 3.4214e-06 | 159
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | METERING | 22 | 50 | 6665 | 0.0011954 | 8.9675e-06 | 133.3
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | FUSE | 9 | 13 | 883 | 0.000159 | 2.3409e-06 | 67.9231
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | U | NONE | 1 | 62 | 15252 | 0.0027465 | 1.1164e-05 | 246
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 2 | 50 | 42311 | 0.007619 | 9.0036e-06 | 846.22
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, UG | 4 | 29 | 8853 | 0.0015878 | 5.2012e-06 | 305.2759
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE | 41 | 4259 | 916329 | 0.16434 | 0.00076385 | 215.1512
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 7 | 211 | 86242 | 0.01553 | 3.7995e-05 | 408.7299
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 42 | 5393 | 0.00097113 | 7.563e-06 | 128.4048
AEP Total | 2023 | 5575683 | PARTIAL POWER | O | NONE | 3 | 3 | 339 | 6.08e-05 | 5.3805e-07 | 113
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 13 | 3461 | 0.00062073 | 2.3316e-06 | 266.2308
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | FUSE | 9 | 232 | 16885 | 0.0030283 | 4.1609e-05 | 72.7802
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 13 | 2743 | 0.00049196 | 2.3316e-06 | 211
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | NONE | 1 | 4 | 152 | 2.7371e-05 | 7.2029e-07 | 38
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | BREAKER | 1 | 1 | 49 | 8.7882e-06 | 1.7935e-07 | 49
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 2 | 6 | 1342 | 0.00024296 | 1.0863e-06 | 223.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | FUSE | 60 | 713 | 49115 | 0.0089557 | 0.00013001 | 68.885
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | SWITCH, OH | 3 | 64 | 12495 | 0.0022784 | 1.167e-05 | 195.2344
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | FUSE | 49 | 483 | 48466 | 0.0088374 | 8.8071e-05 | 100.3437
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | FUSE | 3 | 13 | 1363 | 0.00024853 | 2.3704e-06 | 104.8462
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONN/CLAMP | 2 | 8 | 905 | 0.00016502 | 1.4587e-06 | 113.125
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SWITCH, OH | 3 | 144 | 32708 | 0.005964 | 2.6257e-05 | 227.1389
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 1704 | 182328 | 0.033246 | 0.00031071 | 107
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 3 | 764 | 24799 | 0.0045219 | 0.00013931 | 32.4594
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 7 | 1001 | 0.00018252 | 1.2764e-06 | 143
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | NONE | 4 | 12 | 973 | 0.00017742 | 2.1881e-06 | 81.0833
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | METERING | 2 | 2 | 165 | 3.0086e-05 | 3.6468e-07 | 82.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 2 | 2 | 286 | 5.215e-05 | 3.6468e-07 | 143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 1 | 279 | 5.0039e-05 | 1.7935e-07 | 279
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 0 | 0 | 0 | 0
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 101 | 13251 | 0.0023861 | 1.8187e-05 | 131.198
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 1 | 112 | 2.0168e-05 | 1.8007e-07 | 112
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | SWITCH, OH | 9 | 212 | 64805 | 0.01167 | 3.8175e-05 | 305.684
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 19 | 4571 | 0.00082311 | 3.4214e-06 | 240.5789
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SPLICE, OH | 3 | 11 | 2079 | 0.00037437 | 1.9808e-06 | 189
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | ARRESTER | 70 | 2812 | 244779 | 0.044634 | 0.00051275 | 87.048
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 9 | 79 | 13477 | 0.0024574 | 1.4405e-05 | 170.5949
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR UG | 19 | 58 | 14518 | 0.0026472 | 1.0576e-05 | 250.3103
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 104 | 7964 | 1305838 | 0.23811 | 0.0014522 | 163.9676
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 3 | 1159 | 0.00021133 | 5.4703e-07 | 386.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | FUSE | 1 | 3 | 21 | 3.8292e-06 | 5.4703e-07 | 7
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 11 | 630 | 71509 | 0.013039 | 0.00011488 | 113.5063
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | INSULATOR | 3 | 166 | 33080 | 0.0060319 | 3.0269e-05 | 199.2771
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 4 | 584 | 0.00010649 | 7.2937e-07 | 146
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | TRANSFORMER, GROUNDING | 1 | 2 | 470 | 8.5701e-05 | 3.6468e-07 | 235
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 63 | 53739 | 0.0097989 | 1.1488e-05 | 853
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 3 | 11 | 1943 | 0.00035429 | 2.0058e-06 | 176.6364
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | NONE | 5 | 19 | 1997 | 0.00036414 | 3.4645e-06 | 105.1053
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 3 | 46 | 25279 | 0.0046094 | 8.3877e-06 | 549.5435
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | FUSE | 102 | 1780 | 614199 | 0.11016 | 0.00031924 | 345.0556
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | SWITCH, OH | 3 | 35 | 6060 | 0.0010869 | 6.2773e-06 | 173.1429
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 24 | 1538 | 0.00027695 | 4.3217e-06 | 64.0833
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERO | NONE | 7 | 15 | 1391 | 0.00024948 | 2.6903e-06 | 92.7333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | PEDESTAL | 3 | 12 | 3527 | 0.00063511 | 2.1609e-06 | 293.9167
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 2 | 184 | 3.3e-05 | 3.587e-07 | 92
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 4 | 532 | 9.5798e-05 | 7.2029e-07 | 133
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | FUSE | 1 | 2 | 62 | 1.1164e-05 | 3.6014e-07 | 31
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 63 | 1166 | 479580 | 0.085404 | 0.00020764 | 411.3036
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 81 | 7954 | 956179 | 0.17028 | 0.0014164 | 120.2136
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE | 11 | 983 | 99524 | 0.01785 | 0.0001763 | 101.2452
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 171 | 2067 | 355222 | 0.063258 | 0.00036809 | 171.8539
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | METERING | 1 | 7 | 2330 | 0.00041789 | 1.2555e-06 | 332.8571
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 20 | 3628 | 0.00064607 | 3.5616e-06 | 181.4
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 51 | 7753 | 858191 | 0.15283 | 0.0013807 | 110.6915
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 8 | 102 | 7748 | 0.0013896 | 1.8294e-05 | 75.9608
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | OTHER EQUIPMENT | 1 | 1 | 227 | 4.0713e-05 | 1.7935e-07 | 227
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | POLE | 1 | 5 | 940 | 0.0001674 | 8.904e-07 | 188
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | NONE | 16 | 1076 | 130718 | 0.023278 | 0.00019161 | 121.4851
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, UG | 5 | 21 | 8194 | 0.0014755 | 3.7815e-06 | 390.1905
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | TOR | NONE | 2 | 741 | 43657 | 0.0078614 | 0.00013343 | 58.9163
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 5 | 33 | 4498 | 0.00080996 | 5.9424e-06 | 136.303
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 2 | 76 | 1.3631e-05 | 3.587e-07 | 38
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 36 | 120 | 19527 | 0.0034774 | 2.137e-05 | 162.725
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 22 | 2082 | 338334 | 0.06025 | 0.00037076 | 162.5043
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WU | NONE | 3 | 2196 | 652883 | 0.11709 | 0.00039385 | 297.3056
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 3 | 88 | 13386 | 0.0023838 | 1.5671e-05 | 152.1136
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | NONE | 5 | 8 | 1068 | 0.00019155 | 1.4348e-06 | 133.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | FUSE | 14 | 46 | 5923 | 0.0010548 | 8.1917e-06 | 128.7609
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | POLE | 1 | 38 | 8930 | 0.0015903 | 6.767e-06 | 235
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | FUSE | 6 | 149 | 14993 | 0.00267 | 2.6534e-05 | 100.6242
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | ARRESTER | 1 | 1 | 109 | 1.9549e-05 | 1.7935e-07 | 109
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 9 | 738 | 0.00013361 | 1.6294e-06 | 82
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | NONE | 5 | 9 | 1045 | 0.00018818 | 1.6206e-06 | 116.1111
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 41 | 24436 | 0.004424 | 7.4229e-06 | 596
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 1 | 135 | 2.4212e-05 | 1.7935e-07 | 135
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 4 | 704 | 0.00012626 | 7.174e-07 | 176
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | JUMPER/RISER | 3 | 10 | 11215 | 0.0020304 | 1.8105e-06 | 1121.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 142 | 2.5709e-05 | 1.8105e-07 | 142
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR UG | 4 | 16 | 3185 | 0.00058076 | 2.9175e-06 | 199.0625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 1 | 108 | 1.9693e-05 | 1.8234e-07 | 108
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | U | NONE | 3 | 1921 | 330816 | 0.060322 | 0.00035028 | 172.2103
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | FUSE | 2 | 8 | 522 | 9.5183e-05 | 1.4587e-06 | 65.25
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 64 | 4262 | 727610 | 0.12957 | 0.00075898 | 170.7203
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 237 | 24128 | 1907852 | 0.33975 | 0.0042967 | 79.0721
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 15 | 65 | 5944 | 0.0010585 | 1.1575e-05 | 91.4462
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | SPLICE, OH | 1 | 7 | 466 | 8.2985e-05 | 1.2466e-06 | 66.5714
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 5 | 2875 | 0.00051198 | 8.904e-07 | 575
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | SPLICE, OH | 1 | 1 | 80 | 1.4246e-05 | 1.7808e-07 | 80
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | NONE | 5 | 11 | 1305 | 0.00023499 | 1.9808e-06 | 118.6364
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | TRANSFORMER, UG | 1 | 1 | 303 | 5.4562e-05 | 1.8007e-07 | 303
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 1 | 205 | 3.6915e-05 | 1.8007e-07 | 205
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 9 | 1990 | 368023 | 0.065537 | 0.00035438 | 184.9362
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 8 | 61 | 8777 | 0.001563 | 1.0863e-05 | 143.8852
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 207 | 37342 | 0.0066499 | 3.6863e-05 | 180.3961
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERO | NONE | 1 | 1 | 67 | 1.1931e-05 | 1.7808e-07 | 67
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | FUSE | 4 | 7 | 600 | 0.00010685 | 1.2466e-06 | 85.7143
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 1 | 67 | 1.1931e-05 | 1.7808e-07 | 67
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 66 | 1.1753e-05 | 1.7808e-07 | 66
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | SPLICE, OH | 3 | 13 | 8917 | 0.0015879 | 2.315e-06 | 685.9231
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 3 | 9 | 4612 | 0.0008213 | 1.6027e-06 | 512.4444
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 50 | 3250 | 0.00059261 | 9.1171e-06 | 65
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | POLE | 1 | 554 | 57484 | 0.010407 | 0.0001003 | 103.7617
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | BREAKER | 1 | 1 | 117 | 2.1182e-05 | 1.8105e-07 | 117
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 29 | 2436 | 0.00043866 | 5.2221e-06 | 84
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | METERING | 1 | 2 | 322 | 5.7983e-05 | 3.6014e-07 | 161
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 24 | 1752 | 0.00031549 | 4.3217e-06 | 73
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | SPLICE, OH | 1 | 4 | 796 | 0.00014334 | 7.2029e-07 | 199
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 1 | 13 | 7306 | 0.0013011 | 2.315e-06 | 562
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | OTHER EQUIPMENT | 1 | 6 | 600 | 0.00010685 | 1.0685e-06 | 100
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CUTOUT | 1 | 8 | 1560 | 0.0002778 | 1.4246e-06 | 195
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | POLE HARDWARE | 1 | 4 | 412 | 7.3369e-05 | 7.1232e-07 | 103
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CUTOUT | 2 | 3 | 150 | 2.6712e-05 | 5.3424e-07 | 50
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | INSULATOR | 4 | 10 | 5041 | 0.0008977 | 1.7808e-06 | 504.1
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 49 | 2744 | 0.00048865 | 8.7259e-06 | 56
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 13 | 1123 | 0.00019998 | 2.315e-06 | 86.3846
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 2 | 11 | 3439 | 0.00061242 | 1.9589e-06 | 312.6364
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 1 | 26 | 3536 | 0.00063673 | 4.6819e-06 | 136
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 6 | 3936 | 0.00070592 | 1.0761e-06 | 656
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | NONE | 1 | 12 | 792 | 0.00014104 | 2.137e-06 | 66
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CUTOUT | 1 | 63 | 13370 | 0.0023809 | 1.1219e-05 | 212.2222
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 2 | 303 | 5.3958e-05 | 3.5616e-07 | 151.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 1 | 85 | 1.5499e-05 | 1.8234e-07 | 85
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 90 | 1.6411e-05 | 1.8234e-07 | 90
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | NONE | 1 | 1 | 436 | 7.9501e-05 | 1.8234e-07 | 436
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | NONE | 2084 | 48817 | 5093741 | 0.9222 | 0.0088381 | 104.3436
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | FUSE | 155 | 2985 | 459456 | 0.083183 | 0.00054042 | 153.9216
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE | 34 | 4277 | 1120479 | 0.20286 | 0.00077434 | 261.9778
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR UG | 2 | 8 | 1868 | 0.00033819 | 1.4484e-06 | 233.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CUTOUT | 8 | 428 | 48514 | 0.0087833 | 7.7488e-05 | 113.3505
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | FUSE | 3 | 4 | 347 | 6.2823e-05 | 7.2419e-07 | 86.75
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 9 | 22 | 2469 | 0.000447 | 3.983e-06 | 112.2273
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 11 | 86 | 29429 | 0.005328 | 1.557e-05 | 342.1977
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CROSSARM | 39 | 9074 | 770068 | 0.13942 | 0.0016428 | 84.8653
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 28 | 1051 | 238474 | 0.043175 | 0.00019028 | 226.902
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 1 | 53 | 10983 | 0.0019884 | 9.5955e-06 | 207.2264
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | FUSE | 1 | 2 | 298 | 5.3446e-05 | 3.587e-07 | 149
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 2 | 5 | 2832 | 0.00050792 | 8.9675e-07 | 566.4
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 4 | 361 | 91297 | 0.016258 | 6.4287e-05 | 252.9003
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 2 | 268 | 4.8066e-05 | 3.587e-07 | 134
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 1514 | 151400 | 0.027154 | 0.00027154 | 100
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CUTOUT | 1 | 1 | 137 | 2.4803e-05 | 1.8105e-07 | 137
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | NONE | 2 | 2 | 162 | 2.9539e-05 | 3.6468e-07 | 81
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | INSULATOR | 2 | 29 | 3841 | 0.00070038 | 5.2879e-06 | 132.4483
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | NONE | 33 | 5569 | 780237 | 0.13894 | 0.00099173 | 140.1036
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 2 | 2 | 134 | 2.413e-05 | 3.6014e-07 | 67
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | SWITCH, OH | 1 | 3 | 237 | 4.2677e-05 | 5.4022e-07 | 79
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | NONE | 9 | 14 | 1712 | 0.00030487 | 2.4931e-06 | 122.2857
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | NONE | 7 | 8 | 574 | 0.00010222 | 1.4246e-06 | 71.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 10 | 190 | 33469 | 0.0059602 | 3.3835e-05 | 176.1526
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | NONE | 48 | 8410 | 689553 | 0.1228 | 0.0014977 | 81.992
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 4 | 478 | 8.5122e-05 | 7.1232e-07 | 119.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 11 | 24 | 2633 | 0.00046888 | 4.2739e-06 | 109.7083
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 3 | 8 | 1046 | 0.00018627 | 1.4246e-06 | 130.75
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 10 | 29 | 3214 | 0.00057235 | 5.1643e-06 | 110.8276
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 2 | 162 | 2.8849e-05 | 3.5616e-07 | 81
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 9 | 137 | 17800 | 0.0031698 | 2.4397e-05 | 129.927
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | FUSE | 7 | 12 | 1105 | 0.00019678 | 2.137e-06 | 92.0833
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 5 | 33 | 8632 | 0.0015372 | 5.8766e-06 | 261.5758
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | CUTOUT | 1 | 1 | 172 | 3.063e-05 | 1.7808e-07 | 172
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | CABLE TERMINATOR | 1 | 7 | 11508 | 0.0020493 | 1.2466e-06 | 1644
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | REGULATOR | 1 | 473 | 9460 | 0.0017035 | 8.5174e-05 | 20
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 9 | 828 | 0.00015098 | 1.6411e-06 | 92
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 4 | 1216 | 0.00021897 | 7.2029e-07 | 304
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | NONE | 2 | 10 | 1472 | 0.00026841 | 1.8234e-06 | 147.2
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 1 | 1 | 59 | 1.0758e-05 | 1.8234e-07 | 59
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | FUSE | 1 | 2 | 300 | 5.4703e-05 | 3.6468e-07 | 150
AEP Total | 2022 | 5553337 | PARTIAL POWER | WT | TRANSFORMER, OH | 1 | 1 | 413 | 7.437e-05 | 1.8007e-07 | 413
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CUTOUT | 3 | 12 | 978 | 0.00017611 | 2.1609e-06 | 81.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 3 | 200 | 23453 | 0.0041765 | 3.5616e-05 | 117.265
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | FUSE | 4 | 11 | 684 | 0.00012181 | 1.9589e-06 | 62.1818
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | NONE | 5 | 13 | 1053 | 0.00019064 | 2.3536e-06 | 81
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | NONE | 3 | 14 | 1168 | 0.00021146 | 2.5346e-06 | 83.4286
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 69 | 61504 | 0.011135 | 1.2492e-05 | 891.3623
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | NONE | 602 | 33632 | 2782914 | 0.50112 | 0.0060562 | 82.746
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CIRCUIT SWITCHER | 1 | 42 | 62496 | 0.011315 | 7.6039e-06 | 1488
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 1209 | 179079 | 0.032422 | 0.00021889 | 148.1216
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 4 | 752 | 0.00013615 | 7.2419e-07 | 188
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 3 | 183 | 32982 | 0.0059713 | 3.3131e-05 | 180.2295
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | NONE | 1 | 3 | 768 | 0.00013904 | 5.4314e-07 | 256
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | INSULATOR | 1 | 525 | 108675 | 0.019675 | 9.5049e-05 | 207
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | NONE | 2 | 6 | 1486 | 0.00026903 | 1.0863e-06 | 247.6667
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 270 | 4.8883e-05 | 1.8105e-07 | 270
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | NONE | 650 | 11778 | 1461257 | 0.26645 | 0.0021476 | 124.0666
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | ARRESTER | 10 | 175 | 39053 | 0.007121 | 3.191e-05 | 223.16
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 62 | 2957 | 448103 | 0.081708 | 0.00053919 | 151.5397
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CUTOUT | 85 | 2253 | 277260 | 0.050556 | 0.00041082 | 123.0626
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | INSULATOR | 21 | 2629 | 719649 | 0.13122 | 0.00047938 | 273.7349
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | NONE | 1488 | 24331 | 1845740 | 0.33237 | 0.0043813 | 75.8596
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | NONE | 99 | 3900 | 577559 | 0.104 | 0.00070228 | 148.0921
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, OH | 23 | 86 | 25629 | 0.0046151 | 1.5486e-05 | 298.0116
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 2 | 192 | 3.4574e-05 | 3.6014e-07 | 96
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | SPLICE, OH | 6 | 34 | 3500 | 0.00063025 | 6.1224e-06 | 102.9412
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | ARRESTER | 4 | 6 | 664 | 0.00011957 | 1.0804e-06 | 110.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 220 | 8170 | 1769585 | 0.31738 | 0.0014653 | 216.5955
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | POLE | 4 | 984 | 625891 | 0.11271 | 0.00017719 | 636.0681
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | NONE | 60 | 1517 | 165769 | 0.029731 | 0.00027207 | 109.2742
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | NONE | 109 | 5843 | 458034 | 0.082149 | 0.0010479 | 78.3902
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 123 | 549 | 86283 | 0.015475 | 9.8463e-05 | 157.1639
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONN/CLAMP | 159 | 453 | 50095 | 0.0089845 | 8.1246e-05 | 110.585
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | ARRESTER | 4 | 30 | 2981 | 0.00053679 | 5.4022e-06 | 99.3667
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | JUMPER/RISER | 1 | 993 | 296907 | 0.053465 | 0.00017881 | 299
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 2 | 1493 | 340273 | 0.061028 | 0.00026777 | 227.9123
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CUTOUT | 24 | 1343 | 165297 | 0.029646 | 0.00024087 | 123.0804
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | SS | NONE | 2 | 1109 | 38674 | 0.0069641 | 0.0001997 | 34.8729
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 1 | 69 | 1.2425e-05 | 1.8007e-07 | 69
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 31 | 6089 | 851703 | 0.15275 | 0.0010921 | 139.8757
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE | 8 | 978 | 1056703 | 0.19268 | 0.00017833 | 1080.4734
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, OH | 66 | 4505 | 477838 | 0.08713 | 0.00082145 | 106.0684
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CROSSARM | 22 | 4497 | 743374 | 0.13555 | 0.00081999 | 165.3044
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | PEDESTAL | 1 | 1 | 676 | 0.00012326 | 1.8234e-07 | 676
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 14 | 110 | 16448 | 0.0029992 | 2.0058e-05 | 149.5273
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 2 | 542 | 9.8829e-05 | 3.6468e-07 | 271
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 13 | 1011 | 143566 | 0.026178 | 0.00018435 | 142.004
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 79 | 10343 | 0.001886 | 1.4405e-05 | 130.9241
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONN/CLAMP | 2 | 10 | 980 | 0.0001787 | 1.8234e-06 | 98
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | NONE | 5 | 32 | 16241 | 0.0029614 | 5.8349e-06 | 507.5312
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 2 | 2 | 985 | 0.00017961 | 3.6468e-07 | 492.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | POLE | 1 | 57 | 43377 | 0.0079095 | 1.0393e-05 | 761
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 5 | 25 | 3579 | 0.0006526 | 4.5586e-06 | 143.16
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | R | NONE | 2 | 916 | 114503 | 0.020879 | 0.00016703 | 125.0033
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | INSULATOR | 1 | 2 | 290 | 5.2879e-05 | 3.6468e-07 | 145
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 3613 | 170705 | 21863562 | 3.8935 | 0.030399 | 128.078
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | NONE | 25 | 80 | 7234 | 0.0012974 | 1.4348e-05 | 90.425
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 1 | 23 | 4.1417e-06 | 1.8007e-07 | 23
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | NONE | 1 | 2 | 140 | 2.5109e-05 | 3.587e-07 | 70
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 5 | 680 | 0.00012196 | 8.9675e-07 | 136
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 3 | 84 | 18414 | 0.0033026 | 1.5065e-05 | 219.2143
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 3 | 155 | 79108 | 0.014245 | 2.7911e-05 | 510.3742
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 264 | 9633 | 1731740 | 0.30839 | 0.0017154 | 179.7716
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | NONE | 3 | 27 | 1925 | 0.00034525 | 4.8425e-06 | 71.2963
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 5 | 48 | 10733 | 0.0019113 | 8.5478e-06 | 223.6042
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | FUSE | 92 | 1205 | 217526 | 0.038737 | 0.00021459 | 180.5195
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 1 | 1017 | 0.00018111 | 1.7808e-07 | 1017
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 3 | 3 | 740 | 0.00013272 | 5.3805e-07 | 246.6667
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | NONE | 27 | 87 | 10950 | 0.00195 | 1.5493e-05 | 125.8621
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 10 | 16 | 1885 | 0.00033568 | 2.8493e-06 | 117.8125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 7 | 16 | 4732 | 0.00084267 | 2.8493e-06 | 295.75
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | FUSE | 2 | 16 | 1930 | 0.00034942 | 2.8967e-06 | 120.625
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 65 | 151 | 17014 | 0.0030298 | 2.689e-05 | 112.6755
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | NONE | 15 | 62 | 7773 | 0.0013842 | 1.1041e-05 | 125.371
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 3 | 4 | 739 | 0.0001316 | 7.1232e-07 | 184.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 5 | 1985 | 0.00035601 | 8.9675e-07 | 397
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CROSSARM | 1 | 29 | 5452 | 0.00097782 | 5.2012e-06 | 188
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | FUSE | 4 | 5 | 417 | 7.6037e-05 | 9.1171e-07 | 83.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 4 | 57 | 18132 | 0.0033062 | 1.0393e-05 | 318.1053
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 1802 | 147764 | 0.026944 | 0.00032858 | 82
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | AF | NONE | 1 | 965 | 158260 | 0.028857 | 0.00017596 | 164
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 15 | 197 | 32218 | 0.0057374 | 3.5082e-05 | 163.5431
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 20 | 1415 | 0.00025198 | 3.5616e-06 | 70.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 495 | 38325 | 0.0068249 | 8.815e-05 | 77.4242
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 4 | 344 | 6.1259e-05 | 7.1232e-07 | 86
AEP Total | 2025 | 5615460 | PARTIAL POWER | VIN | TRANSFORMER, OH | 1 | 5 | 250 | 4.452e-05 | 8.904e-07 | 50
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 2 | 280 | 5.0218e-05 | 3.587e-07 | 140
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | FUSE | 1 | 1 | 78 | 1.3989e-05 | 1.7935e-07 | 78
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | RELAY | 2 | 2847 | 45552 | 0.008306 | 0.00051913 | 16
AEP Total | 2020 | 5484199 | PARTIAL POWER | WH | TRANSFORMER, OH | 1 | 7 | 2457 | 0.00044801 | 1.2764e-06 | 351
AEP Total | 2024 | 5615460 | PARTIAL POWER | WFS | NONE | 1 | 6 | 1080 | 0.00019233 | 1.0685e-06 | 180
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | FUSE | 1 | 1 | 67 | 1.1931e-05 | 1.7808e-07 | 67
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | ARRESTER | 1 | 4 | 1156 | 0.00020586 | 7.1232e-07 | 289
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | NONE | 397 | 16721 | 1685667 | 0.30518 | 0.0030273 | 100.8114
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 706 | 36109 | 0.0065374 | 0.00012782 | 51.1459
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | INSULATOR | 2 | 28 | 1587 | 0.00028732 | 5.0693e-06 | 56.6786
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 33 | 96 | 11636 | 0.0021067 | 1.738e-05 | 121.2083
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | NONE | 23 | 5369 | 195491 | 0.035393 | 0.00097204 | 36.4111
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 6 | 2754 | 410743 | 0.074364 | 0.0004986 | 149.1442
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | SWITCH, OH | 3 | 93 | 16617 | 0.0030084 | 1.6837e-05 | 178.6774
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 1 | 101 | 1.8286e-05 | 1.8105e-07 | 101
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 12 | 939 | 0.00017 | 2.1726e-06 | 78.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 2 | 300 | 5.4314e-05 | 3.6209e-07 | 150
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 18 | 3186 | 0.00057681 | 3.2588e-06 | 177
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 2039 | 338549 | 0.061293 | 0.00036915 | 166.0368
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 4 | 6 | 868 | 0.00015715 | 1.0863e-06 | 144.6667
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONN/CLAMP | 3 | 8 | 1646 | 0.000298 | 1.4484e-06 | 205.75
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | NONE | 78 | 637 | 126882 | 0.022848 | 0.00011471 | 199.1868
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | SWITCH, OH | 1 | 151 | 25972 | 0.0046768 | 2.7191e-05 | 172
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | FUSE | 136 | 3542 | 569328 | 0.10252 | 0.00063781 | 160.7363
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | NONE | 26 | 6768 | 954551 | 0.17189 | 0.0012187 | 141.0389
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | NONE | 55 | 239 | 38515 | 0.0069355 | 4.3037e-05 | 161.1506
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CUTOUT | 173 | 6712 | 699046 | 0.12588 | 0.0012086 | 104.1487
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, OH | 75 | 5609 | 664631 | 0.11968 | 0.00101 | 118.4937
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CUTOUT | 26 | 275 | 74054 | 0.013335 | 4.952e-05 | 269.2873
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 12 | 47 | 13436 | 0.0024194 | 8.4634e-06 | 285.8723
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 16 | 151 | 57176 | 0.010296 | 2.7191e-05 | 378.649
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | BREAKER | 2 | 644 | 7378 | 0.0013286 | 0.00011597 | 11.4565
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | FUSE | 8 | 116 | 22595 | 0.0040687 | 2.0888e-05 | 194.7845
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | INSULATOR | 28 | 4733 | 1212260 | 0.21829 | 0.00085228 | 256.1293
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SPLICE, OH | 1 | 1 | 56 | 1.0139e-05 | 1.8105e-07 | 56
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | NETWORK TRANSFORMER | 1 | 1 | 118 | 2.1363e-05 | 1.8105e-07 | 118
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CUTOUT | 1 | 1 | 73 | 1.3311e-05 | 1.8234e-07 | 73
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 57 | 10449 | 0.0018608 | 1.0151e-05 | 183.3158
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONN/CLAMP | 2 | 13 | 654 | 0.00011777 | 2.3409e-06 | 50.3077
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | BREAKER | 10 | 6358 | 563420 | 0.10033 | 0.0011322 | 88.6159
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 2507 | 618752 | 0.11019 | 0.00044645 | 246.8097
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | NONE | 7 | 41 | 8830 | 0.0015724 | 7.3013e-06 | 215.3659
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 519 | 34429 | 0.0061311 | 9.2423e-05 | 66.3372
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 16 | 2128 | 0.00037895 | 2.8493e-06 | 133
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | NONE | 10 | 20 | 2651 | 0.00047209 | 3.5616e-06 | 132.55
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | FUSE | 7 | 156 | 31629 | 0.0056325 | 2.778e-05 | 202.75
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CROSSARM | 3 | 100 | 6934 | 0.0012348 | 1.7808e-05 | 69.34
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | POLE | 2 | 7 | 1526 | 0.00027175 | 1.2466e-06 | 218
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR UG | 4 | 8 | 2052 | 0.00036542 | 1.4246e-06 | 256.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 458 | 108818 | 0.019378 | 8.1561e-05 | 237.5939
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | O | NONE | 3 | 1681 | 136462 | 0.024301 | 0.00029935 | 81.1791
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 8 | 552 | 9.83e-05 | 1.4246e-06 | 69
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | POLE | 2 | 667 | 66731 | 0.011883 | 0.00011878 | 100.0465
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, GROUNDING | 1 | 1 | 7 | 1.2466e-06 | 1.7808e-07 | 7
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | REGULATOR | 2 | 137 | 19049 | 0.0034302 | 2.467e-05 | 139.0438
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | POLE | 3 | 92 | 82406 | 0.015026 | 1.6775e-05 | 895.7174
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | SPLICE, OH | 1 | 1 | 117 | 2.1068e-05 | 1.8007e-07 | 117
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | TRANSFORMER, UG | 1 | 6 | 1164 | 0.00021074 | 1.0863e-06 | 194
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CABLE TERMINATOR | 1 | 9 | 864 | 0.00015558 | 1.6206e-06 | 96
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CUTOUT | 1 | 2 | 186 | 3.3493e-05 | 3.6014e-07 | 93
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | BREAKER | 1 | 54 | 4266 | 0.00076819 | 9.7239e-06 | 79
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 3 | 162 | 86892 | 0.015474 | 2.8849e-05 | 536.3704
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 6 | 293 | 5.2177e-05 | 1.0685e-06 | 48.8333
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 2 | 302 | 5.378e-05 | 3.5616e-07 | 151
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 4 | 6 | 700 | 0.00012466 | 1.0685e-06 | 116.6667
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | TOR | NONE | 3 | 76 | 6806 | 0.001212 | 1.3534e-05 | 89.5526
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 2 | 826 | 209193 | 0.037253 | 0.00014709 | 253.2603
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CROSSARM | 12 | 5894 | 599466 | 0.10795 | 0.0010613 | 101.7078
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 10 | 704 | 0.00012677 | 1.8007e-06 | 70.4
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | NONE | 73 | 364 | 61041 | 0.010948 | 6.5283e-05 | 167.6951
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | FUSE | 1 | 1 | 95 | 1.7107e-05 | 1.8007e-07 | 95
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONN/CLAMP | 9 | 511 | 138099 | 0.024868 | 9.2017e-05 | 270.2524
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR UG | 9 | 41 | 11720 | 0.0021104 | 7.3829e-06 | 285.8537
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | POLE | 1 | 12 | 3336 | 0.00060072 | 2.1609e-06 | 278
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | SWITCH, OH | 25 | 369 | 60925 | 0.010927 | 6.618e-05 | 165.1084
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | INSULATOR | 38 | 5172 | 458445 | 0.082222 | 0.0009276 | 88.6398
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 1 | 263 | 4.7615e-05 | 1.8105e-07 | 263
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 1 | 119 | 2.1545e-05 | 1.8105e-07 | 119
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 2 | 48 | 12240 | 0.002216 | 8.6902e-06 | 255
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | JUMPER/RISER | 1 | 93 | 18042 | 0.0032664 | 1.6837e-05 | 194
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, POWER - LTC | 1 | 2 | 408 | 7.3867e-05 | 3.6209e-07 | 204
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | NONE | 32 | 16385 | 574128 | 0.10469 | 0.0029877 | 35.0399
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | BREAKER | 6 | 4307 | 297154 | 0.054184 | 0.00078535 | 68.9933
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | FUSE | 16 | 378 | 31748 | 0.005789 | 6.8925e-05 | 83.9894
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 1 | 667 | 0.00012162 | 1.8234e-07 | 667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 14 | 271 | 24161 | 0.0044056 | 4.9415e-05 | 89.155
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | POLE HARDWARE | 1 | 38 | 6612 | 0.0012056 | 6.929e-06 | 174
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CROSSARM | 13 | 879 | 244645 | 0.044609 | 0.00016028 | 278.322
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 6 | 534 | 9.7371e-05 | 1.0941e-06 | 89
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CUTOUT | 2 | 125 | 18960 | 0.0034572 | 2.2793e-05 | 151.68
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 2 | 12 | 2669 | 0.00048667 | 2.1881e-06 | 222.4167
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | FUSE | 2 | 4 | 141 | 2.571e-05 | 7.2937e-07 | 35.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CUTOUT | 6 | 52 | 4417 | 0.0008054 | 9.4818e-06 | 84.9423
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | FUSE | 1 | 1 | 37 | 6.6627e-06 | 1.8007e-07 | 37
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | ARRESTER | 1 | 2 | 334 | 6.0144e-05 | 3.6014e-07 | 167
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 62 | 7582 | 0.0013653 | 1.1164e-05 | 122.2903
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 20 | 69 | 7215 | 0.0012992 | 1.2425e-05 | 104.5652
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 6 | 1577 | 0.00028397 | 1.0804e-06 | 262.8333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | FUSE | 5 | 85 | 7029 | 0.0012607 | 1.5245e-05 | 82.6941
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | POLE | 1 | 1 | 1301 | 0.00023427 | 1.8007e-07 | 1301
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | ARRESTER | 9 | 18 | 2592 | 0.00046488 | 3.2283e-06 | 144
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 2 | 26 | 5343 | 0.00095827 | 4.6631e-06 | 205.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 1 | 2 | 32 | 5.7392e-06 | 3.587e-07 | 16
AEP Total | 2020 | 5484199 | PARTIAL POWER | WH | NONE | 1 | 3 | 1830 | 0.00033369 | 5.4703e-07 | 610
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | EQF | RECLOSER, LINE/OCR/BR | 1 | 303 | 226938 | 0.040701 | 5.4343e-05 | 748.9703
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONN/CLAMP | 1 | 2 | 162 | 2.9055e-05 | 3.587e-07 | 81
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 27 | 4680 | 0.00085336 | 4.9232e-06 | 173.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 1 | 4 | 552 | 9.83e-05 | 7.1232e-07 | 138
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 186 | 21762 | 0.0038754 | 3.3123e-05 | 117
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 1 | 54 | 9.6163e-06 | 1.7808e-07 | 54
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | FUSE | 1 | 71 | 3905 | 0.00071205 | 1.2946e-05 | 55
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | RELAY | 1 | 419 | 111873 | 0.020145 | 7.545e-05 | 267
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | RECLOSER, LINE/OCR/BR | 1 | 587 | 21132 | 0.0038259 | 0.00010627 | 36
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 2 | 142 | 2.5709e-05 | 3.6209e-07 | 71
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | NONE | 424 | 6201 | 573110 | 0.10376 | 0.0011227 | 92.4222
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE | 78 | 5288 | 1085520 | 0.19653 | 0.00095737 | 205.2799
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | ARRESTER | 10 | 187 | 14107 | 0.002554 | 3.3856e-05 | 75.4385
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | NONE | 24 | 90 | 8481 | 0.0015355 | 1.6294e-05 | 94.2333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | SWITCH, OH | 24 | 2620 | 268740 | 0.048654 | 0.00047434 | 102.5725
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | ARRESTER | 20 | 891 | 145469 | 0.026337 | 0.00016131 | 163.2649
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | NONE | 54 | 22929 | 2645313 | 0.47892 | 0.0041512 | 115.3698
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | TRANSFORMER, OH | 1 | 1 | 42 | 7.6039e-06 | 1.8105e-07 | 42
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 12 | 312 | 54604 | 0.0098859 | 5.6486e-05 | 175.0128
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 7 | 84 | 19933 | 0.0036088 | 1.5208e-05 | 237.2976
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CROSSARM | 19 | 2411 | 451733 | 0.081785 | 0.0004365 | 187.3633
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 31 | 2232 | 0.0004041 | 5.6124e-06 | 72
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | SWITCH, OH | 1 | 18 | 3618 | 0.00065503 | 3.2588e-06 | 201
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | ARRESTER | 3 | 11 | 1919 | 0.00034743 | 1.9915e-06 | 174.4545
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | JUMPER/RISER | 1 | 6 | 408 | 7.3867e-05 | 1.0863e-06 | 68
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 357 | 14457 | 5505792 | 0.99144 | 0.0026033 | 380.8392
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | NONE | 102 | 984 | 70426 | 0.012682 | 0.00017719 | 71.5711
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 2 | 145 | 14240 | 0.0025781 | 2.6252e-05 | 98.2069
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CUTOUT | 1 | 1 | 79 | 1.4303e-05 | 1.8105e-07 | 79
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | SPLICE, OH | 1 | 1 | 71 | 1.2854e-05 | 1.8105e-07 | 71
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 2 | 684 | 0.00012384 | 3.6209e-07 | 342
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | NONE | 1 | 1 | 68 | 1.2311e-05 | 1.8105e-07 | 68
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | NONE | 2390 | 58999 | 7960501 | 1.4515 | 0.010758 | 134.926
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | NONE | 511 | 12401 | 1212703 | 0.22113 | 0.0022612 | 97.7907
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 4 | 282 | 5.078e-05 | 7.2029e-07 | 70.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 3 | 63 | 52206 | 0.0093632 | 1.1299e-05 | 828.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 5 | 19 | 2072 | 0.00037161 | 3.4077e-06 | 109.0526
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 146 | 423 | 51062 | 0.0090931 | 7.5328e-05 | 120.7139
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 32 | 3617 | 899967 | 0.16027 | 0.00064411 | 248.8159
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 6 | 1332 | 0.00023889 | 1.0761e-06 | 222
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WL | REGULATOR | 3 | 1617 | 423654 | 0.07725 | 0.00029485 | 262
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | ARRESTER | 4 | 11 | 1362 | 0.00024428 | 1.9729e-06 | 123.8182
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONN/CLAMP | 1 | 6 | 228 | 4.0892e-05 | 1.0761e-06 | 38
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | SWITCH, OH | 4 | 178 | 21803 | 0.0039104 | 3.1924e-05 | 122.4888
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 1 | 18 | 450 | 8.0708e-05 | 3.2283e-06 | 25
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 5 | 9 | 507 | 9.0286e-05 | 1.6027e-06 | 56.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 3 | 6 | 1065 | 0.00019101 | 1.0761e-06 | 177.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 143 | 9253 | 1581474 | 0.28163 | 0.0016478 | 170.9147
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 3 | 6 | 650 | 0.00011575 | 1.0685e-06 | 108.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 51 | 2144 | 96544 | 0.017193 | 0.0003818 | 45.0299
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | FUSE | 53 | 303 | 23822 | 0.0042422 | 5.3958e-05 | 78.6205
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | INSULATOR | 1 | 17 | 697 | 0.00012619 | 3.0778e-06 | 41
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 1 | 23 | 4922 | 0.00088631 | 4.1417e-06 | 214
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 7 | 877 | 85809 | 0.015281 | 0.00015618 | 97.8438
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | POLE | 2 | 65 | 4918 | 0.0008758 | 1.1575e-05 | 75.6615
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 8 | 1404 | 0.00025002 | 1.4246e-06 | 175.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | METERING | 1 | 6 | 1086 | 0.00019339 | 1.0685e-06 | 181
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 18 | 4212 | 1051058 | 0.18717 | 0.00075007 | 249.5389
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 3 | 956 | 563612 | 0.10037 | 0.00017024 | 589.5523
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 4 | 6 | 795 | 0.00014157 | 1.0685e-06 | 132.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 1661 | 44847 | 0.0079863 | 0.00029579 | 27
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | NONE | 14 | 7430 | 1051894 | 0.1918 | 0.0013548 | 141.5739
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABI | SWITCH, OH | 4 | 3254 | 851443 | 0.15525 | 0.00059334 | 261.6604
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 76 | 5223 | 1453162 | 0.26497 | 0.00095237 | 278.2236
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 28 | 126 | 20806 | 0.0037938 | 2.2975e-05 | 165.127
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR UG | 6 | 19 | 3283 | 0.00059863 | 3.4645e-06 | 172.7895
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONN/CLAMP | 10 | 69 | 8600 | 0.0015681 | 1.2582e-05 | 124.6377
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | NONE | 107 | 580 | 32106 | 0.0058543 | 0.00010576 | 55.3552
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | POLE | 1 | 12 | 3336 | 0.00060829 | 2.1881e-06 | 278
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CROSSARM | 2 | 53 | 2197 | 0.00040061 | 9.6641e-06 | 41.4528
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONN/CLAMP | 4 | 7 | 2026 | 0.00036942 | 1.2764e-06 | 289.4286
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONN/CLAMP | 72 | 308 | 52663 | 0.0094831 | 5.5462e-05 | 170.9838
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | R | NONE | 3 | 2282 | 192309 | 0.034629 | 0.00041092 | 84.2721
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | NONE | 19 | 45 | 5786 | 0.0010419 | 8.1032e-06 | 128.5778
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE | 69 | 10450 | 1400911 | 0.25125 | 0.0018742 | 134.0585
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 27 | 3483 | 0.00062719 | 4.8619e-06 | 129
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR UG | 6 | 73 | 23892 | 0.0043023 | 1.3145e-05 | 327.2877
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | BREAKER | 10 | 5455 | 523750 | 0.093935 | 0.00097836 | 96.0128
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CROSSARM | 6 | 538 | 165026 | 0.029597 | 9.649e-05 | 306.7398
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 3 | 402 | 7.2099e-05 | 5.3805e-07 | 134
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 4 | 14 | 2535 | 0.00045465 | 2.5109e-06 | 181.0714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 50 | 8232 | 0.0014824 | 9.0036e-06 | 164.64
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 3 | 102 | 1.8367e-05 | 5.4022e-07 | 34
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | JUMPER/RISER | 8 | 250 | 17936 | 0.0032168 | 4.4838e-05 | 71.744
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | NONE | 9 | 66 | 38606 | 0.006924 | 1.1837e-05 | 584.9394
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 11 | 1472 | 146232 | 0.026227 | 0.000264 | 99.3424
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CABLE TERMINATOR | 7 | 17 | 3105 | 0.00055912 | 3.0612e-06 | 182.6471
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | JUMPER/RISER | 14 | 51 | 5195 | 0.00093172 | 9.1469e-06 | 101.8627
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | FUSE | 18 | 82 | 10590 | 0.0018993 | 1.4707e-05 | 129.1463
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | FUSE | 5 | 12 | 1598 | 0.0002866 | 2.1522e-06 | 133.1667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | SPLICE, OH | 2 | 22 | 11474 | 0.0020579 | 3.9457e-06 | 521.5455
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 1 | 2 | 242 | 4.3403e-05 | 3.587e-07 | 121
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 13 | 2782 | 0.00049895 | 2.3316e-06 | 214
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 443 | 27349 | 5425222 | 0.96612 | 0.0048703 | 198.37
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | FUSE | 4 | 14 | 1205 | 0.00021612 | 2.5109e-06 | 86.0714
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | FUSE | 2 | 44 | 3003 | 0.00054757 | 8.023e-06 | 68.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 1114 | 271485 | 0.049503 | 0.00020313 | 243.7029
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | BREAKER | 3 | 1193 | 86881 | 0.015842 | 0.00021753 | 72.8256
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 2 | 10 | 2526 | 0.0004606 | 1.8234e-06 | 252.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 32 | 3232 | 0.00058933 | 5.8349e-06 | 101
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | ARRESTER | 2 | 2 | 180 | 3.2822e-05 | 3.6468e-07 | 90
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | CUTOUT | 1 | 0 | 0 | 0 | 0
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | SPLICE, UG | 1 | 1 | 110 | 1.9589e-05 | 1.7808e-07 | 110
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | SWITCH, OH | 1 | 1 | 203 | 3.6408e-05 | 1.7935e-07 | 203
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | GUY/ANCHOR | 1 | 6 | 660 | 0.00011837 | 1.0761e-06 | 110
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | METERING | 1 | 1 | 139 | 2.5165e-05 | 1.8105e-07 | 139
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 1 | 289 | 5.2322e-05 | 1.8105e-07 | 289
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CROSSARM | 2 | 168 | 160251 | 0.02922 | 3.0633e-05 | 953.875
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | BREAKER | 1 | 81 | 2592 | 0.00046675 | 1.4586e-05 | 32
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | CONDUCTOR UG | 2 | 18 | 1291 | 0.00023247 | 3.2413e-06 | 71.7222
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONN/CLAMP | 1 | 15 | 1275 | 0.00022959 | 2.7011e-06 | 85
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | METERING | 1 | 530 | 95400 | 0.017179 | 9.5438e-05 | 180
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 2 | 132 | 2.3769e-05 | 3.6014e-07 | 66
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 6 | 115 | 56643 | 0.010087 | 2.0479e-05 | 492.5478
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 4 | 300 | 5.3424e-05 | 7.1232e-07 | 75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 3 | 55 | 4409 | 0.00078515 | 9.7944e-06 | 80.1636
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | ARRESTER | 1 | 1 | 30 | 5.3424e-06 | 1.7808e-07 | 30
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | NONE | 22 | 810 | 88274 | 0.01572 | 0.00014424 | 108.9802
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 7 | 12 | 1904 | 0.00033906 | 2.137e-06 | 158.6667
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | METERING | 1 | 1 | 77 | 1.3712e-05 | 1.7808e-07 | 77
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 4 | 13 | 1778 | 0.00031663 | 2.315e-06 | 136.7692
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | TRANSFORMER, UG | 1 | 1 | 397 | 7.0698e-05 | 1.7808e-07 | 397
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 8 | 130 | 15752 | 0.0028051 | 2.315e-05 | 121.1692
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 1835 | 121110 | 0.021567 | 0.00032678 | 66
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | FUSE | 5 | 29 | 1943 | 0.00035429 | 5.2879e-06 | 67
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 82 | 1.4952e-05 | 1.8234e-07 | 82
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONN/CLAMP | 1 | 5 | 870 | 0.00015751 | 9.0523e-07 | 174
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 1 | 84 | 1.5208e-05 | 1.8105e-07 | 84
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | POLE HARDWARE | 1 | 20 | 1600 | 0.00028967 | 3.6209e-06 | 80
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 43 | 3703 | 0.00066681 | 7.7431e-06 | 86.1163
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 238 | 88536 | 0.016144 | 4.3397e-05 | 372
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | NONE | 1 | 1 | 50 | 9.1171e-06 | 1.8234e-07 | 50
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | NONE | 1 | 12 | 1008 | 0.00018151 | 2.1609e-06 | 84
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CIRCUIT SWITCHER | 1 | 6 | 972 | 0.00017598 | 1.0863e-06 | 162
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | PEDESTAL | 1 | 6 | 384 | 6.8383e-05 | 1.0685e-06 | 64
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 8 | 105 | 25589 | 0.0045569 | 1.8698e-05 | 243.7048
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 3 | 16 | 1849 | 0.00032927 | 2.8493e-06 | 115.5625
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 4 | 1009 | 134874 | 0.024018 | 0.00017968 | 133.671
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | FUSE | 1 | 1 | 56 | 1.0044e-05 | 1.7935e-07 | 56
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 22 | 2530 | 0.00045054 | 3.9178e-06 | 115
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | CONN/CLAMP | 1 | 3 | 432 | 7.693e-05 | 5.3424e-07 | 144
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE HARDWARE | 1 | 7 | 1036 | 0.00018655 | 1.2605e-06 | 148
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | BREAKER | 1 | 2 | 482 | 8.6795e-05 | 3.6014e-07 | 241
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 12 | 52 | 9002 | 0.0016031 | 9.2601e-06 | 173.1154
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | POLE | 2 | 61 | 24093 | 0.0042905 | 1.0863e-05 | 394.9672
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | ARRESTER | 2 | 385 | 32782 | 0.0058378 | 6.8561e-05 | 85.1481
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | NONE | 6 | 1959 | 27510 | 0.004899 | 0.00034886 | 14.0429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 12 | 587 | 239291 | 0.042613 | 0.00010453 | 407.6508
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | POLE | 1 | 37 | 3552 | 0.00063254 | 6.589e-06 | 96
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 3 | 1383 | 0.00024628 | 5.3424e-07 | 461
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE | 4 | 138 | 106126 | 0.018899 | 2.4575e-05 | 769.029
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 14 | 5613 | 0.00099956 | 2.4931e-06 | 400.9286
AEP Total | 2025 | 5615460 | PARTIAL POWER | ABI | NONE | 1 | 2 | 56 | 9.9725e-06 | 3.5616e-07 | 28
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR UG | 3 | 256 | 112805 | 0.020423 | 4.6348e-05 | 440.6445
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | SWITCH, UG | 1 | 60 | 23280 | 0.0042449 | 1.0941e-05 | 388
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | METERING | 1 | 1 | 133 | 2.4079e-05 | 1.8105e-07 | 133
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONN/CLAMP | 1 | 4 | 204 | 3.6735e-05 | 7.2029e-07 | 51
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 1 | 352 | 66176 | 0.011916 | 6.3385e-05 | 188
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | CONN/CLAMP | 1 | 1 | 83 | 1.4781e-05 | 1.7808e-07 | 83
AEP Total | 2025 | 5615460 | PARTIAL POWER | WL | ARRESTER | 1 | 2 | 160 | 2.8493e-05 | 3.5616e-07 | 80
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CAPACITOR | 1 | 908 | 36320 | 0.0066227 | 0.00016557 | 40
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | SWITCH, OH | 1 | 2 | 482 | 8.7889e-05 | 3.6468e-07 | 241
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONN/CLAMP | 1 | 1 | 89 | 1.6026e-05 | 1.8007e-07 | 89
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | SWITCH, OH | 1 | 44 | 2640 | 0.00048138 | 8.023e-06 | 60
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | SWITCH, OH | 1 | 100 | 34435 | 0.0061759 | 1.7935e-05 | 344.35
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 1 | 1 | 178 | 3.2226e-05 | 1.8105e-07 | 178
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | NONE | 124 | 1989 | 348875 | 0.063163 | 0.0003601 | 175.4022
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, OH | 50 | 4091 | 516842 | 0.093572 | 0.00074066 | 126.3363
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | FUSE | 22 | 352 | 48250 | 0.0087355 | 6.3728e-05 | 137.0739
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CIRCUIT SWITCHER | 3 | 14 | 2700 | 0.00048883 | 2.5346e-06 | 192.8571
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | BREAKER | 1 | 824 | 159032 | 0.028792 | 0.00014918 | 193
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 46 | 957 | 295050 | 0.053418 | 0.00017326 | 308.3072
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CROSSARM | 20 | 3375 | 1219527 | 0.22079 | 0.00061103 | 361.3413
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 4 | 118 | 118068 | 0.021376 | 2.1363e-05 | 1000.5763
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | NONE | 5 | 25 | 3937 | 0.00071278 | 4.5262e-06 | 157.48
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | NONE | 39 | 785 | 100567 | 0.018207 | 0.00014212 | 128.1108
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 307 | 34833 | 0.0063064 | 5.5581e-05 | 113.4625
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 11 | 73 | 18859 | 0.0034144 | 1.3216e-05 | 258.3425
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 1 | 3 | 213 | 3.7931e-05 | 5.3424e-07 | 71
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | GUY/ANCHOR | 1 | 3 | 816 | 0.00014635 | 5.3805e-07 | 272
AEP Total | 2025 | 5615460 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 2 | 398 | 7.0876e-05 | 3.5616e-07 | 199
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 1 | 8 | 1872 | 0.00033337 | 1.4246e-06 | 234
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CABLE TERMINATOR | 1 | 2 | 882 | 0.00015707 | 3.5616e-07 | 441
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 12 | 1980 | 0.0003526 | 2.137e-06 | 165
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 9 | 7000 | 817797 | 0.14563 | 0.0012466 | 116.8281
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | ARRESTER | 1 | 5 | 485 | 8.6369e-05 | 8.904e-07 | 97
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 13 | 209 | 3.7219e-05 | 2.315e-06 | 16.0769
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | FUSE | 1 | 2 | 74 | 1.3325e-05 | 3.6014e-07 | 37
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 1 | 264 | 4.7539e-05 | 1.8007e-07 | 264
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | POLE | 1 | 26 | 2184 | 0.0003917 | 4.6631e-06 | 84
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | BREAKER | 1 | 31 | 1116 | 0.00019874 | 5.5205e-06 | 36
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CROSSARM | 1 | 32 | 4448 | 0.00079775 | 5.7392e-06 | 139
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 1 | 166 | 2.9892e-05 | 1.8007e-07 | 166
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 1 | 75 | 1.3505e-05 | 1.8007e-07 | 75
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 5 | 1380 | 0.00024984 | 9.0523e-07 | 276
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE | 88 | 21265 | 3314887 | 0.60015 | 0.00385 | 155.8846
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | TRANSFORMER, OH | 3 | 19 | 6106 | 0.0011055 | 3.4399e-06 | 321.3684
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | JUMPER/RISER | 7 | 232 | 17905 | 0.0032416 | 4.2003e-05 | 77.1767
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 15 | 965 | 164281 | 0.029742 | 0.00017471 | 170.2394
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 15 | 78 | 19110 | 0.0034598 | 1.4122e-05 | 245
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, UG | 2 | 8 | 2519 | 0.00045606 | 1.4484e-06 | 314.875
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 73 | 5216 | 0.00094434 | 1.3216e-05 | 71.4521
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 3 | 681 | 0.00012329 | 5.4314e-07 | 227
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 1 | 351 | 6.3547e-05 | 1.8105e-07 | 351
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | OTHER EQUIPMENT | 1 | 111 | 40404 | 0.007315 | 2.0096e-05 | 364
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE | 29 | 4210 | 808003 | 0.14733 | 0.00076766 | 191.9247
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | NONE | 319 | 16258 | 1229630 | 0.22421 | 0.0029645 | 75.6323
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | METERING | 7 | 12 | 985 | 0.00017961 | 2.1881e-06 | 82.0833
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 18 | 1778 | 198034 | 0.03611 | 0.0003242 | 111.3802
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | SWITCH, OH | 19 | 1646 | 220755 | 0.040253 | 0.00030013 | 134.116
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONDUCTOR UG | 2 | 3 | 642 | 0.00011623 | 5.4314e-07 | 214
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 26 | 1066 | 0.000193 | 4.7072e-06 | 41
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 5 | 391 | 7.0789e-05 | 9.0523e-07 | 78.2
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 2 | 174 | 3.1502e-05 | 3.6209e-07 | 87
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 40 | 1979 | 0.00035829 | 7.2419e-06 | 49.475
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 65 | 11180 | 0.0020241 | 1.1768e-05 | 172
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 45 | 4320 | 0.00078212 | 8.1471e-06 | 96
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 12 | 6668 | 0.0012072 | 2.1726e-06 | 555.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONN/CLAMP | 4 | 16 | 2758 | 0.00049933 | 2.8967e-06 | 172.375
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CUTOUT | 1 | 2 | 66 | 1.1949e-05 | 3.6209e-07 | 33
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | NONE | 60 | 139 | 16150 | 0.0029082 | 2.503e-05 | 116.1871
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | JUMPER/RISER | 18 | 582 | 102989 | 0.018545 | 0.0001048 | 176.957
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | METERING | 2 | 4 | 418 | 7.527e-05 | 7.2029e-07 | 104.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | POLE | 1 | 27 | 38556 | 0.0069429 | 4.8619e-06 | 1428
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 47 | 4374 | 0.00078763 | 8.4634e-06 | 93.0638
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | PEDESTAL | 1 | 1 | 1058 | 0.00019052 | 1.8007e-07 | 1058
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CROSSARM | 42 | 5799 | 747319 | 0.13457 | 0.0010442 | 128.8703
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 161 | 5442 | 483890 | 0.086786 | 0.00097602 | 88.9177
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | FUSE | 145 | 1306 | 191912 | 0.034419 | 0.00023423 | 146.9464
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | ARRESTER | 7 | 31 | 2581 | 0.00046477 | 5.5822e-06 | 83.2581
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | JUMPER/RISER | 3 | 31 | 3523 | 0.00063439 | 5.5822e-06 | 113.6452
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, OH | 39 | 116 | 27866 | 0.0049978 | 2.0805e-05 | 240.2241
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SWITCH, OH | 7 | 40 | 4176 | 0.00075198 | 7.2029e-06 | 104.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 285 | 17345 | 4388003 | 0.80012 | 0.0031627 | 252.9837
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE | 71 | 20245 | 3135061 | 0.57165 | 0.0036915 | 154.8561
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 175 | 1505 | 409625 | 0.074692 | 0.00027442 | 272.1761
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | NONE | 139 | 21298 | 2474559 | 0.45122 | 0.0038835 | 116.1874
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | FUSE | 1 | 2 | 266 | 4.8503e-05 | 3.6468e-07 | 133
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR UG | 9 | 51 | 7741 | 0.0014115 | 9.2994e-06 | 151.7843
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | ARRESTER | 3 | 3 | 195 | 3.5557e-05 | 5.4703e-07 | 65
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | JUMPER/RISER | 1 | 1 | 54 | 9.8465e-06 | 1.8234e-07 | 54
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | INSULATOR | 2 | 121 | 15620 | 0.0028482 | 2.2063e-05 | 129.0909
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 7 | 860 | 402316 | 0.073359 | 0.00015681 | 467.8093
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | JUMPER/RISER | 1 | 7 | 924 | 0.00016848 | 1.2764e-06 | 132
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | NONE | 19 | 63 | 5389 | 0.00098264 | 1.1488e-05 | 85.5397
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | POLE HARDWARE | 1 | 120 | 41400 | 0.0074953 | 2.1726e-05 | 345
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | SWITCH, OH | 4 | 1416 | 170964 | 0.030952 | 0.00025636 | 120.7373
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 17 | 1293 | 398054 | 0.072582 | 0.00023577 | 307.8531
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONN/CLAMP | 2 | 3 | 738 | 0.00013457 | 5.4703e-07 | 246
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | FUSE | 2 | 11 | 1458 | 0.00026585 | 2.0058e-06 | 132.5455
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONDUCTOR UG | 1 | 2 | 612 | 0.00011159 | 3.6468e-07 | 306
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 18 | 80 | 10463 | 0.0019078 | 1.4587e-05 | 130.7875
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 6 | 480 | 8.7524e-05 | 1.0941e-06 | 80
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 41 | 5330 | 0.00097188 | 7.476e-06 | 130
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 5 | 8 | 725 | 0.0001322 | 1.4587e-06 | 90.625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CUTOUT | 3 | 61 | 15756 | 0.002873 | 1.1123e-05 | 258.2951
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 37 | 12173 | 0.0022196 | 6.7467e-06 | 329
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | SPLICE, OH | 3 | 4 | 480 | 8.7524e-05 | 7.2937e-07 | 120
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | NONE | 1 | 1062 | 145494 | 0.02653 | 0.00019365 | 137
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | FUSE | 44 | 543 | 72344 | 0.012975 | 9.7387e-05 | 133.2302
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 3 | 94 | 43679 | 0.0078338 | 1.6859e-05 | 464.6702
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | NONE | 84 | 5564 | 1057079 | 0.18959 | 0.0009979 | 189.9854
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | NONE | 121 | 9948 | 1038062 | 0.18618 | 0.0017842 | 104.3488
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 13 | 2050 | 90941 | 0.01631 | 0.00036767 | 44.3615
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 20 | 60 | 14635 | 0.0026248 | 1.0761e-05 | 243.9167
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 7 | 64 | 15912 | 0.0028538 | 1.1478e-05 | 248.625
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 147 | 6260 | 886417 | 0.15962 | 0.0011273 | 141.6002
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 112 | 2933 | 335555 | 0.060424 | 0.00052815 | 114.4068
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | NONE | 110 | 2466 | 429785 | 0.077392 | 0.00044406 | 174.2843
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | ARRESTER | 63 | 1131 | 163808 | 0.029497 | 0.00020366 | 144.8347
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 44 | 151 | 25939 | 0.0046709 | 2.7191e-05 | 171.7815
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | FUSE | 29 | 241 | 26839 | 0.0048329 | 4.3397e-05 | 111.3651
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 3 | 13 | 1639 | 0.00029514 | 2.3409e-06 | 126.0769
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE | 10 | 161 | 52089 | 0.0093798 | 2.8992e-05 | 323.5342
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | FUSE | 1 | 1 | 64 | 1.1525e-05 | 1.8007e-07 | 64
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, OH | 14 | 2924 | 378861 | 0.068222 | 0.00052653 | 129.5694
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 7 | 33 | 12447 | 0.0022414 | 5.9424e-06 | 377.1818
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | FUSE | 30 | 778 | 114749 | 0.020663 | 0.0001401 | 147.4923
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 32 | 110 | 10728 | 0.0019318 | 1.9808e-05 | 97.5273
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | FUSE | 3 | 21 | 7241 | 0.0013039 | 3.7815e-06 | 344.8095
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 1045 | 125400 | 0.022491 | 0.00018742 | 120
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | ARRESTER | 1 | 2 | 142 | 2.5893e-05 | 3.6468e-07 | 71
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 1 | 47 | 8.5701e-06 | 1.8234e-07 | 47
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CONN/CLAMP | 4 | 20 | 5366 | 0.00097845 | 3.6468e-06 | 268.3
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CAPACITOR | 1 | 2 | 798 | 0.00014551 | 3.6468e-07 | 399
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | BREAKER | 1 | 2 | 290 | 5.2879e-05 | 3.6468e-07 | 145
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 148 | 1059 | 341858 | 0.061312 | 0.00018993 | 322.8121
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 18 | 1799 | 149015 | 0.026726 | 0.00032265 | 82.8321
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR UG | 74 | 250 | 72490 | 0.013001 | 4.4838e-05 | 289.96
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | FUSE | 30 | 398 | 64623 | 0.01159 | 7.1381e-05 | 162.3693
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | FUSE | 37 | 1035 | 140500 | 0.025199 | 0.00018563 | 135.7488
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONN/CLAMP | 1 | 0 | 0 | 0 | 0
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | POLE | 4 | 790 | 79617 | 0.014279 | 0.00014169 | 100.781
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | ARRESTER | 19 | 283 | 66820 | 0.011984 | 5.0756e-05 | 236.1131
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 5 | 845 | 0.00015216 | 9.0036e-07 | 169
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AB | NONE | 10 | 8820 | 1167459 | 0.20938 | 0.0015819 | 132.365
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 6 | 38 | 3966 | 0.0007113 | 6.8153e-06 | 104.3684
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 4 | 945 | 94026 | 0.016931 | 0.00017017 | 99.4984
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | INSULATOR | 5 | 409 | 86961 | 0.015596 | 7.3354e-05 | 212.6186
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 454 | 3464 | 722476 | 0.12866 | 0.00061687 | 208.567
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | NONE | 776 | 33137 | 1997396 | 0.3557 | 0.005901 | 60.2769
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 173 | 5227 | 682838 | 0.1216 | 0.00093082 | 130.6367
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 667 | 9205 | 1368312 | 0.24367 | 0.0016392 | 148.6488
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | METERING | 9 | 23 | 2178 | 0.00038786 | 4.0958e-06 | 94.6957
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | NONE | 2 | 2053 | 227883 | 0.040581 | 0.0003656 | 111
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | FUSE | 307 | 3411 | 331784 | 0.059084 | 0.00060743 | 97.2688
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 67 | 10642 | 1773301 | 0.31579 | 0.0018951 | 166.6323
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR UG | 2 | 81 | 14742 | 0.0026253 | 1.4424e-05 | 182
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | PEDESTAL | 2 | 10 | 1454 | 0.00026078 | 1.7935e-06 | 145.4
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | ARRESTER | 7 | 15 | 896 | 0.0001607 | 2.6903e-06 | 59.7333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 2 | 358 | 6.4207e-05 | 3.587e-07 | 179
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | FUSE | 2 | 6 | 519 | 9.3083e-05 | 1.0761e-06 | 86.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | NONE | 15 | 59 | 6051 | 0.0010776 | 1.0507e-05 | 102.5593
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | FUSE | 1 | 4 | 288 | 5.2141e-05 | 7.2419e-07 | 72
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 3 | 4 | 976 | 0.00017797 | 7.2937e-07 | 244
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SWITCH, OH | 4 | 9 | 706 | 0.00012873 | 1.6411e-06 | 78.4444
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | POLE | 2 | 36 | 8202 | 0.0014956 | 6.5643e-06 | 227.8333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | SPLICE, OH | 2 | 2 | 225 | 4.1027e-05 | 3.6468e-07 | 112.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | TRANSFORMER, UG | 2 | 6 | 3841 | 0.00070038 | 1.0941e-06 | 640.1667
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | POLE | 1 | 1 | 177 | 3.2045e-05 | 1.8105e-07 | 177
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | NONE | 17 | 75 | 27284 | 0.0048587 | 1.3356e-05 | 363.7867
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | BREAKER | 2 | 12 | 1000 | 0.00017935 | 2.1522e-06 | 83.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 5 | 159 | 88202 | 0.015707 | 2.8315e-05 | 554.7296
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 29 | 2606 | 0.00046739 | 5.2012e-06 | 89.8621
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | NONE | 52 | 3241 | 110869 | 0.019744 | 0.00057716 | 34.2083
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | NONE | 3 | 12 | 1015 | 0.00018204 | 2.1522e-06 | 84.5833
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 3 | 7 | 2449 | 0.00043923 | 1.2555e-06 | 349.8571
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | NONE | 2 | 14 | 2752 | 0.00049008 | 2.4931e-06 | 196.5714
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 1 | 60 | 3720 | 0.00067831 | 1.0941e-05 | 62
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | ARRESTER | 1 | 1 | 34 | 6.1556e-06 | 1.8105e-07 | 34
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 7 | 1248 | 0.00022756 | 1.2764e-06 | 178.2857
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 81 | 1.4665e-05 | 1.8105e-07 | 81
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 4 | 3394 | 337571 | 0.061116 | 0.00061447 | 99.4611
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WH | NONE | 1 | 1 | 40 | 7.2029e-06 | 1.8007e-07 | 40
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 5 | 226 | 19397 | 0.0034789 | 4.0533e-05 | 85.8274
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 3 | 286 | 62345 | 0.011182 | 5.1294e-05 | 217.9895
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 34 | 8364 | 0.0015001 | 6.0979e-06 | 246
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 2 | 95 | 12870 | 0.0023082 | 1.7038e-05 | 135.4737
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 68 | 9140 | 605100 | 0.10776 | 0.0016276 | 66.2035
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | FUSE | 27 | 376 | 36497 | 0.0064994 | 6.6958e-05 | 97.0665
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 8 | 440 | 48775 | 0.0086858 | 7.8355e-05 | 110.8523
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | TRANSFORMER, OH | 1 | 4 | 900 | 0.00016027 | 7.1232e-07 | 225
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 2 | 408 | 7.3175e-05 | 3.587e-07 | 204
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | TRANSFORMER, OH | 6 | 13 | 2841 | 0.00050953 | 2.3316e-06 | 218.5385
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 103 | 2675 | 884964 | 0.15759 | 0.00047636 | 330.8277
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | NONE | 69 | 355 | 39235 | 0.006987 | 6.3218e-05 | 110.5211
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 31 | 3323 | 84897 | 0.015118 | 0.00059176 | 25.5483
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | SWITCH, UG | 1 | 354 | 73632 | 0.013426 | 6.4549e-05 | 208
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 85 | 1.5499e-05 | 1.8234e-07 | 85
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 70 | 1.2605e-05 | 1.8007e-07 | 70
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | RECLOSER, LINE/OCR/BR | 1 | 52 | 3692 | 0.00066483 | 9.3637e-06 | 71
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | ARRESTER | 2 | 121 | 10517 | 0.0018938 | 2.1789e-05 | 86.9174
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 2 | 300 | 5.3805e-05 | 3.587e-07 | 150
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 243 | 50745 | 0.0091377 | 4.3757e-05 | 208.8272
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 5 | 420 | 7.5327e-05 | 8.9675e-07 | 84
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 15 | 2100 | 0.00037664 | 2.6903e-06 | 140
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | POLE | 2 | 29 | 11009 | 0.0019745 | 5.2012e-06 | 379.6207
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | NONE | 252 | 20167 | 1456615 | 0.25939 | 0.0035913 | 72.2276
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | ARRESTER | 1 | 40 | 960 | 0.0001738 | 7.2419e-06 | 24
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 2 | 52 | 9.4144e-06 | 3.6209e-07 | 26
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 2 | 149 | 2.6976e-05 | 3.6209e-07 | 74.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | SPLICE, OH | 2 | 2 | 261 | 4.7253e-05 | 3.6209e-07 | 130.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | TRANSFORMER, UG | 2 | 21 | 12585 | 0.0022662 | 3.7815e-06 | 599.2857
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 3 | 198 | 38140 | 0.006792 | 3.526e-05 | 192.6263
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONDUCTOR UG | 2 | 5 | 355 | 6.3218e-05 | 8.904e-07 | 71
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | SWITCH, OH | 2 | 12 | 471 | 8.3876e-05 | 2.137e-06 | 39.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 5 | 52 | 15075 | 0.0026846 | 9.2601e-06 | 289.9038
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 3 | 7 | 1416 | 0.00025216 | 1.2466e-06 | 202.2857
AEP Total | 2025 | 5615460 | PARTIAL POWER | WL | TRANSFORMER, UG | 1 | 7 | 1246 | 0.00022189 | 1.2466e-06 | 178
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | TRANSFORMER, UG | 1 | 7 | 1113 | 0.0001982 | 1.2466e-06 | 159
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | METERING | 1 | 1 | 95 | 1.6918e-05 | 1.7808e-07 | 95
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 12 | 12240 | 0.0021797 | 2.137e-06 | 1020
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 3 | 16 | 1050 | 0.00018698 | 2.8493e-06 | 65.625
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 1 | 535 | 9.5273e-05 | 1.7808e-07 | 535
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, UG | 1 | 5 | 1275 | 0.00022705 | 8.904e-07 | 255
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 1 | 9 | 963 | 0.00017149 | 1.6027e-06 | 107
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 3 | 8 | 465 | 8.2807e-05 | 1.4246e-06 | 58.125
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | TRANSFORMER, POWER - LTC | 1 | 8 | 1224 | 0.00022041 | 1.4406e-06 | 153
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | O | NONE | 1 | 1067 | 8536 | 0.0015371 | 0.00019214 | 8
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 2 | 28 | 4536 | 0.00080777 | 4.9862e-06 | 162
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 2 | 1299 | 59754 | 0.010641 | 0.00023133 | 46
AEP Total | 2025 | 5615460 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 238 | 4.2383e-05 | 3.5616e-07 | 119
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 3 | 139 | 15952 | 0.0028407 | 2.4753e-05 | 114.7626
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 3 | 29 | 6453 | 0.0011491 | 5.1643e-06 | 222.5172
AEP Total | 2023 | 5575683 | DISTRIBUTION SOURCE | A | NONE | 1 | 245 | 32095 | 0.0057562 | 4.3941e-05 | 131
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | METERING | 1 | 1 | 97 | 1.7687e-05 | 1.8234e-07 | 97
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 7 | 1883 | 0.00033908 | 1.2605e-06 | 269
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | NONE | 54 | 1511 | 911738 | 0.16507 | 0.00027356 | 603.4004
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 121 | 8272 | 1677667 | 0.30374 | 0.0014976 | 202.8127
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 87 | 3225 | 283705 | 0.051364 | 0.00058387 | 87.9705
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | POLE | 8 | 315 | 68227 | 0.012352 | 5.703e-05 | 216.5937
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | ARRESTER | 7 | 626 | 66629 | 0.012063 | 0.00011334 | 106.4361
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 5 | 14 | 4692 | 0.00084947 | 2.5346e-06 | 335.1429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 6 | 397 | 69761 | 0.01263 | 7.1875e-05 | 175.7204
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 28 | 976 | 102832 | 0.018617 | 0.0001767 | 105.3607
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | INSULATOR | 15 | 471 | 106847 | 0.019344 | 8.5273e-05 | 226.8514
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR UG | 9 | 26 | 6247 | 0.001131 | 4.7072e-06 | 240.2692
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | OTHER EQUIPMENT | 1 | 3 | 165 | 2.9873e-05 | 5.4314e-07 | 55
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | SWITCH, OH | 3 | 207 | 47667 | 0.0086299 | 3.7477e-05 | 230.2754
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | POLE | 1 | 109 | 322858 | 0.058452 | 1.9734e-05 | 2962
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 3 | 2003 | 0.00036264 | 5.4314e-07 | 667.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CROSSARM | 2 | 71 | 39084 | 0.007076 | 1.2854e-05 | 550.4789
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 905 | 46486 | 6245578 | 1.1122 | 0.0082782 | 134.354
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 181 | 2998 | 399995 | 0.071231 | 0.00053388 | 133.4206
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 67 | 2921 | 215697 | 0.038411 | 0.00052017 | 73.8435
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 6 | 1428 | 0.00025853 | 1.0863e-06 | 238
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | A | NONE | 4 | 2537 | 466873 | 0.083141 | 0.00045179 | 184.0256
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 2 | 6 | 714 | 0.00012715 | 1.0685e-06 | 119
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 1 | 2 | 230 | 4.0958e-05 | 3.5616e-07 | 115
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | PEDESTAL | 1 | 1 | 191 | 3.458e-05 | 1.8105e-07 | 191
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | ARRESTER | 1 | 2 | 86 | 1.5681e-05 | 3.6468e-07 | 43
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 1 | 124 | 2.2329e-05 | 1.8007e-07 | 124
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, OH | 1 | 2 | 432 | 7.7791e-05 | 3.6014e-07 | 216
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 3 | 7 | 2386 | 0.00043507 | 1.2764e-06 | 340.8571
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | JUMPER/RISER | 1 | 1 | 28 | 5.042e-06 | 1.8007e-07 | 28
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | SPLICE, OH | 1 | 2 | 498 | 8.9676e-05 | 3.6014e-07 | 249
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 73 | 1.3145e-05 | 1.8007e-07 | 73
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 4 | 19 | 3830 | 0.00068205 | 3.3835e-06 | 201.5789
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 5 | 177 | 39015 | 0.0069478 | 3.152e-05 | 220.4237
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 4 | 377 | 83293 | 0.014833 | 6.7136e-05 | 220.9363
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 3 | 100 | 19559 | 0.0034831 | 1.7808e-05 | 195.59
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | SWITCH, OH | 2 | 316 | 16255 | 0.0028947 | 5.6273e-05 | 51.4399
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 4 | 284 | 5.0575e-05 | 7.1232e-07 | 71
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | FUSE | 2 | 2 | 385 | 6.8561e-05 | 3.5616e-07 | 192.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | VIN | NONE | 5 | 48 | 5345 | 0.00095184 | 8.5478e-06 | 111.3542
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | NONE | 3 | 13 | 2168 | 0.00038608 | 2.315e-06 | 166.7692
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | SPLICE, OH | 2 | 26 | 3138 | 0.00055881 | 4.6301e-06 | 120.6923
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | ARRESTER | 11 | 117 | 58562 | 0.010429 | 2.0835e-05 | 500.5299
AEP Total | 2024 | 5615460 | DISTRIBUTION SOURCE | TIR | NONE | 1 | 49 | 21731 | 0.0038699 | 8.7259e-06 | 443.4898
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 2 | 10 | 1198 | 0.00021334 | 1.7808e-06 | 119.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 1 | 1 | 10 | 1.7808e-06 | 1.7808e-07 | 10
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 1 | 13 | 2067 | 0.00036809 | 2.315e-06 | 159
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | SWITCH, OH | 1 | 16 | 3456 | 0.00062233 | 2.8812e-06 | 216
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CAPACITOR | 1 | 22 | 1430 | 0.0002575 | 3.9616e-06 | 65
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 7 | 469 | 30637 | 0.0054558 | 8.3519e-05 | 65.3241
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 4 | 200 | 3.5616e-05 | 7.1232e-07 | 50
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 882 | 0.00015707 | 1.7808e-07 | 882
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 2 | 122 | 2.1726e-05 | 3.5616e-07 | 61
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | REGULATOR | 1 | 1043 | 185654 | 0.033612 | 0.00018883 | 178
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 2 | 47 | 21472 | 0.0038874 | 8.5092e-06 | 456.8511
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONN/CLAMP | 45 | 838 | 109591 | 0.019734 | 0.0001509 | 130.7768
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 3 | 5 | 354 | 6.409e-05 | 9.0523e-07 | 70.8
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 4 | 682 | 529154 | 0.096487 | 0.00012436 | 775.8856
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | FUSE | 33 | 304 | 50879 | 0.0092774 | 5.5432e-05 | 167.3651
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | NONE | 39 | 19960 | 1556348 | 0.28379 | 0.0036395 | 77.9733
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | NONE | 36 | 148 | 21031 | 0.0038348 | 2.6987e-05 | 142.1014
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CABLE TERMINATOR | 1 | 1 | 25 | 4.5586e-06 | 1.8234e-07 | 25
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | NONE | 25 | 370 | 12080 | 0.0022027 | 6.7467e-05 | 32.6486
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 8 | 39 | 5913 | 0.0010782 | 7.1113e-06 | 151.6154
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 143 | 24116 | 0.0043974 | 2.6075e-05 | 168.6434
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CUTOUT | 8 | 82 | 6100 | 0.0011123 | 1.4952e-05 | 74.3902
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 3 | 1356 | 0.00024726 | 5.4703e-07 | 452
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 301 | 47515 | 0.008664 | 5.4885e-05 | 157.8571
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | ARRESTER | 3 | 17 | 2727 | 0.00049725 | 3.0998e-06 | 160.4118
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | NONE | 12 | 127 | 23645 | 0.0043115 | 2.3157e-05 | 186.1811
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 4 | 16 | 2438 | 0.00044455 | 2.9175e-06 | 152.375
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 39 | 4336 | 0.00079064 | 7.1113e-06 | 111.1795
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 5 | 1590 | 0.00028992 | 9.1171e-07 | 318
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | TRANSFORMER, OH | 3 | 8 | 1115 | 0.00020331 | 1.4587e-06 | 139.375
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | FUSE | 18 | 97 | 9271 | 0.0016694 | 1.7467e-05 | 95.5773
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 77 | 10545 | 1166114 | 0.20998 | 0.0018989 | 110.5845
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | NONE | 242 | 7603 | 498172 | 0.089707 | 0.0013691 | 65.5231
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | ARRESTER | 28 | 654 | 132797 | 0.023913 | 0.00011777 | 203.0535
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CROSSARM | 5 | 1251 | 231734 | 0.041729 | 0.00022527 | 185.239
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 3 | 16 | 3421 | 0.00061603 | 2.8812e-06 | 213.8125
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR UG | 42 | 199 | 49120 | 0.0088451 | 3.5834e-05 | 246.8342
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 9 | 85 | 15573 | 0.0028043 | 1.5306e-05 | 183.2118
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 5 | 2320 | 0.00041777 | 9.0036e-07 | 464
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | NONE | 6 | 3737 | 315035 | 0.056729 | 0.00067293 | 84.3016
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CROSSARM | 16 | 1451 | 365679 | 0.065849 | 0.00026128 | 252.0186
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 439 | 2609 | 703601 | 0.12619 | 0.00046792 | 269.6823
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 6 | 2346 | 0.00042076 | 1.0761e-06 | 391
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | NONE | 42 | 298 | 15495 | 0.0027902 | 5.3661e-05 | 51.9966
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WT | POLE | 1 | 348 | 84019 | 0.014962 | 6.1972e-05 | 241.4339
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | SPLICE, OH | 1 | 4 | 372 | 6.6246e-05 | 7.1232e-07 | 93
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 4 | 326 | 5.8054e-05 | 7.1232e-07 | 81.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | TRANSFORMER, UG | 2 | 3 | 969 | 0.00017379 | 5.3805e-07 | 323
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | REGULATOR | 1 | 2 | 162 | 2.9539e-05 | 3.6468e-07 | 81
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 3 | 675 | 0.00012155 | 5.4022e-07 | 225
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | CONN/CLAMP | 1 | 1 | 76 | 1.3858e-05 | 1.8234e-07 | 76
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | NONE | 27 | 4510 | 515769 | 0.093378 | 0.00081652 | 114.3612
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | NONE | 10 | 24 | 1651 | 0.00029891 | 4.3451e-06 | 68.7917
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | FUSE | 9 | 586 | 50712 | 0.0091812 | 0.00010609 | 86.5392
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE | 13 | 3907 | 697730 | 0.12632 | 0.00070735 | 178.5846
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 115 | 7843 | 1022025 | 0.18503 | 0.0014199 | 130.3105
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | NONE | 87 | 474 | 50608 | 0.0091624 | 8.5816e-05 | 106.7679
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | NONE | 46 | 3930 | 335315 | 0.060708 | 0.00071151 | 85.3219
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | NONE | 105 | 4415 | 370331 | 0.067047 | 0.00079932 | 83.8802
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | NONE | 26 | 328 | 33041 | 0.005982 | 5.9383e-05 | 100.7348
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE | 6 | 252 | 52815 | 0.009562 | 4.5624e-05 | 209.5833
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 3 | 712 | 17481 | 0.0031649 | 0.00012891 | 24.552
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 17 | 799 | 0.00014466 | 3.0778e-06 | 47
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CONDUCTOR UG | 1 | 2 | 608 | 0.00011008 | 3.6209e-07 | 304
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | FUSE | 46 | 560 | 68509 | 0.012403 | 0.00010139 | 122.3375
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | NONE | 9 | 34 | 2361 | 0.00042745 | 6.1556e-06 | 69.4412
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | FUSE | 8 | 756 | 126606 | 0.022922 | 0.00013687 | 167.4683
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 4 | 8 | 987 | 0.00017869 | 1.4484e-06 | 123.375
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | NONE | 16 | 991 | 334957 | 0.061077 | 0.0001807 | 337.999
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CUTOUT | 3 | 7 | 636 | 0.00011597 | 1.2764e-06 | 90.8571
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | NONE | 79 | 3979 | 407907 | 0.074379 | 0.00072554 | 102.515
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | NONE | 49 | 143 | 9709 | 0.0017704 | 2.6075e-05 | 67.8951
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 38 | 3990 | 0.00072754 | 6.929e-06 | 105
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | NONE | 116 | 8136 | 1198041 | 0.21845 | 0.0014835 | 147.2518
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 9 | 1067 | 0.00019456 | 1.6411e-06 | 118.5556
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CROSSARM | 11 | 1867 | 380841 | 0.069443 | 0.00034043 | 203.9855
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | SPLICE, OH | 2 | 2 | 74 | 1.3493e-05 | 3.6468e-07 | 37
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | CONDUCTOR UG | 2 | 3 | 793 | 0.0001446 | 5.4703e-07 | 264.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, OH | 3 | 138 | 12999 | 0.0023703 | 2.5163e-05 | 94.1957
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | SPLICE, UG | 1 | 1 | 483 | 8.7445e-05 | 1.8105e-07 | 483
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 3 | 1134 | 0.00020531 | 5.4314e-07 | 378
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 27 | 1322 | 208367 | 0.037371 | 0.0002371 | 157.615
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE | 141 | 9343 | 1818365 | 0.32612 | 0.0016757 | 194.6232
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 13 | 492 | 68421 | 0.012321 | 8.8595e-05 | 139.0671
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE | 8 | 1164 | 785332 | 0.14142 | 0.0002096 | 674.6838
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 2 | 16 | 9360 | 0.0016855 | 2.8812e-06 | 585
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 1 | 47 | 13160 | 0.0023697 | 8.4634e-06 | 280
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | NONE | 13 | 35 | 4923 | 0.00088294 | 6.2773e-06 | 140.6571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR UG | 11 | 186 | 40560 | 0.0072744 | 3.3359e-05 | 218.0645
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | ARRESTER | 2 | 106 | 11514 | 0.002065 | 1.9011e-05 | 108.6226
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | NONE | 11 | 42 | 5245 | 0.00094448 | 7.563e-06 | 124.881
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 4 | 30 | 10432 | 0.0018785 | 5.4022e-06 | 347.7333
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | NONE | 7 | 3556 | 603846 | 0.10874 | 0.00064034 | 169.8105
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CUTOUT | 6 | 88 | 5231 | 0.00093818 | 1.5783e-05 | 59.4432
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 1 | 229 | 4.1071e-05 | 1.7935e-07 | 229
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 1 | 42 | 9198 | 0.0016497 | 7.5327e-06 | 219
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 6 | 68 | 10433 | 0.0018712 | 1.2196e-05 | 153.4265
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | INSULATOR | 4 | 45 | 15643 | 0.0028056 | 8.0708e-06 | 347.6222
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | NONE | 1 | 25 | 2675 | 0.0004843 | 4.5262e-06 | 107
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CUTOUT | 7 | 37 | 20195 | 0.0036824 | 6.7467e-06 | 545.8108
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 1309 | 226116 | 0.040717 | 0.00023571 | 172.7395
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CROSSARM | 2 | 56 | 8369 | 0.001507 | 1.0084e-05 | 149.4464
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 93 | 17763 | 0.0031986 | 1.6747e-05 | 191
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 16 | 1168 | 0.00020948 | 2.8696e-06 | 73
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 25 | 486 | 53665 | 0.0095567 | 8.6547e-05 | 110.4218
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | NONE | 41 | 121 | 8843 | 0.0015748 | 2.1548e-05 | 73.0826
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | NONE | 47 | 6799 | 1349136 | 0.24025 | 0.0012108 | 198.4315
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | NONE | 163 | 6223 | 773578 | 0.13776 | 0.0011082 | 124.3095
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | FUSE | 64 | 1109 | 125597 | 0.022366 | 0.00019749 | 113.2525
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABX | NONE | 2 | 522 | 103356 | 0.018537 | 9.3621e-05 | 198
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 13 | 130 | 8238 | 0.001467 | 2.315e-05 | 63.3692
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | TRANSFORMER, OH | 1 | 2 | 912 | 0.00016357 | 3.587e-07 | 456
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 78 | 280 | 51109 | 0.0091015 | 4.9862e-05 | 182.5321
AEP Total | 2022 | 5553337 | PARTIAL POWER | WFS | NONE | 1 | 1 | 48 | 8.6435e-06 | 1.8007e-07 | 48
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CAPACITOR | 1 | 1 | 52 | 9.4144e-06 | 1.8105e-07 | 52
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONN/CLAMP | 1 | 5 | 290 | 5.2879e-05 | 9.1171e-07 | 58
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RELAY | 3 | 4843 | 295779 | 0.053933 | 0.00088308 | 61.0735
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | TRANSFORMER, OH | 1 | 21 | 5586 | 0.0010186 | 3.8292e-06 | 266
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CABLE TERMINATOR | 1 | 9 | 585 | 0.00010591 | 1.6294e-06 | 65
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 96 | 1.738e-05 | 1.8105e-07 | 96
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | BREAKER | 1 | 3 | 153 | 2.7898e-05 | 5.4703e-07 | 51
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | FUSE | 1 | 2 | 308 | 5.5462e-05 | 3.6014e-07 | 154
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | STATIC WIRE | 1 | 1053 | 60021 | 0.010808 | 0.00018962 | 57
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | CUTOUT | 1 | 1 | 105 | 1.9146e-05 | 1.8234e-07 | 105
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 3 | 9 | 859 | 0.00015468 | 1.6206e-06 | 95.4444
AEP Total | 2022 | 5553337 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 3 | 5 | 469 | 8.4454e-05 | 9.0036e-07 | 93.8
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | ARRESTER | 1 | 1 | 40 | 7.2029e-06 | 1.8007e-07 | 40
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | INSULATOR | 1 | 608 | 32832 | 0.0059121 | 0.00010948 | 54
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 150 | 14691 | 3114958 | 0.55471 | 0.0026162 | 212.0317
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 4 | 4 | 530 | 9.4382e-05 | 7.1232e-07 | 132.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | NONE | 1 | 6 | 4452 | 0.00079281 | 1.0685e-06 | 742
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE | 25 | 3371 | 370429 | 0.065966 | 0.00060031 | 109.887
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 26 | 100 | 20082 | 0.0035762 | 1.7808e-05 | 200.82
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | NONE | 18 | 339 | 25314 | 0.0045079 | 6.0369e-05 | 74.6726
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 3 | 624 | 0.00011236 | 5.4022e-07 | 208
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | FUSE | 1 | 4 | 176 | 3.1693e-05 | 7.2029e-07 | 44
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | JUMPER/RISER | 1 | 1 | 21 | 3.802e-06 | 1.8105e-07 | 21
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CROSSARM | 1 | 64 | 9420 | 0.0017055 | 1.1587e-05 | 147.1875
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | SWITCH, UG | 1 | 9 | 2538 | 0.00045197 | 1.6027e-06 | 282
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | AF | SWITCH, OH | 1 | 29 | 1160 | 0.00020657 | 5.1643e-06 | 40
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | SPLICE, OH | 1 | 972 | 15552 | 0.0027695 | 0.00017309 | 16
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | FUSE | 22 | 165 | 17388 | 0.0030965 | 2.9383e-05 | 105.3818
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | POLE | 1 | 5 | 705 | 0.00012555 | 8.904e-07 | 141
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 9 | 217 | 36538 | 0.0065067 | 3.8643e-05 | 168.3779
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE | 4 | 87 | 25834 | 0.0046005 | 1.5493e-05 | 296.9425
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 11 | 137 | 14796 | 0.0026349 | 2.4397e-05 | 108
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | NONE | 30 | 653 | 58869 | 0.010483 | 0.00011629 | 90.1516
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | FUSE | 7 | 10 | 490 | 8.7259e-05 | 1.7808e-06 | 49
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | ARRESTER | 5 | 12 | 829 | 0.00014763 | 2.137e-06 | 69.0833
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 8 | 18 | 4519 | 0.00080474 | 3.2054e-06 | 251.0556
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 3 | 62 | 10472 | 0.0018649 | 1.1041e-05 | 168.9032
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 2 | 27 | 3039 | 0.00054118 | 4.8082e-06 | 112.5556
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 4 | 1067 | 75561 | 0.013456 | 0.00019001 | 70.8163
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 2 | 5 | 1055 | 0.00018787 | 8.904e-07 | 211
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | METERING | 1 | 1 | 269 | 4.7903e-05 | 1.7808e-07 | 269
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 124 | 11730 | 0.0020889 | 2.2082e-05 | 94.5968
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SWITCH, OH | 1 | 8 | 1208 | 0.00021512 | 1.4246e-06 | 151
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 6 | 1092 | 765383 | 0.1363 | 0.00019446 | 700.9002
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | NONE | 4 | 20 | 1375 | 0.0002476 | 3.6014e-06 | 68.75
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | CONDUCTOR UG | 1 | 6 | 1278 | 0.00022921 | 1.0761e-06 | 213
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 1 | 158 | 2.8451e-05 | 1.8007e-07 | 158
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | NONE | 8 | 19 | 2053 | 0.0003656 | 3.3835e-06 | 108.0526
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 2 | 1482 | 0.00026391 | 3.5616e-07 | 741
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 173 | 107952 | 0.019224 | 3.0808e-05 | 624
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | FUSE | 97 | 1268 | 245509 | 0.044209 | 0.00022833 | 193.6191
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 326 | 1871 | 513018 | 0.09238 | 0.00033691 | 274.1945
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | NONE | 2 | 2 | 133 | 2.395e-05 | 3.6014e-07 | 66.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | JUMPER/RISER | 7 | 22 | 1737 | 0.00031278 | 3.9616e-06 | 78.9545
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONN/CLAMP | 2 | 6 | 829 | 0.00014928 | 1.0804e-06 | 138.1667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 447 | 23095 | 4495986 | 0.80636 | 0.0041421 | 194.6736
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 1371 | 158726 | 0.028582 | 0.00024688 | 115.7739
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | NONE | 31 | 2251 | 93586 | 0.016785 | 0.00040372 | 41.5753
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | NONE | 3 | 1435 | 175016 | 0.031913 | 0.00026166 | 121.9624
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 3 | 10 | 2196 | 0.00040042 | 1.8234e-06 | 219.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 4 | 151 | 23061 | 0.004205 | 2.7534e-05 | 152.7219
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 154 | 13090 | 0.0023869 | 2.8081e-05 | 85
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | ARRESTER | 1 | 4 | 568 | 0.00010357 | 7.2937e-07 | 142
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | REGULATOR | 3 | 1550 | 170284 | 0.03105 | 0.00028263 | 109.8606
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 2 | 196 | 22311 | 0.0040682 | 3.5739e-05 | 113.8316
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | ARRESTER | 129 | 3851 | 551950 | 0.098992 | 0.00069068 | 143.3264
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 26 | 113 | 26534 | 0.0047589 | 2.0267e-05 | 234.8142
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | ARRESTER | 63 | 2060 | 351786 | 0.063093 | 0.00036946 | 170.7699
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | BREAKER | 1 | 150 | 22950 | 0.0041161 | 2.6903e-05 | 153
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | NONE | 17 | 53 | 4106 | 0.00073641 | 9.5056e-06 | 77.4717
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONN/CLAMP | 1 | 3 | 435 | 7.8017e-05 | 5.3805e-07 | 145
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | NONE | 30 | 90 | 17899 | 0.0032102 | 1.6142e-05 | 198.8778
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CUTOUT | 3 | 9 | 381 | 6.8332e-05 | 1.6142e-06 | 42.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | SPLICE, OH | 1 | 1 | 90 | 1.6142e-05 | 1.7935e-07 | 90
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1308 | 86328 | 0.015373 | 0.00023293 | 66
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 204 | 3868 | 979352 | 0.1744 | 0.00068881 | 253.1934
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 824 | 33784 | 0.0060835 | 0.00014838 | 41
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | NONE | 20 | 94 | 9287 | 0.0016723 | 1.6927e-05 | 98.7979
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 1 | 1 | 242 | 4.3577e-05 | 1.8007e-07 | 242
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 52 | 4732 | 0.0008521 | 9.3637e-06 | 91
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABX | NONE | 1 | 179 | 92543 | 0.016664 | 3.2233e-05 | 517
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 4 | 824 | 0.00014838 | 7.2029e-07 | 206
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 1 | 10 | 930 | 0.0001668 | 1.7935e-06 | 93
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONN/CLAMP | 3 | 7 | 625 | 0.00011209 | 1.2555e-06 | 89.2857
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | NONE | 3 | 812 | 13905 | 0.0025039 | 0.00014622 | 17.1244
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | ARRESTER | 1 | 19 | 2375 | 0.00042767 | 3.4214e-06 | 125
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | FUSE | 268 | 4943 | 1021809 | 0.18196 | 0.00088025 | 206.7184
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CROSSARM | 2 | 37 | 2747 | 0.00049733 | 6.6987e-06 | 74.2432
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CUTOUT | 1 | 4 | 392 | 7.1478e-05 | 7.2937e-07 | 98
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CIRCUIT SWITCHER | 1 | 49 | 17346 | 0.0031629 | 8.9348e-06 | 354
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 231 | 79695 | 0.014532 | 4.2121e-05 | 345
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 2 | 4 | 1005 | 0.00018325 | 7.2937e-07 | 251.25
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | NONE | 1 | 8 | 2336 | 0.00042292 | 1.4484e-06 | 292
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABI | NONE | 8 | 7225 | 790625 | 0.14314 | 0.0013081 | 109.4291
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 1 | 342 | 6.1918e-05 | 1.8105e-07 | 342
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | FUSE | 1 | 1 | 68 | 1.2245e-05 | 1.8007e-07 | 68
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CUTOUT | 2 | 66 | 3291 | 0.00059262 | 1.1885e-05 | 49.8636
AEP Total | 2020 | 5484199 | DISTRIBUTION SOURCE | TIR | NONE | 1 | 729 | 26244 | 0.0047854 | 0.00013293 | 36
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE | 77 | 14997 | 2784760 | 0.49591 | 0.0026707 | 185.6878
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 43 | 3033 | 533390 | 0.094986 | 0.00054012 | 175.8622
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 44 | 5675 | 777319 | 0.13842 | 0.0010106 | 136.9725
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 111 | 9324 | 0.0016723 | 1.9908e-05 | 84
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | PEDESTAL | 1 | 2 | 486 | 8.7164e-05 | 3.587e-07 | 243
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 7 | 14 | 2256 | 0.00040175 | 2.4931e-06 | 161.1429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 23 | 7807 | 819929 | 0.14601 | 0.0013903 | 105.0248
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | TRANSFORMER, OH | 2 | 10 | 1420 | 0.0002557 | 1.8007e-06 | 142
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | FUSE | 4 | 372 | 32884 | 0.005856 | 6.6246e-05 | 88.3978
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 12 | 520 | 50501 | 0.0089932 | 9.2601e-05 | 97.1173
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 13 | 1534 | 0.00027317 | 2.315e-06 | 118
AEP Total | 2025 | 5615460 | DISTRIBUTION SOURCE | EQF | SWITCH, OH | 4 | 2663 | 42608 | 0.0075876 | 0.00047423 | 16
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 22 | 2524 | 282381 | 0.050286 | 0.00044947 | 111.8784
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 14 | 1663 | 173433 | 0.030885 | 0.00029615 | 104.2892
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 23 | 2523 | 186431 | 0.0332 | 0.0004493 | 73.8926
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 25 | 398 | 117724 | 0.020964 | 7.0876e-05 | 295.7889
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | SWITCH, OH | 4 | 15 | 2913 | 0.00051875 | 2.6712e-06 | 194.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 3 | 56 | 14861 | 0.0026464 | 9.9725e-06 | 265.375
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | POLE | 1 | 4 | 1088 | 0.00019592 | 7.2029e-07 | 272
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 1 | 142 | 2.557e-05 | 1.8007e-07 | 142
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 1 | 281 | 5.004e-05 | 1.7808e-07 | 281
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | METERING | 3 | 15 | 4294 | 0.00076467 | 2.6712e-06 | 286.2667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | POLE HARDWARE | 1 | 78 | 18736 | 0.0033365 | 1.389e-05 | 240.2051
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1 | 2 | 102 | 1.8164e-05 | 3.5616e-07 | 51
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CROSSARM | 5 | 1383 | 75616 | 0.013466 | 0.00024628 | 54.6753
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 1 | 4 | 3440 | 0.00061259 | 7.1232e-07 | 860
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | CONDUCTOR OVERHEAD | 2 | 19 | 1849 | 0.00032927 | 3.3835e-06 | 97.3158
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | NONE | 1 | 2 | 488 | 8.6903e-05 | 3.5616e-07 | 244
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 3 | 1335 | 0.00023943 | 5.3805e-07 | 445
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | BREAKER | 5 | 2113 | 335967 | 0.060256 | 0.00037897 | 159
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | SPLICE, UG | 1 | 1 | 238 | 4.3397e-05 | 1.8234e-07 | 238
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 1 | 164 | 2.9205e-05 | 1.7808e-07 | 164
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | SPLICE, OH | 1 | 1 | 64 | 1.1478e-05 | 1.7935e-07 | 64
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | FUSE | 1 | 7 | 637 | 0.00011615 | 1.2764e-06 | 91
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 11 | 2024 | 0.00036906 | 2.0058e-06 | 184
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 63 | 2051 | 0.00037133 | 1.1406e-05 | 32.5556
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 34 | 5018 | 0.0008936 | 6.0547e-06 | 147.5882
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 1109 | 32534 | 0.0057936 | 0.00019749 | 29.3363
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 2 | 49 | 10960 | 0.0019518 | 8.7259e-06 | 223.6735
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CUTOUT | 2 | 11 | 992 | 0.00017666 | 1.9589e-06 | 90.1818
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | PEDESTAL | 2 | 10 | 928 | 0.00016526 | 1.7808e-06 | 92.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | SWITCH, OH | 4 | 1369 | 127037 | 0.022623 | 0.00024379 | 92.7955
AEP Total | 2024 | 5615460 | PARTIAL POWER | WT | NONE | 1 | 9 | 1035 | 0.00018431 | 1.6027e-06 | 115
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR OVERHEAD | 1 | 1 | 175 | 3.1164e-05 | 1.7808e-07 | 175
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 2 | 140 | 2.4931e-05 | 3.5616e-07 | 70
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 98 | 10808 | 0.0019247 | 1.7452e-05 | 110.2857
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SWITCH, OH | 5 | 8 | 1554 | 0.00027674 | 1.4246e-06 | 194.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | INSULATOR | 1 | 461 | 22880 | 0.0040745 | 8.2095e-05 | 49.6312
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | METERING | 1 | 1 | 15 | 2.6712e-06 | 1.7808e-07 | 15
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | POLE | 3 | 3 | 815 | 0.00014514 | 5.3424e-07 | 271.6667
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | PEDESTAL | 1 | 7 | 154 | 2.7424e-05 | 1.2466e-06 | 22
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | REGULATOR | 1 | 323 | 23902 | 0.0042565 | 5.752e-05 | 74
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 2 | 152 | 2.7068e-05 | 3.5616e-07 | 76
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 2 | 250 | 4.452e-05 | 3.5616e-07 | 125
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 7 | 476 | 8.6795e-05 | 1.2764e-06 | 68
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 1 | 105 | 1.9146e-05 | 1.8234e-07 | 105
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 1 | 322 | 5.8714e-05 | 1.8234e-07 | 322
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 3 | 1758 | 0.00031306 | 5.3424e-07 | 586
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | POLE | 1 | 2 | 528 | 9.4026e-05 | 3.5616e-07 | 264
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | NONE | 341 | 29258 | 2752860 | 0.4984 | 0.0052971 | 94.0891
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | TRANSFORMER, OH | 1 | 2 | 532 | 9.6317e-05 | 3.6209e-07 | 266
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 246 | 1288 | 301402 | 0.054568 | 0.00023319 | 234.0078
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CROSSARM | 4 | 1498 | 278436 | 0.05041 | 0.00027121 | 185.8718
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 18 | 340 | 52262 | 0.0094618 | 6.1556e-05 | 153.7118
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 2 | 16 | 1403 | 0.00025401 | 2.8967e-06 | 87.6875
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | JUMPER/RISER | 3 | 3 | 901 | 0.00016312 | 5.4314e-07 | 300.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONN/CLAMP | 36 | 128 | 10015 | 0.0018132 | 2.3174e-05 | 78.2422
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 3 | 1095 | 0.00019825 | 5.4314e-07 | 365
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 174 | 19662 | 0.0035597 | 3.1502e-05 | 113
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 11 | 1571 | 0.00028442 | 1.9915e-06 | 142.8182
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 2 | 563 | 239545 | 0.043369 | 0.00010193 | 425.4796
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | REGULATOR | 2 | 210 | 6340 | 0.0011478 | 3.802e-05 | 30.1905
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | POLE | 11 | 257 | 50288 | 0.0091045 | 4.6529e-05 | 195.6732
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 3 | 53 | 10500 | 0.001901 | 9.5955e-06 | 198.1132
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | SPLICE, OH | 1 | 5 | 930 | 0.00016837 | 9.0523e-07 | 186
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | FUSE | 5 | 13 | 1329 | 0.00024061 | 2.3536e-06 | 102.2308
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | BREAKER | 1 | 413 | 49147 | 0.0088979 | 7.4772e-05 | 119
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 40 | 8640 | 0.0015642 | 7.2419e-06 | 216
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | JUMPER/RISER | 1 | 4 | 568 | 0.00010283 | 7.2419e-07 | 142
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | FUSE | 27 | 294 | 51421 | 0.0092595 | 5.2941e-05 | 174.9014
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 21 | 1727 | 236989 | 0.042675 | 0.00031098 | 137.2258
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 7 | 44 | 10958 | 0.0019732 | 7.9232e-06 | 249.0455
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 12 | 48 | 19416 | 0.0034963 | 8.6435e-06 | 404.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | SWITCH, OH | 15 | 201 | 54206 | 0.009761 | 3.6194e-05 | 269.6816
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE | 38 | 2125 | 521179 | 0.09385 | 0.00038265 | 245.2607
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 56 | 13328 | 0.0024 | 1.0084e-05 | 238
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 1 | 156 | 2.8243e-05 | 1.8105e-07 | 156
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 12 | 420 | 53526 | 0.00976 | 7.6584e-05 | 127.4429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CROSSARM | 27 | 5145 | 1304215 | 0.23781 | 0.00093815 | 253.4917
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONDUCTOR UG | 1 | 3 | 654 | 0.00011925 | 5.4703e-07 | 218
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONN/CLAMP | 10 | 147 | 10958 | 0.0019981 | 2.6804e-05 | 74.5442
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 4 | 764 | 37386 | 0.006817 | 0.00013931 | 48.9346
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | FUSE | 81 | 816 | 181270 | 0.033053 | 0.00014879 | 222.1446
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 9 | 20 | 2326 | 0.00042413 | 3.6468e-06 | 116.3
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 22 | 694 | 175164 | 0.03194 | 0.00012655 | 252.3977
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | REGULATOR | 3 | 934 | 97656 | 0.017807 | 0.00017031 | 104.5567
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONN/CLAMP | 2 | 2 | 287 | 5.2332e-05 | 3.6468e-07 | 143.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CUTOUT | 29 | 733 | 89082 | 0.016243 | 0.00013366 | 121.5307
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | GUY/ANCHOR | 1 | 26 | 3578 | 0.00065242 | 4.7409e-06 | 137.6154
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | REGULATOR | 2 | 127 | 97184 | 0.017721 | 2.3157e-05 | 765.2283
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE HARDWARE | 4 | 218 | 109512 | 0.019969 | 3.9751e-05 | 502.3486
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | POLE | 5 | 81 | 21162 | 0.0038587 | 1.477e-05 | 261.2593
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CUTOUT | 172 | 2920 | 351126 | 0.062975 | 0.0005237 | 120.2486
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CROSSARM | 23 | 4387 | 1060238 | 0.19015 | 0.00078681 | 241.6772
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 9 | 78 | 19347 | 0.0034699 | 1.3989e-05 | 248.0385
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | POLE | 9 | 1674 | 265231 | 0.047569 | 0.00030023 | 158.4415
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SWITCH, OH | 9 | 24 | 2098 | 0.00037628 | 4.3044e-06 | 87.4167
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | ARRESTER | 14 | 543 | 97486 | 0.017484 | 9.7387e-05 | 179.5322
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 3 | 13 | 1448 | 0.0002597 | 2.3316e-06 | 111.3846
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, OH | 3 | 89 | 13814 | 0.0024775 | 1.5962e-05 | 155.2135
AEP Total | 2023 | 5575683 | PARTIAL POWER | TR | NONE | 2 | 3 | 545 | 9.7746e-05 | 5.3805e-07 | 181.6667
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | METERING | 4 | 13 | 1301 | 0.00023333 | 2.3316e-06 | 100.0769
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 2003 | 128192 | 0.023375 | 0.00036523 | 64
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | NONE | 1 | 1 | 281 | 5.1238e-05 | 1.8234e-07 | 281
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 4 | 131 | 13313 | 0.0024275 | 2.3887e-05 | 101.626
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 1079 | 336854 | 0.060658 | 0.0001943 | 312.1909
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 60 | 4648 | 0.00083697 | 1.0804e-05 | 77.4667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 5 | 9 | 971 | 0.00017485 | 1.6206e-06 | 107.8889
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 2 | 74 | 22082 | 0.0039763 | 1.3325e-05 | 298.4054
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 10 | 47 | 5068 | 0.0009126 | 8.4634e-06 | 107.8298
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | NONE | 4 | 2749 | 113357 | 0.020331 | 0.00049303 | 41.2357
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 2 | 332 | 5.9784e-05 | 3.6014e-07 | 166
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 1 | 2 | 1376 | 0.00024778 | 3.6014e-07 | 688
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 3 | 30 | 3950 | 0.00071128 | 5.4022e-06 | 131.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 5 | 41 | 16105 | 0.0029001 | 7.3829e-06 | 392.8049
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 2 | 5 | 457 | 8.1382e-05 | 8.904e-07 | 91.4
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | NETWORK TRANSFORMER | 1 | 185 | 61235 | 0.010983 | 3.318e-05 | 331
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 10 | 1780 | 0.00031924 | 1.7935e-06 | 178
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 5 | 97 | 16050 | 0.0028582 | 1.7274e-05 | 165.4639
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 36 | 6084 | 0.0010834 | 6.4109e-06 | 169
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CROSSARM | 3 | 155 | 22952 | 0.004133 | 2.7911e-05 | 148.0774
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | ARRESTER | 1 | 1 | 350 | 6.382e-05 | 1.8234e-07 | 350
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | BREAKER | 5 | 3954 | 484996 | 0.088435 | 0.00072098 | 122.6596
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 2 | 134 | 2.413e-05 | 3.6014e-07 | 67
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WL | NONE | 1 | 351 | 47736 | 0.0085959 | 6.3205e-05 | 136
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 2 | 114 | 2.0528e-05 | 3.6014e-07 | 57
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CUTOUT | 1 | 3 | 630 | 0.00011345 | 5.4022e-07 | 210
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 953 | 79367 | 0.014292 | 0.00017161 | 83.2812
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | TRANSFORMER, POWER - LTC | 1 | 1 | 188 | 3.3854e-05 | 1.8007e-07 | 188
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 4 | 556 | 9.9719e-05 | 7.174e-07 | 139
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 10 | 62 | 5968 | 0.0010628 | 1.1041e-05 | 96.2581
AEP Total | 2025 | 5615460 | PARTIAL POWER | ERF | NONE | 2 | 2 | 178 | 3.1698e-05 | 3.5616e-07 | 89
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | JUMPER/RISER | 1 | 4 | 124 | 2.2082e-05 | 7.1232e-07 | 31
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONN/CLAMP | 2 | 7 | 962 | 0.00017131 | 1.2466e-06 | 137.4286
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | PEDESTAL | 1 | 1 | 60 | 1.0685e-05 | 1.7808e-07 | 60
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | POLE | 1 | 1 | 112 | 1.9945e-05 | 1.7808e-07 | 112
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | SPLICE, UG | 1 | 10 | 2700 | 0.00048425 | 1.7935e-06 | 270
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | TRANSFORMER, OH | 2 | 8 | 2621 | 0.00046675 | 1.4246e-06 | 327.625
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 612 | 0.00010898 | 1.7808e-07 | 612
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 1 | 85 | 1.5137e-05 | 1.7808e-07 | 85
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 7 | 3213 | 0.00057217 | 1.2466e-06 | 459
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 73 | 9490 | 0.0017089 | 1.3145e-05 | 130
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 30 | 7170 | 0.0012911 | 5.4022e-06 | 239
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | SWITCH, OH | 1 | 749 | 6741 | 0.0012004 | 0.00013338 | 9
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONN/CLAMP | 2 | 12 | 5742 | 0.0010225 | 2.137e-06 | 478.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 1 | 5 | 195 | 3.4726e-05 | 8.904e-07 | 39
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | CONN/CLAMP | 2 | 11 | 1963 | 0.00034957 | 1.9589e-06 | 178.4545
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 2 | 3 | 218 | 3.8821e-05 | 5.3424e-07 | 72.6667
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | CONN/CLAMP | 2 | 4 | 494 | 8.7971e-05 | 7.1232e-07 | 123.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 4 | 93 | 20549 | 0.0036594 | 1.6561e-05 | 220.957
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 785 | 131880 | 0.023485 | 0.00013979 | 168
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 8 | 548 | 9.7588e-05 | 1.4246e-06 | 68.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | POLE | 2 | 418 | 30457 | 0.0054238 | 7.4437e-05 | 72.8636
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 1 | 1 | 262 | 4.6657e-05 | 1.7808e-07 | 262
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 2 | 244 | 4.3938e-05 | 3.6014e-07 | 122
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | BREAKER | 1 | 26 | 2210 | 0.00040298 | 4.7409e-06 | 85
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | PEDESTAL | 1 | 2 | 1170 | 0.00021334 | 3.6468e-07 | 585
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | POLE | 1 | 76 | 18240 | 0.0033259 | 1.3858e-05 | 240
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 3 | 864 | 0.00015754 | 5.4703e-07 | 288
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | NONE | 1195 | 19826 | 1858419 | 0.33646 | 0.0035894 | 93.7365
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | POLE | 5 | 1643 | 255176 | 0.046199 | 0.00029746 | 155.311
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | NONE | 649 | 11604 | 1397746 | 0.25306 | 0.0021009 | 120.4538
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 68 | 5934 | 283400 | 0.051309 | 0.0010743 | 47.7587
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | OTHER EQUIPMENT | 1 | 5 | 595 | 0.00010772 | 9.0523e-07 | 119
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR UG | 18 | 61 | 15091 | 0.0027322 | 1.1044e-05 | 247.3934
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | NONE | 57 | 175 | 25647 | 0.0046433 | 3.1683e-05 | 146.5543
AEP Total | 2021 | 5523447 | PARTIAL POWER | O | CONDUCTOR UG | 2 | 7 | 1589 | 0.00028768 | 1.2673e-06 | 227
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CUTOUT | 1 | 1 | 117 | 2.1182e-05 | 1.8105e-07 | 117
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, OH | 4 | 63 | 5671 | 0.0010267 | 1.1406e-05 | 90.0159
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CONN/CLAMP | 2 | 19 | 2497 | 0.00045207 | 3.4399e-06 | 131.4211
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 2 | 7 | 1162 | 0.00021038 | 1.2673e-06 | 166
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | CROSSARM | 2 | 232 | 187784 | 0.033998 | 4.2003e-05 | 809.4138
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE | 68 | 4815 | 1379415 | 0.25153 | 0.00087798 | 286.4829
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | NONE | 68 | 3018 | 256442 | 0.04676 | 0.00055031 | 84.9708
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | NONE | 9 | 4516 | 209030 | 0.038115 | 0.00082346 | 46.2865
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE | 47 | 8727 | 2270391 | 0.41399 | 0.0015913 | 260.1571
AEP Total | 2020 | 5484199 | PARTIAL POWER | O | NONE | 23 | 52 | 5402 | 0.00098501 | 9.4818e-06 | 103.8846
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 3 | 54 | 47324 | 0.0086292 | 9.8465e-06 | 876.3704
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 2 | 4 | 332 | 6.0538e-05 | 7.2937e-07 | 83
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, OH | 16 | 31 | 11125 | 0.0020286 | 5.6526e-06 | 358.871
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 4 | 58 | 3564 | 0.00064987 | 1.0576e-05 | 61.4483
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WL | NONE | 4 | 5541 | 621124 | 0.11245 | 0.0010032 | 112.096
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 6 | 1079 | 0.00019535 | 1.0863e-06 | 179.8333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | ARRESTER | 5 | 157 | 17772 | 0.0032176 | 2.8424e-05 | 113.1975
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | FUSE | 3 | 29 | 3460 | 0.00062642 | 5.2503e-06 | 119.3103
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 35 | 4441 | 794192 | 0.14301 | 0.0007997 | 178.8318
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | NONE | 549 | 24562 | 3775320 | 0.67983 | 0.0044229 | 153.7057
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | FUSE | 10 | 93 | 22629 | 0.0040748 | 1.6747e-05 | 243.3226
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 38 | 2207 | 121034 | 0.021795 | 0.00039742 | 54.841
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 19 | 4693 | 0.00085573 | 3.4645e-06 | 247
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 36 | 8432 | 0.0015375 | 6.5643e-06 | 234.2222
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | POLE | 8 | 1717 | 322862 | 0.058871 | 0.00031308 | 188.0384
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | ARRESTER | 1 | 1 | 456 | 8.3148e-05 | 1.8234e-07 | 456
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CUTOUT | 1 | 2 | 292 | 5.3244e-05 | 3.6468e-07 | 146
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | NONE | 613 | 27314 | 3909874 | 0.70124 | 0.0048988 | 143.1454
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 196 | 7372 | 1937733 | 0.34753 | 0.0013222 | 262.8504
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | NONE | 142 | 19204 | 2393481 | 0.42927 | 0.0034442 | 124.6345
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 297 | 15671 | 2373548 | 0.4257 | 0.0028106 | 151.4612
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | POLE | 1 | 5 | 1180 | 0.00021163 | 8.9675e-07 | 236
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, OH | 63 | 6813 | 803356 | 0.14408 | 0.0012219 | 117.9152
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | NONE | 1555 | 32437 | 3747927 | 0.66743 | 0.0057764 | 115.5448
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | NONE | 23 | 1308 | 105335 | 0.018892 | 0.00023459 | 80.5313
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 19 | 2039 | 0.0003631 | 3.3835e-06 | 107.3158
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | TRANSFORMER, OH | 2 | 2 | 541 | 9.7028e-05 | 3.587e-07 | 270.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CAPACITOR | 8 | 1713 | 120588 | 0.021627 | 0.00030723 | 70.3958
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 8 | 114 | 23469 | 0.0042092 | 2.0446e-05 | 205.8684
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CABLE TERMINATOR | 6 | 13 | 4272 | 0.00076618 | 2.3316e-06 | 328.6154
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | NONE | 114 | 16065 | 1595785 | 0.28418 | 0.0028609 | 99.333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 15 | 178 | 39247 | 0.0070673 | 3.2053e-05 | 220.4888
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | NONE | 7 | 97 | 7596 | 0.0013678 | 1.7467e-05 | 78.3093
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | NONE | 5 | 41 | 6668 | 0.0012007 | 7.3829e-06 | 162.6341
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONN/CLAMP | 5 | 107 | 27986 | 0.0050193 | 1.919e-05 | 261.5514
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, STATION SERVICE | 1 | 1 | 116 | 2.0888e-05 | 1.8007e-07 | 116
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE | 4 | 534 | 46097 | 0.0083008 | 9.6158e-05 | 86.324
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 82 | 1172 | 200794 | 0.035757 | 0.00020871 | 171.3259
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | POLE | 1 | 12 | 11184 | 0.0020393 | 2.1881e-06 | 932
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | NONE | 1 | 2 | 698 | 0.00012727 | 3.6468e-07 | 349
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 4 | 736 | 0.00013325 | 7.2419e-07 | 184
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 73 | 17301 | 0.0031323 | 1.3216e-05 | 237
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | NETWORK TRANSFORMER | 1 | 1 | 50 | 9.0523e-06 | 1.8105e-07 | 50
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 8 | 5600 | 0.0010084 | 1.4406e-06 | 700
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | POLE | 1 | 2 | 662 | 0.00012071 | 3.6468e-07 | 331
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | TRANSFORMER, UG | 1 | 8 | 3416 | 0.00061513 | 1.4406e-06 | 427
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 216 | 2992 | 361125 | 0.064309 | 0.00053281 | 120.6969
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | U | NONE | 1 | 1741 | 41784 | 0.007494 | 0.00031225 | 24
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE | 9 | 94 | 35185 | 0.0062657 | 1.674e-05 | 374.3085
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 27 | 2510 | 509164 | 0.090672 | 0.00044698 | 202.8542
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | FUSE | 18 | 158 | 25095 | 0.0044689 | 2.8137e-05 | 158.8291
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | BREAKER | 1 | 1 | 28 | 4.9862e-06 | 1.7808e-07 | 28
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 13 | 2710 | 0.00048604 | 2.3316e-06 | 208.4615
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | CONDUCTOR UG | 2 | 7 | 2623 | 0.0004671 | 1.2466e-06 | 374.7143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | GUY/ANCHOR | 1 | 1 | 802 | 0.00014384 | 1.7935e-07 | 802
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONN/CLAMP | 2 | 5 | 2154 | 0.00038632 | 8.9675e-07 | 430.8
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 8 | 186 | 44804 | 0.0079787 | 3.3123e-05 | 240.8817
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | FUSE | 1 | 5 | 285 | 5.132e-05 | 9.0036e-07 | 57
AEP Total | 2022 | 5553337 | DISTRIBUTION SOURCE | WL | CROSSARM | 1 | 2 | 532 | 9.5798e-05 | 3.6014e-07 | 266
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | METERING | 1 | 1 | 54 | 9.6849e-06 | 1.7935e-07 | 54
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 10 | 1390 | 0.0002493 | 1.7935e-06 | 139
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | INSULATOR | 1 | 5 | 2105 | 0.00037753 | 8.9675e-07 | 421
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | NONE | 395 | 5292 | 288028 | 0.051292 | 0.0009424 | 54.4271
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 113 | 631 | 127927 | 0.022781 | 0.00011237 | 202.7369
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 95 | 19520 | 0.0034761 | 1.6918e-05 | 205.4737
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 77 | 1610 | 173771 | 0.030945 | 0.00028671 | 107.9323
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 3 | 4 | 398 | 7.0876e-05 | 7.1232e-07 | 99.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 11 | 2521 | 257680 | 0.045888 | 0.00044894 | 102.2134
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 33 | 101 | 36980 | 0.0065854 | 1.7986e-05 | 366.1386
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 79 | 4156 | 379074 | 0.067505 | 0.0007401 | 91.2113
AEP Total | 2025 | 5615460 | PARTIAL POWER | WL | NONE | 7 | 13 | 625 | 0.0001113 | 2.315e-06 | 48.0769
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | POLE | 1 | 3 | 594 | 0.00010578 | 5.3424e-07 | 198
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | TRANSFORMER, OH | 5 | 10 | 2134 | 0.00038002 | 1.7808e-06 | 213.4
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 21 | 1971 | 633970 | 0.1129 | 0.000351 | 321.6489
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 14 | 159 | 12285 | 0.0021877 | 2.8315e-05 | 77.2642
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CUTOUT | 1 | 35 | 10220 | 0.00182 | 6.2328e-06 | 292
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 5 | 582 | 83527 | 0.014874 | 0.00010364 | 143.5172
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SPLICE, OH | 1 | 26 | 3094 | 0.00055714 | 4.6819e-06 | 119
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | BREAKER | 1 | 1468 | 45508 | 0.0082391 | 0.00026578 | 31
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | BREAKER | 1 | 8 | 1856 | 0.00033052 | 1.4246e-06 | 232
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE | 5 | 1297 | 102544 | 0.018261 | 0.00023097 | 79.0625
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 4 | 304 | 5.4136e-05 | 7.1232e-07 | 76
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 2 | 41 | 4525 | 0.00080581 | 7.3013e-06 | 110.3659
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR UG | 1 | 2 | 614 | 0.00010934 | 3.5616e-07 | 307
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | FUSE | 1 | 3 | 357 | 6.3574e-05 | 5.3424e-07 | 119
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 17 | 952 | 0.00016953 | 3.0274e-06 | 56
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 4 | 376 | 6.6958e-05 | 7.1232e-07 | 94
AEP Total | 2024 | 5615460 | PARTIAL POWER | WT | CONDUCTOR UG | 1 | 1 | 227 | 4.0424e-05 | 1.7808e-07 | 227
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 2 | 19 | 9728 | 0.0017517 | 3.4214e-06 | 512
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 3 | 700 | 58538 | 0.010424 | 0.00012466 | 83.6257
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, STATION SERVICE | 1 | 14 | 980 | 0.00017452 | 2.4931e-06 | 70
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 1 | 42 | 7.4794e-06 | 1.7808e-07 | 42
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | CONDUCTOR UG | 1 | 1 | 109 | 1.9875e-05 | 1.8234e-07 | 109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CIRCUIT SWITCHER | 1 | 1655 | 215150 | 0.039231 | 0.00030178 | 130
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERO | METERING | 1 | 4 | 420 | 7.4794e-05 | 7.1232e-07 | 105
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | METERING | 1 | 1 | 53 | 9.4382e-06 | 1.7808e-07 | 53
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | POLE | 1 | 1 | 380 | 6.767e-05 | 1.7808e-07 | 380
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 21 | 1575 | 0.00028719 | 3.8292e-06 | 75
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CUTOUT | 1 | 1 | 282 | 5.142e-05 | 1.8234e-07 | 282
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 15 | 1818 | 465013 | 0.082809 | 0.00032375 | 255.7827
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 81 | 562 | 86205 | 0.015351 | 0.00010008 | 153.3897
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 48 | 465 | 48723 | 0.0086766 | 8.2807e-05 | 104.7806
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | FUSE | 1 | 19 | 1425 | 0.00025376 | 3.3835e-06 | 75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 4 | 26384 | 0.0046985 | 7.1232e-07 | 6596
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE | 52 | 7898 | 1239857 | 0.22079 | 0.0014065 | 156.9837
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | CONN/CLAMP | 2 | 4 | 2256 | 0.00040461 | 7.174e-07 | 564
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | CUTOUT | 1 | 2 | 58 | 1.0444e-05 | 3.6014e-07 | 29
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 1 | 279 | 132893 | 0.024232 | 5.0873e-05 | 476.319
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | NONE | 1 | 24 | 3282 | 0.00059845 | 4.3762e-06 | 136.75
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 4 | 11 | 4310 | 0.00077611 | 1.9808e-06 | 391.8182
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | REGULATOR | 1 | 2 | 688 | 0.00012389 | 3.6014e-07 | 344
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | INSULATOR | 3 | 116 | 25170 | 0.0045324 | 2.0888e-05 | 216.9828
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 40 | 20217 | 0.0036259 | 7.174e-06 | 505.425
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | R | POLE | 2 | 58 | 15156 | 0.0027182 | 1.0402e-05 | 261.3103
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | STATIC WIRE | 1 | 996 | 73718 | 0.013275 | 0.00017935 | 74.0141
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SPLICE, UG | 2 | 7 | 1999 | 0.00035996 | 1.2605e-06 | 285.5714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 80 | 35474 | 0.0063623 | 1.4348e-05 | 443.425
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | SPLICE, UG | 1 | 1 | 345 | 6.1438e-05 | 1.7808e-07 | 345
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 172 | 3088 | 339762 | 0.060505 | 0.00054991 | 110.0266
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | POLE | 28 | 12272 | 1087551 | 0.19367 | 0.0021854 | 88.6205
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | NONE | 42 | 257 | 24236 | 0.0043159 | 4.5767e-05 | 94.3035
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 254 | 289 | 23591 | 0.0042011 | 5.1465e-05 | 81.6298
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 52 | 135 | 26977 | 0.0048041 | 2.4041e-05 | 199.8296
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 20 | 118 | 11009 | 0.0019605 | 2.1013e-05 | 93.2966
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | SPLICE, OH | 8 | 15 | 1488 | 0.00026498 | 2.6712e-06 | 99.2
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | POLE HARDWARE | 1 | 5 | 690 | 0.00012288 | 8.904e-07 | 138
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | JUMPER/RISER | 7 | 46 | 2499 | 0.00044502 | 8.1917e-06 | 54.3261
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 9 | 347 | 59126 | 0.010529 | 6.1794e-05 | 170.3919
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 13 | 2224 | 0.00039605 | 2.315e-06 | 171.0769
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | NONE | 3 | 11 | 1312 | 0.00023364 | 1.9589e-06 | 119.2727
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | POLE | 1 | 1 | 260 | 4.6301e-05 | 1.7808e-07 | 260
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CAPACITOR | 1 | 652 | 4564 | 0.00081276 | 0.00011611 | 7
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 5 | 28 | 1457 | 0.00025946 | 4.9862e-06 | 52.0357
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 1532 | 154732 | 0.027555 | 0.00027282 | 101
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CUTOUT | 1 | 9 | 1017 | 0.00018111 | 1.6027e-06 | 113
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 1 | 6 | 480 | 8.5478e-05 | 1.0685e-06 | 80
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | CROSSARM | 1 | 2 | 446 | 7.9424e-05 | 3.5616e-07 | 223
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 117 | 7020 | 0.0012501 | 2.0835e-05 | 60
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 5 | 305 | 51020 | 0.0090856 | 5.4314e-05 | 167.2787
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 4 | 33 | 2947 | 0.0005248 | 5.8766e-06 | 89.303
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | POLE | 2 | 128 | 27916 | 0.0049713 | 2.2794e-05 | 218.0938
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | TRANSFORMER, OH | 2 | 29 | 4308 | 0.00076717 | 5.1643e-06 | 148.5517
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 1 | 68 | 1.2245e-05 | 1.8007e-07 | 68
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 42 | 2643 | 238898 | 0.042543 | 0.00047066 | 90.389
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | AF | NONE | 1 | 41 | 2091 | 0.00037236 | 7.3013e-06 | 51
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | NONE | 1 | 3 | 159 | 2.8315e-05 | 5.3424e-07 | 53
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | TRANSFORMER, OH | 2 | 991 | 70067 | 0.012776 | 0.0001807 | 70.7033
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 14 | 1120 | 0.00020087 | 2.5109e-06 | 80
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 5 | 415 | 7.473e-05 | 9.0036e-07 | 83
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | TRANSFORMER, GROUNDING | 1 | 7 | 938 | 0.00016823 | 1.2555e-06 | 134
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CIRCUIT SWITCHER | 1 | 2874 | 145536 | 0.026537 | 0.00052405 | 50.6388
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | REGULATOR | 1 | 360 | 6480 | 0.0011732 | 6.5177e-05 | 18
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE HARDWARE | 2 | 133 | 62417 | 0.011381 | 2.4251e-05 | 469.3008
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | CONN/CLAMP | 1 | 10 | 950 | 0.00017322 | 1.8234e-06 | 95
AEP Total | 2023 | 5575683 | PARTIAL POWER | U | NONE | 239 | 603 | 52198 | 0.0093617 | 0.00010815 | 86.5638
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, UG | 4 | 22 | 1649 | 0.00029575 | 3.9457e-06 | 74.9545
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CONN/CLAMP | 66 | 1821 | 273111 | 0.048983 | 0.0003266 | 149.9786
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 8 | 1676 | 47982 | 0.0086056 | 0.00030059 | 28.6289
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CUTOUT | 528 | 13490 | 1636620 | 0.29353 | 0.0024194 | 121.321
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | PEDESTAL | 4 | 14 | 259 | 4.6452e-05 | 2.5109e-06 | 18.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 247 | 2782 | 416369 | 0.074676 | 0.00049895 | 149.6653
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | SWITCH, UG | 5 | 5183 | 1168517 | 0.20957 | 0.00092957 | 225.4519
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CONN/CLAMP | 63 | 1128 | 153614 | 0.027356 | 0.00020087 | 136.1826
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 81 | 553 | 109961 | 0.019582 | 9.8478e-05 | 198.8445
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | U | NONE | 1629 | 166493 | 6361944 | 1.1329 | 0.029649 | 38.2115
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 3802 | 139443 | 13597477 | 2.4214 | 0.024832 | 97.5128
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | RECLOSER, LINE/OCR/BR | 2 | 106 | 14424 | 0.0025869 | 1.9011e-05 | 136.0755
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 4 | 35 | 12593 | 0.0022586 | 6.2773e-06 | 359.8
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 50 | 7247 | 1082124 | 0.19408 | 0.0012998 | 149.3203
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONN/CLAMP | 12 | 1015 | 293729 | 0.05268 | 0.00018204 | 289.3882
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | SPLICE, OH | 1 | 12 | 2856 | 0.00051222 | 2.1522e-06 | 238
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR UG | 74 | 190 | 36790 | 0.0065983 | 3.4077e-05 | 193.6316
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | METERING | 2 | 2 | 99 | 1.7756e-05 | 3.587e-07 | 49.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | METERING | 5 | 5 | 1156 | 0.00020733 | 8.9675e-07 | 231.2
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 6 | 5776 | 562449 | 0.10088 | 0.0010359 | 97.3769
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | FUSE | 1 | 1 | 22 | 3.9457e-06 | 1.7935e-07 | 22
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | ARRESTER | 15 | 111 | 14951 | 0.0026815 | 1.9908e-05 | 134.6937
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 6 | 18 | 6787 | 0.0012172 | 3.2283e-06 | 377.0556
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | NONE | 13 | 55 | 3552 | 0.00063254 | 9.7944e-06 | 64.5818
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CUTOUT | 17 | 175 | 20224 | 0.0036418 | 3.1513e-05 | 115.5657
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE HARDWARE | 11 | 2850 | 287722 | 0.051811 | 0.0005132 | 100.9551
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 6 | 133 | 10085 | 0.001816 | 2.395e-05 | 75.8271
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | PEDESTAL | 5 | 19 | 5886 | 0.0010599 | 3.4214e-06 | 309.7895
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ERF | NONE | 3 | 7492 | 108476 | 0.019533 | 0.0013491 | 14.4789
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 7 | 581 | 0.00010462 | 1.2605e-06 | 83
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | SPLICE, OH | 11 | 70 | 16712 | 0.0030094 | 1.2605e-05 | 238.7429
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | JUMPER/RISER | 3 | 26 | 3348 | 0.00060288 | 4.6819e-06 | 128.7692
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 91 | 1.6321e-05 | 1.7935e-07 | 91
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | SWITCH, OH | 2 | 430 | 48320 | 0.0087011 | 7.7431e-05 | 112.3721
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | RELAY | 1 | 503 | 15090 | 0.0027064 | 9.0213e-05 | 30
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 5 | 150 | 2.6903e-05 | 8.9675e-07 | 30
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | POLE | 1 | 1 | 49 | 8.8235e-06 | 1.8007e-07 | 49
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE HARDWARE | 6 | 2277 | 520350 | 0.0937 | 0.00041002 | 228.5244
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONN/CLAMP | 2 | 2 | 236 | 4.2497e-05 | 3.6014e-07 | 118
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | PEDESTAL | 1 | 1 | 1151 | 0.00020643 | 1.7935e-07 | 1151
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 130 | 2.3536e-05 | 1.8105e-07 | 130
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | METERING | 1 | 1 | 135 | 2.4441e-05 | 1.8105e-07 | 135
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CABLE TERMINATOR | 2 | 2 | 237 | 4.3215e-05 | 3.6468e-07 | 118.5
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABI | NONE | 25 | 21448 | 2507256 | 0.45718 | 0.0039109 | 116.8993
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 22 | 4.0115e-06 | 1.8234e-07 | 22
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | BREAKER | 2 | 1143 | 116504 | 0.021244 | 0.00020842 | 101.9283
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | GUY/ANCHOR | 1 | 1 | 124 | 2.245e-05 | 1.8105e-07 | 124
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 2 | 7 | 554 | 0.0001003 | 1.2673e-06 | 79.1429
AEP Total | 2021 | 5523447 | PARTIAL POWER | AF | NONE | 1 | 1 | 108 | 1.9553e-05 | 1.8105e-07 | 108
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 1 | 48 | 8.6902e-06 | 1.8105e-07 | 48
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 71 | 1.2785e-05 | 1.8007e-07 | 71
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | FUSE | 3 | 3 | 241 | 4.3944e-05 | 5.4703e-07 | 80.3333
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 2 | 292 | 5.2581e-05 | 3.6014e-07 | 146
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | NONE | 2 | 2 | 576 | 0.00010503 | 3.6468e-07 | 288
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | CONN/CLAMP | 3 | 18 | 1242 | 0.00022365 | 3.2413e-06 | 69
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | METERING | 2 | 2 | 273 | 4.916e-05 | 3.6014e-07 | 136.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 1 | 98 | 65668 | 0.011778 | 1.7576e-05 | 670.0816
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 2 | 37 | 6211 | 0.0011139 | 6.636e-06 | 167.8649
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | TRANSFORMER, OH | 1 | 1 | 465 | 8.3398e-05 | 1.7935e-07 | 465
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 100 | 380 | 65239 | 0.011618 | 6.767e-05 | 171.6816
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 82 | 13326 | 1144924 | 0.20389 | 0.0023731 | 85.9166
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | AB | NONE | 8 | 5052 | 613909 | 0.10932 | 0.00089966 | 121.518
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 31 | 5393 | 0.00096038 | 5.5205e-06 | 173.9677
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 38 | 38 | 3497 | 0.00062275 | 6.767e-06 | 92.0263
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 3 | 3 | 305 | 5.4314e-05 | 5.3424e-07 | 101.6667
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | CONDUCTOR UG | 1 | 1 | 149 | 2.6534e-05 | 1.7808e-07 | 149
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | TRANSFORMER, UG | 1 | 19 | 4161 | 0.00074928 | 3.4214e-06 | 219
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 3 | 126 | 2.2438e-05 | 5.3424e-07 | 42
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | JUMPER/RISER | 3 | 158 | 20504 | 0.0036513 | 2.8137e-05 | 129.7722
AEP Total | 2025 | 5615460 | PARTIAL POWER | ABI | NONE | 6 | 108 | 9817 | 0.0017482 | 1.9233e-05 | 90.8981
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 192 | 33392 | 0.0059464 | 3.4191e-05 | 173.9167
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | OTHER EQUIPMENT | 1 | 3 | 234 | 4.1671e-05 | 5.3424e-07 | 78
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 74 | 8584 | 0.0015286 | 1.3178e-05 | 116
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | GUY/ANCHOR | 1 | 1 | 115 | 2.0479e-05 | 1.7808e-07 | 115
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CUTOUT | 1 | 1 | 161 | 2.8671e-05 | 1.7808e-07 | 161
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 38 | 3762 | 0.00066994 | 6.767e-06 | 99
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 99 | 9798 | 0.0017448 | 1.763e-05 | 98.9697
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 2 | 257 | 35902 | 0.0063934 | 4.5767e-05 | 139.6965
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 3 | 3 | 621 | 0.00011138 | 5.3805e-07 | 207
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | SWITCH, UG | 1 | 1 | 88 | 1.6046e-05 | 1.8234e-07 | 88
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | SPLICE, OH | 2 | 2 | 676 | 0.00012173 | 3.6014e-07 | 338
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE | 322 | 18272 | 3505561 | 0.63467 | 0.0033081 | 191.8543
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 26 | 461 | 131345 | 0.02378 | 8.3462e-05 | 284.9132
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 12 | 202 | 31122 | 0.0056345 | 3.6571e-05 | 154.0693
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONN/CLAMP | 45 | 683 | 77558 | 0.014042 | 0.00012365 | 113.5549
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | POLE | 14 | 352 | 102346 | 0.018529 | 6.3728e-05 | 290.7557
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | PEDESTAL | 13 | 58 | 6981 | 0.0012639 | 1.0501e-05 | 120.3621
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | FUSE | 1 | 1 | 113 | 2.0458e-05 | 1.8105e-07 | 113
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ERF | NONE | 6 | 4930 | 181092 | 0.032786 | 0.00089256 | 36.7327
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CUTOUT | 4 | 95 | 17363 | 0.0031435 | 1.7199e-05 | 182.7684
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | TRANSFORMER, OH | 1 | 1 | 68 | 1.2311e-05 | 1.8105e-07 | 68
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONN/CLAMP | 985 | 1977 | 220558 | 0.040217 | 0.00036049 | 111.562
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CUTOUT | 63 | 1400 | 186567 | 0.034019 | 0.00025528 | 133.2621
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | POLE | 45 | 10417 | 1107668 | 0.20197 | 0.0018995 | 106.3327
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 167 | 370 | 38176 | 0.0069611 | 6.7467e-05 | 103.1784
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONN/CLAMP | 38 | 248 | 22412 | 0.0040866 | 4.5221e-05 | 90.371
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | NONE | 289 | 10861 | 843632 | 0.15383 | 0.0019804 | 77.6754
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | ARRESTER | 122 | 2534 | 357856 | 0.065252 | 0.00046205 | 141.2218
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CUTOUT | 59 | 582 | 98028 | 0.017875 | 0.00010612 | 168.433
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | U | NONE | 26 | 20930 | 1510389 | 0.27541 | 0.0038164 | 72.1638
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | JUMPER/RISER | 26 | 4631 | 543966 | 0.099188 | 0.00084443 | 117.4619
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONN/CLAMP | 23 | 34 | 3948 | 0.00071989 | 6.1996e-06 | 116.1176
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CROSSARM | 9 | 4885 | 489674 | 0.089288 | 0.00089074 | 100.2403
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | POLE HARDWARE | 9 | 1057 | 98479 | 0.017957 | 0.00019274 | 93.1684
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 187 | 794 | 318662 | 0.058105 | 0.00014478 | 401.3375
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | INSULATOR | 6 | 720 | 44161 | 0.0080524 | 0.00013129 | 61.3347
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CUTOUT | 3 | 7 | 840 | 0.00015208 | 1.2673e-06 | 120
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 3 | 42 | 4039 | 0.00073125 | 7.6039e-06 | 96.1667
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | CONN/CLAMP | 3 | 3 | 390 | 7.0608e-05 | 5.4314e-07 | 130
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | NONE | 9 | 11 | 921 | 0.00016674 | 1.9915e-06 | 83.7273
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | TRANSFORMER, UG | 1 | 4 | 1900 | 0.00034399 | 7.2419e-07 | 475
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | OTHER EQUIPMENT | 1 | 33 | 5742 | 0.0010396 | 5.9745e-06 | 174
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | ARRESTER | 3 | 1914 | 194448 | 0.035015 | 0.00034466 | 101.5925
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 160 | 490 | 88415 | 0.015921 | 8.8235e-05 | 180.4388
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | NONE | 340 | 351 | 45177 | 0.0081351 | 6.3205e-05 | 128.7094
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | NONE | 243 | 2625 | 296113 | 0.053322 | 0.00047269 | 112.805
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 160 | 385 | 57509 | 0.010356 | 6.9328e-05 | 149.374
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | NONE | 116 | 13199 | 1095045 | 0.19719 | 0.0023768 | 82.9642
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | ARRESTER | 109 | 2391 | 270803 | 0.048764 | 0.00043055 | 113.2593
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 5 | 451 | 81917 | 0.014751 | 8.1212e-05 | 181.6341
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | POLE | 74 | 22236 | 1849209 | 0.33299 | 0.0040041 | 83.1628
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | NONE | 99 | 331 | 29474 | 0.0053074 | 5.9604e-05 | 89.0453
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 11 | 380 | 68373 | 0.012312 | 6.8427e-05 | 179.9289
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | CF | SWITCH, OH | 3 | 3969 | 383776 | 0.069107 | 0.00071471 | 96.6934
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 12 | 240 | 4.3762e-05 | 2.1881e-06 | 20
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 214 | 3.8381e-05 | 1.7935e-07 | 214
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 5 | 31 | 2959 | 0.0005307 | 5.5599e-06 | 95.4516
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | METERING | 2 | 3 | 310 | 5.5599e-05 | 5.3805e-07 | 103.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | POLE | 1 | 1 | 305 | 5.4702e-05 | 1.7935e-07 | 305
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 167 | 3141 | 336904 | 0.059996 | 0.00055935 | 107.2601
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 893 | 50545 | 0.0090653 | 0.00016016 | 56.6013
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | ARRESTER | 21 | 1930 | 190412 | 0.033909 | 0.00034369 | 98.6591
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CUTOUT | 7 | 377 | 38364 | 0.0069954 | 6.8743e-05 | 101.7613
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 3 | 216 | 3.9386e-05 | 5.4703e-07 | 72
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | CONN/CLAMP | 6 | 8 | 12918 | 0.0023555 | 1.4587e-06 | 1614.75
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 24 | 265 | 149082 | 0.027184 | 4.8321e-05 | 562.5736
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | REGULATOR | 3 | 2384 | 118464 | 0.021601 | 0.0004347 | 49.6913
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | ARRESTER | 3 | 7 | 376 | 6.8561e-05 | 1.2764e-06 | 53.7143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 4 | 3077 | 93508 | 0.01705 | 0.00056107 | 30.3893
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 506 | 9.1609e-05 | 3.6209e-07 | 253
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, OH | 17 | 207 | 48236 | 0.0086859 | 3.7275e-05 | 233.0242
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE | 13 | 499 | 25650 | 0.0046188 | 8.9856e-05 | 51.4028
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | ARRESTER | 8 | 23 | 2380 | 0.00042857 | 4.1417e-06 | 103.4783
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 89 | 6978 | 0.0012565 | 1.6026e-05 | 78.4045
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | POLE | 24 | 1269 | 483921 | 0.086791 | 0.0002276 | 381.3404
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CUTOUT | 10 | 19 | 2476 | 0.00044586 | 3.4214e-06 | 130.3158
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | METERING | 14 | 14 | 1613 | 0.00029046 | 2.521e-06 | 115.2143
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CROSSARM | 13 | 511 | 122991 | 0.022147 | 9.2017e-05 | 240.6869
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | METERING | 10 | 11 | 2491 | 0.00044856 | 1.9808e-06 | 226.4545
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | NONE | 3 | 14 | 739 | 0.00013307 | 2.521e-06 | 52.7857
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 27 | 1469 | 0.00026347 | 4.8425e-06 | 54.4074
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, UG | 2 | 6 | 2083 | 0.00037359 | 1.0761e-06 | 347.1667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | REGULATOR | 4 | 466 | 66148 | 0.011864 | 8.3577e-05 | 141.9485
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | NONE | 42 | 17260 | 1322968 | 0.23559 | 0.0030737 | 76.6494
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONN/CLAMP | 45 | 139 | 18313 | 0.0032612 | 2.4753e-05 | 131.7482
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 289 | 33517 | 5128330 | 0.91325 | 0.0059687 | 153.0068
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 115 | 1794 | 299817 | 0.053391 | 0.00031948 | 167.1221
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | NONE | 73 | 7562 | 1203338 | 0.21429 | 0.0013466 | 159.1296
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 19 | 110 | 17683 | 0.003149 | 1.9589e-05 | 160.7545
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | TRANSFORMER, OH | 5 | 24 | 7780 | 0.0013855 | 4.2739e-06 | 324.1667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 12 | 923 | 83310 | 0.014836 | 0.00016437 | 90.26
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 34 | 944 | 109059 | 0.019421 | 0.00016811 | 115.5286
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | PEDESTAL | 3 | 14 | 1490 | 0.00026723 | 2.5109e-06 | 106.4286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | SPLICE, UG | 1 | 1 | 500 | 8.9675e-05 | 1.7935e-07 | 500
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONDUCTOR UG | 3 | 14 | 7410 | 0.0013343 | 2.521e-06 | 529.2857
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | NONE | 830 | 26632 | 2365373 | 0.42123 | 0.0047426 | 88.8169
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | NONE | 29 | 55 | 6778 | 0.001207 | 9.7944e-06 | 123.2364
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 135 | 7520 | 1212302 | 0.21589 | 0.0013392 | 161.2104
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 115 | 1748 | 339343 | 0.06043 | 0.00031128 | 194.1322
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE | 73 | 8616 | 916167 | 0.16315 | 0.0015343 | 106.3332
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 16 | 101 | 29608 | 0.0052726 | 1.7986e-05 | 293.1485
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 3 | 160 | 23021 | 0.0040996 | 2.8493e-05 | 143.8812
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 44 | 431 | 88402 | 0.015743 | 7.6752e-05 | 205.109
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 10 | 1158 | 95102 | 0.016936 | 0.00020622 | 82.1261
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 5 | 1035 | 0.00018637 | 9.0036e-07 | 207
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 3 | 5 | 1751 | 0.00031531 | 9.0036e-07 | 350.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 1 | 116 | 2.1001e-05 | 1.8105e-07 | 116
AEP Total | 2022 | 5553337 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 2 | 21 | 2471 | 0.00044496 | 3.7815e-06 | 117.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 149 | 57365 | 0.01046 | 2.7169e-05 | 385
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | TRANSFORMER, GROUNDING | 1 | 15 | 3780 | 0.00068067 | 2.7011e-06 | 252
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | BREAKER | 3 | 8290 | 472694 | 0.085119 | 0.0014928 | 57.0198
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CUTOUT | 1 | 1 | 94 | 1.6859e-05 | 1.7935e-07 | 94
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 67 | 1.2016e-05 | 1.7935e-07 | 67
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | O | NONE | 2 | 2711 | 181878 | 0.032389 | 0.00048277 | 67.0889
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | ARRESTER | 36 | 265 | 28000 | 0.0049862 | 4.7191e-05 | 105.6604
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CAPACITOR | 4 | 107 | 8282 | 0.0014749 | 1.9055e-05 | 77.4019
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | NONE | 107 | 7140 | 745801 | 0.13281 | 0.0012715 | 104.4539
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 35 | 7694 | 2211488 | 0.39382 | 0.0013701 | 287.4302
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 4 | 105 | 38004 | 0.0067677 | 1.8698e-05 | 361.9429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1087 | 115763 | 17035977 | 3.0843 | 0.020958 | 147.1625
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 303 | 30864 | 2684097 | 0.48595 | 0.0055878 | 86.9653
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONN/CLAMP | 71 | 71 | 8239 | 0.0014916 | 1.2854e-05 | 116.0423
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE | 286 | 66844 | 9550489 | 1.7291 | 0.012102 | 142.8773
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONN/CLAMP | 88 | 207 | 26349 | 0.0047704 | 3.7477e-05 | 127.2899
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | NONE | 204 | 204 | 25251 | 0.0045716 | 3.6933e-05 | 123.7794
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | NONE | 73 | 918 | 74994 | 0.013577 | 0.0001662 | 81.6928
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | ARRESTER | 155 | 2845 | 616900 | 0.11169 | 0.00051508 | 216.8366
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | ARRESTER | 26 | 1231 | 58747 | 0.010636 | 0.00022287 | 47.723
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | METERING | 20 | 21 | 2867 | 0.00051906 | 3.802e-06 | 136.5238
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | METERING | 1 | 1 | 115 | 2.082e-05 | 1.8105e-07 | 115
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, OH | 28 | 17818 | 1654159 | 0.29948 | 0.0032259 | 92.8364
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SPLICE, OH | 5 | 352 | 29378 | 0.0053188 | 6.3728e-05 | 83.4602
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 9 | 1685 | 0.00030506 | 1.6294e-06 | 187.2222
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 5 | 99 | 14119 | 0.0025562 | 1.7924e-05 | 142.6162
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | ARRESTER | 5 | 17 | 2166 | 0.00039215 | 3.0778e-06 | 127.4118
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 10 | 1180 | 0.00021363 | 1.8105e-06 | 118
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | JUMPER/RISER | 2 | 29 | 6068 | 0.0010986 | 5.2503e-06 | 209.2414
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | ARRESTER | 4 | 1929 | 730511 | 0.13226 | 0.00034924 | 378.6993
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | CF | MOAB | 5 | 4483 | 32142 | 0.0058192 | 0.00081163 | 7.1698
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | CF | JUMPER/RISER | 2 | 2903 | 267405 | 0.048413 | 0.00052558 | 92.1133
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 604 | 135590 | 0.024548 | 0.00010935 | 224.4868
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONN/CLAMP | 97 | 97 | 12748 | 0.0022956 | 1.7467e-05 | 131.4227
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONN/CLAMP | 18 | 705 | 78386 | 0.014115 | 0.00012695 | 111.1858
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | SPLICE, OH | 4 | 62 | 6488 | 0.0011683 | 1.1164e-05 | 104.6452
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | RELAY | 6 | 5064 | 408614 | 0.07358 | 0.00091188 | 80.69
AEP Total | 2022 | 5553337 | PARTIAL POWER | ABI | NONE | 36 | 74 | 4590 | 0.00082653 | 1.3325e-05 | 62.027
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CUTOUT | 2 | 19 | 5690 | 0.0010246 | 3.4214e-06 | 299.4737
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | METERING | 4 | 4 | 326 | 5.8703e-05 | 7.2029e-07 | 81.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 2 | 13 | 410 | 7.3829e-05 | 2.3409e-06 | 31.5385
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 150 | 3944 | 520145 | 0.094844 | 0.00071916 | 131.8826
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | METERING | 9 | 9 | 770 | 0.0001404 | 1.6411e-06 | 85.5556
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONN/CLAMP | 115 | 115 | 12553 | 0.0022889 | 2.0969e-05 | 109.1565
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 9 | 68 | 12703 | 0.0023163 | 1.2399e-05 | 186.8088
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | FUSE | 3 | 12 | 939 | 0.00017122 | 2.1881e-06 | 78.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | NONE | 227 | 227 | 29662 | 0.0054086 | 4.1392e-05 | 130.6696
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | NONE | 12 | 23 | 1722 | 0.00031399 | 4.1939e-06 | 74.8696
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | SPLICE, OH | 1 | 1 | 94 | 1.714e-05 | 1.8234e-07 | 94
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CROSSARM | 20 | 7227 | 655020 | 0.11944 | 0.0013178 | 90.6351
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, OH | 20 | 191 | 35852 | 0.0065373 | 3.4827e-05 | 187.7068
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONN/CLAMP | 32 | 411 | 64403 | 0.011743 | 7.4943e-05 | 156.6983
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 27 | 2244 | 535125 | 0.097576 | 0.00040918 | 238.4693
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | BREAKER | 17 | 15417 | 1045079 | 0.19056 | 0.0028112 | 67.7874
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CUTOUT | 18 | 260 | 27940 | 0.0050946 | 4.7409e-05 | 107.4615
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | REGULATOR | 3 | 2287 | 169576 | 0.030921 | 0.00041702 | 74.1478
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 5 | 2748 | 416434 | 0.075933 | 0.00050108 | 151.5408
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 4 | 1370 | 119036 | 0.021705 | 0.00024981 | 86.8876
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | TRANSFORMER, OH | 3 | 13 | 4521 | 0.00082437 | 2.3704e-06 | 347.7692
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | JUMPER/RISER | 3 | 34 | 9054 | 0.0016509 | 6.1996e-06 | 266.2941
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 5 | 11 | 3185 | 0.00058076 | 2.0058e-06 | 289.5455
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1087 | 6199 | 572255 | 0.10263 | 0.0011118 | 92.3141
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | NONE | 1060 | 9903 | 816211 | 0.14639 | 0.0017761 | 82.4206
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | NONE | 1080 | 46844 | 4700625 | 0.84306 | 0.0084015 | 100.3464
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | NONE | 739 | 12742 | 1276790 | 0.22899 | 0.0022853 | 100.2033
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 404 | 8222 | 1779885 | 0.31922 | 0.0014746 | 216.4784
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | NONE | 51 | 51 | 6229 | 0.0011172 | 9.1469e-06 | 122.1373
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 641 | 7983 | 787043 | 0.14016 | 0.0014216 | 98.5899
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 110 | 10084 | 1113778 | 0.19834 | 0.0017958 | 110.45
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE | 291 | 46921 | 7537853 | 1.3423 | 0.0083557 | 160.6499
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | NONE | 1622 | 24115 | 2186035 | 0.38929 | 0.0042944 | 90.6504
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 2 | 1032 | 111643 | 0.020023 | 0.00018509 | 108.1812
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 82 | 82 | 12174 | 0.0021834 | 1.4707e-05 | 148.4634
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CUTOUT | 15 | 26 | 2040 | 0.00036587 | 4.6631e-06 | 78.4615
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, UG | 17 | 100 | 27253 | 0.0048878 | 1.7935e-05 | 272.53
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CABLE TERMINATOR | 1 | 3 | 297 | 5.289e-05 | 5.3424e-07 | 99
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | JUMPER/RISER | 1 | 1 | 111 | 1.9988e-05 | 1.8007e-07 | 111
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 5 | 14 | 1864 | 0.00033194 | 2.4931e-06 | 133.1429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 39 | 245 | 32758 | 0.0058335 | 4.363e-05 | 133.7061
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 7 | 392 | 11738 | 0.0020903 | 6.9807e-05 | 29.9439
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 21 | 1587 | 168628 | 0.030029 | 0.00028261 | 106.2558
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | SWITCH, OH | 2 | 517 | 41996 | 0.0075623 | 9.3097e-05 | 81.2302
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | U | NONE | 37 | 33687 | 2729259 | 0.48603 | 0.005999 | 81.0182
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 1 | 156 | 2.7979e-05 | 1.7935e-07 | 156
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 143 | 2.575e-05 | 1.8007e-07 | 143
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 3 | 1386 | 0.00024858 | 5.3805e-07 | 462
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | JUMPER/RISER | 3 | 48 | 6160 | 0.001097 | 8.5478e-06 | 128.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 14 | 3650 | 656353 | 0.11688 | 0.00064999 | 179.8227
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | POLE | 2 | 1594 | 3957664 | 0.70478 | 0.00028386 | 2482.8507
AEP Total | 2025 | 5615460 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 2 | 4 | 138 | 2.4575e-05 | 7.1232e-07 | 34.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | SPLICE, OH | 2 | 4 | 498 | 8.8684e-05 | 7.1232e-07 | 124.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | WFS | CONDUCTOR UG | 1 | 1 | 174 | 3.0986e-05 | 1.7808e-07 | 174
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | TRANSFORMER, OH | 1 | 1 | 461 | 8.2095e-05 | 1.7808e-07 | 461
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CABLE TERMINATOR | 1 | 1 | 96 | 1.7096e-05 | 1.7808e-07 | 96
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 1 | 20 | 5354 | 0.00096411 | 3.6014e-06 | 267.7
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | SWITCH, OH | 1 | 232 | 19488 | 0.0034704 | 4.1315e-05 | 84
AEP Total | 2025 | 5615460 | PARTIAL POWER | WL | NONE | 8 | 9 | 1406 | 0.00025038 | 1.6027e-06 | 156.2222
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 2 | 381 | 16875 | 0.0030051 | 6.7848e-05 | 44.2913
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | FO | NONE | 1 | 1 | 16 | 2.8493e-06 | 1.7808e-07 | 16
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 291 | 5.1821e-05 | 1.7808e-07 | 291
AEP Total | 2025 | 5615460 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 1 | 1 | 178 | 3.1698e-05 | 1.7808e-07 | 178
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | INSULATOR | 1 | 1 | 105 | 1.8908e-05 | 1.8007e-07 | 105
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | CIRCUIT SWITCHER | 2 | 883 | 35703 | 0.0064033 | 0.00015837 | 40.4337
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | ARRESTER | 5 | 1815 | 439230 | 0.08009 | 0.00033095 | 242
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CROSSARM | 1 | 2 | 88 | 1.6046e-05 | 3.6468e-07 | 44
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | CUTOUT | 13 | 101 | 8489 | 0.0015117 | 1.7986e-05 | 84.0495
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONN/CLAMP | 8 | 17 | 1682 | 0.00029953 | 3.0274e-06 | 98.9412
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 5 | 39 | 11766 | 0.0020953 | 6.9451e-06 | 301.6923
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | POLE HARDWARE | 9 | 3071 | 362385 | 0.064533 | 0.00054688 | 118.0023
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 2 | 4 | 330 | 5.8766e-05 | 7.1232e-07 | 82.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CUTOUT | 2 | 12 | 1104 | 0.0001966 | 2.137e-06 | 92
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | REGULATOR | 1 | 60 | 5160 | 0.00092545 | 1.0761e-05 | 86
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WL | MOAB | 2 | 2 | 5083 | 0.00091164 | 3.587e-07 | 2541.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | ARRESTER | 4 | 4 | 253 | 4.5054e-05 | 7.1232e-07 | 63.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | POLE | 1 | 3 | 459 | 8.1739e-05 | 5.3424e-07 | 153
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | METERING | 1 | 1 | 205 | 3.6506e-05 | 1.7808e-07 | 205
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | OTHER EQUIPMENT | 1 | 1 | 139 | 2.4753e-05 | 1.7808e-07 | 139
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 774 | 167842 | 0.029889 | 0.00013783 | 216.8501
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CROSSARM | 1 | 1 | 98 | 1.7452e-05 | 1.7808e-07 | 98
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | NONE | 1 | 7 | 392 | 6.9807e-05 | 1.2466e-06 | 56
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | INSULATOR | 1 | 2 | 298 | 5.3068e-05 | 3.5616e-07 | 149
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 5 | 695 | 0.00012377 | 8.904e-07 | 139
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | METERING | 2 | 2 | 366 | 6.5177e-05 | 3.5616e-07 | 183
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONN/CLAMP | 4 | 31 | 6821 | 0.0012147 | 5.5205e-06 | 220.0323
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 26 | 6207 | 653686 | 0.11641 | 0.0011053 | 105.3143
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | ARRESTER | 4 | 40 | 5082 | 0.000905 | 7.1232e-06 | 127.05
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | METERING | 1 | 3 | 78 | 1.389e-05 | 5.3424e-07 | 26
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 4 | 160 | 20741 | 0.0036936 | 2.8493e-05 | 129.6312
AEP Total | 2025 | 5615460 | PARTIAL POWER | O | CONDUCTOR OVERHEAD | 1 | 1 | 84 | 1.4959e-05 | 1.7808e-07 | 84
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 1 | 397 | 7.0698e-05 | 1.7808e-07 | 397
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 1 | 8 | 192 | 3.4191e-05 | 1.4246e-06 | 24
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CUTOUT | 1 | 1 | 300 | 5.3424e-05 | 1.7808e-07 | 300
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | GUY/ANCHOR | 1 | 3 | 543 | 9.9012e-05 | 5.4703e-07 | 181
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | ARRESTER | 1 | 3 | 174 | 3.1728e-05 | 5.4703e-07 | 58
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 9 | 1044 | 0.00018724 | 1.6142e-06 | 116
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CIRCUIT SWITCHER | 1 | 1054 | 31620 | 0.0057657 | 0.00019219 | 30
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 38 | 4522 | 0.00081102 | 6.8153e-06 | 119
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | SPLICE, OH | 1 | 3 | 639 | 0.00011652 | 5.4703e-07 | 213
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CONN/CLAMP | 1 | 1 | 89 | 1.5849e-05 | 1.7808e-07 | 89
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | ARRESTER | 8 | 1254 | 101367 | 0.018253 | 0.00022581 | 80.8349
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 350 | 5010 | 1367922 | 0.24632 | 0.00090216 | 273.0383
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 84 | 7375 | 913462 | 0.16449 | 0.001328 | 123.8593
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 72 | 21947 | 3674169 | 0.66161 | 0.003952 | 167.411
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 90 | 18309 | 0.0032969 | 1.6206e-05 | 203.4333
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | NONE | 79 | 137 | 14224 | 0.0025511 | 2.4571e-05 | 103.8248
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | INSULATOR | 109 | 17947 | 2231981 | 0.40031 | 0.0032188 | 124.3651
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 19 | 185 | 39341 | 0.0071735 | 3.3733e-05 | 212.6541
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | TRANSFORMER, OH | 1 | 1 | 71 | 1.2946e-05 | 1.8234e-07 | 71
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | INSULATOR | 1 | 3081 | 191073 | 0.034841 | 0.0005618 | 62.0166
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | NONE | 44 | 1086 | 786436 | 0.1434 | 0.00019802 | 724.1584
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 2 | 1408 | 0.00025674 | 3.6468e-07 | 704
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 9 | 1386 | 0.00025273 | 1.6411e-06 | 154
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | INSULATOR | 2 | 94 | 51284 | 0.0093512 | 1.714e-05 | 545.5745
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | ARRESTER | 50 | 87 | 10418 | 0.0018685 | 1.5603e-05 | 119.7471
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | TRANSFORMER, OH | 1 | 14 | 6286 | 0.0011274 | 2.5109e-06 | 449
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 176 | 993 | 293035 | 0.052556 | 0.00017809 | 295.1007
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 21 | 6867 | 1219395 | 0.2187 | 0.0012316 | 177.5732
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 193 | 400 | 46281 | 0.0082417 | 7.1232e-05 | 115.7025
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | NONE | 109 | 640 | 82947 | 0.014877 | 0.00011478 | 129.6047
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR UG | 2 | 4 | 1110 | 0.00019767 | 7.1232e-07 | 277.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 7 | 357 | 6.4028e-05 | 1.2555e-06 | 51
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | METERING | 14 | 16 | 5008 | 0.00089819 | 2.8696e-06 | 313
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | ARRESTER | 7 | 23 | 3633 | 0.00065158 | 4.1251e-06 | 157.9565
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 14 | 211 | 27674 | 0.0049633 | 3.7843e-05 | 131.1564
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 4 | 760 | 0.00013631 | 7.174e-07 | 190
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 7 | 111 | 19808 | 0.0035526 | 1.9908e-05 | 178.4505
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | TRANSFORMER, POWER - LTC | 1 | 4 | 1348 | 0.00024176 | 7.174e-07 | 337
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 210 | 690 | 71670 | 0.012763 | 0.00012288 | 103.8696
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | REGULATOR | 1 | 24 | 240 | 4.3044e-05 | 4.3044e-06 | 10
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 4 | 32 | 3688 | 0.00065676 | 5.6986e-06 | 115.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | INSULATOR | 7 | 220 | 50810 | 0.0091495 | 3.9616e-05 | 230.9545
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | METERING | 1 | 3 | 282 | 5.078e-05 | 5.4022e-07 | 94
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | FUSE | 2 | 3 | 657 | 0.00011831 | 5.4022e-07 | 219
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 8 | 60 | 18267 | 0.0032894 | 1.0804e-05 | 304.45
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | SWITCH, OH | 1 | 214 | 8774 | 0.0015736 | 3.8381e-05 | 41
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 2 | 2 | 180 | 3.2413e-05 | 3.6014e-07 | 90
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 10 | 96 | 18414 | 0.0033158 | 1.7287e-05 | 191.8125
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | JUMPER/RISER | 1 | 1 | 51 | 9.1837e-06 | 1.8007e-07 | 51
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 44 | 7.9232e-06 | 1.8007e-07 | 44
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | METERING | 1 | 14 | 2856 | 0.00051429 | 2.521e-06 | 204
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CAPACITOR | 1 | 567 | 24318 | 0.0043614 | 0.00010169 | 42.8889
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 4 | 16 | 1502 | 0.00026938 | 2.8696e-06 | 93.875
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 335 | 6.0324e-05 | 1.8007e-07 | 335
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 12 | 245 | 35246 | 0.0062766 | 4.363e-05 | 143.8612
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 12 | 239 | 31492 | 0.0056081 | 4.2561e-05 | 131.7657
AEP Total | 2021 | 5523447 | PARTIAL POWER | UB | NONE | 1 | 1 | 54 | 9.7765e-06 | 1.8105e-07 | 54
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 807 | 533427 | 0.097266 | 0.00014715 | 661
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | SECTIONALIZER | 1 | 12 | 5448 | 0.0009934 | 2.1881e-06 | 454
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 12 | 2904 | 0.00052576 | 2.1726e-06 | 242
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 96 | 22752 | 0.0041192 | 1.738e-05 | 237
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 1 | 79 | 1.4226e-05 | 1.8007e-07 | 79
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 149 | 143848 | 0.025903 | 2.6831e-05 | 965.4228
AEP Total | 2020 | 5484199 | PARTIAL POWER | WI | CONDUCTOR OVERHEAD | 1 | 1 | 238 | 4.3397e-05 | 1.8234e-07 | 238
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 83 | 1.5027e-05 | 1.8105e-07 | 83
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 649 | 0.00011687 | 1.8007e-07 | 649
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | ARRESTER | 2 | 1860 | 18600 | 0.0033916 | 0.00033916 | 10
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 105 | 20887 | 0.0037612 | 1.8908e-05 | 198.9238
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | NONE | 105 | 342 | 27955 | 0.0049782 | 6.0903e-05 | 81.7398
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | TRANSFORMER, OH | 5 | 17 | 3649 | 0.00064981 | 3.0274e-06 | 214.6471
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WL | NONE | 8 | 3924 | 250924 | 0.044684 | 0.00069879 | 63.946
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | SPLICE, OH | 13 | 61 | 7007 | 0.0012478 | 1.0863e-05 | 114.8689
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | METERING | 1 | 24 | 1224 | 0.00021952 | 4.3044e-06 | 51
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CONN/CLAMP | 2 | 2 | 1784 | 0.00031769 | 3.5616e-07 | 892
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 61 | 9821 | 0.0017908 | 1.1123e-05 | 161
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | NETWORK TRANSFORMER | 1 | 8 | 712 | 0.00012983 | 1.4587e-06 | 89
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | CIRCUIT SWITCHER | 3 | 2489 | 237289 | 0.043268 | 0.00045385 | 95.3351
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | BREAKER | 3 | 3666 | 313826 | 0.057224 | 0.00066847 | 85.6045
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 3 | 631 | 343841 | 0.061916 | 0.00011363 | 544.9144
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | CABLE TERMINATOR | 2 | 3 | 402 | 7.2099e-05 | 5.3805e-07 | 134
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | NONE | 4 | 318 | 375872 | 0.067684 | 5.7263e-05 | 1181.9874
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | NONE | 502 | 4556 | 530872 | 0.094538 | 0.00081133 | 116.5215
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 28 | 1570 | 149055 | 0.026544 | 0.00027959 | 94.9395
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | NONE | 22 | 1916 | 5225938 | 0.93063 | 0.0003412 | 2727.5251
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 24 | 525 | 264742 | 0.047145 | 9.3492e-05 | 504.2705
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CUTOUT | 27 | 467 | 42211 | 0.0075169 | 8.3163e-05 | 90.3876
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 136 | 1360 | 0.00024392 | 2.4392e-05 | 10
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | NONE | 19 | 32 | 3103 | 0.00055258 | 5.6986e-06 | 96.9688
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | NONE | 15 | 10499 | 1137190 | 0.20251 | 0.0018697 | 108.3141
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | PEDESTAL | 5 | 22 | 1716 | 0.00030558 | 3.9178e-06 | 78
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 15 | 52 | 7738 | 0.001378 | 9.2601e-06 | 148.8077
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WH | NONE | 2 | 2 | 339 | 6.08e-05 | 3.587e-07 | 169.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CROSSARM | 1 | 1 | 34 | 6.0547e-06 | 1.7808e-07 | 34
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 5 | 1422 | 25953 | 0.0046217 | 0.00025323 | 18.2511
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 1 | 178 | 3.2226e-05 | 1.8105e-07 | 178
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | GUY/ANCHOR | 1 | 47 | 63309 | 0.011544 | 8.5701e-06 | 1347
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONN/CLAMP | 3 | 138 | 11057 | 0.0020162 | 2.5163e-05 | 80.1232
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | BREAKER | 1 | 1418 | 100678 | 0.018358 | 0.00025856 | 71
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 8 | 3408 | 0.00061701 | 1.4484e-06 | 426
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WH | POLE | 2 | 19 | 918 | 0.0001662 | 3.4399e-06 | 48.3158
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | TRANSFORMER, OH | 2 | 2 | 261 | 4.7253e-05 | 3.6209e-07 | 130.5
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | JUMPER/RISER | 3 | 51 | 9617 | 0.0017318 | 9.1837e-06 | 188.5686
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 2 | 11 | 2193 | 0.0003949 | 1.9808e-06 | 199.3636
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 189 | 3.4034e-05 | 3.6014e-07 | 94.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 88 | 707 | 75614 | 0.013465 | 0.0001259 | 106.9505
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 125 | 7700 | 893211 | 0.15906 | 0.0013712 | 116.0014
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | METERING | 42 | 45 | 3691 | 0.00065729 | 8.0136e-06 | 82.0222
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | SPLICE, OH | 7 | 59 | 6959 | 0.0012393 | 1.0507e-05 | 117.9492
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | POLE | 1 | 90 | 24189 | 0.0043558 | 1.6206e-05 | 268.7667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 9 | 2721 | 164092 | 0.029221 | 0.00048456 | 60.3058
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 11 | 815 | 138999 | 0.024753 | 0.00014514 | 170.5509
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | METERING | 3 | 3 | 101 | 1.7986e-05 | 5.3424e-07 | 33.6667
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | ARRESTER | 22 | 295 | 17107 | 0.0030464 | 5.2534e-05 | 57.9898
AEP Total | 2025 | 5615460 | PARTIAL POWER | CF | CONN/CLAMP | 15 | 66 | 8507 | 0.0015149 | 1.1753e-05 | 128.8939
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 96 | 96 | 14197 | 0.0025282 | 1.7096e-05 | 147.8854
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 9 | 30 | 7959 | 0.0014173 | 5.3424e-06 | 265.3
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 5 | 59 | 10394 | 0.001851 | 1.0507e-05 | 176.1695
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AF | JUMPER/RISER | 2 | 971 | 14565 | 0.0025937 | 0.00017292 | 15
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 2 | 199 | 96788 | 0.017236 | 3.5438e-05 | 486.3719
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | NONE | 5 | 55 | 4581 | 0.00081578 | 9.7944e-06 | 83.2909
AEP Total | 2023 | 5575683 | PARTIAL POWER | AF | CONDUCTOR UG | 1 | 2 | 778 | 0.00013953 | 3.587e-07 | 389
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UB | CONDUCTOR UG | 1 | 1 | 90 | 1.6027e-05 | 1.7808e-07 | 90
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 1 | 8 | 1376 | 0.00024504 | 1.4246e-06 | 172
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 1 | 1 | 107 | 1.9268e-05 | 1.8007e-07 | 107
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONN/CLAMP | 2 | 167 | 7123 | 0.0012827 | 3.0072e-05 | 42.6527
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 9 | 1170 | 0.00021068 | 1.6206e-06 | 130
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 3 | 1280 | 129099 | 0.02299 | 0.00022794 | 100.8586
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | POLE | 1 | 5 | 2515 | 0.00044787 | 8.904e-07 | 503
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ERO | NONE | 2 | 1031 | 43302 | 0.0077112 | 0.0001836 | 42
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | TRANSFORMER, UG | 1 | 13 | 3016 | 0.00053709 | 2.315e-06 | 232
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | CROSSARM | 1 | 1 | 50 | 8.904e-06 | 1.7808e-07 | 50
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | REGULATOR | 9 | 5190 | 623123 | 0.11281 | 0.00093963 | 120.0622
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1150 | 134422 | 16146611 | 2.9076 | 0.024206 | 120.1188
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 370 | 386 | 60360 | 0.010869 | 6.9508e-05 | 156.3731
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | JUMPER/RISER | 68 | 2639 | 314469 | 0.056627 | 0.00047521 | 119.1622
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 112 | 18923 | 1785553 | 0.32153 | 0.0034075 | 94.3589
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 10 | 64 | 13798 | 0.0024846 | 1.1525e-05 | 215.5938
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | POLE | 20 | 373 | 80859 | 0.01456 | 6.7167e-05 | 216.7802
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | POLE | 3 | 224 | 6100 | 0.0010863 | 3.989e-05 | 27.2321
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | BREAKER | 1 | 1 | 284 | 5.0575e-05 | 1.7808e-07 | 284
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 5 | 1115 | 55750 | 0.010093 | 0.00020187 | 50
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 5 | 31 | 24544 | 0.0044754 | 5.6526e-06 | 791.7419
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | TRANSFORMER, UG | 1 | 11 | 1826 | 0.00033296 | 2.0058e-06 | 166
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABI | RECLOSER, LINE/OCR/BR | 1 | 1283 | 198290 | 0.035706 | 0.00023103 | 154.5518
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CUTOUT | 9 | 14 | 4580 | 0.00082919 | 2.5346e-06 | 327.1429
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 38 | 896 | 122519 | 0.022182 | 0.00016222 | 136.74
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WH | NONE | 14 | 1356 | 1044918 | 0.18918 | 0.0002455 | 770.5885
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AB | NONE | 6 | 3693 | 982521 | 0.17788 | 0.0006686 | 266.0496
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | FUSE | 4 | 15 | 967 | 0.00017507 | 2.7157e-06 | 64.4667
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 2 | 1940 | 328443 | 0.059463 | 0.00035123 | 169.3005
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | METERING | 7 | 13 | 1249 | 0.00022613 | 2.3536e-06 | 96.0769
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CUTOUT | 1 | 1 | 442 | 8.0022e-05 | 1.8105e-07 | 442
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | NONE | 4 | 746 | 113458 | 0.020541 | 0.00013506 | 152.0885
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 1 | 1 | 68 | 1.2311e-05 | 1.8105e-07 | 68
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | NONE | 1049 | 11938 | 845208 | 0.15412 | 0.0021768 | 70.7998
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | FUSE | 2 | 43 | 4020 | 0.00073301 | 7.8407e-06 | 93.4884
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 11 | 1512 | 92230 | 0.016817 | 0.0002757 | 60.9987
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 89 | 9547 | 1075458 | 0.1961 | 0.0017408 | 112.6488
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 167 | 50219 | 7587415 | 1.3835 | 0.009157 | 151.0865
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | METERING | 5 | 11 | 1347 | 0.00024561 | 2.0058e-06 | 122.4545
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | NONE | 33 | 1113 | 102428 | 0.018677 | 0.00020295 | 92.0288
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | TRANSFORMER, STATION SERVICE | 3 | 103 | 7107 | 0.0012959 | 1.8781e-05 | 69
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 17 | 247 | 118047 | 0.021525 | 4.5038e-05 | 477.9231
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 3 | 71 | 6805 | 0.0012408 | 1.2946e-05 | 95.8451
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | TRANSFORMER, OH | 1 | 1 | 49 | 8.9348e-06 | 1.8234e-07 | 49
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | METERING | 5 | 5 | 803 | 0.00014642 | 9.1171e-07 | 160.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 8 | 71 | 13098 | 0.0023883 | 1.2946e-05 | 184.4789
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 18 | 1198 | 0.00021689 | 3.2588e-06 | 66.5556
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | POLE HARDWARE | 1 | 7 | 2562 | 0.00046384 | 1.2673e-06 | 366
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 6 | 69 | 31414 | 0.0056874 | 1.2492e-05 | 455.2754
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 145 | 2.6252e-05 | 1.8105e-07 | 145
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | ARRESTER | 10 | 80 | 11520 | 0.0020661 | 1.4348e-05 | 144
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SWITCH, OH | 12 | 7874 | 960815 | 0.17232 | 0.0014122 | 122.0237
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 127 | 127 | 18992 | 0.0034062 | 2.2777e-05 | 149.5433
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 99 | 9702 | 0.0017471 | 1.7827e-05 | 98
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | NONE | 15 | 146 | 36020 | 0.0064602 | 2.6185e-05 | 246.7123
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | CONN/CLAMP | 59 | 123 | 16783 | 0.00301 | 2.206e-05 | 136.4472
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 40 | 3140 | 258066 | 0.046284 | 0.00056316 | 82.1866
AEP Total | 2022 | 5553337 | PARTIAL POWER | UB | NONE | 1 | 1 | 144 | 2.593e-05 | 1.8007e-07 | 144
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CUTOUT | 1 | 1 | 57 | 1.0264e-05 | 1.8007e-07 | 57
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 1 | 1 | 516 | 9.2917e-05 | 1.8007e-07 | 516
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | FUSE | 7 | 22 | 2001 | 0.00035888 | 3.9457e-06 | 90.9545
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | SWITCH, OH | 8 | 1913 | 111543 | 0.020086 | 0.00034448 | 58.3079
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CROSSARM | 5 | 1162 | 136889 | 0.024551 | 0.0002084 | 117.8046
AEP Total | 2022 | 5553337 | PARTIAL POWER | FO | NONE | 6 | 22 | 1516 | 0.00027299 | 3.9616e-06 | 68.9091
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CUTOUT | 11 | 393 | 57204 | 0.010301 | 7.0768e-05 | 145.5573
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 19 | 969 | 0.00017379 | 3.4077e-06 | 51
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONN/CLAMP | 3 | 3 | 255 | 4.5734e-05 | 5.3805e-07 | 85
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 1237 | 2746 | 260469 | 0.046384 | 0.00048901 | 94.854
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CUTOUT | 475 | 14372 | 1295451 | 0.23069 | 0.0025594 | 90.1371
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | OL | NONE | 1 | 4 | 336 | 6.0262e-05 | 7.174e-07 | 84
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | NONE | 45 | 155 | 15818 | 0.002837 | 2.7799e-05 | 102.0516
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 6 | 552 | 9.9001e-05 | 1.0761e-06 | 92
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CROSSARM | 12 | 133 | 29342 | 0.0052625 | 2.3854e-05 | 220.6165
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | TRANSFORMER, UG | 1 | 22 | 2508 | 0.00044981 | 3.9457e-06 | 114
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 3 | 1119 | 979136 | 0.17561 | 0.00020069 | 875.0098
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 2 | 2 | 326 | 5.8054e-05 | 3.5616e-07 | 163
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 271 | 23528 | 2551211 | 0.45432 | 0.0041899 | 108.433
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE HARDWARE | 7 | 1450 | 156950 | 0.02795 | 0.00025822 | 108.2414
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | ARRESTER | 2 | 5 | 604 | 0.00010833 | 8.9675e-07 | 120.8
AEP Total | 2024 | 5615460 | PARTIAL POWER | U | NONE | 100 | 233 | 23686 | 0.004218 | 4.1493e-05 | 101.6567
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | NONE | 43 | 1824 | 865517 | 0.15782 | 0.00033259 | 474.5159
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 5 | 11 | 2103 | 0.0003745 | 1.9589e-06 | 191.1818
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | POLE | 1 | 1 | 361 | 6.5358e-05 | 1.8105e-07 | 361
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | REGULATOR | 2 | 726 | 42038 | 0.0074861 | 0.00012929 | 57.9036
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | JUMPER/RISER | 2 | 8 | 410 | 7.3013e-05 | 1.4246e-06 | 51.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | METERING | 1 | 1 | 85 | 1.5137e-05 | 1.7808e-07 | 85
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | PEDESTAL | 7 | 16 | 2347 | 0.00041795 | 2.8493e-06 | 146.6875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONN/CLAMP | 1 | 6 | 2232 | 0.00040031 | 1.0761e-06 | 372
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | METERING | 3 | 3 | 460 | 8.1917e-05 | 5.3424e-07 | 153.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 7 | 5076 | 343571 | 0.061183 | 0.00090393 | 67.6854
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 1 | 4 | 348 | 6.1972e-05 | 7.1232e-07 | 87
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 3 | 11 | 2062 | 0.0003672 | 1.9589e-06 | 187.4545
AEP Total | 2024 | 5615460 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 95 | 1.6918e-05 | 1.7808e-07 | 95
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 1 | 127 | 2.2616e-05 | 1.7808e-07 | 127
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | SPLICE, OH | 1 | 1 | 55 | 9.7944e-06 | 1.7808e-07 | 55
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CUTOUT | 11 | 55 | 7496 | 0.0013349 | 9.7944e-06 | 136.2909
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | BREAKER | 2 | 3178 | 373787 | 0.066564 | 0.00056594 | 117.6171
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | POLE HARDWARE | 1 | 1 | 110 | 1.9589e-05 | 1.7808e-07 | 110
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | POLE HARDWARE | 1 | 13 | 2249 | 0.0004005 | 2.315e-06 | 173
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | CONN/CLAMP | 1 | 10 | 520 | 9.2601e-05 | 1.7808e-06 | 52
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 85 | 1.5389e-05 | 1.8105e-07 | 85
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 3 | 16 | 4588 | 0.00083064 | 2.8967e-06 | 286.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | BREAKER | 3 | 3920 | 1189393 | 0.21534 | 0.0007097 | 303.4166
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CUTOUT | 5 | 19 | 1568 | 0.00028388 | 3.4399e-06 | 82.5263
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | NONE | 66 | 125 | 13274 | 0.0023903 | 2.2509e-05 | 106.192
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | NONE | 1944 | 40101 | 4241498 | 0.76377 | 0.0072211 | 105.7704
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 9 | 37 | 3187 | 0.00057389 | 6.6627e-06 | 86.1351
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CUTOUT | 27 | 130 | 14777 | 0.0026609 | 2.3409e-05 | 113.6692
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | ARRESTER | 32 | 1228 | 100417 | 0.018082 | 0.00022113 | 81.7728
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | METERING | 1 | 1 | 132 | 2.3898e-05 | 1.8105e-07 | 132
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | ARRESTER | 323 | 6668 | 755744 | 0.1378 | 0.0012159 | 113.3389
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 118 | 859 | 115700 | 0.021097 | 0.00015663 | 134.6915
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONN/CLAMP | 3 | 141 | 13112 | 0.0023909 | 2.571e-05 | 92.9929
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | ARRESTER | 30 | 220 | 24857 | 0.0045325 | 4.0115e-05 | 112.9864
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | NONE | 1 | 1 | 46 | 8.3877e-06 | 1.8234e-07 | 46
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | JUMPER/RISER | 23 | 2002 | 311672 | 0.056831 | 0.00036505 | 155.6803
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | CF | ARRESTER | 2 | 1548 | 271647 | 0.049533 | 0.00028227 | 175.4826
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CROSSARM | 4 | 121 | 3639 | 0.00066354 | 2.2063e-05 | 30.0744
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CUTOUT | 4 | 4 | 277 | 5.0509e-05 | 7.2937e-07 | 69.25
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONDUCTOR UG | 2 | 2 | 279 | 5.0873e-05 | 3.6468e-07 | 139.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | OTHER EQUIPMENT | 4 | 13 | 584 | 0.00010649 | 2.3704e-06 | 44.9231
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | POLE | 1 | 1 | 27 | 4.9232e-06 | 1.8234e-07 | 27
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 58 | 27176 | 0.0049553 | 1.0576e-05 | 468.5517
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | SPLICE, OH | 3 | 3 | 262 | 4.7774e-05 | 5.4703e-07 | 87.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | ARRESTER | 401 | 4346 | 534263 | 0.09582 | 0.00077946 | 122.9321
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | NONE | 4214 | 104810 | 16029556 | 2.8749 | 0.018798 | 152.9392
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONN/CLAMP | 1391 | 3779 | 424981 | 0.076527 | 0.00068049 | 112.4586
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | INSULATOR | 2 | 398 | 157629 | 0.028385 | 7.1669e-05 | 396.0528
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | CF | BREAKER | 7 | 6790 | 755422 | 0.13603 | 0.0012227 | 111.2551
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONN/CLAMP | 80 | 449 | 48331 | 0.0087031 | 8.0852e-05 | 107.6414
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 21 | 505 | 56738 | 0.010217 | 9.0936e-05 | 112.3525
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 11 | 111 | 21403 | 0.0038541 | 1.9988e-05 | 192.8198
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 5 | 93 | 19223 | 0.0034615 | 1.6747e-05 | 206.6989
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WH | NONE | 1 | 16 | 864 | 0.00015558 | 2.8812e-06 | 54
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE | 13 | 388 | 122166 | 0.021999 | 6.9868e-05 | 314.8608
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | U | NONE | 27 | 16605 | 1321275 | 0.23792 | 0.0029901 | 79.5709
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | INSULATOR | 10 | 117 | 26320 | 0.0047395 | 2.1068e-05 | 224.9573
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONN/CLAMP | 5 | 6 | 826 | 0.00014814 | 1.0761e-06 | 137.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, OH | 13 | 712 | 237777 | 0.042645 | 0.0001277 | 333.9565
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 102 | 12815 | 1505105 | 0.26994 | 0.0022984 | 117.4487
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | REGULATOR | 6 | 2944 | 153641 | 0.027666 | 0.00053013 | 52.1878
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | POLE HARDWARE | 1 | 4 | 820 | 0.00014603 | 7.1232e-07 | 205
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 3 | 10 | 1204 | 0.00021441 | 1.7808e-06 | 120.4
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 2 | 5 | 1573 | 0.00028012 | 8.904e-07 | 314.6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 1 | 1 | 330 | 5.8766e-05 | 1.7808e-07 | 330
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, UG | 4 | 204 | 61567 | 0.010964 | 3.6328e-05 | 301.799
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | WI | NONE | 3 | 934 | 552280 | 0.09835 | 0.00016633 | 591.3062
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | NONE | 8 | 18 | 3311 | 0.00058962 | 3.2054e-06 | 183.9444
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | BREAKER | 6 | 3267 | 261031 | 0.046484 | 0.00058179 | 79.8993
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WU | NONE | 20 | 15665 | 1270573 | 0.22626 | 0.0027896 | 81.109
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | NONE | 14 | 17 | 2420 | 0.00043095 | 3.0274e-06 | 142.3529
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 19 | 46 | 6993 | 0.0012453 | 8.1917e-06 | 152.0217
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 4 | 29 | 7568 | 0.0013477 | 5.1643e-06 | 260.9655
AEP Total | 2024 | 5615460 | PARTIAL POWER | UB | CONN/CLAMP | 1 | 3 | 300 | 5.3424e-05 | 5.3424e-07 | 100
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | SPLICE, OH | 7 | 156 | 43032 | 0.0076631 | 2.778e-05 | 275.8462
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | RECLOSER, LINE/OCR/BR | 3 | 1875 | 136988 | 0.024395 | 0.0003339 | 73.0603
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 60 | 3380 | 0.00060191 | 1.0685e-05 | 56.3333
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | CABLE TERMINATOR | 1 | 3 | 204 | 3.6328e-05 | 5.3424e-07 | 68
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 158 | 30336 | 0.0054022 | 2.8137e-05 | 192
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CROSSARM | 3 | 13 | 2326 | 0.00041421 | 2.315e-06 | 178.9231
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 5 | 460 | 8.1917e-05 | 8.904e-07 | 92
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | TRANSFORMER, OH | 2 | 3 | 670 | 0.00012065 | 5.4022e-07 | 223.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE | 23 | 740 | 133368 | 0.02375 | 0.00013178 | 180.227
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 295 | 5.2534e-05 | 1.7808e-07 | 295
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | ARRESTER | 1 | 6 | 450 | 8.0136e-05 | 1.0685e-06 | 75
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | POLE | 1 | 1 | 77 | 1.3712e-05 | 1.7808e-07 | 77
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 3 | 6 | 415 | 7.3903e-05 | 1.0685e-06 | 69.1667
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 1 | 65 | 1.1575e-05 | 1.7808e-07 | 65
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 2 | 2 | 179 | 3.1876e-05 | 3.5616e-07 | 89.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 2 | 50 | 6348 | 0.0011305 | 8.904e-06 | 126.96
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 12 | 1634 | 0.00029098 | 2.137e-06 | 136.1667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | RECLOSER, LINE/OCR/BR | 2 | 244 | 18787 | 0.0034257 | 4.4491e-05 | 76.9959
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | CONDUCTOR UG | 1 | 1 | 446 | 7.9424e-05 | 1.7808e-07 | 446
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | SWITCH, UG | 1 | 160 | 22720 | 0.004046 | 2.8493e-05 | 142
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | TRANSFORMER, UG | 1 | 1 | 102 | 1.8599e-05 | 1.8234e-07 | 102
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | JUMPER/RISER | 35 | 312 | 48676 | 0.0088126 | 5.6486e-05 | 156.0128
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONN/CLAMP | 34 | 86 | 13283 | 0.0024048 | 1.557e-05 | 154.4535
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 2 | 5 | 488 | 8.8351e-05 | 9.0523e-07 | 97.6
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CUTOUT | 15 | 280 | 47849 | 0.0086629 | 5.0693e-05 | 170.8893
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | ARRESTER | 27 | 1239 | 118581 | 0.021469 | 0.00022432 | 95.707
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CUTOUT | 90 | 1769 | 200565 | 0.036312 | 0.00032027 | 113.3776
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | POLE | 14 | 56 | 12953 | 0.0023451 | 1.0139e-05 | 231.3036
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | CONDUCTOR OVERHEAD | 1 | 5 | 1005 | 0.00018195 | 9.0523e-07 | 201
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | POLE | 23 | 4504 | 915375 | 0.16573 | 0.00081543 | 203.236
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | INSULATOR | 5 | 664 | 96398 | 0.017453 | 0.00012021 | 145.1777
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 13 | 3487 | 149530 | 0.027072 | 0.00063131 | 42.8821
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 702 | 21472 | 0.0038874 | 0.00012709 | 30.5869
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | SPLICE, OH | 1 | 1 | 210 | 3.7397e-05 | 1.7808e-07 | 210
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | NONE | 6 | 1407 | 61840 | 0.011136 | 0.00025336 | 43.9517
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | CONN/CLAMP | 465 | 998 | 108186 | 0.019266 | 0.00017772 | 108.4028
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | NONE | 174 | 950 | 88436 | 0.015749 | 0.00016918 | 93.0905
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | NONE | 39 | 3318 | 282498 | 0.050307 | 0.00059087 | 85.141
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | JUMPER/RISER | 9 | 124 | 14848 | 0.0026441 | 2.2082e-05 | 119.7419
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 65 | 113 | 10683 | 0.0019024 | 2.0123e-05 | 94.5398
AEP Total | 2025 | 5615460 | PARTIAL POWER | A | NONE | 11 | 101 | 3684 | 0.00065605 | 1.7986e-05 | 36.4752
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | CROSSARM | 27 | 8856 | 910405 | 0.16212 | 0.0015771 | 102.8009
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 12 | 417 | 22368 | 0.0039833 | 7.4259e-05 | 53.6403
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 9 | 26 | 2308 | 0.00041101 | 4.6301e-06 | 88.7692
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 10 | 144 | 25370 | 0.0045179 | 2.5643e-05 | 176.1806
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 3 | 8 | 938 | 0.00016704 | 1.4246e-06 | 117.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | SWITCH, UG | 1 | 8 | 2704 | 0.00048955 | 1.4484e-06 | 338
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | BREAKER | 2 | 1788 | 236289 | 0.042779 | 0.00032371 | 132.1527
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | POLE | 2 | 2 | 159 | 2.8631e-05 | 3.6014e-07 | 79.5
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 2 | 3506 | 396533 | 0.071118 | 0.0006288 | 113.1013
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR UG | 1 | 1 | 258 | 4.6459e-05 | 1.8007e-07 | 258
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABX | NONE | 1 | 229 | 89310 | 0.016018 | 4.1071e-05 | 390
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | BREAKER | 1 | 1406 | 102638 | 0.018482 | 0.00025318 | 73
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | CONN/CLAMP | 35 | 479 | 61926 | 0.011028 | 8.53e-05 | 129.2818
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 48 | 48 | 5922 | 0.0010546 | 8.5478e-06 | 123.375
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | POLE | 2 | 4 | 644 | 0.00011743 | 7.2937e-07 | 161
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | JUMPER/RISER | 8 | 330 | 26111 | 0.004683 | 5.9186e-05 | 79.1242
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CABLE TERMINATOR | 6 | 70 | 14801 | 0.0026652 | 1.2605e-05 | 211.4429
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 1 | 135 | 2.431e-05 | 1.8007e-07 | 135
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE | 19 | 85 | 29786 | 0.0053421 | 1.5245e-05 | 350.4235
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | INSULATOR | 22 | 671 | 127581 | 0.022882 | 0.00012034 | 190.1356
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | METERING | 15 | 16 | 1783 | 0.00031978 | 2.8696e-06 | 111.4375
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | NONE | 27 | 33735 | 1937668 | 0.34752 | 0.0060504 | 57.4379
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 26 | 3012 | 0.00054238 | 4.6819e-06 | 115.8462
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 4 | 19 | 6016 | 0.0010833 | 3.4214e-06 | 316.6316
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | SPLICE, OH | 13 | 45 | 6296 | 0.0011292 | 8.0708e-06 | 139.9111
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | METERING | 1085 | 1357 | 131907 | 0.02349 | 0.00024165 | 97.2049
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 989 | 126198 | 14334212 | 2.5526 | 0.022473 | 113.5851
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | METERING | 124 | 147 | 11397 | 0.0020296 | 2.6178e-05 | 77.5306
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 341 | 16869 | 2547270 | 0.45362 | 0.003004 | 151.003
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 14 | 35 | 4945 | 0.0008806 | 6.2328e-06 | 141.2857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 104 | 104 | 11879 | 0.0021154 | 1.852e-05 | 114.2212
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CUTOUT | 32 | 1620 | 169259 | 0.030142 | 0.00028849 | 104.4809
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONDUCTOR UG | 47 | 78 | 12970 | 0.0023097 | 1.389e-05 | 166.2821
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 113 | 19631 | 2873174 | 0.51165 | 0.0034959 | 146.359
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | JUMPER/RISER | 2 | 2 | 218 | 3.9098e-05 | 3.587e-07 | 109
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CABLE TERMINATOR | 3 | 32 | 4418 | 0.00079237 | 5.7392e-06 | 138.0625
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONN/CLAMP | 3 | 225 | 15347 | 0.0027525 | 4.0354e-05 | 68.2089
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | GUY/ANCHOR | 1 | 57 | 11400 | 0.0020446 | 1.0223e-05 | 200
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | ARRESTER | 3 | 12 | 815 | 0.00014617 | 2.1522e-06 | 67.9167
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | ARRESTER | 2 | 2 | 161 | 2.8875e-05 | 3.587e-07 | 80.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 47 | 139 | 12270 | 0.002185 | 2.4753e-05 | 88.2734
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | METERING | 5 | 5 | 708 | 0.00012818 | 9.0523e-07 | 141.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | CROSSARM | 2 | 102 | 351644 | 0.064119 | 1.8599e-05 | 3447.4902
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | POLE | 18 | 1274 | 223566 | 0.040765 | 0.0002323 | 175.4835
AEP Total | 2020 | 5484199 | PARTIAL POWER | WH | POLE HARDWARE | 1 | 14 | 26908 | 0.0049065 | 2.5528e-06 | 1922
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | SPLICE, OH | 3 | 221 | 11788 | 0.0021494 | 4.0298e-05 | 53.3394
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | SWITCH, OH | 4 | 3614 | 278092 | 0.049876 | 0.00064817 | 76.9485
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONN/CLAMP | 2 | 2 | 184 | 3.3e-05 | 3.587e-07 | 92
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | METERING | 5 | 35 | 856 | 0.00015352 | 6.2773e-06 | 24.4571
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONN/CLAMP | 7 | 14 | 1324 | 0.00023746 | 2.5109e-06 | 94.5714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 3 | 101 | 29048 | 0.0052098 | 1.8114e-05 | 287.604
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | NONE | 94 | 351 | 24381 | 0.0043418 | 6.2506e-05 | 69.4615
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CUTOUT | 1 | 36 | 10152 | 0.0018511 | 6.5643e-06 | 282
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | NETWORK LIMITER | 1 | 362 | 60092 | 0.010957 | 6.6008e-05 | 166
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | PEDESTAL | 2 | 44 | 2380 | 0.00043397 | 8.023e-06 | 54.0909
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | TRANSFORMER, UG | 2 | 2 | 927 | 0.00016783 | 3.6209e-07 | 463.5
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONDUCTOR UG | 1 | 1 | 108 | 1.9553e-05 | 1.8105e-07 | 108
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | TRANSFORMER, POWER - LTC | 3 | 3811 | 463626 | 0.083486 | 0.00068625 | 121.6547
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | INSULATOR | 2 | 28 | 26328 | 0.0047409 | 5.042e-06 | 940.2857
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | INSULATOR | 5 | 1904 | 295804 | 0.053266 | 0.00034286 | 155.3592
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | UB | NONE | 2 | 11 | 198 | 3.5654e-05 | 1.9808e-06 | 18
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | JUMPER/RISER | 9 | 71 | 16862 | 0.0030242 | 1.2734e-05 | 237.493
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | INSULATOR | 4 | 2607 | 170027 | 0.030494 | 0.00046757 | 65.2194
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | PEDESTAL | 1 | 16 | 4832 | 0.00086662 | 2.8696e-06 | 302
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 295 | 5.3121e-05 | 3.6014e-07 | 147.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | CONN/CLAMP | 1 | 1 | 99 | 1.7756e-05 | 1.7935e-07 | 99
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | GUY/ANCHOR | 1 | 1 | 129 | 2.2972e-05 | 1.7808e-07 | 129
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | ARRESTER | 2 | 12 | 3577 | 0.00063699 | 2.137e-06 | 298.0833
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | TRANSFORMER, UG | 2 | 13 | 1586 | 0.00028243 | 2.315e-06 | 122
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | NONE | 222 | 2524 | 212810 | 0.037897 | 0.00044947 | 84.3146
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | INSULATOR | 23 | 671 | 61069 | 0.010875 | 0.00011949 | 91.0119
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | METERING | 1 | 1 | 74 | 1.3272e-05 | 1.7935e-07 | 74
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | BREAKER | 2 | 291 | 16196 | 0.0029048 | 5.2191e-05 | 55.6564
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | CUTOUT | 2 | 6 | 1337 | 0.00023979 | 1.0761e-06 | 222.8333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | CAPACITOR | 1 | 1 | 153 | 2.7898e-05 | 1.8234e-07 | 153
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CUTOUT | 9 | 152 | 12578 | 0.0022399 | 2.7068e-05 | 82.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CONN/CLAMP | 24 | 168 | 23025 | 0.0041003 | 2.9917e-05 | 137.0536
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 8 | 635 | 91753 | 0.016339 | 0.00011308 | 144.4929
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | ARRESTER | 9 | 39 | 4107 | 0.00073956 | 7.0228e-06 | 105.3077
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | NONE | 31 | 98 | 6755 | 0.0012115 | 1.7576e-05 | 68.9286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | POLE HARDWARE | 23 | 424 | 58188 | 0.010436 | 7.6044e-05 | 137.2358
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CUTOUT | 12 | 281 | 25113 | 0.0045221 | 5.06e-05 | 89.3701
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 22 | 8529 | 1225431 | 0.21978 | 0.0015297 | 143.6782
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 14 | 182 | 22218 | 0.0040513 | 3.3186e-05 | 122.0769
AEP Total | 2020 | 5484199 | PARTIAL POWER | A | NONE | 38 | 85 | 4420 | 0.00080595 | 1.5499e-05 | 52
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AO | NONE | 19 | 5342 | 774785 | 0.14128 | 0.00097407 | 145.0365
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | CUTOUT | 1 | 1 | 57 | 1.0393e-05 | 1.8234e-07 | 57
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 22 | 76 | 20550 | 0.0037471 | 1.3858e-05 | 270.3947
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 10 | 35 | 2627 | 0.00047901 | 6.382e-06 | 75.0571
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | NONE | 7 | 1593 | 120894 | 0.022044 | 0.00029047 | 75.8908
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CAPACITOR | 6 | 2853 | 192284 | 0.035061 | 0.00052022 | 67.3971
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | NONE | 3 | 4 | 414 | 7.549e-05 | 7.2937e-07 | 103.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | FUSE | 1 | 6 | 510 | 9.2994e-05 | 1.0941e-06 | 85
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CROSSARM | 3 | 14 | 2086 | 0.00038037 | 2.5528e-06 | 149
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | NONE | 8 | 360 | 13158 | 0.0023993 | 6.5643e-05 | 36.55
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 145 | 2.644e-05 | 3.6468e-07 | 72.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | ARRESTER | 13 | 230 | 23193 | 0.0042291 | 4.1939e-05 | 100.8391
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | INSULATOR | 15 | 1966 | 269673 | 0.049173 | 0.00035848 | 137.1684
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | NONE | 9 | 285 | 132535 | 0.024167 | 5.1967e-05 | 465.0351
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONN/CLAMP | 9 | 247 | 18360 | 0.0033478 | 4.5038e-05 | 74.332
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CUTOUT | 1 | 1 | 67 | 1.213e-05 | 1.8105e-07 | 67
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | RECLOSER, LINE/OCR/BR | 1 | 264 | 16632 | 0.0030112 | 4.7796e-05 | 63
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR UG | 83 | 158 | 31846 | 0.0058069 | 2.881e-05 | 201.557
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 7 | 34 | 4666 | 0.00085081 | 6.1996e-06 | 137.2353
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 11 | 23 | 4722 | 0.00086102 | 4.1939e-06 | 205.3043
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CROSSARM | 6 | 633 | 63876 | 0.011647 | 0.00011542 | 100.91
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 3 | 11 | 4316 | 0.00078699 | 2.0058e-06 | 392.3636
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | PEDESTAL | 5 | 46 | 8442 | 0.0015393 | 8.3877e-06 | 183.5217
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | ARRESTER | 5 | 213 | 16604 | 0.0030276 | 3.8839e-05 | 77.9531
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CROSSARM | 3 | 3162 | 710751 | 0.1296 | 0.00057657 | 224.7789
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | ARRESTER | 196 | 3232 | 370477 | 0.066445 | 0.00057966 | 114.6278
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | NONE | 68 | 133 | 11270 | 0.0020213 | 2.3854e-05 | 84.7368
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 52 | 339 | 55610 | 0.0099737 | 6.08e-05 | 164.0413
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | POLE HARDWARE | 6 | 393 | 54516 | 0.0097775 | 7.0485e-05 | 138.7176
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 7 | 63 | 16338 | 0.0029302 | 1.1299e-05 | 259.3333
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | TRANSFORMER, OH | 76 | 315 | 92235 | 0.016542 | 5.6495e-05 | 292.8095
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 7 | 203 | 3.6408e-05 | 1.2555e-06 | 29
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CUTOUT | 4 | 148 | 11283 | 0.0020236 | 2.6544e-05 | 76.2365
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 11 | 521 | 46031 | 0.0082557 | 9.3441e-05 | 88.3512
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AB | NONE | 10 | 8288 | 792941 | 0.14221 | 0.0014865 | 95.6734
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 11 | 93 | 15317 | 0.0027471 | 1.668e-05 | 164.6989
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ERF | NONE | 12 | 4145 | 55122 | 0.0098861 | 0.00074341 | 13.2984
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 3 | 1842 | 81178 | 0.014559 | 0.00033036 | 44.0706
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 127 | 127 | 21113 | 0.0038019 | 2.2869e-05 | 166.2441
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 64 | 1.1525e-05 | 1.8007e-07 | 64
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | METERING | 1606 | 1832 | 171532 | 0.030888 | 0.00032989 | 93.631
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 107 | 109 | 14950 | 0.0026921 | 1.9628e-05 | 137.156
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | REGULATOR | 5 | 1529 | 16884 | 0.0030403 | 0.00027533 | 11.0425
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | NONE | 77 | 191 | 29628 | 0.0053352 | 3.4394e-05 | 155.1204
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 29 | 179 | 57143 | 0.01029 | 3.2233e-05 | 319.2346
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 2 | 63 | 8778 | 0.0015807 | 1.1345e-05 | 139.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | JUMPER/RISER | 13 | 904 | 86059 | 0.015497 | 0.00016279 | 95.198
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 58 | 13965 | 0.0025147 | 1.0444e-05 | 240.7759
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SPLICE, UG | 6 | 58 | 12430 | 0.0022293 | 1.0402e-05 | 214.3103
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 933 | 26124 | 0.0047042 | 0.00016801 | 28
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | ARRESTER | 2 | 756 | 75216 | 0.013544 | 0.00013613 | 99.4921
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | POLE | 2 | 2 | 864 | 0.00015558 | 3.6014e-07 | 432
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 42 | 6835 | 0.0012308 | 7.563e-06 | 162.7381
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONN/CLAMP | 14 | 49 | 7375 | 0.0013448 | 8.9348e-06 | 150.5102
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CUTOUT | 2 | 2 | 187 | 3.4098e-05 | 3.6468e-07 | 93.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | TRANSFORMER, UG | 1 | 1 | 58 | 1.0576e-05 | 1.8234e-07 | 58
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | OTHER EQUIPMENT | 2 | 873 | 178020 | 0.032461 | 0.00015918 | 203.9175
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 106 | 38796 | 0.0069088 | 1.8876e-05 | 366
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 1 | 3 | 174 | 3.0986e-05 | 5.3424e-07 | 58
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONN/CLAMP | 1 | 1 | 238 | 4.2383e-05 | 1.7808e-07 | 238
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, UG | 1 | 27 | 2484 | 0.00044235 | 4.8082e-06 | 92
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 715 | 72369 | 0.012887 | 0.00012733 | 101.2154
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | METERING | 1 | 1 | 74 | 1.3178e-05 | 1.7808e-07 | 74
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | INSULATOR | 1 | 1 | 224 | 3.989e-05 | 1.7808e-07 | 224
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 1 | 1 | 102 | 1.8599e-05 | 1.8234e-07 | 102
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | SPLICE, OH | 1 | 1 | 102 | 1.8599e-05 | 1.8234e-07 | 102
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 55 | 9557 | 1434315 | 0.25968 | 0.0017303 | 150.08
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | NONE | 218 | 1618 | 157907 | 0.028588 | 0.00029293 | 97.5939
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 90 | 15799 | 1872876 | 0.33908 | 0.0028604 | 118.544
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | NONE | 62 | 97 | 10444 | 0.0018908 | 1.7561e-05 | 107.6701
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | NONE | 13 | 31 | 2735 | 0.00049516 | 5.6124e-06 | 88.2258
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | NONE | 86 | 10646 | 1025263 | 0.18562 | 0.0019274 | 96.305
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | POLE | 4 | 94 | 804310 | 0.14562 | 1.7018e-05 | 8556.4894
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CROSSARM | 18 | 1987 | 180656 | 0.032707 | 0.00035974 | 90.919
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR UG | 111 | 353 | 106641 | 0.019307 | 6.3909e-05 | 302.0992
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | JUMPER/RISER | 6 | 139 | 21005 | 0.0038029 | 2.5165e-05 | 151.1151
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 3 | 90 | 1.6294e-05 | 5.4314e-07 | 30
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONN/CLAMP | 2 | 41 | 4236 | 0.00076691 | 7.4229e-06 | 103.3171
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | METERING | 1 | 1 | 151 | 2.7338e-05 | 1.8105e-07 | 151
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 2 | 349 | 6.3185e-05 | 3.6209e-07 | 174.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | O | NONE | 2 | 38 | 3595 | 0.00065086 | 6.8798e-06 | 94.6053
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | ARRESTER | 9 | 4498 | 495978 | 0.089795 | 0.00081435 | 110.2663
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 247 | 4.4718e-05 | 1.8105e-07 | 247
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | RECLOSER, LINE/OCR/BR | 1 | 2 | 102 | 1.8467e-05 | 3.6209e-07 | 51
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | NONE | 3787 | 80491 | 8451737 | 1.5411 | 0.014677 | 105.0023
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 2089 | 17487 | 2006341 | 0.36584 | 0.0031886 | 114.7333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 47 | 12104 | 1472994 | 0.26859 | 0.0022071 | 121.6948
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | NONE | 163 | 25044 | 2651049 | 0.4834 | 0.0045666 | 105.8557
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE | 66 | 8246 | 1868466 | 0.3407 | 0.0015036 | 226.5906
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 6 | 1455 | 53278 | 0.0097148 | 0.00026531 | 36.6172
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 82 | 454 | 59437 | 0.010838 | 8.2783e-05 | 130.9185
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 4 | 13 | 1898 | 0.00034363 | 2.3536e-06 | 146
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CROSSARM | 4 | 44 | 2615 | 0.00047344 | 7.966e-06 | 59.4318
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | ARRESTER | 6 | 7 | 1966 | 0.00035594 | 1.2673e-06 | 280.8571
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | JUMPER/RISER | 16 | 327 | 32227 | 0.0058346 | 5.9202e-05 | 98.5535
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 3 | 2070 | 98820 | 0.017891 | 0.00037477 | 47.7391
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | BREAKER | 22 | 15897 | 1658029 | 0.30018 | 0.0028781 | 104.2982
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | INSULATOR | 14 | 5642 | 614012 | 0.11116 | 0.0010215 | 108.8288
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | POLE | 2 | 71 | 12621 | 0.002285 | 1.2854e-05 | 177.7606
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | CONDUCTOR UG | 1 | 1 | 273 | 4.9426e-05 | 1.8105e-07 | 273
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CONDUCTOR UG | 1 | 1 | 489 | 8.8532e-05 | 1.8105e-07 | 489
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, UG | 1 | 1 | 10 | 1.8105e-06 | 1.8105e-07 | 10
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | ARRESTER | 351 | 8452 | 919247 | 0.16553 | 0.001522 | 108.7609
AEP Total | 2022 | 5553337 | PARTIAL POWER | TOR | NONE | 66 | 66 | 9637 | 0.0017354 | 1.1885e-05 | 146.0152
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CROSSARM | 50 | 16503 | 2366494 | 0.42614 | 0.0029717 | 143.3978
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE | 19 | 2039 | 330371 | 0.059491 | 0.00036717 | 162.026
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1579 | 9521 | 2036856 | 0.36678 | 0.0017145 | 213.933
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | CUTOUT | 7 | 160 | 23483 | 0.0042286 | 2.8812e-05 | 146.7688
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 14 | 8277 | 564518 | 0.10165 | 0.0014905 | 68.2032
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | INSULATOR | 114 | 13898 | 1492383 | 0.26874 | 0.0025026 | 107.3811
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | CF | NONE | 5 | 2718 | 171509 | 0.030884 | 0.00048944 | 63.1012
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | JUMPER/RISER | 30 | 234 | 30285 | 0.0054535 | 4.2137e-05 | 129.4231
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | POLE HARDWARE | 22 | 1543 | 280351 | 0.050483 | 0.00027785 | 181.6922
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CROSSARM | 42 | 8978 | 1366929 | 0.24615 | 0.0016167 | 152.2532
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | NONE | 50 | 93 | 11354 | 0.0020445 | 1.6747e-05 | 122.086
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 22 | 147 | 31009 | 0.0055838 | 2.6471e-05 | 210.9456
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 303 | 4441 | 1030270 | 0.18478 | 0.00079649 | 231.9905
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 268 | 268 | 42971 | 0.0077069 | 4.8066e-05 | 160.3396
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | CONN/CLAMP | 1 | 1 | 161 | 2.8992e-05 | 1.8007e-07 | 161
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | POLE | 364 | 23265 | 3338105 | 0.59869 | 0.0041726 | 143.4818
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | TRANSFORMER, OH | 4 | 8 | 1683 | 0.00030306 | 1.4406e-06 | 210.375
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | METERING | 2 | 3 | 878 | 0.0001601 | 5.4703e-07 | 292.6667
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | NONE | 4 | 50 | 4413 | 0.00079466 | 9.0036e-06 | 88.26
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | BREAKER | 3 | 3775 | 726478 | 0.13082 | 0.00067977 | 192.4445
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | ARRESTER | 2 | 6 | 872 | 0.00015702 | 1.0804e-06 | 145.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR UG | 1 | 67 | 10759 | 0.0019479 | 1.213e-05 | 160.5821
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | POLE | 11 | 260 | 80052 | 0.014256 | 4.6301e-05 | 307.8923
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONN/CLAMP | 21 | 48 | 7013 | 0.0012489 | 8.5478e-06 | 146.1042
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONN/CLAMP | 332 | 899 | 94311 | 0.016795 | 0.00016009 | 104.9066
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 5 | 174 | 19035 | 0.0033897 | 3.0986e-05 | 109.3966
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 11 | 9301 | 149024 | 0.026538 | 0.0016563 | 16.0224
AEP Total | 2024 | 5615460 | PARTIAL POWER | WW | CONN/CLAMP | 2 | 3 | 516 | 9.1889e-05 | 5.3424e-07 | 172
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ERF | NONE | 4 | 4299 | 54278 | 0.0096658 | 0.00076557 | 12.6257
AEP Total | 2025 | 5615460 | PARTIAL POWER | CF | JUMPER/RISER | 1 | 16 | 1760 | 0.00031342 | 2.8493e-06 | 110
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | JUMPER/RISER | 4 | 726 | 73687 | 0.013122 | 0.00012929 | 101.4972
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 36 | 6.4109e-06 | 1.7808e-07 | 36
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | METERING | 5 | 15 | 3581 | 0.0006377 | 2.6712e-06 | 238.7333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | POLE HARDWARE | 2 | 28 | 80024 | 0.014251 | 4.9862e-06 | 2858
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 2 | 3880 | 855779 | 0.1524 | 0.00069095 | 220.5616
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | POLE | 1 | 472 | 105237 | 0.018741 | 8.4054e-05 | 222.9597
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | INSULATOR | 3 | 628 | 35077 | 0.0062465 | 0.00011183 | 55.8551
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 6 | 586 | 0.00010435 | 1.0685e-06 | 97.6667
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | INSULATOR | 2 | 2 | 177 | 3.152e-05 | 3.5616e-07 | 88.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, UG | 2 | 4 | 53 | 9.6641e-06 | 7.2937e-07 | 13.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | O | NONE | 5 | 12 | 2613 | 0.00047646 | 2.1881e-06 | 217.75
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CROSSARM | 1 | 29 | 4263 | 0.0007718 | 5.2503e-06 | 147
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WL | ARRESTER | 3 | 1671 | 62818 | 0.011373 | 0.00030253 | 37.5931
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABX | NONE | 1 | 140 | 13300 | 0.0023685 | 2.4931e-05 | 95
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | CONN/CLAMP | 4 | 4 | 421 | 7.4972e-05 | 7.1232e-07 | 105.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 8 | 27 | 6221 | 0.0011078 | 4.8082e-06 | 230.4074
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | SPLICE, UG | 4 | 5 | 1305 | 0.00023239 | 8.904e-07 | 261
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | SPLICE, OH | 5 | 5 | 615 | 0.00010952 | 8.904e-07 | 123
AEP Total | 2024 | 5615460 | PARTIAL POWER | ERF | NONE | 1 | 3 | 261 | 4.6479e-05 | 5.3424e-07 | 87
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 1 | 6 | 1428 | 0.0002543 | 1.0685e-06 | 238
AEP Total | 2024 | 5615460 | PARTIAL POWER | O | NONE | 2 | 2 | 132 | 2.3507e-05 | 3.5616e-07 | 66
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | METERING | 1 | 2 | 182 | 3.2411e-05 | 3.5616e-07 | 91
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 4 | 29 | 11790 | 0.002123 | 5.2221e-06 | 406.5517
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CROSSARM | 1 | 2 | 386 | 6.9508e-05 | 3.6014e-07 | 193
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | SPLICE, OH | 7 | 14 | 5185 | 0.00092334 | 2.4931e-06 | 370.3571
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | POLE | 1 | 15 | 1620 | 0.00028849 | 2.6712e-06 | 108
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | SPLICE, OH | 2 | 2 | 157 | 2.7959e-05 | 3.5616e-07 | 78.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CUTOUT | 1 | 1 | 146 | 2.6185e-05 | 1.7935e-07 | 146
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | TRANSFORMER, OH | 1 | 2 | 506 | 9.2265e-05 | 3.6468e-07 | 253
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 4 | 59 | 13833 | 0.002481 | 1.0582e-05 | 234.4576
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | INSULATOR | 1 | 741 | 6669 | 0.0011876 | 0.00013196 | 9
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | POLE | 1 | 1 | 84 | 1.4959e-05 | 1.7808e-07 | 84
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | SWITCH, OH | 1 | 16 | 1568 | 0.00028122 | 2.8696e-06 | 98
AEP Total | 2020 | 5484199 | PARTIAL POWER | WH | CONDUCTOR OVERHEAD | 1 | 1 | 77 | 1.404e-05 | 1.8234e-07 | 77
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | OTHER EQUIPMENT | 1 | 1 | 100 | 1.8234e-05 | 1.8234e-07 | 100
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | TRANSFORMER, OH | 1 | 152 | 17176 | 0.0031319 | 2.7716e-05 | 113
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | NONE | 229 | 635 | 71473 | 0.01294 | 0.00011496 | 112.5559
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | RECLOSER, LINE/OCR/BR | 1 | 45 | 5220 | 0.00094506 | 8.1471e-06 | 116
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | NONE | 25 | 4272 | 347880 | 0.062982 | 0.00077343 | 81.4326
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 25 | 2933 | 727908 | 0.13179 | 0.00053101 | 248.1787
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONDUCTOR UG | 4 | 17 | 1643 | 0.00029746 | 3.0778e-06 | 96.6471
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | ARRESTER | 4 | 46 | 3802 | 0.00067706 | 8.1917e-06 | 82.6522
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WL | CROSSARM | 2 | 58 | 4012 | 0.00071446 | 1.0329e-05 | 69.1724
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 2097 | 44415 | 0.0079094 | 0.00037343 | 21.1803
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | PEDESTAL | 1 | 1 | 122 | 2.1726e-05 | 1.7808e-07 | 122
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | PEDESTAL | 4 | 24 | 3636 | 0.0006475 | 4.2739e-06 | 151.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 7 | 1099 | 0.00019571 | 1.2466e-06 | 157
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, UG | 1 | 1 | 166 | 2.9561e-05 | 1.7808e-07 | 166
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | OTHER EQUIPMENT | 1 | 2 | 218 | 3.8821e-05 | 3.5616e-07 | 109
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | CONDUCTOR OVERHEAD | 1 | 1 | 88 | 1.5783e-05 | 1.7935e-07 | 88
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 5 | 293 | 13448 | 0.0023948 | 5.2177e-05 | 45.8976
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 4 | 21 | 5881 | 0.0010724 | 3.8292e-06 | 280.0476
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 99 | 14896 | 0.0027162 | 1.8052e-05 | 150.4646
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CUTOUT | 26 | 195 | 24367 | 0.0043878 | 3.5114e-05 | 124.959
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | NONE | 45 | 14017 | 1505405 | 0.27108 | 0.0025241 | 107.3985
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 57 | 540 | 113973 | 0.020523 | 9.7239e-05 | 211.0611
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | POLE HARDWARE | 3 | 613 | 128627 | 0.023069 | 0.00010994 | 209.832
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | U | NONE | 3551 | 119350 | 7214200 | 1.2939 | 0.021405 | 60.4457
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1524 | 19267 | 1656370 | 0.29707 | 0.0034555 | 85.9693
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | METERING | 1196 | 1389 | 121329 | 0.02176 | 0.00024912 | 87.3499
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 5 | 12 | 3749 | 0.00067238 | 2.1522e-06 | 312.4167
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WU | NONE | 13 | 8656 | 875585 | 0.15704 | 0.0015525 | 101.1535
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 186 | 357 | 49108 | 0.0088075 | 6.4028e-05 | 137.5574
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | METERING | 3 | 3 | 106 | 1.9088e-05 | 5.4022e-07 | 35.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | NONE | 72 | 6977 | 384031 | 0.068876 | 0.0012513 | 55.0424
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | CONN/CLAMP | 3 | 8 | 976 | 0.00017505 | 1.4348e-06 | 122
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERO | NONE | 8 | 3312 | 126370 | 0.022756 | 0.0005964 | 38.1552
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | CONN/CLAMP | 2 | 2 | 380 | 6.8427e-05 | 3.6014e-07 | 190
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | POLE HARDWARE | 13 | 1129 | 274041 | 0.049347 | 0.0002033 | 242.729
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | SPLICE, OH | 3 | 13 | 2154 | 0.00038787 | 2.3409e-06 | 165.6923
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 2 | 38 | 1288 | 0.00023193 | 6.8427e-06 | 33.8947
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | JUMPER/RISER | 5 | 2444 | 517298 | 0.093151 | 0.0004401 | 211.6604
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | JUMPER/RISER | 2 | 2 | 363 | 6.5366e-05 | 3.6014e-07 | 181.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | RECLOSER, LINE/OCR/BR | 3 | 736 | 91300 | 0.016441 | 0.00013253 | 124.0489
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 25 | 159 | 36592 | 0.0065628 | 2.8517e-05 | 230.1384
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 6 | 9 | 2568 | 0.00046242 | 1.6206e-06 | 285.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 506 | 86186 | 0.01552 | 9.1116e-05 | 170.3281
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 4 | 91 | 30792 | 0.0055226 | 1.6321e-05 | 338.3736
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE HARDWARE | 3 | 1986 | 573770 | 0.10291 | 0.00035619 | 288.9074
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | ARRESTER | 12 | 319 | 50917 | 0.009132 | 5.7213e-05 | 159.6144
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 4 | 18 | 1000 | 0.00017935 | 3.2283e-06 | 55.5556
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | TRANSFORMER, OH | 1 | 2 | 704 | 0.00012626 | 3.587e-07 | 352
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1394 | 9066 | 1473308 | 0.26237 | 0.0016145 | 162.5092
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | SPLICE, OH | 7 | 57 | 6059 | 0.0010867 | 1.0223e-05 | 106.2982
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 3 | 22 | 5044 | 0.00090464 | 3.9457e-06 | 229.2727
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | ARRESTER | 2 | 2 | 101 | 1.8114e-05 | 3.587e-07 | 50.5
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CABLE TERMINATOR | 3 | 3 | 237 | 4.2506e-05 | 5.3805e-07 | 79
AEP Total | 2023 | 5575683 | PARTIAL POWER | WFS | NONE | 1 | 9 | 585 | 0.00010492 | 1.6142e-06 | 65
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | JUMPER/RISER | 22 | 120 | 13372 | 0.0023813 | 2.137e-05 | 111.4333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 1 | 90 | 1.6411e-05 | 1.8234e-07 | 90
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WI | NONE | 3 | 587 | 76650 | 0.013877 | 0.00010627 | 130.5792
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CABLE TERMINATOR | 1 | 89 | 15130 | 0.0027588 | 1.6228e-05 | 170
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | TRANSFORMER, OH | 1 | 1 | 112 | 2.0422e-05 | 1.8234e-07 | 112
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | POLE | 2 | 27 | 2159 | 0.00038722 | 4.8425e-06 | 79.963
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | BREAKER | 3 | 1028 | 148682 | 0.026773 | 0.00018511 | 144.6323
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 1 | 127 | 2.2869e-05 | 1.8007e-07 | 127
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | POLE HARDWARE | 1 | 40 | 3360 | 0.00060262 | 7.174e-06 | 84
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 1 | 165 | 2.9593e-05 | 1.7935e-07 | 165
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 5 | 2883 | 188742 | 0.033987 | 0.00051915 | 65.4672
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | CABLE TERMINATOR | 2 | 5 | 1070 | 0.00019055 | 8.904e-07 | 214
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 12 | 569 | 40614 | 0.0072325 | 0.00010133 | 71.3779
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CUTOUT | 24 | 82 | 8129 | 0.0014476 | 1.4603e-05 | 99.1341
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONN/CLAMP | 123 | 123 | 18218 | 0.0032443 | 2.1904e-05 | 148.1138
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | SWITCH, OH | 1 | 11 | 1606 | 0.000286 | 1.9589e-06 | 146
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 85 | 350 | 47152 | 0.0083968 | 6.2328e-05 | 134.72
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | POLE | 10 | 4371 | 540536 | 0.096259 | 0.00077839 | 123.6642
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | JUMPER/RISER | 20 | 4965 | 643515 | 0.1146 | 0.00088417 | 129.6103
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 8 | 1072 | 0.0001909 | 1.4246e-06 | 134
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | POLE | 3 | 3 | 465 | 8.2807e-05 | 5.3424e-07 | 155
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 2 | 45 | 18810 | 0.0033497 | 8.0136e-06 | 418
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | ARRESTER | 6 | 6 | 528 | 9.4026e-05 | 1.0685e-06 | 88
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 2 | 33 | 5023 | 0.0009094 | 5.9745e-06 | 152.2121
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | POLE HARDWARE | 1 | 12 | 1044 | 0.00018901 | 2.1726e-06 | 87
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 235 | 4.2546e-05 | 1.8105e-07 | 235
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 5 | 4665 | 0.00084458 | 9.0523e-07 | 933
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 828 | 169740 | 0.030951 | 0.00015098 | 205
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | ARRESTER | 7 | 149 | 36041 | 0.0065718 | 2.7169e-05 | 241.8859
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WL | BREAKER | 5 | 6534 | 948700 | 0.17015 | 0.0011719 | 145.1944
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | SPLICE, UG | 2 | 2 | 488 | 8.7523e-05 | 3.587e-07 | 244
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1348 | 5672 | 609491 | 0.10854 | 0.0010101 | 107.4561
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 6 | 1691 | 298757 | 0.053203 | 0.00030113 | 176.6747
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 15 | 43 | 5449 | 0.00097036 | 7.6574e-06 | 126.7209
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 19 | 86 | 12057 | 0.0021471 | 1.5315e-05 | 140.1977
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 4 | 14 | 2486 | 0.00044586 | 2.5109e-06 | 177.5714
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | NONE | 15 | 4198 | 245363 | 0.043694 | 0.00074758 | 58.4476
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, OH | 81 | 343 | 76176 | 0.013565 | 6.1081e-05 | 222.0875
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | JUMPER/RISER | 17 | 2722 | 391285 | 0.06968 | 0.00048473 | 143.7491
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | ARRESTER | 2 | 384 | 92928 | 0.016667 | 6.887e-05 | 242
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | JUMPER/RISER | 1 | 4 | 760 | 0.00013631 | 7.174e-07 | 190
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | CO | CONN/CLAMP | 1 | 1 | 14 | 2.5109e-06 | 1.7935e-07 | 14
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | JUMPER/RISER | 8 | 93 | 9649 | 0.0017594 | 1.6958e-05 | 103.7527
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | POLE HARDWARE | 9 | 3668 | 542254 | 0.098876 | 0.00066883 | 147.8337
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | CONN/CLAMP | 7 | 7 | 1016 | 0.00018526 | 1.2764e-06 | 145.1429
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | AB | NONE | 4 | 1647 | 128087 | 0.023356 | 0.00030032 | 77.7699
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CROSSARM | 8 | 367 | 81563 | 0.014628 | 6.5822e-05 | 222.2425
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR UG | 2 | 8 | 2616 | 0.00046918 | 1.4348e-06 | 327
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | TRANSFORMER, GROUNDING | 1 | 4 | 436 | 7.8197e-05 | 7.174e-07 | 109
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | RECLOSER, LINE/OCR/BR | 3 | 6165 | 463793 | 0.083181 | 0.0011057 | 75.23
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | METERING | 1 | 1 | 211 | 3.7843e-05 | 1.7935e-07 | 211
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CABLE TERMINATOR | 2 | 2 | 887 | 0.00016059 | 3.6209e-07 | 443.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | METERING | 11 | 15 | 2595 | 0.00046212 | 2.6712e-06 | 173
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SPLICE, OH | 24 | 977 | 125855 | 0.022412 | 0.00017398 | 128.8178
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | REGULATOR | 1 | 159 | 13674 | 0.0024524 | 2.8517e-05 | 86
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | JUMPER/RISER | 5 | 907 | 66309 | 0.01194 | 0.00016333 | 73.108
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABX | NONE | 6 | 1849 | 205591 | 0.037222 | 0.00033475 | 111.1904
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 489 | 2759 | 592247 | 0.10547 | 0.00049132 | 214.66
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | NONE | 705 | 9839 | 972015 | 0.1731 | 0.0017521 | 98.7921
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 100 | 3689 | 471914 | 0.084038 | 0.00065694 | 127.9246
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | INSULATOR | 1 | 1 | 158 | 2.8137e-05 | 1.7808e-07 | 158
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CROSSARM | 126 | 13614 | 1590037 | 0.28315 | 0.0024244 | 116.7943
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | ARRESTER | 2 | 4 | 422 | 7.599e-05 | 7.2029e-07 | 105.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 10 | 2240 | 0.00040336 | 1.8007e-06 | 224
AEP Total | 2022 | 5553337 | PARTIAL POWER | ERF | CONN/CLAMP | 2 | 2 | 402 | 7.2389e-05 | 3.6014e-07 | 201
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 1 | 104 | 21424 | 0.0038579 | 1.8727e-05 | 206
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | ARRESTER | 3 | 269 | 105873 | 0.019065 | 4.8439e-05 | 393.5799
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 1 | 88 | 17072 | 0.0030908 | 1.5932e-05 | 194
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AF | NONE | 8 | 1431 | 74427 | 0.013254 | 0.00025483 | 52.0105
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CUTOUT | 1 | 1 | 99 | 1.763e-05 | 1.7808e-07 | 99
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 9 | 43 | 3689 | 0.00065694 | 7.6574e-06 | 85.7907
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | U | NONE | 10 | 8064 | 424789 | 0.075646 | 0.001436 | 52.6772
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | POLE | 10 | 66 | 17690 | 0.0031502 | 1.1753e-05 | 268.0303
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 3 | 7 | 547 | 9.741e-05 | 1.2466e-06 | 78.1429
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 24 | 299 | 22063 | 0.003929 | 5.3246e-05 | 73.7893
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 5 | 11 | 3215 | 0.00058623 | 2.0058e-06 | 292.2727
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 25 | 2800 | 0.00051056 | 4.5586e-06 | 112
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONN/CLAMP | 57 | 170 | 43221 | 0.007881 | 3.0998e-05 | 254.2412
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 2 | 2 | 305 | 5.5614e-05 | 3.6468e-07 | 152.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | ARRESTER | 36 | 822 | 81897 | 0.014933 | 0.00014989 | 99.6314
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | POLE | 13 | 1272 | 451887 | 0.082398 | 0.00023194 | 355.2571
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | NONE | 89 | 1744 | 146221 | 0.026662 | 0.000318 | 83.8423
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 3 | 10 | 968 | 0.00017651 | 1.8234e-06 | 96.8
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 4 | 4 | 382 | 6.9655e-05 | 7.2937e-07 | 95.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CUTOUT | 11 | 12 | 1975 | 0.00036013 | 2.1881e-06 | 164.5833
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | NONE | 83 | 458 | 86188 | 0.015716 | 8.3513e-05 | 188.1834
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | POLE | 9 | 35 | 5472 | 0.00099778 | 6.382e-06 | 156.3429
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 2 | 722 | 46622 | 0.0085012 | 0.00013165 | 64.5734
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | CONN/CLAMP | 4 | 12 | 1870 | 0.00034098 | 2.1881e-06 | 155.8333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 5 | 128 | 46677 | 0.0085112 | 2.334e-05 | 364.6641
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 2 | 371 | 49435 | 0.0090141 | 6.7649e-05 | 133.248
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | POLE | 1 | 1 | 120 | 2.1881e-05 | 1.8234e-07 | 120
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CIRCUIT SWITCHER | 1 | 1 | 178 | 3.2457e-05 | 1.8234e-07 | 178
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 9 | 64 | 10205 | 0.0018303 | 1.1478e-05 | 159.4531
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | METERING | 11 | 12 | 1330 | 0.00023854 | 2.1522e-06 | 110.8333
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 5 | 11 | 1007 | 0.00018133 | 1.9808e-06 | 91.5455
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | U | NONE | 27 | 19792 | 2134058 | 0.38274 | 0.0035497 | 107.8243
AEP Total | 2023 | 5575683 | PARTIAL POWER | FO | NONE | 11 | 15 | 1721 | 0.00030866 | 2.6903e-06 | 114.7333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | INSULATOR | 11 | 1224 | 112856 | 0.020241 | 0.00021952 | 92.2026
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 776 | 14293 | 0.0025635 | 0.00013918 | 18.4188
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 92 | 14452 | 0.002592 | 1.65e-05 | 157.087
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 16 | 2444 | 598837 | 0.1074 | 0.00043833 | 245.0233
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | NONE | 13 | 35 | 3186 | 0.00057141 | 6.2773e-06 | 91.0286
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CUTOUT | 5 | 173 | 21091 | 0.0037979 | 3.1152e-05 | 121.9133
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 1 | 6 | 534 | 9.5095e-05 | 1.0685e-06 | 89
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | CONDUCTOR OVERHEAD | 1 | 1 | 89 | 1.6228e-05 | 1.8234e-07 | 89
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 3 | 25 | 9858 | 0.0017975 | 4.5586e-06 | 394.32
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AO | INSULATOR | 3 | 974 | 392849 | 0.069958 | 0.00017345 | 403.3357
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | AF | BREAKER | 1 | 642 | 79608 | 0.014177 | 0.00011433 | 124
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CUTOUT | 1 | 15 | 810 | 0.00014424 | 2.6712e-06 | 54
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | ARRESTER | 1 | 1 | 94 | 1.674e-05 | 1.7808e-07 | 94
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 1 | 163 | 35860 | 0.0063859 | 2.9027e-05 | 220
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 8 | 168 | 3.0633e-05 | 1.4587e-06 | 21
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | BREAKER | 1 | 11 | 3542 | 0.00063526 | 1.9729e-06 | 322
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CROSSARM | 1 | 1 | 99 | 1.7827e-05 | 1.8007e-07 | 99
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CUTOUT | 460 | 13636 | 1846475 | 0.3343 | 0.0024687 | 135.4118
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | INSULATOR | 11 | 2781 | 80412 | 0.014558 | 0.00050349 | 28.9148
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 292 | 292 | 45927 | 0.0083149 | 5.2866e-05 | 157.2842
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 12 | 54 | 9274 | 0.001679 | 9.7765e-06 | 171.7407
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | INSULATOR | 11 | 516 | 85302 | 0.015444 | 9.342e-05 | 165.314
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | NONE | 186 | 2084 | 222996 | 0.040373 | 0.0003773 | 107.0038
AEP Total | 2021 | 5523447 | PARTIAL POWER | A | NONE | 51 | 89 | 7787 | 0.0014098 | 1.6113e-05 | 87.4944
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 3 | 14 | 1074 | 0.00019444 | 2.5346e-06 | 76.7143
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, OH | 65 | 229 | 62141 | 0.01125 | 4.146e-05 | 271.3581
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | FUSE | 1 | 164 | 55671 | 0.010079 | 2.9692e-05 | 339.4573
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | NONE | 21 | 945 | 48163 | 0.0087197 | 0.00017109 | 50.9661
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR UG | 74 | 187 | 30969 | 0.0056068 | 3.3856e-05 | 165.6096
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | REGULATOR | 12 | 5808 | 318341 | 0.057634 | 0.0010515 | 54.8108
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CUTOUT | 25 | 623 | 50283 | 0.0091036 | 0.00011279 | 80.7111
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 19 | 236 | 181663 | 0.032889 | 4.2727e-05 | 769.7585
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CROSSARM | 14 | 496 | 114817 | 0.020787 | 8.9799e-05 | 231.4859
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | NONE | 3 | 14 | 1726 | 0.00031249 | 2.5346e-06 | 123.2857
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | ARRESTER | 2 | 2 | 515 | 9.3239e-05 | 3.6209e-07 | 257.5
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | INSULATOR | 6 | 6478 | 466870 | 0.084525 | 0.0011728 | 72.0701
AEP Total | 2021 | 5523447 | PARTIAL POWER | WFS | CONDUCTOR UG | 1 | 1 | 279 | 5.0512e-05 | 1.8105e-07 | 279
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | TRANSFORMER, OH | 1 | 1 | 6 | 1.0863e-06 | 1.8105e-07 | 6
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 443 | 15767 | 2276982 | 0.41002 | 0.0028392 | 144.4144
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CROSSARM | 285 | 42915 | 5084592 | 0.91559 | 0.0077278 | 118.4805
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | NONE | 1310 | 14091 | 1020710 | 0.1838 | 0.0025374 | 72.437
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | ARRESTER | 11 | 96 | 8775 | 0.0015801 | 1.7287e-05 | 91.4062
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | TRANSFORMER, OH | 1 | 1 | 30 | 5.4022e-06 | 1.8007e-07 | 30
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | METERING | 123 | 126 | 10361 | 0.0018657 | 2.2689e-05 | 82.2302
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | FUSE | 2 | 6 | 338 | 6.1194e-05 | 1.0863e-06 | 56.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | U | CONN/CLAMP | 2 | 4 | 308 | 5.5762e-05 | 7.2419e-07 | 77
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | CONDUCTOR OVERHEAD | 1 | 19 | 3078 | 0.00055726 | 3.4399e-06 | 162
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 2 | 11 | 758 | 0.00013723 | 1.9915e-06 | 68.9091
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 4 | 19 | 2610 | 0.00047253 | 3.4399e-06 | 137.3684
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONN/CLAMP | 659 | 2649 | 388090 | 0.070765 | 0.00048302 | 146.5043
AEP Total | 2020 | 5484199 | PARTIAL POWER | U | NONE | 88 | 255 | 33629 | 0.006132 | 4.6497e-05 | 131.8784
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE | 354 | 24504 | 3000719 | 0.54716 | 0.0044681 | 122.4583
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | NONE | 56 | 56 | 9056 | 0.0016513 | 1.0211e-05 | 161.7143
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CUTOUT | 475 | 12933 | 1500766 | 0.27365 | 0.0023582 | 116.0416
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, OH | 7 | 17 | 1368 | 0.00024944 | 3.0998e-06 | 80.4706
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WL | BREAKER | 7 | 4660 | 496653 | 0.090561 | 0.00084971 | 106.5779
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CUTOUT | 39 | 161 | 23542 | 0.0042927 | 2.9357e-05 | 146.2236
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CUTOUT | 3 | 5 | 477 | 8.4944e-05 | 8.904e-07 | 95.4
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 5 | 34 | 6111 | 0.0010882 | 6.0547e-06 | 179.7353
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UB | CONN/CLAMP | 2 | 4 | 163 | 2.9027e-05 | 7.1232e-07 | 40.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE | 23 | 204 | 41581 | 0.0074047 | 3.6328e-05 | 203.8284
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | POLE HARDWARE | 9 | 919 | 198692 | 0.035383 | 0.00016366 | 216.2046
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | METERING | 2 | 2 | 231 | 4.1136e-05 | 3.5616e-07 | 115.5
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | CF | JUMPER/RISER | 1 | 536 | 8040 | 0.0014318 | 9.5451e-05 | 15
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | ARRESTER | 5 | 14 | 1397 | 0.00024878 | 2.4931e-06 | 99.7857
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | ARRESTER | 2 | 2 | 54 | 9.6163e-06 | 3.5616e-07 | 27
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 25 | 4125 | 0.00073458 | 4.452e-06 | 165
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 863 | 6904 | 0.0012295 | 0.00015368 | 8
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | RECLOSER, LINE/OCR/BR | 1 | 59 | 2773 | 0.00049382 | 1.0507e-05 | 47
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 1 | 1 | 91 | 1.6387e-05 | 1.8007e-07 | 91
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | JUMPER/RISER | 1 | 10 | 3010 | 0.00054885 | 1.8234e-06 | 301
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | TRANSFORMER, UG | 1 | 8 | 2400 | 0.00043217 | 1.4406e-06 | 300
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | CONDUCTOR UG | 1 | 1415 | 139504 | 0.025121 | 0.0002548 | 98.5894
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | INSULATOR | 1 | 1 | 99 | 1.7756e-05 | 1.7935e-07 | 99
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 6 | 774 | 0.00013882 | 1.0761e-06 | 129
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | CF | INSULATOR | 2 | 5096 | 609154 | 0.10925 | 0.00091397 | 119.5357
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 1 | 737 | 0.00013124 | 1.7808e-07 | 737
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 10 | 3941 | 317033 | 0.057089 | 0.00070966 | 80.4448
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | POLE HARDWARE | 2 | 7 | 1288 | 0.00023193 | 1.2605e-06 | 184
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | INSULATOR | 3 | 4472 | 1010733 | 0.182 | 0.00080528 | 226.0136
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 2 | 5 | 1100 | 0.00019589 | 8.904e-07 | 220
AEP Total | 2025 | 5615460 | PARTIAL POWER | VIN | NONE | 2 | 4 | 330 | 5.8766e-05 | 7.1232e-07 | 82.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 6 | 285 | 50113 | 0.0089241 | 5.0753e-05 | 175.8351
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 2 | 194 | 3.4547e-05 | 3.5616e-07 | 97
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | POLE HARDWARE | 1 | 5 | 715 | 0.00012733 | 8.904e-07 | 143
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 2 | 6 | 767 | 0.00013659 | 1.0685e-06 | 127.8333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERO | NONE | 1 | 36 | 396 | 7.052e-05 | 6.4109e-06 | 11
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 1 | 60 | 1.0685e-05 | 1.7808e-07 | 60
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 119 | 2.1191e-05 | 1.7808e-07 | 119
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1047 | 114656 | 14793479 | 2.6532 | 0.020564 | 129.0249
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | NONE | 198 | 33546 | 3745030 | 0.67167 | 0.0060165 | 111.6386
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 12 | 39 | 5243 | 0.00094033 | 6.9947e-06 | 134.4359
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 187 | 477 | 67937 | 0.012185 | 8.555e-05 | 142.4256
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | JUMPER/RISER | 55 | 416 | 52128 | 0.0093492 | 7.461e-05 | 125.3077
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | SPLICE, OH | 4 | 11 | 3705 | 0.00066717 | 1.9808e-06 | 336.8182
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 16 | 4904 | 0.00088307 | 2.8812e-06 | 306.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CROSSARM | 38 | 12119 | 1113458 | 0.1997 | 0.0021735 | 91.8771
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SPLICE, UG | 6 | 42 | 15408 | 0.0027745 | 7.563e-06 | 366.8571
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | POLE | 82 | 36860 | 3929109 | 0.70469 | 0.0066108 | 106.5955
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CUTOUT | 58 | 124 | 17116 | 0.0030698 | 2.2239e-05 | 138.0323
AEP Total | 2023 | 5575683 | PARTIAL POWER | WW | NONE | 17 | 43 | 10969 | 0.0019673 | 7.7121e-06 | 255.093
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | NONE | 99 | 351 | 52111 | 0.0093461 | 6.2952e-05 | 148.4644
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 36 | 147 | 30511 | 0.0054722 | 2.6364e-05 | 207.5578
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONDUCTOR UG | 1 | 1 | 55 | 9.9576e-06 | 1.8105e-07 | 55
AEP Total | 2021 | 5523447 | PARTIAL POWER | VIN | CONN/CLAMP | 3 | 3 | 342 | 6.1918e-05 | 5.4314e-07 | 114
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | CF | CAPACITOR | 1 | 1451 | 31922 | 0.0057794 | 0.0002627 | 22
AEP Total | 2021 | 5523447 | PARTIAL POWER | TR | CONN/CLAMP | 1 | 1 | 85 | 1.5389e-05 | 1.8105e-07 | 85
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 674 | 22229 | 4074688 | 0.74299 | 0.0040533 | 183.3051
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 441 | 11219 | 2356902 | 0.42976 | 0.0020457 | 210.0813
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE | 291 | 67999 | 7678412 | 1.4001 | 0.012399 | 112.9195
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 3 | 232 | 21478 | 0.0039163 | 4.2303e-05 | 92.5776
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | INSULATOR | 17 | 705 | 83660 | 0.015255 | 0.00012855 | 118.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 29 | 2551 | 537823 | 0.098068 | 0.00046515 | 210.8283
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | INSULATOR | 76 | 15788 | 1703279 | 0.31058 | 0.0028788 | 107.8844
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WU | NONE | 29 | 24464 | 2086292 | 0.38042 | 0.0044608 | 85.2801
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | NONE | 39 | 54 | 6169 | 0.0011249 | 9.8465e-06 | 114.2407
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 1 | 4 | 212 | 3.8657e-05 | 7.2937e-07 | 53
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WT | POLE | 2 | 17 | 7888 | 0.0014383 | 3.0998e-06 | 464
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONDUCTOR UG | 4 | 4 | 685 | 0.0001249 | 7.2937e-07 | 171.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - LTC | 1 | 1 | 227 | 4.1392e-05 | 1.8234e-07 | 227
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CUTOUT | 16 | 492 | 134054 | 0.024444 | 8.9712e-05 | 272.4675
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | NONE | 1497 | 15817 | 1081554 | 0.1926 | 0.0028167 | 68.3792
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 21 | 381 | 113458 | 0.020205 | 6.7848e-05 | 297.79
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 24 | 334 | 54099 | 0.0096339 | 5.9479e-05 | 161.9731
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 1 | 94 | 1.674e-05 | 1.7808e-07 | 94
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | INSULATOR | 12 | 1889 | 81765 | 0.014561 | 0.00033639 | 43.2848
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | BREAKER | 4 | 2056 | 251366 | 0.045083 | 0.00036874 | 122.2597
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 18 | 1332 | 0.00023889 | 3.2283e-06 | 74
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CROSSARM | 1 | 3 | 2082 | 0.00037076 | 5.3424e-07 | 694
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UB | NONE | 4 | 16 | 1311 | 0.00023346 | 2.8493e-06 | 81.9375
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | SWITCH, UG | 1 | 65 | 8255 | 0.00147 | 1.1575e-05 | 127
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | NONE | 280 | 3460 | 217930 | 0.038809 | 0.00061616 | 62.9855
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | NONE | 46 | 2458 | 281235 | 0.050082 | 0.00043772 | 114.4162
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 216 | 10398 | 968023 | 0.17239 | 0.0018517 | 93.097
AEP Total | 2025 | 5615460 | PARTIAL POWER | CF | NONE | 5 | 6 | 542 | 9.6519e-05 | 1.0685e-06 | 90.3333
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | NONE | 39 | 115 | 9372 | 0.001669 | 2.0479e-05 | 81.4957
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | SWITCH, OH | 4 | 2759 | 164265 | 0.029252 | 0.00049132 | 59.5379
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | TRANSFORMER, UG | 1 | 10 | 12950 | 0.0023226 | 1.7935e-06 | 1295
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 408 | 7.3175e-05 | 3.587e-07 | 204
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | BREAKER | 1 | 1563 | 35949 | 0.006555 | 0.000285 | 23
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | ARRESTER | 2 | 2 | 169 | 3.0816e-05 | 3.6468e-07 | 84.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 38 | 4482 | 0.00081726 | 6.929e-06 | 117.9474
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | JUMPER/RISER | 2 | 5 | 822 | 0.00014882 | 9.0523e-07 | 164.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | RECLOSER, LINE/OCR/BR | 1 | 1 | 251 | 4.5443e-05 | 1.8105e-07 | 251
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 1 | 1 | 92 | 1.6383e-05 | 1.7808e-07 | 92
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | NONE | 11 | 5916 | 243901 | 0.043434 | 0.0010535 | 41.2273
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 11 | 136 | 19297 | 0.0034364 | 2.4219e-05 | 141.8897
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | UB | CONDUCTOR OVERHEAD | 1 | 3 | 1002 | 0.00017844 | 5.3424e-07 | 334
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 1 | 186 | 24738 | 0.0044053 | 3.3123e-05 | 133
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | POLE HARDWARE | 1 | 67 | 3953 | 0.00070395 | 1.1931e-05 | 59
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | CF | NONE | 1 | 414 | 50922 | 0.0090682 | 7.3725e-05 | 123
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | CF | JUMPER/RISER | 1 | 2095 | 206679 | 0.036805 | 0.00037308 | 98.6535
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 69 | 1173 | 0.00021389 | 1.2582e-05 | 17
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | CF | INSULATOR | 1 | 398 | 87162 | 0.015522 | 7.0876e-05 | 219
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 1 | 1 | 115 | 2.0479e-05 | 1.7808e-07 | 115
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CUTOUT | 1 | 1 | 50 | 8.904e-06 | 1.7808e-07 | 50
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 622 | 22823 | 3836342 | 0.69456 | 0.004132 | 168.091
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONN/CLAMP | 950 | 1966 | 259798 | 0.047035 | 0.00035594 | 132.1455
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 114 | 114 | 15274 | 0.0027653 | 2.0639e-05 | 133.9825
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | NONE | 152 | 483 | 90594 | 0.016402 | 8.7445e-05 | 187.5652
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | FUSE | 22 | 200 | 21413 | 0.0038767 | 3.6209e-05 | 107.065
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | ARRESTER | 6 | 33 | 2189 | 0.00039631 | 5.9745e-06 | 66.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | BREAKER | 1 | 5 | 50 | 9.0523e-06 | 9.0523e-07 | 10
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 51 | 17331 | 2409204 | 0.43618 | 0.0031377 | 139.0113
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | NONE | 48 | 19322 | 1710253 | 0.30964 | 0.0034982 | 88.5132
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CROSSARM | 17 | 1694 | 144303 | 0.026126 | 0.00030669 | 85.1848
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 4 | 1256 | 101937 | 0.018455 | 0.00022739 | 81.16
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 1 | 88 | 1.5932e-05 | 1.8105e-07 | 88
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 2 | 47 | 22287 | 0.004035 | 8.5092e-06 | 474.1915
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | NONE | 2828 | 101449 | 10525256 | 1.8953 | 0.018268 | 103.7492
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CUTOUT | 437 | 12376 | 1531725 | 0.27582 | 0.0022286 | 123.7658
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | NONE | 113 | 3112 | 396519 | 0.071402 | 0.00056038 | 127.4161
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 221 | 5148 | 643799 | 0.11593 | 0.00092701 | 125.0581
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | FUSE | 11 | 569 | 35575 | 0.0064061 | 0.00010246 | 62.522
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CONN/CLAMP | 11 | 33 | 4485 | 0.00080762 | 5.9424e-06 | 135.9091
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | SPLICE, OH | 3 | 6 | 374 | 6.7347e-05 | 1.0804e-06 | 62.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | METERING | 1 | 45 | 2655 | 0.00048068 | 8.1471e-06 | 59
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 499 | 16240 | 0.0029402 | 9.0342e-05 | 32.5451
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | SPLICE, OH | 2 | 3 | 211 | 3.8201e-05 | 5.4314e-07 | 70.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | METERING | 2 | 2 | 1022 | 0.00018403 | 3.6014e-07 | 511
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 5 | 29 | 3008 | 0.00053566 | 5.1643e-06 | 103.7241
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WI | INSULATOR | 1 | 1 | 60 | 1.0804e-05 | 1.8007e-07 | 60
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | BREAKER | 6 | 6030 | 375753 | 0.067663 | 0.0010858 | 62.3139
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 1 | 15 | 2.7011e-06 | 1.8007e-07 | 15
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 11 | 149 | 33014 | 0.0058791 | 2.6534e-05 | 221.5705
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | SWITCH, OH | 1 | 1254 | 24768 | 0.0044107 | 0.00022331 | 19.7512
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | METERING | 1 | 1 | 89 | 1.6113e-05 | 1.8105e-07 | 89
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 123 | 26032 | 4752442 | 0.85578 | 0.0046876 | 182.5615
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | NONE | 1375 | 41337 | 3702260 | 0.66667 | 0.0074436 | 89.5629
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | POLE HARDWARE | 6 | 1018 | 86069 | 0.015582 | 0.00018431 | 84.5472
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | FUSE | 5 | 16 | 2772 | 0.00050186 | 2.8967e-06 | 173.25
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 1 | 31 | 23312 | 0.0042206 | 5.6124e-06 | 752
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | SWITCH, UG | 1 | 797 | 29489 | 0.0053389 | 0.00014429 | 37
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 1 | 1 | 311 | 5.6305e-05 | 1.8105e-07 | 311
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | SWITCH, OH | 1 | 49 | 1813 | 0.00032824 | 8.8713e-06 | 37
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | JUMPER/RISER | 2 | 211 | 21151 | 0.0038293 | 3.8201e-05 | 100.2417
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | CIRCUIT SWITCHER | 1 | 221 | 11934 | 0.0021606 | 4.0011e-05 | 54
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | CONN/CLAMP | 2 | 13 | 1436 | 0.00025998 | 2.3536e-06 | 110.4615
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 17 | 1598 | 0.00028931 | 3.0778e-06 | 94
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 390 | 4397 | 978810 | 0.17848 | 0.00080176 | 222.6086
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | METERING | 1924 | 2143 | 189415 | 0.034538 | 0.00039076 | 88.3878
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | NONE | 3360 | 90323 | 14354959 | 2.6175 | 0.01647 | 158.9292
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | NONE | 28 | 4606 | 104764 | 0.019103 | 0.00083987 | 22.7451
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 108 | 1538 | 166802 | 0.030036 | 0.00027695 | 108.4538
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONN/CLAMP | 111 | 345 | 53731 | 0.0096754 | 6.2125e-05 | 155.742
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | NONE | 21 | 8180 | 1355520 | 0.24409 | 0.001473 | 165.7115
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONN/CLAMP | 44 | 196 | 29591 | 0.0053285 | 3.5294e-05 | 150.9745
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | METERING | 4 | 9 | 684 | 0.00012317 | 1.6206e-06 | 76
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | NONE | 2863 | 120686 | 11625630 | 2.0851 | 0.021645 | 96.3296
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 91 | 19918 | 1602995 | 0.2875 | 0.0035723 | 80.4797
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 297 | 29491 | 3227014 | 0.57877 | 0.0052892 | 109.4237
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CUTOUT | 2 | 2 | 434 | 7.8151e-05 | 3.6014e-07 | 217
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 18 | 73 | 36974 | 0.006658 | 1.3145e-05 | 506.4932
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | SPLICE, OH | 3 | 7 | 1129 | 0.00020249 | 1.2555e-06 | 161.2857
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | ARRESTER | 2 | 5 | 1658 | 0.00029856 | 9.0036e-07 | 331.6
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | CONN/CLAMP | 93 | 93 | 10035 | 0.0017998 | 1.668e-05 | 107.9032
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 19 | 249 | 59693 | 0.010749 | 4.4838e-05 | 239.7309
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ERF | NONE | 20 | 1421 | 80343 | 0.01441 | 0.00025486 | 56.5398
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONN/CLAMP | 39 | 170 | 27951 | 0.005013 | 3.049e-05 | 164.4176
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | ARRESTER | 15 | 2280 | 120844 | 0.021761 | 0.00041056 | 53.0018
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 23 | 7146 | 854299 | 0.15384 | 0.0012868 | 119.5493
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | NONE | 7 | 4347 | 383896 | 0.069129 | 0.00078277 | 88.3129
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | NONE | 38 | 13853 | 1937566 | 0.3475 | 0.0024845 | 139.8662
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CUTOUT | 9 | 58 | 3253 | 0.00058343 | 1.0402e-05 | 56.0862
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 41 | 312 | 78074 | 0.014003 | 5.5957e-05 | 250.2372
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | POLE | 61 | 11364 | 2449994 | 0.43941 | 0.0020381 | 215.5926
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | BREAKER | 45 | 38792 | 4148030 | 0.74395 | 0.0069574 | 106.93
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | ARRESTER | 2 | 2 | 207 | 3.7275e-05 | 3.6014e-07 | 103.5
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 44 | 5263 | 0.00094772 | 7.9232e-06 | 119.6136
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CUTOUT | 13 | 132 | 17244 | 0.0030927 | 2.3674e-05 | 130.6364
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 4 | 424 | 7.6044e-05 | 7.174e-07 | 106
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | JUMPER/RISER | 22 | 312 | 31753 | 0.0056949 | 5.5957e-05 | 101.7724
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CUTOUT | 4 | 22 | 4149 | 0.00074412 | 3.9457e-06 | 188.5909
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, OH | 52 | 143 | 30975 | 0.005648 | 2.6075e-05 | 216.6084
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 55 | 245 | 36269 | 0.0066134 | 4.4674e-05 | 148.0367
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | TRANSFORMER, OH | 6 | 39 | 30820 | 0.0056198 | 7.1113e-06 | 790.2564
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR UG | 1 | 1 | 123 | 2.2428e-05 | 1.8234e-07 | 123
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | INSULATOR | 1 | 1 | 132 | 2.4069e-05 | 1.8234e-07 | 132
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | NONE | 10 | 73 | 5299 | 0.00096623 | 1.3311e-05 | 72.589
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | METERING | 1 | 1 | 76 | 1.3858e-05 | 1.8234e-07 | 76
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | FO | NONE | 5 | 6516 | 768258 | 0.14009 | 0.0011881 | 117.9033
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CROSSARM | 3 | 2932 | 221178 | 0.039668 | 0.00052585 | 75.4359
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | NONE | 3150 | 80410 | 10474971 | 1.8654 | 0.014319 | 130.2695
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CONN/CLAMP | 1328 | 2826 | 281482 | 0.050126 | 0.00050325 | 99.6044
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | PEDESTAL | 18 | 192 | 43144 | 0.0076831 | 3.4191e-05 | 224.7083
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | ARRESTER | 3 | 6 | 301 | 5.4202e-05 | 1.0804e-06 | 50.1667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | GUY/ANCHOR | 6 | 1173 | 23030 | 0.0041304 | 0.00021038 | 19.6334
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONN/CLAMP | 8 | 20 | 2572 | 0.00046129 | 3.587e-06 | 128.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | NONE | 1 | 11 | 2728 | 0.00048927 | 1.9729e-06 | 248
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | RELAY | 1 | 260 | 5720 | 0.0010186 | 4.6301e-05 | 22
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR UG | 1 | 1 | 1069 | 0.00019037 | 1.7808e-07 | 1069
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | TRANSFORMER, OH | 1 | 1 | 190 | 3.3835e-05 | 1.7808e-07 | 190
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 3 | 537 | 9.5629e-05 | 5.3424e-07 | 179
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR UG | 1 | 3 | 858 | 0.00015279 | 5.3424e-07 | 286
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | SPLICE, OH | 1 | 1 | 87 | 1.5493e-05 | 1.7808e-07 | 87
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | INSULATOR | 1 | 11 | 627 | 0.00011433 | 2.0058e-06 | 57
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 196 | 49284 | 7968459 | 1.4427 | 0.0089227 | 161.6845
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 301 | 5.4495e-05 | 3.6209e-07 | 150.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | NONE | 587 | 10974 | 834989 | 0.15117 | 0.0019868 | 76.0879
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CROSSARM | 261 | 27466 | 3829509 | 0.69332 | 0.0049726 | 139.4273
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | POLE HARDWARE | 12 | 308 | 48674 | 0.0088123 | 5.5762e-05 | 158.0325
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CUTOUT | 7 | 23 | 2428 | 0.00043958 | 4.1641e-06 | 105.5652
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 167 | 7651 | 1248683 | 0.22607 | 0.0013852 | 163.2052
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CUTOUT | 34 | 189 | 32018 | 0.0057967 | 3.4218e-05 | 169.4074
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 85 | 551 | 99127 | 0.017947 | 9.9757e-05 | 179.9038
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | RECLOSER, LINE/OCR/BR | 1 | 1 | 126 | 2.2812e-05 | 1.8105e-07 | 126
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | TRANSFORMER, OH | 4 | 39 | 10491 | 0.0018994 | 7.0608e-06 | 269
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WH | TRANSFORMER, OH | 1 | 3 | 450 | 8.1471e-05 | 5.4314e-07 | 150
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 6 | 178 | 53472 | 0.0096809 | 3.2226e-05 | 300.4045
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | ARRESTER | 1 | 3 | 276 | 4.9501e-05 | 5.3805e-07 | 92
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 9 | 29 | 3280 | 0.00059064 | 5.2221e-06 | 113.1034
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | SWITCH, UG | 1 | 13 | 1690 | 0.0003031 | 2.3316e-06 | 130
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CONN/CLAMP | 1 | 13 | 286 | 5.1779e-05 | 2.3536e-06 | 22
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | ARRESTER | 3 | 333 | 7659 | 0.0013966 | 6.072e-05 | 23
AEP Total | 2020 | 5484199 | PARTIAL POWER | VIN | CONN/CLAMP | 1 | 20 | 6300 | 0.0011488 | 3.6468e-06 | 315
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | ARRESTER | 2 | 2 | 223 | 4.0662e-05 | 3.6468e-07 | 111.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | CONDUCTOR UG | 2 | 3 | 7163 | 0.0013061 | 5.4703e-07 | 2387.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | JUMPER/RISER | 2 | 1433 | 217029 | 0.039574 | 0.0002613 | 151.4508
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | CROSSARM | 5 | 94 | 29368 | 0.005317 | 1.7018e-05 | 312.4255
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ERF | NONE | 3 | 5736 | 235863 | 0.043008 | 0.0010459 | 41.1198
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, GROUNDING | 1 | 1 | 29 | 5.2503e-06 | 1.8105e-07 | 29
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | TRANSFORMER, OH | 1 | 1 | 204 | 3.6933e-05 | 1.8105e-07 | 204
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | CONN/CLAMP | 2 | 5 | 504 | 9.1247e-05 | 9.0523e-07 | 100.8
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CONN/CLAMP | 1 | 200 | 35800 | 0.0065278 | 3.6468e-05 | 179
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CROSSARM | 2 | 15 | 2961 | 0.00053319 | 2.7011e-06 | 197.4
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | POLE HARDWARE | 1 | 9 | 243 | 4.3757e-05 | 1.6206e-06 | 27
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 577 | 5969 | 676205 | 0.12042 | 0.001063 | 113.2861
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | U | NONE | 184 | 36746 | 1534555 | 0.27327 | 0.0065437 | 41.7611
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | SPLICE, OH | 6 | 23 | 3330 | 0.00059301 | 4.0958e-06 | 144.7826
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | CUTOUT | 15 | 1728 | 34759 | 0.0061899 | 0.00030772 | 20.1152
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CROSSARM | 10 | 152 | 23366 | 0.004161 | 2.7068e-05 | 153.7237
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | INSULATOR | 18 | 532 | 86285 | 0.015366 | 9.4738e-05 | 162.1898
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 1 | 131 | 2.3717e-05 | 1.8105e-07 | 131
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 1 | 1 | 26 | 4.6819e-06 | 1.8007e-07 | 26
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RELAY | 1 | 1 | 212 | 3.8175e-05 | 1.8007e-07 | 212
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CAPACITOR | 1 | 1503 | 48096 | 0.0086607 | 0.00027065 | 32
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | CONDUCTOR UG | 5 | 5 | 700 | 0.00012466 | 8.904e-07 | 140
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | NONE | 13 | 23 | 2061 | 0.00036702 | 4.0958e-06 | 89.6087
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | NONE | 11 | 80 | 5848 | 0.0010414 | 1.4246e-05 | 73.1
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | NONE | 13 | 389 | 27454 | 0.004889 | 6.9273e-05 | 70.5758
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | WL | CIRCUIT SWITCHER | 5 | 760 | 72566 | 0.012923 | 0.00013534 | 95.4816
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CROSSARM | 16 | 174 | 15081 | 0.0026856 | 3.0986e-05 | 86.6724
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 1 | 48 | 8.6902e-06 | 1.8105e-07 | 48
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 2 | 3 | 564 | 0.00010044 | 5.3424e-07 | 188
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CROSSARM | 4 | 1857 | 537738 | 0.09576 | 0.00033069 | 289.5735
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 61 | 13969 | 0.0025154 | 1.0984e-05 | 229
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | CF | ARRESTER | 2 | 816 | 51408 | 0.00922 | 0.00014635 | 63
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | OTHER EQUIPMENT | 1 | 1 | 100 | 1.8007e-05 | 1.8007e-07 | 100
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | FUSE | 2 | 13 | 2015 | 0.00036284 | 2.3409e-06 | 155
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | SPLICE, OH | 1 | 5 | 180 | 3.2054e-05 | 8.904e-07 | 36
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | CUTOUT | 1 | 13 | 260 | 4.6301e-05 | 2.315e-06 | 20
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | ARRESTER | 2 | 2 | 53 | 9.4382e-06 | 3.5616e-07 | 26.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | METERING | 2 | 2 | 290 | 5.1643e-05 | 3.5616e-07 | 145
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | JUMPER/RISER | 7 | 76 | 8778 | 0.0015632 | 1.3534e-05 | 115.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 9 | 586 | 30150 | 0.0053691 | 0.00010435 | 51.4505
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | INSULATOR | 2 | 46 | 12896 | 0.0023129 | 8.2501e-06 | 280.3478
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | ARRESTER | 24 | 656 | 43157 | 0.0076854 | 0.00011682 | 65.7881
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 2 | 2 | 183 | 3.2821e-05 | 3.587e-07 | 91.5
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | BREAKER | 4 | 1659 | 174921 | 0.031372 | 0.00029754 | 105.4376
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | CONDUCTOR UG | 1 | 11 | 132 | 2.3674e-05 | 1.9729e-06 | 12
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | NONE | 141 | 391 | 44775 | 0.0079735 | 6.9629e-05 | 114.5141
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | ARRESTER | 378 | 6633 | 679278 | 0.12097 | 0.0011812 | 102.4089
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONN/CLAMP | 16 | 57 | 12710 | 0.0022634 | 1.0151e-05 | 222.9825
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | NONE | 104 | 288 | 23983 | 0.0042709 | 5.1287e-05 | 83.2743
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | POLE | 372 | 20919 | 3630566 | 0.64653 | 0.0037253 | 173.5535
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 2 | 1082 | 88292 | 0.015723 | 0.00019268 | 81.6007
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | CIRCUIT SWITCHER | 3 | 311 | 23526 | 0.0042194 | 5.5778e-05 | 75.6463
AEP Total | 2024 | 5615460 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 7 | 17 | 1387 | 0.000247 | 3.0274e-06 | 81.5882
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 18 | 10810 | 1403522 | 0.24994 | 0.001925 | 129.8355
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | INSULATOR | 4 | 26 | 2298 | 0.00040923 | 4.6301e-06 | 88.3846
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 6 | 551 | 70560 | 0.012655 | 9.8822e-05 | 128.0581
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, UG | 10 | 23 | 5651 | 0.0010063 | 4.0958e-06 | 245.6957
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CONN/CLAMP | 14 | 1529 | 246709 | 0.043934 | 0.00027228 | 161.3532
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CAPACITOR | 5 | 2351 | 277841 | 0.049478 | 0.00041867 | 118.1799
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | OTHER EQUIPMENT | 1 | 4 | 148 | 2.6651e-05 | 7.2029e-07 | 37
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | SPLICE, OH | 1 | 1 | 104 | 1.8829e-05 | 1.8105e-07 | 104
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 247 | 68304 | 0.0123 | 4.4478e-05 | 276.5344
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ERF | BREAKER | 2 | 2 | 116 | 2.0805e-05 | 3.587e-07 | 58
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | METERING | 1 | 1 | 26 | 4.6631e-06 | 1.7935e-07 | 26
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | POLE | 5 | 14 | 3855 | 0.0006865 | 2.4931e-06 | 275.3571
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | JUMPER/RISER | 1 | 15 | 2175 | 0.00039009 | 2.6903e-06 | 145
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WH | CUTOUT | 1 | 31 | 57381 | 0.010463 | 5.6526e-06 | 1851
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | NONE | 2 | 2 | 139 | 2.5346e-05 | 3.6468e-07 | 69.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 416 | 45299 | 4696859 | 0.83642 | 0.0080668 | 103.6857
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 16 | 201 | 22954 | 0.0040876 | 3.5794e-05 | 114.199
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | INSULATOR | 4 | 194 | 60468 | 0.010889 | 3.4934e-05 | 311.6907
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | ARRESTER | 18 | 654 | 70973 | 0.012639 | 0.00011646 | 108.5214
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | O | NONE | 3 | 4 | 545 | 9.7053e-05 | 7.1232e-07 | 136.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 13 | 1296 | 0.00023079 | 2.315e-06 | 99.6923
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | CONN/CLAMP | 14 | 41 | 4483 | 0.00079833 | 7.3013e-06 | 109.3415
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 18 | 66 | 10755 | 0.0019152 | 1.1753e-05 | 162.9545
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 7 | 794 | 97213 | 0.017312 | 0.0001414 | 122.4345
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | ARRESTER | 8 | 95 | 14853 | 0.002645 | 1.6918e-05 | 156.3474
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 995 | 154225 | 0.027464 | 0.00017719 | 155
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | TRANSFORMER, OH | 1 | 2 | 230 | 4.0958e-05 | 3.5616e-07 | 115
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | POLE HARDWARE | 20 | 820 | 87978 | 0.015667 | 0.00014603 | 107.2902
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | CF | SWITCH, OH | 1 | 785 | 7065 | 0.0012581 | 0.00013979 | 9
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | RECLOSER, LINE/OCR/BR | 1 | 26 | 1586 | 0.00028243 | 4.6301e-06 | 61
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | TRANSFORMER, GROUNDING | 1 | 1 | 117 | 2.0835e-05 | 1.7808e-07 | 117
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SWITCH, UG | 1 | 1 | 193 | 3.4369e-05 | 1.7808e-07 | 193
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | CABLE TERMINATOR | 1 | 1127 | 61985 | 0.011038 | 0.0002007 | 55
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UB | TRANSFORMER, OH | 1 | 3 | 804 | 0.00014318 | 5.3424e-07 | 268
AEP Total | 2024 | 5615460 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 1 | 1 | 47 | 8.3698e-06 | 1.7808e-07 | 47
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | POLE | 1 | 7 | 1561 | 0.00028464 | 1.2764e-06 | 223
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | JUMPER/RISER | 1 | 1 | 54 | 9.7765e-06 | 1.8105e-07 | 54
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | JUMPER/RISER | 1 | 26 | 4004 | 0.00071812 | 4.6631e-06 | 154
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | POLE | 1 | 1 | 108 | 1.9448e-05 | 1.8007e-07 | 108
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | BREAKER | 1 | 592 | 44992 | 0.0080122 | 0.00010542 | 76
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | CONN/CLAMP | 1 | 2 | 218 | 3.9256e-05 | 3.6014e-07 | 109
AEP Total | 2025 | 5615460 | PARTIAL POWER | CF | CUTOUT | 1 | 1 | 104 | 1.852e-05 | 1.7808e-07 | 104
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 20 | 3.5616e-06 | 1.7808e-07 | 20
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | CROSSARM | 1 | 3 | 1365 | 0.00024308 | 5.3424e-07 | 455
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 2 | 2421 | 67788 | 0.012072 | 0.00043113 | 28
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 2 | 2 | 281 | 5.004e-05 | 3.5616e-07 | 140.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | SPLICE, OH | 2 | 485 | 77689 | 0.013835 | 8.6369e-05 | 160.1835
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | AB | INSULATOR | 5 | 3054 | 321937 | 0.05733 | 0.00054386 | 105.4149
AEP Total | 2025 | 5615460 | PARTIAL POWER | CF | TRANSFORMER, OH | 1 | 83 | 25066 | 0.0044637 | 1.4781e-05 | 302
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | ARRESTER | 11 | 294 | 40905 | 0.0073658 | 5.2941e-05 | 139.1327
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | INSULATOR | 1 | 1 | 368 | 6.6001e-05 | 1.7935e-07 | 368
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONDUCTOR UG | 60 | 125 | 31546 | 0.0056578 | 2.2419e-05 | 252.368
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CAPACITOR | 3 | 1141 | 40867 | 0.007359 | 0.00020546 | 35.8168
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | JUMPER/RISER | 4 | 302 | 31863 | 0.0057146 | 5.4164e-05 | 105.5066
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | SWITCH, OH | 2 | 869 | 44769 | 0.0080293 | 0.00015586 | 51.5178
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AO | NONE | 9 | 7933 | 737694 | 0.13231 | 0.0014228 | 92.9905
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | ARRESTER | 1 | 1 | 84 | 1.5208e-05 | 1.8105e-07 | 84
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 1 | 468 | 79560 | 0.014404 | 8.473e-05 | 170
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 225 | 686 | 115606 | 0.02108 | 0.00012509 | 168.5219
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SWITCH, OH | 18 | 13308 | 1262459 | 0.2302 | 0.0024266 | 94.8647
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CONDUCTOR OVERHEAD | 1093 | 111878 | 13037334 | 2.3773 | 0.0204 | 116.5317
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 12 | 20 | 3244 | 0.00059152 | 3.6468e-06 | 162.2
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONN/CLAMP | 118 | 563 | 69700 | 0.012709 | 0.00010266 | 123.8011
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 115 | 115 | 18418 | 0.0033584 | 2.0969e-05 | 160.1565
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | STATIC WIRE | 1 | 18 | 3888 | 0.00070895 | 3.2822e-06 | 216
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | PEDESTAL | 4 | 29 | 6176 | 0.0011261 | 5.2879e-06 | 212.9655
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | TRANSFORMER, OH | 5 | 33 | 4649 | 0.00084771 | 6.0173e-06 | 140.8788
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - NON LTC | 13 | 12248 | 2391642 | 0.4361 | 0.0022333 | 195.268
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | NONE | 21 | 88 | 5777 | 0.0010534 | 1.6046e-05 | 65.6477
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 12 | 639 | 30370 | 0.0055377 | 0.00011652 | 47.5274
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE | 17 | 678 | 118011 | 0.021518 | 0.00012363 | 174.0575
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CABLE TERMINATOR | 4 | 63 | 4682 | 0.00085373 | 1.1488e-05 | 74.3175
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 126 | 2.2975e-05 | 1.8234e-07 | 126
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 13 | 35 | 5470 | 0.00099741 | 6.382e-06 | 156.2857
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | CF | SWITCH, OH | 2 | 2114 | 132167 | 0.0241 | 0.00038547 | 62.5199
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SPLICE, UG | 3 | 10 | 1543 | 0.00028135 | 1.8234e-06 | 154.3
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 10 | 14667 | 2346902 | 0.42794 | 0.0026744 | 160.0124
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | SPLICE, UG | 1 | 1 | 70 | 1.2555e-05 | 1.7935e-07 | 70
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 1175 | 79084 | 0.014241 | 0.00021158 | 67.3055
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | SPLICE, OH | 5 | 13 | 4128 | 0.00074036 | 2.3316e-06 | 317.5385
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | JUMPER/RISER | 22 | 4587 | 739238 | 0.13258 | 0.00082268 | 161.1594
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 3 | 4 | 1073 | 0.00019322 | 7.2029e-07 | 268.25
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | POLE | 53 | 1869 | 489853 | 0.087855 | 0.00033521 | 262.0936
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 6 | 22 | 5093 | 0.00091711 | 3.9616e-06 | 231.5
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | R | RELAY | 7 | 5628 | 308611 | 0.055349 | 0.0010094 | 54.8349
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 90 | 24445 | 2415829 | 0.44051 | 0.0044574 | 98.8271
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, UG | 12 | 101 | 18172 | 0.0033135 | 1.8417e-05 | 179.9208
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | NONE | 43 | 6334 | 773838 | 0.1411 | 0.001155 | 122.1721
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | NONE | 224 | 618 | 66303 | 0.01209 | 0.00011269 | 107.2864
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CONN/CLAMP | 96 | 192 | 22122 | 0.0040338 | 3.501e-05 | 115.2188
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | OL | NONE | 1 | 240 | 8400 | 0.0015317 | 4.3762e-05 | 35
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 14 | 48 | 7851 | 0.0014316 | 8.7524e-06 | 163.5625
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CUTOUT | 4 | 12 | 750 | 0.00013676 | 2.1881e-06 | 62.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CAPACITOR | 3 | 1608 | 186348 | 0.033979 | 0.00029321 | 115.8881
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | WL | NONE | 24 | 11874 | 1533562 | 0.27963 | 0.0021651 | 129.1529
AEP Total | 2020 | 5484199 | PARTIAL POWER | VA | NONE | 6 | 12 | 1095 | 0.00019966 | 2.1881e-06 | 91.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 6 | 10 | 959 | 0.00017487 | 1.8234e-06 | 95.9
AEP Total | 2020 | 5484199 | PARTIAL POWER | CF | CUTOUT | 8 | 18 | 2439 | 0.00044473 | 3.2822e-06 | 135.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | TRANSFORMER, OH | 1 | 1 | 63 | 1.1488e-05 | 1.8234e-07 | 63
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | METERING | 9 | 9 | 749 | 0.00013657 | 1.6411e-06 | 83.2222
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 229 | 12025 | 0.0021927 | 4.1756e-05 | 52.5109
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | SPLICE, OH | 4 | 4 | 997 | 0.0001818 | 7.2937e-07 | 249.25
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 141 | 2.571e-05 | 1.8234e-07 | 141
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | METERING | 1 | 1 | 93 | 1.6958e-05 | 1.8234e-07 | 93
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | RECLOSER, LINE/OCR/BR | 1 | 287 | 21238 | 0.0038726 | 5.2332e-05 | 74
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | CONDUCTOR OVERHEAD | 2 | 11 | 1903 | 0.0003413 | 1.9729e-06 | 173
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | NONE | 11 | 581 | 53735 | 0.0096374 | 0.0001042 | 92.4871
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | ARRESTER | 10 | 23 | 4927 | 0.00088366 | 4.1251e-06 | 214.2174
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 9 | 712 | 141633 | 0.025402 | 0.0001277 | 198.9228
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 5 | 17 | 4217 | 0.00075936 | 3.0612e-06 | 248.0588
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 3 | 170 | 92778 | 0.016707 | 3.0612e-05 | 545.7529
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | NONE | 159 | 27573 | 2601805 | 0.46333 | 0.0049102 | 94.3606
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CONN/CLAMP | 32 | 123 | 13188 | 0.0023485 | 2.1904e-05 | 107.2195
AEP Total | 2022 | 5553337 | PARTIAL POWER | VIN | NONE | 13 | 21 | 3073 | 0.00055336 | 3.7815e-06 | 146.3333
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CUTOUT | 78 | 1200 | 141907 | 0.025553 | 0.00021609 | 118.2558
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | CROSSARM | 6 | 158 | 32603 | 0.0058709 | 2.8451e-05 | 206.3481
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE | 294 | 58926 | 7230234 | 1.302 | 0.010611 | 122.7002
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 107 | 814 | 132144 | 0.023795 | 0.00014658 | 162.3391
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | NONE | 62 | 816 | 141709 | 0.025656 | 0.00014773 | 173.663
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CROSSARM | 1 | 556 | 89516 | 0.016207 | 0.00010066 | 161
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | SWITCH, OH | 2 | 1332 | 49284 | 0.0089227 | 0.00024115 | 37
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | REGULATOR | 2 | 32 | 9660 | 0.0017203 | 5.6986e-06 | 301.875
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 1 | 213 | 25773 | 0.0045897 | 3.7931e-05 | 121
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 1 | 13 | 3328 | 0.00059265 | 2.315e-06 | 256
AEP Total | 2025 | 5615460 | PARTIAL POWER | VA | NONE | 1 | 6 | 1266 | 0.00022545 | 1.0685e-06 | 211
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | METERING | 1 | 1 | 218 | 3.8821e-05 | 1.7808e-07 | 218
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | SPLICE, OH | 1 | 1 | 1272 | 0.00022652 | 1.7808e-07 | 1272
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | WU | NONE | 3 | 3425 | 478731 | 0.085252 | 0.00060992 | 139.7755
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CUTOUT | 2 | 41 | 4020 | 0.00072781 | 7.4229e-06 | 98.0488
AEP Total | 2025 | 5615460 | PARTIAL POWER | OL | TRANSFORMER, UG | 1 | 3 | 564 | 0.00010044 | 5.3424e-07 | 188
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | JUMPER/RISER | 3 | 59 | 8387 | 0.0014936 | 1.0507e-05 | 142.1525
AEP Total | 2020 | 5484199 | PARTIAL POWER | UB | CONDUCTOR UG | 1 | 1 | 160 | 2.9175e-05 | 1.8234e-07 | 160
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | TRANSFORMER, GROUNDING | 1 | 3 | 1398 | 0.00025491 | 5.4703e-07 | 466
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1982 | 10456 | 2164273 | 0.39183 | 0.001893 | 206.9886
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | NONE | 3340 | 124300 | 13055694 | 2.3637 | 0.022504 | 105.0337
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | NONE | 1271 | 16283 | 1380253 | 0.24989 | 0.002948 | 84.7665
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE | 64 | 7890 | 1479517 | 0.26786 | 0.0014285 | 187.518
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | NONE | 35 | 132 | 8763 | 0.0015865 | 2.3898e-05 | 66.3864
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | TRANSFORMER, UG | 8 | 77 | 16594 | 0.0030043 | 1.3941e-05 | 215.5065
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | ARRESTER | 35 | 292 | 25180 | 0.0045587 | 5.2866e-05 | 86.2329
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | JUMPER/RISER | 22 | 1969 | 339629 | 0.061489 | 0.00035648 | 172.4881
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CONDUCTOR OVERHEAD | 129 | 368 | 63379 | 0.011475 | 6.6625e-05 | 172.2255
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CONDUCTOR OVERHEAD | 14 | 94 | 22415 | 0.0040582 | 1.7018e-05 | 238.4574
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 29 | 146 | 30441 | 0.0055112 | 2.6433e-05 | 208.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 4 | 15 | 1826 | 0.00033059 | 2.7157e-06 | 121.7333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 3 | 20 | 2584 | 0.00046782 | 3.6209e-06 | 129.2
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ABI | NONE | 14 | 8163 | 891905 | 0.16148 | 0.0014779 | 109.2619
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | FUSE | 1 | 1 | 182 | 3.295e-05 | 1.8105e-07 | 182
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 2 | 12 | 254 | 4.5986e-05 | 2.1726e-06 | 21.1667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 14 | 963 | 144067 | 0.026083 | 0.00017435 | 149.6023
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SPLICE, OH | 4 | 71 | 6438 | 0.0011656 | 1.2854e-05 | 90.6761
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | ARRESTER | 10 | 261 | 33256 | 0.0060209 | 4.7253e-05 | 127.4176
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR OVERHEAD | 11 | 51 | 8425 | 0.0015253 | 9.2334e-06 | 165.1961
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 392 | 70959 | 0.012847 | 7.097e-05 | 181.0179
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | TRANSFORMER, GROUNDING | 2 | 2 | 279 | 5.0512e-05 | 3.6209e-07 | 139.5
AEP Total | 2020 | 5484199 | PARTIAL POWER | WW | CONDUCTOR OVERHEAD | 2 | 2 | 354 | 6.4549e-05 | 3.6468e-07 | 177
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 176 | 176 | 24433 | 0.0044552 | 3.2092e-05 | 138.8239
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 2041 | 13834 | 1698807 | 0.30591 | 0.0024911 | 122.7994
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 112 | 11813 | 1449225 | 0.26096 | 0.0021272 | 122.6805
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | NONE | 148 | 2529 | 174758 | 0.031469 | 0.0004554 | 69.1016
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONDUCTOR UG | 49 | 119 | 28491 | 0.0051304 | 2.1429e-05 | 239.4202
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, OH | 53 | 194 | 45745 | 0.0082374 | 3.4934e-05 | 235.799
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CUTOUT | 32 | 511 | 82557 | 0.014866 | 9.2017e-05 | 161.5597
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | CONN/CLAMP | 39 | 553 | 45481 | 0.0081899 | 9.958e-05 | 82.2441
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1472 | 9500 | 2181433 | 0.39124 | 0.0017038 | 229.6245
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | JUMPER/RISER | 89 | 2192 | 252152 | 0.045224 | 0.00039314 | 115.0328
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 65 | 321 | 64565 | 0.011626 | 5.7803e-05 | 201.1371
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 7 | 40 | 7666 | 0.0013804 | 7.2029e-06 | 191.65
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CONN/CLAMP | 1200 | 3235 | 351024 | 0.062956 | 0.0005802 | 108.5082
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | CONN/CLAMP | 1312 | 2835 | 310128 | 0.055622 | 0.00050846 | 109.3926
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 75 | 355 | 75375 | 0.013519 | 6.3669e-05 | 212.3239
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WU | NONE | 4 | 831 | 70179 | 0.012637 | 0.00014964 | 84.4513
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | METERING | 146 | 163 | 18979 | 0.0034039 | 2.9234e-05 | 116.4356
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | ARRESTER | 7 | 12 | 1098 | 0.00019772 | 2.1609e-06 | 91.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CROSSARM | 230 | 29109 | 3094066 | 0.55492 | 0.0052207 | 106.2924
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CUTOUT | 17 | 983 | 72355 | 0.012977 | 0.0001763 | 73.6063
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | JUMPER/RISER | 15 | 133 | 22811 | 0.0041076 | 2.395e-05 | 171.5113
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | CONN/CLAMP | 2 | 2 | 389 | 7.0931e-05 | 3.6468e-07 | 194.5
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | JUMPER/RISER | 2 | 1944 | 337427 | 0.060761 | 0.00035006 | 173.5736
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 173 | 3618 | 478224 | 0.085162 | 0.00064429 | 132.1791
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | SWITCH, OH | 1 | 68 | 3332 | 0.00060325 | 1.2311e-05 | 49
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | BREAKER | 1 | 2468 | 207312 | 0.037331 | 0.00044442 | 84
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | JUMPER/RISER | 4 | 13 | 841 | 0.00015144 | 2.3409e-06 | 64.6923
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | INSULATOR | 1 | 2360 | 292706 | 0.052708 | 0.00042497 | 124.028
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SPLICE, UG | 1 | 1 | 114 | 2.0639e-05 | 1.8105e-07 | 114
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 1 | 37 | 3700 | 0.00066627 | 6.6627e-06 | 100
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 2 | 517 | 12275 | 0.0022104 | 9.3097e-05 | 23.7427
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | R | NONE | 3 | 1653 | 64070 | 0.01141 | 0.00029437 | 38.7598
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | NONE | 18 | 110 | 7872 | 0.0014018 | 1.9589e-05 | 71.5636
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 7 | 57 | 30432 | 0.0054193 | 1.0151e-05 | 533.8947
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | POLE HARDWARE | 2 | 7 | 980 | 0.00017452 | 1.2466e-06 | 140
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | JUMPER/RISER | 40 | 1096 | 135197 | 0.024076 | 0.00019518 | 123.3549
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | JUMPER/RISER | 9 | 616 | 45629 | 0.0081256 | 0.0001097 | 74.0731
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | INSULATOR | 7 | 1377 | 329930 | 0.058754 | 0.00024522 | 239.6006
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 212 | 45594 | 0.0081194 | 3.7753e-05 | 215.066
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | SWITCH, OH | 4 | 1166 | 23443 | 0.0041747 | 0.00020764 | 20.1055
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CUTOUT | 2 | 23 | 898 | 0.00015992 | 4.0958e-06 | 39.0435
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | SPLICE, OH | 1 | 1 | 113 | 2.0123e-05 | 1.7808e-07 | 113
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | NONE | 3 | 4 | 329 | 5.8588e-05 | 7.1232e-07 | 82.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | PEDESTAL | 1 | 1 | 1561 | 0.00027798 | 1.7808e-07 | 1561
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | RECLOSER, LINE/OCR/BR | 1 | 491 | 64321 | 0.011454 | 8.7437e-05 | 131
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | FUSE | 2 | 38 | 3116 | 0.0005611 | 6.8427e-06 | 82
AEP Total | 2022 | 5553337 | PARTIAL POWER | WL | CUTOUT | 1 | 1 | 132 | 2.3769e-05 | 1.8007e-07 | 132
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | INSULATOR | 1 | 1 | 125 | 2.2793e-05 | 1.8234e-07 | 125
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | ARRESTER | 1 | 552 | 46920 | 0.0084151 | 9.9001e-05 | 85
AEP Total | 2022 | 5553337 | PARTIAL POWER | WW | OTHER EQUIPMENT | 1 | 1 | 115 | 2.0708e-05 | 1.8007e-07 | 115
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | CAPACITOR | 1 | 1 | 34 | 6.1224e-06 | 1.8007e-07 | 34
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 1 | 1 | 241 | 4.2917e-05 | 1.7808e-07 | 241
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 2 | 165 | 2.9383e-05 | 3.5616e-07 | 82.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | TRANSFORMER, STATION SERVICE | 1 | 3 | 57 | 1.0151e-05 | 5.3424e-07 | 19
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 54 | 9666 | 0.0017213 | 9.6163e-06 | 179
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | CROSSARM | 2 | 1711 | 131034 | 0.023335 | 0.00030469 | 76.5833
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | NONE | 2 | 2 | 510 | 9.0821e-05 | 3.5616e-07 | 255
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | POLE | 2 | 2 | 647 | 0.00011522 | 3.5616e-07 | 323.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | WU | ARRESTER | 1 | 1 | 261 | 4.6479e-05 | 1.7808e-07 | 261
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TR | JUMPER/RISER | 1 | 11 | 385 | 6.8561e-05 | 1.9589e-06 | 35
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WFS | CONDUCTOR UG | 1 | 1 | 254 | 4.6315e-05 | 1.8234e-07 | 254
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CABLE TERMINATOR | 1 | 10 | 980 | 0.0001787 | 1.8234e-06 | 98
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | BREAKER | 1 | 16 | 1904 | 0.00034148 | 2.8696e-06 | 119
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 136 | 10744 | 0.0019591 | 2.4799e-05 | 79
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | SWITCH, UG | 1 | 352 | 3520 | 0.00062684 | 6.2684e-05 | 10
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CUTOUT | 1 | 5 | 215 | 3.8287e-05 | 8.904e-07 | 43
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONN/CLAMP | 1 | 5 | 1020 | 0.00018164 | 8.904e-07 | 204
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | BREAKER | 1 | 1 | 53 | 9.4382e-06 | 1.7808e-07 | 53
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | METERING | 1911 | 2088 | 194278 | 0.035173 | 0.00037802 | 93.045
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONDUCTOR UG | 477 | 11082 | 2103925 | 0.38091 | 0.0020064 | 189.8507
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | ARRESTER | 12 | 208 | 15533 | 0.0028122 | 3.7658e-05 | 74.6779
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | CONN/CLAMP | 41 | 158 | 16084 | 0.0029119 | 2.8605e-05 | 101.7975
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 23 | 65 | 17993 | 0.0032576 | 1.1768e-05 | 276.8154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 24 | 66 | 12408 | 0.0022464 | 1.1949e-05 | 188
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CONN/CLAMP | 5 | 11 | 1271 | 0.00023011 | 1.9915e-06 | 115.5455
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | METERING | 1 | 1 | 112 | 2.0277e-05 | 1.8105e-07 | 112
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | SPLICE, OH | 9 | 13 | 2847 | 0.00051544 | 2.3536e-06 | 219
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 18 | 343 | 52347 | 0.0094772 | 6.2099e-05 | 152.6152
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | RECLOSER, LINE/OCR/BR | 1 | 1638 | 276208 | 0.050006 | 0.00029655 | 168.6252
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 16 | 76 | 9608 | 0.0017395 | 1.376e-05 | 126.4211
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | POLE HARDWARE | 6 | 944 | 162942 | 0.0295 | 0.00017091 | 172.6081
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | INSULATOR | 2 | 63 | 11833 | 0.0021423 | 1.1406e-05 | 187.8254
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | METERING | 4 | 4 | 224 | 4.0554e-05 | 7.2419e-07 | 56
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | CONDUCTOR OVERHEAD | 5 | 5 | 456 | 8.2557e-05 | 9.0523e-07 | 91.2
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | SPLICE, OH | 1 | 1 | 97 | 1.7561e-05 | 1.8105e-07 | 97
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | NONE | 40 | 40 | 4427 | 0.00078836 | 7.1232e-06 | 110.675
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | POLE | 48 | 10983 | 2607702 | 0.46438 | 0.0019559 | 237.4308
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 7 | 1295 | 0.00023613 | 1.2764e-06 | 185
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | POLE | 3 | 3 | 855 | 0.0001559 | 5.4703e-07 | 285
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERO | METERING | 1 | 1 | 150 | 2.7351e-05 | 1.8234e-07 | 150
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | POLE | 5 | 3910 | 179351 | 0.032703 | 0.00071296 | 45.8698
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | SWITCH, OH | 1 | 3038 | 244838 | 0.043912 | 0.00054487 | 80.5918
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, POWER - LTC | 1 | 11 | 3289 | 0.00058988 | 1.9729e-06 | 299
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | GUY/ANCHOR | 1 | 9 | 1080 | 0.0001937 | 1.6142e-06 | 120
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CONN/CLAMP | 711 | 2467 | 333529 | 0.059395 | 0.00043932 | 135.1962
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | NONE | 533 | 8723 | 908656 | 0.16181 | 0.0015534 | 104.1678
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | CUTOUT | 52 | 859 | 74391 | 0.013248 | 0.00015297 | 86.6019
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | CONDUCTOR UG | 17 | 43 | 7448 | 0.0013263 | 7.6574e-06 | 173.2093
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WFS | METERING | 2 | 2 | 77 | 1.3712e-05 | 3.5616e-07 | 38.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | GUY/ANCHOR | 1 | 1 | 45 | 8.1471e-06 | 1.8105e-07 | 45
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | SPLICE, UG | 1 | 74 | 1282 | 0.0002283 | 1.3178e-05 | 17.3243
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | ARRESTER | 4 | 21 | 3788 | 0.00067457 | 3.7397e-06 | 180.381
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 1 | 17 | 4301 | 0.00076592 | 3.0274e-06 | 253
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 1 | 1 | 30 | 5.3424e-06 | 1.7808e-07 | 30
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 33 | 2410 | 130393 | 0.02322 | 0.00042917 | 54.105
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 4 | 71 | 10240 | 0.0018235 | 1.2644e-05 | 144.2254
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VIN | CONN/CLAMP | 6 | 27 | 4769 | 0.00084926 | 4.8082e-06 | 176.6296
AEP Total | 2025 | 5615460 | PARTIAL POWER | WI | NONE | 2 | 2 | 55 | 9.7944e-06 | 3.5616e-07 | 27.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | POLE HARDWARE | 1 | 67 | 16750 | 0.0029828 | 1.1931e-05 | 250
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 1 | 72 | 1.2822e-05 | 1.7808e-07 | 72
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | FUSE | 4 | 54 | 3874 | 0.00068988 | 9.6163e-06 | 71.7407
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | METERING | 6 | 6 | 609 | 0.00010845 | 1.0685e-06 | 101.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 17 | 8966 | 0.0015967 | 3.0274e-06 | 527.4118
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CONN/CLAMP | 4 | 9 | 480 | 8.7524e-05 | 1.6411e-06 | 53.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 2 | 93 | 17467 | 0.003185 | 1.6958e-05 | 187.8172
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | OTHER EQUIPMENT | 4 | 2221 | 272835 | 0.049749 | 0.00040498 | 122.8433
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | CF | NONE | 2 | 83 | 14204 | 0.00259 | 1.5134e-05 | 171.1325
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABI | NONE | 8 | 9038 | 863880 | 0.15556 | 0.0016275 | 95.5831
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 1 | 10 | 3890 | 0.00070931 | 1.8234e-06 | 389
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | SWITCH, UG | 1 | 13 | 2483 | 0.00044217 | 2.315e-06 | 191
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 3 | 1361 | 211554 | 0.037673 | 0.00024237 | 155.4401
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AB | BREAKER | 2 | 1230 | 225976 | 0.040242 | 0.00021904 | 183.7203
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 2 | 756 | 122346 | 0.021787 | 0.00013463 | 161.8333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR UG | 1 | 1 | 150 | 2.6712e-05 | 1.7808e-07 | 150
AEP Total | 2025 | 5615460 | PARTIAL POWER | EQF | ARRESTER | 6 | 8 | 430 | 7.6574e-05 | 1.4246e-06 | 53.75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 7 | 49 | 18923 | 0.0033698 | 8.7259e-06 | 386.1837
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | ARRESTER | 1 | 1 | 30 | 5.3424e-06 | 1.7808e-07 | 30
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ERF | NONE | 2 | 347 | 12201 | 0.0021728 | 6.1794e-05 | 35.1614
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VA | CROSSARM | 1 | 582 | 96319 | 0.017152 | 0.00010364 | 165.4966
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE HARDWARE | 1 | 34 | 6086 | 0.0010838 | 6.0547e-06 | 179
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 2 | 10 | 1760 | 0.00031566 | 1.7935e-06 | 176
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | BREAKER | 2 | 3112 | 459644 | 0.082437 | 0.00055814 | 147.7005
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | ARRESTER | 2 | 26 | 2513 | 0.00045071 | 4.6631e-06 | 96.6538
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | METERING | 3 | 3 | 8547 | 0.001522 | 5.3424e-07 | 2849
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | ARRESTER | 10 | 152 | 23718 | 0.0042237 | 2.7068e-05 | 156.0395
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | REGULATOR | 9 | 9456 | 1483715 | 0.26422 | 0.0016839 | 156.9073
AEP Total | 2023 | 5575683 | PARTIAL POWER | WL | TRANSFORMER, OH | 3 | 10 | 1283 | 0.00023011 | 1.7935e-06 | 128.3
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 42 | 5669 | 919704 | 0.16378 | 0.0010095 | 162.2339
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | FO | NONE | 3 | 6777 | 644132 | 0.11662 | 0.001227 | 95.0468
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | POLE HARDWARE | 2 | 23 | 4944 | 0.00089028 | 4.1417e-06 | 214.9565
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | PEDESTAL | 3 | 20 | 3172 | 0.00057119 | 3.6014e-06 | 158.6
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | NONE | 304 | 15289 | 1249597 | 0.22253 | 0.0027227 | 81.7318
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | ARRESTER | 12 | 166 | 44168 | 0.0078654 | 2.9561e-05 | 266.0723
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TIR | POLE | 5 | 316 | 31103 | 0.0055388 | 5.6273e-05 | 98.4272
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | JUMPER/RISER | 1 | 1 | 188 | 3.4037e-05 | 1.8105e-07 | 188
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | UB | NONE | 4 | 22 | 791 | 0.00014423 | 4.0115e-06 | 35.9545
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 2 | 72 | 2340 | 0.00042668 | 1.3129e-05 | 32.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 363 | 6.572e-05 | 1.8105e-07 | 363
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | PEDESTAL | 1 | 22 | 14366 | 0.0026009 | 3.983e-06 | 653
AEP Total | 2023 | 5575683 | PARTIAL POWER | A | CONDUCTOR OVERHEAD | 2 | 3 | 149 | 2.6723e-05 | 5.3805e-07 | 49.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | CF | NONE | 6 | 10439 | 1242350 | 0.22282 | 0.0018722 | 119.0104
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 4 | 101 | 29096 | 0.0052394 | 1.8187e-05 | 288.0792
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WT | CONDUCTOR OVERHEAD | 3 | 3 | 246 | 4.412e-05 | 5.3805e-07 | 82
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 4 | 27 | 1004 | 0.00018007 | 4.8425e-06 | 37.1852
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR OVERHEAD | 291 | 2563 | 360628 | 0.064221 | 0.00045642 | 140.7054
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | NONE | 1304 | 54908 | 4918163 | 0.87583 | 0.009778 | 89.571
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 32 | 73 | 13373 | 0.0023815 | 1.3e-05 | 183.1918
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 135 | 18090 | 3200064 | 0.56987 | 0.0032215 | 176.8968
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | POLE | 103 | 28530 | 2831486 | 0.50423 | 0.0050806 | 99.2459
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | JUMPER/RISER | 50 | 384 | 41453 | 0.0073819 | 6.8383e-05 | 107.9505
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | NONE | 75 | 143 | 16186 | 0.0028824 | 2.5465e-05 | 113.1888
AEP Total | 2023 | 5575683 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 54 | 9.6849e-06 | 1.7935e-07 | 54
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CUTOUT | 7 | 74 | 9024 | 0.0016185 | 1.3272e-05 | 121.9459
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CROSSARM | 29 | 6760 | 791262 | 0.14091 | 0.0012038 | 117.0506
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | ARRESTER | 7 | 8 | 2502 | 0.00044556 | 1.4246e-06 | 312.75
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | JUMPER/RISER | 4 | 34 | 3923 | 0.00070359 | 6.0979e-06 | 115.3824
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | CONN/CLAMP | 2 | 3 | 820 | 0.00014603 | 5.3424e-07 | 273.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WI | CONDUCTOR OVERHEAD | 1 | 6 | 1914 | 0.00034084 | 1.0685e-06 | 319
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | CONDUCTOR OVERHEAD | 2 | 375 | 29292 | 0.0052535 | 6.7256e-05 | 78.112
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | SPLICE, OH | 2 | 47 | 5455 | 0.00098761 | 8.5092e-06 | 116.0638
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | INSULATOR | 13 | 331 | 48603 | 0.008752 | 5.9604e-05 | 146.8369
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | METERING | 1 | 1 | 111 | 1.9988e-05 | 1.8007e-07 | 111
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | METERING | 4 | 4 | 325 | 5.8523e-05 | 7.2029e-07 | 81.25
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | SWITCH, OH | 22 | 9638 | 543738 | 0.097912 | 0.0017355 | 56.4161
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | NONE | 54 | 114 | 11681 | 0.002095 | 2.0446e-05 | 102.4649
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | NONE | 23 | 4523 | 90964 | 0.01638 | 0.00081447 | 20.1114
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 19 | 706 | 175916 | 0.031551 | 0.00012662 | 249.1728
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | CONN/CLAMP | 49 | 136 | 16393 | 0.0029519 | 2.449e-05 | 120.5368
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | NONE | 315 | 2216 | 198786 | 0.035652 | 0.00039744 | 89.7049
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | NONE | 125 | 1185 | 115907 | 0.020788 | 0.00021253 | 97.8118
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CUTOUT | 29 | 2348 | 127550 | 0.022876 | 0.00042111 | 54.3228
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SWITCH, OH | 1 | 1 | 141 | 2.539e-05 | 1.8007e-07 | 141
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CROSSARM | 38 | 9461 | 1005665 | 0.18037 | 0.0016968 | 106.2958
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | WL | NONE | 12 | 3676 | 925515 | 0.16599 | 0.00065929 | 251.7723
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | CONDUCTOR UG | 6 | 10 | 1932 | 0.0003465 | 1.7935e-06 | 193.2
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | TRANSFORMER, OH | 1 | 1 | 62 | 1.1164e-05 | 1.8007e-07 | 62
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | ARRESTER | 5 | 7 | 1690 | 0.00030432 | 1.2605e-06 | 241.4286
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR UG | 3 | 29 | 10149 | 0.0018202 | 5.2012e-06 | 349.9655
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 9 | 258 | 143617 | 0.026187 | 4.7044e-05 | 556.655
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 35 | 167 | 19653 | 0.0035836 | 3.0451e-05 | 117.6826
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | POLE HARDWARE | 9 | 1352 | 111668 | 0.020362 | 0.00024653 | 82.5947
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | METERING | 4 | 6 | 394 | 7.1843e-05 | 1.0941e-06 | 65.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CROSSARM | 32 | 7347 | 1403126 | 0.25585 | 0.0013397 | 190.9794
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | OTHER EQUIPMENT | 1 | 11 | 3212 | 0.00058568 | 2.0058e-06 | 292
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | CABLE TERMINATOR | 1 | 1 | 255 | 4.6497e-05 | 1.8234e-07 | 255
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 4 | 1991 | 309149 | 0.056371 | 0.00036304 | 155.2732
AEP Total | 2020 | 5484199 | PARTIAL POWER | WL | JUMPER/RISER | 2 | 2 | 563 | 0.00010266 | 3.6468e-07 | 281.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | OL | CONN/CLAMP | 60 | 164 | 19803 | 0.0035265 | 2.9205e-05 | 120.75
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 783 | 43694 | 0.0078365 | 0.00014043 | 55.8033
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | CUTOUT | 3 | 5 | 533 | 9.5594e-05 | 8.9675e-07 | 106.6
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | JUMPER/RISER | 11 | 6408 | 671508 | 0.12044 | 0.0011493 | 104.7921
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | REGULATOR | 15 | 14457 | 1364703 | 0.24476 | 0.0025929 | 94.3974
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | POLE | 5 | 5 | 600 | 0.00010761 | 8.9675e-07 | 120
AEP Total | 2023 | 5575683 | PARTIAL POWER | ERF | METERING | 1 | 1 | 441 | 7.9093e-05 | 1.7935e-07 | 441
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | POLE | 6 | 2504 | 338865 | 0.060776 | 0.00044909 | 135.3295
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | ARRESTER | 4 | 6 | 597 | 0.00010707 | 1.0761e-06 | 99.5
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CROSSARM | 4 | 455 | 237739 | 0.042639 | 8.1604e-05 | 522.5033
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 8 | 184 | 73508 | 0.013184 | 3.3e-05 | 399.5
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CROSSARM | 53 | 13532 | 1909869 | 0.34011 | 0.0024098 | 141.1372
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | INSULATOR | 115 | 14238 | 1765461 | 0.31439 | 0.0025355 | 123.9964
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | TRANSFORMER, UG | 1 | 1 | 98 | 1.7452e-05 | 1.7808e-07 | 98
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | SPLICE, OH | 3 | 27 | 11546 | 0.0020708 | 4.8425e-06 | 427.6296
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 21 | 281 | 72269 | 0.01287 | 5.004e-05 | 257.1851
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | METERING | 143 | 157 | 12721 | 0.0023031 | 2.8424e-05 | 81.0255
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR OVERHEAD | 99 | 20096 | 2354928 | 0.42635 | 0.0036383 | 117.1839
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | ARRESTER | 13 | 115 | 21206 | 0.0038393 | 2.082e-05 | 184.4
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WL | NONE | 22 | 15706 | 1997749 | 0.36169 | 0.0028435 | 127.1965
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WT | POLE | 3 | 74 | 116463 | 0.021085 | 1.3397e-05 | 1573.8243
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | METERING | 21 | 86 | 13771 | 0.0024932 | 1.557e-05 | 160.1279
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 7 | 514 | 31968 | 0.0057877 | 9.3058e-05 | 62.1946
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | POLE | 42 | 10191 | 682686 | 0.1236 | 0.001845 | 66.9891
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONN/CLAMP | 5 | 95 | 29282 | 0.0053014 | 1.7199e-05 | 308.2316
AEP Total | 2021 | 5523447 | PARTIAL POWER | FO | NONE | 12 | 43 | 2900 | 0.00052503 | 7.785e-06 | 67.4419
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 14 | 76 | 10158 | 0.0018391 | 1.376e-05 | 133.6579
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 2 | 77 | 18767 | 0.0033977 | 1.3941e-05 | 243.7273
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | NONE | 4 | 158 | 12497 | 0.0022625 | 2.8605e-05 | 79.0949
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | PEDESTAL | 7 | 14 | 2708 | 0.00049027 | 2.5346e-06 | 193.4286
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | POLE | 3 | 15 | 767 | 0.00013886 | 2.7157e-06 | 51.1333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONN/CLAMP | 5 | 73 | 4455 | 0.00080656 | 1.3216e-05 | 61.0274
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | NONE | 1 | 1 | 118 | 2.1363e-05 | 1.8105e-07 | 118
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | RECLOSER, LINE/OCR/BR | 1 | 60 | 15780 | 0.0028569 | 1.0863e-05 | 263
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WW | NONE | 189 | 9531 | 1081841 | 0.19481 | 0.0017163 | 113.5076
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ABI | NONE | 434 | 9160 | 615671 | 0.11087 | 0.0016495 | 67.213
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 406 | 41677 | 4035015 | 0.72659 | 0.0075049 | 96.8163
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | JUMPER/RISER | 11 | 56 | 7159 | 0.0012961 | 1.0139e-05 | 127.8393
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | TRANSFORMER, UG | 4 | 86 | 22874 | 0.0041413 | 1.557e-05 | 265.9767
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | CROSSARM | 1 | 2 | 146 | 2.6433e-05 | 3.6209e-07 | 73
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | TRANSFORMER, UG | 2 | 31 | 4683 | 0.00084784 | 5.6124e-06 | 151.0645
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | CABLE TERMINATOR | 2 | 3 | 313 | 5.6668e-05 | 5.4314e-07 | 104.3333
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | TRANSFORMER, OH | 1 | 6 | 1332 | 0.00024115 | 1.0863e-06 | 222
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR OVERHEAD | 9 | 4067 | 188972 | 0.034213 | 0.00073632 | 46.4647
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | CONN/CLAMP | 1491 | 3135 | 351832 | 0.064154 | 0.00057164 | 112.2271
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | NONE | 3139 | 118774 | 12186532 | 2.2221 | 0.021657 | 102.6027
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | NONE | 90 | 414 | 62143 | 0.011331 | 7.549e-05 | 150.1039
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | TRANSFORMER, OH | 4 | 4 | 181 | 3.3004e-05 | 7.2937e-07 | 45.25
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | ARRESTER | 30 | 87 | 10553 | 0.0019243 | 1.5864e-05 | 121.2989
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CONDUCTOR UG | 48 | 87 | 16025 | 0.002922 | 1.5864e-05 | 184.1954
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | POLE HARDWARE | 18 | 352 | 46912 | 0.008554 | 6.4184e-05 | 133.2727
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 2 | 775 | 64103 | 0.011689 | 0.00014132 | 82.7135
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | NONE | 24 | 10672 | 788410 | 0.14197 | 0.0019217 | 73.8765
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 13 | 1661 | 71825 | 0.012934 | 0.0002991 | 43.242
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | JUMPER/RISER | 51 | 343 | 51318 | 0.0092409 | 6.1765e-05 | 149.6152
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, UG | 5 | 19 | 6198 | 0.0011161 | 3.4214e-06 | 326.2105
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 10 | 3483 | 431322 | 0.077669 | 0.00062719 | 123.8363
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | NONE | 187 | 9558 | 2066532 | 0.37063 | 0.0017142 | 216.2097
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | NONE | 108 | 9932 | 862317 | 0.15466 | 0.0017813 | 86.8221
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | TRANSFORMER, STATION SERVICE | 1 | 5 | 380 | 6.8153e-05 | 8.9675e-07 | 76
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | METERING | 3 | 3 | 206 | 3.6946e-05 | 5.3805e-07 | 68.6667
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | ABX | NONE | 3 | 102 | 11554 | 0.0020806 | 1.8367e-05 | 113.2745
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | FO | CUTOUT | 5 | 33 | 6595 | 0.0011876 | 5.9424e-06 | 199.8485
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR UG | 3 | 5 | 855 | 0.00015396 | 9.0036e-07 | 171
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | JUMPER/RISER | 14 | 4615 | 909172 | 0.16372 | 0.00083103 | 197.0037
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AB | NONE | 7 | 8769 | 300176 | 0.054053 | 0.0015791 | 34.2315
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CROSSARM | 11 | 4732 | 782495 | 0.14091 | 0.0008521 | 165.3624
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | OTHER EQUIPMENT | 1 | 1 | 47 | 8.4634e-06 | 1.8007e-07 | 47
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | INSULATOR | 2 | 21 | 3903 | 0.0007 | 3.7664e-06 | 185.8571
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | JUMPER/RISER | 4 | 479 | 46257 | 0.0083296 | 8.6254e-05 | 96.5699
AEP Total | 2022 | 5553337 | PARTIAL POWER | WU | CONN/CLAMP | 4 | 20 | 3291 | 0.00059262 | 3.6014e-06 | 164.55
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CUTOUT | 38 | 410 | 72890 | 0.013073 | 7.3534e-05 | 177.7805
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 6 | 1182 | 80742 | 0.014481 | 0.00021199 | 68.3096
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | ABI | TRANSFORMER, STATION SERVICE | 3 | 1023 | 400449 | 0.071821 | 0.00018348 | 391.4457
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 46 | 11697 | 0.0021063 | 8.2833e-06 | 254.2826
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | CROSSARM | 2 | 3 | 153 | 2.7441e-05 | 5.3805e-07 | 51
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | INSULATOR | 1 | 25 | 2100 | 0.00037664 | 4.4838e-06 | 84
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | SWITCH, OH | 6 | 6770 | 744601 | 0.13408 | 0.0012191 | 109.9854
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | TRANSFORMER, OH | 6 | 15 | 1525 | 0.00027351 | 2.6903e-06 | 101.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 12 | 303 | 77686 | 0.013933 | 5.4343e-05 | 256.3894
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | FUSE | 1 | 1 | 44 | 7.966e-06 | 1.8105e-07 | 44
AEP Total | 2021 | 5523447 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 69 | 341 | 76683 | 0.013883 | 6.1737e-05 | 224.8768
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | PEDESTAL | 6 | 47 | 1098 | 0.00019879 | 8.5092e-06 | 23.3617
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | JUMPER/RISER | 2 | 4 | 1001 | 0.00018123 | 7.2419e-07 | 250.25
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CROSSARM | 1 | 1272 | 125568 | 0.022734 | 0.00023029 | 98.717
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 4 | 10 | 1672 | 0.00030271 | 1.8105e-06 | 167.2
AEP Total | 2021 | 5523447 | PARTIAL POWER | WW | NONE | 2 | 2 | 170 | 3.0778e-05 | 3.6209e-07 | 85
AEP Total | 2021 | 5523447 | PARTIAL POWER | ERF | CONN/CLAMP | 1 | 1 | 52 | 9.4144e-06 | 1.8105e-07 | 52
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CONN/CLAMP | 1191 | 2857 | 318154 | 0.057291 | 0.00051447 | 111.3595
AEP Total | 2021 | 5523447 | PARTIAL POWER | WI | NONE | 3 | 3 | 503 | 9.1066e-05 | 5.4314e-07 | 167.6667
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CONDUCTOR UG | 4 | 4 | 799 | 0.00014466 | 7.2419e-07 | 199.75
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 4 | 2093 | 197686 | 0.03579 | 0.00037893 | 94.451
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONDUCTOR UG | 5 | 257 | 45992 | 0.0083267 | 4.6529e-05 | 178.9572
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | JUMPER/RISER | 1 | 57 | 4731 | 0.00085653 | 1.032e-05 | 83
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | JUMPER/RISER | 287 | 22300 | 2402779 | 0.43813 | 0.0040662 | 107.7479
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | TRANSFORMER, OH | 40 | 217 | 55275 | 0.010079 | 3.9568e-05 | 254.7235
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 287 | 41615 | 0.0075882 | 5.2332e-05 | 145
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | METERING | 7 | 7 | 696 | 0.00012691 | 1.2764e-06 | 99.4286
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | INSULATOR | 6 | 2185 | 196703 | 0.035867 | 0.00039842 | 90.0243
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 5 | 5 | 477 | 8.6977e-05 | 9.1171e-07 | 95.4
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | POLE | 1 | 3 | 315 | 5.7438e-05 | 5.4703e-07 | 105
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | POLE | 1 | 6 | 1278 | 0.00023303 | 1.0941e-06 | 213
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | NONE | 63 | 8477 | 650322 | 0.11858 | 0.0015457 | 76.7161
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 42 | 2196 | 164407 | 0.029605 | 0.00039544 | 74.8666
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | POLE | 44 | 13978 | 1420853 | 0.25586 | 0.002517 | 101.6492
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | ARRESTER | 27 | 46 | 9101 | 0.0016388 | 8.2833e-06 | 197.8478
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | RECLOSER, LINE/OCR/BR | 2 | 600 | 47334 | 0.008631 | 0.00010941 | 78.89
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | TRANSFORMER, POWER - LTC | 1 | 1 | 47 | 8.5701e-06 | 1.8234e-07 | 47
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | CONDUCTOR UG | 14 | 35 | 10512 | 0.001872 | 6.2328e-06 | 300.3429
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | SPLICE, OH | 1 | 1 | 129 | 2.3355e-05 | 1.8105e-07 | 129
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | INSULATOR | 6 | 2222 | 184071 | 0.032779 | 0.00039569 | 82.8402
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | CONN/CLAMP | 3 | 4 | 485 | 8.6369e-05 | 7.1232e-07 | 121.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | SPLICE, UG | 2 | 2 | 437 | 7.7821e-05 | 3.5616e-07 | 218.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 25 | 951 | 102698 | 0.018288 | 0.00016935 | 107.9895
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 2 | 9 | 1715 | 0.00030541 | 1.6027e-06 | 190.5556
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | JUMPER/RISER | 1 | 2263 | 72279 | 0.012871 | 0.00040299 | 31.9395
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 3 | 278 | 4.9506e-05 | 5.3424e-07 | 92.6667
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | TRANSFORMER, GROUNDING | 1 | 3 | 166 | 2.9561e-05 | 5.3424e-07 | 55.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | POLE | 11 | 362 | 43048 | 0.007666 | 6.4465e-05 | 118.9171
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 1 | 1 | 106 | 1.8876e-05 | 1.7808e-07 | 106
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | POLE | 6 | 424 | 14985 | 0.0026685 | 7.5506e-05 | 35.342
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | GUY/ANCHOR | 2 | 5 | 510 | 9.0821e-05 | 8.904e-07 | 102
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | GUY/ANCHOR | 1 | 1 | 60 | 1.0685e-05 | 1.7808e-07 | 60
AEP Total | 2024 | 5615460 | PARTIAL POWER | TIR | TRANSFORMER, OH | 2 | 12 | 953 | 0.00016971 | 2.137e-06 | 79.4167
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | RECLOSER, LINE/OCR/BR | 1 | 1016 | 61976 | 0.011037 | 0.00018093 | 61
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | EQF | ARRESTER | 1 | 1426 | 71300 | 0.012697 | 0.00025394 | 50
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | TRANSFORMER, OH | 1 | 1 | 319 | 5.7443e-05 | 1.8007e-07 | 319
AEP Total | 2020 | 5484199 | PARTIAL POWER | FO | CONN/CLAMP | 1 | 1 | 159 | 2.8992e-05 | 1.8234e-07 | 159
AEP Total | 2024 | 5615460 | PARTIAL POWER | VA | POLE | 1 | 3 | 600 | 0.00010685 | 5.3424e-07 | 200
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | TRANSFORMER, POWER - LTC | 1 | 1033 | 50617 | 0.0091147 | 0.00018601 | 49
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 2 | 180 | 3.2413e-05 | 3.6014e-07 | 90
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CONDUCTOR UG | 2 | 68 | 17696 | 0.0031513 | 1.2109e-05 | 260.2353
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | EQF | INSULATOR | 3 | 3476 | 167745 | 0.029872 | 0.00061901 | 48.2581
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | VIN | CONDUCTOR OVERHEAD | 1 | 2 | 154 | 2.7424e-05 | 3.5616e-07 | 77
AEP Total | 2025 | 5615460 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 138 | 2.4575e-05 | 1.7808e-07 | 138
AEP Total | 2020 | 5484199 | PARTIAL POWER | WH | NONE | 6 | 6 | 1002 | 0.00018271 | 1.0941e-06 | 167
AEP Total | 2020 | 5484199 | PARTIAL POWER | ABI | CUTOUT | 1 | 1 | 249 | 4.5403e-05 | 1.8234e-07 | 249
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | CF | ARRESTER | 2 | 196 | 17168 | 0.0030573 | 3.4904e-05 | 87.5918
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | AB | CIRCUIT SWITCHER | 3 | 1505 | 113014 | 0.020126 | 0.00026801 | 75.0924
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | REGULATOR | 1 | 402 | 26532 | 0.0047248 | 7.1588e-05 | 66
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 1 | 77 | 1.381e-05 | 1.7935e-07 | 77
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | POLE | 1 | 1 | 220 | 4.0115e-05 | 1.8234e-07 | 220
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONDUCTOR OVERHEAD | 168 | 483 | 79687 | 0.014427 | 8.7445e-05 | 164.9834
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1836 | 14156 | 1590755 | 0.288 | 0.0025629 | 112.3732
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 7 | 3352 | 427512 | 0.077953 | 0.00061121 | 127.5394
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | CONDUCTOR OVERHEAD | 8 | 56 | 7225 | 0.0013174 | 1.0211e-05 | 129.0179
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 46 | 474 | 113184 | 0.020638 | 8.643e-05 | 238.7848
AEP Total | 2020 | 5484199 | PARTIAL POWER | ERF | FUSE | 1 | 1 | 71 | 1.2946e-05 | 1.8234e-07 | 71
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ERF | METERING | 3 | 3 | 136 | 2.4799e-05 | 5.4703e-07 | 45.3333
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | POLE HARDWARE | 3 | 87 | 17205 | 0.0031372 | 1.5864e-05 | 197.7586
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | PEDESTAL | 2 | 3 | 395 | 7.2025e-05 | 5.4703e-07 | 131.6667
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | POLE HARDWARE | 4 | 94 | 19135 | 0.0034891 | 1.714e-05 | 203.5638
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | SWITCH, UG | 1 | 6 | 378 | 6.8925e-05 | 1.0941e-06 | 63
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 18 | 5598 | 0.0010208 | 3.2822e-06 | 311
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | ARRESTER | 10 | 87 | 5016 | 0.00091463 | 1.5864e-05 | 57.6552
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | ABX | NONE | 3 | 202 | 13368 | 0.0024375 | 3.6833e-05 | 66.1782
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TR | POLE | 1 | 1 | 501 | 9.1353e-05 | 1.8234e-07 | 501
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | RECLOSER, LINE/OCR/BR | 2 | 480 | 69018 | 0.012585 | 8.7524e-05 | 143.7875
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | CONDUCTOR OVERHEAD | 166 | 52828 | 8597812 | 1.542 | 0.0094747 | 162.751
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CUTOUT | 4 | 28 | 5997 | 0.0010799 | 5.042e-06 | 214.1786
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CAPACITOR | 3 | 63 | 2204 | 0.00039688 | 1.1345e-05 | 34.9841
AEP Total | 2023 | 5575683 | PARTIAL POWER | VIN | NONE | 13 | 29 | 2420 | 0.00043403 | 5.2012e-06 | 83.4483
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | CUTOUT | 89 | 930 | 124275 | 0.022289 | 0.0001668 | 133.629
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | CONDUCTOR OVERHEAD | 26 | 111 | 12667 | 0.002281 | 1.9988e-05 | 114.1171
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 37 | 4107 | 0.00073956 | 6.6627e-06 | 111
AEP Total | 2023 | 5575683 | PARTIAL POWER | WU | CONDUCTOR OVERHEAD | 10 | 44 | 7503 | 0.0013457 | 7.8914e-06 | 170.5227
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | NONE | 10 | 773 | 46649 | 0.0083665 | 0.00013864 | 60.348
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | PEDESTAL | 1 | 13 | 13533 | 0.0024369 | 2.3409e-06 | 1041
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CF | PEDESTAL | 5 | 45 | 36831 | 0.0066322 | 8.1032e-06 | 818.4667
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WT | CONDUCTOR UG | 1 | 1 | 39 | 7.0228e-06 | 1.8007e-07 | 39
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | POLE HARDWARE | 6 | 112 | 4079 | 0.00073451 | 2.0168e-05 | 36.4196
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WFS | NONE | 1 | 41 | 70159 | 0.012634 | 7.3829e-06 | 1711.1951
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | JUMPER/RISER | 1 | 83 | 17596 | 0.0031685 | 1.4946e-05 | 212
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | SWITCH, UG | 1 | 559 | 17778 | 0.0031885 | 0.00010026 | 31.8032
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | METERING | 4 | 5 | 222 | 3.9816e-05 | 8.9675e-07 | 44.4
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CROSSARM | 14 | 424 | 128610 | 0.022903 | 7.5506e-05 | 303.3255
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 361 | 5530 | 1176565 | 0.20952 | 0.00098478 | 212.7604
AEP Total | 2024 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 138 | 138 | 18245 | 0.0032491 | 2.4575e-05 | 132.2101
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 688 | 29232 | 4967870 | 0.88468 | 0.0052056 | 169.9463
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CUTOUT | 107 | 1056 | 110168 | 0.019619 | 0.00018805 | 104.3258
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | TRANSFORMER, OH | 17 | 234 | 79416 | 0.014142 | 4.1671e-05 | 339.3846
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | NONE | 111 | 9526 | 767434 | 0.13666 | 0.0016964 | 80.562
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | TRANSFORMER, UG | 1 | 1 | 467 | 8.3757e-05 | 1.7935e-07 | 467
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | NONE | 74 | 184 | 22562 | 0.0040178 | 3.2767e-05 | 122.6196
AEP Total | 2023 | 5575683 | PARTIAL POWER | OL | JUMPER/RISER | 2 | 23 | 3133 | 0.0005619 | 4.1251e-06 | 136.2174
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | TRANSFORMER, POWER - LTC | 2 | 698 | 36250 | 0.0065014 | 0.00012519 | 51.9341
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | NONE | 8 | 2227 | 383816 | 0.06835 | 0.00039658 | 172.3467
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | O | CONDUCTOR OVERHEAD | 2 | 1146 | 126903 | 0.02276 | 0.00020554 | 110.7356
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 726 | 62436 | 0.011198 | 0.00013021 | 86
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | OTHER EQUIPMENT | 5 | 8 | 1303 | 0.00023204 | 1.4246e-06 | 162.875
AEP Total | 2024 | 5615460 | PARTIAL POWER | WFS | CONN/CLAMP | 4 | 4 | 319 | 5.6807e-05 | 7.1232e-07 | 79.75
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 6 | 27 | 4120 | 0.00073369 | 4.8082e-06 | 152.5926
AEP Total | 2024 | 5615460 | PARTIAL POWER | WU | CUTOUT | 1 | 2 | 90 | 1.6027e-05 | 3.5616e-07 | 45
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | UB | CONN/CLAMP | 2 | 3 | 283 | 5.0397e-05 | 5.3424e-07 | 94.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 1 | 1 | 70 | 1.2555e-05 | 1.7935e-07 | 70
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | CABLE TERMINATOR | 1 | 1 | 45 | 8.1032e-06 | 1.8007e-07 | 45
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 99 | 99 | 13435 | 0.0023925 | 1.763e-05 | 135.7071
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 59 | 12324 | 1365530 | 0.24317 | 0.0021947 | 110.8025
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | FO | JUMPER/RISER | 1 | 20 | 1000 | 0.00017935 | 3.587e-06 | 50
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | PEDESTAL | 1 | 4 | 448 | 8.0349e-05 | 7.174e-07 | 112
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | TRANSFORMER, UG | 322 | 4829 | 1163094 | 0.21057 | 0.00087427 | 240.8561
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | ARRESTER | 324 | 8314 | 873184 | 0.15809 | 0.0015052 | 105.0257
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | CONDUCTOR OVERHEAD | 36 | 6386 | 748875 | 0.13558 | 0.0011562 | 117.2682
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | OL | RELAY | 1 | 1340 | 16080 | 0.0029112 | 0.0002426 | 12
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | NONE | 171 | 31345 | 3089329 | 0.55931 | 0.0056749 | 98.5589
AEP Total | 2021 | 5523447 | PARTIAL POWER | ABI | NONE | 33 | 82 | 5742 | 0.0010396 | 1.4846e-05 | 70.0244
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | NONE | 629 | 11007 | 1054873 | 0.19098 | 0.0019928 | 95.8366
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | CAPACITOR | 8 | 2819 | 165834 | 0.030024 | 0.00051037 | 58.8272
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | METERING | 1 | 1 | 56 | 1.0084e-05 | 1.8007e-07 | 56
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | RECLOSER, LINE/OCR/BR | 1 | 686 | 60755 | 0.01094 | 0.00012353 | 88.5641
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | SWITCH, OH | 1 | 14 | 3987 | 0.00071795 | 2.521e-06 | 284.7857
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | RECLOSER, LINE/OCR/BR | 4 | 799 | 89786 | 0.015989 | 0.00014229 | 112.373
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TIR | CUTOUT | 20 | 1331 | 183626 | 0.0327 | 0.00023702 | 137.9609
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | PEDESTAL | 6 | 39 | 3669 | 0.00065337 | 6.9451e-06 | 94.0769
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 5 | 34 | 5637 | 0.0010038 | 6.0547e-06 | 165.7941
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | POLE | 3 | 3 | 628 | 0.00011183 | 5.3424e-07 | 209.3333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | TRANSFORMER, GROUNDING | 3 | 14 | 2712 | 0.00048295 | 2.4931e-06 | 193.7143
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR UG | 4 | 1552 | 308657 | 0.054966 | 0.00027638 | 198.8769
AEP Total | 2025 | 5615460 | PARTIAL POWER | TIR | ARRESTER | 1 | 2 | 322 | 5.7342e-05 | 3.5616e-07 | 161
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | RECLOSER, LINE/OCR/BR | 2 | 333 | 17670 | 0.0031467 | 5.9301e-05 | 53.0631
AEP Total | 2025 | 5615460 | PARTIAL POWER | CF | ARRESTER | 2 | 2 | 229 | 4.078e-05 | 3.5616e-07 | 114.5
AEP Total | 2024 | 5615460 | PARTIAL POWER | EQF | SPLICE, UG | 3 | 17 | 2187 | 0.00038946 | 3.0274e-06 | 128.6471
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | CABLE TERMINATOR | 5 | 36 | 11260 | 0.0020052 | 6.4109e-06 | 312.7778
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | ABI | TRANSFORMER, OH | 2 | 8 | 242 | 4.3095e-05 | 1.4246e-06 | 30.25
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | OL | CROSSARM | 1 | 19 | 3781 | 0.00067332 | 3.3835e-06 | 199
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | JUMPER/RISER | 1 | 1 | 103 | 1.8342e-05 | 1.7808e-07 | 103
AEP Total | 2025 | 5615460 | PARTIAL POWER | U | NONE | 3 | 20 | 3821 | 0.00068044 | 3.5616e-06 | 191.05
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | ABI | ARRESTER | 1 | 1200 | 66945 | 0.011922 | 0.0002137 | 55.7875
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | CONDUCTOR UG | 4 | 7 | 650 | 0.00011852 | 1.2764e-06 | 92.8571
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | CUTOUT | 2 | 3 | 259 | 4.6123e-05 | 5.3424e-07 | 86.3333
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | TRANSFORMER, UG | 1 | 3 | 2796 | 0.00049791 | 5.3424e-07 | 932
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 40 | 7.1232e-06 | 1.7808e-07 | 40
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AF | TRANSFORMER, STATION SERVICE | 2 | 938 | 64992 | 0.011703 | 0.00016891 | 69.2878
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 2 | 2 | 111 | 1.9767e-05 | 3.5616e-07 | 55.5
AEP Total | 2025 | 5615460 | PARTIAL POWER | UB | CONN/CLAMP | 2 | 2 | 150 | 2.6712e-05 | 3.5616e-07 | 75
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | REGULATOR | 1 | 22 | 1936 | 0.00034476 | 3.9178e-06 | 88
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 9 | 819 | 0.00014585 | 1.6027e-06 | 91
AEP Total | 2024 | 5615460 | PARTIAL POWER | VIN | ARRESTER | 1 | 3 | 231 | 4.1136e-05 | 5.3424e-07 | 77
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | CAPACITOR | 1 | 1 | 222 | 3.9534e-05 | 1.7808e-07 | 222
AEP Total | 2023 | 5575683 | PARTIAL POWER | ABI | TRANSFORMER, OH | 1 | 1 | 60 | 1.0761e-05 | 1.7935e-07 | 60
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | CROSSARM | 1 | 1 | 96 | 1.7505e-05 | 1.8234e-07 | 96
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | OTHER EQUIPMENT | 1 | 1 | 289 | 5.2697e-05 | 1.8234e-07 | 289
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | WL | REGULATOR | 2 | 1218 | 113276 | 0.020398 | 0.00021933 | 93.0016
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | TRANSFORMER, STATION SERVICE | 1 | 1 | 47 | 8.3698e-06 | 1.7808e-07 | 47
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | ARRESTER | 1 | 1 | 53 | 9.4382e-06 | 1.7808e-07 | 53
AEP Total | 2020 | 5484199 | PARTIAL POWER | WI | NONE | 1 | 1 | 35 | 6.382e-06 | 1.8234e-07 | 35
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | ERF | RELAY | 1 | 898 | 33226 | 0.0060154 | 0.00016258 | 37
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CROSSARM | 5 | 474 | 43484 | 0.0078726 | 8.5816e-05 | 91.7384
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | SWITCH, OH | 1 | 1150 | 8050 | 0.0014574 | 0.0002082 | 7
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | CUTOUT | 9 | 74 | 8334 | 0.0015088 | 1.3397e-05 | 112.6216
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | REGULATOR | 1 | 791 | 59325 | 0.010741 | 0.00014321 | 75
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AO | NONE | 24 | 12844 | 595614 | 0.10783 | 0.0023254 | 46.3729
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | SPLICE, UG | 1 | 1 | 196 | 3.5485e-05 | 1.8105e-07 | 196
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | METERING | 2 | 2 | 300 | 5.4314e-05 | 3.6209e-07 | 150
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | SWITCH, OH | 4 | 711 | 10445 | 0.001891 | 0.00012872 | 14.6906
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | METERING | 1 | 1 | 211 | 3.8201e-05 | 1.8105e-07 | 211
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CROSSARM | 1 | 1 | 285 | 5.1598e-05 | 1.8105e-07 | 285
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | U | NONE | 2845 | 131458 | 8329835 | 1.5 | 0.023672 | 63.365
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 3704 | 338025 | 0.060869 | 0.00066699 | 91.2594
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SPLICE, OH | 13 | 39 | 5756 | 0.0010365 | 7.0228e-06 | 147.5897
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 99 | 648 | 142510 | 0.025662 | 0.00011669 | 219.9228
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TR | NONE | 21 | 735 | 64357 | 0.011589 | 0.00013235 | 87.5605
AEP Total | 2022 | 5553337 | PARTIAL POWER | UB | TRANSFORMER, UG | 1 | 9 | 720 | 0.00012965 | 1.6206e-06 | 80
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | A | CONN/CLAMP | 8 | 29 | 2734 | 0.00049232 | 5.2221e-06 | 94.2759
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | AF | POLE | 2 | 1189 | 48950 | 0.0088145 | 0.00021411 | 41.169
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | POLE | 60 | 5267 | 610479 | 0.11132 | 0.0009604 | 115.9064
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CONDUCTOR OVERHEAD | 41 | 1929 | 302068 | 0.05508 | 0.00035174 | 156.5931
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | SPLICE, OH | 5 | 17 | 1792 | 0.00032676 | 3.0998e-06 | 105.4118
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | FO | NONE | 88 | 6460 | 481001 | 0.087707 | 0.0011779 | 74.4584
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | ARRESTER | 14 | 147 | 9644 | 0.0017585 | 2.6804e-05 | 65.6054
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | METERING | 190 | 204 | 20367 | 0.0037138 | 3.7198e-05 | 99.8382
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WL | METERING | 15 | 16 | 3301 | 0.00060191 | 2.9175e-06 | 206.3125
AEP Total | 2024 | 5615460 | PARTIAL POWER | CO | PEDESTAL | 5 | 9 | 2273 | 0.00040478 | 1.6027e-06 | 252.5556
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | CUTOUT | 36 | 2005 | 152562 | 0.027168 | 0.00035705 | 76.0908
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | CAPACITOR | 2 | 626 | 49447 | 0.0088055 | 0.00011148 | 78.9888
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | INSULATOR | 3 | 13 | 4987 | 0.00089442 | 2.3316e-06 | 383.6154
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | POLE | 2 | 11 | 1149 | 0.0002069 | 1.9808e-06 | 104.4545
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | SWITCH, OH | 1 | 1 | 371 | 6.6807e-05 | 1.8007e-07 | 371
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | TRANSFORMER, OH | 53 | 341 | 69452 | 0.012368 | 6.0725e-05 | 203.6716
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 30 | 108 | 22984 | 0.004093 | 1.9233e-05 | 212.8148
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | CONDUCTOR OVERHEAD | 29 | 29 | 2648 | 0.00047156 | 5.1643e-06 | 91.3103
AEP Total | 2023 | 5575683 | PARTIAL POWER | VA | CONN/CLAMP | 3 | 6 | 1292 | 0.00023172 | 1.0761e-06 | 215.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | TRANSFORMER, POWER - NON LTC | 1 | 26 | 13847 | 0.0024835 | 4.6631e-06 | 532.5769
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WFS | NONE | 2 | 13 | 1831 | 0.00032839 | 2.3316e-06 | 140.8462
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 1 | 55 | 1.0029e-05 | 1.8234e-07 | 55
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | SWITCH, OH | 2 | 4207 | 208847 | 0.037191 | 0.00074918 | 49.6427
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 5 | 49 | 6724 | 0.0011974 | 8.7259e-06 | 137.2245
AEP Total | 2024 | 5615460 | PARTIAL POWER | A | CONDUCTOR UG | 1 | 3 | 243 | 4.3273e-05 | 5.3424e-07 | 81
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | METERING | 11 | 13 | 963 | 0.00017149 | 2.315e-06 | 74.0769
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | INSULATOR | 1 | 1049 | 58744 | 0.010461 | 0.00018681 | 56
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 9 | 3059 | 330798 | 0.058908 | 0.00054475 | 108.1393
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WT | CONN/CLAMP | 1 | 4 | 280 | 4.9862e-05 | 7.1232e-07 | 70
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | FO | ARRESTER | 2 | 6 | 851 | 0.00015155 | 1.0685e-06 | 141.8333
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | JUMPER/RISER | 5 | 56 | 4587 | 0.00081685 | 9.9725e-06 | 81.9107
AEP Total | 2025 | 5615460 | PARTIAL POWER | CF | PEDESTAL | 1 | 1 | 53 | 9.4382e-06 | 1.7808e-07 | 53
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WW | INSULATOR | 2 | 44 | 10325 | 0.0018387 | 7.8355e-06 | 234.6591
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | JUMPER/RISER | 2 | 3 | 588 | 0.00010471 | 5.3424e-07 | 196
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | O | OTHER EQUIPMENT | 1 | 1 | 122 | 2.1726e-05 | 1.7808e-07 | 122
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | AF | JUMPER/RISER | 1 | 19 | 3439 | 0.00061242 | 3.3835e-06 | 181
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | WU | SPLICE, OH | 2 | 12 | 4226 | 0.00075257 | 2.137e-06 | 352.1667
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | FO | CONN/CLAMP | 2 | 2 | 157 | 2.7959e-05 | 3.5616e-07 | 78.5
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | TOR | TRANSFORMER, OH | 2 | 2 | 112 | 1.9945e-05 | 3.5616e-07 | 56
AEP Total | 2025 | 5615460 | DISTRIBUTION STATION | AF | INSULATOR | 2 | 590 | 27730 | 0.0049382 | 0.00010507 | 47
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | FUSE | 1 | 1 | 597 | 0.00010808 | 1.8105e-07 | 597
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | TRANSFORMER, GROUNDING | 1 | 1 | 106 | 1.9088e-05 | 1.8007e-07 | 106
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | POLE HARDWARE | 1 | 36 | 4572 | 0.00081999 | 6.4566e-06 | 127
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CABLE TERMINATOR | 1 | 1 | 51 | 9.1469e-06 | 1.7935e-07 | 51
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | POLE | 1 | 6 | 894 | 0.00016034 | 1.0761e-06 | 149
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | SECTIONALIZER | 1 | 6 | 1734 | 0.00031099 | 1.0761e-06 | 289
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | OL | INSULATOR | 1 | 291 | 32883 | 0.0058558 | 5.1821e-05 | 113
AEP Total | 2025 | 5615460 | PARTIAL POWER | WW | SPLICE, OH | 1 | 1 | 175 | 3.1164e-05 | 1.7808e-07 | 175
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 94 | 1.714e-05 | 1.8234e-07 | 94
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | ARRESTER | 1 | 1 | 39 | 6.9947e-06 | 1.7935e-07 | 39
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | AO | REGULATOR | 2 | 1122 | 113938 | 0.020517 | 0.00020204 | 101.549
AEP Total | 2020 | 5484199 | PARTIAL POWER | WH | CONN/CLAMP | 3 | 19 | 17119 | 0.0031215 | 3.4645e-06 | 901
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | JUMPER/RISER | 1 | 8 | 424 | 7.7313e-05 | 1.4587e-06 | 53
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | METERING | 1 | 1 | 132 | 2.4069e-05 | 1.8234e-07 | 132
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | ARRESTER | 1 | 3 | 57 | 1.032e-05 | 5.4314e-07 | 19
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | CUTOUT | 1 | 148 | 53428 | 0.0095144 | 2.6356e-05 | 361
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | U | NONE | 3932 | 143253 | 8353072 | 1.5123 | 0.025935 | 58.3099
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | TRANSFORMER, OH | 262 | 1257 | 445828 | 0.080716 | 0.00022758 | 354.6762
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONN/CLAMP | 103 | 1030 | 89779 | 0.016254 | 0.00018648 | 87.1641
AEP Total | 2021 | 5523447 | PARTIAL POWER | TOR | NONE | 36 | 36 | 4618 | 0.00083607 | 6.5177e-06 | 128.2778
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WI | FUSE | 1 | 1 | 64 | 1.1587e-05 | 1.8105e-07 | 64
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 30 | 209 | 37862 | 0.0068548 | 3.7839e-05 | 181.1579
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | PEDESTAL | 3 | 7 | 1491 | 0.00026994 | 1.2673e-06 | 213
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | NONE | 52 | 2248 | 328198 | 0.059419 | 0.00040699 | 145.9956
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | POLE HARDWARE | 2 | 1123 | 228926 | 0.041446 | 0.00020332 | 203.8522
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 9 | 769 | 0.00013922 | 1.6294e-06 | 85.4444
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 13 | 3259 | 116383 | 0.021071 | 0.00059003 | 35.7113
AEP Total | 2021 | 5523447 | PARTIAL POWER | CO | SPLICE, OH | 2 | 2 | 114 | 2.0639e-05 | 3.6209e-07 | 57
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CROSSARM | 4 | 1416 | 17126 | 0.0031006 | 0.00025636 | 12.0946
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | METERING | 1 | 176 | 28718 | 0.0051993 | 3.1864e-05 | 163.1705
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | CONN/CLAMP | 13 | 45 | 4318 | 0.00078176 | 8.1471e-06 | 95.9556
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TR | CROSSARM | 1 | 158 | 12324 | 0.0022312 | 2.8605e-05 | 78
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WW | ARRESTER | 1 | 7 | 882 | 0.00015968 | 1.2673e-06 | 126
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | INSULATOR | 3 | 3877 | 409886 | 0.073513 | 0.00069534 | 105.7225
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | JUMPER/RISER | 65 | 1836 | 246794 | 0.043949 | 0.00032695 | 134.4194
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 36 | 7299 | 693981 | 0.12358 | 0.0012998 | 95.0789
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | AF | CONN/CLAMP | 1 | 271 | 49051 | 0.0087973 | 4.8604e-05 | 181
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | AB | NONE | 17 | 13529 | 735613 | 0.131 | 0.0024092 | 54.3731
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | EQF | SWITCH, OH | 6 | 6993 | 609382 | 0.10929 | 0.0012542 | 87.1417
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 10 | 964 | 130224 | 0.02319 | 0.00017167 | 135.0871
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WL | TRANSFORMER, UG | 11 | 171 | 103804 | 0.018485 | 3.0452e-05 | 607.0409
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CF | SWITCH, OH | 6 | 6285 | 349385 | 0.062218 | 0.0011192 | 55.5903
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | NETWORK LIMITER | 1 | 2 | 298 | 5.3068e-05 | 3.5616e-07 | 149
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | OTHER EQUIPMENT | 1 | 340 | 18010 | 0.0032301 | 6.0979e-05 | 52.9706
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 16 | 5656 | 388983 | 0.06927 | 0.0010072 | 68.7735
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | CUTOUT | 7 | 22 | 1211 | 0.00021565 | 3.9178e-06 | 55.0455
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WH | CONDUCTOR OVERHEAD | 4 | 23 | 82748 | 0.014736 | 4.0958e-06 | 3597.7391
AEP Total | 2024 | 5615460 | PARTIAL POWER | WH | CONN/CLAMP | 1 | 1 | 1120 | 0.00019945 | 1.7808e-07 | 1120
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | SPLICE, OH | 8 | 8 | 1226 | 0.00021833 | 1.4246e-06 | 153.25
AEP Total | 2024 | 5615460 | PARTIAL POWER | WL | CUTOUT | 5 | 38 | 6291 | 0.0011203 | 6.767e-06 | 165.5526
AEP Total | 2023 | 5575683 | PARTIAL POWER | EQF | GUY/ANCHOR | 1 | 2 | 488 | 8.7523e-05 | 3.587e-07 | 244
AEP Total | 2022 | 5553337 | PARTIAL POWER | OL | TRANSFORMER, OH | 2 | 19 | 1907 | 0.0003434 | 3.4214e-06 | 100.3684
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | CO | TRANSFORMER, OH | 15 | 64 | 9323 | 0.0016602 | 1.1397e-05 | 145.6719
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | ABI | NONE | 68 | 3930 | 175240 | 0.031207 | 0.00069985 | 44.5903
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | GUY/ANCHOR | 1 | 1 | 151 | 2.7191e-05 | 1.8007e-07 | 151
AEP Total | 2022 | 5553337 | PARTIAL POWER | CO | SPLICE, UG | 2 | 11 | 997 | 0.00017953 | 1.9808e-06 | 90.6364
AEP Total | 2025 | 5615460 | PARTIAL POWER | TOR | NONE | 8 | 8 | 775 | 0.00013801 | 1.4246e-06 | 96.875
AEP Total | 2025 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, OH | 5 | 4236 | 422341 | 0.07521 | 0.00075435 | 99.7028
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | A | METERING | 18 | 18 | 1407 | 0.00025056 | 3.2054e-06 | 78.1667
AEP Total | 2023 | 5575683 | DISTRIBUTION STATION | AF | SWITCH, UG | 1 | 903 | 140868 | 0.025265 | 0.00016195 | 156
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | OTHER EQUIPMENT | 2 | 14 | 518 | 9.4453e-05 | 2.5528e-06 | 37
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | CONDUCTOR OVERHEAD | 1 | 805 | 95676 | 0.017446 | 0.00014679 | 118.8522
AEP Total | 2020 | 5484199 | PARTIAL POWER | OL | JUMPER/RISER | 1 | 19 | 3648 | 0.00066518 | 3.4645e-06 | 192
AEP Total | 2020 | 5484199 | PARTIAL POWER | TOR | SPLICE, OH | 2 | 2 | 673 | 0.00012272 | 3.6468e-07 | 336.5
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WFS | CONN/CLAMP | 2 | 10 | 2203 | 0.00039885 | 1.8105e-06 | 220.3
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CAPACITOR | 1 | 129 | 3999 | 0.000724 | 2.3355e-05 | 31
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CAPACITOR | 1 | 62 | 992 | 0.0001796 | 1.1225e-05 | 16
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | SWITCH, UG | 3 | 386 | 5422 | 0.00096555 | 6.8739e-05 | 14.0466
AEP Total | 2024 | 5615460 | DISTRIBUTION STATION | CF | NONE | 18 | 21744 | 1772373 | 0.31562 | 0.0038722 | 81.5109
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | SWITCH, OH | 1 | 1218 | 63336 | 0.011405 | 0.00021933 | 52
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | OTHER EQUIPMENT | 1 | 1 | 216 | 3.874e-05 | 1.7935e-07 | 216
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 8 | 77 | 21023 | 0.0037705 | 1.381e-05 | 273.026
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | INSULATOR | 10 | 579 | 82636 | 0.014821 | 0.00010384 | 142.7219
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | CABLE TERMINATOR | 3 | 7 | 989 | 0.00017738 | 1.2555e-06 | 141.2857
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | METERING | 2 | 73 | 10085 | 0.0018389 | 1.3311e-05 | 138.1507
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | RELAY | 6 | 8820 | 898940 | 0.16391 | 0.0016083 | 101.9206
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | JUMPER/RISER | 42 | 1949 | 218921 | 0.039919 | 0.00035538 | 112.3248
AEP Total | 2020 | 5484199 | PARTIAL POWER | TIR | CONDUCTOR OVERHEAD | 88 | 394 | 85435 | 0.015578 | 7.1843e-05 | 216.8401
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CF | CUTOUT | 28 | 501 | 63349 | 0.011551 | 9.1353e-05 | 126.4451
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | REGULATOR | 11 | 3356 | 207382 | 0.037814 | 0.00061194 | 61.7944
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VA | METERING | 1 | 1 | 30 | 5.4703e-06 | 1.8234e-07 | 30
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | CABLE TERMINATOR | 4 | 12 | 9474 | 0.0017275 | 2.1881e-06 | 789.5
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | ARRESTER | 3 | 3 | 242 | 4.4127e-05 | 5.4703e-07 | 80.6667
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | CABLE TERMINATOR | 7 | 54 | 10150 | 0.0018508 | 9.8465e-06 | 187.963
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WW | CROSSARM | 1 | 12 | 19200 | 0.003501 | 2.1881e-06 | 1600
AEP Total | 2020 | 5484199 | DISTRIBUTION STATION | EQF | INSULATOR | 2 | 1533 | 345026 | 0.062913 | 0.00027953 | 225.0659
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | OTHER EQUIPMENT | 1 | 1 | 110 | 1.9729e-05 | 1.7935e-07 | 110
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | CROSSARM | 1 | 42 | 7584 | 0.0013602 | 7.5327e-06 | 180.5714
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VIN | CUTOUT | 3 | 28 | 3882 | 0.00069624 | 5.0218e-06 | 138.6429
AEP Total | 2023 | 5575683 | PARTIAL POWER | CF | TRANSFORMER, OH | 3 | 8 | 1144 | 0.00020518 | 1.4348e-06 | 143
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | TRANSFORMER, POWER - LTC | 4 | 3386 | 162832 | 0.029321 | 0.00060972 | 48.0898
AEP Total | 2024 | 5615460 | PARTIAL POWER | ABI | NONE | 45 | 168 | 10405 | 0.0018529 | 2.9917e-05 | 61.9345
AEP Total | 2024 | 5615460 | PARTIAL POWER | CF | CONN/CLAMP | 68 | 392 | 48929 | 0.0087133 | 6.9807e-05 | 124.8189
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | VA | TRANSFORMER, UG | 19 | 1355 | 332185 | 0.059155 | 0.0002413 | 245.155
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | WW | NONE | 92 | 7804 | 899302 | 0.16015 | 0.0013897 | 115.236
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | NONE | 303 | 303 | 38932 | 0.006933 | 5.3958e-05 | 128.4884
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | POLE HARDWARE | 40 | 1618 | 215099 | 0.038305 | 0.00028813 | 132.9413
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | OL | CONN/CLAMP | 25 | 88 | 9594 | 0.0017207 | 1.5783e-05 | 109.0227
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CROSSARM | 9 | 2652 | 148821 | 0.026798 | 0.00047755 | 56.1165
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WU | BREAKER | 1 | 612 | 76874 | 0.013843 | 0.0001102 | 125.6111
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WL | OTHER EQUIPMENT | 1 | 1 | 183 | 3.2821e-05 | 1.7935e-07 | 183
AEP Total | 2023 | 5575683 | PARTIAL POWER | CO | SPLICE, UG | 1 | 1 | 89 | 1.5962e-05 | 1.7935e-07 | 89
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | GUY/ANCHOR | 1 | 1 | 181 | 3.2462e-05 | 1.7935e-07 | 181
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | EQF | CONN/CLAMP | 1642 | 10966 | 1207989 | 0.21512 | 0.0019528 | 110.1577
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 69 | 541 | 166919 | 0.029725 | 9.6341e-05 | 308.5379
AEP Total | 2024 | 5615460 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 315 | 315 | 48942 | 0.0087156 | 5.6095e-05 | 155.3714
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | VIN | NONE | 122 | 1126 | 147981 | 0.026983 | 0.00020532 | 131.4218
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | CROSSARM | 13 | 2788 | 391898 | 0.071459 | 0.00050837 | 140.566
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | SWITCH, OH | 1 | 2704 | 432310 | 0.078268 | 0.00048955 | 159.878
AEP Total | 2022 | 5553337 | PARTIAL POWER | U | NONE | 152 | 362 | 33767 | 0.0060805 | 6.5186e-05 | 93.279
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1207 | 6214 | 635937 | 0.11451 | 0.001119 | 102.3394
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | NONE | 2860 | 70396 | 9310091 | 1.6765 | 0.012676 | 132.2531
AEP Total | 2022 | 5553337 | PARTIAL POWER | TIR | NONE | 71 | 302 | 45201 | 0.0081394 | 5.4382e-05 | 149.6722
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 538 | 17291 | 3480475 | 0.62674 | 0.0031136 | 201.2882
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | RECLOSER, LINE/OCR/BR | 31 | 8678 | 1579483 | 0.28442 | 0.0015627 | 182.01
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 12 | 124 | 34470 | 0.0062071 | 2.2329e-05 | 277.9839
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | NONE | 177 | 35900 | 3540478 | 0.63754 | 0.0064646 | 98.6206
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | U | NONE | 33 | 22151 | 2490846 | 0.45096 | 0.0040104 | 112.4485
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERF | CONN/CLAMP | 3 | 1012 | 23590 | 0.0042709 | 0.00018322 | 23.3103
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | JUMPER/RISER | 2 | 767 | 13689 | 0.0024783 | 0.00013886 | 17.8475
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ABI | CONDUCTOR OVERHEAD | 3 | 57 | 9425 | 0.0017064 | 1.032e-05 | 165.3509
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | WU | NONE | 5 | 3289 | 399712 | 0.072366 | 0.00059546 | 121.5299
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VIN | POLE | 1 | 1 | 50 | 9.0523e-06 | 1.8105e-07 | 50
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | JUMPER/RISER | 7 | 171 | 25151 | 0.0045535 | 3.0959e-05 | 147.0819
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | SPLICE, UG | 1 | 1 | 284 | 5.1417e-05 | 1.8105e-07 | 284
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | METERING | 2 | 2 | 162 | 2.933e-05 | 3.6209e-07 | 81
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | A | TRANSFORMER, OH | 5 | 197 | 44737 | 0.0080995 | 3.5666e-05 | 227.0914
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WH | CONN/CLAMP | 1 | 1 | 43 | 7.785e-06 | 1.8105e-07 | 43
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | U | NONE | 1693 | 86725 | 5264287 | 0.9599 | 0.015814 | 60.7009
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | POLE HARDWARE | 86 | 11404 | 1256372 | 0.22909 | 0.0020794 | 110.1694
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CROSSARM | 226 | 32275 | 3839932 | 0.70018 | 0.0058851 | 118.9754
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | GUY/ANCHOR | 5 | 820 | 22485 | 0.0041 | 0.00014952 | 27.4207
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | OL | TRANSFORMER, UG | 19 | 314 | 81032 | 0.014776 | 5.7255e-05 | 258.0637
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | TOR | SPLICE, OH | 7 | 7 | 1957 | 0.0003524 | 1.2605e-06 | 279.5714
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 24 | 285 | 72283 | 0.013016 | 5.132e-05 | 253.6246
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WW | CONN/CLAMP | 5 | 9 | 2748 | 0.00049285 | 1.6142e-06 | 305.3333
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONDUCTOR OVERHEAD | 582 | 13651 | 2533446 | 0.45437 | 0.0024483 | 185.5868
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TOR | NONE | 240 | 240 | 29380 | 0.0052693 | 4.3044e-05 | 122.4167
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | ABI | NONE | 475 | 6359 | 463698 | 0.083164 | 0.0011405 | 72.92
AEP Total | 2022 | 5553337 | PARTIAL POWER | VA | NONE | 3 | 54 | 3492 | 0.00062881 | 9.7239e-06 | 64.6667
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CO | POLE | 15 | 341 | 43176 | 0.0077436 | 6.1158e-05 | 126.6158
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 11 | 4279 | 0.00077053 | 1.9808e-06 | 389
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | POLE HARDWARE | 15 | 3994 | 479132 | 0.085932 | 0.00071632 | 119.9629
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 22 | 390 | 78108 | 0.014009 | 6.9947e-05 | 200.2769
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | VA | BREAKER | 3 | 2233 | 187791 | 0.033816 | 0.0004021 | 84.0981
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | TRANSFORMER, UG | 10 | 88 | 29512 | 0.0053143 | 1.5846e-05 | 335.3636
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | TRANSFORMER, OH | 12 | 19 | 5710 | 0.0010241 | 3.4077e-06 | 300.5263
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | FUSE | 20 | 170 | 13827 | 0.0025212 | 3.0998e-05 | 81.3353
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WU | JUMPER/RISER | 11 | 57 | 8771 | 0.0015993 | 1.0393e-05 | 153.8772
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | NONE | 46 | 23539 | 2150149 | 0.39206 | 0.0042921 | 91.3441
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | PEDESTAL | 4 | 4 | 703 | 0.00012819 | 7.2937e-07 | 175.75
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | ARRESTER | 2 | 13 | 1012 | 0.00018453 | 2.3704e-06 | 77.8462
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | METERING | 4 | 4 | 308 | 5.6161e-05 | 7.2937e-07 | 77
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | ARRESTER | 6 | 20 | 2348 | 0.00042814 | 3.6468e-06 | 117.4
AEP Total | 2020 | 5484199 | PARTIAL POWER | TR | CONDUCTOR OVERHEAD | 6 | 30 | 2584 | 0.00047117 | 5.4703e-06 | 86.1333
AEP Total | 2020 | 5484199 | PARTIAL POWER | WU | TRANSFORMER, UG | 1 | 7 | 147 | 2.6804e-05 | 1.2764e-06 | 21
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | SPLICE, UG | 2 | 5 | 993 | 0.00018107 | 9.1171e-07 | 198.6
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | POLE HARDWARE | 5 | 226 | 74002 | 0.013494 | 4.1209e-05 | 327.4425
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | AF | TRANSFORMER, UG | 1 | 32 | 11968 | 0.0021823 | 5.8349e-06 | 374
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TIR | RELAY | 1 | 933 | 124089 | 0.022627 | 0.00017013 | 133
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TR | CONN/CLAMP | 2 | 2 | 320 | 5.7392e-05 | 3.587e-07 | 160
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONN/CLAMP | 1000 | 2911 | 357535 | 0.06473 | 0.00052703 | 122.8221
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | NONE | 1265 | 45574 | 4760762 | 0.86192 | 0.008251 | 104.4622
AEP Total | 2021 | 5523447 | PARTIAL POWER | CF | CUTOUT | 5 | 5 | 477 | 8.6359e-05 | 9.0523e-07 | 95.4
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | JUMPER/RISER | 70 | 4015 | 378228 | 0.068477 | 0.0007269 | 94.2037
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | NONE | 128 | 9152 | 586344 | 0.10616 | 0.0016569 | 64.0673
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | CONDUCTOR UG | 10 | 152 | 22719 | 0.0041132 | 2.7519e-05 | 149.4671
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | CUTOUT | 52 | 1600 | 259374 | 0.046959 | 0.00028967 | 162.1087
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | POLE | 11 | 225 | 122924 | 0.022255 | 4.0735e-05 | 546.3289
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WU | CONN/CLAMP | 21 | 256 | 37150 | 0.0067259 | 4.6348e-05 | 145.1172
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | POLE | 2 | 2 | 214 | 3.8744e-05 | 3.6209e-07 | 107
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | ERO | NONE | 3 | 9 | 402 | 7.2781e-05 | 1.6294e-06 | 44.6667
AEP Total | 2021 | 5523447 | PARTIAL POWER | WL | CONDUCTOR OVERHEAD | 5 | 118 | 11581 | 0.0020967 | 2.1363e-05 | 98.1441
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CONN/CLAMP | 1198 | 2670 | 323051 | 0.058487 | 0.00048339 | 120.9929
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | NONE | 4509 | 113438 | 15280518 | 2.7665 | 0.020538 | 134.7037
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TOR | CONN/CLAMP | 85 | 85 | 12100 | 0.0021907 | 1.5389e-05 | 142.3529
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 80 | 606 | 109301 | 0.019789 | 0.00010971 | 180.3647
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | INSULATOR | 89 | 13082 | 1694972 | 0.30687 | 0.0023684 | 129.5652
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CO | CONDUCTOR UG | 83 | 415 | 100270 | 0.018154 | 7.5134e-05 | 241.6145
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | CF | CONDUCTOR UG | 13 | 468 | 24302 | 0.0043998 | 8.473e-05 | 51.9274
AEP Total | 2021 | 5523447 | PARTIAL POWER | OL | NONE | 14 | 33 | 2490 | 0.00045081 | 5.9745e-06 | 75.4545
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | POLE | 9 | 4588 | 688528 | 0.12466 | 0.00083064 | 150.0715
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | PEDESTAL | 3 | 3 | 523 | 9.4687e-05 | 5.4314e-07 | 174.3333
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SPLICE, OH | 17 | 1032 | 186225 | 0.033715 | 0.00018684 | 180.4506
AEP Total | 2021 | 5523447 | PARTIAL POWER | VA | CONDUCTOR OVERHEAD | 3 | 8 | 1155 | 0.00020911 | 1.4484e-06 | 144.375
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | AF | CONDUCTOR OVERHEAD | 19 | 5459 | 877706 | 0.15891 | 0.00098833 | 160.7815
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | UB | NONE | 4 | 349 | 25561 | 0.0046277 | 6.3185e-05 | 73.2407
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | EQF | SWITCH, UG | 2 | 91 | 3305 | 0.00059836 | 1.6475e-05 | 36.3187
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | FO | CONDUCTOR OVERHEAD | 7 | 5529 | 629682 | 0.114 | 0.001001 | 113.8871
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | OL | POLE | 4 | 7 | 1723 | 0.00031194 | 1.2673e-06 | 246.1429
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | POLE | 376 | 17313 | 3897096 | 0.70176 | 0.0031176 | 225.0965
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | WL | CONN/CLAMP | 21 | 235 | 69202 | 0.012461 | 4.2317e-05 | 294.4766
AEP Total | 2022 | 5553337 | PARTIAL POWER | EQF | CONDUCTOR UG | 68 | 201 | 52052 | 0.0093731 | 3.6194e-05 | 258.9652
AEP Total | 2022 | 5553337 | PARTIAL POWER | CF | NONE | 13 | 31 | 2649 | 0.00047701 | 5.5822e-06 | 85.4516
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | EQF | PEDESTAL | 24 | 143 | 19691 | 0.0035458 | 2.575e-05 | 137.6993
AEP Total | 2022 | 5553337 | DISTRIBUTION STATION | EQF | BREAKER | 39 | 34823 | 3541105 | 0.63765 | 0.0062706 | 101.6887
AEP Total | 2022 | 5553337 | PARTIAL POWER | A | NONE | 53 | 132 | 17856 | 0.0032154 | 2.3769e-05 | 135.2727
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | AF | RELAY | 3 | 1654 | 34798 | 0.0063001 | 0.00029945 | 21.0387
AEP Total | 2021 | 5523447 | PARTIAL POWER | EQF | CABLE TERMINATOR | 6 | 10 | 1469 | 0.00026596 | 1.8105e-06 | 146.9
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | VA | OTHER EQUIPMENT | 2 | 16 | 2464 | 0.0004461 | 2.8967e-06 | 154
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | FUSE | 1 | 7 | 147 | 2.6614e-05 | 1.2673e-06 | 21
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | TIR | TRANSFORMER, GROUNDING | 1 | 7 | 1827 | 0.00033077 | 1.2673e-06 | 261
AEP Total | 2021 | 5523447 | DISTRIBUTION STATION | EQF | CIRCUIT SWITCHER | 8 | 5598 | 418173 | 0.075709 | 0.0010135 | 74.7004
AEP Total | 2021 | 5523447 | DISTRIBUTION LINE | WL | REGULATOR | 1 | 15 | 1965 | 0.00035576 | 2.7157e-06 | 131
AEP Total | 2021 | 5523447 | PARTIAL POWER | WU | POLE | 1 | 1 | 13 | 2.3536e-06 | 1.8105e-07 | 13
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | TRANSFORMER, OH | 1814 | 10414 | 2040376 | 0.37205 | 0.0018989 | 195.9263
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | ABI | NONE | 713 | 6427 | 457518 | 0.083425 | 0.0011719 | 71.1869
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | TOR | CONDUCTOR OVERHEAD | 431 | 431 | 67485 | 0.012305 | 7.8589e-05 | 156.5777
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | BREAKER | 3 | 2359 | 561578 | 0.1024 | 0.00043014 | 238.0577
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | CO | TRANSFORMER, UG | 19 | 118 | 18073 | 0.0032955 | 2.1516e-05 | 153.161
AEP Total | 2020 | 5484199 | PARTIAL POWER | EQF | JUMPER/RISER | 32 | 448 | 43083 | 0.0078558 | 8.1689e-05 | 96.1674
AEP Total | 2020 | 5484199 | PARTIAL POWER | CO | NONE | 35 | 209 | 51745 | 0.0094353 | 3.8109e-05 | 247.5837
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | EQF | CABLE TERMINATOR | 24 | 543 | 184155 | 0.033579 | 9.9012e-05 | 339.1436
AEP Total | 2020 | 5484199 | DISTRIBUTION LINE | WI | JUMPER/RISER | 1 | 4 | 1120 | 0.00020422 | 7.2937e-07 | 280
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | VA | POLE | 291 | 59931 | 9223239 | 1.6542 | 0.010749 | 153.8976
AEP Total | 2023 | 5575683 | PARTIAL POWER | TIR | CONN/CLAMP | 56 | 173 | 21295 | 0.0038193 | 3.1028e-05 | 123.0925
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | TIR | CONN/CLAMP | 79 | 376 | 55534 | 0.00996 | 6.7436e-05 | 147.6968
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | ERF | JUMPER/RISER | 1 | 599 | 15269 | 0.0027495 | 0.00010786 | 25.4908
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | CF | ARRESTER | 27 | 488 | 41489 | 0.0074411 | 8.7523e-05 | 85.0184
AEP Total | 2022 | 5553337 | DISTRIBUTION LINE | CO | PEDESTAL | 6 | 28 | 7284 | 0.0013116 | 5.042e-06 | 260.1429
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR OVERHEAD | 89 | 6651 | 1266231 | 0.2271 | 0.0011929 | 190.382
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | EQF | PEDESTAL | 19 | 73 | 13404 | 0.002404 | 1.3093e-05 | 183.6164
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | TRANSFORMER, OH | 24 | 116 | 19378 | 0.0034754 | 2.0805e-05 | 167.0517
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | A | ARRESTER | 18 | 412 | 24002 | 0.0043048 | 7.3892e-05 | 58.2573
AEP Total | 2023 | 5575683 | DISTRIBUTION LINE | WU | CONDUCTOR UG | 2 | 3 | 40 | 7.174e-06 | 5.3805e-07 | 13.3333

## Count of Failures by Year
Operating Unit Abbreviation | AEP-KYP
Major Cause Name | (Multiple Items)
Count of Equipment Name | Column Labels
Row Labels | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Grand Total
ARRESTER | 12 | 12 | 9 | 9 | 8 | 7 | 57
BREAKER | 3 | 1 | 2 | 1 | 1 |  | 8
CABLE TERMINATOR | 1 | 1 | 2 | 3 | 1 |  | 8
CIRCUIT SWITCHER | 3 | [5 empty] | 3
CONDUCTOR OVERHEAD | 33 | 37 | 39 | 34 | 32 | 25 | 200
CONDUCTOR UG | 12 | 15 | 12 | 7 | 14 | 6 | 66
CONN/CLAMP | 15 | 18 | 19 | 18 | 18 | 9 | 97
CROSSARM | 11 | 7 | 10 | 5 | 9 | 8 | 50
CUTOUT | 17 | 19 | 17 | 15 | 17 | 10 | 95
FUSE | 33 | 41 | 39 | 30 | 34 | 25 | 202
GUY/ANCHOR | 7 | 6 | 6 | 6 | 7 | 5 | 37
INSULATOR | 9 | 6 | 6 | 8 | 8 | 5 | 42
JUMPER/RISER | 4 | 3 | 6 | 7 | 2 | 4 | 26
METERING | 11 | 11 | 8 | 7 | 7 | 6 | 50
MOAB |  |  |  | 1 |  |  | 1
NONE | 40 | 35 | 36 | 34 | 35 | 28 | 208
OTHER EQUIPMENT | 11 | 8 | 9 | 5 | 6 | 4 | 43
PEDESTAL | 1 | 2 | 4 | 1 | 3 | 1 | 12
POLE | 16 | 20 | 22 | 19 | 19 | 13 | 109
POLE HARDWARE | 4 | 4 | 5 | 4 | 3 | 3 | 23
RECLOSER, LINE/OCR/BR | 4 | 9 | 9 | 5 | 5 | 4 | 36
REGULATOR | 3 | 4 | 3 | 4 | 3 | 1 | 18
RELAY | 2 | [5 empty] | 2
SECTIONALIZER | 1 | 4 | 2 |  | 2 |  | 9
SPLICE, OH | 6 | 12 | 13 | 10 | 10 | 4 | 55
SPLICE, UG | 1 | 1 |  | 1 | 1 | 1 | 5
STATIC WIRE |  |  | 1 |  |  | 1 | 2
SWITCH, OH | 5 | 4 | 4 | 4 | 4 | 1 | 22
TRANSFORMER, GROUNDING | 1 | 1 |  | 1 | 1 |  | 4
TRANSFORMER, OH | 15 | 14 | 19 | 15 | 17 | 10 | 90
TRANSFORMER, POWER - LTC |  | 1 | 2 |  | 1 | 1 | 5
TRANSFORMER, STATION SERVICE |  | 1 |  | 1 |  | 1 | 3
TRANSFORMER, UG | 3 | 4 | 5 | 5 | 2 | 1 | 20
Grand Total | 284 | 301 | 309 | 260 | 270 | 184 | 1608

## CMI by Equipment Failed
Operating Unit Abbreviation | AEP-KYP
Major Cause Name | (Multiple Items)
Minor Cause Code | EQF
Sum of CMI | Column Labels
Row Labels | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Grand Total
ARRESTER | 2125857 | 832512 | 38575 | 743748 | 678908 | 174089 | 4593689
BREAKER | 5760 |  | 1071661 |  | 87561 |  | 1164982
CABLE TERMINATOR |  | 456 | 15478 | 282 | 94 |  | 16310
CAPACITOR |  | 13884 |  |  |  |  | 13884
CIRCUIT SWITCHER | 140766 | 57 |  |  |  |  | 140823
CONDUCTOR OVERHEAD | 2611522 | 622877 | 1565594 | 526269 | 815014 | 1594727 | 7736003
CONDUCTOR UG | 44643 | 119099 | 357051 | 61743 | 74348 | 64331 | 721215
CONN/CLAMP | 651464 | 925459 | 1111618 | 434377 | 1094207 | 384191 | 4601316
CROSSARM | 864042 | 763591 | 1292497 | 951503 | 522427 | 354064 | 4748124
CUTOUT | 1769482 | 2290386 | 1849019 | 1688497 | 2139446 | 441880 | 10178710
FUSE | 158952 | 97791 | 149699 | 97065 | 155026 | 82075 | 740608
GUY/ANCHOR | 9174 | 1564 | 1060 | 3295 | 137988 | 6413 | 159494
INSULATOR | 2008072 | 1430600 | 4600384 | 1317580 | 1998643 | 1383378 | 12738657
JUMPER/RISER | 299840 | 69713 | 818751 | 136681 | 131500 | 13100 | 1469585
METERING | 11591 | 555 | 5556 | 1049 | 52152 | 312 | 71215
MOAB | 1469 | [5 empty] | 1469
OTHER EQUIPMENT | 40642 | 19769 | 180809 | 33324 | 421951 | 705746 | 1402241
PEDESTAL |  |  | 99 | 216 |  |  | 315
POLE | 1025075 | 1442643 | 2014537 | 508770 | 329096 | 287960 | 5608081
POLE HARDWARE | 295652 | 54826 | 42749 | 630 | 66978 | 52664 | 513499
RECLOSER, LINE/OCR/BR | 340570 | 135007 | 725198 |  | 650816 | 95529 | 1947120
REGULATOR | 218479 | 66160 | 225246 | 478992 | 102642 | 429 | 1091948
RELAY | 644255 | [5 empty] | 644255
SECTIONALIZER |  |  | 82701 |  |  |  | 82701
SPLICE, OH | 96348 | 64108 | 1091774 | 45602 | 107289 | 45673 | 1450794
SPLICE, UG | 6349 |  |  | 1328 | 523 | 429 | 8629
STATIC WIRE | 33128 |  | 3849 |  |  | 50180 | 87157
SWITCH, OH | 185286 | 373149 | 31367 | 191586 | 83262 | 59904 | 924554
TRANSFORMER, GROUNDING |  | 462 |  | 1068 | 1773 |  | 3303
TRANSFORMER, OH | 404189 | 295327 | 365717 | 241078 | 386911 | 221626 | 1914848
TRANSFORMER, POWER - LTC |  | 641170 | 484 |  | 1230 | 4674 | 647558
TRANSFORMER, STATION SERVICE | 362814 | 1502922 |  | 226569 |  |  | 2092305
TRANSFORMER, UG | 20154 | 38796 | 3364 | 3804 | 4744 | 6281 | 77143
Grand Total | 14375575 | 11802883 | 17644837 | 7695056 | 10044529 | 6029655 | 67592535

## 2008-2022
Row number | Area Name | GIS Circuit ID | Substation Name | Circuit Name | Outage Start Date and Time | Outage End Date and Time | CI | Total Outage Duration | Outage Number | CMI | Major Cause Name | Minor Cause Name | Equipment Name | Crew Work Required
1 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-01-01 05:24 | 2022-01-02 11:10 | 963 | 1786 | 4243181 | 1699168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1172704/ reclr 1081-300 is open,is toggling between open&closed might be an electronics issue/ have notified mtr electrician/ tried to close locally,but it wouldnt close/ Cannot access switching points @ this time due to flood waters/closed N.O. 1057-D-307 at 2120 restoring 25cc/Saw flash when test energizing/area is flooded and unable to isolate/will have to hold until water recedes in the morning/
2 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2021-03-04 05:33 | 2021-03-05 13:47 | 1251 | 1934 | 4300681 | 1502922 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | SDB / 0905 / Station de-energized due to suspected issue with station transf. Station crews are onsite performing tests. Looking at possible load transfers.--- sdb/ 1800 / Falied Station TR, mobile TR required. Crews on site installing Mobile TR
3 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-07-27 08:14 | 2020-07-28 04:09 | 1537 | 1195 | 4236161 | 1038144 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | Failed Station Transformer crews enroute/Some customers will be on before 2359// /// **** I DIDNT COMPLETE RESTORATION OF THIS OUTAGE ONLY CLOSED THE OUTAGE AFTER SHIFT CHANGE , NOT SURE ABOUT CAUSE CODES OR TIMES ON/OFF. ALAN JORDAN ****
4 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-07-07 02:21 | 2013-07-07 22:04 | 841 | 1183 | 4477481 | 994903 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | COLEMAN-SPRIGG 69KV LINE LO // 69 CONDUCTOR DOWN T-LINE CREWS TO MAKE REPAIRS - TRANSFER CUSTOMERS TO ALT SOURCES WHERE AVAILABLE. ** UPDATE MULTIPLE T- LINE CREWS AND HEAVY CRANE ENROUTE TO ASSIST. . *** UPDATE TIME TO 2000 *******SA FAILED AT BARREHSHE, UPDATED FETR TO 2330 IDC XXXX
5 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-05-03 16:20 | 2008-05-04 03:31 | 1786 | 671 | 56767-1 | 962426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801//CREW REQUIRED ALSO TECH BURNT OFF POLECREW REQUIRED ALSO TECH BURNT OFF POLE //CREW ON SITE/FETR 0100 5-04-08/VEM/ SLOW GOING DIGGING HOLE IN ROCK TO REPLACE POLE/REPLACED POLE AND CLOSED CKT BREAKER AT 0116 3 PHASE TAP STILL OPEN TOWARDS POLE 269-304 CLOSED AT 0331 AND ALL CUSTOMERS RESTORED //VER-GAH IDC XXXX DEB OK
6 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2022-07-31 15:53 | 2022-08-03 19:58 | 210 | 4565 | 4643921 | 932742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Phases B & C reclosers open at pole 151-252 / 50T fuse blown at pole 151-56 / Pri. & Neut. down between pole 151-228 & 151A4-291 / Phase B pri. down between pole 151-35 & 151-262 / No truck access / I cant get to see two spans of overhead primary between pole 151-235 & 151-237 due to tree down across drive Released by crew 042M03 Reclosers on 151-252 back in @ 15:38. Line fuse on 151-56 back in @ 17:51. All power restored, ticket can be closed.
7 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-08-03 07:26 | 2016-08-03 21:55 | 1839 | 869 | 4726741 | 843443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CAUSE UNKNOWN VER/ARN //// ADDED STEPS TO THIS ORDER FROM 4727491 = SEE 4731021 FOR DROP & PICK OUTAGE TO RETURN TO NORMAL (112 CUST) L3/HFP HFPC STP AJB
8 | South Williamson | 3411401 | DEWEY | INEZ | 2014-04-03 17:24 | 2014-04-03 22:32 | 2981 | 308 | 4567981 | 815565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FAILED INSULATOR ON THE STEEL ON EXIT SPAN/CREWS ENROUTE TO REPAIRRELEASED BY CREW 074S03/ADJUSTED CUSTOMER COUNTS ON 4-4-14 AFTER CIRCUIT WAS NORMAL VER/KEP IDC XXXX
9 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-14 15:33 | 2008-12-14 23:18 | 3487 | 465 | 58325-1 | 796473 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// OPENED LOOPS AT 205-223 // AT 1719 CLOSED FEEDER CB - RESTORED 2298 @ 2115 UPDATED FETR . TO 0030 DUE TO UNEXPECTED PROBLEMS *** JAMES GILLEY NOW IN CHARGE OF THIS JOB. .. 3308401// OPENED LOOPS AT 205-223 // AT 1719 CLOSED FEEDER CB - RESTORED 2298 @ 2115 UPDATED FETR . TO 0030 DUE TO UNEXPECTED PROBLEMS JAMES GILLEY NOW IN CHARGE OF THIS JOB. .. RELEASED BY CREW 077S01 VER/PDP IDC XXXX
10 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-06-06 19:15 | 2020-06-07 15:47 | 724 | 1232 | 4971731 | 795398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 37830246B00009 top rotted off. opened switches on pole 37830270A00439 and closed rec on pole 37830270D00183 at 21:17. manual pole. need 2 line crews, row crew and tech Released by crew 077S10 closed sws at 1547
11 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-01-05 09:47 | 2010-01-06 00:07 | 923 | 860 | 61082-1 | 779512 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | TRANSMISSION LINE OUTAGE TRANSMISSION & DISTRIBUTION DISPATCH CENTERS ARE WORKING TO ISOLATE & SECTIONALIZE TRANSMISSION LINES IN TROUBLE WILL AIR PATROL AS WEATHER PERMITS. CREWS IN AREA PATROLLING BY FOOT. FIELD ETR IS APPROX MIDNIGHT TONIGHT. // HAVE TRANSMISSION LINE REPAIRED// WILL BEGIN ENERGIZING STATION// WILL PICK UP CUSTOMERS SECTIONS TO AVOID TRIPPING OUT DUE TO COLD LOAD// FETR FOR LAST CUSTOMER IF ALL STEPS HOLD VER/ARN IDC STEP AT 103-210 XXXX
12 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-07-15 01:59 | 2016-07-15 10:05 | 1571 | 486 | 4639041 | 748920 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | OPENED 34KV CB S VIA SCADA @ 0159 TO REMOVE LOAD FROM SWITCH INSIDE SUBSTATION WHICH IS ARCING//COD 1571///THIS IS THE ORDER FOR THE BREAKER GOING OUT AND PART OF THIS CKT WAS RESTORED (221 CUSTS) BY CLOSING THE N.O. TIE SWS BETWEEN IT AND LESLIE0WOOTEN 34JV CKT ON POLE 318-B-282 AFTER OPENING THE RECLOSER ON POLE 270-D-61//// VER/DKM AJB PER DISP LOG.
13 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-07-31 20:02 | 2022-08-01 21:55 | 469 | 1553 | 4653771 | 728357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WATER OVER ROAD//WILL TRY TO PATROL THIS AFTERNOON//loops burnt open on poles 40-8 and 41-61//opened sec. on pole 40-23@20:40 closed at 21:55 Released by crew 074H07
14 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-09-12 04:54 | 2015-09-12 11:51 | 1718 | 417 | 4230391 | 716406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW ON SITE MAKING REPAIRSRELEASED BY CREW 074H21 VER/ARN // VER TIMES PER SCADA & DISPATCH LOG L3/HFP HFPXXX AJB
15 | Hazard | 3310502 | HADDIX | CANOE | 2022-08-02 19:54 | 2022-08-06 19:00 | 356 | 5706 | 4665931 | 693304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Created ticket so Three phase pole 145-112 that's tied off with a rope does not get forgot about, per luke mccoy, no outage, dig sent 8/4/22 2208041863 jlb
16 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-07-13 06:32 | 2012-07-13 15:09 | 1332 | 517 | 4709581 | 687500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICERS AND CREW PATROLLING MAY HAVE FOUND BAD INSULATOR// FOUND 2 PHASES OFF PINS AND BLOWN INSULATORS// CREW ON SITE -DIFFICULT LOCATION/// AFTER CHECKING HAVE FOUND ADDITIONAL LINE DAMAGE - FETR 1530 - DKG/VERIFIED OUTAGE WITH LARRY IDC XXXX
17 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-12-07 09:02 | 2011-12-07 14:14 | 2156 | 312 | 4147441 | 672672 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONDUCTOR UG | 138 KV TR 1 LOCKED OUT AT JOHNS CREEK , STATION SERVICER DISPATCHED TO CHECK. 2156 CC. ON META CKT /// UNDERGROUND CABLE AT STATION FAULTED - LOOKING AT LOAD TRANSFER /// COD-2156 IDCC TOF0904 XXXX
18 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-04-20 23:57 | 2010-04-21 06:08 | 2165 | 371 | 65784-1 | 671631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SWITCH LINE FEED FROM BEAVER CR STATION 45-25 TO POLE 1125-619 RECLOSER POLE/POLE 1101-282 INSULATOR BROKE AND POLE BURNT OFF/SWITCH LINE FEED FROM BEAVER CR STATION 45-25 TO POLE 1125-619 RECLOSER POLE. TOP OF POLE BURNT OFF 1101-282 IDCC FEC60 XXXX
19 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-05-10 10:31 | 2015-05-11 03:44 | 912 | 1033 | 4407911 | 660129 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | SCADA INDICATED 69-12KV TR 1 @ SOUTH PIKEVILLE DE-ENERGIZED. THIS HAS STATION INTERRUPTED AND APPROX 1786 PIKEVILLE AREA CUSTOMERS// STATION SERVICER AND D-LINE SERVICER CALLED IN//TOM WILL UPDATE AS INFORMATION BECOMES AVAILABLE//TOM ***UPDATE @ 1135 DETERMINED STATION TRANSFOMER LTC HAS FAILED - LOOKING AT LOAD TRANSFER OPPORTUNITIES AND WILL NEED A MOBILE TRANSFOMER INSTALLED // EXTENDED OUTAGE DUE TO MOBIL TRIPPING OUT 6 MIN AFTER 2ND REST STEP - TIMES PER LOG & SOS3065 REV77 VER/HFP L3/HFP
20 | Hazard | 3310502 | HADDIX | CANOE | 2010-06-16 19:07 | 2010-06-17 05:57 | 1223 | 650 | 66562-1 | 609150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | WR# 35603156 / POLE 51-42 HAS BROKEN CROSSARMS/ @1958 OPEN 52-108 / @2045 OPEN SW 121-A-152 / @2104 CLOSE SW 169-305 /RELEASED BY CREW 077S05///RELOCATED LINE OFF HILL SIDE PUT BESIDE ROAD, RESTORE POWER AT 5:57 AM @ 0635 OPEN N.O. 296 CC H1138560-1 CREATED TO SHOW THIS OUTAGE ALL CUST REST AT 0730 VER/PDP
21 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2021-10-07 11:42 | 2021-10-08 02:05 | 1263 | 863 | 4327131 | 592090 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | 69/12kV TR 1 tripped from service due to failed bushing at station Emergency mobile TR being installed FETR 0100 10/8/21
22 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-08-14 09:38 | 2015-08-14 21:36 | 846 | 718 | 4134221 | 587447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SERVICER PATROLING LINE//CREW REQUIRED POLE 126-126 ROTTED AND FELL OVER WE NEED A 45-4 2 8 ARMS WITH 6 ANGLE PINS AND INSULATORS, 2 SETS OF BIG WOOD BRACES, AND A GUY ASSEMBLY WITH ANCHOR. TIM HALL IS CALLING OUT SOME ELLIOTT CREWS WHO WILL BE DOING THE REPAIRS. VER/SEF // VER TIMES PER DOL - EXTENDED THIS OUTAGE DUE TO RECL ON POLE 37820126000123 NOT PICKING UP WHEN CB CLOSED IN ORDER 4136321 L3/HFP AJB
23 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-05-06 03:26 | 2010-05-06 10:15 | 1401 | 409 | 56280-1 | 573009 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | TRANSMISSION OUTAGE / PATROLLING BY HELICOPTER / OUTAGE FROM 1916-1924 RETURNING CKTS NORMAL. IDC XXXX
24 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-07-16 13:29 | 2021-07-16 17:16 | 2523 | 227 | 4920281 | 572721 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 1132373/ top of pole 217-203 broke out and top set of arms laid over////Crew is onsight lowering arms///Lowererd arms and re-sagged conductors///Repairs made Restored breaker @ 17:16
25 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-04-04 04:02 | 2014-04-04 16:05 | 883 | 723 | 4571461 | 548478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE#448-C3-114 BURNT/ISOLATED 448-530 CLOSED CB AT 0602/FBR LOCKED OUT , BAD INSULATOR ON POLE 448-114, CUT LOOPS ON POLE 448-530 & PLACED TAGS FOR DDC.FBR LOCKED OUT , BAD INSULATOR ON POLE 448-114 POLE BURNT OFF, CUT LOOPS ON POLE 448-530 & PLACED TAGS FOR DDC. RELEASED BY CREW 077S11 SEE DDC LOG // //VER/GAH IDC XXXX
26 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-02-15 05:48 | 2014-02-15 16:47 | 842 | 659 | 4389081 | 543478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1089-C-425 BURNT OFF DUE TO FAILED CUTOUT // HOLD ORDER REQUIRED FROM DDC TO MAKE REPAIRS //EXTENDED FETR DUE TO AWP FLAGGING CREW GETTING LOST // DUE TO COLD LOAD PICKUP OPENED RECL POLE 1090-D-169 // CLOSED STA BREAKER AT 1607 // CLOSED RECL POLE 1090-D-169 @ 1647 RELEASED BY CREW 079S02 VER/HFP L3/HFP IDC XXXX
27 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-06-02 22:15 | 2019-06-03 02:17 | 2539 | 242 | 4417051 | 539148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER DOL 927116/ LOOKS LIKE BAD INSULATOR ON POLE 197-167/// OPENED SWITCHES ON POLE 193-163 TO ISOLATE TROUBLE AND GET BREAKER BACK IN// WILL NEED CREW/ ¦¦¦ VERIFIED TIMES PER DOL L3/HFP
28 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-11-30 03:00 | 2022-11-30 06:37 | 2480 | 217 | 4204281 | 538160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER/ DOL 1255356/ Bad dead-end insulator on pole 193-30///Will need line crew ,and other help to switch/ Opened HenryClay - Regina 34kV CB A @ 0605/ Closed HenryClay - Regina 34kV CB A @ 0637 LR- 1st all out call came in at 0300
29 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-04-29 21:22 | 2021-04-30 00:53 | 2527 | 211 | 4498501 | 533197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1111881//POR INDICATED CB OUTAGE/CREWS EN ROUTEHenry Clay -Regina breaker is locked out//willbe checking//Crew found issue and making repairs/Hold Order issued//Henry Clay -Regina breaker is locked out//willbe checking///Bad 19.9 deadened insulator on pole193-26///Crew enroute to make repairsHenry Clay -Regina breaker is locked out//willbe checking///Bad 19.9 deadened insulator on pole193-26///Crew enroute to make repairs///Changed 6 deadend insulators and cutout on pole 193-26 and closed b
30 | Hazard | 3310502 | HADDIX | CANOE | 2008-01-25 02:49 | 2008-01-25 13:09 | 1234 | 620 | 59575-1 | 533027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3310502// COD-1235 // TOP OF POLE BROKE OFF // WILL LOWER LINE ON POLE & REPLACE CROSSARM//3310502 RELEASED BY CREW 077S05 VER/LDA DEBBIE/149 CUST OFF AGAIN ON ORDER 59575-1H...245 CUST OFF AGAIN ON ORDER 59575-1HA IDC XXXX
31 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-07-27 21:01 | 2008-07-28 06:00 | 1122 | 539 | 60909-1 | 524287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3310501/// POLE NUMBER 4..36 BROKE ALL POWER RESTORYED TO NORMAL AT 06.00 IDCC CNT2063, TON XXXX
32 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-03-31 02:45 | 2010-03-31 07:40 | 1717 | 295 | 56286-1 | 506515 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | MOBILE CS6 TRIPPED OUT@HAYWARD -STATION OUTAGE, SERVICERS DISP. CAUSE UNKNOWN@ THIS TIME, WILL UPDATE ASAP.@0400 , SERVICER @STATION REPORTS MOBILE CB TRIPPED OUT,ISOLATING EQUIPMENT&IF NO PROBLEMS ARE FOUND MOBILE CB CAN BE RESTORED.@0446 , ATTEMPTED TO CL MOBILE CB TRIPPED BACK OUT. 0520 , STATION CREW REPORTS PROBLEMS WITH MOBILE CB, PLAN NOW TO PLACE STATION TR BACK IN SERVICE.RELEASED BY AJBC TON06:26 FEC57 WIRE IN FAN ON XFR CAUSED MOBILE CB TO LO.
33 | Hazard | 3303902 | LESLIE | WOOTON | 2022-11-15 03:28 | 2022-11-15 10:19 | 1349 | 411 | 4143141 | 502647 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | DOL 1252142 // station outage // high side ckt swroperated to l/o at 0328 // cod 1424 //
34 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-03-29 08:26 | 2020-03-29 11:50 | 2484 | 204 | 4521641 | 500993 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | Station Outage Off @ 0826 On at 1135 //// 193-390 on @ 1146 742 customers //// 194-115 on @ 1149 420 customers //// 194-33 on @ 1150 1198 customers
35 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-07-14 07:46 | 2013-07-14 20:28 | 1905 | 762 | 4520971 | 498366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 205-117 HAS BURNT OFF AT LOWER SET OF ARMS, CALLING FOR HELP /// COLLETT, MARSHALL --- SDB / 1004 / LOOPS CUT AT POLE 206-B-47 & CB CLOSED REST 174 CC. -- SDB / 1034 / LOOPS CUT AT POLE 181-D-28, TIE SW AT POLE 181-D-401 CLOSED, REST 1422 CC. ** UPDATE AT 1926 - CREWS OUTAGED CUST TO MAKE UP LOOPS PRIOR TO TOTAL RESTORE OF CUSTOMERS AND RESTORE CKTS NORMAL.POLE 205-117 HAS BURNT OFF AT LOWER SET OF ARMS, CALLING FOR HELP. ALL POWER RESTORED EXCEPT SECONDARY ON POLE 117 AT 20:28 **** IDC XXXX
36 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-19 20:24 | 2015-02-20 14:58 | 785 | 1114 | 4044661 | 479600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PATROLLED LINE TO SW 720-91 AND OPENED. CLOSED REC 744-311 @ 22:44 RESTORING UP TO OPEN SW. PATROLLING NEXT SECTION. CLOSED SW ON 720-91 @ 2:50 RESTORING TO OPEN SW ON 673-10. PRI DOWN ON 672-259. CLOSED SW 673-10 @ 3:23 RESTORING TO OPEN REC 649-202. ISOLATED HOTLINE CLAMP ON 672-5 AND PLACED TEMP GROUND ON PRIMARY TOWARD FAULT. TAG PLACED TO DDC. RELEASED BY CREW 076S02/ 854 73 CUSTOMERS/ 920 75 CUSTOMERS AJB
37 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-01-21 04:55 | 2012-01-21 10:40 | 1532 | 345 | 4279271 | 476862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATED BIG CREEK 34KV CKT LOCKED OUT//----- PATROLLING LINE--- BAD INSULATORS ON POLE 37830271A00167 -- OPENED GOAB ON POLE 37830271A00168 RELEASED BY CREW 077S04 // 1040 - CLOSE GOAB 271-A-168 RESTORING ALL CUSTOMERS //VER/GAH IDC XXXX
38 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-06-10 20:39 | 2020-06-11 13:14 | 766 | 995 | 4994731 | 470045 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | fault @ 1099-90. open intelleropter @ 1099-6965 & tagged to ddc. open 3 600a disc @ 1099-68 & ddc tag. hold order to mphelps. Released by crew 078S07 sjg related to 90110811, 90110813
39 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-01-01 06:08 | 2011-01-01 13:27 | 1071 | 439 | 57494-1 | 467024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICER PATROLLING, TRIED BREAKER VIA SCADA DID NOT HOLD, ADDITIONAL CREWS ENROUTE TO ASSIST PATROLLING// SERVICERS FOUND BAD EPOXILATOR AT POLE 413-67 // CREW REPLACING EPOXILATORS // LAST CUSTOMERS RESTORED AT 1327 VER/TOM IDCC TOF610 XXXX
40 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-05-15 10:16 | 2014-05-15 14:54 | 1756 | 278 | 4707651 | 466198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3401002// HOLD ORDER NEEDED FROM DDC SW DESK// SCADA INDICATED CKT LOCKED OUT //CC1756 BAD INSULATOR CREW ENROUTE. / DEFECTIVE INSULATOR AT POLE 215-A-194 / OPENED/TAGGED SWS AT POLE 214-C-37 TAGGED TO KYDDC AND CLOSED CB AT 1205 RESTORING 130 CUSTS / 1626 CUSTS REMAIN OUT / CREW NEAR JOB WAITING ON FLAGGERS , WILL TAKE LESS THAN 15 MIN TO MAKE REPAIRS.3401002// // MADE REPAIRS AND CLOSED SWITCHES IN AT 14:54 TIM MCCOY PSC REPORT SUBMITTED. AT 1416. VER/HFP L3/HFP IDC XXXX
41 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-02-03 19:36 | 2022-02-03 22:39 | 2562 | 183 | 4431361 | 465684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1180725 // POR predicts feeder L/O @ 1936 / cod 2511 //circuit breake open will patrolcircuit breaker open will patrol///Insulator bad on pole 193-30///Opened switches on pole 193-163 to isolate trouble///Crew enroute//Changed bad insulator on pole 193-30///Closed breaker in @ 22:39//
42 | Hazard | 3310502 | HADDIX | CANOE | 2014-10-20 02:26 | 2014-10-20 21:38 | 617 | 1152 | 4645181 | 463855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW ONSITE PATROLLING HEAVY FOG/ BROKEN POLE#73-23/POLE # 73-23 BROKE OPEN SWITCHES ON POLE 73-197 , GOT RECLOSER ON POLE 51-58 CLOSED AT 0839 // @ 2100 CREW IN PROCESS OF RESTORING CUSTOMERS//TOMCREW ONSITE PATROLLING HEAVY FOG/ BROKEN POLE#73-23/POLE # 73-23 BROKE OPEN SW ON POLE 73-197 , GOT RECLOSER ON POLE 51-58 CLOSED AT 0839 CLOSED SWITCHES ON P#73/197 AT 2122// SEE DUP H4645181 FOR 274 CUST //VERIFIED VIA LOG & SCADA // VER/HFP L3/HFP SEE HA4645181 FOR MOME PAR ALSO SEE H4645181 2NDMOME AJB
43 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-03-02 06:46 | 2010-03-02 11:40 | 1844 | 294 | 62082-1 | 458703 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | PATROLING LINE/PARTIAL RESTORED / FAILED LINE REGULATOR AND FAILED LINE SIDE DISCONNECT /SEE ALSO 62126 ALL CUSTOMERS RESTORED 1140 VER/KEP L3/KEP IDC XXXX
44 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-04-20 09:17 | 2019-04-20 14:35 | 1983 | 318 | 4139921 | 448710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | servicer and foreman enroute //Rec. open @1083-B-145, checking.//cod 1983// Isolated trouble with 3 cutouts @1082-98, closed rec. back in @1303, will be making repairs. Got all 3 cutouts changed and back in @1435. Released by crew 074S05 L3/HFP
45 | South Williamson | 3411401 | DEWEY | INEZ | 2019-10-06 09:33 | 2019-10-06 13:57 | 2565 | 264 | 4100171 | 436159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | DOL 960244///Phase off pin and layin on crossarm at pole 38830791C09001///DA scheme not available due to RTU's that are down///Phase on arm crew inroute to replace.. Released by crew 076H06 ¦¦¦¦ OUTAGE EXTENT WOULD HAVE BEEN LESS IF RTU'S WERE NOT DOWN = L3/HFP
46 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-09-05 18:41 | 2022-09-06 05:52 | 722 | 671 | 4842091 | 435614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DDC TAGS/DOL CASE # 1235605//OPENED SWITCHES ON POLE 38820771B20089 ( NOT SHOWN ON MAP) CLOSED RECLOSER 38820771A40412 @ 2024//broken crossarm on pole 38820794C00005//found tree on pole 38820794C00009 after making repairs to broke xarm // calling for tree crew // tree crew unable to get a bucket to the tree, will work manually, moved ETR to 0800 //
47 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-08-04 00:26 | 2008-08-04 08:19 | 996 | 473 | 64790-1 | 435299 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | STATION TRANSFORMER FAULTED AND CREWS ARE WORKING TO RESTORE CUSTOMERS VER/DKG CUST TRANSFERRED TO BECKHAM CARR VIA COLLIER UPPER ROCKHOUSE AND VICCO RED FOX CIRCUITS....THIS COUNT ALSO DOES NOT INCLUDE 2 PRIMARY METERING LOCATIONS ON ORDERS 64896 AND 64894 WHICH REMAINS OFF UNTIL MOBILE IS INSTALLED IDC XXXX
48 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-05-08 01:52 | 2011-05-08 12:24 | 1508 | 632 | 4018181 | 426314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | POLE FIRE // PAINTSVILLE/CITY 12KV CKT LOCKED OUT // SERVICER ENROUTE TO STATION// WILL NEED LINE CREW AND FLAGGERS // APPEARS THAT TEMPORARY SAFETY COVERS CAUGHT FIRE DUE TO HEAVY RAINS. CREW ENROUTE TO ASSIST./ //VER/GAH MAF IDC XXXX
49 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-06-07 11:27 | 2015-06-07 23:48 | 789 | 741 | 4520571 | 419957 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SCADA INDICATED THE UNIVERSITY OF KY 12KV CB A OPERATED TO LOCKOUT// CREWS REPORTING BROKEN POLE, 3 TRANSFORMERS ON GROUND, BROKEN CONDUCTOR// FORESTRY CREW REQUESTED// TOM FETR SET TO 2300, WILL UPATE IF NEEDED AS PROGRESS CONTINUES//TOMSCADA INDICATED THE UNIVERSITY OF KY 12KV CB A OPERATED TO LOCKOUT//ARCOSING SERVICER//TOM CREWS ENROUTE TO REPAIR. CREWS WORKING TO REPAIR.//RESTORED ALL BUT 1 CUSTOMER @ 2019// VER/DBM L3/HFP HFP AJB
50 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-08-05 11:42 | 2022-08-05 18:41 | 994 | 419 | 4684091 | 416486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Opened CB to allow crews to safely close OCRs at 3783-0004-C0-0277 (Order4680521) Outage should last 5 mins from start Off at 1825 On at 1841 LR- It appears the device was not taken completely open till 1825 but the 1st All Out call came in at 11:42 DOL 1228059
51 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2019-06-12 17:09 | 2019-06-13 17:26 | 523 | 1457 | 4490561 | 412755 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | DOL Case 929886///Station L/O/Failed Bushing on TR 1/station crew enrouteStation L/O Released by crew 079H03//// Made corrections per DOL
52 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2015-07-21 01:54 | 2015-07-21 13:18 | 598 | 684 | 4921301 | 402337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SCADA INDICATED CB OPEN/ CREW PATROLLING LINES/ - STATION PERSONNEL ON SITE - ISOLATED AT STATION AND CREWS TESTING UNDERGROUND CABLES// TOM CONTINUING TO TROUBLESHOOT WILL UPDATE W/COMMENTS AS MORE DETAILS ARE AVAILABLE @ 1119//TOMSCADA INDICATED CB OPEN // OMS CROSSING CKT // TIMES PER SCADA & LOG VER/HFP L3/HFP AJB
53 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-11-29 03:05 | 2010-11-29 06:13 | 2133 | 188 | 60412-1 | 401004 | TRANSMISSION STATION | EQUIPMENT FAILURE | METERING | AT 0305, JOHNS CREEK STATION TR #1 LOCKED OUT INTERRUPTING THE META AND RACCOON 34KV CKTS. STATION & DISTR. SERVICERS HAVE BEEN DISPATCHED TO CHECK.** ** UPDATE AT 0540 , SERVICER FOUND BAD STATION METERING POT TR. IN PROCESS OF ISOLATING AND SWITCHING TO RESTORE STATION TR. VER/PDP IDCC TOF0307 XXXX
54 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-01-06 20:54 | 2010-01-07 04:30 | 1804 | 456 | H64122-1 | 399794 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 46KV TRANSMISSION LINE OPERATING // A PHASE WAS OUT AT 1929 - ALL CUSTOMER DROPPED WHEN 46KV CB "A" AT ELKHORN CITY WAS OPENED TO ISOLATE SECTION OF 46KV LINE. RESTORED PART OF CIRCUIT @ 2259 // DDC CURRENTLY WORKING TO SECTIONALIZE FURTHER AND WILL RESTORE IN SMALL INCREMENTS TO PREVENT TRIPPING OUT THE LINE// IDC NOT OUT UNTIL OPENED AT 1929 THEN PH A ONLY CHANGED TIME OFF FROM 1819 XXXX
55 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-11-15 03:28 | 2022-11-15 10:19 | 967 | 411 | 4143111 | 397437 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | DOL 1252142 // station outage // high side ckt swroperated to l/o at 0328 // cod 967 //
56 | Hazard | 3308001 | JACKSON | S.JACKSON | 2012-11-12 22:07 | 2012-11-13 04:33 | 1022 | 386 | 4390501 | 394492 | TRANSMISSION STATION | EQUIPMENT FAILURE | SWITCH, OH | SDB / 2207 / STATION OUT. CC 1022. --- SDB / 2320 / FAILED 69KV CB B BUS DISC. UNABLE TO FIELD TRANSFER --- SDB / 0432 / RESTORED. VER/SDB VER/DKG....OK IDC XXXX
57 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-05-28 22:39 | 2008-05-29 05:42 | 1051 | 423 | 52429-1 | 393725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308602// CUTOUT WENT BAD AND HAS BURNED TOP OF POLE OFF WILL NEED RIGHTOFWAY CREW AND 3 CO MEN AND 1 8FT ARM 3 INSULATORS 1 CUTOUT AND T BRACKETT WE WILL LOWER MATERIAL DOWN ON POLE 374-33 VER/ARN IDC XXXX
58 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-07-25 20:15 | 2017-07-26 05:09 | 737 | 534 | 4179581 | 393558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OFF @ 0815 PER SCADA OPERATIONS SERVICER ON SITE: ASSESSING//3 BROKEN CROSSARMS IN A VERY REMOTE LOCATION//NEED BULL DOZER/SIX-WHEELER/ADDITIONAL MEN TO REPAIR/ETR: 0730SERVICER EN ROUTE - ETA: 2130---38830502000041 BUCK ARM POLE LOWER BUCKS BROKE---38830502000057 BROKE X ARM--NBTSERVICER EN ROUTE - ETA: 2130---38830502000042 BUCK ARM POLE LOWER BUCKS BROKE---38830502000057 BROKE X ARM--NBT VER/ARN // FP PER L RAYBURN = L3/HFP HFPC CCU FP38830478D10090 SJG
59 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-11-12 22:07 | 2012-11-13 04:32 | 1008 | 385 | 4390491 | 388080 | TRANSMISSION STATION | EQUIPMENT FAILURE | SWITCH, OH | SDB / 2207 / STATION OUT. CC 1022. --- SDB / 2320 / FAILED 69KV CB B BUS DISC. UNABLE TO FIELD TRANSFER --- SDB / 0432 / RESTORED. VER/SDB VER/DKG IDC XXXX
60 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-06-12 15:29 | 2018-06-12 18:38 | 1998 | 189 | 4592391 | 377622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | changing bad insulator on pole 1082-29
61 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-07-17 17:47 | 2019-07-17 22:07 | 1815 | 260 | 4723981 | 371088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | BREAKER | DOL 939402 // crews patrolling //breaker in station bad//load xfer to Fords BR-Robinson Cr//see DOL log for switching//cod 1815// ¦¦¦ VERIFIED TIMES PER SCADA & DOL - HFP
62 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-10-26 15:28 | 2010-10-26 19:11 | 1664 | 223 | 64385-1 | 371072 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | STATION OUTAGE// STATION CREW ENROUTE//, LINE DISC TO BELLEFONTE 12KV CB AT BELLEFONTE BURNT OFF & FLATWOODS 12KV CB TROUBLE //VER/GAH IDC FLATWOOD BREAKER FAILED TAKING OUT TRANSFORMER XXXX
63 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-08-04 00:26 | 2008-08-04 04:28 | 1520 | 242 | 64781-1 | 367840 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | STATION TRANSFORMER FAULTED AND CREWS ARE WORKING TO RESTORE CUSTOMERS VER/ARN IDC XXXX
64 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-02-15 18:10 | 2018-02-16 02:23 | 842 | 493 | 4845471 | 367682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recloser on 38830478D10090 confirmed open. Patrolling for faults./Opened switches on 38830478D40294//PSC report sent 2206 // Recloser back in at 22:35 picking up cust to pole 38830478D40294 // pole 38830503D40058A neutral broke and wrapped around ph A// Moab switch back in on pole 38830478D40294. //total cod 842//AED created /// NOTE THERE IS A DUPLICATE RECORD ON THIS OUTAGE
65 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-08-11 00:31 | 2014-08-11 05:25 | 1488 | 294 | 4351791 | 365712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BIG CREEK 34KV CB S LOCKED OUT// SERVICER WILL ISOLATE IN FIELD AND WILL TRY TO CLOSE CB VIA SCDA// INFORMATION TO COME AS IT IS KNOWN//TOM CLOSED CB @ 0049// SERVICER ONSITE//TREE CREW ENROUTE//TOM SEE 4351681 (OUTAGE THAT CAUSED BREAKER OUTAGE) VER/DKG L3/DKG AJB
66 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-08-31 18:13 | 2020-09-01 15:45 | 1010 | 547 | 4408891 | 361728 | TRANSMISSION LINE | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | DOL 1050048 & 1050401 // T-Line outage // Station source is out // investigating load xfers // xfered as much load as was possible and t-line completed repairs and restored CB @ 0314//will xfer load back in the morning //
67 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2015-07-21 01:54 | 2015-07-21 13:18 | 527 | 684 | 4921301 | 360468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SCADA INDICATED CB OPEN/ CREW PATROLLING LINES/ - STATION PERSONNEL ON SITE - ISOLATED AT STATION AND CREWS TESTING UNDERGROUND CABLES// TOM CONTINUING TO TROUBLESHOOT WILL UPDATE W/COMMENTS AS MORE DETAILS ARE AVAILABLE @ 1119//TOMSCADA INDICATED CB OPEN // OMS CROSSING CKT // TIMES PER SCADA & LOG VER/HFP L3/HFP
68 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-08-22 12:56 | 2011-08-22 18:42 | 1139 | 346 | 4743641 | 357806 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE | SYDNEY STATION INTERRUPTED DUE TO TRANSMISSION.. TDC WORKING TO RESTORE STATION AS SOON AS POSSIBLE. VERIFIED BY DKG/TRANSMISSION POLE SPLIT ALLOWING STATIC WIRE TO FALL ON CONDUCTOR .. IDC XXXX
69 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-08-17 22:12 | 2021-08-18 04:30 | 1588 | 378 | 4093261 | 351278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | DOL 1140598 // feeder breaker lockout at 2210 per SCADA // cod 1586 // unable to fidn trouble, sectionalizing to find location of the fault //DOL 1140598 // feeder breaker lockout at 2210 per SCADA // cod 1586 //tried recloser on pole 96-C1-465 and it locked back out// opened goab on pole 96-C-236, will try recloser, recloser stayed in// found bad arrester at 73-B-9 and isolatedDOL 1140598 // feeder breaker lockout at 2210 per SCADA // cod 1586 //tried recloser on pole 96-C1-465 and it locked b
70 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-10 08:19 | 2016-01-10 20:36 | 834 | 737 | 4598731 | 346748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38831027D00064/ CUTOUT FAILED AND BURNT POLE OFF. AJB SEE 4602611 FOR OUTAGE ON 3400301 SEE H4598731 TO H4598731C
71 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-03-09 20:59 | 2014-03-10 02:08 | 1616 | 309 | 4463531 | 344049 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WIRE DOWN POLE#1101-76 RIVER CROSSING CENTER PHASE DOWN @ POLE# 38831101C40219 WILL ISOLATE & SWITCH MOST TO BETSYLAYNE MUD CREEK/LOAD TRANSFER RESTORED 1191 CUSTOMERS FROM THE MUD CREEK CKT/ VER/KEP L3/HFP IDC XXXX
72 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2015-08-06 18:13 | 2015-08-07 13:51 | 292 | 1178 | 4105771 | 343976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | AT 1906 VERIFIED CB LOCKED OUT - SERVICER PATROLLING CKT//TOM1 @ 1813//YELLOW HILL BREAKER OUT WILL PATROL//A//TOM **2121 - UPDATE CB CLOSED AND HELD FOR A WHILE - LOCKED BACK OUT// ISOLATING CB - SAW FLASCH BACK ON THE MOUNTAIN//TOM - NO FETR AT THIS TIME - REMOTE LOCATION - BROKEN CROSS ARMS - CREW WILL PROVIDE FETR UPON ARRIVAL// **MATERIALS SET OF 9` ARMS & BRACES AND 4 PINS &INSULATORS**HOLD ORDER REQUIRED****//ALL WORK COMPLETE, FEEDER RESTORED 8-7-15 1351// TIMES PER DISPATCH LOG == VER/HFP L3/HFP
73 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-12-08 16:53 | 2009-12-08 19:57 | 1865 | 184 | 57666-1 | 343160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 37830230C00203 WE HAVE BAD DEADEND INSULATOR, HAVE CALL CREW TO BRING INSULATORS AND HEAD THIS WAY. RELEASED BY CREW 077S08 AJBC TOF16:54 PER SCADA AND OUTAGE REPORT.
74 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-06-20 02:15 | 2015-06-20 08:04 | 1452 | 349 | 4614821 | 341666 | DISTRIBUTION STATION | EQUIPMENT FAILURE | NONE | SCADA INDICATES THE LOWER ROCKHOUSE 34KV CB J AT COLLIER LOCKED OUT INTERRUPTING 1452 CUSTOMERS.//SERVICER ENROUTE//SERVICER PATROLLING LINE//BREAKER CLOSURE FAILED//SEE OUTAGE LOG FOR DETAILS/STATION PERSONEL ENROUTE//OPENED SW 376-A-147 AND @ 0606 CLOSED 376-106//RESTORED 1399 CUST//SCADA INDICATES THE LOWER ROCKHOUSE 34KV CB J AT COLLIER LOCKED OUT INTERRUPTING 1452 CUSTOMERS.//SERVICER ENROUTE// MOTOR LIMIT SW ON CB FAILED TIMES PER LOG & SCADA VER/HFP L3/HFP AJB
75 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-01-11 03:27 | 2016-01-11 12:29 | 991 | 542 | 4605141 | 338039 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | @ 230/234 & 230/235 45-4, BROKE X ARM @ 230/236 NEED LINE CREW & FLAGING CREWSERVICER ENROUTE,POLE BROKE/CREW ON SITE/VEM/HOLD ORDER ISSUED 0708/FETR1430/VEM/ANCHOR RUSTED GAVE WAY BROKE TWO POLES/JOB GOING WELL/NEW FETR 1330/VEM VER/KEP AJB
76 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-11-19 06:10 | 2008-11-19 09:27 | 1873 | 197 | 66467-1 | 336567 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | MOBILE TR L.O. BOTH RACCOON AND META CKTS ARE INTERRUPTED. STATION SERVICERS ARE DISPATCHED SERVICERS OPENED RECLS AT POLE 4-203 FOR COLD LOAD PICKUP PROBLEMS.... OPEN AT 4-203 & 2-54 .....TRANSFERRING SOME CUST/CLOSED ON POLE 74-190 AT 0905 467 CUST/CLOSED ON 26A2-232 AT 0906 931 CUST/UPDATED FETR RELEASED BY CREW 074S06 IDCC TOF612 XXXX
77 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-07-07 08:57 | 2013-07-07 12:15 | 1690 | 198 | 4478891 | 334620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATES FEEDER BREAKER LOCKOUT @ 0857 CREWS PATROLLING CKT. *UPDATE @ 1127 CLOSED CB VIA SCADA * DID NOT STAY * FAILED INSULATOR JUST OUTSIDE STATION , XTRA PERSONNEL CALLED OUT. IDC XXXX
78 | South Williamson | 3411401 | DEWEY | INEZ | 2015-04-16 22:06 | 2015-04-16 23:58 | 2897 | 112 | 4327921 | 324464 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED 138KV MOAB X2 OPENED @ DEWEY//THIS HAS DEWEY STATION INTERRUPTED// STATION SERVICER DISPATCED// DISTRIBUTION SERVICER DISPATCHER//WILL MAKE UPDATES AS INFORMATION BECOMES AVAILABLE//TOM // RESTORED STATION, FOUND BAD FUSED DISC ON 34KV BUS, DE-ENERGIZED TO MAKE REPAIRS// UPDATED FETR// RELEASED BY CREW 076H07 VER/TOM L3/TOM L3/DKGXXX VERIFIED WITH ALARM HISTORY AJB
79 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-09-06 02:27 | 2011-09-06 05:27 | 1858 | 180 | 4827211 | 324248 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | CREW ON SITE PATROLLING LINES/SECTIONALIZING TO FIND FAULT/BAD REGULATOR IN THE STATION ISOLATED AND RESTORED BREAKER/SWITCHING OPENED DEVICES BACK TO NORNAL// RELEASED BY CREW 074H03 VER/KEP IDC XXXX
80 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-01-06 19:29 | 2010-01-07 04:30 | 979 | 541 | 64122-1 | 322166 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 46KV TRANSMISSION LINE OPERATING // A PHASE WAS OUT AT 1929 - ALL CUSTOMER DROPPED WHEN 46KV CB "A" AT ELKHORN CITY WAS OPENED TO ISOLATE SECTION OF 46KV LINE. RESTORED PART OF CIRCUIT @ 2259 // DDC CURRENTLY WORKING TO SECTIONALIZE FURTHER AND WILL RESTORE IN SMALL INCREMENTS TO PREVENT TRIPPING OUT THE LINE// IDC NOT OUT UNTIL OPENED AT 1929 THEN PH A ONLY CHANGED TIME OFF FROM 1819 XXXX
81 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-05-23 02:25 | 2015-05-23 05:46 | 1602 | 201 | 4458241 | 322002 | TRANSMISSION LINE | EQUIPMENT FAILURE | CAPACITOR | SDB / 0220 / 138KV BUS 1 AND BUS 2 AT BEAVER CREEK RELAYED OUT DUE TO ____. THIS INTERRUPTED 2, 048 CC. STATION AND LINE CREWS EN ROUTE. LIGON 34KV CKT - 1602 CC VER/SEF L3/HFP HFPC CDC82 AJB
82 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-12-07 09:02 | 2011-12-07 14:23 | 1441 | 321 | 4147541 | 320503 | TRANSMISSION STATION | EQUIPMENT FAILURE | CONDUCTOR UG | 138 KV TR 1 LOCKED OUT AT JOHNS CREEK , STATION SERVICER DISPATCHED TO CHECK. 1451 CC. ON RACCOON CREEK CKT. // UNDERGROUND CABLE AT STATION FAULTED - LOOKING AT LOAD TRANSFER ** COD-1451 IDCC TOF0904, CNT1956 XXXX
83 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-04-10 21:56 | 2021-04-11 06:47 | 1422 | 531 | 4439721 | 317949 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER REQ/ DOL 1106184/ crossarm broke at 37830375A00066 due to age/ COLLIER-LOWER ROCKHOUSE (34 KV) CKT between poles 375-D2-2781 and 375-A-419crossarm broke at 37830375A00066 due to age/ COLLIER-LOWER ROCKHOUSE (34 KV) CKT between poles 375-D2-2781 and 375-A-419 6:30
84 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-12-26 11:00 | 2008-12-26 13:21 | 2220 | 141 | 64021-1 | 313020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3310501//INSULATOR 3 SPANS OUTSIDE OF STATION HAS FAILED//CREW ENROUTE// NO ALT SWITCHING IS AVAILABLE , FEEDER WAS OPENED AT 1100 JOB IS NON-TRUCK CREWS WILL WILL CLIMB POLE TO MAKE REPAIRS . CSC WAS NOTIFIED.//VER/CRB L3/JMS IDCC TON1323 XXXX
85 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-03-05 16:26 | 2018-03-05 19:46 | 1561 | 200 | 4968831 | 312200 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | DOL 808163 // SCADA Indicated 3403201 Open @ 1626 // bad arrester found in sub station // restored 1946
86 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-11-17 06:33 | 2011-11-17 14:17 | 837 | 464 | 4086101 | 309087 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | RECLOSER IS OPEN PATROLLING, PATROLLED TO 502-294, NOTHING FOUND LINE HOT TO 502-294. POLE 502-35 POLETOP BURNNED OFF NO TRUCKS TO POLE.NEW FETR1445/VEM/3 PHASE ANGLE POLE TOP BROKEN /CAUSE UNKNOWN/ARMS REPLACED AND POWER RESTORED TO REMAINING 630 CUST AT 1417/NO FURTHER ACTION REQUIRED/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 /// COD-837 ISO OCR 38830478D10090 VER/HFP L3/HFP IDC XXXX
87 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-11-17 06:33 | 2011-11-17 14:17 | 837 | 464 | 4086101 | 309087 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007906 RECLOSER IS OPEN PATROLLING, PATROLLED TO 502-294, NOTHING FOUND LINE HOT TO 502-294. POLE 502-35 POLETOP BURNNED OFF NO TRUCKS TO POLE.NEW FETR1445/VEM/3 PHASE ANGLE POLE TOP BROKEN /CAUSE UNKNOWN/ARMS REPLACED AND POWER RESTORED TO REMAINING 630 CUST AT 1417/NO FURTHER ACTION REQUIRED/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 COD-837 ISO OCR 38830478D10090 IDC XXXX
88 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-02-01 16:51 | 2010-02-01 19:08 | 2246 | 137 | 62117-1 | 307702 | TRANSMISSION STATION | EQUIPMENT FAILURE | BREAKER | STATION TR OUTAGE. **UPDATE AT 1840 T-DISP. IS PROCESS OF REST. TR AT THIS TIME ASAP KYDDC WILL CLOSE META AND RACCOON CREEK CB VIA SCADA . VER/KEP L3/KEP IDC XXXX
89 | Paintsville | 3409302 | KENWOOD | AUXIER | 2009-10-08 03:25 | 2009-10-08 09:25 | 1013 | 360 | 62229-1 | 306771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FEEDER OUTAGE -SERVICER NOW PATROLLING CKT , OUTAGE WILL BE UPDATED WHEN INFORMATION IS AVAILABLE. RECLOSER AT POLE 882-565 OPENED AT TAGGED. RECLS 882-A-457 OPENED REC 882-457. DIDNT FIND PROBLEM. TRYING BREAKER.. VER/ARN IDC XXXX
90 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-07-16 09:16 | 2011-07-16 13:11 | 1301 | 235 | 4552911 | 305735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3007906 SERVICER PATROLLINGBAD POLETOP INSULATOR ON 478-3001, LINE CREW HAS BEEN NOTIFIED;BAD POLETOP INSULATOR ON 478-3001, LINE CREW HAS BEEN NOTIFIED; REPAIRES MADE ALL POWER RESTORED AT 1311 CLOSE TICKET VER/ARN IDC XXXX 0916 TO 1311
91 | Hazard | 3310502 | HADDIX | CANOE | 2013-03-19 14:07 | 2013-03-19 19:33 | 1188 | 326 | 4920321 | 304229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POWERON INDICATED CANOE 34KV CKT LOCKED OUT// SERVICERS ENROUTE PATROLLING CKT// FOUND BAD INSULATOR AT POLE 27-65 MADE REPAIRS AND TRIED BREAKER - RE-TRIPPED// POSSIBLE LOAD TRANSFER// SERVICERS PATROLLING RELEASED BY CREW 077S05 /// SEE LOG // IDCC STP TIMES, CNT1077 XXXX
92 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-11-16 11:16 | 2011-11-16 22:20 | 1104 | 664 | 4081961 | 303259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF, CONTRACT CREWS REPLACING DEWEY AKERS HAS A HOLD ORDER // ALL CUSTOMERS RESTORED AT 2209 IDC XXXX
93 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-07-10 04:37 | 2022-07-10 13:48 | 916 | 551 | 4450141 | 298379 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 1220966 HOLD ORDER REQ Recloser open at 1081-99 LIGHTNING STRUCK POLE ON MAIN 3-PH/CREWS EN ROUTERecloser open at 1081-99,Pole 1056-C-92 has burned into,Will need 50 Class 2 Pole and line crew to make repairs..Recloser open at 1081-99,Pole 1056-C-92 has burned into,Will need 50 Class 2 Pole and line crew to make repairs.. Released by crew 074S01
94 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-02-01 18:20 | 2015-02-01 23:15 | 1671 | 295 | 4979301 | 297555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | AM PATROLLING 2 INSULATORS ON STATION EXIT. WILL SWITCH & PICK UP ON HAROLD CIRCUIT AT POLE #38831125C30408 CLOSED IN @ 21:18 RESTORING (1670) COUSTOMERS ON MUD CREEK CIRCUIT. AT 2315 1 CUST REST // VER/HFP L3/HFP AJB
95 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-10-19 03:59 | 2012-10-19 15:15 | 455 | 676 | 4155751 | 296755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SERVICER PATROLLLING CKT.TREE FELL ON HILL SIDE ACROSS FROM 7921 RT. 5TREE FELL ON HILL SIDE ACROSS FROM 7921 RT. 5 RELEASED BY CREW 078S08//RECLOSER ISOLATED AND GROUNDED AT POLE 91-6106//PATROLLING LINE PRT/91-14 40/4 ANGLE POLE 2 TAPS NO TRUCKS BROKE//CALLED TECH//\CLOSED RECLOSER AT 14:50 MAIN LINE RESTORED//CLOSED 2 40TS ON POLE 91-14 AT 15:15 ALL POWER RESTORED CLOSE TKT PRT RELEASED BY CREW 078H03 FAILURE PER TOLLIVER///VER/CRB L/3 CRB// IDC XXXX
96 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-05-14 09:02 | 2012-05-14 12:50 | 1295 | 228 | 4790151 | 293516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FEEDER OUTAGE *** SERVICER PATROLLING. **** CKTS. CREWS MAY HAVE FOUND BAD INSULATOR.. WILL UPDATE WHEN HAVE MORE INFOR ** AT 1049 CB SHOT DID NOT HOLD COULD BE CB TROUBLE -STATION CREW ENROUTE.BAD ARRESTER --...... CHECKED BY DKG OK...CHANGED TIME OFF TO CORRESPOND WITH CUST CALLS IDC XXXX
97 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-03-19 02:17 | 2008-03-19 07:32 | 946 | 315 | 58375-1 | 293502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3309103/ FEEDER OUT ***** SERVICER PATROLLING CKT ....POLE FAILED/ ISOLATEING AT POLE 448-518. FOUND POLE 448-435 BROKEN. I HAVE ISOLATED AT POLE 448-518. WE CAN CLOSE STATION BRKR BACK. WE WILL LOOK AT PICKING SOME OF THE COWAN LOAD BEYOND BROKEN POLE UP OFF THE WHBG CIRCUIT AS SOON AS WE GET BRKR IN. WILL NEED 3 MAN CREW, LINE TRUCK AND BIG BUCKET. @ 0408 CLOSED COWAN CB REST 22 CUSTOMERS.REMAINING CUST REST BY 0732/ 58407-1 IS RELATED VER/HFP IDC XXXX
98 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-08-03 20:24 | 2016-08-04 12:15 | 332 | 951 | 4730601 | 292404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ***SEE 4733931*** CLOSED RECLOSER ON 37830174A00220 AT 0006 UP TO OPEN SWITCHES ON 198-A-49 (32 CUST). PATROLLING LINES. POLE LEANING 198-60. WILL ATTEMPT TO STRAIGHTEN TEMPORARILY. POLE 37830198B00060 IS ROTTED OFF AND COUNTY NEEDS TO FILL DITCH WHERE WE CAN CHANGE POLE NEED 50 CL2 2 8 FOOT ARMS//OPEN SWS 198-A-49 AND RESTORED UP TO// ALSO ANOTHER SET OF SWITCHES OPEN ON 221-64//NO TAGS, NO GROUNDS PLACED// 37830198A00049 1215 (300 CUST)/ VER/BOW AJB
99 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2013-07-07 02:21 | 2013-07-07 21:58 | 350 | 1177 | 4477511 | 292367 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | COLEMAN-SPRIGG 69KV LINE LO // 69 CONDUCTOR DOWN T-LINE CREWS TO MAKE REPAIRS - TRANSFER CUSTOMERS TO ALT SOURCES WHERE AVAILABLE. ** UPDATE MULTIPLE T- LINE CREWS AND HEAVY CRANE ENROUTE TO ASSIST. . *** UPDATE TIME TO 2000 *******SA FAILED AT BARRENSHE, UPDATED FETR TO 2330 IDC XXXX
100 | Hazard | 3303902 | LESLIE | WOOTON | 2010-03-11 15:57 | 2010-03-11 18:52 | 1842 | 175 | 65123-1 | 290356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CKT FEEDER OPERN FOR UNKNOWN TROUBLE / SERVICER ENROUTE // SECTIONALLIZING TO LOCATE TRBL//GOT POWER ON UP TO 365-D2-323 @ 1727//FOUND BAD CUTOUT ON 365-181 AND IS CUT IN CLEAR // RECLOSER ON POLE 365-323 IS CLOSED AT 1811 UP TO 389-C-328//WILL CLOSE 389-328 ONCE ALL HAZARDS PAST THISPOINT HAVE BEEN CHECKED// CLOSED 389-328 AT 1852. IDCC TOF1558 XXXX
101 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-05-23 02:33 | 2018-05-23 13:22 | 1377 | 649 | 4398581 | 289936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | broke pole crews making repairs.. Notes from DOL state pole 38830045B33241 caused this outage from top burned off, and this pole does not show up on the map.
102 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-10-14 04:44 | 2014-10-14 11:53 | 728 | 429 | 4615741 | 289528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3-PHASE RECLOSER IS OPEN ON 37830190D00313. I AM PATROLLING LINE NOW. POLE 214-92 IS ROTTED AND FELL OVER INTO TREES. I GIVE TIM MCCOY MATERIAL LIST. SEND TT TO HIM. RELEASED BY CREW 074S01// MADE REPAIRS OPENED RECLOSER AT 11:52 CLOSED BACK IN AT 11:53 AND RESTORED ALL CUST. TIM MCCOY // SEE 4620331 FOR SECOND RECL OUTAGE TO CLOSE SW // VER/HFP L3/HFP AJB PER POSW: OCR OUT W/728. OP SW37830214A40930 W/600. @08:55 CL OCR, R128. @11:52 OP OCR, OUT 128. CL SW. @11:53 CL OCR R128 & 600. SEE4620331.
103 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-07-25 02:14 | 2012-07-25 16:52 | 390 | 878 | 4819831 | 289313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER LOCKED OUT @ POLE 30-35,,WILL NEED SERVICER & 2 ACCESSORS TO PATROL IDC CHANGED TIME OFF FROM 1515 7/24, COUNT FROM 443 XXXX
104 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2017-11-18 23:07 | 2017-11-19 04:18 | 926 | 311 | 4573921 | 287986 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | 2150502 - cc=926 SCADA indicates CB locked out/ CB open due to broken station service cutout/ bus outage necessary to replace/ restored @ 04182150502 - cc=926 SCADA indicates CB locked out/ CB open due to broken station service cutout/ bus outage necessary to replace/ restored @ XXXX Released by crew 080S02
105 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-11-19 06:10 | 2008-11-19 08:58 | 1816 | 168 | 66469-1 | 287831 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | MOBILE TR AT JOHNS CREEK L.O. BOTH RACCOON AND META CKTS ARE INTERRUPTED. STATION PERSONNEL AND SERVICERS ARE DISPATCHED . ALT. SWITCHING TO TRANSFER RACCOON CKT 34KV CKT ON GOING. ... ALL CUST ON META CIRCUIT ON AT 0858 ... POLE 99 CLOSED AT 0845/POLE 347 CLOSED AT 0858 MLRC OK IDCC TOF612 XXXX
106 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2021-11-07 17:45 | 2021-11-07 21:56 | 1230 | 251 | 4064971 | 285382 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | 69/12kV TR 1 tripped from service, Station crews on site reporting to failed arrestors working to transfer load for some customers FETR for all customers 2300station transformer issues Released by crew 078S07
107 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-01-16 06:57 | 2013-01-16 12:12 | 917 | 315 | 4609981 | 285135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SDB / 0659 / SCADA INDICATED DORTON 34KV CB R OPERATED AND LOCKED OUT// DORTON CIRCUIT BREAKER IS OPEN. I AM PATROLLING LINE NOW. FAILED INSULATOR AT POLE 214-D-404 --- SDB / 1154 / 32 CC REST ---- SDB / 1208 / 786 CC REST ---- SDB / 1212 / 99 CC REST . VER/SDB IDCC TOF0659 XXXX
108 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-01-02 18:20 | 2014-01-03 15:45 | 455 | 1285 | 4219861 | 279953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE ONLY OUT AT RECL 459-166 DUE TO SLIDE ***326CC. *5 POLES HAS BROKE 8FT ARMS WILL NEED R/W CREW 3 LINECREWS AND A FLAGGING CREW LOOPS OPENED AT 576-85 & TAGS PLACED FOR DDC.* TAGS TO BE REPLACED BY FIELD LCS. AND WORKED CREW DISP AUTHORITY. DAVOX SAYS SLIDEC PHASE ONLY OUT AT RECL 459-166 DUE TO STIRUP FAILURE 326CC. 5 POLES HAS BROKE 8FT ARMS WILL NEED R/W CREW 3 LINECRWS AND A FLGGNG CREW LOOPS OPND AT 576-85 & TAG//?????? IDCC TON2150 STEP 2 XXXX
109 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2013-11-23 00:34 | 2013-11-23 12:58 | 376 | 744 | 4066511 | 279155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED RECLOSER @ 0034 (BY ADX LOADING) TO REMOVE LOAD AND ALLOW CREWS TO OPEN SB @ 810-24 // CLOSED OCR @ 1239// HAVE BAD INSULATOR AT POLE 810-D-9 // CLOSED SOLID BLADES AT 1258// VER/TOM L3/TOM IDC XXXX
110 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-01-13 04:43 | 2017-01-13 07:36 | 1610 | 173 | 4293911 | 278530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FAILED INSULATOR POLE 1101-76/CB ISOLATED TIM MCCOY HAS HOLD ORDER// CC 1610 RESTORED @ 0736 VIA SVC - SEE DOL CASE 714344DEAD END INSULATOR BAD 1101-C4-76. VER/TOM L3/TOM /// VER TIMES PER SCADA HFP AJB
111 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-12-22 04:32 | 2013-12-22 09:45 | 882 | 313 | 4186351 | 276066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FEDS CREEK STATION BREAKER OUT WE ARE PATROLLING LINE. INSULATOR BROKE ON POLE 126-136 CALLING FOR HELP . REPAIRS MADE C LOSED BREAKER @9:45 VER/HFP L3/HFP IDCC TON935 XXXX
112 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-12-22 15:53 | 2020-12-22 23:38 | 1858 | 297 | 4795621 | 275913 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | DOL 1078079 // fire on station TR 1 at Jackson // interrupted station to isolate // station servicer(s) enroute //cod 310 (+619) // Released by crew 077H03
113 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-11-27 05:08 | 2019-11-27 08:35 | 1326 | 207 | 4071591 | 274482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | found bad tie wire on pole 37830246D00124
114 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-10-02 15:29 | 2009-10-03 00:30 | 655 | 541 | 65367-1 | 273680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED REC TO ISOLATE OUTAGE 65305 RELEASED BY CREW 078S06//WR#32026406--CREWS ON SITE, CHANGING POLE AND ARMS ON SWITCH POLE VER/TOM IDC XXXX
115 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-07-26 05:16 | 2009-07-26 14:30 | 494 | 554 | 50861-1 | 273676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY "B" PHASE RECLOSER OPEN//COD 352//OPENED OTHER 2 PHASES @ 11:56 (INTERRUPTED 951 MORE CUST) //5 MAN CREW AND TREE CREWS ON SITE//FAILED CUTOUT BURRNED CROSSARMS//STS WR #30912392// IDC LOOKS LIKE SOME MISSMAPPED CUSTOMERS ESTIMATED COUNT IDC XXXX
116 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-06-26 12:14 | 2018-06-27 14:03 | 691 | 1549 | 4671111 | 273399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 837978 // Pole top insulator failed burned pole at 239-190/ 2 DHE crews enroute to sasist.Dead end insulator failed burned pole at 239-190/ 2 DHE crews enroute to sasist. Rec. open @214-D-175, opened inline switches and tagged to DDC @239-A1-325 to isolate trouble, closed rec. back @1602, Dewey Akers to take hold order on line.Dead end insulator failed burned pole at 239-190/ 2 DHE crews enroute to sasist. Rec. open @214-D-175, opened inline switches and tagged to DDC @239-A1-325 to isolate
117 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2020-07-27 08:14 | 2020-07-27 13:05 | 1658 | 291 | 4236181 | 271023 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | Failed Station Transformer crews enroute **** I DIDNT COMPLETE RESTORATION OF THIS OUTAGE ONLY CLOSED THE OUTAGE AFTER SHIFT CHANGE , NOT SURE ABOUT CAUSE CODES OR TIMES ON/OFF. ALAN JORDAN ****
118 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-09-28 05:39 | 2015-09-28 19:40 | 486 | 841 | 4280801 | 269259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF MAIN LINE POLE BURNT OFF, POLE 184-200, CAN OPEN SWITCHES ON POLE 207-177, MADE RECLOSER BACK HOT AT 07:40, CUT LOOPS ON 207-239 AND MADE HOT AT 08:33/ UPDATE ALL CUSTOMERS RESTORED THAT CAN BE, REMAINDER OUTAGED UNTIL REPAIRS COMPLETE/ TO MAKE HOT TAP UP @ 1935 ON 207-239 OPENED SWITCH 207-54 @1928 CLOSED @1940/ SEE DUP H4280801 FOR OUTAGE TO MAKE UP LOOPS = VER/HFP L3/HFP AJB
119 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-11-29 03:05 | 2010-11-29 06:14 | 1415 | 189 | 60418-1 | 267435 | TRANSMISSION STATION | EQUIPMENT FAILURE | METERING | AT 0305, JOHNS CREEK STATION TR #1 LOCKED OUT INTERRUPTING THE META AND RACCOON 34KV CKTS. STATION & DISTR. SERVICERS HAVE BEEN DISPATCHED TO CHECK.* ** UPDATE AT 0540 , SERVICER FOUND BAD STATION METERING POT TR. IN PROCESS OF ISOLATING AND SWITCHING TO RESTORE STATION TR. VER/PDP IDCC TOF0308 XXXX
120 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2015-02-17 02:49 | 2015-02-17 15:04 | 498 | 735 | 4035331 | 267206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER TIM HALL ARCOSED JOEY REED. THREE PHASE POLE BURNED OFF. 1111-88 MUST BE REPLACED.TRUCK APPROACH. CAN PICK UP SOME CUSTOMERS FROM BARRENSHE/ SLATE BRANCH CIRCUIT. I WILL TAKE HOLD ORDER VER/HFP L3/HFP AJB
121 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-02-19 14:40 | 2017-02-19 19:37 | 892 | 297 | 4407671 | 264924 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | POWERON INDICATED THE TRAM 12KV CB D LOCKED OUT// SERVICERS AND STATION PERSONNEL ON SITE - THE 46-12KV TR 1A (STATION TRANSFORMER) HAS BLOWN HIGH SIDE FUSES. CREWS WILL MAKE REPAIRS - FETR UPDATD TO BE 2300, WILL UPDATE IF CHANGES ARE MADE//TOM RELEASED BY CREW 074S03/// VER/DKM /// VERIFIED TIMES PER DOL & SCADA = L3/HFP XXXHFP AJB
122 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2020-05-24 16:26 | 2020-05-25 11:45 | 228 | 1159 | 4902051 | 264252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Released by crew 077H20..loop open on cutout, all power restored @ 11:45 hrs p.hicks
123 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-07-08 18:43 | 2016-07-08 22:36 | 1128 | 233 | 4563551 | 262824 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | WEST PAINTSVILLE STATION DE-ENERGIZED DUE TO THELMA-THEMLA 69KV LINE OUTAGE//TOM - 1925 - SERVICER IN STATION MAKING CHECKS//TOM- SDB / 2035 / DAMAGED 69KV TRANSFORMER ARRESTER, CREWS MAKING REPAIRS. CLOSED CB @ 2236 VER/TOM L3/TOM/// VER/DKM AJB
124 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-07-15 01:22 | 2016-07-15 07:15 | 912 | 353 | 4638971 | 262376 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | SCADA INDICATES FEEDER BREAKER LOCKOUT @ 0122//SEE DOL CASE 671791//COD 912//ON SITE,BAD MOAB SWITCH///MOAB SWITCH 1 JUMPER OUT ,STATION BREAKERS BACK IN RELEASED BY CREW 077H07 AJB ADDED 3 STP PER DISP LOG.
125 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-05-03 18:46 | 2017-05-03 23:42 | 886 | 296 | 4741461 | 262256 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | FAILED 12KV ARRESTER ON 46/12KV TR 1A, 2 FLASHED 12KV TRANSFER BUS DISCS, AND CENTER PHASE HS FUSE BLOWN ON 46/12KV TR 1 A AT BETSY LAYNE//STATION CREW ONSITE - CLEARANCE ISSUED AND REPARIS ARE UNDERWAY - FETR 0100//TOM. - STATION CREW READY TO ENERGIZE CKT - UPDATE - SHOULD BE RESTORED AROUND 2345BREAKER BACK IN @ 23:42 VER/AWD L3/HFP HFPC TOF1918 FEC58 AJB
126 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-10-26 15:28 | 2010-10-26 18:04 | 1666 | 156 | 64388-1 | 259896 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | STATION OUTAGE, LINE DISC TO BELLEFONTE 12KV CB AT BELLEFONTE BURNT OFF & FLATWOODS 12KV CB TROUBLE //VER/GAH IDC XXXX
127 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-11-18 22:03 | 2017-11-19 11:59 | 515 | 836 | 4572071 | 259558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop burnt off middle phase GOAB, pole 37830172A00479/ will need flagers big bucket///sws on pole 194-115 did not closeloop burnt off middle phase GOAB, pole 37830172A00479/ will need flagers big bucket , repairs to loop made switching to get customers back on complted 1427 , line still has fault open inbetween switches on p#194-88 and p#169-193 Released by crew 077H03
128 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-03-09 19:07 | 2019-03-10 12:15 | 950 | 1013 | 4964861 | 258817 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER REQ//DOL 903956//CREW ENROUTE//pole#254-25 viper rec, B phase locked out,tried to close recloser @ aprox 21:10 and all phases locked open, open GOAB 278b-257 and closed viper 254-25 @ 21:40//open & tag rec 302-49, & closed GOAB 303-162 on reedy/dean @ 00:58 hrs // Released by crew 077H03 L3/HFP
129 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-05-27 00:44 | 2009-05-27 04:30 | 1420 | 226 | 54784-1 | 257060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTEN ARRESTER BROKE DOWN ON POLE 96-342 AND OPENED STATION BREAKER. WE ARE GOING TO CHANGE ARRESTER. RELEASED BY CREW 074S01 OPENED BREAKER AGAIN SHOWN ON SEPERATE ORDER VER/KEP L3/KEP IDCC STEP ONE TON0157 XXXX
130 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-01-12 07:50 | 2018-01-12 14:00 | 1118 | 370 | 4734031 | 256930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF @ 38830044A00113// //CAN NOT BACK FEED BECAUSE OF MOBILE AT HOODS CREEK STATION//OPENED SWITCHES @ POLE 38830044A00413 AND CLOSED RECLOSER 38830020B33033 @ 0903//Released by crew 078H01,switch closed @pole 44-413 @ 1155 UPTO FUSES ON POLE 38830044A00113 / ALL ON 1400
131 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-01-08 08:22 | 2016-01-08 14:59 | 709 | 397 | 4594381 | 252448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TREE POSSIBLE LAYING ON LINE CAUSING REC. ON POLE 214-175 TO OPERATE.TALKED TO TIM HALL AND HE HAS LINE CREW ON WAY WITH SIDE BY SIDE TO HELP PATROL LINE.. RELEASED BY CREW 074H21// FOUND 6 INSL. BAD ON POLE 239-72 WILL NEED OUTAGE TO REPAIR. MADE REPAIRS AND CLOSED RECLOSER IN AT 14:59 TIM MCCOY RELEASED BY CREW 074H10 AJB
132 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-12-18 04:04 | 2016-12-18 11:23 | 564 | 439 | 4208221 | 247596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLED LINE ,SHOT LINE AT 10:34 DIDNT STAY , FOUND BAD CUTOUT REPLACED AND POWER RESTORED @ 11:23 JDM /RM //// NEED TO VERIFY FAULT POLE ? EVERTHING ELSE LOOKS OKAY HFP AJB
133 | Hazard | 3303902 | LESLIE | WOOTON | 2018-01-02 05:30 | 2018-01-02 08:13 | 1512 | 163 | 4694931 | 246456 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | See DOL Case 794154///69-34kV TR 2 is out--failed phase 1 regulator /// VERIFIED TIMES PER SCADA & POA & DOL = HFP
134 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-03-31 10:24 | 2014-03-31 17:27 | 897 | 423 | 4547221 | 245520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE RELEASED BY CREW 078S09/TRIED BREAKER IN @1220/CAME BACK OUT/THREE CREWS PATOLLING LINE/CAN FIND NO OBVIOUS TROUBLE/VEM FAILED CUTOUT ON POLE392-A-997 /REMAINING CUST SHOULD BE RESTORED BY 1730/VEM RELEASED BY CREW 078H14 VER/KEP IDC XXXX
135 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-07-26 11:15 | 2020-07-26 15:24 | 1179 | 249 | 4233861 | 245312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOLD ORDER REQ //DOL 1039767 //COD 605 FROM BEGINNING OF OUTAGE //wire down at pole 37830024B20765 // will transfer load //cod 605 //A phase conductor burnt in two, at pole 24-B2-765 will need crew to make repairs // A phase conductor burnt in two, at pole 24-B2-765 will need crew to make repairs //
136 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-06-14 12:54 | 2010-06-14 16:40 | 1083 | 226 | 63976-1 | 244758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | RECLOSER OPEN ON POLE 375-383... BAD CUTOUT ON POLE 374-26 ,WIRE DOWN ON POLE 398-100,, WIRE DOWN ON POLE 374-118 ISOLATED ON POLE 374-42 .ISOLATED BOTH TAPS , CLOSED RECLOSER ON POLE 375-383 RESTORING POWER AT 16:40 RELEASED BY CREW 077S11
137 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-09-09 16:33 | 2018-09-09 22:02 | 1292 | 329 | 4066101 | 243356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | opened and tagged GOAB on pole 96-391. closed recloser in on pole 96-C-339 at 18:24.. opened switches on pole 120-454 and closed N/O GOAB on pole 167-520. Hold order issued at 19:40 released at 22:00 Released by crew 079H07
138 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-09-09 16:33 | 2018-09-09 22:02 | 1289 | 329 | 4066101 | 243023 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | opened and tagged GOAB on pole 96-391. closed recloser in on pole 96-C-339 at 18:24.. opened switches on pole 120-454 and closed N/O GOAB on pole 167-520. Hold order issued at 19:40 released at 22:00 Released by crew 079H07
139 | South Williamson | 3202201 | LOVELY | LOVELY | 2019-06-13 00:31 | 2019-06-13 10:31 | 943 | 600 | 4491151 | 242181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Hold Order Req/Kyddc Tags////DOL Case 929917/// PATROLLING//bad 19.9 insulator on pole 747-219//need line crew and manual tree crew//have lovely hot up to switches on771-a-53 tagged to DDC//back fed up to 747-b-28 from dewey, ¦¦ CHANGED TOF TO THAT OF FIRST CALL IN WV SIDE OUTAGE L3/HFP
140 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2017-10-09 09:45 | 2017-10-09 17:50 | 499 | 485 | 4432631 | 242015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE TOP BURNED OUT ON 380-311. NO POWER OUT UNTIL RECL OPENED @ 0945 38830380000311 55/2 POLE BURNT OFF---38830380000306 3 REC OPEN AT 09:45 (499 CUST) --TAG TO MR TACKET--CREW, FLAGGERS, AND TECH REQ-DSPOLE TOP BURNED OUT ON 380-311. VER/AWD ACB
141 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-05-10 10:35 | 2015-05-10 16:20 | 700 | 345 | 4407901 | 241500 | DISTRIBUTION STATION | EQUIPMENT FAILURE | NONE | SCADA INDICATED 69-12KV TR 1 @ SOUTH PIKEVILLE DE-ENERGIZED. THIS HAS STATION INTERRUPTED AND APPROX 1786 PIKEVILLE AREA CUSTOMERS// STATION SERVICER AND D-LINE SERVICER CALLED IN//TOM WILL UPDATE AS INFORMATION BECOMES AVAILABLE//TOM ***UPDATE @ 1135 DETERMINED STATION TRANSFOMER HAS FAILED - LOOKING AT LOAD TRANSFER OPPORTUNITIES AND WILL NEED A MOBILE TRANSFOMER INSTALLED - ALL NECESSARY PARTIES NOTIFIED//TOM - ALL CUSTOMERS RESTORED FROM PIKEVILLE/MAIN STREET @ 1620 VER/KEP AJB
142 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-06-02 16:43 | 2014-06-02 22:42 | 980 | 359 | 4962301 | 240013 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN ON POLE#1081-99 WILL PATROL // B PHASE TARGET ON RECL // CLOSED RECLOSER IN @20:23 COD-980 ISO OCR 38821081000099 /// ADDED STEPS FROM ORDER 4962821 - CUSTOMERS NOT RESTORED INITALLY AS EXPECTED MAKING THAT ORDER A DUPLICATE // VER/HFP L3/HFP IDCC CNT1195 XXXX
143 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-02-29 12:19 | 2012-02-29 15:38 | 1412 | 199 | 4517971 | 239798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | SCADA INDICATED THE BURNING FORK 12KV CKT OPERATED AND LOCKED OUT// MEN WALKING THE MOUNTAIN TO FIND TROUBLE.LIGHTNING HIT RECLOSER.B PHASE RECLOSER ..OFF LINE BACK ON 15.38LIGHTNING HIT RECLOSER.B PHASE RECLOSER ..OFF LINE BACK ON 15.38 RELEASED BY CREW 076S01 VER/ARN AJB CDC86 PER DISP LOG AND ALARM LOG.
144 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-02-22 05:12 | 2009-02-22 16:00 | 1067 | 648 | 50199-1 | 238575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308001 - SERVICER FOUND A BURNED UP POLE AND OPENED LINE FUSE TO ISOLATE... STS GOT POLE 1108-569 BURNED OFF , GOT CREW COMMING TO HELP WITH POLE. THIS SERV BASEBALL FIELD LIGHTS, NO RES. CUSTOMERS POWER RESTORE AT 1550 RELEASED BY CREW 077S05//VER/CRB IDC XXXX
145 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-12-29 08:49 | 2011-12-29 12:39 | 1425 | 230 | 4212561 | 238220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW MAKING REPAIRSLINE BURNED DOWN.876-25 TO 876-28..ISOLATED ON P 876-198 AT 10.04..LINE BURNED DOWN.876-25 TO 876-28..ISOLATED ON P 876-198 AT 10.04.. RELEASED BY CREW 076S01 VER/ARN IDCC CNT2295 XXXX
146 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-09-12 07:07 | 2015-09-12 11:51 | 837 | 284 | 4230651 | 237708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW ON SITE MAKING REPAIRS RESTORED 1151 VER/ARN // VER TIMES PER SCADA & DISPATCH LOG L3/HFP HFPXXX AJB
147 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-03-10 17:36 | 2011-03-11 10:19 | 1012 | 1003 | 53128-1 | 237672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1104-38 BURNED OFF,WILL REPLACE IT.DEWEY AKERS.CUT LOOPS ON 1104-54,CLOSED REC 1056-299 TO THAT POINT.RECL 1081-99 WAS OUT,OPEND 1081-299 IN ORDER TO CLOSE 1081-99 RELEASED BY CREW 074S06 // 0610 - CREW REPORTED 0900 ON RESTORATION //MADE MDC//VER/CRB IDC WENT THROUGH RECLOSERS, INVESTIGATING COORDINATORS. XXXX
148 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-07-23 13:21 | 2008-07-23 18:35 | 934 | 314 | 58260-1 | 237347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FOUND BAD INSULATORS ON POLE 69-5 ISOLATED AT POLE 45-24 LEADS REMOVED AND TAGS PLACED, DONNY JENT PLACED GROUNDS MAKING REPAIRS, PATROLLING LINE TO RELEASED BY CREW 076H02// ACBS CALL - CUST IS ON MLR OK IDC CHANGED TIME OFF FROM 1922 7/22 XXXX
149 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-05-04 07:45 | 2009-05-04 14:21 | 1048 | 396 | 65386-1 | 237120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SERVICER FOUND WIRE DOWN POLE 902-138, ISOLATING ON 902-116 AND PICK UP CUSTS, AND BACKFEED FROM THE SILOAM STA. PHASE FALL OFF END OF ARM ON 901-128, I CUT LOOP ON 902-116, THEN I FOUND A BAD TWO HOLE PAD ON POLE 302SS50, ON A 600AMP DISCONNECT, WELL NEED TWO HOLE PAD, AND NEW 600AMP DISCONNECTED SWITCH, MR. TOLLIVER IS ON THE SITE AT THIS TIMEPHASE FALL OFF END OF ARM ON POLE 901-128, I CUT LOOP ON 902-116, THEN I FOUND A BAD TWO HOLE PAD ON POLE 302SS50, VER/TOM L3/TOM IDC XXXX
150 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-01-12 09:29 | 2018-01-12 18:34 | 884 | 545 | 4734481 | 236899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 796560 // BURNT OFF POLE @ 38830828000282//WILL HAVE TO OPEN BREAKER TO MAKE REPAIRS//cutout broke down burning the top of pole off. p-828-282..roger maynard called..dig # 1801120201..//opened Feeder @ 0929 via SCADA //cod 643 // see DOL for step times and cust counts
151 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-01-06 04:10 | 2017-01-06 08:14 | 970 | 244 | 4272691 | 236680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SCADA TRANSMISSION OPERATIONS SUGGEST EAST PRESTONSBURG STATION TRANSFORMER LOCKOUT//COD 609///DKM/0834/ARRESTOR BLEW ON STATION SERVICE PHASE 3/// VER/DKM // VER PER SCADA & DOL L3/HFP HFPC TOF0415 AJB
152 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-02-20 02:40 | 2015-02-20 14:02 | 395 | 682 | H4046741 | 233554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 PHASE DOWN ON POLE 900-6.1 REC OUT ON 876-28.OPENING UP OTHER 2 REC.OPEN AT 2.40.//TAGGED TO DDC//..2AA WIRE AND SLEEVES..3 MAN CREW. TRUCK ACCESSIBLE.. RELEASED BY CREW 076S01 AJB SEE 4046741 FOR INLT OUTAGE.
153 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-08-08 00:50 | 2019-08-08 02:47 | 1979 | 117 | 4856841 | 231543 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 944833/SCADA indicated Johns Ck-Meta 34kV ckt L/O, interrupting 1979 cc/patrolling/Found broken insulator at pole 38821083D00092/Making repairsDOL 944833///////FOUND BAD INSULATOR ON STATION EXIT POLE,REPLACED IT.THEN FOUND A BAD REGULATOR ON A PHASE AT STATION EXIT.ISOLATED THAT PARTICULAR REGULATOR Released by crew 074S06 ¦¦¦ VERIFIED TIMES PER SCADA & DOL = L3/HFP
154 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-09-22 05:05 | 2014-09-22 11:32 | 1050 | 387 | 4517441 | 231110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | INST TARGETS PH A & B. PATROLLING. GUY STRAIN INSULATOR BROKE AND ALLOWED PHASE CONDUCTORS TO SAG INTO TREE TOPS. OPENED SW ON 882-953 TO ISOLATE. CLOSED BREAKER @ 8:06 RESTORING UP TO OPEN SW ON 882-953. TAGGED TO S HALL. RELEASED BY CREW 076S02 VER/DKG L3/DKG AJB
155 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-03-04 20:54 | 2015-03-04 23:07 | 1737 | 133 | 4103191 | 231021 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FEEDER BREAKER LOCKOUT @ 2054 PER SCADA//SERVICER ENROUTE/ FAILED INSULATOR ON EXIT POLE/ CREW ENROUTE/ RELEASED BY CREW 074S01 VER/KEP - TIMES PER SCADA & LOG - L3/HFP FP AJB
156 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-10-02 23:55 | 2014-10-03 06:45 | 703 | 410 | 4546131 | 230205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 503-C2-43 BROKEN, TRUCK ACCESSIBLE NEED FLAGERS. OPENED GOAB ON POLE 478-294,TO ISOLATE TROUBLE.NEED LINE CREW. RELEASED BY CREW 078S01/,,CREW ON SITE,,ALL REPAIRS MADE, CLOSED GOAB AT 06:45 RELEASED BY CREW 078H03 // VER TIMES BY VOICE RECORDER SEE DUP FOR WV CUST`S // VER/HFP L3/HFP AJB
157 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-01-07 07:41 | 2010-01-07 11:53 | 900 | 252 | 64821-1 | 226800 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | OUTAGE NECESSARY TO ALLOW CREWS TO MAKE REPAIRS TO A LOOP THAT BURNT OPEN IN THE DORTON-ELKHORN CITY-ELWOOD 46KV CIRCUIT VER/HFP L3/HFP IDC XXXX
158 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-02-07 15:19 | 2019-02-07 17:26 | 1849 | 127 | 4764411 | 226695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CB Opened cod-1849///cross arm broke on pole 215-42..will need line crew with 8ft cross arm and 19.9 xfm cutout and bracket.. ¦¦¦¦ VERIFIED TIMES PER DOL - L3/HFP/// Dol Comments: Reason: Failed crossarm at pole 3783-0215-A0-0042
159 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-02-01 16:51 | 2010-02-01 19:27 | 1492 | 156 | 62118-1 | 225572 | TRANSMISSION STATION | EQUIPMENT FAILURE | BREAKER | STATION TR OUTAGE. **UPDATE AT 1840 T-DISP. IS PROCESS OF REST. TR AT THIS TIME ASAP KYDDC WILL CLOSE META AND RACCOON CREEK CB VIA SCADA . HAZARD AT 27 R FORK IS TV CABLE//REC IS OPENED AT 1802 TO ISOLATE SO CREW CAN PUT PHASE BACK ON INSULATOR, THIS HAD NOTHING TO DO WITH STA OUTAGE//VER/CRB IDCC CNT1465 XXXX
160 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-11-23 05:00 | 2013-11-23 11:45 | 556 | 405 | 4066641 | 225180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE ** MAY BE POSSIBLE TO LOWER * CREW ENROUTE TO MAKE REPAIRS. VER/CRB L3/HFP IDC XXXX
161 | Hazard | 3303901 | LESLIE | HYDEN | 2009-08-03 17:55 | 2009-08-03 23:19 | 990 | 324 | 51724-1 | 225180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STATION FEEDER BREAKER OPERATED DUE TO UNKNOWN TROUBLE AND REMAINS OPEN// SERVICER IS ENROUTE // VER/HFP 37830412D00278 WE HAVE A BROKEN C/O/// POLE 37830412C00103 IS SWITCH POLE WE CAN OPEN SWITCHES AND ISOLATE HURRICANE BR. AND TRY TO CLOSE STATION BR. AND GET POWER RESTORED TO MOST? // 2131 CB CLOSED // SWITCH CLOSED @ 2319 L3/HFP IDC XXXX
162 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-02-06 00:06 | 2020-02-06 14:45 | 359 | 879 | 4366761 | 225121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3308602/gaj/0209/patrolled line no problems found, tried OCRs & tripped back out, continuing patrolling for cause --- gaj/0351/tried OCR found failed insulator at 421-150, opened GOAB at 421C3-172 & tagged to George Whitaker to isolate fault bad insulators on pole 421-150 /// gaj/0359/OCRs closed restoring 140 CC3308602/gaj/0011/all out possible Reclosers out at 37830398B22384 affecting 359 customers disp 3114 R Maggard. bad insulators on pole 421-150 L3/HFP
163 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-01-17 00:26 | 2022-01-17 08:22 | 472 | 476 | 4356751 | 224672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Broken stirrup on a solid blade at pole 248-C-559. This is manual and help is on the way. Closed at 248-559 @ 0822 confirmed by SCADA//
164 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-05-06 17:20 | 2022-05-06 21:16 | 946 | 236 | 4849181 | 223256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1203889 // PowerOn restore predicts feeder lockout @ 1720 // cod 946 // Insulator failed on 833-403. Repairs underway. Released by crew 076S02 Cb closed at 2116 restoring all customers
165 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-04-29 19:49 | 2022-04-30 00:20 | 989 | 271 | 4816321 | 223166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | DOL 1201992/POR PREDICTED CB OPENED AT 1949/CREWS EN ROUTE TO ASSESS Released by crew 077S11
166 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-06-20 17:14 | 2015-06-20 20:19 | 1323 | 185 | 4621881 | 222777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELATED TO 4620741/SERVICER OPENING RECLOSER 141-116 DUE TO POLE FIRE INSULATOR BURNING/CREW ENROUTE/OPENED RECLOSER 1820 (SEE 4623331)/ OPENING SWITCH ON POLE 93-261, CLOSED RECLOSER BACK IN @ 1925//RELATED TO 4620741/SERVICER OPENING RECLOSER 141-116 DUE TO POLE FIRE INSULATOR BURNING/CREW ENROUTE/OPENED RECLOSER 1820/ OPENING SWITCH ON POLE 93-261, CLOSED RECLOSER BACK IN @ // REPAIRS MADE RELEASED BY CREW 074S05//COD 1320 AJB
167 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-01-24 10:12 | 2020-01-24 12:31 | 1965 | 139 | 4334471 | 222490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLR OPEN,SHOWING B&C PHASE FAULT//isolated failed insulator by opening SW 38821057D00215 and closed RECL 38821083B00145 @ 1124 //restored 743 cust//MADE REPAIRS,CLOSED 1057-215@12:28 (288 cust) //closed 1081-99 @ 1231 (934 cust) // L3/HFP
168 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-09-19 10:56 | 2012-09-19 15:58 | 868 | 302 | 4068281 | 221400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 1090A287 BROKE WHILE CREW WAS REPLACING IT .WIRE DOWN.STATION BREAKER LOCKED OUT...OPENED & TAGGED SWITCHES ON 1090B288 TO ISOLATE TROUBLE..STA BREAKER CLOSED IN UP TO POLE 1090B288 @ 11:30.// RELEASED BY CREW 080S01 VER/KEP IDC XXXX
169 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-04-03 10:47 | 2009-04-03 13:21 | 1431 | 154 | 64579-1 | 220374 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | 3311101// SCADA INDICATES STATION OUTAGE HERE @ 10:47 // BUS REG ON PH 1 BURNED UP3311101// SCADA INDICATES STATION OUTAGE HERE @ 10:47 // BAD REG VER/KEP L3/KEP IDC XXXX AJB PER ALARM LOG AND DISP LOG.
170 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-06-26 06:06 | 2009-06-26 14:55 | 479 | 529 | 61570-1 | 220071 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DENSIL WHEELER ON SITE BEGINNING WORK TO REPLACE BROKEN CROSSARMS/// RELEASED BY CREW 078S04 VER/KEP L3/KEP IDC XXXX
171 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-11-01 00:30 | 2014-11-01 11:29 | 1205 | 659 | 4678561 | 218552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATD THE STAFFORDSVILLE 12KV CB B OPERATED TO LOCKOUT//1205 CUSTOMERS OUTAGED// SERVICER PATROLLING AND RUNNING DOWN HAZARD CALLS// @ 0224 CLOSED STATION CB VIA SVC// ENERGIZED TO 761-290 TOP OF POLE BROKE OUT. CREWS WORKING TO REPAIR. INSULATOR BROKE DOWN AND BURNT POLE OFF AT GUY FITTING. RELEASED BY CREW 076S02 VER/SEF L3/HFP HFPC TOF0032 AJB
172 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-05-23 04:51 | 2018-05-23 10:54 | 1056 | 363 | 4399321 | 218208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | only A phase open, open other 2 @ 0907 pole 69-191 a phase loop open, switches open @ 69-124 tagged to ddc.hold order to m. phelps. Released by crew 078S07--crew on site--making repairs--repaired 2 burnt loops on buck pole 69-129--released Hold Order @ 10:50--closed 69-124 @ 10:54---pwr restored 10:54---tbl tkt comp--rmv Released by crew 078H16
173 | Pikeville | 3402003 | KEYSER | MULLINS | 2013-10-18 04:59 | 2013-10-18 13:04 | 1109 | 485 | 4945231 | 217464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38831127B00294 BURNED OFF// OPENED AND TAG ON POLE 1127-257// BREAKER CLOSED AT 6:27 RELEASED BY CREW 074S05 CLOSED 1127-257 AT 13:02 CLOSED 1127-821 AT 13:04 RELEASED BY CREW 074H04// VER/DBM L3/HFP IDC CHANGED START TIME FROM 0457, THREE PHASE ANGLE POLE XXXX
174 | Hazard | 3308002 | JACKSON | PANBOWL | 2020-12-22 16:29 | 2020-12-22 20:02 | 1024 | 213 | 4795731 | 215412 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | DOL 1078079 // fire on station TR 1 at Jackson // interrupted station to isolate // station servicer(s) enroute //cod 1024 //
175 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-11-04 03:21 | 2008-11-04 11:46 | 567 | 505 | 61951-1 | 214824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | VER/HFP GOT POLE #1086-7 BROKE , CALL GREG SHOUSE AND HE IS GETTING CREW TO COME TO HELP GOT RECLOSER BACK IN TO POLE# 1086-6 AT 0543 ROTTEN POLE, REPLACED NEUTRAL YESTERDAY IT PULLED THE TOP OF ROTTEN POLE OVER AFTER IT GOT COLD ORDER 62083-1 CREATED FOR OUTAGE TO MAKE UP LOOPS/ IDC XXXX
176 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-09-05 07:30 | 2011-09-05 15:30 | 1493 | 480 | 4814971 | 214173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WEST VAN LEAR CKT OUT **** SERVICER PATROLLING CKT , ADD. HELP CALLED OUT. CUTOUT BROKE DOWN AND BURNED ARM OFF ON RECLOSER POLE.CUTOUT BROKE DOWN AND BURNED ARM OFF ON RECLOSER POLE. ISOLATED LATTERAL - CLOSED BREAKER @ 9:53. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE.CUTOUT BROKE DOWN AND BURNED ARM OFF ON RECLOSER POLE. ISOLATED LATTERAL - CLOSED BREAKER @ 9:53. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. RELEASED BY CREW 076S02 VER/HFP L3/HFP IDC XXXX
177 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-11-30 23:36 | 2016-12-01 11:17 | 347 | 701 | 4155751 | 212771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAGS IN PLACE @ 37830262000034; REC. OPEN ON POLE 262-177/OPENED 262-177 AT 0405 TO CLOSE GOAB 262-C1-315 WHEN CLOSED BACK AT 0413 RECL 214-D-175 OPENED- OPENED SW AT 262-34 THEN CLOSED AT 0433 THEN CLOSED RECL 262-177 AT 0436/FOUND BAD CUTOUT ON POLE 262-C1-317.MADE REPAIRS..BUT STILL FEEDS THROUGH REC. 262-177 AND TAKING REC. OUT ON POLE 214D-175.ENERGIZED BACK TO SWITCH POLE 262-34.ISOLATED AND TAGGED TO DDC. NO GROUNDS PLACED.MAY HAVE BAD DEAD-END INSU DDC TAGS OFF 0853 VER/AWD AJB
178 | South Williamson | 3411401 | DEWEY | INEZ | 2012-07-08 17:11 | 2012-07-09 01:02 | 1099 | 471 | 4611991 | 212608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BROKEN POLE 791-63 // OPENED SWS POLE 815-A-151 & 791-C-160 - HOLD ORDER ISSUED // N.O. 34KV DA SWS POLE 746-B-218 CLOSED //REPLACED BROKEN CROSS ARM////CLOSED SWITCHES IN @ 01:02 RESTORING ALL CUST.///COMPLETE BR //VER/GAH IDC 768-225 CLOSE 20:09, 767-111 CL 20:10, 838-155 CL 20:33, 815-151 CL 0102 XXXX
179 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-01-07 07:42 | 2010-01-07 11:51 | 850 | 249 | 64822-1 | 211650 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | OUTAGE NECESSARY TO ALLOW CREWS TO MAKE REPAIRS TO A LOOP THAT BURNT OPEN IN THE DORTON-ELKHORN CITY-ELWOOD 46KV CIRCUIT VER/HFP L3/HFP IDC XXXX
180 | Hazard | 3311103 | STINNETT | WENDOVER | 2010-05-06 03:26 | 2010-05-06 09:55 | 542 | 389 | 56281-1 | 210838 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | TRANSMISSION OUTAGE / PATROLLING BY HELICOPTER / OUTAGE FROM 1916-1924 RETURNING CKTS NORMAL. IDC XXXX
181 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2022-07-18 03:42 | 2022-07-18 06:28 | 1266 | 166 | 4508591 | 210156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DDC TAGS / DOL 1222982 / HOLD ORDER REQUIRED /Released by crew 078H33 broke set of crossarms @ 69-650 switching complete // At 0628 closed SWS at 3883-0069-C4-5608 restoring all customers from 47th Street/39th Street 12kV Ckt
182 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2018-10-20 03:59 | 2018-10-20 12:06 | 431 | 487 | 4271841 | 209897 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulaters on pole 514-1.Crew called
183 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-07-22 14:24 | 2020-07-22 22:28 | 1239 | 373 | 4202131 | 208319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1038711 // predicted feeder outage // cod 626 //. opened switches on p-654-456 at 16:40.bad insulator on p-678-166. // cod 626 //777-6 restored at 2228
184 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-02-28 23:15 | 2009-03-01 13:15 | 328 | 840 | 52635-1 | 207440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307301 OUT SIDE PHASES OPEN AC PHASE CC 303 PATROLLING /POLE 37830153B00074 BURNED INTO AT CROSSARM NEED 4 MAN CREW MANUEL POLE/ OPENED SWITCHES AT 153-84 AT 00:50 CLOSED AT 177-287 AT 01:05 CUST OUT FROM POLE 84 TO OPEN RECL ENTIRE OUTAG. CREW WILL BEGIN AT DAYLIGHT . 126 CC TRANS TO HADDIX/QUICKSAND SEE LOG.3307301 VER/KEP L3/KEP IDC B & C PHASE IDC XXXX
185 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-10-08 22:37 | 2009-10-09 03:14 | 1049 | 277 | 66163-1 | 207125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3308001//CROSSARM BROKEN POLE#1083-D3-261 3308001// BROKE CROSSARM RELEASED BY CREW 077S05//VER/CRB IDC XXXX
186 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-06-08 14:34 | 2015-06-08 22:09 | 453 | 455 | 4532391 | 206115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | C PHASE SWITCH OPEN ONLY/ GONNA OPEN C PHASE RECLOSER TO CLOSE IN SWITCH AND THEN CLOSE BACK IN RECLOSER.300CUTOUT OPEN ON C PHASE AT POLE //OUT FROM EARLIER OUTAGE//OPENED RECLOSER TO CLOSE SWITCH//RESTORED RECLOSER AT 22:09//COMPLETE//EM RELEASED BY CREW 079S01/PER BUB SHETLIFF CLOSE IT RESTORED/ AJB
187 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-05-17 14:14 | 2009-05-17 19:55 | 980 | 341 | 61157-1 | 204424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409303//OPENED BREAKER @1414 TO ISOLATE POLE FIRE , WILL WORK TO MAKE REPAIRS OR SECTIONALIZE AND TRANSFER CUSTOMERS @ 1530 UPDATE POLE IS IN DIFFICULT LOCATION TO ISOLATE AND OR TRANSFER CREWS ARE TRYING TO FIND SOLUTION. * UPDATE *//VER/CRB @ 1601 , CB ISOLATED FOR HOLD ORDER. CREWS CUTTING LOOPS AT POLE 833-C-587 , AFTER THIS IS COMPLETE CB CAN BE REST. APPROX. 80% OF CUST REST. BY 1730 . IDCC TOF1357 XXXX
188 | South Williamson | 3411401 | DEWEY | INEZ | 2014-01-29 08:29 | 2014-01-29 11:29 | 2575 | 180 | 4322511 | 204024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SEEING FLICKER DUE TO RECLOSER OPERATIONS ON ORDER 4322431//MIDDLE PHASE BLADE BURNED OUT OF GOAB ON POLE 838-139//CREWS MAKING REPAIRS//REPAIRS MADE//RESTORED AT 11:29// RELEASED BY CREW 079S01 IDCC FEC58, CHANGED START FROM 0636, MIDDLE PHASE AT SWITCH AND FIRST 2 DA RECLOSERS WERE OUT. XXXX
189 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-07-01 21:40 | 2018-07-02 04:18 | 506 | 398 | 4701881 | 201388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Sec. open @213-66, patrolling. Bad pole top insulator @237-A-24, Joey Reed crew coming to change. Made repairs, closed sec. back in @0418.
190 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-04-24 05:43 | 2011-04-24 12:07 | 1164 | 384 | 63372-1 | 201222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BREAKER OPEN COALTON, US 60.. POLE BURNED OFF UNDER CROSSARM ON RECLOSURE POLE 186-75.. OPENED 600 AMP DISC AN TAGED AT POLE 38830186000158 BREAKER BACK IN 07:14--CUT LOOPS AN INSTALLED MACS ON POLE 38830186000064 --REMOVED TAGS AN CLOSED 600AMP DISC ON POLE 38830186000158 AT 08:27RELEASED BY CREW 078S07 IDC XXXX
191 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-04-24 02:57 | 2018-04-24 14:22 | 293 | 685 | 4270531 | 200705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | end of deadend insulator pulled out on pole 166-16 causing wire to lay on arm burning top of pole out and into crossarms..will need line crew with 9ft set of arms and big bucket to frame down on pole and put one phase of 4/0 alum back up from pole 166-16 to 166-17.talked to Tim Hall and will work @ regular shift. made safe. no tags and no grounds placed. Released by crew 074S01// Crew is on site making repairs./// Repairs made closed in at 14:22 Tim McCoy Released by crew 074H10 // PER SERVICER INSULATOR FAILED L3/HFP
192 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-05-12 19:13 | 2016-05-13 03:01 | 454 | 468 | 4209431 | 200614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FOUND WIRE PULLED OUT AT RECLOSER POLE 1/0 SLEEVE---SHOUSE IN RT-30 FT SPAN---WILL HAVE TO DROP FEED TO MAKE REPAIRSMAY HAVE ANOTHER FAULT B,C SHOWING// TRIED TO CLOSE @ 2321 - OPERATED STATION CB// CREW SAW FLASH OVER THE RIVER//TOMFOUND WIRE PULLED OUT AT RECLOSER 1/0 SLEEVE---SHOUSE IN RT-30 FT VER/TOM L3/SPAN---WILL HAVE TO DROP FEED TO MAKE REPAIRSMAY HAVE ANOTHER FAULT B,C SHOWFOUND WIRE OFF INSULATOR OPENEN GOAB AT 54--FOUND WIRE PULLED OUT AT RECLOSER POLE 1/0 SLEEVE---SHOUSE IN RT-30 AJB
193 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-12-16 15:12 | 2008-12-16 20:10 | 671 | 298 | 59052-1 | 199958 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SCADA INDICATED THE SOUTH PIKEVILLE/PIKEVILLE 12KV CB B LOCKED OUT @ 1512 // FOUND TROUBLE @ POLE 48-49,CROSSARM BROKEN 2 SPANS OF LINE DOWN CREW ENROUTE //VER/GAH L3/KEP IDC LOOKS LIKE REPLACE ARE ON 48A4/47 XXXX
194 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-06-18 17:58 | 2015-06-18 23:36 | 659 | 338 | 4601251 | 199502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | KYDDC OPENED ALL KEYSER CKTS VIA SCADA @ 1842 DUE TO PROBLEM WITHIN THE STATION//LTC REPAIRED AND FEEDER RESTORED 2336//COD 1087 // TIMES PER SCADA & LOG SEE DUP H4601251 FOR INITAL C PHASE OUTAGE VER/HFP L3/HFP AJB
195 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-02-07 22:26 | 2017-02-08 00:05 | 2015 | 99 | 4369511 | 199485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FAILING INSULATER ON POLE 1082-340//WILL NEED TO TAKE OUTAGE ONCE CREW ARRIVES AT RECLOSER POLE 38821083B00145//COD 2015//FAULT 38821082C40340/2226-0005. NO OUTAGE UNTIL 2226. VER/AWD /// VERIFIED TIMES PER VOICE RECORDER = L3/HFP XXXHFP AJB
196 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-05-01 11:27 | 2018-05-01 20:15 | 581 | 513 | 4293761 | 199220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Top of angle pole 37830178D00040 rotted off. Manual pole. replaced pole 178-40 Released by crew 077H14 // ADDED STEP FOR INTERRUPTION FROM ORDER 4295711 TO THIS ORDER - SEPARATE ORDER CREATED TO RETURN CKT TO NORMAL - MAKING IT A DUPLICATE- VERIFIED TIMES FROM DOL Case #: 822355 = L3/HFP
197 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-02-16 08:04 | 2018-02-16 12:48 | 699 | 284 | 4848331 | 198516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | rec. locked out on pole 214-175/////will patrol////tried rec. and came back out... showing A and C phase fault..crew found bad insulator at pole 37830239000221 / isolated recls at pole 214-175 and will make repairs - will have to R/T and close SWs at pole 239-284 which were opened when we were planning on transferring to alt source/ rec. locked out on pole 214-175/////will patrol////tried rec. and came back out... showing A and C phase fault/////bad 19.9 cross arms insualtors on pole 239-221 Re
198 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-05-18 13:35 | 2009-05-18 16:50 | 1018 | 195 | 63141-1 | 198510 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3308002// TRANSFORMER AT STATION TRIPPED OUT...SERVICER DISPATCHED & STATION PERSONEL ALSO ENROUTE TREE FELL AND SPLIT POLE#1083-886 LINES OK LOOKS LIKE A HIGH GUST OF WIND TOOK TREE DOWN THIS WASN`T THE CAUSE OF OUTAGE/BAD UG/ WR#29870820 IDC 12KV UG CABLE TO BUS WAS FAILED XXXX
199 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-05-22 17:05 | 2011-05-22 21:15 | 802 | 250 | 4123051 | 198495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATES FEEDER BREAKER LOCKOUT @ 1703 // UPPER ROCKHOUSE BREAKER OUT BAD INSULATOR ON POLE 376-202.. OPENED GOAB ON POLE 376-385 TO ISOLATE AT 18:55 ***CB WILL REMAIN OUT UNTIL REPAIRS ARE COMPLETED. FIELD SWSCADA INDICATES FEEDER BREAKER LOCKOUT @ 1703 // UPPER ROCKHOUSE BREAKER OUT BAD INSULATOR ON POLE 376-202.. OPENED GOAB ON POLE 376-385 TO ISOLATE AT 18:55 FIELD SW.. CLOSED GOAB ON 376-385 AT 20:57.. CLOSED CB AT 21:10 * 1 OUTAGE FOR HOIS. 1705-2110
200 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-08-01 02:47 | 2021-08-01 21:10 | 234 | 1103 | 4988621 | 197950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3 broke poles Ocr out on 529/143 patrolling 553A/56 58 and 85 all broke opened switch on 553A/193 tagged to P.Hicks 529/143 closed ocr at 07:26 EST. time 23:30 Released by crew 077S03. poles replaced, closed sw
201 | Hazard | 3311101 | STINNETT | REDBIRD | 2013-11-24 02:41 | 2013-11-24 13:20 | 769 | 639 | 4068811 | 197907 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER PATROLLING// 3 PHASE RECLOSER LOCED OUT// ADX LOADING SHOWS FAULT ON MIDDLE PHASE (AT STATION)37830459B00084 // ISOLATING FAULT OPEN 459-B-120 AND 458-D4-364 // CLOSED 459-B-166 @ 0523 RESTORING 12 CC// CLOSED 505-65 @ 0600 RESTORED TRANSFER APPROX 602 CC// **HOLD ORDER ISSUED TO TIM SMITH SEE DOL.SERVICER PATROLLING// 3 PHASE RECLOSER LOCED OUT// ADX LOADING SHOWS FAULT ON MIDDLE PHASE (AT STATION)37830459B00084 // ISOLATING FAULT OPEN 459-B-120 AND 458-D4-364 // VER/HFP L3/HFP IDC XXXX
202 | Hazard | 3310502 | HADDIX | CANOE | 2009-06-17 14:55 | 2009-06-17 18:37 | 891 | 222 | 63913-1 | 197802 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S05 BAD CUTOUT ON POLE 50-135 CUTOUT DID NOT SERV ANYTHING
203 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-01-10 23:20 | 2017-01-11 06:20 | 573 | 420 | 4285211 | 196587 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PER DOUG WILLIAMS, P&C, WIRE DOWN REPORTED TO BE AT POLE 1100-220//COD 573// DEAD-END ISULATOR ON CORNER POLE FAILED CAUSING CONDUCTOR TO FALL INTO ROADWAY , REPLACED INSULATORS POLE 220 & 219, ALL WORK COMPLETE / GXJ// VER/DBM /// VER PER VOICE RECORDER - ADDED STEP FOR CUST THAT DID NOT PICK BACKUP WHEN RECL CLOSED (42 A PHASE CUST) FROM ORDER 4285741 = L3/HFP HFPC STP AJB
204 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-01-03 11:33 | 2013-01-03 13:36 | 1650 | 123 | 4566271 | 194339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SDB / 1132 / SCADA INDICATES FEEDER OUTAGE. 1650 CC. --- SDB / 1154 / FAILED RIDGE PIN INSULATOR AT POLE 20-4509, PRIMARY DOWN ON TOP OF POLE. WILL NEED CREW TO SPLICE PRIMARY. --- SDB / 1210 / 12KV SWS AT POLE 20-4516 OPENED & TAGGED TO KYDDC ---- SDB / 1217 / CB CLOSED, RESTORES 109 CC --- SDB / 1336 / SWS AT POLE 20-4516 CLOSED, & CB CLOSED.. ALL CUST REST. SECOND CB OUTAGE FROM 1331-1336 ON PO ORDER 4566721. IDCC TON1355 STP ONE XXXX
205 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-01-09 05:25 | 2008-01-09 15:10 | 466 | 585 | 55004-1 | 194200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202//ON SITE, PATROLLING LINE//POLE TOP BURNT ON 1185-36//OPENED SOLID BLADES ON POLE # 1139-109 AT 0727// RELEASED BY CREW 080S01 // ISOLATING SWITCH CLOSED UP TO THE TWO SETS OF RECLOSERS ON 11-536 @ 1505//@ 1510, RECLOSER FEEDING HURRICANE CRK CLOSED//@ 1510 OTHER REC ON POLE 11-536 CLOSED ON A & B PHASES BUT C PHASE MUST BE BYPASSED//C PHASE NOT RESTORED UNTIL 1518//NOT SURE ON CUST COUNT AS MAP SHOW NO C PHASE CUST FROM POLE 11-536 TOWARDS CAMP CRK// VER/DBM IDC XXXX
206 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-06-08 07:39 | 2008-06-08 12:19 | 693 | 280 | 60054-1 | 194040 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | KIMPER 69-12KV STATION OUT 0739 ** GREG HALL AND TERRY FIELDS DISPATCHED TO CHECK.ETR IS PROJECTED WILL UPDATED TIME WHEN MORE IS KNOWN ABOUT THE OUTAGE AT THIS TIME THE STATION TRANSFORMER IS OUT. VER/HFP DEBBIE/CORRECTED TIME OFF IDCC MCCDL XXXX
207 | Pikeville | 3403001 | PIKEVILLE | CITY | 2022-01-29 20:36 | 2022-01-29 23:50 | 1203 | 194 | 4415301 | 193562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SCADA indicated loss of voltage on ph 2 near station/Opened CB at 2059/Ph down at 24-765/Backfed arena N.O. 48-C1-1303 @ 2200/HOLD ORDER REQ/DOL 1179457/SCADA indicated loss of voltage on ph 2 near station/Opened CB at 2059/Crews en route to assess. Bad connection burndt down C phase coming off pole 24-B2-765, Shawn Goble crew coming to help with repairs.SCADA indicated loss of voltage on ph 2 near station/Opened CB at 2059/Crews en route to assess. Bad connection burndt down C phase coming off
208 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2018-09-24 03:23 | 2018-09-24 16:36 | 452 | 793 | 4147941 | 193548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HOLD ODER/ all 3 reclosers are open, found pole 177-57 broke off at telephone, will have to replace. bad manuelall 3 reclosers are open, found pole 177-57 broke off at telephone, will have to replace. bad manuel. opened solid blades on pole 201-42, closed reclosers back in at 08:56/ closed switch 37830201C10042 @ 1831 (39cc)///// 303 went back out around 1400, see related outage.
209 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-10-28 13:42 | 2009-10-28 18:36 | 658 | 294 | 63283-1 | 193452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 32427958 // FOUND POLE BURNTED OFF, POLE NUMBER IS 1121-59, WHICH IS A 452, SHOULD BE ABLE TO USE CROSSARMS AND INS, BACK, NO DAMAGE TO THEM, I SAVED THEM, I PUT THE FIRE OUT, WELL NEED CREW TO MAKE REPAIRS, HAVE 3 RECLOSER ISOLATED ON POLE 1098-B1-24, DO NOT HAVE GROUNDED, DID NOT HAVE ANY MORE GROUNDS,FOUND POLE BURNTED OFF, POLE NUMBER IS 1121-59, WHICH IS A 452, SHOULD BE ABLE TO USE CROSSARMS AND INS, BACK, NO DAMWR # 32427958 // FOUND POLE BURNTED OFF, POLE NUMBER IS 1121-59/CREW ON IDC XXXX
210 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-11-07 11:57 | 2019-11-07 16:15 | 1806 | 258 | 4006151 | 193148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 4/0 loop on D.E. vertical structure fallen down and contacted fiberglass guy rod ,burning loop into. will do partial restore at aprox, 13:40.open sw on 206-14 and closed in GOAB on #181-401 @ 13:29 for partial restore,.also found poles 206-138a and 230-165 broken at bottom, repaired loops, change poles later,all restored p.hicks Released by crew 077H09 L3/HFP//// times are reversed for restore and open sw 206-14. Did not mark RL4 due to confusion ACB
211 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-11-15 08:23 | 2020-11-15 11:49 | 930 | 206 | 4677231 | 191580 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | Defective TR #1 12kV Reg Disc (Single Step) & Insulator On Ph 3/ Opened JACKSON - SOUTH JACKSON 12KV - CB L at 1119/ power restored 1149
212 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-02-07 20:22 | 2011-02-08 00:35 | 1856 | 253 | 55131-1 | 191468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FEEDER LOCKED OUT SERVICER PATROLLING **UPDATE AT 2128- SERVICER FOUND BAD CLFS WILL ISOLATE AND REPORT BACK.. OTHER SW PERSON READY TO ISOLATE & SECTIONALIZE OR CLOSE BREAKER WHEN READY. ** CB SHOT AT 2150 DID NOT STAY, SMALL LIMB REMOVED AT POLE 143-421 AND AT VER/PDP 2205 CB CLOSED AND HOLDING. DONNIE HAS TR BANK AT POLE 143-3 OPEN AND WILL C/O CLFS AFTER CREW COMPLETES WORK ON LARGER OUTAGE. IDCC CNT1856, TON2319 XXXX
213 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-01-02 23:17 | 2010-01-03 07:50 | 409 | 513 | 58016-1 | 191139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | COD-439/ LOAD ON CB WHEN OUTAGED 286/272/258 AMPS // LOAD AFTER OUTAGE 286/271/0 AMPS // APPEARS "C" PHASE IS OUT ONLY // FOUND LOOP OPEN AT POLE 382-9004 WHICH INTERRUPTED 446 CUSTOMERS/ REPAIRED LOOP & SW ON "C" PHASE //VER/GAH IDC PICKED UP IN STEPS FOR COLD LOAD IT IS PH C BUT ADD 39 MISSMAPPED IDC XXXX
214 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-08-18 09:36 | 2014-08-18 12:25 | 1263 | 169 | 4378311 | 189982 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLYMER INSULATOR MELTED CAUSING A PHASE TO GROUND FAULT. CREW ENROUTE RELEASED BY CREW 074S02 VER/DKG L3/DKG OPENED ON POLE 0170-C3-605 AND CLOSED AT 0194-A-33 AT 1120...MADE REPAIRS CLOSED ON POLE 605 AT 1225 AJB
215 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2022-02-03 00:18 | 2022-02-03 02:46 | 1277 | 148 | 4425841 | 188996 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | DOL 1180514 // SCADA indicates station l/o @ 0017 // cod 1277
216 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-05-06 02:47 | 2018-05-06 13:25 | 369 | 638 | 4313641 | 188892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | recloser open on pole 398-2384, pole 421-147 boke at ground level, open GOAB on 421-172 to isolate, closed recloser at 07:55 closed sw at 1325.recloser open on pole 398-2384, pole 421-147 boke at ground level, open GOAB on 421-172 to isolate, closed recloser at 07:55 power restored at 13:25 37830398B22384 37830421C30172 37830421C30147 L3/HFP
217 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-07-17 13:22 | 2014-07-17 20:28 | 634 | 426 | 4257091 | 187594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SDB / BROKEN CROSS ARM AT POLE 29-8. RECL AT POLE 29-186 OPEN INTERRUPTING 634 CC. SWS AT POLE 29-6 OPEN AND RECL CLOSED AT 1448 REST 118 CC. --- SDB / SW AT POLE 55-32 OPENED AND N.O. TIE RECL AT POLE 104-B-90 CLOSED REST 192 CC AT 1645.. VER/SEF AJBC CNT514 LAST REST STEP. 634 ON OCR.
218 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-02-23 22:39 | 2014-02-24 00:42 | 1523 | 123 | 4429421 | 187329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3-PHASE RECLOSER ON POLE 96-339 IS OPEN. I AM PATROLLING LINE NOW. CUTOUT IS BROKEN DOWN ON POLE 144-20. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT AND CLOSED RECLOSER AT 12:42 //VER/GAH IDC XXXX
219 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2017-03-15 14:36 | 2017-03-15 23:43 | 835 | 547 | 4560091 | 186536 | TRANSMISSION STATION | EQUIPMENT FAILURE | CROSSARM | DOL 727713//1435 = SCADA INDICATED COL3MAN - STONE 69KV LINE LOCKED OUT/T LINE FELL ON D LINE AT POLE 1038-134, MIDDLE PHASE OFF AT POLE 1062-D-241/OPENED SW 1062-40, ENERGIZED STATION DOWN TO THERE @ 1657/ RELEASED BY CREW 079S02 AJB CCTIN FEC57
220 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2021-02-26 16:32 | 2021-02-26 21:04 | 700 | 272 | 4257851 | 185556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A-phase pin and insulator broken/missing on pole 230-B-21 the energized phase laying on the cross arm. Contacting the duty supervisor to help make repairs.//OPENED SW @ 2008 CLOSED @A-phase pin and insulator broken/missing on pole 230-B-21 the energized phase laying on the cross arm. Contacting the duty supervisor to help make repairs. Switches on pole 230-B-22 opened at 20:08 and closed at 20:57//NO OUTAGE TILL 2008.
221 | Paintsville | 3401101 | FALCON | FALC-OILS | 2010-04-25 05:24 | 2010-04-25 13:00 | 648 | 456 | 50577-1 | 183222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401101// 805-217..TOP OF POLE BURNED OFF..DUE TO BAD CUTOUT ..CALLED TIM MILLER POLE CHG OUT .. //VER/GAH IDCC CDC86 TOF0526 XXXX
222 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2019-11-30 04:56 | 2019-11-30 08:49 | 785 | 233 | 4104131 | 182905 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B Phase (380cc originally out) Loop burnt off between the 46-12kV TR 1 and Allen 12kV CB E At Allen (KP)/ opened Allen 12kV CB E @ 0634 (405cc additional)/Loop as burned open between station xfmr and breaker. Will need Foreman to bring 4/0 wire to make repairs and staition servicer to isolate station xfmr/// Released by crew 076S03/ closed Allen 12kV CB E @ 0849 (785cc)//// trouble tickets show all cust out from start
223 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-07-08 20:33 | 2009-07-08 21:40 | 2811 | 67 | 63370-1 | 182739 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3400301//FOUND SURGE ARRESTOR FAILED ON TR ON POLE 1125-41, ISOLATED TR & RESTORED STATION BREAKER AT 2138.RESTORED ALL CUST AT 21:40 VER/DKG L3/DKG AJB PER DISP LOG AND ALARM LOG.
224 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-11-26 05:07 | 2010-11-26 09:13 | 874 | 246 | 59713-1 | 181344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THREE PHASE POLE FIRE WILL OPEN SWS AT POLE 1090-B-288 , FEEDER LOCKED OUT. FEEDER CLOSED AT 0533. D/S CALLED CREW ENROUTE TO CHANGE POLE.POLE FIRE FROM BAD CUTOUT ON POLE 1090-A-13...POLE BURNT IN TWO BELOW CROSSARM.....STA BRKR LOCKED OUT @ APPROX 04:55.....OPENED SWITCHES ON 1090-B-288 TO ISOLATE TROUBLE....CLOSED STA BRKR @ 05:33......CREW ENROUTE....FETR OF 11:30......//....REPAIRS MADE.....IF NO MORE HZRDS, READY TO CLOSE IN AT POLE 1090-B-288....//....CLSED @ 09:13.... VER/TOM IDC XXXX
225 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2020-02-07 08:58 | 2020-02-07 22:12 | 844 | 794 | 4376461 | 180206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recloser is open on 38830478D10090 844cc patrolling line. One phase dn at 38830478D40110. Isolated @38830478D27281//// Recloser 38830478D10090 in @ 1015 Hot to 38830478D27281. Crew making repaires/// Closed 38830478D27281@1248 Released by crew 078S11,pole broke @ 38830502000221 line fuse open @ 38830502000118 & tag to bt,line fuse in @ 2212 Released by crew 078H02
226 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2013-10-17 17:15 | 2013-10-17 22:23 | 1510 | 308 | 4944281 | 179762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CROSSARM BURNT OFF AND PRIMARY PHASES ARE DOWN ON 809-377 DUE TO FAILED CUTOUT. C PHASE RECLOSER ON 785-640 DID NOT OPEN UNDER FAULT AND LOCKED STATION BREAKER OUT. ISOLATED THREE RECLOSERS ON 785-640. //CLOSED STA BREAKER AT 1821 // CREWS WORKING TO REPAIR. COMPLETED REPAIRS & CLOSED RECLOSERS AT 22:23. SH RELEASED BY CREW 076S02 VER/SEF L3/HFP IDC XXXX
227 | Hazard | 3303902 | LESLIE | WOOTON | 2014-02-13 05:42 | 2014-02-13 15:45 | 298 | 603 | 4378991 | 179694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICER WILL CHECK ONCE THE ROAD CONDITIONS IMPROVE// BAD INSULATOR VER/SEF IDC XXXX
228 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-02-22 05:35 | 2008-02-22 09:14 | 1608 | 219 | 66138-1 | 179122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3400303// AT 0646 CLOSED BREAKER BACK IN AND OPENED GOAB AT 1126-518//FOUND MELTED PRIMARY INSULATOR AT POLE 1126-539//INSULATOR IS BAD ON POLE 1126-539. CREW & FLAG MEN ARE IN ROUTE.POWER ON FROM STATION TO POLE 1126-518 @ 06:48 RESTORED GOAB 1126-518 AT 0914 VER/KEP IDC XXXX
229 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-10-28 21:14 | 2017-10-28 23:55 | 2017 | 161 | 4506501 | 178883 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1083-4,CUTOUT ON MAINLINE BROKEN,NEED BIG BUCKET,1 MAN,2 19.9 CUTOUTS///////ISOLATED 1083-4,CLOSED RECLR @22:42////////REPLACED XFR&TAP CUTOUT ALSO RELEASED BY CREW 074S06/// VER/DKM L3/HFP HFPC CNT17 ACB
230 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-06-19 04:40 | 2012-06-19 09:50 | 794 | 310 | 4929941 | 177800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICER PATROLLING CKT * UPDATE @ 0600 - SERVICER REPORTS NO PROBLEMS STILL PATROLLING.**JIM MULLINS WILL MAKE ALL CREW ARRANGEMENTS.SERVICER PATROLLING CKT CENTER PHASE INSULATOR FAILED WILLREQUIRED CREW TO REPLACESERVICER PATROLLING CKT CENTER PHASE INSULATOR FAILED WILL REQUIRE CREW TO REPLACE, MADE REPAIRS CLOSED GOAB 482-288 @ 0950 ///VER/CRB L/3 CRB IDC XXXX
231 | Hazard | 3309302 | VICCO | JEFF | 2019-05-02 19:05 | 2019-05-03 09:36 | 204 | 871 | 4202321 | 177684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | tried to energize the recloser on pole 323-649 but it came back out. Narrowed the issue down to pole 323-241 bad deadend or loop insulator. Need manual ROW crew and line crew in the morning as per supervison. Go up Maple Dr to access the pole. Released by crew 077H20//NO TAGS// L3/HFP
232 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-03-27 16:22 | 2017-03-28 03:51 | 257 | 689 | 4589141 | 177073 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL RECLOSER 37830246B10648 OPENED @ 1622//NO WAY TO TRANSFER CUSTS//COD 257//POLE 245D-13 BURNING , NEED LINE CREW , 45 POLE MATERIAL FOR BUCKARM POLE WITH TAP COMING OF BACK . OPENED RECLOSERS ON POLE 246B-648 @ 16:22 . RELEASED BY CREW 075H04 RESTORED POWER AT 0351/// VER/DKM L3/HFP XXXHFP AJB
233 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2019-03-14 19:08 | 2019-03-15 01:14 | 999 | 366 | 4984321 | 176636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 905407 // Feeder L/O at approx 1908 per customer calls//cod 999//broke pole 878-102//isolating for partial restore // cod 253 opened 3 300 amp switch on 902-116, proceed to station to restore so shore siloam cb B, RESTORED CB AT 2103, TO OPEN PIONT ON 902-116, TG TO RICK MORGAN, crew on site, grd at work site, 452 pole, 3 600amp, 2 10 crossarms, 2 heavy duty braces, 6 2hole pads for 4/0 cu, small bit of 4/0 copper wire, Released by crew 078S06/arrived RM solid blades Released by crew 078H20 ¦¦¦ VERFIED TIMES PER DOL - L3/HFP
234 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-04-03 09:50 | 2009-04-03 17:54 | 372 | 484 | 64526-1 | 176088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REC OUT ON POLE # 174-220 PATROLLING LINE POLE # 198A-47 IS BROKEN MANUAL POLE -3-PHASE//COD 373// POWER RESTORED TO ALL CUSTOMERS. ON AT 1754 - NOT SURE WHAT CAUSED POLE TO BREAK // VER/TOM IDC XXXX
235 | South Williamson | 3411401 | DEWEY | INEZ | 2022-01-09 07:08 | 2022-01-09 11:39 | 1416 | 271 | 4326891 | 175564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | servicer enroute, crew making repairsservicer enroute//crossarm broke on 768-214 Released by crew 079S01/// DOL 1174623
236 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-02-13 06:12 | 2014-02-13 18:10 | 253 | 718 | 4377501 | 175354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER WILL CHECK ONCE THE ROAD CONDITIONS IMPROVE// CLOSED RECL. ON POLE 513 102 AT 17;45 ALL POWER RESTORED BUT TRANSFORMER ON POLE 512 19 WILL B CHANGEING CUTOUT P0WER RESTORED TO POLE 512 ; 19 AT 18:10 RELEASED BY CREW 077H02 -- CAN CLOSE TICKET ALL POWER RESTORED - SEPERATE TICKET WAS CREATED FOR 512-19 (4385191) MWL VER/KEP IDCC STP MISSING, TOF0038 XXXX
237 | Pikeville | 3421001 | BREAKS | CITY | 2016-04-11 12:05 | 2016-04-11 18:31 | 831 | 386 | 4079821 | 173221 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TRANSMISSION CREW MAKING REPAIRS ON HV LINE IN VIRGINIA VER/ARN AJB CCO FEC57
238 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2014-03-09 00:48 | 2014-03-09 13:50 | 336 | 782 | 4462401 | 173077 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LOOKS LIKE POLE 188-60 ROTTED OFF AT GROUND LINE AND FELL OVER. CREW REQUIRED NEED 4 MEN 2 BUCKET TRUCKS LINE TRUCK 40-4 POLE 2 CROSS ARMS BRACESES 3 STEEL PINS INSULATORS CUTOUT ARRESTER 50KVA # 4 COPPER // OPENED LOOPS AT POLES 188-A-63 & 188-A-449, CLOSED RECL 187-15 AT 0825 (50 CC), CLOSE N.O. 188-B-83 AT 0915 (267 CC) FROM WEEKSBURY/DIST CKT // OPENED REC 187-C-15 AT 1334 TO CLOSE LOOPS //VER/GAH IDC XXXX
239 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-10-07 23:51 | 2014-10-08 03:20 | 821 | 209 | 4570611 | 171589 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECL 8-378 IS OUT,C PHASE GRND FAULT,WILL PTRL////////////FOUND BAD CUTOUT POLE 1136-15// REPLACED IT AND RESTORED POWER FRM RECL 8-378// ISO 37820008C10378/// COD 821// VER/BOW L3/HFP AJB
240 | Hazard | 3303901 | LESLIE | HYDEN | 2022-11-15 03:28 | 2022-11-15 06:56 | 879 | 208 | 4143101 | 171577 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | DOL 1252142 // station outage // high side ckt swroperated to l/o at 0328 // cod 879 //
241 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2015-04-04 05:47 | 2015-04-04 10:21 | 626 | 274 | 4272081 | 171524 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | TRANSFORMER FAILURE SWITCHING TO OTHER XFMR.STATION XFR FAULTED AND BAD,XFERRED TO ALTERNATE XFR. RELEASED BY CREW 074S06 VER/KEP L3/HFP XXX AJB
242 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2009-01-22 00:54 | 2009-01-22 04:30 | 789 | 216 | 58987-1 | 170424 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | 3000901//A 69KV INSULATOR ON THE TRANSMISSION LINE HAS FAILED OPENING THE TRANSMISSION LINE/AT 0430 CLOSED SWITCH ON POLE 1124-553 TRANSFERING THE LOAD FROM THE HIGHLAND/RUSSELL 12KV CKT TO THE RUSSELL/BEAR RUN 12KV CKT VER/KEP L3/KEP MLR OK
243 | Pikeville | 3421001 | BREAKS | CITY | 2008-05-11 16:42 | 2008-05-11 19:48 | 916 | 186 | 61587-1 | 170376 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | 1642 ** ELKHORN CITY 69-12 KV TR 1 STATION OUTAGE. LITTLE GRASSY AND CITY 12K FEEDERS OUT.STATION SERVICER AND DENNIS MASSEY ENROUTE.VER/ARN MAFC CC-WL, FEC57 JUST CHANGED CUTOUT ON TRANSFORMER PER CONF CALL
244 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2017-01-15 19:14 | 2017-01-15 23:06 | 812 | 232 | 4300471 | 170223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1914 SCADA INDICATES FEEDER BREAKER LOCKOUT ON THE ALLEN-ALLEN 12KV CKT//BURNT OFF CROSSARM ON RECLOSER POLE 1027-C-590//CALLING CREW//CROSSARM BURNT OFF ON REC POLE DUE TO CUTOUT FAILURE. OPENED SW 1027-64 AND TAGGED TO DDC.//SEE DOL CASE 714714//COD 813//CLOSED CB @ 2059//CLOSED SWS 1027-64 @ 2306 // NOTE DUP DUE TO OMS AREA CROSSING VERIFIED TIMES PER DOL & SCADA L3/HFP AJB
245 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2016-07-08 18:43 | 2016-07-08 22:37 | 726 | 234 | 4584631 | 169884 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | WEST PAINTSVILLE STATION DE-ENERGIZED DUE TO THELMA-THEMLA 69KV LINE OUTAGE//TOM - 1925 - SERVICER IN STATION MAKING CHECKS//TOM- SDB / 2035 / DAMAGED 69KV TRANSFORMER ARRESTER, CREWS MAKING REPAIRS. CLOSED CB @ 2237 VER/TOM L3/TOM AJB
246 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2016-03-28 04:32 | 2016-03-28 17:46 | 682 | 794 | 4886031 | 169103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B& C PH ONLY//COD 369// FAULT POLE 38830381000033//0738 A PHASE RECLOSER OPENED HLT TAGGED TO KYDDC//B& C PH ONLY//COD 369// FAULT POLE 38830381000033// OPENED A PHASE 07:38 TAGED TO DDC PLACED HOT TAG ON.B& C PH ONLY//COD 369// FAULT POLE 38830381000033// OPENED A PHASE 07:38 TAGED TO DDC PLACED HOT TAG ON. NEED LINE CREW TRACK DIGGER AND 40/4 POLE DOUBLE 8 FOOT ARMS . CAN GET 4 WHEEL DR TO POLE.B& C PH ONLY//COD 369// FAULT POLE 38830381000033// OPENED A PHASE 07:38 TAGED TO DDC PLACED HOT AJB
247 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-05-05 07:27 | 2012-05-05 10:54 | 988 | 207 | 4748111 | 168379 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | IS BEING PATROLLEDRELEASED BY CREW 078S01 VER/ARN IDCC TOF0731 XXXX
248 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-03-28 19:46 | 2008-03-29 07:04 | 734 | 678 | 61769-1 | 168037 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001102//FEEDER LOCKED OUT **@ 2129 UPDATE CREW WILL BE ABLE TO CUT LOOPS AND RESTORE CKT IN ABOUT 1 HR FETR ON CKT REST 2230 ,DISPATCHED KEVIN BROWN AND BOB GALLAHER TO PATROL CKT AND ISOLATE FEEDER.//POLE 90-108 BAD CUT BURNT POLE INTO NEED 50-2NEW CUT-OUT BUCK-ARM DOUBLE BRACES ISO-LATED ON POLE90-36 ** APPROX 135 CUST WILL REMAIN OUT UNTIL REPAIRS ARE MADE. VER/ LDA IDC XXXX
249 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-05-18 15:36 | 2013-05-18 18:40 | 1285 | 184 | 4131341 | 167488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 174-28 , NEED BIG BUCKET ONE MAN . ALSO CHANGED XARM. CLOCED GOAB @ 18:40 ///VER/CRB L/3 CRB IDC XXXX
250 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2010-11-26 09:42 | 2010-11-26 17:53 | 602 | 491 | 59783-1 | 167426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3 PHASE ANGLE POLE 454-B4-3507 BURNT, TOP OF POLE HANING BY CONDUCTORS - OPENED SWS 454-B4-3543 OUTSIDE STATION TO ISOLATE POLE// VERNON D/S NOTIFIED - POLE WILL HAVE TO BE CHANGED// THIS OUTAGED 602 CUSTOMERSRELEASED BY CREW 078S12//WR#37889053 // WORKING ON TRANSFERRING CUSTOMERS//CREW ON SITE/FETR 1800/VEM/SHOULD BE ABLE TO SWITCH PRIMARY BACK IN AROUD 1600/VEM VER/TOM IDCC TOF0803 XXXX
251 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2020-12-29 17:19 | 2020-12-29 23:53 | 988 | 394 | 4834111 | 166868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 38830230000086 B Phase loop burnt open on switch (330cc)/ possible need to chg switches and safest to open station breaker/send to mr reynolds Released by crew 078S03,,, Released by crew 078H07/ opened breaker at 2257 658cc/ all power restored 2353
252 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-09-01 22:00 | 2020-09-02 04:50 | 650 | 375 | 4416621 | 166673 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER//DOL 1050488 // Feeder Breaker L/O predicted @ 2200 per PowerOn //We have a broke crossarm on pole 335-B-35,Will need line crew to make repairs.//HOLD ORDER//cod 650//
253 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-12-13 05:56 | 2017-12-13 09:15 | 888 | 199 | 4644441 | 166178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | BREAKER | DOL 790822 // SCADA indicates feeder L/O @ 0556 // Released by crew 074S05
254 | South Williamson | 3411401 | DEWEY | INEZ | 2021-02-20 01:06 | 2021-02-20 13:50 | 248 | 764 | 4189021 | 165600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | recloser out on38830767C00110//closed to switches 767-674//OPENED SW 38830742D10090 AND CLOSED SW 38830767A40674 @ 1112//closed sw SW 38830742D10090 @ 1204 upto recloser 38830790A00112//CUSTOMERS RESTORED @ 1350 ON 02-20-2021
255 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-07-18 05:58 | 2012-07-18 16:02 | 272 | 604 | 4752971 | 164288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER DISPATCHED *911 ETA CALL BACK OF 0600 STS POLE #246-78 IS BURNED OFF, CALL JIM MULLINS AND HE IS GETTING CREW TOGETHER RELEASED BY CREW 077S05 IDCC TOF0501 XXXX
256 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-01-02 05:30 | 2018-01-02 08:15 | 988 | 165 | 4694951 | 163020 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | See DOL Case 794154///69-34kV TR 2 is out--failed phase 1 regulator
257 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-12-08 23:18 | 2009-12-09 03:00 | 734 | 222 | 58982-1 | 162948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PHASE A & B ARE OUT ON POLE 204-264, PATROLLING LINE. OPENING OTHER RECLOSER SO WE CAN GET UP HILL TO SEE WHAT NEEDS TO BE DONE//OPENED PHASE C RECLOSER @ 01:15, INTERRUPTING 681 CUST//, BAD ARRESTER ON POLE 204-7 RESTORED AT 0300 MLR CNT 1414
258 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-08-18 00:24 | 2016-08-18 04:12 | 713 | 228 | 4808281 | 162564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSERS ON P 573-102 BYPASSED AND TAGGED TO DDC BYPASSES IN @ 4:10 VER/KEP /// VER TIMES PER SCADA L3/HFP HFPC TOF0052 TON0410 AJB
259 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-07-21 17:45 | 2008-07-21 19:11 | 1888 | 86 | 56060-1 | 162368 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3411802//MOBILE OVERLOAD//RACCOON AND META//VER/CRB IDC CHANGED FROM OVERLOAD, A FAN WAS NOT OPERATING PROPERLY IDCC TON1841 XXXX
260 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-02-01 03:04 | 2008-02-01 16:26 | 1539 | 802 | 63001-1 | 162270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3401001/FEEDER LOCKED OUT *** SERVICER DISPATCHED. AT 0437 AT POLE 238-184 N.O. 34KV GOAB SWS CK OPEN OK 0425 AT POLE 238-26 N.C. 12KV SB SWS OPEN TAG 0430 AT KENTUCKY DDC SET UP ON SCADA AND CLOSED THE DORTON 34KV CB R AT ELWOOD OK 0437 RESTORES 1512 CUSTOMERSTOP OF POLE HAS BURNED OFF. WE HAVE IT ISOLATED AND CLOSED STATION BREAKER IN AT 04:37. THIS WILL LEAVE 27 CUSTOMERS OUT.// VER/TOM IDCC TOF0306 XXXX
261 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-02-22 06:17 | 2015-02-22 12:00 | 473 | 343 | 4069991 | 162237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE #38831053B00260 BURNED INTO WILL ISOLATE @1053-144NEED STOREROOM MAN 2 A LINEMEN LINE TRUCK MATERIAL HANDLER 50/2 POLE ,10 FT ARM &BRACES POLE TOP PIN 2 STEEL ARM PINS 3 PIN INSULATORS FOR 7200 FIBERGLASS T BRACKET 7200 CUTOUT & ARRESTOR 1 CLEVIS & SPOOL.ALL ON @1053-230 @ 12:00// ISOLATED LOW SIDE OF RECLOSER 38831053B00230 TO TAKE LOAD OFF AND PUT LOOPS BACK ON AT 38831053B00144/ ISO 38831077A00477/ COD 360 TOTAL AJB
262 | Hazard | 3302704 | HAZARD | KENMONT | 2017-05-27 17:56 | 2017-05-27 21:36 | 735 | 220 | 4871071 | 161700 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | RELEASED BY CREW 077H07 TIMES PER SCADA & DOL & SOS 3521 REV 37 L3/HFP HFPC CDC80 FEC78 AJB
263 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-07-21 17:45 | 2008-07-21 19:14 | 1814 | 89 | H56060-1 | 161446 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3411802//MOBILE OVERLOAD//RACCOON AND META//VER/CRB IDC CHANGED FROM OVERLOAD, A FAN WAS NOT OPERATING PROPERLY IDC XXXX
264 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-02-22 10:57 | 2016-02-22 12:53 | 1388 | 116 | 4746851 | 161008 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | POSSIBLE FAULT ON STATION EQUIPMENT AT GRAYSON STATION // STATION SERVICER EN ROUTE //, RELEASED BY CREW 078S05//TR 1 69KV METERING PT FAILED, MOAB DID NOT OPEN BECAUSE RELAYING COULD NOT SEE THE FAULT ON THE PT//TERMINAL BREAKERS ON THE ARGENTUM-LEON 69KV CKT OPENED//SEE ALSO DOL CASE 639195//COD 1388 VER/HFP L3/HFP AJB
265 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2013-01-17 03:17 | 2013-01-17 16:09 | 552 | 772 | 4613431 | 160978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED CB @ 0317 CLOSED @ 0420 CREW ON SITE CHANGING POLE VER/TOM L3/TOM IDCC TOF0225 XXXX
266 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-01-24 17:53 | 2010-01-25 01:15 | 478 | 442 | 58887-1 | 160926 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3008702// STS 33566652 IDC XXXX
267 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2018-10-20 21:45 | 2018-10-21 00:30 | 973 | 165 | 4278461 | 160545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 230-86 a phase 600 amp switch failed ,,,,NO OUTAGE TIL OPENED BREAKER at 2145,, replaced switch and all customers restored @ 00:30 COMPLETE /// VERIFIED TIMES PER DOL Case #: 869108 L3/HFP
268 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-09-14 08:45 | 2017-09-14 12:46 | 661 | 241 | 4361611 | 159301 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | DOL 771556 // CENTER PHASE FUSE OPEN ON STATION XFMR // OPENED 46KY CB D @ BURDINE @ 0941 //N.O. SWS @ 37830382A30267 ALSO BURNT UP//COD 661// VER/DBM L3/HFP HFPC TOF 0855 SJG
269 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-02-12 09:11 | 2022-02-12 10:51 | 1591 | 100 | 4476571 | 159100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Outage to transfer conductor to new pole do to broke pole. Open @ 0911 Closed @ 1051
270 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-06-10 02:56 | 2008-06-10 04:44 | 1472 | 108 | 61205-1 | 158976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3117601// COD-1463 // FOUND PART OF N.O. LINE TIE GOAB SW ON CROSSARM - REMOVED PART OF THE SWITCH AND PLACED TAG. VER/LDA IDCC TOF0301 XXXX
271 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-09-11 07:28 | 2010-09-11 10:12 | 968 | 164 | 65402-1 | 158752 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | FLEMING STATION OUT.. RANDY LOVINS ENROUTE // BROKEN CUTOUT ON STA SER TR - LEAD FELL ONTO STEEL // ALL RESOTRED AT 1012// VER/TOM L3/TOM IDCC MCCDL XXXX
272 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2009-06-13 08:36 | 2009-06-13 11:53 | 804 | 197 | 60108-1 | 158388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND HENDRIX CABLE BURNT DOWN IN SPACER CREW IN ROUTE TCM// AT 0915 TIM MILLER REPORTS HE WILL ISOLATE FEEDER FOR HOLD ORDER, NO WAY TO TRANFER LOAD. MLR OK PER LOG
273 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-06-27 00:39 | 2009-06-27 10:47 | 262 | 608 | 64139-1 | 158099 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF #447-58 ISOLATED ON POLE 447-229 GOING TO NEED 45 POLE CROSS ARM 3 PINS AND INSULATORSCLOSED RECLOSER AT 330CLOSED SOLID BLADES AT 1035 CLOSED RECLOSER ON POLE 477-121 AT 1040
274 | Hazard | 3310502 | HADDIX | CANOE | 2018-07-02 14:04 | 2018-07-03 06:20 | 165 | 957 | 4706411 | 157740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 839668/broken pole across the river/ crew onsite and making repairs
275 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-09-27 13:42 | 2011-09-27 16:47 | 848 | 185 | 4925121 | 156880 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | 69-12KV TR 1 TRIPPED DURING MOBILE TRANSFORMER INSTALLATION - SDB / 1647 / ALL CUST RESTORED. 848CC// SCADA INDICATED BREAKER TRIPPED BACK OUT @ 1703 RESTORED @ 1714 --- COD-848 ISO FB SEE H4925121 FOR DUPLICATE WHICH MAY OR MAY NOT BE RELATED TO THIS??? VER/HFP L3/HFP IDCC TOF1346 XXXX
276 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-05-11 19:41 | 2011-05-12 10:00 | 181 | 859 | H4046181 | 155479 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | GIVE TO TERRY FIELDS PLUS TREE CREW...TREES ON LINE NEAR POLE #1104-37 DOWN MTN ON LEFT UP ON HILL AT OLD BLUE COAL HOPPER. FUSE OUT ON POLE # 1128-68. TREE CREW REQUIRED. LOOKS LIKE NO LINES DOWN. RELEASED BY CREW 074F12.ON POLE 1128-D-131 HAD 3 PHASE RECL. LOCKED OUT AT 17:00 ON 5-11-11 FOUND ARR. BAD CLOSED IN AT 10:00 5-12-11. ALL CUST. RESTORED ACCEPT THOSE BEYOND POLE 1128-68.TREES IN LINE AT POLE 1104-37. IDC CHANGED TO TWO OUTAGES XXXX
277 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-08-10 19:15 | 2022-08-11 11:29 | 185 | 974 | 4720721 | 155134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | closed recloser in on pole 37830302A00049 at 21:05 up to opened switches on pole 302-D-156 tagged to ddc no grounds placed, fault pole is 303-33 wire off insulator manual gonna need line crew, pole top pin, 2 straight arm pins and 3 insulators 19.9. Released by crew 077H05
278 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-01-05 23:01 | 2014-01-06 13:18 | 181 | 857 | 4231561 | 155117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ON POLE 55-41 GOT 4 / 0 WIRE PULL OUT LOOP SLEEVE ON RT. HAND PHASE, NEED TWO MEN TO HELP OPEN LINE AND GROUND LINE TO FIX LINE AND SOME WIRE TO CHANGE LOOP SLEEVES OUT. ** CREW TO BE DISPATCHED AT DAYLIGHT AS WEATHER & ROAD CONDITIONS ALLOW..//COD 181//ISO/// VER/DBM IDC NOT LIKELY ALL THREE PHASES PULLED OUT BUT CALLS DO NOT INDICATE OTHERWISE XXXX
279 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-05-21 23:21 | 2014-05-22 13:10 | 187 | 829 | 4734081 | 155023 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | "C" PHASE WIRE DOWN AT 201-236 /1 PHASE ONLY COD-187/WILL NEED TO OPEN AT 200-D-117 TO MAKE REPAIRS VERY MANUAL/C PHASE WIRE DOWN AT 201-236 /1 PHASE ONLY COD-187/WILL NEED TO OPEN AT 200-D-117 TO MAKE REPAIRS VERY MANUAL/ RELEASED BY CREW 077S04 OPENED ALL THREE PHASES AT ROUGHLY 1000 AT 200-117-- MADE REPAIRS AND CLOSED IN AT 200117 RESTORING ALL CUSTOMERS AT 1310 -- CAN CLOSE - THIS NEED PROPERLY MODELED TO REFLECT CUSTOMER COUNT MWL VER/KEP AJB SEE H4734081.
280 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-04-11 23:22 | 2011-04-12 06:35 | 855 | 433 | 55435-1 | 154882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SDB / 2322 / FEEDER OUT CC= 855. ---- SDB / 0008 / FAILED INSULATOR AT POLE 266-24, CREW OPENED SW AT POLE 266-85 TO ISOLATE. --- SDB / 0046 / CB CLOSED, RESTORING 617 CUSTOMERS. RELEASED BY CREW 074S02 VER/KEP IDC WIRE FELL IN CK NEEDED FLAGGERS AND CONTRACTORS IDC XXXX
281 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2017-02-13 03:21 | 2017-02-13 06:33 | 805 | 192 | 4391741 | 154560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | DISTRIBUTION CKT REGULATOR INSIDE ALLEN STATION (PH A) FAILED. REGULATOR BYPASSED AND TAGGED TO THE DDC. POLE 1027-213 XFMR READING 247 VOLTS. RELEASED BY CREW 076S02 VER/KEP L3/HFP XXXHFP AJB
282 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2015-07-09 20:35 | 2015-07-10 03:35 | 368 | 420 | 4759391 | 154560 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | TRANSMISSION LINE DOWN CREW ENROUTE // RELEASED BY CREW 074S03//STATIC WIRE SPLICE FAILED ON TRANSMISSION LINE WHICH PASSES OVER DISTRIBUTION CKT, BURTON/LBEVINSVILLE, AT POLE 163-B-63//T-LINE CLEARED STATIC LINE OFF OF DISTRIBUTION CONDUCTORS AND SERVICER RESTORED FEEDER @ 0335 AJB
283 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-07-15 22:22 | 2015-07-17 15:10 | 63 | 2448 | 4897651 | 154224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | C PHASE REC OPEN ON POLE 37830482C00151 RELEASED BY CREW 077S04//COD 63//CAN CLOSE POWER RESTORED AT ROUGHLY 1530 MWL C PHASE REC OPEN ON POLE 37830482C00151 RELEASED BY CREW 077S04//COD 63..ALL POWER RESTORED AT 15:10 HRS AJB
284 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2021-03-15 23:49 | 2021-03-16 12:22 | 342 | 753 | 4338991 | 154095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DDC TAGS / HOLD ORDER REQ / DOL 1099100 // REC on 139-A4-432 locked out, patroling// 3 in line switches open at pole 37830139C00324 and tagged to ddc// rec on 139-A4-432 back in @ 01:46, patroling// no hazards found to end of spewing camp will need sxs to patrol the rest of line// pole 91-A-63 att has set a pole and its laying on center phase and has burned hard cover off pole, will need to have conductors transfered before energizing //
285 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-10-08 12:22 | 2017-10-08 15:47 | 751 | 205 | 4421521 | 153955 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DUE TO 4420491 VER/ARN
286 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2010-01-05 09:47 | 2010-01-05 23:34 | 186 | 827 | 61078-1 | 153822 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | TRANSOUTAGE TRANS DISPATCHING CENTER AND KENTUCKY DISTRI DISPATCH CENTER ARE WORKING WITH CREWS ON A PLAN TO ISOLATE & SECTIONALIZE SECTIONS OF THE TRANS LINES IN TROUBLE , THEN WORK ON PLAN TO SWITCH FEDS CREEK & RUSSELL FORK STATIONS TO ALTERNATE SOURCES. TRANS DEPT. HAD PLANNED TO PATROL THE LINE BY AIR BUT WEATHER CONDITIONS HAVE CANCELLED THAT PLAN , CREWS WILL NOW PATROL BY VEHICLE AND OR FOOT. PSC REPORT FILED. VER/PDP. AS PER OUTAGE REPOR IDC XXXX
287 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-08-27 22:23 | 2012-08-28 03:32 | 520 | 309 | 4978981 | 153400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | <<PHASE C RECLOSER ONLY>>OPEN ON 785-121.//410 CUSTOMERS//. #4 CU PRIMARY DOWN ON 785-45.. CREW ENROUTE TO REPAIR.< CLOSED RECLOSER ON 785-121 (PH C) @ 2:12 ENERGIZING UP TO OPEN SWITCHES ON 809-81. CLOSED SWITCHES @ 3:32 RESTORING REMAINING CUSTOMERS. SH RELEASED BY CREW 07 IDCC CNT787 XXXX
288 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-03-29 08:47 | 2016-03-29 15:18 | 604 | 391 | 4001361 | 153181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WHILE SWITCHING SOS 3183 REV 39// OCR @ 620-D3-325 WAS FOUND TO HAVE C PHASE RISER BURNT - RESULTING IN OUTAGING 157 CUSTOMER - FROM THIS POLE TO 549-97 (TEMP NO)// BYPASSES CLOSED AT 1016 - RESTORING UP TO 573-102 AJB
289 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-10-25 12:23 | 2012-10-25 14:04 | 1515 | 101 | 4171391 | 153015 | DISTRIBUTION STATION | EQUIPMENT FAILURE | MOAB | EQUIPMENT FAILURE ON HIGH SIDE OF STATION TRANSFORMER/PREPARING LOAD TRANSFER. VER/KEP IDCC TOF1227 XXXX
290 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-11-08 07:14 | 2011-11-08 08:55 | 1515 | 101 | 4058281 | 153015 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | TRANSFORMER OUTAGE - TDC NOTIFIED STATION PERSONNEL ENROUTE / DISTRIBUTION SERVICER ENROUTE. CUSTOMER SAID HIS FRIEND LIVES BESIDE SUB STSTION HEARD LOUD NOISE - PH 3 34KV BUS POT TR FAILED AT SUBSTATION VER/TOM L3/TOM IDC X CHANGED COUNT FROM 1636 XXX
291 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-04-15 03:04 | 2018-04-15 16:20 | 2009 | 714 | 4226171 | 152743 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 0304 CB locked out via scada/Pole top has let go at 38820941D00129. Contractor has spotted all the material. Load has been transferred to Borderland / Chattaroy. Released by crew 079S02/// Waiting on crews to arrive/// Have made repairs and grounds removed men and equipment in clear. Waiting to get people in place to start switching.//All customers restored at 14:36 Switching complted and back to normal at 16:20 TimMcCoy Released by crew 074H10/// transferred 210 customers form outage 4228351, originally out at 04/15 15:50
292 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-08-06 10:27 | 2012-08-06 15:25 | 512 | 298 | 4902511 | 152576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3PHSE RECL IS OUT,WILL PATRL.BAD XFR AT 1056-171,ISOLATED.TRIED RECL,DID NOT CLOSE.WILL PATRL,JAY ENROUTE TO HELP,S RAY BRINGING XFR. RELEASED BY CREW 074S06/CENTER PHASE "B" COD-113// 6 DE INSUL. BAD PLUS 25 KVA ALSO RECL. IN BAD PLACE HAD TO CUT DE TO ISOL. NEEDED AWP IF NOT P COD-512 ISO OCR 38821058B00347 VER/HFP IDC XXXX
293 | Whitesburg | 3312901 | JENKINS | KONA | 2009-11-11 02:12 | 2009-11-11 09:39 | 552 | 447 | 57485-1 | 152168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD AND BURNED TOP OF POLE OFF CONTRACT CREW IS GOING TO MAKE REPAIRS ON THIS I OPENED DISC ON POLE 404-117 AND CLOSED GOAB ON POLE 403-228 AT 0522 CLOSED BREAKER AT 0929 VER/LDA IDCC TOF0218, TON0552, TON0929 XXXX
294 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-01-16 02:22 | 2013-01-16 14:27 | 374 | 725 | 4609341 | 151747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN ON POLE 446-300, BAD DEADEND BELLS ON 446-187 TOOK LINE OUT, WILL ISOLATE ON POLE 446-87.. CLOSED RECLOSER IN AT 07:08 ON POLE 446-300.CUT LOOPS ON POLE 446-152 CLOSED GOAB ON POLE 422-232 AT 09:05 ENERGIZING UP TO POLE 446-152. RELEASED BY CREW 077S11 RELEASED BY CREW 075H01//CLOSED SWITCHES AT 1427 AND RESTORED 5 CUSTOMERS ON THIS OUTAGE// THE OTHER 133 WERE RESTORED ON OUTAGE 4611951// VER/TOM L3/TOM IDC XXXX
295 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-03-17 20:36 | 2009-03-17 22:40 | 1214 | 124 | 59600-1 | 150536 | TRANSMISSION STATION | EQUIPMENT FAILURE | SWITCH, OH | VER/HFP EMERGENCY OUTAGE TO REPAIR SWITCH ON 69KV TRANSMISSION LINE THAT IS BURNING. *** UPDATED FETR ** @ 2200 CREWS HAVING PROBLEMS WITH SWS AND OPENING 69KV LOOPS ** THIS WILL EXTEND THE OUTAGE TO 2245. L3/HFP IDC XXXX
296 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2013-07-07 02:21 | 2013-07-07 21:47 | 357 | 1166 | 4477471 | 149817 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | COLEMAN-SPRIGG 69KV LINE LO // 69 CONDUCTOR DOWN T-LINE CREWS TO MAKE REPAIRS - TRANSFER CUSTOMERS TO ALT SOURCES WHERE AVAILABLE. ** UPDATE MULTIPLE T- LINE CREWS AND HEAVY CRANE ENROUTE TO ASSIST. *** UPDATE TIME TO 2000 ******* SA FAILED AT BARRENSHE, UPDATED FETR TO 2330 // SEE DDC LOG FOR DETAILS //VER/GAH IDC XXXX
297 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-06-18 17:42 | 2015-06-18 23:36 | 429 | 354 | H4601251 | 149376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | KYDDC OPENED ALL KEYSER CKTS VIA SCADA @ 1842 DUE TO PROBLEM WITHIN THE STATION//LTC REPAIRED AND FEEDER RESTORED 2336//COD 1087 // TIMES PER SCADA & LOG DUP OF 4601251 FOR INITAL C PHASE OUTAGE VER/HFP L3/HFP AJB
298 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2017-01-06 04:10 | 2017-01-06 08:13 | 609 | 243 | 4272681 | 147987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SCADA TRANSMISSION OPERATIONS SUGGEST EAST PRESTONSBURG STATION TRANSFORMER LOCKOUT//COD 609 RELEASED BY CREW 076S02///DKM/0834/ARRESTOR BLEW ON STATION SERVICE PHASE 3/// VER/DKM // VER PER SCADA & DOL L3/HFP HFPC TOF0414 AJB
299 | Hazard | 3303901 | LESLIE | HYDEN | 2022-11-25 11:34 | 2022-11-25 19:02 | 879 | 448 | 4179641 | 147660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER/DOL 1254373//SCADA INDICATED CB LO AT 1134//Wire down between poles 388-164 and 388-172/DOL 1254373//SCADA INDICATED CB LO AT 1134// C Phase down between poles 388-D-164 and 388-B-172.repairs comp. Released by crew 077H13
300 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-01-24 23:22 | 2008-01-25 15:42 | 161 | 980 | 59551-1 | 147604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303903//// STEPDOWN BURNT UP ON POLE 362-5// 362-5 CLOSED IN @ 1420 GOOD TO 362-78 RECL// CLOS 362-78 @ 1436 GOOD TO 362-83 - CLOSED 362-83 @ 1512 GOOD TO 362-201 CLOSED @ 1523 GOOD TO 362-79 CLOSED IN @ 1542// ALL CUSTOMERS RESTORED @ 1542 - THIRD STEP REMOVED 4 CUST (NOW 24 INSTEAD OF 28 DUE TO BAD CSP THESE DID NOT COME BACK ON - OUTAGED ON 59974-1// VER/TOM IDC XXXX
301 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-11-04 22:15 | 2010-11-04 23:35 | 1838 | 80 | 52056-1 | 147040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ON POLE 143-199//ISOLATING IN ORDER TO RESTORE BREAKER //CUTOUT BROKE DOWN AT POLE#-143-199 AND TOOK OUT CIRCUIT BREAKER. I HAVE CUTOUT CHANGED AND FRANK IS TRYING BREAKER.//COD 1838//CUTOUT BROKE DOWN AT POLE#-143-199 AND TOOK OUT CIRCUIT BREAKER. I HAVE CUTOUT CHANGED AND FRANK IS TRYING BREAKER. FRANK CLOSED STATION BREAKER AT 23:35 AND IT STAYED.// VER/DBM IDC DCMT XXXX
302 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-06-03 09:18 | 2008-06-03 12:04 | 882 | 166 | 54825-1 | 146412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202202/ CREW OPENED RECLOSER TO SAFELY REPLACE POLE VER/HFP IDC XXXX
303 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-08-06 09:40 | 2012-08-06 12:16 | 938 | 156 | 4902081 | 146328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSURE @ 38831125C20625 IS OPEN .AM NOW PATROLLING BAD CUTOUT ON POLE #38831125A00519 COD-938 ISO OCR @ 38831125C20625 VER/HFP L3/HFP IDC XXXX
304 | Pikeville | 3413401 | GARRETT | GARRETT | 2020-06-30 11:49 | 2020-06-30 17:20 | 477 | 331 | 4093751 | 146142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | opened 300amp switches on pole 65-a-68 tagged for myself//CLOSED SECTIONALIZER ON POLE 37830040C40023 @ 1455//COD NOW 396//BAD INSULATER ON POLE 37830065D00392 Released by crew 074S03
305 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-12-16 17:40 | 2012-12-16 19:21 | 1439 | 101 | 4473221 | 145339 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED POSSIBLE LOSS OF # 2 TR @ HOWARD COLLINS STATION @ 1740 // STATION SERVICE TR CUTOUT FAILED - SERVICER REPLACING & PERFORMING TCG GAS TEST ON STATION TR //VER/GAH IDC XXXX
306 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2020-07-30 03:34 | 2020-07-30 09:10 | 432 | 336 | 4252881 | 145152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | switch inside siloam station busted/ station mech on site/ Line crew for switching onsite/ Released by crew 078H08 Released by crew 078H22 Restored @ 0910
307 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-06-09 14:56 | 2015-06-09 19:26 | 1451 | 270 | 4545711 | 145138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN AT PL.39831148B30483 NEAR HOSP, CREW REQ CREW HAS STARTED WORK MAY BE RESTORED IN ABOUT 2 HR S FROM NOW RELEASED BY CREW 078S09 VER/SEF /// VER TIMES PER DISPATCH LOG - L3/HFP HFP AJB
308 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-05-29 14:59 | 2019-05-30 12:19 | 113 | 1280 | 4373071 | 144640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Rec. open @1058-B2-370, patrolling. 8 ft. crossarm broke @1058-A-944, will be changing. Got crossarm changed out , closed rec. back in @1219. L3/HFP
309 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-04-03 05:41 | 2015-04-03 09:13 | 1463 | 212 | 4262201 | 143716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STATION BREAKER IS OPEN. I AM PATROLLING LINE NOW//FOUND BROKEN CUTOUT ON XFMR BANK 49-218//STATION BREAKER IS OPEN. I AM PATROLLING LINE NOW. WE CLOSED TRANS. FUSE IN AT 09:13. RELEASED BY CREW 074S01//SEE OUTAGE LOG FOR FURTHER DETAILS//COD 1463// VER/HFP L3/HFP AJB
310 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-05-29 12:34 | 2012-05-29 15:06 | 1289 | 152 | 4840911 | 143583 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POWERON INDICATED CKT OUT//SERVICER ENROUTENEED CREW--ONE PHASE OF 556 SPACER DOWN IN FRONT OF OAKVIEW SCHOOL--LARGE BUCKET CAN WORK IT FROM ALLEY WITHOUT BLOCKING BLACKBURN--NEED CREW---- RELEASED BY CREW 078S07POWERON INDICATED CKT OUT//SERVICER ENROUTENEED CREW- IDC XXXX
311 | South Williamson | 3411401 | DEWEY | INEZ | 2010-01-08 09:45 | 2010-01-08 12:12 | 1521 | 147 | 66424-1 | 143549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | PH "A" RECLOSER OPEN ON POLE 838-A4-155//ALL 3 PH OPEN @ 744-D-578//HOT FROM OTHER SIDE OF 744-D-578 SINCE N.O. SWS ON 746-B-218 ARE NOW CLOSED//FAULT SEEMS TO BE SWS 815-B-15, PH `A` IS BURNT UP ON SWS POLE//CUST COUNT FOR PH `A` FROM 838-155 TO 744-578 IS **1522** //CREWS ATTEMPTING TO FIX FAILED SWITCH//@ 1034 OPENED 3 PH REC 767-111 AND CLOSED IN N.O. SWS 744-A-577 AND PICKED UP TOMAHAWK (MAP NOT GIVING GOOD CUSTOMER COUNTS NOW... NOT SURE HOW MANY PICKED UP) IDC XXXX
312 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2020-03-29 08:26 | 2020-03-29 11:35 | 758 | 189 | 4521711 | 143262 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | Station Outage Off @ 0826 On @ 1135
313 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2008-08-27 07:13 | 2008-08-27 13:39 | 431 | 386 | 55869-1 | 143131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404301//0N SITE, PATROLLING LINE RELEASED BY CREW 080S01 IDCC SC3417602, CNT577 XXXX
314 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-01-13 12:54 | 2013-01-13 17:36 | 507 | 282 | 4600821 | 142974 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SAME AS 4600321 34.5 INSUL. BAD ON POLE NO NTRUCK COMPL. WR. VER/PDP IDC CHANGED START TIME FROM 1534 XXXX
315 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-01-29 05:19 | 2014-01-29 09:42 | 1012 | 263 | 4321201 | 142548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3202201--CKT LOCKED OUT--CC3325--KYDDC DA RECL 746-D-249 OPENED UNDER LOSS OF AC--KY CLOSED MOAB 746-218 AT 0626 TRANSFERRING CC366 TO THE DEWEY/INEZ--KY OPENED SWS 747-B-28--KY CLOSED CB AT 0704 REST CC131--KY OPENED SWS 747-A2-45--AT 0752 CLOSED SWS 747-B-28 CC315--AT 0924 CLOSED SWS 747-A2-45 CC89--AT 0936 CLOSED RECL 747-A2-1847 CC215--AT 0942 CC336--AT 1038 CC379--AT 1112 CC70--AT 1136 CC74--AT 1203 CC90--AT 1230 CC94--AT 1234 CC82--AT 1242 CC134--AT 1300 CC168--AT 1306 CC782 //VER ANM IDC XXXX
316 | South Williamson | 3411401 | DEWEY | INEZ | 2009-06-25 13:24 | 2009-06-25 17:28 | 805 | 244 | 59175-1 | 142381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | #4 COPPER DOWN ON POLE 696-C-4 OPENED LINE ON POLE 672-D-16 RELEASED BY CREW 079S01 POSSIBLY SAME AS 59175-1 DELETE LAST RESTORATION STEP IN HOIS WRONG SWITHC WAS OPENED ON POLE 38830672D00016 SHOULD HAVE BEEN THE FUSE NOT THE SWITCH THAT WAS OPENED BEFORE RECL WAS CLOSED IN
317 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2019-11-05 19:11 | 2019-11-06 03:20 | 669 | 489 | 4295421 | 142137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 968437/SCADA INDICATED CB L/O AT 1911/POLE TOP BURNED OFF AND WIRE DOWN ACROSS US23/ISOLATING TO SAFELY CLEAR DOWNED CONDUCTOR/Pole 48-A2-1089/ Released by crew 074S05 ¦¦¦ VERIFIED TIMES PER SCADA & DOL L3/HFP
318 | Pikeville | 3402002 | KEYSER | STONECOAL | 2015-06-18 18:41 | 2015-06-18 23:34 | 485 | 293 | H4601311 | 142105 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | KYDDC OPENED ALL KEYSER CKTS VIA SCADA @ 1842 DUE TO PROBLEM WITHIN THE STATION// TREE AT TIM SHORT IS ON THE PHONE COMPANY PER BILL JOHNSON//STATION DEPT MADE REPAIRS TO LTC AND THIS FEEDER RETURNED TO SERVICE @ 2334//COD 768// VER/DBM // TIMES PER SCADA & LOG - DUP OF 4601311 FOR INITIAL C PHASE OUTAGE = L3/HFP HFPC DUP AJB
319 | Hazard | 3303902 | LESLIE | WOOTON | 2008-12-24 12:01 | 2008-12-24 17:23 | 441 | 322 | 63393-1 | 142002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP STS WR # 27802497 DIVERTED TO TROUBLE ATWOOTON. RELEASED BY CREW 077H02. 3 PHASE RECLOSER OPEN ON POLE 389-6. B PHASE OFF OF INSULATOR ON POLE 437-36. FETR 1800HRS L3/HFP IDC XXXX
320 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-04-16 13:49 | 2015-04-16 15:55 | 1125 | 126 | 4326381 | 141750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER ENROUTE//BROKE CUTOUT ON C PHASE ON POLE 37830204000239, ALL 3 XFMR FUSES ARE BLOWN. G. SHOUSE ON WAY TO MAKE REPAIRS. WILL NEED HIS HELP JUST TO ISOLATE TROUBLEBROKE CUTOUT ON C PHASE ON POLE 204-239, ALL 3 XFMR FUSES ARE BLOWN. G. SHOUSE ON WAY TO MAKE REPAIRS. WILL NEED HIS HELP JUST TO ISOLATE TROUBLE//RECLOSER 37830204000264 IS OPENED//BROKE CUTOUT ON C PHASE ON POLE 204-239, VER/CRB //SCADA INDICATES 3 PHASE OUTAGE --- L3/HFP XXX AJB
321 | Hazard | 3303902 | LESLIE | WOOTON | 2018-01-28 02:56 | 2018-01-28 12:54 | 286 | 579 | 4777891 | 141242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DDC HOLD ORDER // DOL 800215 // Running line out // found bad insulator on pole 37830438000073 // will attempt load xfer to Slemp-Leatherwood // @ 0949, restored 145 COD to adjacent ckt // Released by crew 077S03 VERIFIED TIMES PER DOL 800215 = HFP
322 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-12-07 08:57 | 2020-12-07 10:24 | 1618 | 87 | 4750531 | 140766 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CIRCUIT SWITCHER | DOL 1074349 // TR2 outage at Stanville Station per SCADA @ 0857 //cod 1618
323 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-06-21 16:13 | 2021-06-21 18:47 | 991 | 154 | 4782791 | 140732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 38831132000092//REPLACING CUTOUT //FETR 1900//open recloser on pole 1108-6119 and closed recloser on pole 4-277 at 1821. closed recloser on pole 1108-6119 at 1847 Released by crew 077S05
324 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-10-27 18:51 | 2012-10-28 04:29 | 1193 | 578 | 4177031 | 140720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 1851 / FEEDER OUTAGE. CC 1193. CUTOUT BROKE AND BURNT THREE PHASE HIGHWAY CROSSING POLE OFF. 45-4 BUCKARM HIGHWAY CROSSING. CREW ENROUTE TO REPLACE. CLOSED BREAKER @ 20:02 RESTORING UP TO OPEN SW ON 785-1147. 822 CUST REST --- SDB / 2048 / FIELD TIE, 271 CC REST --- SDB / 0238 / 43 CC REST.... JUMER BURNT OFF AT POLE 785-1379, DID NOT REST 57 CC. SEE ORDER 4177521 FOR THOSE REPAIRS. VER/SDB IDC XXXX
325 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-11-15 11:12 | 2020-11-15 13:41 | 943 | 149 | 4679561 | 140507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | DOL: 1069567///Wind had blown loose pole ground on 771-A4-366 onto phase loop causing breaker to lockout. I was able to clear up and restore breaker @ 13:41///KY customers
326 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2017-05-25 21:33 | 2017-05-26 20:27 | 322 | 1374 | 4863601 | 140014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HOLD ORDER REQUIRED RELEASED BY CREW 079H03 RELEASED BY CREW 079S02/// VER/DKM // TIMES PER DOL = L3/HFP HFPC LCDDCB3200201-1 FP38821089A00004 AJB
327 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-10-09 20:03 | 2019-10-10 05:46 | 528 | 583 | 4125911 | 139941 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HOLD ORDER DOL 961320/ pole 231B-06 top broke out, gonna need 4 man line crew also gonna need 2 8ft arms, 6 19.9 deadends complete, 3 19.9 arm pins and insulators, 2 guy attachmenst, 2 guy breakers, and also 2 sets for braces Released by crew 077H05/ 37830230D00072 new switches md done/ Contractors installing new conductor and when new conductor was pulled tight the top of pole broke out/ couldve been pulled to tight because of field error or it couldve been pulled to specs and the pole was just old and ready to break so equipment failure but who knows if it was either one of those causes so maybe its just unknown ¦¦¦ QUESTIONS ABOUT THE CAUSE ??? L3/HFP
328 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-01-22 00:54 | 2009-01-22 03:45 | 817 | 171 | 59039-1 | 139707 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | 3000902//A 69KV INSULATOR ON THE TRANSMISSION LINE HAS FAILED OPENING THE TRANSMISSION LINE/TIED WITH BELHAVEN/ARGILLITE AT POLE 1123-4546 AT 0345 THIS RESTORED ALL CUSTOMERS VER/KEP L3/KEP MLR OK
329 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-09-07 14:46 | 2009-09-07 20:28 | 437 | 342 | 52712-1 | 139674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | MIDDLE PHASE OUT ONLY (PHASE A) // COD 437// PATROLLING LINE// TRIED RECLOSER, CAME BACK OUT. CALLING DUTY FOR HELP. CREW FOUND TROUBLE.AT POLE 179-169. REPLACED BAD INSULATOR AND RESTORED POWER AT 20:25. K. NAPIER ** NEED TO SHOW BANK OF SECTIONALIZERS ON POLE 204-1 ENTER M.D . MIKE LASSLO WILL CALL WITH UPDATE TOMORROW. VER/PDP IDCC STP XXXX
330 | South Williamson | 3411401 | DEWEY | INEZ | 2018-01-12 13:16 | 2018-01-12 16:36 | 2811 | 200 | 4736391 | 139302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL796626 // sdb // 1316 / SCADA shows feeder breaker locked out. Crews en route. 2811 cc //pole 837-8 insulator failed ,burned cross arm off//repairs made Released by crew 079S01//times are wrong, see DOL// Verified times and customer count per DOL
331 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-08-03 06:56 | 2022-08-03 13:26 | 624 | 390 | 4667001 | 139076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DDC TAGS / HOLD ORDER / DOL/ 1227427 / OCRs at 247-A-498 open 624 CC / opened 247-C1-1793, 247-C-657, 247-C3-1354 & 247-C2-1788 // Closed 247-A-498 (11 CC at 1006) // Closed 247-C1-1793 (30 CC at 1019) // Closed 247-C3-1354 (27 CC at 1029) // Closed 247-C2-1788 (474 CC at 1050) Opened 223-D4-578 Closed N.O. DA at 223-D3-1250 (23 CC at 1050) Opened 223-D3-1250 Closed at 247-C-657 (55 CC at 1135) Closed OCRs at 224-B1-482 at 1326 // isolated UG at 224-B2-515DDC TAGS / HOLD ORDER / DOL. Bad UG el
332 | Hazard | 3310502 | HADDIX | CANOE | 2020-07-28 09:12 | 2020-07-28 15:19 | 591 | 367 | 4243011 | 138471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | failed insulator on pole 121-59bad loop insulator on pole 121-59. manual. help on the waybad loop insulator on pole 121-59. manual. help on the way Released by crew 077S10
333 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-02-01 05:00 | 2008-02-01 12:33 | 686 | 453 | 63044-1H | 137881 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411802- POLE FIRE SERVICER ISOLATED AND RESTORED RECLOSERS. A PHASE ONLY OUT AT POLE 26-2 AT SERV OPENED ALL RECL AT 0500 -OPENED SWS AT POLE 2-54 CLOSED ALL RECL AT POLE 26-2 AT 0530- AT 0600 OPENED SWS AT POLE 2-118 & CLOSED AT 2-54 AT 0626 OPENED & TAGGED SWS AT POLE 1130-267 . AT CLOSED N.O. RECL AT POLE 1081-16 REST .... CUST FROM THE JOHNS CR META 34KV CKT. IDCC DUP TO OPEN OTHER 2 PHASES XXXX
334 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-12-25 07:55 | 2008-12-25 12:17 | 525 | 262 | 63849-1 | 137550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27804891 // SERVICER ON SITE AND ON HIS WAY TO THE STATION TO CHECK TARGETS AND OPERATION. WILL NEED TO ISOLATED AND INTERRUP TO MAKE REPAIRS. CB IS NOT OPEN AT THIS TIME.POLE 64-218 BURNT INTO DUE TO BAD CUTOUT. CALLED DENNIS CREW ON THE WAY. 378300640900218 CLOSED CB @ 1217. . EV ERYONE SHOULD BE B L3/HFP IDC RECLOSERS WERE LOCKED OUT 1 SPAN AWAY ON THE LOAD SIDE OF THE FAULT XXXX
335 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-03-11 03:15 | 2008-03-11 04:53 | 1399 | 98 | 56067-1 | 137102 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | STATION SERVICER AND GENERAL SERVICER IN STATION CHECKING--------12KV STATION ARRESTER BLOWN VER/ARN IDC XXXX
336 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2011-08-22 12:56 | 2011-08-22 18:40 | 430 | 344 | 4743751 | 136790 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE | SYDNEY STATION INTERRUPTED DUE TO TRANSMISSION.. TDC WORKING TO RESTORE STATION AS SOON AS POSSIBLE. VERIFIED BY DKG/TRANSMISSION POLE SPLIT ALLOWING STATIC WIRE TO FALL ON CONDUCTOR ..FINAL STEP INCLUDES 45 CUST THAT WERE ON ONLY 4 MINUTES FROM TRANSFER THEN DROPPED IDC XXXX
337 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-15 10:26 | 2018-02-15 15:42 | 577 | 316 | 4843231 | 136780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ETA: 1130//insulator failed on pole 649-196 and phase burned down//also off insulator on 649-30///right hand recloser locked out on 649-202///crew enroute//will have to open other two reclosers when crew arrives to make repairs//ETA: 1130//insulator failed on pole 649-196 and phase burned down//also off insulator on 649-30///left hand recloser locked out on 649-202///crew enroute//will have to open other two reclosers when crew arrives to make repairs//opened other two at 14:05ETA: 1130//insula
338 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2016-01-18 20:25 | 2016-01-19 01:48 | 423 | 323 | 4629811 | 136629 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PATROLLING//LOOPED BURNT OPEN @ POLE 283-116//LOOP SLEEVE BURNDT INTO ON POLE 283-116, WILL REQUIRE 3 FT. 556 WIRE, 2 LOOP SLEEVES, BIG BUCKET, AND ANOTHER A LINEMAN.//166 COD FROM BEGINNING OF OUTAGE//ISO 37830283000116//COD 166//OPENED FEEDER BREAKER @ 0120 01/19/16 TO MAKE REPAIRS (SEE ORDER 4630571)//SEE DOL CASE 632712 FOR SWITCHING// RELEASED BY CREW 075H02 AJB
339 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-08-07 15:07 | 2021-08-07 20:01 | 580 | 294 | 4015841 | 136386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1137775///1100-334 pri metering had cutout broke that fell onto conductor phase to phase//cod 580
340 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-03-26 14:10 | 2010-03-26 19:30 | 1488 | 320 | 54710-1 | 135853 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED .POLE FIRE , POLE FELL . FEEDER L.O CREWS WORKING TO SECTIONALIZE TROUBLE AND RESTORE CUSTOMER TO OTHER SOURCES. AT 1535 , RECLS AT POLE 26-237 ISOLATED CLOSED NO AT REST 669 CC FROM HC/REGINA CKT WILL PROVIDE FETR AFTER STEP REST IS COMPLETE AND CREW STARTS WORK ON POLE. AT 1625 , LOAD TRANSFER COMPLETE , 57 CUSTOMER REMAIN OUT UNITL CREW REPLACES POLE , TOTAL REST BY 1900.CUTOUT FAILED . FEEDER L.O CREWS WORKING TO SECTIONALIZE TROUBLE AND RESTORE CUSTOMER TO OTHER SOURCES. IDC XXXX
341 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2010-06-03 22:32 | 2010-06-04 05:56 | 305 | 444 | 56247-1 | 135420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | FEEDER LOCKOUT - SERVICER PATROLLLING CKT. WR/35414533 * CROSSARMS BROKEN BY TREE OUT OF RIGHT OF WAY. WORK IS ALL BY HAND ON MT. NO ALT SOURCE AVAIL TO RESTORE CUST. OUTAGE UNTIL CREWS COMPLETE REPAIRS.FEEDER LOCKOUT - SERVICER PATROLLLING CKT. WR/35414533 RELEASED BY CREW 074S02 VER/PDP IDC CHANGED FROM TREE IN PER TREE DEPARTMENT XXXX
342 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-04-10 14:13 | 2015-04-10 19:39 | 653 | 326 | 4304921 | 135118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 26-1 NEARLY BURNED INTO,NEEDS ATTN ASAP/////////OPENED RECLR 26-2 DUE TO POSSIBILITY OF POLE FAILURE,CREW ENROUTE VER/KEP L3/HFP XXX AJB
343 | Hazard | 3302703 | HAZARD | HAZARD | 2011-03-06 01:58 | 2011-03-06 06:22 | 707 | 264 | 50279-1 | 135074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED THE HAZARD 12KV CB C IS LOCKED OUT// PATROLLING LINE // POLE 296-415 BURNT OFF// IN PROCESS OF ISOLATION TROUBLE AND TRANSFERRING SOME CUSTOMER TO ALTERNATE SOURCE// UPDATED FETR FROM FIELD IDC CORRECT CUSTOMER COUNT IDCC TOF0201, CNT1414 XXXX
344 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-08-04 14:55 | 2017-08-04 18:24 | 977 | 209 | 4225871 | 134884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED ARM INTWO AT 38830955D00165 WILL ISOLATE. HAVE ISOLATED @ 38830955D00571 CLOSED LANCER 12 V CB-B @15:53 VER/KEP SJG
345 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2022-04-14 00:58 | 2022-04-14 13:40 | 177 | 762 | 4760911 | 134874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL#1198277 /crew requried.///// TAGGED TO DDC.////got bye-pass cutout broke on recloser pole 115-55 and and jumper laid on arm and has brunt end of arm off.//// went back to step-down pole 37830115C20227 and opened up A phase fuse to isolate A phase recloser B and C phases are still in and hot.///// crew will need 2- 8 foot arms, 3 new 7,200 cutouts, 3 drop in pins,and pair of braces. Released by crew 074S03
346 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-01-19 20:23 | 2022-01-20 02:25 | 700 | 362 | 4387861 | 134149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Recloser open at 190-D3-406,(ASSESSING CONDITION)Recloser open at 190-D3-406,The top of pole 166-4 is split out,Rick Ray and crew is on the way to make repairs,Opened Recloser @ 167-A-428 to isolate Trouble and closed in Recloser 190-D3-406 @ 21:32..CREW ON SITE. REPAIRS COMPLETE. ON AT 02:25 //
347 | Pikeville | 3421001 | BREAKS | CITY | 2012-03-01 01:57 | 2012-03-01 05:04 | 934 | 187 | 4524561 | 133843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | SDB / 0157 / FEEDER OUTAGE, CC 934. --- SDB / 0318 / POLE TOP INSULATOR BENT W/ PRIMARY OFF AT POLE 220-D1-331. OPENED 65T LINE FUSE AT POLE 220-D1-389 TO ISOLATE. --- SDB / 0419 / CB CLOSED RESTORING 907 CC. ---- SDB / 0504 / LINE FUSE AT POLE 389 CLOSED, REST 27 CC. VER/SDB L3/DKG IDC XXXX VER/DKG
348 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-02-27 04:44 | 2021-02-27 14:06 | 238 | 562 | 4259781 | 133282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout broke on 239-C-30352,This is a Manual pole,Paul Layne is sending somebody to help me change it..//opened recl 215-D4-494 long enough to repair cutout--off at1345 - on at 1408. Released by crew 074S01
349 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-02-05 04:14 | 2014-02-05 12:40 | 713 | 506 | 4353111 | 132938 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT SERVING XFMR ON POLE 446-133 , I ISOLATED CUTOUT AND RESTORED ALL BUT ONE AT 07:20 RELEASED BY CREW 077S12 REPLACED CUTOUT BACK ON AT 1240 RELEASED BY CREW 075H01 VER/TOM L3/TOM IDC XXXX
350 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-07-15 02:57 | 2015-07-15 16:58 | 158 | 841 | 4870391 | 132878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEVERAL SPANS OF WIRE DOWN AT BERT KINNEY`S MYLES HAS THIS ISOLATED AT THE PHONE COMPANY. NO TRUCK CHECK TICKET 4854161 SEVERAL SPANS OF WIRE DOWN AT BERT KINNEYS MYLES HAS THIS ISOLATED AT THE PHONE COMPANY(3-1PH SECTZ OPEN ON POLE 25-63)// OCRS ON POLE 24 ARE IN - FOUND LOOP BURNT OPEN ON 24-33 ON B PHASE./OPENING RECLOSER 48-24OPENED B PH OCR ON 48-24 AT 16:35-REPAIRED LOOP-CLOSED AT 16:58-ON UP TO 25-63/BJ NO TRUCK CHECK TICKET 4854161 COMPLETW @ 1658 AJB
351 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-10-01 09:39 | 2020-10-01 13:03 | 650 | 204 | 4516881 | 132600 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Arrived and ( Patroling )..On pole 358-D-290,C Phase is broke,Will need a line crew to make repairs.Wire size looks to be #2 ACSR. FETR 1300Arrived and ( Patroling )..On pole 358-D-290,C Phase is broke.Wire size looks to be #2 ACSR. Released by crew 074S01
352 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2019-06-26 16:56 | 2019-06-26 20:28 | 625 | 212 | 4602551 | 132500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE PADDLE BURNT UP ON POLE 37830048A21712//COD 208 FROM BEGINNING//A phase paddle burndt into at the switch @48-A2-1712, will keep track of times, crew enroute./// trouble tickets show all phases out.
353 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-02-22 10:58 | 2016-02-22 12:51 | 1171 | 113 | 4746951 | 132323 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | POSSIBLE FAULT ON STATION EQUIPMENT AT GRAYSON STATION // STATION SERVICER EN ROUTE //, RELEASED BY CREW 078S05//TR 1 69KV METERING PT FAILED, MOAB DID NOT OPEN BECAUSE RELAYING COULD NOT SEE THE FAULT ON THE PT//TERMINAL BREAKERS ON THE ARGENTUM-LEON 69KV CKT OPENED//SEE ALSO DOL CASE 639195//COD 1171 VER/HFP L3/HFP AJB
354 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-04-05 05:37 | 2012-04-05 10:00 | 1572 | 263 | 4648711 | 132227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STATION BREAKER OPEN // SERVICER PATROLLING - // STATION BREAKER OPEN //TRANSFORMER CUTOUT HAS FAILED IN THE PROCESS OF CLEARING IT POLE 38831101C40093. TIM MCCOY // CLOSED BREAKER 0701// RESTORED ALL BUT 1 CC//REPLACED DEFECTIVE CUTOUT AND RESTORED POWER AT 10:00 RELEASED BY CREW 074H10//COD TOTAL 1572// VER/DBM IDC XXXX
355 | Whitesburg | 3401301 | FLEMING | NEON | 2010-09-11 07:28 | 2010-09-11 10:11 | 811 | 163 | 65403-1 | 132193 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | FLEMING STATION OUT.. RANDY LOVINS ENROUTE // BROKEN CUTOUT ON STA SER TR - LEAD FELL ONTO STEEL // ALL RESOTRED AT 1012// VER/TOM L3/TOM IDC CHANGED ON TIME FROM 1012 PER ALARM LOG XXXX
356 | Hazard | 3302704 | HAZARD | KENMONT | 2018-05-05 11:15 | 2018-05-05 22:19 | 979 | 664 | 4310111 | 132117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 823499 // SCADA indicates Feeder L/O @ 1113 // cod 732 //failed crossarms on 37830296D10103 // crew foreman enroute //DOL 823499 // SCADA indicates Feeder L/O @ 1113 // cod 732 // CROSSARM BROKE ON 296-103//HOLD ORDER issued//DOL 823499 // SCADA indicates Feeder L/O @ 1113 // cod 732 // CROSSARM BROKE ON 296-103 Released by crew 077S01
357 | Hazard | 3303902 | LESLIE | WOOTON | 2019-12-11 15:09 | 2019-12-11 17:36 | 898 | 147 | 4145591 | 132006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACING POLE37830389D00031 and had recloser 37830389C00015 on hot line tag//conductor broke and caused the recloser to lock out @ 1509 ON @ 1736
358 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-03-05 22:10 | 2011-03-06 03:05 | 447 | 295 | 50231-1 | 131865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR# 39052075// SERVICER AND CREW PATROLLING //STS WR# 39052075// STS BAD INSULATORS ON POLE 30-57, THIS POLE IS DOWN IN BOTTOM CLOSE TO THE RIVER IDC XXXX
359 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-09-22 17:26 | 2020-09-22 19:43 | 964 | 137 | 4487331 | 131786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | DOL 1055624/ Possible bad PT in SW 387-C-594/ Restored 282cc @1942 via N.O.37830387C00594 /restored 683 @1943 via 37830387C40721
360 | South Williamson | 3411401 | DEWEY | INEZ | 2009-03-03 09:53 | 2009-03-03 13:24 | 2746 | 211 | H54432-1B | 131716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3411401// WHILE RETURNING CIRCUIT TO NORMAL FROM A DA OPERATION/ A SWITCH THAT WAS BURNT OPEN CAUSED A SINGLE PHASE CONDITION WHICH LOCKED CIRCUT OUT FROM POLES 767C-111,768A-225 TO 746B-218. TOTAL CUST COUNT OF 2746 CUST/THIS LEFT 289 CUST IN SERVICE FROM THE BRK TO THE OPEN REC AT 111 AND 225. THE 289 CUST WILL BE REPORTED ON ANOTHER OUTAGE SEE H54432-1A AND 54432-1 IDC CHANGED FROM DSTATION 5/19/09 XXXX
361 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-07-25 19:55 | 2009-07-25 21:51 | 1594 | 116 | 59067-1 | 131444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BRACES ON CROSSARM ARE LOOSE AND LYING ON LOOP AT POLE 37830247C00479//CLOSED OPEN GOAB AT POLE 247-639 AT 22:51 RELEASED BY CREW 077S04 IDC XXXX
362 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2008-08-04 00:26 | 2008-08-04 03:06 | 819 | 160 | 64827-1 | 131040 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | STATION TRANSFORMER FAULTED AND CREWS ARE WORKING TO RESTORE CUSTOMERS VER/ARN IDC XXXX
363 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-12-23 05:32 | 2022-12-23 08:39 | 700 | 187 | 4294541 | 130900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | b phase loop burnt into @ 230-179/closed @ 824//
364 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-09-23 20:07 | 2011-09-23 22:10 | 1062 | 123 | 4910591 | 130626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 2007 SCADA INDICATED THE LESLIE/HAL`S FORK / GILLEY COMING OUT ALSO IDCC TOF2009, FOUND BAD INSULATOR NEXT DAY CHANGED CAUSE FROM UNKNOWN XXXX
365 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-02-20 01:49 | 2015-02-20 14:02 | 201 | 733 | 4046741 | 129779 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 PHASE DOWN ON POLE 900-6.1 REC OUT ON 876-28.OPENING UP OTHER 2 REC.OPEN AT 2.40.//TAGGED TO DDC//..2AA WIRE AND SLEEVES..3 MAN CREW. TRUCK ACCESSIBLE.. RELEASED BY CREW 076S01 AJBC CNT596 PH A INLT OUT SEE H4046741
366 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-02-23 18:46 | 2012-02-24 14:10 | 131 | 1164 | 4489081 | 129516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ALL 3 REC. LOCKED OUT AT POLE 426-665, THE SINGLE REC. IS ALSO LOCKED OUT ON POLE 426-685. POLE TOP BURNDT OFF AT POLE 426-25. GOING TO CUT LOOPS AT POLE 426-670 AND CLOSE THE SINGLE PHASE REC. IN AT POLE 426-685.CLOSED REC. AT 20:46.//PER SUPERVISION, WILL HAVE DHE CONTRACTORS MAKE REPAIRS HERE IN THE MORNING // OPENED RECLOSER AT 1350 TO MAKE UP LOOPS CLOSED RSCLOSERS AT1410 VER/HFP AJB
367 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-09-27 13:42 | 2011-09-27 16:47 | 700 | 185 | 4925151 | 129500 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | 69-12KV TR 1 TRIPPED DURING MOBILE TRANSFORMER INSTALLATION - SDB / 1647 / ALL CUST RESTORED. 700CC VER/SDB IDC XXXX
368 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-02-20 06:44 | 2015-02-20 20:58 | 174 | 854 | 4050121 | 129399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 38830784C30521CHECKING LINE NOWLINE FUSE OUT ON POLE 38830784C00040 CHECKING LINE NOW LINE DOWN AT POLE 38830760D00010 BAD LIGHTENING ARREST. ALSOLINE FUSE OUT ON POLE 38830784C00040 CHECKING LINE NOW LINE DOWN AT POLE 38830760D00010 BAD LIGHTENING ARREST. ALSO CREW REQUIRED //19 AJB
369 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-01-22 22:50 | 2013-01-23 04:30 | 407 | 340 | 4731171 | 129245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED PRC CREW /WIRE BURNED DOWN AT 94-258 "B" PHASE ONLY COD-407.OPENED SWITCHES ON 70-3503 @ 02:50 TO SAFELY MAKE REPAIRS..BLR.ALSO OPENED REC ON 94-6574 (FOR COLD LOAD PICK UP AFTER REPAIRS) CLOSED SWITCHES @ 03:55,RECLOSURES @ 04:30 VER/KEP IDC XXXX
370 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2019-06-12 22:03 | 2019-06-13 01:28 | 666 | 205 | 4490421 | 129222 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | DOL Case 929886/// Station L/O/Failed Bushing on TR 1/station crew enroute Released by crew 079S02//// Made corrections per DOL
371 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-07-03 00:04 | 2011-07-03 14:19 | 615 | 855 | 4449911 | 129221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | LOOKS LIKE 3 PHASE RECLOSER OUT - 615 CUSTOMERS OUTAGED// REC. OPEN ON POLE 37830254C00022. CLOSED REC. 01:22 LOCK OUT. OPENING GOAB ON POLE 37830278B00257, WILL TRY TO HEAT LINE DOWN TO GOAB. 01:45 CLOSED REC AND LINE IS HOT TO GOAB.OPENED SWITCHES ON POLE 37830302B00132, GOING TO CLOSE GOAB ON POLE 278-257//// LINE HOT DOWN TO SWITCHES ON POLE 302-132 AT 04:15.//// ARMS SPLIT DROPPING PHASE, ON POLE 37830326A00098, ARM BAD ON POLE 326-97. R/W BAD WILL NEED CUT.// VER/DBM IDC XXXX
372 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-01-22 00:54 | 2009-01-22 02:31 | 1331 | 97 | 58988-1 | 129107 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | 3110902/A 69KV INSULATOR ON THE TRANSMISSION LINE HAS FAILED OPENING THE TRANSMISSION LINE VER/KEP L3/KEP MLR OK
373 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-05-11 06:04 | 2019-05-11 10:13 | 1200 | 249 | 4251031 | 128857 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATED PIKEVILLE-CITY 12KV CKT OUTAGE/FOUND WIRE DOWN AT /ISOLATED AND CREWS ON SITE MAKING REPAIRS/. inulator failed and heat damaged transformer..making repairs Released by crew 079H07/DOL 920989 ¦¦¦ FAULT POLE PER VOICE RECORDER IS CORRECT - LINE HAS BEEN REBUILT & MAPS NOT UPDATED - VERIFIED TIMES PER SCADA & DOL
374 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-10-01 09:12 | 2022-10-01 14:44 | 980 | 293 | 4955031 | 128824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke switch Cutout caused Pole 358-D3-424 burned into at Braces,Crew in Route to make repairs..Closed Switches at pole 358-D-422 at 16:24.. Released by crew 074S01 LR- DOL 1241736
375 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-06 15:30 | 2008-07-06 18:43 | 1313 | 193 | 63232-1 | 128758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSS ARM BROKEN ON POLE 38830140A20520 CREW ON SITE REPLACING CROSSARM NOW. @ 1715 CREW REPORTED NEW FETR. OUTAGE TO RETURN TO NORMAL IN ORDER 63364-1 VER/HFP IDC XXXX
376 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-08-28 12:42 | 2008-08-28 20:42 | 319 | 480 | 56954-1 | 128684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3000701// 88 CUSTOMERS OFF ORIGINALLY - PHASE A CONDUCTOR DOWN @ 1048-818// OPENED RECLOSER ON POLE 1024-4 @ 1504 AND CLOSED IN @ // @ 1530 GAVE TONY PERMISSION TO OPEN NC DISCONNECTS @ POLE 1048-6 AND PLACE TAGS// @ 1544 TONY CLOSED THE NO SWITCH @ POLE 1072C-5025 RESTORING 82 CUSTOMER FROM THE WURTLAND/GREENUP//WR#26009076 AT 20:26 OPENED NO. SW AT 1072C-5025 CC 82 ALL REST AT 2042 VER/PDP IDCC CNT401, TON1548 XXXX
377 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2020-03-06 12:00 | 2020-03-06 16:07 | 1454 | 247 | 4456221 | 128375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAGS///DOL 998501/Emergency outage required due to pole fire. Crews on site performing switching to restore the majority of customers while repairs are being completed.///Released by crew 078H22
378 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-06-04 21:55 | 2020-06-05 06:03 | 386 | 488 | 4958811 | 127666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #6 cu primary down 834-129. Opened sw 834-15 to isolate. Closed rec 810-782 @ 23:21. Made repairs and closed sw 834-15 @ 6:03. sh//cod 386
379 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-07 10:55 | 2008-03-07 13:20 | 879 | 145 | 54470-1H | 127455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3308401// COD-344 A PHASE // 1 PHASE OUT ON POLE 204-264, PATROLLING LINE NOW. BROKE CROSSARM ON 204-40. CALLING FOR HELP//ISO 37830204000135////@ 1055, OPENED REMAINING 2 PHASES (836 ADDITIONAL CUSTOMERS) IN ORDER TO COMPLETE REPAIRS//ALL POWER RESTORED 1320// VER/DBM IDC CHANGED COUNT PH A AND C XXXX
380 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-04-07 18:35 | 2008-04-07 20:36 | 1051 | 121 | 64996-1 | 127171 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | 3301402//BUSTED INSULATOR3301402 BAD INSULATOR ON BUS WORK IN STATION 20:00 FETR3301402 BAD INSULATOR ON BUS WORK IN STATION 20:45 FETR VER/ARN IDC XXXX
381 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2008-03-28 02:18 | 2008-03-28 11:30 | 316 | 552 | 61422-1 | 127098 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | ON SITE, RECLOSER OUT, CALLED R MARCUM FOR HELP, PATROLLING LINE ** UPDATE AT 0500 * CREW SECTIONALIZING LINE, WILL CONTINUE TO PATROL CKT AND LOOK FOR TROUBLE WHEN DAYLIGHT ARRIVES. AT 0547 SWS AT POLE 1041-10 OPEN & N.O. SWS AT POLE 1064-C-284 CLOSED CC 138 REST. . VER/DKG IDC XXXX
382 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2017-02-07 13:18 | 2017-02-07 18:43 | 391 | 325 | 4365211 | 127075 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | RECLS ISOLATED & GNDS & TAGS PLACED FOR F BLANKENSHIP // XARMS BROKEN AT POLE 37820103B00002 / CALLING FOR CREW / CLOSED 37820103B00210 @ 1843. COD 391 VER/AWD L3/HFP XXXHFP AJB
383 | Hazard | 3303902 | LESLIE | WOOTON | 2019-09-07 12:23 | 2019-09-07 17:35 | 407 | 312 | 4991071 | 126984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | cross arm broke on pole 413;d;82 bad manual working on trouble replaced arm and restored power at 17:35
384 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-05-27 17:57 | 2017-05-27 23:05 | 412 | 308 | 4871041 | 126896 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | RELEASED BY CREW 077H07 TIMES PER SCADA & DOL & SOS 3521 REV 37 L3/HFP HFPC CDC80 FEC78 LCD37830368000097 AJB
385 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-10-14 13:12 | 2017-10-14 22:00 | 240 | 528 | 4456491 | 126720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ETA: 1445// 3 PHASE POLE BROKE RELEASED BY CREW 077S01 REPLACED POLE AND HAD TO REPLACE BYPASS CUTOUT ON OCR POLE #221/158//VER/ADH L3/HFP XXXHFP ACB
386 | Hazard | 3303902 | LESLIE | WOOTON | 2011-02-21 21:55 | 2011-02-22 08:32 | 268 | 637 | 59968-1 | 126652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 38889024 // PATROLING FOUND BAD INSULATOR ON 486-67// OPENED SWITCH ON POLE 486-47 AND CLOSED RECLOSER IN UP TO SWITCH @ 0120 // UPDATED FETR, POLE IS NOT TRUCK ACCESSIBLE, WILL HAVE TO CLIMB // CREW ENROUTE WITH NEW INSULATOR// COD 268// VER/DBM IDC XXXX
387 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-05-23 18:47 | 2020-05-23 22:45 | 578 | 238 | 4893681 | 126546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER IS PATROLLING//broke cutout on pole 30-23. all power restored 22:45 Released by crew 077S10
388 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2010-08-14 21:01 | 2010-08-15 00:43 | 570 | 222 | 54942-1 | 126540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000901 // NEED TO OPEN THE CB FOR CREWS TO MAKE REPAIRS TO POLE JUST OUTSIDE THE STATION.. SAME AS 54927 AND 54952//IT FORCE CLOSED IDC HAD TO WAIT ON KEY BUT FINALLY CUT LOCK WE ARE CORRECTING THIS ISSUE CHANGE COUNT 500
389 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-02-17 12:55 | 2018-02-17 14:30 | 1867 | 95 | 4854711 | 125720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CB L/O 1255/DOL 804636////xfm cutout 19.9 failed on pole 190-77 and fed back through rec. on pole 190-406 and took feeder breaker out////will make repairs. please send copy to Tom Mamming.. Released by crew 074S01
390 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-06-18 17:31 | 2009-06-18 21:45 | 748 | 254 | 64821-1 | 125642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3308401// EMERGENCY OPEN RECLOSER ON POLE 179B-194 TO ISOLATE BURNING GOAB ON POLE 177-64//WR#303695293308401// EMERGENCY OPEN RECLOSER ON POLE 179B-194 TO ISOLATE BURNING GOAB ON POLE 177-64//CLOSED GOAB ON POLE 178 297 AT 21 45.//VER/CRB AJBC TON21:50 SECOND REST STEP, PER COMM.
391 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2022-08-09 02:42 | 2022-08-09 13:00 | 615 | 618 | 4707321 | 125478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulator on p-655-99.. opened switches on p-655-106.tagged myself ..isolated primary from p-655-98 to 655-99..back on at 5:38.need 6a cu, dead end insulator, flaggers. Released by crew 076S01// restored recloser @655-B-99 @ 13:00// Complete AP LR- DOL 1228829
392 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2010-01-05 09:47 | 2010-01-06 01:22 | 190 | 935 | 61244-1 | 125232 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | TRANSMISSION LINE OUTAGE TRANSMISSION & DISTRIBUTION DISPATCH CENTERS ARE WORKING TO ISOLATE & SECTIONALIZE TRANSMISSION LINES IN TROUBLE WILL AIR PATROL AS WEATHER PERMITS. CREWS IN AREA PATROLLING BY FOOT. FIELD ETR IS APPROX MIDNIGHT TONIGHT. VER/ARN IDC XXXX
393 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-04-11 18:56 | 2011-04-12 00:05 | 405 | 309 | 55304-1 | 125145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 393-C-31 ROTTED OFF AND FELL OVER IN TREES. WIRE DOWN, CREW ENROUTE.//VER/CRB IDC XXXX
394 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2008-03-11 03:15 | 2008-03-11 04:52 | 1290 | 97 | 56065-1 | 125130 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | STATION SERVICER AND GENERAL SERVICER IN STATION CHECKING ----------STATION 12KV ARRESTER BLOWN VER/ARN IDC XXXX
395 | South Williamson | 3200301 | BELFRY | BELFRY | 2009-05-26 21:28 | 2009-05-27 04:34 | 292 | 426 | 53985-1 | 124392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NOTE TO SERVICER// CALL RUDY VASS FOR INFO ON THIS OUTAGE 606-794-0544 /// CUTOUT BROKEN INTO ON POLE 1014-888 SDRAY ONSITE WAITING FOR DEH CREW OPENED BELFRY/BELFRY CB AT 0424 CLOSED AT 0434 TO SAFELY MAKE REPAIRS MADE H ORDER VER/KEP L3/KEP IDC XXXX
396 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-07-26 11:56 | 2009-07-26 14:30 | 807 | 154 | H50861-1 | 124278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY "B" PHASE RECLOSER OPEN//COD 352//OPENED OTHER 2 PHASES @ 11:56 (INTERRUPTED 951 MORE CUST) //5 MAN CREW AND TREE CREWS ON SITE//FAILED CUTOUT BURRNED CROSSARMS//STS WR #30912392// IDC LOOKS LIKE SOME MISSMAPPED CUSTOMERS ESTIMATED COUNT DUP TO OPEN OTHER PHASES XXXX
397 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2010-01-05 08:03 | 2010-01-06 00:24 | 177 | 981 | 60782-1 | 124264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RIGHT HAND PHASE SWITCH IS BURNT UP//COD 170 // POLE 149-103 TREES AT POLE 37820124000030 NEED TO BE CUT. THIS NEEDS TO BE SENT TO J. BRADSHAW. RELEASED BY CREW 074S02//REPLACED 2 - 300 AMP SWITCHES. POWER STILL OFF DUE TO TRANSMISSION. RELEASED BY CREW 074H03 SOME SWITCHING WAS DONE TO PICK UP CUSTOMERS NOT SURE ON HOW MANY VER/KEP L3/KEP IDC ADDED 7 MISSMAPPED CUSTOMERS TO COUNT XXXX
398 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2019-05-05 00:57 | 2019-05-05 13:42 | 677 | 765 | 4222011 | 123278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER DOL 918962/ Failed insulator pole 446-216/Released by crew 077S12 3 bad post top insulators on pl 446-216 power restored at 13:42 Released by crew 075H03 ¦¦¦ VERIFIED TIMES PER DOL 918962 - L3/HFP
399 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-02-03 06:15 | 2014-02-03 10:23 | 497 | 248 | 4342361 | 123256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STATION CB B OPERATED ON THIS - LOOKS LIKE B PHASE OUT PER SCADA // TIM MILLER COMING OUT TO HELP LOOP BURNT OPEN ON PHASE B 785-680. POLE IS ROTTEN. DU // SEE RELATED ORDER 4343361 // COD-497 VER/KEP VER/HFP L3/HFP IDC XXXX
400 | Hazard | 3303901 | LESLIE | HYDEN | 2010-02-22 06:32 | 2010-02-22 10:40 | 982 | 248 | 59653-1 | 123242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FEEDER LOCKED OUT DUE TO 3 BAD CUTOUTS AT HOSPITAL / COD-982 / WILL RESTORE PART OF THE CIRCUIT BEFORE 0900 TROUBLE ISOLATED. REPLACED 3 BAD CUTOUTS AND ARRESTERS VER/LDA L3/DKG TIME OFF PER SCADA IDC XXXX
401 | Hazard | 3303901 | LESLIE | HYDEN | 2020-11-04 12:23 | 2020-11-04 16:35 | 895 | 252 | 4642361 | 123084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL: 1066925/// phase off insulator help on the way Released by crew 077S07
402 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-07-01 14:59 | 2021-07-01 18:40 | 578 | 221 | 4837611 | 122840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Rec. open @1100-D4-325, checking. Opened switches @1100-D1-360 to split line,closed rec. @1100-D4-325 @1738. Bad cutout @1100-4, will be changing out. Got cutout replaced, closed all 3 switches @1100-D1-360 @1840//cod 578
403 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-09-12 09:13 | 2015-09-12 18:36 | 415 | 563 | 4230921 | 122774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE SMOKING REALLY BAD ABOUT TO CATCH FIRE AT 108 HONEY CUT, OPENED RECLOSERS ON POLE 231-291, 811 DIG # IS 1509120062, GAVE MATERIAL LIST TO T. SMITH, CAN CUT LOOPS WHEN CREW ARRIVES ON POLE 255-200/OPENED 1030/CLOSED 1215POLE SMOKING REALLY BAD ABOUT TO CATCH FIRE AT 108 HONEY CUT, OPENED RECLOSERS ON POLE 231-291, 811 DIG # IS 1509120062, GAVE MATERIAL LIST TO T. SMITH, CAN CUT LOOPS WHEN CREW ARRIVES ON POLE 255-200. OPENED RECLOSERS TO MAKE LOOPS UP AT 18:14/ON 1836// VER/ ADH L3/HFP XXXHFP AJB
404 | South Williamson | 3411401 | DEWEY | INEZ | 2008-04-27 02:34 | 2008-04-27 04:27 | 3025 | 113 | 54474-1 | 121982 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3411401//DDC ISSUED A HOLD ORDER TO ROGER MAYNARD BETWEEN THE DEWEY/INEZ 34KV CB C AND THE GOAB AT POLE 837-57// AT 0427 ALL CUSTOMERS SHOULD BE RESTORED// FOREST FIRE 1 MILE OUT OF STATION - PERSONNEL WILL CHECK DURING DAYLIGHT HOURS// BOLT TO INSULATOR BROKEN/CKTS BACK TO NORMAL AT 0946 VER/KEP IDC ADDED 7 CUSTOMERS FOR ADJUSTED COUNT AND ADJUSTED SOME TIMES TO MATCH SCADA XXXX
405 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-02-10 13:31 | 2018-02-10 16:42 | 638 | 191 | 4823271 | 121858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Servicer found broken cutout. Will need 1 A to assist in replacement. POLE 1130-165,CUTOUT BROKEN.NEED 2 MEN,1 19.9 CUTOUT,NO ACCESS.POLE ACTUALLY BEHIND A LOCKED GATE&FENCE///////CHANGED CUTOUT,RESTORED @16:42 Released by crew 074S06 L3/HFP
406 | South Williamson | 3411401 | DEWEY | INEZ | 2020-05-14 19:01 | 2020-05-14 22:45 | 544 | 224 | 4836781 | 121856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | reclosers locked out on pole 649-322//A phase burnt down at a fault indicator at pole 38820649B00057 ,havent seen any thing else //reclosers locked out on pole 649-322//A phase burnt down at a fault indicator at pole 649-57,havent seen any thing else //making repairs//repairs made//complete//em
407 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-03-27 00:54 | 2008-03-27 04:20 | 935 | 206 | 61031-1 | 121778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001101// ISOLATED SECTION OF LINE BETWEEN 87 AND 995 AND RESTORED CB AT 0304 RELEASED BY CREW 078S07 VER/LDA IDCC TOF 0013 XXXX
408 | Whitesburg | 3309302 | VICCO | JEFF | 2019-05-02 19:05 | 2019-05-03 09:36 | 139 | 871 | 4202321 | 121069 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | tried to energize the recloser on pole 323-649 but it came back out. Narrowed the issue down to pole 323-241 bad deadend or loop insulator. Need manual ROW crew and line crew in the morning as per supervison. Go up Maple Dr to access the pole. Released by crew 077H20//NO TAGS// L3/HFP
409 | Hazard | 3310502 | HADDIX | CANOE | 2013-02-19 01:01 | 2013-02-19 08:52 | 450 | 471 | 4828341 | 120911 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKE CROSSARM ON POLE 121-40 GOT CREW COMMING TO REPLACE RELEASED BY CREW 077S05 //VER/GAH IDC XXXX
410 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-06-09 08:27 | 2021-06-09 13:04 | 679 | 277 | 4694801 | 120342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Recloser open @ pole 214-D-944 (ASSESSING CONDITION)..Fault on B and C PHASE..Pole 239-182 is laid over into a couple trees going to need Line crew to try and Strighten pole and Put a Anchor and Guy on it also Tree Crew to Remove Tree.. Released by crew 074S01 REPAIRS COMPLETE 13:04
411 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2021-07-12 09:18 | 2021-07-12 14:10 | 1257 | 292 | 4897351 | 120204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | sdb / 0918 / CB operated. circuit exit pole 69-650 (PH A) disc. burnt open. 322 cc currently affected. Will need to open CB to make repairs. Looking at possible field load transfers opened CB at 1342 dropping remaining 935 CC closed NO SWS at 38830069C45608 restoring all CC at 1410 LR- The time on for all is 14:10 on 7-12-21
412 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-03-01 01:32 | 2019-03-01 03:57 | 990 | 145 | 4940591 | 120006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | rec. open on pole 144-581..will patrol..bypass switch broke on rec. pole 144-535. isolated @ pole 144-293 and made repairs. restored..please send copy to Mike Hatfeild to get bypass switches changed out on pole 144-535. Released by crew 074S01 L3/HFP
413 | South Williamson | 3411401 | DEWEY | INEZ | 2011-04-16 14:08 | 2011-04-16 16:49 | 803 | 161 | 57918-1 | 119889 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND 3 HASE POLE BURNT OFF HANGING HOT WILL GO BACK TO SWITCHES AND OPEN TO MAKE SAFE , CREW LOADING NOW , TCM // WILL ISOLATE SWITCHES ON 720-118 WHEN CREW ARRIVES TCM// OPENED REC ON 744-C-311 @ 1408 - CLOSED @ 1415FOUND 3 HASE POLE BURNT OFF HANGING HOT WILL GO BACK TO SWITCHES AND OPEN TO MAKE SAFE , CREW LOADING NOW , TCM // WILL ISOLATE SWITCHES ON 720-118 WHEN CREW ARRIVES TCM// OPENED SWITCHES AT 14:11 STARTING WORK TCM// CLOSED SWITCHES AT 16:49 TCM// VER/HFP L3/HFP IDCC PN7 DCMT XXXX
414 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-10-14 08:47 | 2011-10-14 13:50 | 395 | 303 | 4977621 | 119685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE, POLE # ON FIRE IS 182-29, J. COMBS CREW IS COMING TO REPAIR // COD 395 // VER/DBM IDC XXXX
415 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-07-20 | 2015-07-20 05:13 | 392 | 313 | 4914061 | 119618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELEASED BY CREW 074S02 VER/SEF AJB
416 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2017-05-23 21:12 | 2017-05-24 04:28 | 302 | 436 | 4845161 | 119512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | RECLOSER ON 53-143 OUT PATROLLED LINE SAW NO HAZARDS TRIED RECLOSER IT CAME BACK OUT DENNIS ISOLATED LINE AT 53-21 AND CLOSED RECLOSER ON 53-143 AT 02;20 CPHASE OFF OF INSULATOR ON 53-148 NTA MADE REPAIRS OPENED RECL ON 53-143 AT 04:15 REINSTALLED HOT TAPS ON 53-21 AND REENERGZED RECL ON 53-143 AT 04:28 RELEASED BY CREW 079H03///C PHASE OFF PIN AT 53-148///ORIGINAL OUTAGE RECORD/// VER/DKM L3/HFP XXXHFP AJB
417 | Hazard | 3301401 | COMBS | COMBS | 2015-02-01 21:35 | 2015-02-02 01:54 | 460 | 259 | 4979851 | 119140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ROTTEN CROSSARM BROKE ON POLE 37830271C00323, NEED 3 MAN CREW WITH BIGGEST BUCKET, 8 FT ARM PINS AND INS. AND FLAGGERS. RELEASED BY CREW 077S04 CHANGED CROSSARM AND RESTORED POWERAT 0154 CREW 077H01 VER/SEF L3/HFP XXX AJB
418 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-01-23 15:11 | 2017-01-23 19:05 | 508 | 234 | 4323281 | 118872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON POLE 213-66.WILL PATROL////FOUND XFM. CUTOUT BROKEN ON POLE 237B-196//.REPAIRS MADE AND CLOSED BACK IN @ 19:05/ ISO 37830213000066/ COD 508/ VER/BOW L3/HFP XXXHFP AJB
419 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2017-07-28 10:35 | 2017-07-28 13:05 | 786 | 150 | 4193621 | 117900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | DOL 760626 // SCADA INDICATES FEEDER BREAKER LOCKOUT @ 1035//COD 786 // RELEASED BY CREW 078S01 /// TIMES PER DOL & SCADA = L3/HFP XXXHFP SJG
420 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2018-12-01 01:31 | 2018-12-01 08:47 | 533 | 436 | 4495731 | 117848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 879195 // Feeder Lockout @ 0131 per SCADA // cod 533 //. bad cutout on pole 401-66, opened disconnects on pole 425-47 to isolate. closed feeder cb @ 0302 restoring 332 customers///cutout burnt top of pole 401-66 off, replaced pole restored power at 08:47 to 201 customers.. Released by crew 077S11 /// VERIFIED TIMES PER SCADA & DOL = L3/HFP
421 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-09-20 03:18 | 2017-09-20 07:16 | 659 | 238 | 4374791 | 117626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | 38830164A13664 BAD ARRESTOR--REPLACED-RV,DM,DS092017 RELEASED BY CREW 078S01/DOL LOG 772682 SJGC STEP3 TON07:25 PER DOL, FP 38830140B12028, CDC86, FEC40 (ORIGINAL OUTAGE WAS CAUSED BY ARRESTER), STEP1 TON03:19 CNT333 (DELETED, ONLY MOMENTARY STEP)
422 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-12-25 16:35 | 2022-12-25 20:27 | 930 | 232 | 4356851 | 117301 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ORIGINAL OUTAGE STEPDOWN 38830501000034 (COD 52)FEEDER OUTAGE STARTED AT 1643. lifted hottap on pole 501-289 to isolate burnt of pole 501-34. 3phse back in @ 18:18. crew required truck to pole need wooden poletop extension. hottap on pole 501-289 back in @ 20:22. fuses on pole 501-34 back in @ 20:27 restoring all customers. complete LR- DOL 1261457
423 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-06-16 17:47 | 2012-06-17 00:47 | 334 | 420 | 4921271 | 116805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM ON POLE 1039-21 IS ROTTED OFF, OPEN GOAB ON POLE 1039-107 AND CLOSED RECLOSER ON POLE 1062-64 AT 1934 RELEASED BY CREW 077S05 // RESTORED AT 0047 IDCC FP NULL TRUCK BECAME STUCK NEED A WRECKER, EXTENDED OUTAGE XXXX
424 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2021-10-30 18:15 | 2021-10-30 23:02 | 459 | 287 | 4041921 | 116721 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 1159117 // feeder lockout predicted by POR @ 1815 // Verified breaker open will be patrolling/// End of crossarm has broke off and phase is laying on side tap @ pole 834-B-271. Opened goab on pole 38830834B31029 to isolate and closed breaker restoring up to that point @ 21:14. Have lineman and big bucket onsite to assist with repairs/// Made repairs and restored @ 23:02 Released by crew 076S03
425 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-03-02 02:33 | 2015-03-02 05:30 | 657 | 177 | 4089721 | 116289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HARVEY TO ASSIST.AM PATROLLING LINE.HAVE A BAD LINE CUTOUT ON POLE 69-17.WILL REPLACE.WORK COMPLTED VER/SEF L3/HFP XXX AJB
426 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-02-07 07:30 | 2019-02-07 10:55 | 1028 | 205 | 4761361 | 115960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CB C L/O 0728/ cc1028/ Insulator failed on 810-13 and burned 4/0 primary down (Ph C). Crew onsite to repair. Completed repairs and closed switches on 810-24 @ 10:55. sh Released by crew 076S02
427 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-01-27 11:34 | 2022-01-27 15:00 | 661 | 206 | 4409201 | 114378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B phase down between 42-C-9 to 42-C-6 Opened 3 SWS at 42-C4-1064wire down from pole 42-c-9 to pole 42-c-6, opened up switches on pole 42-c-1064 to make repairs, made repairs an got switches back in at 15:00 on pole 42-C-1064
428 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-07-16 18:53 | 2018-07-16 20:50 | 975 | 117 | 4783431 | 114075 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON HALS FORK XFMR FEEDING CT TO FLIP FLOP SWITCH L3/HFP
429 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2015-02-20 18:13 | 2015-02-20 22:00 | 501 | 227 | 4058701 | 113727 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | EMERGENCY OUTAGE DUE TO GOAB SW FAILING // OPENED CB VIA SCADA @ 1914 - 567 CUST PHASE A AND C IS BURNED UP ON THE GOAB. THE GOAB WILL NEED TO BE BYPASSED. LINE CREW IS EN-ROUTE TO MAKE REPAIRS. POLE 37820008A00150 IS OPENED AND TAGGED TO KYDDC. RELEASED BY CREW 079S02// CLOSED CB VIA SVC @ 2200 VER/TOM L3/TOM L3/HFP HFPC CNT 567 AJB
430 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-06-10 13:13 | 2009-06-10 15:00 | 1062 | 107 | 50310-1 | 113634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | EMERGENCY OUTAGE TO MAKE REPLACE INSULATORS THAT HAVE FAILED // OPENED 3 - 600 AMP SOLID BLADES @ 1073-17 @ 1313 AND CLOSED IN @ 1500 ALL CUSTOMERS RESTORED IDC CHECK FOR PREVIOUS OUTAGE MLR OK
431 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-09-09 17:13 | 2009-09-09 20:44 | 1037 | 211 | 61153-1 | 112828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP /// SHOULD HAVE APPROXIMATELY 809 CUSTOEMRS RESTORED BY 1900 WILL PROVIDE UPDATE FOR 228 CUSTOMERS THAT REMAIN INTERRUPTED.WR # 31642281WIRE DOWN ON POLE 902-142 4/0 B PHASE OPEN UP ON 902-116 3 -300AMP SOLID BLADE CREW REQ, GIVE TO VERNON MULLINS RELEASED BY CREW 078S06/CREW ON SITE/FETR2130/VEM/REMAINING CUST RESTORE2044/PLEASE CLOSE RELEASED BY CREW 078H14 L3/HF IDC XXXX
432 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-10-08 07:19 | 2017-10-08 11:22 | 463 | 243 | 4419671 | 112509 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 463 CUSTOMERS OUT WHEN LINE FELLDEAD END INSULATOR PULLED INTO ON POLE 1101-D4-578 ON C PHASE, 1 SPAN OF 556 DOWN, CREW ENROUTE TO HELP MAKE REPAIRS, WILL HAVE TO OPEN STATION BREAKER TO MAKE REPAIRS. RELEASED BY CREW 074S05 ON @ 1122 VER/ARN ACB (SEE OUTAGE 4421011)
433 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-04-17 16:56 | 2018-04-17 23:00 | 309 | 364 | 4246621 | 112476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened @ 1656crew on site/ 50/2 p burnt off at cutout. material list in the assessment tap/ ISO 38831125D00638/ COD 309/ L3/HFP
434 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-12-21 10:28 | 2013-12-21 16:46 | 297 | 378 | 4180921 | 112266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ONLY PHASE A IS OPEN// MIDDLE PHASE (A) JUMMPED OFF OF INSULATOR ON POLE 179-B-148//SUSPECT DUE TO WIND//LINE CREW REQUIRED//COD 297//REC. POLE 202-208 ARE ALL CLOSED./// POLE 37830179B00148 MIDDLE HAS JUMPED OFF INSULATOR AND LAYING ON THE ARM. CREW REQUIRED. MANUAL POLE. THIS IS ACROSS ROAD FROM EMALENA GRADE SCHOOL. MIDDLE PHASE REC. IS OPEN ON POLE 179-194. WILL LEAVE OTHER 2-PHASES IN.REC. POLE 202-208 ARE ALL CLOSED.///OPENED OTHER 2 PHASES @ 1511 (COD +461)// VER/HFP L3/HFP IDC XXXX
435 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-01-22 00:54 | 2009-01-22 02:31 | 1157 | 97 | 59030-1 | 112229 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | 3110903/A 69KV INSULATOR ON THE TRANSMISSION LINE HAS FAILED OPENING THE TRANSMISSION LINE VER/KEP L3/KEP MLR OK
436 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-12-18 08:29 | 2016-12-18 09:44 | 1490 | 75 | 4212651 | 111750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | SCADA INDICATED THE EUCLID 12KV CB B OPERATED TO LOCKOUT// 1490 CC AFFECTED// RECLOSER ON FIRE - PLAN IS TO OPEN SWS - FIRE DEPT WILL EXTINGUISH, SERVICER WILL BYPASS AND DDC WILL CLOSE CB// APPROX 45-60 MINUTES//TOM / CLOSED CB VIA SVC @ 0944 /// VER TIMES PER DOL & SCADA VER/HFP L3/HFP AJB
437 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-09-01 01:24 | 2021-09-01 10:40 | 219 | 556 | 4189181 | 111460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened 2 fuses on 98-278 to cut tree @ 8:50 closed back in @ 9:44///Broke cutout on 98-277 Restored @ 10:40
438 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-02-24 19:50 | 2016-02-25 17:18 | 271 | 1288 | 4766781 | 110933 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLD ORDER REQUIRED/ENERGIZED FROM POLE 16D-280 TO 16C-53 AT 22:04 , GROUNDS PLACED AT POLE 3783-16C-38, 16C-45 ISOLATED AND TAGGED FOR KY DDC, 300A SWITCHES INSTALLED AT POLE 16C-296 ISOLATED AND TAGGED FOR KY DDC, CLOSED AT POLE 16-53 TO POLE 16-296 AT 02:35 RELEASED BY CREW 074S03 VER/KEP // TIMES PER DOL = L3/HFP XXXHFP AJB
439 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-06-18 00:31 | 2020-06-18 04:42 | 1160 | 251 | 4038871 | 110912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 1028692 // DDC HOLD ORDER //feeder lockout @ 1231 per SCADA // #2 AA primary down (PH C) middle //found tree on line at pole 761-8, fault current burned down conductor at 761-198 // cod 1160 // DDC HOLD ORDER //
440 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2008-10-07 22:58 | 2008-10-08 04:05 | 371 | 307 | 54004-1 | 110647 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3200204//, ONE PHASE OF 69KV LINE IN ROAD, PRIMARY AND NEUTRAL DOWN, MAKING REPAIRS RELEASED BY CREW 080S01 VER/ARN IDC XXXX
441 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-06-02 23:23 | 2008-06-03 01:28 | 882 | 125 | 54766-1 | 110250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | CREWS OPENED RECLS AT POLE 771-A-412 TO ISOLATE POLE FIRE AT 771-73 CLOSED AT 01228 VER/PDP IDC XXXX
442 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-07-12 07:26 | 2011-07-12 14:14 | 270 | 408 | 4528171 | 110160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ONLY B PHASE OUT (MIDDLE PHASE)---POSSIBLE BAD POST TOP ---WILL HAVE TO DROP 3 DV AT POLE 270-183-1 HOUR--NOT SURE IF THIS IS FAULT TIL WE LOOK AT CLOSER-FETR -1400--JEFF COMBS CREW--B PHASE OUT 0730-1405--A&C 1315 TIL 1405-- RELEASED BY CREW 077S06 IDC XXXX
443 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-09-01 22:05 | 2011-09-02 01:40 | 512 | 215 | 4782141 | 110080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW OPENED SWITCH TO SAFELY REPLACE A BROKEN POLE/NO OUTAGE TILL 2205 //VER/GAH IDC XXXX
444 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-01-13 02:15 | 2017-01-13 10:32 | 448 | 497 | 4293731 | 110012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ***SEE 4294591*** FAILED EPXOLATOR POLE 150-107 ISOLATED & CLOSED RECL 37830150000099 AT 0620 RESTORED 447 CUST/FOUND BAD DEADEND INSULATOR ON POLE 150-107 . TOOK CLAMP OF TO CLEAR INSULATOR . CLOSED RECLOSER BACK IN @ 6:20 , ALL POWER BACK ON EXCEPT 1 CUST. NEED CREW WITH BIG BUCKET & FLAGERS / 37830150000107 @ 1032/ VER/BOW L3/HFP XXXHFP AJB
445 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-08-19 09:22 | 2021-08-19 11:36 | 1039 | 134 | 4116831 | 109898 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 114135 / Bad bypass cutout on REC. pole 882-A-457. Opened switches on 882-A1-953 to isolate for repairs. Closed breaker and partially restored @ 10:48/// Replaced all 3 bypasses and restored @11:36 Released by crew 076S03
446 | South Williamson | 3202201 | LOVELY | LOVELY | 2021-07-24 14:14 | 2021-07-25 01:42 | 190 | 688 | 4951641 | 109754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HOLD ORDER REQ //DOL 1134267//left hand recloser open on pole 746-243//patrolling//fault indicator flashing at pole 721-d-50///didn't see anything and next one was not flashing//tried recloser and it came back out//POLE 38820697D00060 IS BROKE //HOLD ORDER REQ//
447 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-06-21 01:04 | 2011-06-21 15:46 | 327 | 882 | 4359131 | 109371 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC OUT ON 679-363 ISOLATED ON POLE 728-8..RECLOSER BACK ON AT 2.21..CALLED TIM MILLER TO HELP PATROL..TOP OF POLE BURNED OFF 728-43.. RELEASED BY CREW 076S01//CREW ON SITE STARTING REPAIRS TCM// CLOSED IN AT 15:46 SHOULD HAVE PICKED ALL 50 CUSTOMERS BACK UP TCM// RELEASED BY CREW 076H01 // SEE LOG FOR ADDITIONAL SWITCHING // //VER/GAH IDCC FP363. TON STEP ONE XXXX
448 | Hazard | 3303902 | LESLIE | WOOTON | 2020-01-09 09:19 | 2020-01-09 13:57 | 465 | 278 | 4227161 | 109223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RECLOSER 37830389C00015 OPEN//COD 459//PATROLLING//RECLOSER 37830414000134 IS ALSO OPEN //OPENED RECLOSER 37830462D30333//CLOSED A & C RECLOSER ON POLE 37830389C00015 @ 1252//CLOSED RECLOSER 37830462D30333 @ 1303// Released by crew 077H14//CLOSED RECLOSER 37830414000134 @ 1357
449 | Pikeville | 3403001 | PIKEVILLE | CITY | 2021-06-19 08:33 | 2021-06-19 10:00 | 1572 | 87 | 4770921 | 109110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | conductor broke off insulator due to deteriated brackets/ CLosed CB 3403001 at 0927 restored 838 customers/ closed switches 37830048C10648 at 1000 restoed 735 customers
450 | South Williamson | 3411401 | DEWEY | INEZ | 2022-02-22 07:04 | 2022-02-22 09:10 | 969 | 126 | 4526541 | 108354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1185278 // SCADA indicates DA RECL 744-D2-578 operated to l/o @ 0704 // DA RECL 744-D2-527 opened (de-energized)at 0705 //N.O DA SW 746-B-218 closed at 0705 //cutout broke on 744-a-398//
451 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-06-10 14:27 | 2021-06-10 16:15 | 1002 | 108 | 4707101 | 108216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | insulator went bad causing wire to burn down @ pole 374-97. one span of primary down and busted insulator. power restored
452 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-03-31 02:48 | 2010-03-31 07:40 | 369 | 292 | 56301-1 | 107748 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | MOBILE CS6 TRIPPED OUT@HAYWARD -STATION OUTAGE, SERVICERS DISP. CAUSE UNKNOWN@ THIS TIME, WILL UPDATE ASAP.@0400 , SERVICER @STATION REPORTS MOBILE CB TRIPPED OUT,ISOLATING EQUIPMENT&IF NO PROBLEMS ARE FOUND MOBILE CB CAN BE RESTORED.@0446 , ATTEMPTED TO CL MOBILE CB TRIPPED BACK OUT. 0520 , STATION CREW REPORTS PROBLEMS WITH MOBILE CB, PLAN NOW TO PLACE STATION TR BACK IN SERVICE.RELEASED BY AJBC TON06:26 FEC57 WIRE IN FAN ON XFR CAUSED MOBILE CB TO LO.
453 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2016-03-25 08:17 | 2016-03-25 14:49 | 712 | 392 | 4881071 | 107705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE IN BREAKER ZONE OPENED CB TO ISOLATE/BAD CUTOUT ON POLE 376-109, BURNT POLE OFF, ISOLATED BREAKER AT STATION./LOAD TRANSFER FOR PARTIAL RESTORE/ RELEASED BY CREW 077H16 SEE H4881071 FOR OUTAGE TO RETURN TO NORMAL (589 CUST) (PROBLEMS WITH SW PREVENTED TYING AND SEPERATING THESE CKTS) VER TIMES PER DOL & SCADA VER/HFP L3/HFP AJB
454 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-08-12 06:45 | 2022-08-12 09:48 | 588 | 183 | 4731661 | 107604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recloser is open on 527-18, A phase dn at 576-9004, Opened Sec on 552-581 to isolate. Rec 527-18 in @ 0809 hot to 552-581. Crew in route Grounds and tagged to dwest @ 576-9004//// All repairs made & apr @ 0948. Ticket comp. Released by crew 078S11
455 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-01-05 11:09 | 2013-01-05 13:07 | 1252 | 118 | 4571081 | 107457 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | INTERNAL PROBLEMS WITH THE STATION TRANSFORMER - TRANSFERRING LOAD TO ALT SOURCES & CALLING STATION CREW TO INSTALL MOBILE TR AT CANNONSBURG STATION //VER/GAH IDC XXXX
456 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2009-01-22 00:54 | 2009-01-22 04:50 | 455 | 236 | 59033-1 | 107380 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | 3000903/A 69KV INSULATOR ON THE TRANSMISSION LINE HAS FAILED OPENING THE TRANSMISSION LINE VER/KEP L3/KEP MLR OK
457 | Whitesburg | 3409503 | BURDINE | JENKINS | 2017-09-14 08:45 | 2017-09-14 14:23 | 353 | 338 | 4361341 | 107308 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | DOL 771556//CENTER PHASE FUSE OPEN ON STA XFMR // OPENED 46KY CB D @ BURDINE @ 0941 //N.O. SWS @ 37830382A30267 ALSO BURNT UP// @ 1325 REPORTED FETR UPDATE TO1530 HAVING TROUBLE WITH BOLTS ON SWS, IF NO MORE TROUBLE WITH BOLTS POSSIBLY 1 - 1 1/2 HOURS APPROX 1430 - 1500//COD 353//TWO UNDERARM SWS FAILED AND TOOK THE BURDINE STA -JENKINS CIRCUT BREAKER OUT , I ISOLATED AT 358-317 AND 382-44, WE CHANGED BAD SWS RELEASED BY CREW 077S12// VER/DBM // L3/HFP HFPC TOF 0850 SJG
458 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-03-31 11:25 | 2015-03-31 15:45 | 1316 | 260 | 4246761 | 106775 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATES FEEDER BREAKER LOCKOUT @ 1125//SERVICER PATROLLING//COD 1316//FOUND NO CAUSE//BREAKER CLOSED VIA SCADA @ 1246//AFTER RESTORATION FOUND BAD INSULATOR ON POLE 37830483A00150//1 CUSTOMER REMAINS OUT// RELEASED BY CREW 077S01 POWER RESTORED 077H18// VER/DBM AJB
459 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2019-02-28 22:46 | 2019-03-01 12:02 | 134 | 796 | 4940271 | 106664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | middle & left hand recloser locked out//tried recloser and came back out//saw flash,going to patrol again//found bad pole top insulator on pole 188-c-22//i believe this is right pole # ,not tagged in field//back on hill//will need line crew to work in the morning//need flaggers to isolate reclosers//opened xfmr bank on 188-17//SEE NOTHING OBVIOUS WOULD LIKE TO CLOSE IN AT PL#188A416 AND STAND BY AT PL#188C22 WHERE CUST SEEN FLASH- CENTER PH. ALL REST @ 1202//// Trouble tickets show all cust out
460 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-04-28 12:57 | 2008-04-28 15:31 | 778 | 154 | 55041-1 | 106562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3303903//CROSSARM BROKE//ISOLATED AT SWITCH POLE 387-693 AND RESTORED UP TO @ 1345//TOTAL COD 778// VER/DBM IDC XXXX DEB OK
461 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-08-18 09:47 | 2014-08-18 12:35 | 634 | 168 | 4378421 | 106512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | THERE IS A BAD PIN INSULATOR ON POLE38831125A00157 WILL HAVE CREW CHANGE . HAVE ALREADY NOTIFIED SUPERVISOR. RELEASED BY CREW 074H04 VER/CRB AJBC TOF04:19
462 | Hazard | 3303902 | LESLIE | WOOTON | 2009-04-29 10:41 | 2009-04-29 15:44 | 433 | 303 | 57520-1 | 105947 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303902//@1235 TRIED RECLOSER AN IT CAME BACK OUT//TIM SMITH ENROUTE TO HELP RUN OUT//FAULT WENT THROUGH THE 40T FUSE ON POLE#413-82//BAD CUTOUT ON 413-353// VER/DBM IDC XXXX
463 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-03-10 04:03 | 2011-03-10 08:14 | 931 | 251 | 52650-1 | 105875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN AT POLE 45-6710, ISOLATING BY OPENING SWITCHES ON POLE 45-6511REXLOSERS BACK IN AT 05;15--- POWER ON @ 08:14 HENDRIX BURNT IN TWO VER/KEP IDC XXXX
464 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2013-12-24 22:23 | 2013-12-25 02:13 | 460 | 230 | 4199481 | 105800 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | ATTEMPTING TO CALLOUT CREW. *** 2238- CALLOUT CREW ENROUTE TO PATROL CKT *** WILL CK OUT REPORT OF TR FIRE ON DUNAWAY LN.ATTEMPTING TO CALLOUT CREW., BLOWN ARRESTORS ON STATION TRANSFORMER, TWO FUSES BLOWN ON XFMR HIGH SIDE, STATION HAS BEEN CONTACTED ** DIST LOAD TRANSFER IN PROGRESS. CB A ISOATED AT LDS LOAD TRANSF TO SS/SILOAM 12KV CKT VIA N.O. SWS AT POLE 878-102 VER/PDP L3/HFP IDC XXXX
465 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-09-24 18:56 | 2011-09-24 20:36 | 1062 | 100 | 4912691 | 105549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED CKT FOR CREW TO MAKE REPAIRS IN DIFFICULT LOCATION IDC XXXX
466 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-06-22 00:29 | 2010-06-22 09:33 | 194 | 544 | 54268-1 | 105536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER ISSUE - OPEN INTERNALLY - REMOVED A/C - OPENED AND THEN CLOSED BACK - ALL RESTORED ON THIS OUTAGE PAF IDC XXXX
467 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2020-07-02 20:04 | 2020-07-02 22:34 | 702 | 150 | 4105711 | 105300 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE HARDWARE | DOL 1032777///Beaver Creek-Elwood 46kV Ckt locked out interrupting Burton Station.///CB closed at 2234
468 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2011-06-21 21:42 | 2011-06-22 09:50 | 144 | 728 | 4377681 | 104832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | B PHASE ONLY (144 CUSTOMERS) , PATROLED LINE AND FOUND NO HAZARDS, BYPASSED BAD RECLOSURE AT POLE 280-237 AND COMPLTED SOS 1061 REV 8, PLEASE ADD TO ABNORMAL. ALL POWER RESTORED CCC---- COD-144 ISO OCR 38830280A40020 VER/HFP L3/HFP IDC XXXX
469 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-01-17 23:02 | 2022-01-18 01:43 | 749 | 161 | 4378781 | 104443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Hold Order/ DOL 1176609/ Defective Pole Top Insulator Center (B) Phase at pole 38821082C40340
470 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-03-08 09:13 | 2008-03-08 12:10 | 956 | 177 | 54917-1 | 104272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008702// BAD 19.9 CUTOUT ON POLE 116-350//RESTORED MAIN LINE (ALL BUT 1 CUSTOMER) @ 1102//CREWS TO REPLACE BAD LINE CUTOUT// ........REPLACED CUT OUT, POLE WILL NEED CHANGED @ A LATER DATE DUE TO POLE FIRE. BLR//LAST CUSTOMER ON @ 1210// VER/DBM IDC XXXX
471 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2019-07-30 19:53 | 2019-07-31 09:59 | 123 | 846 | 4812421 | 104058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | At 1952 SCADA Indicated that the Sprigg/ Matewan 34kV Ckt locked out. closed fbr at 03:20 to open l/s on 992c429 //closed sws and restored all custs at 0959
472 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-03-23 21:32 | 2014-03-23 22:50 | 1334 | 78 | 4520401 | 104052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT DOWN POLE 150-127, LIFTED HOT TAP POLE 150-149, SINGLE PHASE TAP FEEDS NOTHING, WILL BE REPAIRED LATER // SEE 4520611 FOR OUTAGE ON WATER TOWER, CHANGED TIME OFF & ON TO WHAT SCADA INDICATED ON THE BONNYMAN-HAZARD #1 69KV CKT FROM HAZARD CB F ...HFP// VER/GAH L3/HFP HFPC TOF2135 TON2252 IDC XXXX
473 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-11-08 07:14 | 2011-11-08 08:56 | 1018 | 102 | 4058271 | 103836 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | TRANSFORMER OUTAGE - TDC NOTIFIED STATION PERSONNEL ENROUTE / DISTRIBUTION SERVICER ENROUTE // 34KV PHASE 3 BUS POT FAILED //VER/TOM L3/TOM IDC XXXX
474 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-06-11 03:30 | 2013-06-11 15:01 | 411 | 691 | 4256451 | 103661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SDB / 0330 / FEEDER LOCKED OUT. 411 CC --- SDB / 0603 / SWS AT POLE 139-C-324 OPENED TO ISOLATE PROBLEM, CB CLOSED REST 190 CCPOLE #37830139C00326BURNED OFF AB. NETURAL. WILL NEED TRACK MACHINE, DOZER ,42/2 ,2-9 ARMS,4PINS & INSULATORS 2 POLE TOP PINS & INSULATORS, CLEVIS & SPOOL.THIS IS 19.9/ 34.5 // 0820 - IN PROCESS OF TRANSFERRING LOAD// POLE #37830139C00326,RELEASED BY CREW 074H03 VER/TOM L3 IDCC TOF0333, STP MISSING XXXX
475 | Hazard | 3302703 | HAZARD | HAZARD | 2017-05-27 17:57 | 2017-05-27 20:30 | 677 | 153 | 4871031 | 103581 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | RELEASED BY CREW 077H07 TIMES PER SCADA & DOL & SOS 3521 REV 37 L3/HFP HFPC LCD37830272B40346 CDC80 FEC78 TON2108 AJB
476 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-08-03 18:09 | 2021-08-04 00:45 | 324 | 396 | 4999211 | 103539 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap lead burned into on pole 818-178 on solid blade switch//left hand phase out only//opened switches at 00:30 to make repairs//repairs made//restored at 00:45//complete//em //cod 259 +65 // ISO
477 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-12-16 22:55 | 2008-12-17 01:20 | 714 | 145 | H59315-1 | 103530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3007904//SWITCH ON POLE 549-97 WAS ON FIRE PHASE CLOSER TO THE ROAD. I OPEN RECLOSER ON POLE 501-337,,,DHE CREW ON THE WAY , 34KV SW AT POLE 459-97 WAS NOT FULLY CLOSED, OPENED & RECLOSED SWITCH THEN AT 0120 CLOSED 34KV RECLOSER AT POLE 501-337 //VER/GAH "A" PHASE OPEN TILL RECLOSER OPENED L3/KEP IDC XXXX
478 | Pikeville | 2974101 | BIG ROCK STATION | CONAWAY | 2018-07-26 15:02 | 2018-07-26 18:05 | 565 | 183 | 4860161 | 103395 | SUBTRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | 2974101; SOS 15984/4; DAVOX scheduled from 1500; opened Big Rock 34kV CB D at Grundy via SCADA @ 1502; 34kv sub-transmission; cc 565; restored @ 1805; /// QUESTION ABOUT CLEARING DEVICE ? L3/HFP
479 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-06-01 15:03 | 2012-06-01 21:12 | 279 | 369 | 4864631 | 102951 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN OVER ON HILLSIDE === NEED LINE CREW AND ROW CREW === NEED SOME 1/0 WIRE == POLE 37830393C40342 == GOING OPEN AT POLE 37830393C00255 == UNDER HUNG SWITCHES == RELEASED BY CREW 077S03 OPENED SWITCHES ON POLE 255 AT 19.10 CLOSED AT 21.12 ALL POWER RESTORED SEE 4869521 FOR ASSOCIATED OUTAGE COD-279 ISO 37830393C00255 VER/HFP L3/HFP IDC ORIGINAL WIRE DOWN AT 37830393C40342, OPENING SWITCHES ONLY OUTGE 7 MORE CUSTOMERS XXXX
480 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2021-12-11 16:20 | 2021-12-11 20:49 | 382 | 269 | 4181751 | 102758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 4173231 // Draffin Belcher circuit breaker B is open will be patrolling////Crossarm broke on pole 147-86 will need line crew///Replaced crossarm and restored service @ 20:49//cod 382
481 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-02-19 23:22 | 2015-02-20 05:35 | 275 | 373 | 4045841 | 102575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQUIRED C PHASE DOWN OPEN RECLOSER ON POLE 219-135 TO MAKE SAFE AT 0123 HRS/POLE 38830219000036 # 2 ALUM RELEASED BY CREW 078S03--ISOL REC, TAGD AND GNDS PLACED PL#219-135,,,RMV--FETR 06:30---REPAIRED 1 SPAN #2AA---CLOSED 3 NOVA RECLS @ 05:35---TBL TKT COMP---RMV AJB
482 | Hazard | 3303902 | LESLIE | WOOTON | 2018-04-13 12:53 | 2018-04-13 19:35 | 1408 | 402 | 4220461 | 101970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | DOL Case 817684///Underslung switch bad on 37830414000064. Isolating at 37830414000107.BAD 600 AMP SWITCH ON REC POLE/// CUT LOOPS ON 414-107 AND 438-1BAD 600 AMP SWITCH ON REC POLE/// CUT LOOPS ON 414-107 AND 438-1 Released by crew 077S01
483 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2011-04-25 20:46 | 2011-04-26 12:35 | 116 | 949 | 65071-1 | 101964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURNT OPEN AT POLE 538-17 VER/KEP IDC LOOKS LIKE OPENED WHEN BREAKER OPENED CHANGED START TIME FROM 2302 OPENED AT POLE 37830538D30201 FOR MORE TROUBLE XXXX
484 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-12-28 03:00 | 2011-12-28 14:10 | 152 | 670 | 4209321 | 101840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 37830151000016 IS BURNT OFF ABOVE TRANSFORMER, MANUAL POLE, BUCKARM, RECLOSERS OPEN AT POLE 37830151000089 RELEASED BY CREW 077S04 POWER RESTED AT 1410 IDC XXXX
485 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-07-22 09:38 | 2020-07-22 14:38 | 339 | 300 | 4200391 | 101700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | PER GEORGE WHITAKER BROKEN CROSSARM AT HIS HOUSE // repaired and restored @1438
486 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2011-05-12 06:34 | 2011-05-12 11:03 | 519 | 269 | 4070011 | 101611 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 39935825 // BAD INSULATOR 319-14/ OPENED SWS 343-188 AND CLOSE REC 344-144 AT VER/HFP L3/HFP
487 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2016-11-02 13:23 | 2016-11-02 16:56 | 477 | 213 | 4070211 | 101601 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER 37830174D44412 WAS ON NON-RECLOSE WHEN AN INSULATER FAILED //GREG FUGATE ENROUTE TO ASSIST KEITH CAMPBELL//RECLOSER SOURCE SIDE RISERS ISOLATED AND EACH TAGGED //GRNDED @ POLE 37830223A00173//KEITH CAMPBELL REMOVED HIS TAG AND GREG REPLACED WITH HIS OWN //GREG FUGATE ENROUTE TO ASSIST KEITH CAMPBELL... BAD INSULATOR ON POLE 37830223A00172 VER/CRB L3/HFP XXXHFP AJB
488 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-11-04 00:26 | 2012-11-04 02:05 | 1026 | 99 | 4353841 | 101574 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE HARDWARE | CAUSE UNKNOWN, TRANSMISSION LINE OUTA (TIME MODIFIED BY DST CHANGE) VER/ARN IDC BROKEN CROSS ARM BRACE XXXX
489 | South Williamson | 3411401 | DEWEY | INEZ | 2012-12-31 15:48 | 2013-01-01 00:17 | 275 | 509 | 4560611 | 101404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECLOSER OPEN //PATROLING NOW//HOUSE FIRE AT ABANDONED HOUSE AT 766-81,SERVICE HAD ALREADY BEEN REMOVED//BURNED DOWN PRIMARY AND NEUTRAL AT 766-45//THIS WAS LAST SPAN,I CUT LOOP TO MAKE SAFE//BLEW LINE FUSE ON 766-28 AND LOCKED OUT RECLOSER ON 742-54//HAVE ALL CLOSED GOING TO CLOSE IN AT 767-110// RECLOSER LOCKED BACK OUT//WIRE DOWN AT 766-62///RESTORED AT POLE 110 AT 1905//OPENED SWITCH ON 766-27 BYPASS RECLOSER ON 742-54//CREW ENROUTE TO REPAIR//RES RELEASED BY CREW 079S01 //VER/GAH IDC XXXX
490 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-11-02 08:31 | 2014-11-02 14:00 | 457 | 329 | 4692151 | 101285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING RECLOSERS AT POLE 91-6106 TO ISOLATE POLE FIRE AT 90-262, OPENED AT 0831. OPENED SOLID BLADES AT POLE 90-281 TAGGED TO BRENT TACKETT, AND CLOSED RECLOSERS AT POLE 90-262 AT 0918.RELEASED BY CREW 078H12,,CREW ON SITE,,SHOULD BE ABLE TO USE POLE EXTENSION,,WAITING ON FLAGGERS.,,ALL REPAIRS MADE, ALL POWER RESTORED VER/SEF AJB
491 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-01-20 21:21 | 2011-01-20 23:40 | 728 | 139 | 63163-1 | 101192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SERVICER FOUND BAD CUTOUT , IN PROCESS OF REPLACING . VER/PDP IDC XXXX
492 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-06-12 09:26 | 2021-06-12 19:30 | 174 | 604 | 4722711 | 101046 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Only 174 COD (B phase) currently out///PATROLING LINE, HAVE NOT FOUND FAULT//center phase primary burned down on 38830752000005.need manual tree crew, line crew, flaggers..//center phase primary burned down on p-752-5.need manual tree crew, line crew, flaggers..center phase primary burned down on p-752-5.need manual tree crew, line crew, flaggers..isolated grd tagged p-752-77 777-20 .. Released by crew 076S01
493 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2011-03-31 07:35 | 2011-03-31 11:42 | 492 | 247 | 60807-1 | 101009 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN ON POLE 264-183---- POWER RESTORED AT 11:42 ALSO SEE 60651-1 VER/KEP IDC XXXX
494 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2012-03-18 04:11 | 2012-03-18 09:50 | 612 | 339 | 4591281 | 100893 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830343C00006 TOOK CUTOUT OFF LINE === PUT RECLOSER IN AT 6:55 AM == NEED 1 MAN TO HELP CHANGE CUTOUT UP ON HILLSIDE //WALLACE MELTON TO ASSIST /== CHANGED CUTOUT == GOT LAST CUTS ON AT 0950 COD-612 ISO OCR @ 37830344000144 VER/HFP L3/HFP IDCC TON950 STEP 1 XXXX
495 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2018-08-16 23:56 | 2018-08-17 04:19 | 580 | 263 | 4962771 | 100809 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | DOL 852127 // C Ph Loop burnt open on 38830046A20155 //cod 291 // opened feeder @ 0255 adding 289 addtl cust to outage//all power restored 0419// /// VERIFIED TIMES VIA SCADA & DOL = L3/HFP
496 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2008-12-21 21:04 | 2008-12-22 02:30 | 309 | 326 | 61830-1 | 100734 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 27767407 // DEADEND INSULATOR HAS BROKEN INTO AT POLE 37820147B00347 TOOK OUT BREAKER IN STATION. CONTRACT CREW TO HELP .NO SCADA AT STATION FEEDER IS PREDICTED OUT DUE TO AMOUNT OF FLICKERING LIGHT CALLS ON THE CIRCUIT. WILL SEND SERVICER TO PATROL CIRCUIT ASAP. . WE CHANGED INSULATON AND CLOSED STATION BREAKER IN AT 02:30. VER/KEP L3/KEP IDC CHANGED TIME OFF FROM 1942, STARTED AS FLICKERING XXXX
497 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-02-02 17:25 | 2016-02-02 21:13 | 441 | 228 | 4667321 | 100548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | TOP BROKE OFF ON 3 PHASE CROSS ARM POLE 235-101 45/4 , TOP TWO FEET BROKEOFF. NEED LINE CREW AND AWP TO FLAG. THIS IS A BUCK ARM POLE WITH SINGLE PHASE TAP. TRUCKS TO POLE. RELEASED BY CREW 078S01.. CREW ON SITE OPENING REC AT AT 17:25 TO TRANSFER CONDUCTORS FROM BROKE POLE.,. ETR 22:00.. POLE CHANGED AND REC BACK IN AT 21:13.. PLEASE CLOSE TICKET CY/ ISO 38830211000216/ COD 441/ VER/BOW L3/HFP XXXHFP AJB
498 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-03-26 14:51 | 2015-03-26 16:05 | 1888 | 74 | 4231391 | 100348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1451 SCADA INDICATED CB LOCKED OUT - SERVICER ENROUTE // FAILED CUTOUT 73-48. I CHANGED CUTOUT ON POLE 73-48. IT OPENED RECLOSER ON POLE 96C-465 AND ALSO STATION BREAKER. NEEDS TO BE CHECKED OUT. RELEASED BY CREW 074S01 VER/KEP AJB
499 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2012-02-02 09:37 | 2012-02-03 00:02 | 636 | 865 | 4315221 | 100198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSMISSION STRUCTURE BURNT/PERSONNELL ON-SITE/WORKING ON TRANSFER HIGH LINE POLE BURNT OFFHIGH LINE POLE BURNT OFF /PRT ON SITE HOLD ORDER AT 12:01//POLE SET TRANSMISSION ATTACHED, DIST. MAKING TRANSFERS.//613 CC RESTORED VIA FIELD TIE AT 1148 /// CB CLOSED AT 0002 REST 23 CC. NOTE: SEE ORDER 4317141 FOR FOLLOW UP OUTAGE. VER/SDB IDC XXXX
500 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-04-17 09:28 | 2010-04-17 14:55 | 463 | 327 | 64367-1 | 100088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SWITCH POLE 1139-109 HAS XARM BURN OFF/ SERVICER ISOLATED BY LIFTING HOTTAP ON POLE 1139-58 AND CLOSED RECLOSER @ 1013//CREW ENROUTE // ALL REPAIRS MADE POWER RESTOREDPUT HOT TAPS ON POLE 1139-58 AT 14:35AND CLOSED SWITCHES ON POLE 1139-109 AT 14:38//RIGHT-HAND PHASE REC 11-A-536 OPENED UPON PREVIOUS RESTORATION STEP // STILL HAVE 79 CUST OUT // PATROLLED OUT AND CLOSED RECLOSER IN @ 1455//ALL POWER RESTORED // IDCC STP TON XXXX
501 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-12-14 18:34 | 2018-12-15 01:10 | 485 | 396 | 4566211 | 99856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | b phase recloser locked out @ 292-325,,,b phase off pin laying on arm @ 268-51, CREW REQUIRED NO TRUCKS, will have to open other 2 phases when crew arrives to make repairs,, Released by crew 078S05, a and c phase open at 00:30 for about one hour so we can safely make repairs to b phase ¦¦¦ L3/HFP
502 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-12-25 16:58 | 2021-12-25 20:33 | 464 | 215 | 4225961 | 99760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | DDC TAGS DOL#1171722 send copy to doug hall and shawn goble \\\ recloser would not close, bypassed and restored customers at 2033
503 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-05-31 15:16 | 2015-05-31 18:40 | 489 | 204 | 4488881 | 99756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICE OPENED RECLOSER 1058B347 @1513/INSULATOR BAD1058-347/FLAGGERS AND 3 MEN CREW ARCOSD//// MADE REPAIRS IN THE PROCESS OF GETTING TAPS ON. // CLOSED RECLOSER AT 18:40 AND RESTORED POWER. TIM MCCOY RELEASED BY CREW 074H10// VER/ ADH AJB
504 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-05-22 10:00 | 2014-05-22 13:10 | 525 | 190 | H4734081 | 99750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | "C" PHASE WIRE DOWN AT 201-236 /1 PHASE ONLY COD-187/WILL NEED TO OPEN AT 200-D-117 TO MAKE REPAIRS VERY MANUAL/C PHASE WIRE DOWN AT 201-236 /1 PHASE ONLY COD-187/WILL NEED TO OPEN AT 200-D-117 TO MAKE REPAIRS VERY MANUAL/ RELEASED BY CREW 077S04 OPENED ALL THREE PHASES AT ROUGHLY 1000 AT 200-117-- MADE REPAIRS AND CLOSED IN AT 200117 RESTORING ALL CUSTOMERS AT 1310 -- CAN CLOSE - THIS NEED PROPERLY MODELED TO REFLECT CUSTOMER COUNT MWL VER/KEP AJB SEE 4734081 FOR INLT OUTAGE.
505 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2013-07-12 14:12 | 2013-07-12 17:03 | 583 | 171 | 4513771 | 99693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 1412 SCADA INDICATED CB OPEN // SERVICER ENROUTE// LINE CREW IN ROUTE TO MAKE REPAIRS LRM// WILL HAVE TO ISOALTE STATION CB TO MAKE REPAIRS/// WILL UPDATE FETR IF CHANGES/HOLD ORDER ISSUED AT 1532/CREW ON SITE/FETR 1730/VEM// CB CLOSED VIA SCADA AND ALL CUSTOMERS RESTORED AT 1703. IDC XXXX
506 | Williamson | 3202201 | LOVELY | LOVELY | 2022-11-04 19:20 | 2022-11-04 20:32 | 1384 | 72 | 4099461 | 99648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | opening AB phase recl 746c-459 to safely make repairs to wire down and broke xarm 38820747A10183 // cc 1384 // need times // ....opened @ 19:20 closed @2032
507 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-06-11 08:41 | 2008-06-11 14:44 | 274 | 363 | 62462-1 | 99462 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308002 TRANSMISSION CONDUCTOR FELL INTO 3 PHASE LINE//COD 274// 1 PHASE OF TRANSMISSION LINE BROKE @ SLEVE AND FELL IN DIST LINE. VER/HFP MLR OK L3/DKG IDC XXXX
508 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-04-16 11:39 | 2011-04-16 18:08 | 332 | 389 | 58311-1 | 99140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SDB / RECLOSERS OPEN AT POLE 21-146 DUE TO FAILED INSULATOR (POLE BURNT OFF ) AT POLE 45-174 . --- SDB / 1336 / GOAB AT POLE 45-234 OPENED. --- SDB / 1400 / SW AT POLE 117-107 CLOSED, RESTORES 745 CUSTOMERS. --- SDB / 1808 / RECLOSER AT POLE 21-156 CLOSED, RESTORING FINAL 211 CUSTOMERS. SDB / 1815 / COMPLETED SWITCHING TO PUT CKT BACK TO NORMAL.SDB VER/HFP L3/HFP IDC XXXX
509 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-06-03 14:21 | 2010-06-03 16:21 | 826 | 120 | 55958-1 | 99120 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | 3309001 STATION BRAKER OUT == FUSE BLOWN ON STATION SERVICE TRANSF FOR THE 120 = 240 V ==STATION BRAKER OUT == FUSE BLOWN ON TRANSF FOR THE 120 = 240 V == STATION SERV TRANSF BAD == BREAKER WONT CLOSED BACK WITHOUT AC V == IDC XXXX
510 | Pikeville | 3408401 | KIMPER | LONGFORK | 2008-06-08 07:39 | 2008-06-08 12:18 | 355 | 279 | 60052-1 | 99045 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | KIMPER 69-12KV STATION OUT 0739 ** GREG HALL AND TERRY FIELDS DISPATCHED TO CHECK. ETR IS PROJECTED WILL UPDATED TIME WHEN MORE IS KNOWN ABOUT THE OUTAGE AT THIS TIME THE STATION TRANSFORMER IS OUT. VER/HFP CORRECTED START TIME/DEBBIE IDCC MCCDL XXXX
511 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-06-27 21:44 | 2022-06-28 00:53 | 524 | 189 | 4336871 | 99036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER// DOL 1217698 // emergency outage required to replace broke crossarm //will be from approx 2130 to 0300 // cod 524 //
512 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-10-03 16:23 | 2021-10-03 19:32 | 524 | 189 | 4312351 | 99036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3 phase rec. locked out @1125-C2-619, patrolling. Bad insulator and cutout @1125-D-67, will be making repairs. Got repairs made closed rec. back in @1932.
513 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2021-03-12 13:32 | 2021-03-12 22:18 | 314 | 526 | 4331811 | 99035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Loop burndt into on A phase @893-B-29 (175 customers), will have to open rec. @893-A-304 to make repairs, will keep track of times. Opened rec. 38820893A00304 @2121 (140 additional customers) / Cosed recl @ 2218/
514 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-09-04 16:17 | 2022-09-04 22:10 | 314 | 353 | 4835981 | 98732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECL 38831062000064 L/O//crews patrolling and preparing to sectionalize outage for partial restorationfound bad dead end bells on pole 38831039000133.made repairs and power restored @22:10.
515 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-01-26 12:57 | 2010-01-26 15:25 | 664 | 148 | 59996-1 | 98272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SOS 1501-REV 72 **EMERG. SW AND LOAD TRANSFER OF 754 CUSTOMERS FROM THE BECKHAM/HINDMAN 34KV CKT TO THE BULAND/AJAX-DWARF 12KV CKT. OUTAGE OF 668 CC ON THE BECK/HIND CKT HOLD ORDER ISSUED TO JEFF COMBS. TO REPLACE BAD CROSS-ARMS ETR 2-3 HRS OFF AT 1257. REST BY 1600. VER/PDP IDC XXXX
516 | Hazard | 3303901 | LESLIE | HYDEN | 2010-02-22 03:00 | 2010-02-22 04:40 | 982 | 100 | 59613-1 | 98200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303901//PATROLLED AND DIDNT FIND ANYTHING SHOT BREAKER AND STAYED IDCC TOF0302, FOUND 3 BAD CUTOUTS AND ARRESTERS LATER IN THE DAY XXXX
517 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-09-16 13:33 | 2008-09-16 16:50 | 498 | 197 | 64618-1 | 98106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3408103//OPENED RECLOSER IN ORDER TO REPAIR A BROKEN POLE//COD 498// VER/DBM MLR OK IDC XXXX
518 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-11-04 00:26 | 2012-11-04 02:05 | 990 | 99 | 4353591 | 98010 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE HARDWARE | CAUSE UNKNOWN, TRANSMISSION LINE OUTAGE (TIME MODIFIED BY DST CHANGE) VER/ARN IDC BROKEN CROSS ARM BRACE XXXX
519 | Hazard | 3309302 | VICCO | JEFF | 2015-03-30 08:43 | 2015-03-30 14:39 | 318 | 356 | 4241971 | 97860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE OUT ONLY/ BAD CUTOUT ON POLE 37830347A00091 === CUTOUT BURNED END OF CROSS ARM OFF === NEED LINE CREW == NEED CROSS ARM CUTOUT AND 25 KVA 7200 KV TRANSFBAD CUTOUT ON POLE 37830347A00091 === CUTOUT BURNED END OF CROSS ARM OFF === NEED LINE CREW == NEED CROSS ARM CUTOUT AND 25 KVA 7200 KV TRANSF RELEASED BY CREW 077S03 RELEASED BY CREW 077H04/ 1300 RECLOSER CAME BACK OUT BAD STEPDOWN/ 1358 STEPDOWN AND 1400 RECLOSER ALL POWER RESTORED AJB
520 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2022-01-07 08:29 | 2022-01-07 15:36 | 252 | 427 | 4318891 | 97844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recl was in on arrival-found line down on ground and burning--is opening recl to make safe Released by crew 074H07 /// ?????????? LR- The total recloser is 251 Customers and it appears that each Phase came in at different times
521 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-07-26 03:20 | 2009-07-26 13:59 | 153 | 639 | 64110-1 | 97767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNED UP CROSSARMS OPENED "C" PHASE RECLOSER AT 1140 TO MAKE REPAIRS VER/KEP L3/KEP IDC CHANGED COUNT FROM 61 XXXX
522 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-11-07 14:59 | 2019-11-07 17:09 | 752 | 130 | 4007201 | 97760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Tie wire broke and phase is almost laying on the arm on pole 193-207//This is tracking and firing up will need crew to tie phases back in//Opened recloser on pole 193-D-390B @ 16:41/// Repairs made closed recloser back in @17:09 L3/HFP
523 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-04-06 22:34 | 2009-04-07 01:18 | 596 | 164 | 50049-1 | 97744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3301402 - BAD ARRESTER POLE 248C- 305 == CUT IN CLEAR == RESTORED POWER == //VER/GAH IDC XXXX
524 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-07-25 12:41 | 2012-07-25 14:38 | 834 | 117 | 4826111 | 97578 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLED LINE AND CLOSED OCR AT POLE 771-A4-412 @ 1438 RESTORING ALL CUSOTMERS// VER/TOM L3/TOM IDCC CDC82 XXXX
525 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2019-08-28 03:55 | 2019-08-28 06:51 | 580 | 176 | 4954201 | 97520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON POLE 38821137A00331//COD 580//CLOSED REC IN @ 0613 UPTO GOAB 38821137D10753//recl out on 1137A331 due to bad cutout on 38821137D00247 restored power at 06:51 Released by crew 079H03 L3/HFP
526 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-12-15 10:38 | 2010-12-15 17:10 | 260 | 392 | 50662-1 | 97360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 38120874 // ON SITE CKING TROUBLE//BAD INSULATOR ON POLE 37830221000018 //RESTORE POWER TO 3 PHASE POLE 37830221000158 AT 16:35//RESTORE POWER ON POLE 37830220000002 AT 1700//RESTORE POWER AT POLE 37830196B00190 17:10 COD-260 ISO RECL 37830221000158 VER/HFP L3/HFP IDC CHANGED START TIME FROM 1144 TO MATCH PREVIOUS OUTAGE, LOOKS LIKE CUSTOMERS DID NOT COME BACK ON XXXX
527 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-08-21 13:27 | 2009-08-21 17:52 | 367 | 265 | 59391-1 | 97255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 600 AMP SWITCH NEEDS TO REPLACED "A"PHASE IS OUT COD-245 RELEASED BY CREW 077S01 OPENED OTHER 2 RECLOSURE AT1648 COD-569 MADE REPAIRS AND RESTORED POWER TO ALL CUSTOMERS AT 1752 CREW 077H01 VER/KEP L3/KEP IDC PH C NOT A IDC XXXX
528 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2014-10-14 19:59 | 2014-10-15 12:04 | 312 | 965 | 4627561 | 97096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT ON POLE 966-B-612. I WILL REPLACE CUTOUT BUT FOUND CROSSARM BRACES BROKE AND THE ARM TILTED UP. WILL DO PARTIAL RESTORATION TILL ARM BRACES ARE REPLACED ON POLE 38820966A40618. I OPENED SWITCHES ON POLE 38820966A40732 AND TAGGED TO JOEY REED. RELEASED BY CREW 079S02 VER/KEP AJB
529 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-01 02:51 | 2016-02-01 04:38 | 952 | 107 | 4662231 | 97056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | DA SCHEME//POLE 141-389 LOOKS LIKE BAD LA SEND TO YOUNGMAN//BAD LA AND BLOWN FUSE ON POTENTIAL XFMR FOR DA RECLOSER//RESTORED ALL CUSTOMERS FROM PRINCESS-MEADE BY CLOSING 116-*45 @ 0430 (601CC) AND THEN CLOSING 117-6028 @ 0438 (351CC)//DA SCHEME//POLE 141-389 LOOKS LIKE BAD LA SEND TO YOUNGMAN//BAD LA AND BLOWN FUSE ON POTENTIAL XFMR FOR DA RECLOSER//RESTORED ALL CUSTOMERS FROM PRINCESS-MEADE BY CLOSING 116- 45 @ 0430 (601CC) AND THEN CLOSING 117-6028 @ 0438 (351CC)// CREW ON SITE OPENING X AJB
530 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-12-27 08:00 | 2016-12-27 10:04 | 782 | 124 | 4240941 | 96968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN ON POLE #147-488 WILL PATROL/// BAD DEAD-END INSULATOR ON POLE#37820146000039 HAVE CREW ENROUTE// CAN USE TRUCK/// REPAIRS MADE CLOSED RECLOSER IN @ 10:04 AND RESTORED SERVICE VER/CRB L3/HFP XXXHFP AJB
531 | South Williamson | 3411401 | DEWEY | INEZ | 2011-02-02 09:59 | 2011-02-02 13:27 | 465 | 208 | 53296-1 | 96720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SINGLE PHASE OUT 235 CC.RECLOSER ON POLE 311 SHOWING VOLTAGE ON B AND C PHASE,, HAVE CUSTOMERS WITH PART POWER BEFORE THIS RECLOSER, PATROLING NOW///FOUND LOOP BURNT OPEN ON POLE 744-38// @ 1300 OPENED SWS AT 744-34 ALL PHS NOW OPEN. DUP ORDER CREATED VER/PDP IDCC DCMT CNT611, CDC90 XXXX
532 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-11-16 10:08 | 2022-11-16 16:53 | 238 | 405 | 4148181 | 96390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required with flaggers/45/2 /292-294 open tagged to griffith Released by crew 078S03 broke pole at 38830222A00171 Repairs made, Closed on 222-B-294 at 16:53. Ticket complete.
533 | Hazard | 3303902 | LESLIE | WOOTON | 2018-01-02 08:34 | 2018-01-02 12:30 | 408 | 236 | 4696331 | 96288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | center phase off of insulator on pole 365-182, need flaggers to setup in road to make repairs. recloser 265-323 closed at 12:30, came back out. closed at 12:35/ ISO 37830365D20323/ COD 408
534 | Hazard | 3420001 | SOFT SHELL | VEST | 2020-06-05 02:22 | 2020-06-05 16:41 | 130 | 859 | 4960101 | 96282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | patrolling line, crossarms are upside down on pole 157-220, extremly difficult location Released by crew 077S02//IT Force Closed
535 | Pikeville | 3402002 | KEYSER | STONECOAL | 2015-06-18 17:54 | 2015-06-18 23:34 | 283 | 340 | 4601311 | 96220 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | KYDDC OPENED ALL KEYSER CKTS VIA SCADA @ 1842 DUE TO PROBLEM WITHIN THE STATION// TREE AT TIM SHORT IS ON THE PHONE COMPANY PER BILL JOHNSON//STATION DEPT MADE REPAIRS TO LTC AND THIS FEEDER RETURNED TO SERVICE @ 2334//COD 768// VER/DBM // TIMES PER SCADA & LOG - SEE DUP H4601311 FOR INITIAL C PHASE OUTAGE = L3/HFP HFPC DUP AJB
536 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-12-23 04:46 | 2017-12-23 11:38 | 298 | 412 | 4665361 | 96099 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL Case 792655///cutout failed on pole 169-4 caught pole on fire and broke pole above xfm. will need 3 man line crew to make repairs..opened sec. on pole 169-232 @ 4:46 Released by crew 074S01
537 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-04-16 07:49 | 2021-04-16 12:50 | 693 | 301 | 4455531 | 96063 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Ph 2 load at the station has dropped off completely // calls begin after REC 38830381D10259 //B PHASE RECLOSER 38830381D10259 IS OPEN//COD 289//will have to open other 2 phases @ 1151 CLOSED @ 1250Ph 2 load at the station has dropped off completely // calls begin after REC 38830381D10259 //B PHASE RECLOSER 38830381D10259 IS OPEN//COD 289// crew on site pin ins. burnt on pole 381-283 FETR 13:30 LRM all pwr restored 12:50 please close ticket LRM Released by crew 078H06 LR- There is 228 on Phase B and 465 on Phase A & C- Total 693 CC
538 | Hazard | 3301101 | CHAVIES | CHAVIES | 2021-02-27 09:51 | 2021-03-22 07:26 | 185 | 32975 | 4261241 | 95993 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER REQ/ DOL 1094613/ pole down at pole down at pole 37830194000101/ Pole 194-101 is burnt off right at guy/ insulator failed causing the conductor to lay on the crossarm and burn the pole/ opened SW 37830194000088/ Closed DA SW 37830194000115 @ 1227 de-energized switching/ Closed DA SW 37830194C40167 @ 1232/ opened SW 37830169D00193 @ 1309/ Closed N.O. DA SW 21330/ army corps engineer customer that is still out is fine with being left out email sent to glen combs/ need 40 foot 2-8 arms 1
539 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-02-01 01:50 | 2013-02-01 12:55 | 144 | 665 | 4778921 | 95760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WILL WORK IN THE AM DUE TO HAZARDOUS ROAD CONDITIONS. WE HAD TO OPEN RECLOSERS AT POLE 402-418 TO MAKE REPAIRS AT POLE 378-272 . OPEN AT 11:43 CLOSED AT 12:55 ///VER/CRB L/3 CRB IDCC CHANGED OFF TIME FROM 1143 FOR PH C ONLY CREATED H ORDER FOR OPENING PH A AND B XXXX
540 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-05-20 03:12 | 2020-05-20 11:33 | 191 | 501 | 4864201 | 95691 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva on 69-5680 No truck///pole is rotten having to replace pole///making repairs///opened sws on 38830069C45547 at 0945 and closed at 1133 (191 COD)
541 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-05-05 17:52 | 2011-05-05 19:26 | 1017 | 94 | 4012691 | 95598 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | SCADA INDICATES STATION OUTAGE ON SOFTSHELL TANSFORMER #1 @ 1752 // SERVICER AND STATION PERSONEL ENROUTE //RESTORED AT 1926 VER/TOM L3/TOM MAF IDCC TOF1755 XXXX
542 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2013-02-26 19:17 | 2013-02-27 02:09 | 275 | 412 | 4856601 | 95216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B PHASE RECLOSER BACK OUT 275 CUST ORIG ORDER 4855661 OFF @ 1917 //B PHASE RECLOSER BACK OUT 275 CUST FOUND BAD PRI DEAD END INS, ON POLE 925-187, LIFTED HOT TAP ON POLE 925-6, GROUNDED AND TAGGED LINE FOR V MULLINS IS ON SCENE AT THE PRESENT TIME RELEASED BY CREW 078S06/CREW ON SITE/FETR 0245/VEM/REPAIRS MADE AND POWER RESTORED 0209/PLEASE CLOSE TICKET/THANKS/VEM //VER/GAH IDC XXXX
543 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2018-05-17 18:36 | 2018-05-17 21:28 | 553 | 172 | 4367051 | 95116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD pole top insulater @ 38830186000007 burnt b phase down,,reclosers back in @ 21:28 complete Released by crew 078S05 B phase only 125 open until 1951 // opened a and c phase to safely repair b phase conductor on 38830186000007 // restored all 553 @ 2128/// trouble tickets showing all out from the start
544 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2020-07-27 08:14 | 2020-07-27 14:09 | 360 | 355 | 4236221 | 95040 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | Failed Station Transformer crews enroute/crews in process of redistributing load **** I DIDNT COMPLETE RESTORATION OF THIS OUTAGE ONLY CLOSED THE OUTAGE AFTER SHIFT CHANGE , NOT SURE ABOUT CAUSE CODES OR TIMES ON/OFF. ALAN JORDAN ****
545 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2018-05-03 20:42 | 2018-05-04 04:10 | 212 | 448 | 4304411 | 94976 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | FAILED PHASE 2 34KV BUS ARRESTOR /// VERIFIED TIMES PER SCADA & DOL = L3/HFP
546 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2022-07-07 06:14 | 2022-07-07 15:18 | 201 | 544 | 4416001 | 94952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | A&B phases open on Recl 38831027D00087///pole 1027-423 top burned offpole 1027-423 top burned off/// POWER RESTORED @ 15:18 Released by crew 074H18
547 | Hazard | 3309302 | VICCO | JEFF | 2016-12-24 05:39 | 2016-12-24 09:39 | 624 | 240 | 4233511 | 94669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830347A00306 === PUT MAIN LINE AT 8:10 === REPLACED CUTOUT TAP FUSE IN AT 9:39 ALL ON RELEASED BY CREW 077S03//COD 624 VER/HFP L3/HFP AJB
548 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2008-12-27 17:21 | 2008-12-27 21:28 | 667 | 247 | 64417-1 | 94653 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3403002//CONDUCTOR FAILED/ CREW ENROUTE// SPACER BROKE ALLOWING CONDUCTOR TO GET TOGETHER & BURN DOWN - 2128 - REPAIRS MADE & ALL CUSTOMERS RESTORED. //VER/GAH L3/JMS IDC XXXX
549 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-11-04 00:26 | 2012-11-04 02:05 | 956 | 99 | 4353751 | 94644 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE HARDWARE | CAUSE UNKNOWN, TRANSMISSION LINE OUTA (TIME MODIFIED BY DST CHANGE) VER/ARN IDC BROKEN CROSS ARM BRACE XXXX
550 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2015-05-10 10:35 | 2015-05-11 02:41 | 174 | 966 | 4407921 | 94593 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | SCADA INDICATED 69-12KV TR 1 @ SOUTH PIKEVILLE DE-ENERGIZED. THIS HAS STATION INTERRUPTED AND APPROX 1786 PIKEVILLE AREA CUSTOMERS// STATION SERVICER AND D-LINE SERVICER CALLED IN//TOM WILL UPDATE AS INFORMATION BECOMES AVAILABLE//TOM - ***UPDATE @ 1135 DETERMINED STATION TRANSFOMER LTC HAS FAILED - LOOKING AT LOAD TRANSFER OPPORTUNITIES AND WILL NEED A MOBILE TRANSFOMER INSTALLED - ALL NECESSARY PARTIES NOTIFIED//TOM VER/KEP AJB
551 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-08-23 21:02 | 2020-08-24 01:50 | 328 | 288 | 4362271 | 94464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | recl out on 1138-C235 due to middle phase at 1138-C-120 coming off of pin and contacting xarm,trk app with big bucket.crew required. Released by crew 079S03/// repairs made // on @ 01:50
552 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-06-22 12:19 | 2010-06-23 00:01 | 142 | 702 | 54468-1 | 94436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED. WE WILL NEED TO CHANGE POLOE AND 2 20 CROSSARMS. TRUCK ACCESSIBLE. CUTOUT IS BAD. CAUGHT POLE 120-417 ON FIRE AND BURNED IT INTO. THIS HAS A BANK OF STEPDOWNS ON IT. I AM GOING TO OPEN SWITCHES ON POLE120-463 TO ISOLATE TROUBLE. WE OPENED SWITCHES ON POLE 120-463 AT 13:12. RELEASED BY CREW 074S01 IDC CHANGED TIME OFF FROM 1136 XXXX
553 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-04-05 12:28 | 2011-04-05 14:06 | 963 | 98 | 65956-1 | 94374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED BREAKER TO SAFELY ISOLATE POLE ON FIRE AT 356-379 VER/KEP IDCC TOF1224 XXXX
554 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2018-06-01 05:43 | 2018-06-01 12:35 | 451 | 412 | 4537191 | 94319 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Case 831027//// crew on site All wire up pwr restored @ 12:35 please close ticket LRM Released by crew 078H06//// trouble tickets show A phase open at 0740
555 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-12-01 04:05 | 2019-12-01 20:40 | 345 | 980 | 4108851 | 94284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER REQ/ DOL 974429/ recloser open on pole 335-305 will patrol/ recloser open on pole 335-305 will patrol/// Pole 336-1 is burnt off @ the xfm// will need to replace pole 336-1// Rick Ray has material list// This is no truck but i think they can get a yard dog to this pole/ recloser open on pole335-305 will patrol/// Pole 336-1 is burnt off @ the xfm// will need to replace pole 336-1// Rick Ray has material list// This is no truck but i think they can get a yard dog to this pole Released by cr
556 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-05-04 02:03 | 2008-05-04 05:29 | 1076 | 206 | 56872-1 | 94216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3402001//CROSSARM BROKEN ON POLE 1127-501 CAUSING PHASE TO PHASE CONTACT ISOLATEING AT POLE 1127-500/CLOSED BREAKER AT 0314 RESTORED 944 CUST/CREW ENROUTE TO MAKE REPAIRS/REPAIRS COMPLETE AND POWER RESTORED AT 0529 IDC XXXX DEB OK
557 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-07-26 18:06 | 2022-07-26 18:44 | 2476 | 38 | 4585831 | 94088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER//DOL 1225454 // 34.5 insulator burnt up on pole 194-2///Will have to open station breaker to make repairs///Paul Layne is going to come and make repairs // opened feeder @ 1806 // cod 2476 //
558 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-07-23 15:34 | 2010-07-23 19:27 | 403 | 233 | 56060-1 | 93899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SINGLE PHASE CONDITION ON THE US 60 WEST 12KV CKT. 387 CC . CREWS PATROLLING CKT. CREWS FOUND CENTER PHASE OPEN AT SET OF JUMPERS AT POLE 162-6084, TROUBLE IS IN THE CLEAR AT THIS TIME AND PHASE A-C CAN REMAIN ENERGIZED UNTIL CREW IS PREPARED TO MAKE REPAIRS , WHEN REPAIRS BEGIN PHASE A-C WILL BE OPENED UNTIL REPAIRS R MADE. ** ALL WORK NTA .. HOOKS AND HANDS. OUTAGE ON 56108 IDCC MCCNI, CCDOT XXXX
559 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-07-05 08:48 | 2016-07-05 09:53 | 1444 | 65 | 4535941 | 93860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DKM/1842/FAILED CUT OUT AT POLE 37820073A00028 /2113/OFFICE REPORTS THIS TRANSFORMER JUST FEEDS AN OUTDOOR LIGHT AND THEY WILL REPLACE THE CUTOUT AT A LATER DATE/// VER/DKM // VER TIME PER SCADA L3/HFP HFPC FP38730073A00028 TOF 0850 AJB PER DOL AND SCADA.
560 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-08-22 19:50 | 2014-08-22 23:02 | 488 | 192 | 4409461 | 93696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3 PHASES OPEN AT 0950 CLOSED AT 2302 ON 8-22-14 AJBC TOF19:11 TON10:57 8/23. 6 CUST OFF ON XFR 38830809C30429. PH A OFF ON 38830809C30089 W/47. PH B OFF INLT ON 38830785D40121. @09:50(19:50) OP OTHER TWO PH PUTTING 488 MORE OUT.
561 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-01-25 09:50 | 2008-01-25 11:25 | 1552 | 95 | 59700-1 | 93640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3103101//STATION MAN KEN RIGSBY IN STATION//BREAKER LOCKED OUT//1028 SERVICER OPENED REC 247-12 AND CLOSED STA BREAKER BACK IN AT 1038 PICKING UP 1076 LEAVING 476COD//RESTORED AT 1125//VER/CRB IDC XXXX
562 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-08-09 04:58 | 2009-08-09 08:45 | 411 | 227 | 65243-1 | 93297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401802//HENDRIX BURNT IN TWO ON POLE 654-600 CALLED MILLER DISPATCHING CREW/// C PHASE RECLOSURE OUT ON POLE 654-529 WILL NEED TO OPEN ALL THREE RECLOSURES WHEN CREW ARRIVES//HENDRIX BURNT IN TWO ON POLE 654-600 CALLED MILLER DISPATCHING CREW/// C PHASE RECLOSURE OUT ON POLE 654-529 OPENED A AND B PHASE ON 654-529 AT 0649// CLOSED ALL THREE RECLOSURES IN AT 0845 //VER/GAH IDC XXXX
563 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-12-08 11:31 | 2013-12-08 16:30 | 312 | 299 | 4115171 | 93288 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | OPENED CB @ 1430, FUSE BLOWN AT STATION EARLIER, CREW IS MAKING REPAIRS NOW.ARRESTER ON LOW SIDE OF STATION TRANS. IS BAD. SUBSTATION CREW IS ON SITE. CLOSED CB @ 1630. SUBSTATION CREW IS ON SITE. WE CHANGED ARRESTER AND GOT STATION BREAKER BACK ON AT 16:30 BASED ON ADX LOOKS LIKE A PHASE OUT AT APROX 1131 - 181 CUST SEE H4115171 FOR B & C PHSE CUST WHEN CB OPENED VER/HFP L3/HFP IDCC TOF0958, PH B NOT C CHANGED COUNTE FROM 181 XXXX
564 | Hazard | 3310502 | HADDIX | CANOE | 2015-02-05 03:34 | 2015-02-05 06:35 | 920 | 181 | 4991581 | 93252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310502/FAILED CUTOUT POLE#27-30 /// PLEASE CLOSE ORDER .... THANKS...HFP//IT FORCE CLOSED /// SEE DUP H4991581 TO RETURN CKT TO NORMAL DROP & PICK 240 CUST DACHAHAD // TIMES PER LOG & ADX VER/KEP VER/HFP L3/HFP AJB
565 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-03-04 22:15 | 2008-03-05 01:41 | 452 | 206 | 53491-1 | 93112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3401103 /// A PHASE SWITCH ON POLE 876-222 BROKEN (452 CUSTOMERS) VER/HFP DEBBIE OK IDC XXXX
566 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-06-28 19:53 | 2011-06-28 21:25 | 1011 | 92 | 4433191 | 93012 | TRANSMISSION STATION | EQUIPMENT FAILURE | CAPACITOR | 69KV BUS AT JACKSON LOCKED OUT // 69KV CAP BANK SWR AA WAS CALLED UPON TO OPERATE & FAILED TO OPEN WHICH TRIPPED 69KV BUS, CAP BANK ISOLATED & ALL RESTORED TO SERVICE AT 2125 //VER/GAH IDC XXXX
567 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-06-28 19:53 | 2011-06-28 21:25 | 1011 | 92 | 4433201 | 93012 | TRANSMISSION STATION | EQUIPMENT FAILURE | CAPACITOR | 69KV BUS AT JACKSON LOCKED OUT // 69KV CAP BANK SWR AA WAS CALLED UPON TO OPERATE & FAILED TO OPEN WHICH TRIPPED 69KV BUS, CAP BANK ISOLATED & ALL RESTORED TO SERVICE AT 2125 //VER/GAH IDC XXXX
568 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-03-19 18:24 | 2008-03-20 04:35 | 211 | 611 | 58844-1 | 92931 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403201// 3 PHASE BUCKARM POLE NEARLY BURNT THROUGH -OPENED RECLOSER ON POLE 115-55 TO DE-ENERGIZE LINE// GETTING CREW AND POLE - WILL PROVIDE FETR ONCE CREW ARRIVES// IDC XXXX
569 | Hazard | 3309301 | VICCO | REDFOX | 2015-04-10 10:33 | 2015-04-10 16:41 | 258 | 368 | 4303491 | 92896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | RECL OUT OPENED GOAB @ 326-A-5 TO GIVE VISUAL OPEN POINT - BROKEN CROSSARM. 256 CC REST FROM ALT SOURCE AT 1633. 2 CC REST AT 1641. SWITCHING TRANSFERRED TO PO ORDER 4305981. AJB
570 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2010-06-25 20:45 | 2010-06-25 22:43 | 784 | 118 | 57612-1 | 92512 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | SCHEDULED 2 HR OUTAGE FOR EMERGENCY WORK IN STATION /@2232 SWITCHING STARTED TO RETURN NORMAL / IDCC MCCST, CCSCO XXXX
571 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-01-19 22:20 | 2011-01-20 06:23 | 244 | 483 | 62871-1 | 92386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING LINE, FOUND NOTHING SO FAR, TRIED RECLOSER, CAME BACK OUT. FOUND BAD INSULATOR ON POLE # 154-152. TIM SMITH AND RONNIE RICE WITH BIG BUCKET ON THEIR WAY FOUND BAD INSUATORS PAST 154-149, WILL CUT LOOPS AT THAT POLE AND CLOSE RECLOSERS. AT 0340 SDB / 0436 / LOOPS CUT AT POLE 154/149, RECLOSER CLOSED AT POLE 177D/64. 6 CUST REMAIN OUT --- SDB / 0623 / CUSTOMERS RESTORED. ALSO SEE OUTAGES 62903-1 & 62900-1 IDC XXXX
572 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-07 08:14 | 2008-03-07 13:20 | 301 | 306 | 54470-1 | 92106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3308401// COD-344 A PHASE // 1 PHASE OUT ON POLE 204-264, PATROLLING LINE NOW. BROKE CROSSARM ON 204-40. CALLING FOR HELP//ISO 37830204000135////@ 1055, OPENED REMAINING 2 PHASES (836 ADDITIONAL CUSTOMERS) IN ORDER TO COMPLETE REPAIRS//ALL POWER RESTORED 1320// VER/DBM IDC B PH NOT A CHANGED COUNT FROM 344 XXXX
573 | South Williamson | 3411401 | DEWEY | INEZ | 2012-01-25 22:51 | 2012-01-26 06:26 | 203 | 455 | 4293531 | 91961 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SAME AS ORDER 4293441- RECL AT POLE 742-54 EITHER NEVER PICKED UP OR WAS OPEN ENTIRE OUTAGE, CREW WILL PATROL AND ATTEMPT TO CLOSE. CREW SECTIONALIZED , RECL AT POLE 790-113 NOW OPEN, CREW FOUND BAD CUTOUT ON POLE 766-62, VER/ARN IDCC TOF0444 XXXX
574 | Hazard | 3308001 | JACKSON | S.JACKSON | 2019-12-13 17:16 | 2019-12-13 20:12 | 929 | 176 | 4151621 | 91931 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout 38831083C40205 failed B phase (39cc originally) on pole 38831083C40205 catching pole on fire/ SOUTH JACKSON 12KV - CB L at jackson locked out @ 1827 interrupting 929cc/ opened switches 38831083D10098/ closed SOUTH JACKSON 12KV - CB L at jackson @ 1852 restoring 633cc/broke cutout on pole38831083C40205broke cutout on pole38831083C40205 Released by crew 077S05/
575 | Hazard | 3303901 | LESLIE | HYDEN | 2018-01-02 05:30 | 2018-01-02 08:54 | 905 | 165 | 4694921 | 91804 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | See DOL Case 794154///69-34kV TR 2 is out--failed phase 1 regulator /// VERIFIED TIMES PER SCADA & POA & DOL = HFP
576 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-12-27 23:33 | 2009-12-28 12:00 | 140 | 747 | 59584-1 | 91392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WR#33209031 / WIRE ON GROUND BETWEEN POLES 600/52 AND 600/62 STILL HOT; OPENED RECLOSER ON 38830576B00140 C PHASE AND TAGGED POLE; 4 SOLID SLEEVE FAILED AT POLE 600/52; OLD HOLD CARD AT BASE OF POLE WARNS DO NOT CLIMB ; 4-WHEEL DRIVE BUCKET TRUCK ACCESSABLE; NEED HAND COIL OF 4 SOLID AND SLEEVES; RELEASE TO LINE CREW RELEASED BY CREW 078S12 IDC CHECK CUSTOMER COUNT AND HOW LONG
577 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2008-03-27 00:54 | 2008-03-27 02:57 | 743 | 123 | 61034-1 | 91389 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001204// ISOLATING TROUBLE AT PRISON AND WILL RESTORE CKT NORMAL. VER/LDA IDC XXXX
578 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-10 14:05 | 2016-01-10 20:36 | 316 | 391 | H4598731 | 91253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38831027D00064/ CUTOUT FAILED AND BURNT POLE OFF. AJB FOR SEC OUTAGE OF A AND B PH 316 CUST.
579 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-05-12 11:12 | 2008-05-12 19:05 | 279 | 473 | 62671-1 | 91230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308503//POLE#245-45 IS ON FIRE//PLACED OPEN POINT AT POLE 245-41//7200 VOLT CUTOUT FAILED ON XFMR//OPENED RECLOSERS AT POLE 246-75 AT 18:56 AND CLSOED BACK AT 19:05// OPEN RECLOSER TO MAKE-UP LOOPS ON OTHER RECLOSER OUTAGE 63229-1 // VER/TOM IDCC TOF0958, CNT447, PN272 XXXX
580 | Hazard | 3301101 | CHAVIES | CHAVIES | 2022-10-09 02:11 | 2022-10-09 15:40 | 114 | 809 | 4007721 | 91128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | One span of #2 acsr down at pole #241-93. Solid blades open at #218-142 at 11:20.
581 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-02-23 20:49 | 2019-02-24 09:22 | 121 | 753 | 4851151 | 91113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | // A phase post top insulator failed and burndt down a span of 1/0 primary @25-D1-400, had to load bust 3 sectionalizers @25-A-63 @2136 to isolate trouble, tagged sectionalizers to DDC, no grounds, cleared up conductor, this will take a line crew with big bucket, 1/0 acsr, post top insulator 7200, and flaggers. Released by crew 074S05
582 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-02-25 02:44 | 2021-02-25 09:45 | 216 | 421 | 4247471 | 90936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | a bad cutout on pole 351-434, we isolated it and restored power to everyone but the xfmr on pole 351-434. we closed the recloser back in at 7:45 Released by crew 077S12 REPLACED CUTOUT POWER RESTORED LAST 2 CUSTOMER AT 09:45 Released by crew 075H03
583 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-11-02 16:43 | 2009-11-02 20:59 | 355 | 256 | 56302-1 | 90880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WORK 32499861//2 PHASES ON SPACER CABLE DOWN-NEED LINE CREW--FLAGMAN2 PHASES ON SPACER CABLE DOWN-NEED LINE CREW--SEND TO LLOYD RELEASED BY CREW 078S07 IDC LOOKS LIKE PH A AND B INITIALLY AND WE OPENED C AROUND 1925 IDC XXXX
584 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-05-26 04:11 | 2020-05-26 14:33 | 382 | 622 | 4906521 | 90878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | C ph only // cod 245 //c phase recloser is locked out on pole 1056-C-323, will patrol. no hazards found./ opened c phase recloser on pole 1032-132 going to try recloser on pole 1056-C-323 and see if it will stay. Opened recl up @ 1007-167 @ 13:33 to change out bad stepdown xfer on pole 38831007D40164 CLOSED @ 14:33 . bACK TO NORMAL
585 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2021-07-16 13:28 | 2021-07-16 15:38 | 698 | 130 | 4920341 | 90740 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 1132376/ Checked pole 37830187C00029 and everything looked good// Spoke with neighbor and he didnt hear anything/// Nothing found on transmission line/ transmission closed breaker at 1538 restoring Burton Station/ Transmission found dead end bell failed
586 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-08-21 00:43 | 2016-08-21 03:31 | 540 | 168 | 4819971 | 90720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD BROKE CUTOUT ON CAP BANK THAT BROKE ON OFF AND TOOK LINE OUT VER/KEP /// IS THERE A CAP BANK ON POLE 37830050000012? NONE ON MAP IN POR = HFP AJB
587 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-12-31 15:42 | 2022-12-31 17:00 | 1161 | 78 | 4382361 | 90558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken transformer fuse at 37820146000010/Will be making repairs..Broke Trans cutout at 146-10,Will be making repairs..Restored Recloser at 17:00.
588 | Hazard | 3303902 | LESLIE | WOOTON | 2014-11-16 17:44 | 2014-11-16 21:20 | 419 | 216 | 4732671 | 90504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICER AKEMONS TRUCK BROKE DOWN //CALLED OUT JAMES GILLEY//1906 SERVICER VERIFIED REC IS OPENED// // BAD INSULATOR ON 365-D-194//ARCOSED FLAGGERS//365-D-194//ARCOSED FLAGGERS// VER/HFP L3/HFP AJB
589 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-12-11 02:08 | 2018-12-11 11:33 | 177 | 565 | 4550031 | 90491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1011-132,BAD SOLID-BLADE TYPE CUTOUT IS BAD,DOOR WONT STAY CLOSED.WILL NEED TO OPEN GOAB@1011-528 TO REPLCE IT.ALSO OPEND RECLR@RAY BR.NEED COUPLE MEN ,BUCKET ,SOLID BLADE,TO HOLD OUTAGE TO A MINIMUM&KEEP FRM HAVING TO RUN BACK&FORTH // OPENED GOAB @ 0948 10 CUSTREPAIRS MADE AND SERVICE RESTORED..D LEWIS 12-11-18.OPENED GOAB @09:48 AND CLOSED @ 10:15..CLOSED RECLOSER 1011-100 @RAY BR @11:34..
590 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-09 06:15 | 2016-02-09 12:50 | 949 | 395 | 4684821 | 90325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED 34KV DA RECL 141-C-423 OPERATED TO LOCKOUT// POLE FIRE 141-429 141-74 40T LINE FUSE SEND TO BOB RELEASED BY CREW 078S08//SEE DOL CASE 636625// RELEASED BY CREW 078H07//COD 949 VER/HFP L3/HFP AJB
591 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2020-11-15 11:49 | 2020-11-15 18:04 | 283 | 375 | 4680301 | 90060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Center phase primary burndt down between poles 1065-B-84 and 85, isolated trouble with 3 -600 amp switches @1065-D2-287 and tagged to Miles R. to isolate trouble @1333.///repairs made // restored @ 18:04
592 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-02-01 04:30 | 2008-02-01 15:00 | 369 | 630 | 63044-1 | 90001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411802- POLE FIRE SERVICER ISOLATED AND RESTORED RECLOSERS. A PHASE ONLY OUT AT POLE 26-2 AT SERV OPENED ALL RECL AT 0500 -OPENED SWS AT POLE 2-54 CLOSED ALL RECL AT POLE 26-2 AT 0530- AT 0600 OPENED SWS AT POLE 2-118 & CLOSED AT 2-54 AT 0626 OPENED & TAGGED SWS AT POLE 1130-267 . AT CLOSED N.O. RECL AT POLE 1081-16 REST .... CUST FROM THE JOHNS CR META 34KV CKT. IDCC CNT 1055 XXXX
593 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-08-23 02:04 | 2017-08-23 11:42 | 186 | 578 | 4290731 | 89633 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FOUND DEADEND INSULATOR BURNT INTO ON POLE 555-90 OPENED GOAB ON POLE 555-117 TAGGED TO JIM MULLINS PER DDC TRUCK ACESS NEED FLAGGERS 7 DEADEND INSULATORS BIG BUCKET , POLE IS 6 POLES PAST GOAB SWITCH //COD 186 VER/KEP SJG
594 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-07-08 14:01 | 2008-07-08 16:52 | 524 | 171 | 64500-1 | 89604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3413402//CENTER PHASE HOT TAP BURNT OFF OF RECLOSER POLE 64-190//COD 242//OPENED OTHER 2 PHASES @ __:__ TO MAKE REPAIRS WHICH INTERUPTED 282 MORE CUST//3413402//CENTER PHASE HOT TAP BURNT OFF OF RECLOSER POLE 64-190//COD 242//OPENED OTHER 2 PHASES @ 15:15 TO MAKE REPAIRS WHICH INTERUPTED 282 MORE CUST//3413402//CENTER PHASE HOT TAP BURNT OFF OF RECLOSER POLE 64-190//COD 242//OPENED OTHER 2 PHASES @ 15:15 TO MAKE REPAIRS WHICH INTERUPTED 282 MORE CUST// REPAIRS COMPLETE / GXJ IDC XXXX
595 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-03-16 00:18 | 2012-03-16 02:24 | 711 | 126 | 4586811 | 89586 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | OUTAGE TO INSTALL MOBILE TRANSFORMER VER/ARN IDC XXXX
596 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-09-21 18:44 | 2022-09-21 21:57 | 464 | 193 | 4906521 | 89552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Reclosure back online from abnormal has fault // closed recl at 2057 // Rick Ray reported the recloser opened back up at 2045 and would like to bypass recloser, bypassed and restored @ 21:57
597 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-01-30 12:16 | 2016-01-30 17:38 | 282 | 322 | 4660181 | 89324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECL OUT,WILL PTRL//NOTHING EVIDENT,WILLTRY RECLR.RECLR WOULD NOT CLOSE.NEED CREW TO HELP//FAILED INSULATER ON POLE 1086-C-12//CLOSED IN RECLOSER 1086-C-458 @ 1722//CLOSED RECLOSER 1086-D-119 @ 1730//CLOSED RECLOSER 1086-D1-608 @ 1738REPLACED XARM&INSULATORS. RELEASED BY CREW 074S06 VER/CRB AJB
598 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-07-17 22:27 | 2009-07-18 02:35 | 360 | 248 | 58200-1 | 89280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CROSSARM ON FIRE .. SERVICER OPENED L.S. 1072-C4-5521 TO ISOLATE DUTY CREW WORKING ON TROUBLE IN THE LOUISA AREA AND WILL BE DISPATCHED TO THIS JOB ASAP.HAVE 8FT CROSSARM BURNTED OFF, ON POLE 1072-5660, NEED ARM, AND 3 CUTOUTS AND ARRESTORS, ALSO FOUND ANOTHER BAD 8FT CROSSARM ON POLE 1072-5564, WELL NEED TO BRING TWO ARMS, SOLIDS BLADES OPEN ON POLE 1072-5521 TAGGED, ALSO HAVE LINE GROUNDED ON POLE 1072-5568, CAN USE TRUCK ON THIS, BUT NEED CREW TO COMP THIS WORK VER/PDP IDCC CDC90 XXXX
599 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-05-23 02:27 | 2015-05-23 05:47 | 446 | 200 | 4458141 | 89200 | TRANSMISSION LINE | EQUIPMENT FAILURE | CAPACITOR | SDB / 0220 / 138KV BUS 1 AND BUS 2 AT BEAVER CREEK RELAYED OUT DUE TO ____. THIS INTERRUPTED 2, 048 CC. STATION AND LINE CREWS EN ROUTE. LIGON 34KV CKT - 1602 CC AND PRICE 34KV CKT - 446 CC. VER/SEF L3/HFP HFPC CDC82 AJB
600 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-11-13 04:26 | 2016-11-13 09:10 | 314 | 284 | 4096931 | 89176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECLOSURE IS OUT ON 38831125D00638 WILL BE PATROLLING LINE FOR TROUBLE. HAVE #4 PRIMARY DOWN BETWEEN 38831149000125 & 38831149000024 WILL NEED BARREL CREW #4 COPPER & MATERIAL HANDLER.OCR IS ISOLATED & LINE GROUNDED @ POLE 638 AJB
601 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-07-23 01:55 | 2009-07-23 03:35 | 890 | 100 | 63703-1 | 89000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSURE WAS OUT . NEED TO SEND PERRY FARMER A NOTE TO HAVE CONTROL CHECKED OUT. THANKS G.R. // SENT TO PERRY VER/TOM L3/TOM PLC IDC XXXX
602 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-07-19 22:06 | 2011-07-20 04:15 | 241 | 369 | 4565401 | 88929 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING.TRIED REC., CAME OUT BACK OUT. SUSPECT BAD INSULATORS ON POLE 470-19, CHANGED ONE FOUND 2 MORE BAD. CLOSED REC. AT 04:15 IDC XXXX
603 | South Williamson | 3411401 | DEWEY | INEZ | 2011-05-08 17:27 | 2011-05-08 23:00 | 267 | 333 | 4020111 | 88911 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39870107 //POLE 767-27 BURNT OFF//THIS POLE HAS A CAPACITOR BANK// CAN USE A POLE TOPPER//TRUCK APPROACH/RECLOSER LOCKED OUT ON POLE 767-110//HAVE REPAIRS MEDE//CAPACITOR LEFT OFF LINE//RESTORED AT 23:00//COMPLETE//EM// VER/TOM L3/TOM IDC XXXX
604 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-01-03 00:31 | 2020-01-03 04:13 | 818 | 222 | 4206021 | 88874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase source side disconnect open on pole 37830174C14426//cod 300 (+518)//opened other phases in order to replace failed disconnects @ 0330//closed all back in @ 0413//B phase source side disconnect open on pole 37830174C14426 // L3/HFP
605 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-04-29 12:23 | 2020-04-29 14:37 | 662 | 134 | 4767681 | 88708 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | DOL1014258///CB was on NRO and went out ands found bad relay on CB after it tripped - transferred customers to Pounding Mill ckt-vulcan breaker malfunctioned,isolated vulcan breaker and fed vulcan circuit customers from Freeburn breaker. Released by crew 079S03
606 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2019-12-10 02:36 | 2019-12-10 14:41 | 407 | 725 | 4140231 | 88706 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER REQ // DOL 976596// CB predicted out @ 0236 // cod 407 //Confirmed CB is open @ 0415 // breaker zone impossible to patrol without special equipment//will attempt load xfers and patrol in the daylight // 1 customer remains out until crews can patrol CB Zone no FETR Release077H14.found bad insulator pole 199-319, ..made repairs and closed shamrock breaker A @ 14:41.
607 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-01-30 01:23 | 2008-01-30 09:00 | 193 | 457 | 61167-1 | 88201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | POLE 200-117 HAD MIDDLE PHASE OUT, ALSO ON POLE 177-287 MIDDLE PHASE SWITCH BAD CHANGED TO SOLID BLADE ,ALL SHOULD BE ON COD-158 VER/ARN IDCC PH A IS IN CENTER CNT158 XXXX
608 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-04-16 11:39 | 2011-04-16 14:00 | 624 | 141 | 58311-1 | 87984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SDB / RECLOSERS OPEN AT POLE 21-146 DUE TO FAILED INSULATOR (POLE BURNT OFF ) AT POLE 45-174 . --- SDB / 1336 / GOAB AT POLE 45-234 OPENED. --- SDB / 1400 / SW AT POLE 117-107 CLOSED, RESTORES 745 CUSTOMERS. --- SDB / 1808 / RECLOSER AT POLE 21-156 CLOSED, RESTORING FINAL 211 CUSTOMERS. SDB / 1815 / COMPLETED SWITCHING TO PUT CKT BACK TO NORMAL.SDB / RECLOSERS OPEN AT POLE 21-146 DUE TO FAILED INSULATOR (POLE BURNT OFF ) AT POLE 45-174 . --- SDB / 1336 / GOAB AT POLE 45-234 OPENED. --- VER/HFP IDC XXXX
609 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-01-23 18:07 | 2022-01-23 20:43 | 561 | 156 | 4398831 | 87516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 254C/25 ocr out wire off insulator 254B/164
610 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-04-15 00:32 | 2013-04-15 05:05 | 320 | 273 | 4009011 | 87360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICER PATROLLING TIE WIRE BROKE.MIDDLE PHASE OFF PIN INSULATOR POLE 53-24.HAS BEEN FLASHING AGAINST POLE.LOCATED JUST A FEW POLES PAST WHERE WIRE WAS DOWN DUE TO CUT TREE A FEW DAYS AGO.NEED CREW, CLIMBER, INSULATOR & TIE WIRE..//TIE WIRE BROKE.MIDDLE PHASE OFF PIN INSULATOR POLE 53-24.HAS BEEN FLASHING AGAINST SIDE OF POLE.LOCATED JUST A FEW POLES PAST WHERE WIRE WAS DOWN DUE TO CUT TREE A FEW DAYS AGO.NEED CREW, CLIMBER, INSULATOR & TIE WIRE..//.REPAIRS MADE..CLOSED RECLOSE. VER;PDP IDC XXXX
611 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-05-05 10:31 | 2013-05-05 15:34 | 288 | 303 | 4072951 | 87264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B PHASE CONDUCTOR BURNT DOWN ON POLE 38830527009005//ISO//COD 288 // VER/DBM IDC XXXX
612 | Hazard | 3309301 | VICCO | REDFOX | 2015-02-22 04:02 | 2015-02-22 09:40 | 258 | 338 | 4069511 | 87204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | POLE # 326-44 HAS BROKEN CROSS ARM BRACES, MANUEL POLE, WILL NEED CREW. POWER RESTORED VER/SEF AJB
613 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-04-14 16:40 | 2015-04-14 17:51 | 1227 | 71 | 4318411 | 87117 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POWER RESTORED AT 1751 BONNYMAN-HAZARD #2 69 LINE BURNT DOWN ACROSS OUR DISTRIBUTION CAUSING THIS OUTAGE VER/SEF L3/HFPXXX AJB
614 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-02-27 18:58 | 2021-02-27 23:27 | 584 | 269 | 4263901 | 87066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 37830069000017, all manual will need line crew for repairs/// opened switches at 37830069000100 and tagged to ddc Closed N.O DA OCRs at 21-14 restoring 472 CC Line crew enroute to make repiars will update FETR when crews are on sitebroke cutout on pole 37830069000017, all manual will need line crew for repairs/// opened switches at 37830069000100 and tagged to ddc// opened disc on pole 69-278 and tagged to ddc Released by crew 074S09
615 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-10-11 10:17 | 2017-10-11 14:00 | 1157 | 223 | 4446211 | 86931 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LLOYD RAYBURN ISSUED HOLD ORDER @ 1056//// OPENED CB @ 1017 VIA SCADA // SERVICER TRYING TO CLEAR POLE FIRE NEED IT OPENED ASAP // RELATED TO 4446211 CB BACK IN @ 1052 910 CUST // RECL BACK IN @ 1400 247 CUST VER/HFP L3/HFP ACB
616 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-02-19 05:00 | 2014-02-19 08:41 | 393 | 221 | 4399561 | 86853 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER PATROLLING LINE.FOUND TREE CLOSE TO THREE BUT NOT SURE ON POLE 79-11. VER/SEF IDC LATER FOUND BAD CUTOUT CHANGED FROM WEATHER UNKNOWN XXXX
617 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2021-09-22 04:52 | 2021-09-22 14:31 | 321 | 573 | 4267091 | 86661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOL/// 1149115/// Station Breaker open at Barrenshe Freeburn(ASSESSING CONDITION)..We have a broke crossarm at pole 1089-A-11,Paul Layne is on is way to help make repairs.. Released by crew 074S01
618 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-01-05 11:09 | 2013-01-05 12:59 | 1245 | 110 | 4570781 | 86612 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | INTERNAL PROBLEMS WITH THE STATION TRANSFORMER - TRANSFERRING LOAD TO ALT SOURCES & CALLING STATION CREW TO INSTALL MOBILE TR AT CANNONSBURG STATION //VER/GAH IDC XXXX
619 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-02-27 07:30 | 2009-02-27 09:54 | 601 | 144 | 51982-1 | 86544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3408303// COD-601 FAULT POLE 37820008A00048 BAD XFMR CUTOUT POLE 8-48 SECT. CLOSED AT 9:54 D SAMMONS L3/HFP IDC XXXX
620 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-04-03 14:55 | 2008-04-03 15:49 | 1598 | 54 | 63446-1 | 86292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001002/BROKEN CUTOUT ON POLE 38830279000192, REPLACED CUTOUT /// ALL CUST RESTORED @ 1549// VER/HFP IDCC CNT1 XXXX
621 | Hazard | 3309302 | VICCO | JEFF | 2019-10-31 22:48 | 2019-11-01 12:00 | 116 | 792 | 4267821 | 86262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ocr B phase out on p#299/254 , patroling found wire down p#275 / 74 -----75 #4 copper counted 9 splices , replacing span 270 ft. opened other 2 ocrs at 0809 repairs made and power restored at 1200
622 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-11-27 03:43 | 2019-11-27 07:13 | 627 | 210 | 4071491 | 85922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 37820002000010/ closed recl 37820026000002 @ 0555 (538cc)/ clsoed sw 38821130000287 @ 0630 (88cc)/ xfmr 37820002000010 still openB PHASE TO GRND FAULT INDICATED@RECLR,WILL PTRL/////////BROKEN CUTOUT 2-10 IN FROZEN CR,WILL REPLACE IT//////////B PHASE TO GRND FAULT INDICATED@RECLR,WILL PTRL/////////BROKEN CUTOUT 2-10 IN FROZEN CR,WILL REPLACE IT//////////REPLACED CUTOUT&RESTORED ALL Released by crew 074S06
623 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2018-09-24 11:18 | 2018-09-24 18:31 | 306 | 433 | 4150751 | 85836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B & C Phasesare off insulator 3783-0177-C0-0010/ Resotred by switch 37830201C10042 @ 1831/ 303cc/// 3 Cust transferred from outage 4149911 off at 1118
624 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2017-09-15 09:30 | 2017-09-15 15:07 | 360 | 337 | 4364161 | 85680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | TOP SET OF CROSSARMS BROKENCROSS ARM BROKE ON POLE 55/28 SHOUSECROSS ARM BROKE ON POLE 55/28 SHOUSE RELEASED BY CREW 077H04 37830055000216 37830055000028 VER/AWD SJGC STEP1 CNT17, STEP2 CNT20
625 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-04-10 08:34 | 2015-04-10 12:11 | 458 | 217 | 4302141 | 85553 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 0834 OPENED CB DUE TO POLE FIRE & WIRE DOWN // 600 AMP SWITCH FAILED AND WAS BURNING ON POLE 37830248A00406, LINE CREW AND FLAGGERS ENROUTE. OPENED SWITCH ON 37830247C00061, BREAKER RESTORED AT 09:32 RELEASED BY CREW 077S04 AJB
626 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2020-03-03 18:03 | 2020-03-03 22:47 | 301 | 284 | 4449091 | 85484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 997582//connection failed burning A phase conductor down at 1065-B-263.opened switches on 1065-D2-287 to make repairs//after completing repairs when attempting to restore, the CB at the station is unresponsive// have called station servicer to investigate// will attempt to pick up this ckt from another feed //connection failed burning A phase conductor down at 1065-B-263.opened switches on 1065-D2-287 to make repairs Released by crew 079S03
627 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-06-11 06:55 | 2020-06-11 10:15 | 427 | 200 | 90110811 | 85400 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | fault @ 1099-90. open intelleropter @ 1099-6965 & tagged to ddc. open 3 600a disc @ 1099-68 & ddc tag. hold order to mphelps. Released by crew 078S07
628 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-07-14 19:28 | 2013-07-14 20:28 | 1422 | 60 | H4520971B | 85320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 205-117 HAS BURNT OFF AT LOWER SET OF ARMS, CALLING FOR HELP /// COLLETT, MARSHALL --- SDB / 1004 / LOOPS CUT AT POLE 206-B-47 & CB CLOSED REST 174 CC. -- SDB / 1034 / LOOPS CUT AT POLE 181-D-28, TIE SW AT POLE 181-D-401 CLOSED, REST 1422 CC. ** UPDATE AT 1926 - CREWS OUTAGED CUST TO MAKE UP LOOPS PRIOR TO TOTAL RESTORE OF CUSTOMERS AND RESTORE CKTS NORMAL.POLE 205-117 HAS BURNT OFF AT LOWER SET OF ARMS, CALLING FOR HELP. ALL POWER RESTORED EXCEPT SECONDARY ON POLE 117 AT 20:28 **** IDC XXXX
629 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-01-10 16:59 | 2017-01-10 18:22 | 1027 | 83 | 4284141 | 85241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER OPEN ON POLE 230C-341 , SHOWING BPHASE TO GROUND FAULT . FOUND BAD RECLOSER ON POLE 231B-199 . CLEARED RECLOSER . CLOSED RECLOSER ON POLE 230C-341 @ 18:22 .//MADE AED AND NOTES ON MAP VER/CRB // NOTE THIS CKT CROSSES OMS BOUNDS & DUPLICATED FOR THAT REASON - SCADA AGREES WITH TIMES - L3/HFP XXXHFP AJB
630 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-08-14 10:38 | 2018-08-14 17:25 | 1738 | 98 | 4952401 | 85162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | failed equipment pole 424-209/ opened cb at 1038 to safely isolate /DOL 851328/ // SEE ALSO 4951081 = VERIFIED TIMES PER DOL & SCADA = L3/HFP
631 | Hazard | 3311103 | STINNETT | WENDOVER | 2009-04-03 10:47 | 2009-04-03 13:21 | 552 | 154 | 64578-1 | 85008 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | 3311103// SCADA INDICATES STATION OUTAGE HERE @ 10:47 // BUS REG BURNED UP ON PH 1 AJB PER ALARM LOG AND DISP LOG.
632 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2010-06-26 15:05 | 2010-06-26 17:38 | 567 | 153 | 57839-1 | 84959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CHECKING NOW RELEASED BY CREW 076H06 RISER BURNT OFF AT POLE 1121-D-188. FEEDER BREAKER OPEN & ALSO RECL AT POLE 18-D4-564 OPEN //VER/GAH IDCC FEC NONE XXXX
633 | Whitesburg | 3314401 | MAYKING | ERMINE | 2011-10-02 07:46 | 2011-10-02 10:20 | 635 | 154 | 4939511 | 84726 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | FEEDER OUT CREW PATROLLING CKT CREW FOUND FUSE OUT ON POLE 426-B-153 . CC ON THIS FUSE WILL BE OUT FROM 0746 65 FUSE N.O. CC 15 ONLY NO TR OUT FH " STATIC CB RELAY FAILURE - " ERMINE CB FAILED TO RECLOSE AFTER FAULT. RELAY REPAIRS COMPLETED NEXT DAY , SEE DOL AND SOS VER/PDP IDCC MCCDL, FEC57 XXXX
634 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-11-16 16:51 | 2016-11-16 22:00 | 274 | 309 | 4106381 | 84666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BEHIND THE POND CREEK FIRE DEPT BUCK ARM POLE 38821086C00019 IS ROTTEN AND THE RIDGE PIN HAS PULLED OUT AND IS AGAINST THE B PHASE. THE ARMS ARE ALSO ROTTEN BUT YOU MIGHT BE ABLE TO PUT THE MIDDLE PHASE ON THE ARM, OR LOWER EVERYTHING AND REPLACE THE ARMS. NO TRUCK ACCESS, WILL NEED FLAGGERS TO ISO THE RECLOSER. FOREMAN NEEDS TO LOOK AT THIS POLE TO MAKE SURE ITS SAFE TO WORK TONIGHT. RELEASED BY CREW 079S02.. MAKING REPAIRS. 38821086C00458 VER/AWD L3/HFP XXXHFP AJB
635 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2011-08-24 02:55 | 2011-08-24 16:38 | 130 | 823 | 4749621 | 84646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3301701 - "B" PH RECL OUT (131 CUST) - TOP OF POLE 420-137 ROTTED OFF, OPENED OTHER 2 PH RECLS (6 MORE CUSTS) CUT DEADENDS IN POLE 419-40 TO ISOLATE, CLOSED RECLS AT 0624 RECLOSER OPEN ON POLE 419-366, , CUT DEADENDS IN POLE 419-40 TO ISOLATE.. OPENED RECLOSERS AT 05:35 CLOSED AT 06:24 ENERGIZING UP TO 419-403301701 - RECLOSER OPEN ON POLE 419-366, TOP OF POLE 420-137 ROTTED OFF , CUT DEADENDS IN POLE 419-40 TO ISOLATE.. OPENED RECLOSERS AT 05:35 CLO IDC XXXX
636 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-10-27 10:41 | 2010-10-27 15:35 | 330 | 294 | 65631-1 | 84644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 728-9 TOP OF POLE BURNED OFF HANGING DOWN.WE ARE OPENING UP REC. ON POLE679-363 SO ROGER M. CAN OPEN SWITCH AT POLE 728-17..//ISO 38830679B10363 // COD 330 // VER/DBM IDC XXXX
637 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2021-06-22 03:52 | 2021-06-22 10:10 | 325 | 378 | 4788321 | 84338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1126343 // Recloser open at 1151-D-444,(ASSESSING CONDITION)On pole 1152-328 a cutout Failed and burned crossarm into..Crew Required also will need Flaggers,Opened switches at pole 1152-97 and restored recloser on 1151-D-444 at 06:18..Will need 8 foot crossarm and 3 7200 cutouts.
638 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-06-28 21:11 | 2008-06-29 14:00 | 314 | 1009 | 58671-1 | 84266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED TRANSFORMER CUTOUT ON POLE 1098-633 ... WILL NEED 2 MEN TO REPLACE CUTOUT / GXJ //GREG CALLED PIKEVILLE DISPATCH. WILL GO BACK TO THIS AND CLOSE THE RECLOSER...OCR CLOSED AT 01:20 06-29-08, TP 1098-633 STILL OUT / GXJ RELEASED BY CREW 074S03 COD-8 AJBC CDC92 CCWL FEC57
639 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-04-19 23:54 | 2019-04-20 03:18 | 413 | 204 | 4138951 | 84252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recloser on 141-252 is open. Bad cutout & arrester on 38830142B00292. Also B phase off the pin. Waiting on line crew for assistance. Fetr 0345///////apr at 0318 close ticket/ ISO 38830141D00252/ cOD 413 ¦¦ VERIFIED BY VOICE RECORDER OPTIONS FOR SECTIONALIZING WERE OFFERED AND NOT ACCEPTED GOAB @ POLE 38830142B02004 WOULD HAVE ISOLATED TROUBLE L3/HFP
640 | Pikeville | 3413402 | GARRETT | LACKEY | 2022-11-22 08:42 | 2022-11-22 11:55 | 436 | 193 | 4171791 | 84148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C phase fault @ recloser 64-190.//Wire down @ 37830064000034.//Crew required.//Restored @ 11:55
641 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2018-03-05 16:26 | 2018-03-05 19:45 | 421 | 199 | 4968851 | 83779 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | DOL 808163 // SCADA Indicated 3403202 Open @ 1626 //// bad arrester found in sub station // restored 1945
642 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-01-20 08:40 | 2008-01-20 15:40 | 270 | 420 | 157891-1HA | 83765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NO. 4 COPPER WIRE DOWN ONE SPAN 1 PHASE ONLY/C PHASE COD-114/0845 RESTORED 20 CUST UP TO POLE 49 OPENED SWITCH AT POLE 49 366 CUST ALL 3 PHASES SO CREW COULD MAKE REPAIRS SAFELY ON PLE 71-197/MADE REPAIRS TRIED TO ENERGIZE SWITCH AT 1115 CUTOUT BURNT UP ON C PHASE AND OPENED RECLOSER POLE 72-383 ON B&C PHASE COD-311 REPAIRED CUTOUT TRIED RECLOSER AT 1210 IT CAME OUT OPENED RCLOSER POLE 70-151 AND 47-6 TO SECTIONALIZE,B PHASE RECLOSER POLE 383 WILL NOT STAY IN BYPASSED RECLOSER RESTORED AT 1 IDC XXXX
643 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-02-20 16:27 | 2019-02-20 21:30 | 307 | 303 | 4820001 | 83628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | B PHASE RECLOSER OPEN ON POLE 37830048C10800//COD 101//FROM BEGINNING OF OUTAGE//B phase recloser is open on 48-C1-800.patrolling line.patrolled line saw no hazards.tried Bphase recl and it came back out. will be patrolling line/ found trans riser laying against pole at 25-A-199 .isolated trans to energize line/ recl back on at 2059 xfmr 37830025A00199 on at 2130//// Trouble tickets show all phases out.
644 | Hazard | 3303902 | LESLIE | WOOTON | 2019-12-17 06:58 | 2019-12-17 12:42 | 278 | 344 | 4161531 | 83602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | patrolling ¦¦ tried ocr's and they came back out//BY PASSED RECLOSER AND ENERGIZED UP TO GOAB 37830462000214 @ 1151//LF OPEN @ POLE 37830462000019 CLOSED GOAB @ 1206 BAD ARRESTER @ POLE 37830462000233//DOL# 978633//AED # AED# 100006412//note on map
645 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-04-25 19:01 | 2020-04-25 23:26 | 927 | 265 | 4749681 | 83458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1901/CB open affecting 927 CC servicer enroute --- gaj/1930primary down between 37830426D00012 & 37830426D00325 due to phase contact FETR for 799 CC will be gaj/2326/ jumpers installed restoring all customers
646 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-02-25 03:15 | 2022-02-25 06:00 | 701 | 165 | 4542581 | 82701 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | Recloser Open at 190-D3-406,Will be looking it over..Closed Recloser back in at 04:38..Recloser open at 190-C3-459 have a broke cutout at 190-B-113,Will be making repairs..Restored @ 06:00.
647 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-02-21 15:35 | 2015-02-21 19:23 | 388 | 228 | 4065051 | 82632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 37830167B00189 POLE FIRE BAD DEAD END INSULATOR. INSULATOR SHORTED OUT AND CAUGHT POLE ON FIRE. IT TOOK OUT RECLOSER ON POLE 144B-380. I AM CALLING FOR HELP. I OPENED GOAB ON POLE 167-403 AND CLOSED RECLOSER ON 144B-380 IN AT 16:41. I CLOSED GOAB IN ON POLE 167-403 AT 19:23. THIS SHOULD HAVE PICKED UP EVERYONE UP. RELEASED BY CREW 074S01 VER/KEP AJB
648 | Hazard | 3303901 | LESLIE | HYDEN | 2016-02-24 14:04 | 2016-02-24 16:55 | 483 | 171 | 4759751 | 82593 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR B PHASE POLE 388-A-101 VER/CRB L3/HFP HFPC FP37830388A10101 AJB
649 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-02-11 20:21 | 2012-02-11 22:55 | 595 | 154 | 4337671 | 82510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | SERVICER PATROLLINGRECLOSER ON POLE 1100-325 CLOSED IN AT 22:25. CLOSED IN RECLOSER ON POLE 1076-206 AT 22:55. RECLOSER ON POLE 1100-325 JUST OPENED UP NO FAULTS INDICATED. I HAVE RECLOSER BYPASSED AND RECLOSER CONTROL IS IN OPEN. RELEASED BY CREW 074S11 VER/ARN IDCC TON STEP 1 XXXX
650 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2021-11-02 05:45 | 2021-11-02 10:07 | 315 | 262 | 4048051 | 81807 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLD ORDER REQ/ DOL 1159738/SCADA INDICATED 12KV DA SW 1147-C3-5028 OPENED/ 8ft crossarm burnt in two @ pole 39831123D47534, Has 3 7200 cutouts on arm. Pole not on fire @ this time. Crew required, Trucks to pole. No flaggers/ HOLD ORDER REQ/ crew on site FETR 10:45 LRM Released by crew 078H06
651 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2022-01-24 10:17 | 2022-01-24 15:21 | 267 | 304 | 4400141 | 81168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B phase Recl open (267 COD) found wire down pole 9-D-232 to 9-36 made repairs and got rec on pole 1137A-331 back in at 15:21
652 | Hazard | 3303901 | LESLIE | HYDEN | 2022-08-08 04:59 | 2022-08-08 18:21 | 101 | 802 | 4704711 | 81002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DDC TAGS DOL Case # 1228683//One span of primary down on 37830243000056. Need line crew and manual ROW crew to make repairs. #2acsr. Isolated recloser on 37830267000177and tagged to DDC Released by crew 077S06
653 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-02-06 15:42 | 2008-02-06 17:45 | 657 | 123 | 51588-1 | 80811 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BURNT JUMPER ON POL.E 501-295 ABOUT FOUR SPANS OUTSIDE THE BUSSYVILLE SUB.,,, CONTRACTOR ON SITE,,, JUMPER HAS BEEN REPAIRED AND BACK ON AT 17:45 VER/KEP DEBBIE/CHECKED WITH LOCAL OFFICE/B PHASE BURNT OPEN AT POLE 388305010310....SEE OUTAGE 51588-1A FOR OPENING BRK TAKING OUT A AND C PHASES ...FAULT AND DEV POLE SAME FOR THIS OUTAGE DUE TO LOOP BURNT OPEN...SUB 42 WV CUST IDC XXXX
654 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-08-09 20:35 | 2012-08-10 04:38 | 167 | 483 | 4921661 | 80661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | HAD TO OPEN STATION CB TO SAFELY OPEN SWS TO ISOLATE OPEN LOOP CONDITION// THIS OUTAGED 1149 CUSTOMERS// 698 WILL BE RESTORED WHEN BREAKER CLOSED/ REMAINING WILL BE OUTAGED FOR DURATION OF REPAIRS - OPEN CB AT 0343 CLOSED 0349 IDC THIS IS THE OUTAGE FOR THE LOOP OPEN XXXX
655 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2022-12-03 10:19 | 2022-12-03 15:05 | 411 | 286 | 4223671 | 80652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1256142 // failed cutout on 37830234000102 cause CB to operate but CB had bad closing spring charge motor and could not reclose // cod 411
656 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2010-11-16 20:31 | 2010-11-16 23:50 | 405 | 199 | 56775-1 | 80595 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | RECLOSER ON 182-20 IS OPEN. ..CROSSARM BROKEN ON 182-24....ISOLATED RECLOSER, GOING AFTER ARM AND MATERIAL NOW..PLEASE REVISE CUSTOMER COUNT....ALL POWER RESTORED @ 23:50 HRS RELEASED BY CREW 077H01 VER/HFP L3/HFP IDC LOOKS LIKE FIRST CUSTOMER MAY HAVE CALLED FOR OPERATIONS CHANGED TIME OFF FROM 2023 XXXX
657 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-02-23 10:20 | 2022-02-23 17:05 | 199 | 405 | 4535481 | 80595 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED 3 PHASE RECLOSURE ON POLE 1056-299 @ 10:20/// POLE 38831080000024 BURNED IN TWO CAN BE FRAMED DOWN//// NEED MAN ROW CREW AND FLAGGERS//// DHE CREWS COMING TO MAKE REPAIRS Released by crew 074S06//closed 1705//NO OUTAGE TILL OCR OPENED
658 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2017-03-05 13:14 | 2017-03-05 17:54 | 287 | 280 | 4523461 | 80360 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | C PHASE DEAD-END INSULATOR ON THE STEEL AT THE STATION HAS FALLEN ONTO NEUTRAL STATION CREW TO MAKE REPAIRS///FAILED STRAIN INSULATOR /// TIMES PER DOL & BUS OBJ = L3/HFP XXXHFP AJB
659 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-08-11 13:54 | 2014-08-11 18:03 | 595 | 249 | 4354301 | 80159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 37830343C00197A TROUBLE POLE ==== OPEN GOABE SWITCH ON POLE 37830343D00269 = CLOSED RECLOSER IN AT 14:52 ===DEAD END INSULATER BAD ON POLE 343C-197 === NEED LINE CREW AND FLAGERS === RELEASED BY CREW 077S03/// VER/BOW AJB
660 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2014-07-10 01:41 | 2014-07-10 08:55 | 451 | 434 | 4223851 | 80152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | STATION BREAKER BACK IN AT 04:38. AT 04:55 GOT THE SECTIONALIZER BACK IN ON POLE 235-168 UP TO OPEN SWITCHES ON POLE 235-171// TAGGED TO KYDDCSTATION BREAKER BACK IN AT 04:38. AT 04:55 GOT THE SECTIONALIZER BACK IN ON POLE 235-168 UP TO OPEN SWITCHES ON POLE 235-171. THIS IS ALL DUE TO POLE259-127 BEING BURNT OFFSTATION BREAKER BACK IN AT 04:38. AT 04:55 GOT THE SECTIONALIZER BACK IN ON POLE 235-168 UP TO OPEN SWITCHES ON POLE 235-171. THIS IS ALL DUE TO POLE259-127 BEING BURNT OFF. OPENED GOAB VER/ARN AJB
661 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-11-30 12:59 | 2009-11-30 19:03 | 281 | 364 | 51649-1 | 79736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40/5 POLE BURNT OFF CREW REQUIRED INLINE 3 PHASE WITH SINGLE PHASE TAP AND 15 KVA WITH SERVICE/ISOLATED ON 219-60 3 SOLID BLADES/219-135 BACK ON AT 1414 HRS RELEASED BY CREW 078S03 // WORK REQUEST 32862327 //CREW ON SITE/FETR2000/VEM/NEW FETR1930/VEM/SOLID BLADES 219-60 BACK IN AT 1839/VEM 4 CUST STILL OUT/FETR1945/VEM/LAST 4 CUST BACK ON AT1903/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 IDCC DUP STP CNT341 XXXX
662 | South Williamson | 3411401 | DEWEY | INEZ | 2020-10-29 23:11 | 2020-10-30 00:23 | 1190 | 72 | 4603451 | 79730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Failed PT ar 38830744D00275 (feeding OCRs at 38830744D20578)Released by crew 079S01 /// **** Note: CC will be not be accurate if you check POR CC since outage 4603111 already on Ckt before this outage started **** 2310 - OCRs at 38830744D20578 open (1096 CC) 2310 - OCRs at 38830768A00225 open (affecting additional 396 CC) 2311 - SWS at 37830169D00305 closed (restores 301 CC from Lovely-Lovely) 0013 - OCRs at 38830768A00225 closed (restores 395 CC from normal Dewey-Inez feed) 0015 - OCRs at 38830744D20527 closed (restores 250 CC from Lovely-Lovely) 0023 - OCRs at 38830744C00311 closed (restores remaining 545 CC from Lovely-Lovely)
663 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-11-10 22:25 | 2018-11-11 01:29 | 1206 | 184 | 4388001 | 79444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A phase only cod-368//Two hole pad burnt off of Goab on pole 170-147// will need foreman and A lineman/// Need piece of 4/0 alum//19.9 insulator and pin // TIMES PER VOICE RECORDER OPENED RECL @ 0115 CLOSED @ 0129 L3/HFP
664 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2012-02-24 23:37 | 2012-02-25 01:32 | 683 | 115 | 4501791 | 78545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 12KV SURGE ARRESTOR FAILED AT POLE 24-494 - SAME CUT IN CLEAR - STA BREAKER CLOSED AT 0132 //VER/GAH AJB PER DISP LOG.
665 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-02-07 19:44 | 2019-02-08 00:30 | 274 | 286 | 4765801 | 78364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 219-60 b phase cutout broke no trucks chg all 3 while theregoing to have to open recloser on 219-135 too fix/send to b tackett Released by crew 078S03,open reclosers @ 2329,repairs made reclosers closed @ 0030 please close ticket thanks.bt
666 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-11-08 13:17 | 2008-11-08 16:10 | 492 | 173 | 63217-1 | 78312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW WILL WORK THIS ORDER NEXT . C/L TR IN HAZARD AT THIS TIME. POLE BURNED OFF BAD LINE CUTOUT POLE 153-66 // LOAD BUSTED SECTIONALIZERS ON POLE 177-287 @ 1317 (INTERRUPTING 494 CUSTOMERS) TO DE-ENERGIZE AND OPEN 3-600 AMP SWICHES @ POLE 153-84// OPENED SWITCHES @ 1326 AND CLOSED SWITCHES @ 1610 // CLOSED SECTIONALIZERS ON POLE 177-287 @ 1328 RESTORING 43 CUSTOMER// LEAVING 451 CUSTOMERS OUT OF SERVICE FOR DURATION OF JOB//// IDCC CNT452, CDC86, PN67 XXXX
667 | Hazard | 3302703 | HAZARD | HAZARD | 2015-10-13 11:15 | 2015-10-13 17:05 | 680 | 350 | 4344691 | 77854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE TOP ROTTED OFF AT POLE 296-C1-210//COD 680//SEE OUTAGE LOG FOR DETAILS//TOP OF POLE 37830296C10210 ROTTED AND MESSENGER FOR HENDRIX HAS FALLEN ON PHASE, REPAIRS IN PROGRESS.TOP OF POLE 37830296C10210 ROTTED AND MESSENGER FOR HENDRIX HAS FALLEN ON PHASE, REPAIRS IN PROGRESS. MIDDLE PHASE BURNT DOWN AT POLE 37830296A30748, CAN RESTORE UP TO POLE 37830296A30741 WHEN FLAGGERS ARRIVE. AJBC PFL296-A3-741 TOF1538 CNT517 2ND REST. PER DISP LOG AND SCADA. SEE 4346171 & 4345671.
668 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2009-09-26 10:29 | 2009-09-26 12:30 | 641 | 121 | 63672-1 | 77561 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TRANSMISSION FEED TO STATION OUTAGED DUE TO TROUBLE / VER/KEP L3/KEP IDC XXXX
669 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2018-12-02 15:06 | 2018-12-02 20:57 | 441 | 323 | 4501561 | 77474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 879433//Pole is burned 3/4 into. Might be able to make temporary repair.Need to send to Bill Johnson have job on pole made to change out Released by crew 074H04//cod 377
670 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-08-17 08:18 | 2014-08-17 12:45 | 916 | 267 | 4375371 | 77310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON 38831125A00157 IS BAD// LIFTING HOT TAP AT CUTOUT TO ISOLATE// ISO 38831125C20625//// COD 916// OPENED HOT TAP THAT FEEDS POLE 1125-167 ON POLE 1125-A-157 CLOSED IN @ 38831125C20625 @ 09:42. ALL ON BUT 1125-A-167. WILL NEED 1 A , 1 D & FOREMAN .3 FIBERGLASS T BRACKETS ,3 19.9 CUTOUTS & ARRESTORS. NOT TRUCK ACCESABLE.// ALL POWER RESTORED AT 12:45 VER/HFP L3/HFP AJB
671 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2019-01-13 01:30 | 2019-01-13 03:32 | 632 | 122 | 4662751 | 77104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 888745 // cod 632 //Replaced 2 bad cutouts on 454-7620, apr at 0332 close ticket// L3/HFP
672 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-10-11 21:53 | 2011-10-12 07:12 | 140 | 559 | 4966711 | 77092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE RECLOSER OPEN ON POLE 37830225A00081, PATROLLING LINE. OPENED B PHASE SWITCH ON POLE 37830224C00195, RESTORED POWER TO THERE AT 02:20 (RESTORED 10 CUSTOMERS)--- BROKEN CUTOUT ON POLE 37830176000025--- ALL POWER RESTORED AT 07:12 ///VER/CRB IDCC CNT151 DOUBLE DIPPED COUNT. LOOKS LIKE PH A NOT B CHANGED COUNT FROM WHAT WOULD HAVE BEEN 77. PH A IS CENTER PHASE XXXX
673 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-12-14 07:29 | 2011-12-14 09:03 | 819 | 94 | 4175851 | 76986 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | PH 3 34KV REGULATOR FAILED IN STATION, SAME ISOLATED & STATION RESTORED AT 0903 //VER/GAH NOTE TO DALE: NEED TO 820 CUSTS BETWEEN PIKEVILLE, HAZARD & WHITESBURG IDC XXXX
674 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2013-11-17 16:34 | 2013-11-17 20:53 | 297 | 259 | 4046301 | 76923 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PREDICTED YELLOW HILL 12KV CB A LOCKED OUT DUE TO POLE FIRE// IF UNABLE TO ISOLATE FAULT, WILL ISOLATE STATION CB AND ISSUE HOLD ORDER ON CKT.// CREW ENROUTE//BURNT OFF POLE AT 37820147A00387..STEVE RAY/JAY GARRETT/ROBBIE WORRIX ENROUTE WITH MATERIAL TO REPAIR.DRAFFIN/YELLOW HILL CIRCUIT OPEN..VER/ARN L3/HFP IDC CHANGED TIME OFF PER CALLS FROM 1625 XXXX
675 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-01-27 18:32 | 2019-01-27 22:22 | 334 | 230 | 4726491 | 76820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | OCR WENT BAD//bypassed and placed in AED//cod 334// L3/HFP
676 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2011-05-24 11:01 | 2011-05-24 12:40 | 772 | 99 | 4156961 | 76428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RELAY | DPU 2000R FAILURE TO STATION BREAKER //VER/GAH IDC XXXX
677 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-02-05 00:43 | 2020-02-05 06:00 | 241 | 317 | 4363001 | 76397 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | crossarm braces broke at pole 37830220000047. restored power at 6:00/ ISO 37830221000158/ COD 241
678 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-06-25 19:52 | 2009-06-25 20:47 | 1389 | 55 | 60975-1 | 76395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLOWN ON STATION EXIT POLE. WILL ATTEMPT TO CLEAR UP WITH LONG-STICK. CLEARED UP BAD ARRESTER AND CLOSED BREAKER AT 20:47. I WILL TURN IN JOB TO REPLACE ARRESTER. SH VER/ARN IDCC TOF1954 XXXX
679 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2022-12-18 15:18 | 2022-12-19 18:00 | 108 | 1602 | 4273921 | 76332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Source side stepdown fuse blown on 96-C3-395A 96cc// bad 500kva step down//open GOAB 374 @ 2220/ crew closed in GOAB @ 2318 and stepdown fuse blew on 96-C3-395A// opened goab on 96-C-374 @ 0137 to change stepdown, restored goab @ 0247 to open REC on 96-C-413, restored REC @ 0250 84cc//Found LF open on 72-C-640 12cc/ bad UG//Source side stepdown fuse blown on 96-C3-395A// Checking// bad 500kva step down// crew req// opened goab on 96-C-374 @ 0137 to change stepdown, restored goab @ 0247 to open
680 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2012-12-16 17:40 | 2012-12-16 19:22 | 748 | 102 | 4473261 | 76296 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED POSSIBLE LOSS OF # 2 TR @ HOWARD COLLINS STATION @ 1740 // STATION SERVICE TR CUTOUT FAILED - SERVICER REPLACING & PERFORMING TCG GAS TEST ON STATION TR //VER/GAH IDC XXXX
681 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2020-03-21 01:44 | 2020-03-21 04:55 | 399 | 191 | 4498371 | 76209 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | DOL 1002603 // suspect station outage at Reedy // Beaver Cr - Fleming 69kV line operated @ 0144 and started receiving outage calls at reedy // Distribution servicer and Station servicer enroute// found blown arrestor on 34kv bus regulator ph 3//cod 400
682 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-10-25 12:23 | 2012-10-25 13:38 | 1014 | 75 | 4171421 | 76050 | DISTRIBUTION STATION | EQUIPMENT FAILURE | MOAB | EQUIPMENT FAILURE ON HIGH SIDE OF STATION TRANSFORMER/PREPARING LOAD TRANSFER VER/KEP IDCC TOF1228 XXXX
683 | Hazard | 3311103 | STINNETT | WENDOVER | 2009-03-06 06:39 | 2009-03-06 09:44 | 411 | 185 | 55604-1 | 76035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3311103//SWITCH FAIED TO CLOSE COMPLETELY ON 435-23//VER/CRB IDC REMOVED 141 CUSTOMERS AND LENGTHENED LAST STEP ON THE FIRST ORDER XXXX
684 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-01-31 08:06 | 2019-01-31 16:09 | 303 | 483 | 4742461 | 75846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STEPDOWN BURNT UP - 38830117A00504 -'B' PHASE STEPDOWN ¦¦¦ OPENED RECL @ 0810 ¦¦ CLOSED RECL @ 0835 ¦¦STEPDOWN BURNT UP - 38830117A00504 -B PHASE STEPDOWN ¦¦¦ OPENED RECL @ 0810 ¦¦ CLOSED RECL @ 0835 ¦¦ SEE 4742581 ALSO ¦¦ Need linecrew, and flaggersSTEPDOWN BURNT UP - 38830117A00504 -B PHASE STEPDOWN ¦¦¦ OPENED RECL @ 0810 ¦¦ CLOSED RECL @ 0835 ¦¦ Need linecrew, and flaggers. Tagged to ddc at 117-504STEPDOWN BURNT UP - 38830117A00504 -B PHASE STEPDOWN ¦¦¦ OPENED RECL @ 0810 ¦¦ CLOSED RECL @
685 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2019-01-19 17:28 | 2019-01-19 22:23 | 257 | 295 | 4688351 | 75815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Only 1 phase open on recl 182-A-259 (A phase - 257 COD) 205-29 no trucks crew required pole fire 2 deadend bells burnt up/chg cutout also 205-29 no trucks crew required pole fire 2 deadend bells burnt up/chg cutout also/tagged to r morgan205-29 no trucks crew required pole fire 2 deadend bells burnt /up/chg cutout also/tagged to r morgan Released by crew 078S03/Arrived RM RECLOSER 182-259 RESTORED @ 2223 Only 1 phase open on recl 182-A-259 (A phase - 257 COD) 205-29 no trucks crew required pole fir L3/HFP
686 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-12-22 01:21 | 2013-12-22 16:55 | 111 | 934 | 4183841 | 75793 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 93-188 NUMBER 4 COPPER DOWN TRUCK MAYBE NEED TO CK, STEP DOWN ON POLE 93-504 MAYBE LOOSE HOT TAP FIRE SHOOT OFF POLE WHEN ON PUT REC. ON C PHASE ONLY COD-111 5:00 AM RESTORED 11 CUSTOMERS// NOT ENOUGH INFORMATION IDCC CNT132 XXXX
687 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-11-30 09:44 | 2022-11-30 15:20 | 225 | 336 | 4206671 | 75600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | closed viper switch in on source had a connection bad had to open back up, send to will jones he is coming to make repairs Released by crew 077H05 // restored @1520 LR- Per PowerOn, there shows to be 225 CC on 37830184B00266
688 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2022-01-04 18:09 | 2022-01-04 23:20 | 243 | 311 | 4303041 | 75573 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | all 3 phases out//B phase burnt out of sleeve at pole 221-14. help on the way. power restored 23:20 //cod 243
689 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-09-26 16:02 | 2009-09-26 18:21 | 560 | 139 | 64207-1 | 75284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM ROTTED OFF ON POLE 1061-25 GOING TO OPEN GOAB SWICH1061-3 AND CLOSED RECLOSER ON POLE 1108-6119 AT 1710 STS CLOSED GOAB SW ON 1061-3 AT 1821 RELEASED BY CREW 077S05 VER/KEP L3/KEP IDC XXXX
690 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2018-06-11 21:29 | 2018-06-12 11:22 | 90 | 833 | 4587021 | 74970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | line fuse blown on 1121-D-28 will patrol//a ph out only (cod: 62)A phase line fuse blown on 1121-D-28 will patrolA phase line fuse blown on 1121-D-28 will patrol.end of cross arm on pole 1121-D-30 has split out and has phase touching arm. will need 4 man line crew and man ROW crew to make repairs this is no truck.Bring 1 8ft arm, braces,2 7200 pins and insulators will also need cutout&arrestor with arm mounting bracket//will need to open C phase line fuse on 1121-D-28 for repairs to be made// trouble tickets show c phase out from beginning of outage
691 | Hazard | 3307301 | BULAN | ARY-HEINE | 2018-08-07 20:54 | 2018-08-08 12:05 | 163 | 911 | 4922501 | 74930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 2 phases in , center phsae out shows to be Bphase, cross arm cocked up in the air needs pulled back downand braces . Released by crew 077H03//COD 70 FROM BEGINNING//OPENING OTHER 2 PHASES @ 1005//2 phases in , center phsae out shows to be Bphase, cross arm cocked up in the air needs pulled back downand braces . Released by crew 077H03 opened ohase A &C at 10:05 to make repairs closed back and restored all power at
692 | Hazard | 3310502 | HADDIX | CANOE | 2015-10-24 11:50 | 2015-10-24 18:20 | 192 | 390 | 4373291 | 74880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ON POLE 75-13 GOT BAD DE INSULATOR, NEED CREW AND SEVEN 19.9 INSULATORS AND TWO PT INSULATORS RELEASED BY CREW 077S05 REPLACED ARMS AND INSULATORS AND RESTORED POWER AT 18:20// VER/ ADH L3/HFP XXXHFP AJB
693 | Hazard | 3311103 | STINNETT | WENDOVER | 2020-12-26 13:13 | 2020-12-26 16:57 | 337 | 224 | 4824751 | 74473 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DA Scheme // DOL 1078773 // SCADA indicates DA SW 435-23 locked open at 1313 12/26/20 // cod 337 //
694 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-05-15 16:42 | 2020-05-15 22:41 | 334 | 359 | 4839691 | 74438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | crew required. B phase loop burnt in two on 38820746D10042 nta Released by crew 079S03/ SEE DOL 1019030
695 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-02-05 07:23 | 2010-02-05 09:38 | 572 | 135 | 63197-1 | 74385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#33753277 PATROLLING LINE . FOUND BAD CUTOUT ON POLE 1137-649.ISOLATED THERE AND RESTORED RECLOSER AT 0933 .CLOSED RECLOSER IN AT 09:33. LAST TWO CUSTOMERS ON AT 09:38. IDC XXXX
696 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2008-07-29 06:35 | 2008-07-29 12:43 | 237 | 368 | 61624-1 | 74378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202203 -POLE TOP BURNED OFFPOLE TOP BURNED OFF POLE 771-497 BAD CUTOUT RELEASED BY CREW 079S01//CREW ON SITE STARTING REPAIRS TCMILLER //SAM CLOSED BREAKER IN AT 12:43 //VER/GAH IDC XXXX
697 | Hazard | 3420001 | SOFT SHELL | VEST | 2019-11-27 12:30 | 2019-11-27 18:12 | 217 | 342 | 4078621 | 74214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Bad pole top insulator on pole 108-126 on Highway 1087 across from Beckham Combs School. Flaggers Needed power restored @ 1812, please close this order GRF//cod 217
698 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-01-19 18:01 | 2011-01-19 19:44 | 719 | 103 | 62772-1 | 74057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEND FEEDER BREAKER IN ORDER TO MAKE REPAIRS DUE TO POLE FIRE//COD 719 // FEEDER OPENED AT 1801 VER/ARN IDC XXXX
699 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2017-12-24 21:18 | 2017-12-25 15:41 | 67 | 1103 | 4672831 | 73901 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Recloser is open with a fault on C phase, patrolling the line. Tried recloser, seen flash near the top of the mountain. Need utv to try and get to the line from old road at Dix Knob. Released by crew 079S02// Top of pole is burnt off 7-C-102 can lower everything and make repairs. Grnds 7-5, 7-111/ Released by crew 074H10
700 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-09-17 14:37 | 2012-09-17 17:10 | 483 | 153 | 4054051 | 73899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REC. OPEN ON POLE 37830174D44412, PATROLLING LINE. --- BAD INSULATORS ON POLE 37830223A00058, CREW ENROUTE. === REPAIRS MADE, POWER RESTORED AT 17:10 COD-483 ISO OCR 37830174D44412 VER/HFP L3/HFP IDC XXXX
701 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-12-26 12:26 | 2008-12-26 13:37 | 1039 | 71 | 64058-1 | 73769 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | STATION OUTAGE ***STATION SERVICER AND DIST. SERVICER DISPATCHED.XFMR CUTOUT THAT SERVES AC IN STATION BLEW UP. REPAIRS IN PROGRESS. FAILED STATION SERVICE CUTOUT...XFMR CUTOUT THAT SERVES AC IN STATION BLEW UP. REPAIRS IN PROGRESS. CUTOUT REPLACED AND SERVICE RESTORED AT 13:35. SH CODED 58 TO OTHER EQUIP FOR SYSTEM TO ACCEPT IT. VER/PDP IDCC TOF1236 XXXX
702 | Pikeville | 3409502 | BURDINE | LEVISA | 2021-08-15 20:41 | 2021-08-15 22:36 | 641 | 115 | 4073551 | 73715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Servicer found CSP TR at 37830335B00037 has broken bushing. isolated (See Order # 4074321 (1 CC) Closed CB at 2236 restoring 641 CC
703 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2020-01-12 00:32 | 2020-01-12 10:24 | 124 | 592 | 4272161 | 73408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2150103-- at 0032 SCADA indicated the Sprigg/Sprigg 34kv ckt locked out, cc316--left hand phase down @ pole 992-b-415 going to old abandoned building. Transformer bank has been opened for years. Isolated @ pole 992-b-36. closed via scada at 1024
704 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-01-15 15:29 | 2016-01-15 18:30 | 1255 | 181 | 4623321 | 73405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON POLE 194A-33..WILL PATROL..FOUND BAD CUTOUT..MADE REPAIRS CLOSED XFM BACK IN @ 18:30.. VER/KEP AJB
705 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-07-04 11:56 | 2011-07-04 19:23 | 164 | 447 | 4453531 | 73308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 37830129B00042 RECS OPEN ON POLE . CHECKING LINE///// MIDDLE PHASE LINE BROKE AT DEADEND. # 4 CU. MANUAL POLE? CREW REQUIRED. RELEASED BY CREW 077S08 VER/HFP L3/HFP IDC XXXX
706 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-06-02 21:26 | 2008-06-02 22:49 | 882 | 83 | 54727-1 | 73206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | AT 2126, LOVELY/WOLF CREEK FEEDER OUT . DISP SEV.. ALSO 428 OUT ON THE WV SIDE FED BY MIDDLE BURNING CREEK STATION CONT CARL HUNDLEY ROANOKE DDC .TIM KINCAID WORKING THE WV SIDE. SAM WHITT PATROLLING CKT & WORKING WITH TIM KINCAID ON WV SIDE. 224 @ 2249 CLOSED WOLF CREEK VIA SCADA. ** WORKING WITH PETE IN ROANOKE DDC OK FOR HIM TO CLOSE HIS MIDDLE BURNING CREEK -FEEDERS. OK 2343. ** POLE FIRE WAS FOUND LATER P.O. 54767-1 ** THIS WAS THE INTIAL CAUSE OF THE FEEDER L.O. VER/PDP IDC XXXX
707 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-11-03 02:24 | 2008-11-03 04:33 | 567 | 129 | 61659-1 | 73143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3310501 - FOUND NOTHING WRONG //VER//GAH IDC FOUND ROTTEN POLE ON 11/4 SEE OUTAGE NUMBER 61591-1 ALLOWING PRIMARY TO SAG DURING COLD CONDITIONS CHANGED FROM UNKNOWN XXXX
708 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-11-12 13:13 | 2015-11-12 15:45 | 656 | 152 | 4435541 | 73140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 600 AMP DISC HAS FAILED OUTSIDE JACKSON STATION// SERVICER ON SITE AND CREW ENROUTE// WILL REQUIRE BREAKER OUTAGE TO MAKE REPAIRS// APPROX 90 MINUTES TO MAKE REPAIRS - CREWS ON SITE MAKING REPAIRS @ 1500//TOM - CLOSED STATION CB @ 1545//600 AMP DISC HAS FAILED OUTSIDE JACKSON STATION// SERVICER ON SITE AND CREW ENROUTE// WILL REQUIRE BREAKER OUTAGE TO MAKE REPAIRS// SEE DUP H4435541 FOR `A` PHASE OUTAGE MENTIONED IN DOL VER/HFP L3/HFP AJB
709 | Hazard | 3301401 | COMBS | COMBS | 2019-11-27 05:08 | 2019-11-27 08:35 | 353 | 207 | 4071591 | 73071 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | found bad tie wire on pole 37830246D00124
710 | South Williamson | 3200302 | BELFRY | TOLER | 2013-09-21 11:05 | 2013-09-21 13:20 | 540 | 135 | 4873251 | 72900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | PATROLLING LINE. RECLOSER HAS A CLOSE MALFUNCTION ALARM RELEASED BY CREW 079S02 VER/HFP L3/HFP IDC XXXX
711 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-04-06 06:35 | 2009-04-06 14:51 | 207 | 496 | 66162-1 | 72669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701 SAME AS OUTAGE 66147 LINE CREW TO REPLACE 50/2 POLE , 2 CUTOUTS. CUT LOOP ON POLE 212-178, LINE FUSE BACK ON AT POLE 188-9001 AT 0800 RELEASED BY CREW 078S01//VER/CRB AJBC CNT214 7 CUST REST STEP TWO 141-7=134. INT OUT ON STEP XFR 212/11 W/7 CUST FIRST CALL AT 5:22. SEE 66147-1
712 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-03-24 11:15 | 2018-03-24 15:49 | 348 | 274 | 4047471 | 72552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recloser open @143-C4-411, patrolling. Opened up NC switch @143-A-66, closed rec. back in @1409, still patrolling. BAD CUTOUT ON 37830167A00167. Recloser open @143-C4-411, patrolling. Opened up NC switch @143-A-66, closed rec. back in @1409, still patrolling. Cut out busted on pole 167-A-167, manual pole and cant reach with stick to isolate, will be changing out.Recloser open @143-C4-411, patrolling. Opened up NC switch @143-A-66, closed rec. back in @1409, still patrolling. Cut out busted on p
713 | South Williamson | 3411401 | DEWEY | INEZ | 2015-04-17 00:03 | 2015-04-17 00:28 | 2897 | 25 | H4327921 | 72425 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED 138KV MOAB X2 OPENED @ DEWEY//THIS HAS DEWEY STATION INTERRUPTED// STATION SERVICER DISPATCED// DISTRIBUTION SERVICER DISPATCHER//WILL MAKE UPDATES AS INFORMATION BECOMES AVAILABLE//TOM // RESTORED STATION, FOUND BAD FUSED DISC ON 34KV BUS, DE-ENERGIZED TO MAKE REPAIRS// UPDATED FETR// RELEASED BY CREW 076H07 VER/TOM L3/TOM L3/DKGXXX VERIFIED WITH ALARM HISTORY THIS IS SECOND OUTAGE WHEN C/O SIZZLED AJB
714 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-02-19 09:09 | 2014-02-19 14:44 | 375 | 335 | 4400101 | 72283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | RICK OPENING RECLOSERS ( COD-374)TO CHANGE OUT CROSSARM FOR APPROX. 3 HRS OPENED REC AT 0909 CLOSED AT 1215 UP TP FUSE 444-42 (COD-16) CLOSED ALL @14:44 VER/SEF L3/GSL IDC XXXX
715 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-03-06 06:29 | 2012-03-06 07:08 | 1851 | 39 | 4555281 | 72189 | TRANSMISSION STATION | EQUIPMENT FAILURE | CAPACITOR | DE-ENERGIZED STATION DUE TO FIRE IN STATION // 46KV CAP BANK FAILED AT FORDS BRANCH STATION // //VER/GAH IDC XXXX
716 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-07-17 15:41 | 2018-07-17 16:55 | 975 | 74 | 4789441 | 72150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | DOL 843831///SCADA indicated 34kV DA Sw at 37830387C00594 is open///BAD ARRESTER CUT IN THE CLEAR WILL REPLACE IN THE MORNING Released by crew 077S01 // VER TIMES PER SCADA & DOL - L3/HFP
717 | South Williamson | 3411401 | DEWEY | INEZ | 2022-01-21 17:19 | 2022-01-21 19:30 | 550 | 131 | 4394261 | 72050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | reclosers open showing no faults//didn't see anything//recloser will not close//control not working//have recloser bypassed and tagged to DDC//restored at 19:30//please put in abnormal database// Released by crew 079S01
718 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-08-07 09:33 | 2017-08-07 12:46 | 372 | 193 | H4232481 | 71796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | A PHASE AND GROUND SHOWS FAULTS (206 CUST), PATROLLING LINE. CROSSARM BROKE ON POLE 179-14, WILL NEED LINE CREW AND MANUEL R-O-W CREW // OPENED B&C PHASES @ (269 CUST)A PHASE AND GROUND SHOWS FAULTS, PATROLLING LINE. CROSSARM BROKE ON POLE 179-14, WILL NEED LINE CREW AND MANUEL R-O-W CREW, POWER RESTORED. OPENED RECLOSER AT 09:33 VER/ARN/// PER B.O. C INITALLY OUT - 106 CUST = L3/HFP HFPC FP37830179B00194 SJG
719 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-05-03 15:01 | 2009-05-04 00:23 | 414 | 562 | 64296-1 | 71676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 29637583 ///CREW REQUIRED45/4 SINGLE ARMS 3 PHASE 556 WIRE TRUCKS OK/ISOLATED ON 182-73 BACKFED FROM183-48 REST//REST 229 CUST @ 1627// FAULT POLE 38830182B43580 //CREW REQUIRED45/4 SING---CREW LOADING MATERIAL---CREW WILL CUT LOOPS TO GET MOST CUST ON//1906 RESTORED ADDITIONAL 164 //MOVED FETR DUE TO HAND DIG L3/DKG IDC XXXX
720 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-01-03 12:28 | 2012-01-03 14:28 | 595 | 120 | 4229001 | 71400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | METERING THINKS CONTROL CABLE FOR RECLOSER IS BAD.WILL CHANGE OUT. CHANGED CONTROL CABLE AND CLOSED AT 1428//COD 595// VER/DBM IDC XXXX
721 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-08-24 05:42 | 2020-08-24 13:10 | 235 | 448 | 4362671 | 71244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Ocr out on 529/143 patrolling bad insulators on 552/62 opened GOAB on 37840552B40508 closed ocr on 529/143 at 08:56 Released by crew 077S03
722 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2020-07-30 19:37 | 2020-07-31 00:40 | 235 | 303 | 4258461 | 71205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | L/F ON POLE 38830020C45614 OPEN//COD 235// BROKEN CROSSARMS//CREW HAS BEEN CALLED OUT @ 20103 100t open @ 21-5614, 1 phase down from 537 to 538, bad xfmer, braces @ 5383 100t open @ 21-5614, 1 phase down from 537 to 538, bad xfmer, braces @ 538. bad c/o @ 21-536. Released by crew 078S07,repairs made all cust restored @ 0040 please close ticket thanks.bt/ ISO 38830020C45614/ COD 235
723 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-06-28 09:12 | 2020-06-28 10:46 | 757 | 94 | 4082731 | 71158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1031416 // SCADA indicates feeder l/o @ 0912 // cod 757 //insulator failed on hillside on pole 771-a-129//this is on WV side///opened switches on 771-a-408// ky ddc tags//
724 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-09-18 12:52 | 2020-09-18 15:40 | 721 | 168 | 4476061 | 71108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER REQD //DOL 1054679// burnt off arm @ 1123-7571//opened SWS at 1147C3-5028 closed intellirupter at 1148a1-358 restoring 410 CC //FETR 1600 burnt off arm @ 1123-7571// crew on site FETR 13:30 LRM /// closed SWS at 1147C3-5028 restoring remaining 311 CC//
725 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2022-12-14 22:10 | 2022-12-15 04:50 | 519 | 400 | 4260631 | 70980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ETA 2145//NO OUTAGE TILL RECLOSER 37820049D20331 OPENED @ 2210//TAGGED TO THE DDC // Bad poletop insulator @49-220 burndt the top of the pole off, will have to open rec.@49-D2-331 to make safe.ETA 2145//NO OUTAGE TILL RECLOSER 37820049D20331 OPENED @ 2210// // Bad poletop insulator @49-220 burndt the top of the pole off, will have to open rec.@49-D2-331 to make safe. Got pole lowered and closed rec. @49-D2-331 @0450. Released by crew 074S05
726 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-10-23 17:45 | 2017-10-24 12:05 | 285 | 1100 | 4485111 | 70832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER REQUIRED/FAULT POLE 37830343A00037, POLE ON FIRE, TRANSFER LOAD TO BONNYMAN-BIG CREEK DOL CASE 780444 OPENED SET OF LOOPS BETWEEN POLES 343-194 & 343-135 RESTORE RECLOSER AT 22:10 ON POLE 344-144// RELEASED BY CREW 077H04 VER/KEP ACB
727 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-08-26 13:48 | 2013-08-26 14:40 | 1360 | 52 | 4708811 | 70720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER OPEN ON POLE 141-116.PATROLLING NOW.DWAYNE THACKER DOWNLOADED INFO..WILL CHANGE CONTROL AND / OR CABLE SOON.RECLOSER IS CLOSED IN NOW BUT DOES NOT APPEAR TO BE GOING THRU OPERATIONS..JUST DROPS OUT FOR NO REASON..RECLOSER IS BY-PASSED AS OF NOW. //VER/GAH AED ENTERED ON RECL HFPC FEC58 L3/HFP IDC XXXX
728 | South Williamson | 3411401 | DEWEY | INEZ | 2009-08-04 10:47 | 2009-08-04 17:05 | 187 | 378 | 54331-1 | 70686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 7200 VOLT CUTOUT BAD ON POLE 768-C-184//TRIED TO RESTORE BUT STEPDOWN TRANSFORMER APPEARS TO BE BAD// 500 KVA STEPDOWN TRANSF BAD L3/HFP IDCC CDC92 XXXX
729 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-12-06 05:10 | 2009-12-06 11:21 | 202 | 371 | 61848-1 | 70670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP ONLY A PHASE RECL OUT 202 CUST// RELATED TO ORDER 60704-1 WHICH SHOULD BE EXTENDED TO THE COMPLETION TIME OF THIS ORDER.RELEASED BY CREW 074S06 DALE I AM EXTENDING THE RESTORATION TIMES IN ORDER 60704-1 & 61741-1 DUE TO COLD LOAD IN THIS ORDER THIS ONE CAN BE DELETED IN HOIS...HFP L3/HFP IDC XXXX
730 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2008-05-03 14:14 | 2008-05-04 01:38 | 461 | 684 | 56690-1 | 70431 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | 3004301// TRANSMISSION POLE ON FIRE, CREW TO CHANGE OUT POLE, ALL THE CUSTS BACK ON BUT 10 THAT WILL BE OUT THE DURATION. TRANSMISSION CREW TO MAKE REPAIRS DEBBIE ..... TRANSMISSION EQUIPMENT FAILED DROPPED LINE INTO DISTRIBUTION DEB CHECKED IDC XXXX
731 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-06-28 09:22 | 2009-06-28 12:15 | 407 | 173 | 65770-1 | 70411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | PATROLLED LINE FOUND NO PROBLEM FUSE BLOWN ON CONTROL ON RV IDC CHANGED CAUSE FROM UNKNOWN XXXX
732 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-02-16 07:33 | 2015-02-16 09:11 | 717 | 98 | 4031571 | 70266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | PATROLLING LINE/VEM/FAILED REGULATOR @116-5058/CREW TO BY PASS AND ISOLATE REG/FETR 1000/VEM/C PHASE RELEASED BY CREW 078H14//COD 717//NO REPLACEMENT REGULATOR AVAILABLE AT THIS TIME//AED CREATED// VER/DBM // VERIFIED TIMES VIA SCADA // L3/HFP XXX AJB
733 | Cannonsburg | 3001401 | LOUISA | CITY | 2010-07-09 14:35 | 2010-07-09 16:45 | 539 | 130 | 64088-1 | 70070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35924055 // END OF CROSSARM POLE 454/3112 BURNING; OPENED SOLID-BLADES ON POLE 454/6002 TO ISOLATE TROUBLE; CREW REQUIRED; NEED 8FT CROSSARM, BRACES, 3-7200 CUTOUTS AND ARRESTORS WITH CROSSARM BRACKETS RELEASED BY CREW 078S12//ISO 38830454D16002//COD 539//COMPLETED REPAIRS AND RESTORED @ 1645 // IDCC TOF1404 XXXX
734 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2019-04-22 12:07 | 2019-04-22 15:04 | 690 | 177 | 4147061 | 69946 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE NECESSARY TO ISOLATE FAULT AT POLE 38821137D00318 - POLE FIRE I opened recloser on pole 38821137A00331 at 12:07, source side riser removed and tagged to Matney. Released by crew 079S02
735 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-06-27 01:25 | 2018-06-27 12:20 | 334 | 655 | 4675641 | 69920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | on pole 37830409000024 primary burned into were sturip and hlc is holding primary wire took clamp off pole 37830409000023 to get three phase back in at 0442 who ever repair this needs to look at take off pole before repairs and can use flagmen to get to pole//cod 334//
736 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-03-02 20:35 | 2015-03-03 04:15 | 152 | 460 | H4092911 | 69920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "B" PHASE OPEN COD-13/ POLE 199-197 "C" PHASE OFF AT 2035 COD-152/GROUNDED AND TAGGED TO DDC /FAILED CUTOUT BURNT POLE INTO POLE 198-93/45/2 POLE DOUBLE DEADEND 2 PHASE WITH SINGLE PHASE TAP ALSO HAS UNDERGROUND ON POLE WITH 15 KVA RELEASED BY CREW 078S 03 RECLOSER CLOSED AT 0415 ALL RESTORED EXCEPT XFMER POLE#93/XFMER CLOSED 0515/ VER/KEP L3/HFP XXX AJB
737 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2021-07-17 11:38 | 2021-07-17 13:18 | 698 | 100 | 4923981 | 69800 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL1132519/ Transmission line outage/ she on deadend bell failed on 46kv line/restored 1318
738 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-05-23 23:17 | 2017-05-24 12:00 | 133 | 763 | 4846031 | 69799 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STEP DOWN FUSE BLOWN PATROLLED LINE BBAD CSP TRANS ON 99-95 ISOLATED TAP AT 99-38 BY REMOVING HOT TAP POLE WILL HAVE TO BE CLIMBED TO INSTALL OT TAP NEED 25 KVA TRANS 7200 CUUTOUT AND STANDOFF BRACKET NTA SPOKE TO TIM HALL AND HE HAS CREW EN ROUTE THERE IS ROW CREWS WORKING THIS LINE IF THEY NEED THEM RESTORED FUSE ON STEPDOWN AT 06;52 RESTORED RECLOSER AT 08:00 RELEASED BY CREW 079H03.. REPLACED TRANSFORMER AND INSTALLED XFMR CUTOUT. COD-133 ISO LF 37820098D20148B VER/HFP L3/HFP AJB
739 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-07-24 07:46 | 2017-07-24 11:05 | 413 | 199 | 4170491 | 69713 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | DOL 759463//PER SCADA, 138/34 MOBILE TR AP-1 TRIPPED OUT AT 0746//COD 413// VER/DBM /// SEE DUPLICATE ALSO - ABNORMAL LOAD XFER ON 05/21/17 DOL CASE#: 743587 = L3/HFP XXXHFP SJG
740 | Hazard | 3309301 | VICCO | REDFOX | 2017-02-05 09:16 | 2017-02-05 11:26 | 535 | 130 | 4359411 | 69550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | SCADA INDICATED THE REDFOX 34KV CB A OPERATED TO LOCKOUT// THIS HAS 535 CC OUTAGED//, PATROLLING LINE. LOOKED LIKE SOMEONE HAS SHOT THE RECLOSER, BY-PASSED REC/ ISO 3309301/ COD 535/ RESTORED 1126/ 0916 OPENED/ VER/BOW // PER AED & DOL EQUIPMENT FAILURE = L3/HFP XXXHFP AJB
741 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-06-11 22:08 | 2014-06-12 09:48 | 99 | 700 | 4068101 | 69300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | BAD RECLOSER ON POLE 374-185, WILL PATROLL LINE TOMORROW. RELEASED BY CREW 077S11BAD RECLOSER ON POLE 374-185, WILL PATROLL LINE TOMORROW. REPLACED RECLOSER RESTORED POWER AT 09:48 AJB
742 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2013-06-07 15:16 | 2013-06-07 19:14 | 291 | 238 | 4237101 | 69258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER LOCKED OUT ON 1086C458..BURNT OFF POLE TOP ON 3 PHASE POLE 1086C15..CAN PROBABLY GET BUCKET TO POLE..NEED CREW, SINGLE 8 ARM, ARM PINS & INSULATORS, CUTOUT..CREW NOTIFIED, THEY ARE ENROUTE.WILL ISOLATE RECLOSER, TAG FOR JOEY REED, & GROUND LINE..//..REPAIRS MADE.MEN & EQUIPMENT IN THE CLEAR.GROUNDS REMOVED.NO NEW HAZRDS.REMOVED TAGS.PUT RIZERS BACK ON RECLOSER.CLOSED RECLOSER.POWER ON.JRV..06/07/13//COD 291// VER/DBM IDC XXXX
743 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-04-15 06:32 | 2014-04-15 11:18 | 364 | 286 | 4605341 | 69176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED GOAB ON POLE 143-66 AND CLOSED RECLOSER ON POLE 143-411 AT 0850,ISOLATING THE TROUBLE ON POLE 143-83. CREW ENROUTE. RELEASED BY CREW 074S02..REPLACED 7 DEAD END INSULATORS AND 1 PIN TYPE INSULATOR..SERVICE RESTORED AT 11:18.D LEWIS RELEASED BY CREW 074H08 VER/CRB IDC XXXX
744 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-10-15 18:09 | 2009-10-16 01:00 | 168 | 411 | 50040-1 | 69048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT POLE 38830164D00362, OPENED RECLOSURES AT POLE 3883016D00110; POLE NOT ACCESSABLE TO TRUCKS, 3-PHASE TAP POLE, NEED 45 CLASS 2 POLE, 3- 8 FOOT ARMS, 3 SETS OF BRACES, 2 DROP PINS, 1 POLE TOP PIN, ---3-19.9 KVA INSULATORS, 3-19.9 KVA BELLS, 2 CLEVISS, 3-19.9 KVA CUTOUTS; BILL LYNCH ON SITE RELEASED BY CREWCREW ON SITE VER.PDP IDCC FP110 XXXX
745 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-02-12 13:10 | 2020-02-12 14:28 | 884 | 78 | 4396651 | 68952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DDC HOLD ORDER // DOL 992224 //outage necessary to replace broken cross-arms on pole 852-196//outage will last approx 1.5 hrs //cod 884 // crew has run into difficulties due to terrain and weather, ETR extened to 1530 //
746 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-07-12 07:06 | 2010-07-12 09:02 | 593 | 116 | 65190-1 | 68788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202202STS WR # 35939445 //PREDICTED RECLOSER IS LOCKED OUT....PATROLLED.....PORCELAIN ARRESTER ON 1114-C-64 HAS BOTTOM GROUND LUG BLOWN OFF....REST OF LINE LOOKS CLEAR...WILL CLEAR ARRESTER...//....CUT ARRESTER LOOSE....FOUND PROBLEM...BURNT UP CUTOUT THAT PROTECTS LATERAL (FUSE BLOWN....DOOR DIDNT DROP & BURNT UP) ON POLE 1114-C-128..ISOLATED...CLOSED RECLOSER ON POLE 1090-D-169 @ 09:02 // JOHNNY TO TALK WITH RANDALL VER/HFP L3/HFP IDC XXXX
747 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2016-06-07 12:32 | 2016-06-07 18:24 | 250 | 352 | 4319491 | 68734 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE PER DALE SIZMORE// OPENED REC. 37830177D00366 ON 1307 (250CC) // OPENED ON 37830177D40583 & TAGGED TO GREG FOR VISABLE OPEN // @ POLE 37830178A10619 CUTTING LOOPS INSTALLING 300 AMP SWS. // JEFF HAS PERMISSION FROM GREG TO REMOVE HIS TAGS/ POWER RESTORED AT 1824 , CLOSED SWITCHES ON P#37830178A10619/ MD DONE/ VER/BOW AJB
748 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2014-02-02 10:41 | 2014-02-02 13:03 | 688 | 142 | 4336581 | 68638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | / BREAKER LOCKED OPEN// PHASE A TARGET// PATROLING SPACER CABLE BKT. BROKEN @ 24-1394// OPEN 3 600 AMP SWITCHES @ 24-249 // SEE H4336581 ALSO TO REST ALL CUST// VER/KEP VER/HFP L3/HFP IDC XXXX
749 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2020-04-17 22:32 | 2020-04-18 04:16 | 907 | 344 | 4714611 | 68592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1010868/EMERGENCY BREAKER OUTAGE DUE TO WIRE DOWN/ISOLATING AND PREPARING TO RESTORE PORTION OF CIRCUIT/bad crossarm @ 1124-1595/opened 1124-b3-8240///ARRIVED RM making repairs replaced xfm fuses in @ 04:16 please close tic RM Released by crew 078H20
750 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-07-12 07:06 | 2010-07-12 09:02 | 591 | 116 | 65190-1 | 68556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35939445 //PREDICTED RECLOSER IS LOCKED OUT....PATROLLED.....PORCELAIN ARRESTER ON 1114-C-64 HAS BOTTOM GROUND LUG BLOWN OFF....REST OF LINE LOOKS CLEAR...WILL CLEAR ARRESTER...//....CUT ARRESTER LOOSE....FOUND PROBLEM...BURNT UP CUTOUT THAT PROTECTS LATERAL (FUSE BLOWN....DOOR DIDNT DROP & BURNT UP) ON POLE 1114-C-128..ISOLATED...CLOSED RECLOSER ON POLE 1090-D-169 @ 09:02 // JOHNNY TO TALK WITH RANDALL VER/HFP L3/HFP IDC XXXX
751 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-05-04 04:30 | 2013-05-04 07:37 | 366 | 187 | 4069901 | 68442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3-PHASE RECLOSER ON POLE 143C-411 IS OPENED. THE A-PHASE AND GROUND TARGETS ARE UP. I AM PATROLLING LINE NOW. // BROKE INSULATOR POLE 143-202 // CLOSED RECL AT 0737 //, BUT EVERYTHING WAS IN THE CLEAR. I CLOSED RECLOSER IN AT 07:37 AND IT STAYED. I WILL GIVE TIM HALL A NOTE ON BROKEN INSULATOR. //VER/GAH IDC XXXX
752 | Hazard | 3302704 | HAZARD | KENMONT | 2017-07-24 07:46 | 2017-07-24 09:18 | 742 | 92 | 4170501 | 68264 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | DOL 759463//PER SCADA, 138/34 MOBILE TR AP-1 TRIPPED OUT AT 0746//COD 742// VER/DBM L3/HFP XXXHFP SJG
753 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2011-05-03 20:43 | 2011-05-04 01:20 | 263 | 277 | 4004381 | 68101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLSR OUT ON 893A304...CUSTS SAW FLASHES ON STRETCH OF MTN LINE NEAR 917C9014...CALLED CREW..FOOT PATROLLING...BAD CUTOUT PROTECTING 3 PHS LATERAL HAS BURNT FRONT CROSSARM OFF..CREW HERE TO MAKE REPAIRS..//...ISOLATED TROUBLE...OPENED 3 SWITCHES ON 917C101...CLOSED RECLOSER ON 893A304 @ 23:15...//....TEMP REPAIRS MADE....CLOSED SWITCHES ON 917C101 @ 01:20....JRV....05/04/11//VER/CRB IDC XXXX
754 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-11-30 06:30 | 2009-11-30 10:12 | 566 | 222 | 50895-1 | 68022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, PATROLLING LINE RELEASED BY CREW 080S01. REPLACED BAD CUTOUT RESTORED POWER TO ONE CUSTOMER AT 10:12 AM. WILL SHOW SINGLE CUSOTMER ON HOIS.. IDCC STP MISSING, FP331, CDC83 XXXX
755 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-03-16 18:03 | 2014-03-17 16:21 | 61 | 1338 | 4498041 | 67989 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LOOP BURNED INTO ON POLE 102-10 , 2 POLES FROM RECLOSER , POLE IS ACROSS CREEK & MANUEL. NEED CREW WHEN . ALSO NEED FLAGING CREW. // DUE TO THE RISING WATER CREW COULD NOT ACCESS POLE // DUTY SUP SAID TO HOLD UNTIL DAYLIGHT //RECL ISOLATED & HOLD TAG PLACED FOR KY DDC//GAVE TIM PERMISSION TO REMOVE TAGS AND TAG TO SELF POLE 126;166 BURNED OFF CUT DEAD END AT POLE 126;223 RESTORED POWER AT RECL. 102;228 AT 12;30 THIS LEAVES ONE TAP OUT ;; JEFF COMBS ON SITE VER/SEF L3/HFP IDC XXXX