11389 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-01-17 06:02 | 2010-01-17 07:25 | 7 | 83 | 55218-1 | 581 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE LINE FUSE OUT ON POLE 351-2, BAD CUTOUT ON 351-216, ISOLATED CUTOUT ... CLOSED LINE FUSE IN AT 07:25... REPLACED CUTOUT RESTORED POWER TO XFMR ON POLE 351-216 AT 08:15 RELEASED BY CREW 077S11 IDCC CNT3, PH A NOT B, PN283 XXXX
11390 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-07-23 09:36 | 2017-07-23 19:17 | 1 | 581 | 4162961 | 581 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | POWER TEMP IS BAD AT THIS LOC, CUST HAS BAD URD, HAD POWER TEMP ON, CHK VOLTAGE TOP AND BOTTOM OF BREAKER ON TEMP HAD NOTHING, NEED CREW TO BRING ANOTHER POWER TEMP AND REPLACE THIS ONE, ON TOOTSIE DR, ALMOST TO THE END ON RIGHT, TWO YUKON IN DRIVE WAY, BLACK AND RED, ADDRESS 108 TOOTSIE DR RELEASED BY CREW 078S06/CREW ON SITE/FETR1630/VEM/BOTH LEGS BAD/DIGGING UP U/G FOR REPAIRS/VEM/REPAIRS MADE AND ONE CUST RESTORED 1917/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP
11391 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-02-25 02:26 | 2011-02-25 03:49 | 7 | 83 | 61019-1 | 581 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 38830598000032 CUTOUT REPLACED AND ALL POWER RESTORED AT 0349 CLOSE TICKET VER/SDB IDC CHANGED START TIME FROM 0217 XXXX
11392 | Pikeville | 3407101 | TOPMOST | DEMA | 2021-05-08 09:40 | 2021-05-08 11:03 | 7 | 83 | 4550151 | 581 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOUG HALL REPORTS PRIMARY NEUTRAL LOW OVER ROAD AND CROSSARM INSULATOR BROKE ON POLE 37830186000010 // NO OUTAGE AND NO DANGER RIGHT NOW RICK RAY AND CREW GOING TO WORK IN THE MORNING; CROSSARM IS ROTTED ON POLE #186-10, WILL NEED TO ISOLATE THE LINE AT 186-8 (50-T) TO MAKE SAFE, ALL WORK IS MANUAL WILL TAKE ABOUT AN HOUR.OFF AT 09:40 ON AT 11:03
11393 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-11-24 13:04 | 2013-11-24 15:00 | 5 | 116 | 4070201 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, LINE FUSE ON POLE 256-170, POWER RESTORED VER/CRB L3/HFP
11394 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-11-24 11:01 | 2014-11-24 15:51 | 2 | 290 | 4762701 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP HALF OF XFR. CUTOUT IS BROKEN AND HANGING IN THE CLEAR. NO TRUCK TO POLE. BACK YARD. RELEASED BY CREW 078E01 CHANGED CUTOUT CLOSED BACK IN AT 1551/ ISO 38830092A00475/ COD 2/ VER/BOW
11395 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-07-04 16:00 | 2015-07-04 17:10 | 13 | 70 | 4721051 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED 911 WITH AN ETA OF 1600//OPENED L/F @ 1600 POLE 208-26CALLED 911 WITH AN ETA OF 1600// 0PENED LINE FUSE ON POLE 208-26 AT 1600 CLOSED BACK IN AT 1640 ONE CUSTOMER STILL OUT ON POLE 208-140CALLED 911 WITH AN ETA OF 1600// 0PENED LINE FUSE ON POLE 208-26 AT 1600 CLOSED BACK IN AT 1640 ONE CUSTOMER STILL OUT ON POLE 208-140 POWER RESTORED AT 1710 POLE 208-140 NEEDS REPLACED ASAP POLE BURNED BADLY CREW 077H01 VER/CRB L3/DKG
11396 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-04-13 11:24 | 2008-04-13 13:22 | 8 | 118 | 50797-1 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAULT POLE 38830188A00399 1ST HOUSE ON RIGHT OFF RT 3 AS U TURN ON TO BONANZA DRIVE. NO TRUCK ACCESS NEED 19.9 CUTOUT.RELEASED BY CREW 078S01 BAD 19.9 CUTOUT ON POLE 188-399, NEEDS LINE CREW. RELEASED BY CREW 078S01 CREW REPLACED CUTOUT POWER RESTORED AT 13:22 COD - HFP VER/HFP AJBC CNT8 FIRST REST STEP. ONLY 8 ON LINE FUSE.
11397 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2012-01-11 10:55 | 2012-01-11 13:20 | 4 | 145 | 4247291 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT ON POLE 1051-684. LOOKS LIKE FUSE WAS BROKEN FUSED UP EVERYTHING OK. THIS JOB WAS DONE YESTERDAY 2 POLE EXT OFF OF POLE 1027-500 VER/KEP IDC XXXX
11398 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-03-19 19:54 | 2010-03-19 22:19 | 4 | 145 | 51885-1 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34328222 // CUT OUT GATE BURNT UP-- MANUAL POLE NEED 1 MAN AND A 7.2 KV CUT OUT. POWER RESTORED. VER/HFP L3/HFP IDC XXXX
11399 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-02-01 15:10 | 2008-02-01 20:00 | 2 | 290 | 64573-1 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3413401// NEED TO REPLACE 15KVA WITH 25KVA, D. SAMMONS ENROUTE / GXJ RELEASED BY CREW 074S03//COD 2//ALL WORK COMPLETE / 02-01-08 GXJ// VER/DBM IDC XXXX
11400 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-09-12 21:15 | 2015-09-12 23:40 | 4 | 145 | 4232951 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-2616 POLE BURNT NEED CREW CUTOUT LONG RIDGE PIN AND INS. POLE 45-2617 OPEN LOOP GROUNDED LINE RED TAG RELEASED BY CREW 078S08.. CREW ON SITE MAKING REPAIRS ETR 01:30 9/13/15.. REPAIRS MADE AND CUSTOMERS RESTORED AT 23:40 PLEASE CLOSE TICKET CAY VER/SEF
11401 | Hazard | 3303902 | LESLIE | WOOTON | 2011-09-26 16:34 | 2011-09-26 18:30 | 5 | 116 | 4920541 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A COD-5 ISO LF 37830464000030 - VER/HFP L3/HFP IDC XXXX
11402 | Hazard | 3303902 | LESLIE | WOOTON | 2017-01-31 20:25 | 2017-02-01 01:15 | 2 | 290 | 4350391 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 120/240 VER/KEP L3/HFP XXXHFP
11403 | Paintsville | 3410602 | E.PRESTON | LANCER | 2021-10-07 01:39 | 2021-10-07 03:35 | 5 | 116 | 4325311 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Arrestor was bad on CSP xfmr on hillside. Had to open xfmr @ 02:46 to get cleared up. Restored @ 03:35
11404 | Hazard | 3309003 | JEFF | VIPER | 2017-04-13 16:50 | 2017-04-13 21:40 | 2 | 290 | 4644681 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER, NEED 2 MAN LINE CREW AND A 25KV TRANSFORMER 7200KVA,NEED BIG BUCKET RELEASED BY CREW 077H07 37830441000039 VER/AWD L3/HFP XXXHFP
11405 | South Williamson | 3411401 | DEWEY | INEZ | 2010-04-29 19:50 | 2010-04-29 22:15 | 4 | 145 | H52868-1 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CARHIT GUY PULLING SERVICE LOSSE FIXING NOW.BAD XFRMER CALLING CREW RELEASED BY CREW 076H06 WR#34900726CARHIT GUY PULLING SERVICE LOSSE FIXING NOW.BAD XFRMER CALLING CREW WR#34900726WORK COMPLETED//VER/CRB IDCC DUP TO OPEN REPLACE TRANSFORMER XXXX
11406 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-07-17 13:10 | 2018-07-17 15:35 | 4 | 145 | 4787871 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 263-343.cutout broken on xfm. bank pole 263-344.will need big bucket to make repairs...opened line fuses @ 13:10 made repairs and closed back in @ 15:35..//PER SERVICER L3/HFP
11407 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2008-04-27 22:55 | 2008-04-28 01:20 | 4 | 145 | 54715-1 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402202// COD-4 //3402202// BAD CUT OUT ON POLE 42C455. 2 65T FUSES OUT ON POLE 42C66. I WILL BE CHANGING CUTOUT.3402202// BAD CUT OUT ON POLE 42C455. GHANGED CUTOUTS EVERYTHANG OK. VER/LDA IDC XXXX
11408 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2017-03-04 01:50 | 2017-03-04 11:30 | 1 | 580 | 4518271 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | X-FMR CUT-OUT BROKE ON POLE 401-22. CHANGED CUT-OUT AND RE-ENERGIZED X-FMR AT 11:30 VER/CRB
11409 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2021-02-23 07:55 | 2021-02-23 17:35 | 1 | 580 | 4227541 | 580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | A phase xfmr fuse was blown on bank/// Bad 50kva 7200 120/208. Opened B&C phase xfmrs @ 10:55. Customer has opened gate to access with truck to replace.// Replaced can and restored @17:35
11410 | Hazard | 3302703 | HAZARD | HAZARD | 2013-08-13 06:06 | 2013-08-13 15:45 | 1 | 579 | 4658721 | 579 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ON SITE TRANSFORMER FUSE BLOWED REFUSED POWER RESTORED AT 08 05 POWER STAYED ON ABOUT 10 MIN. NEED TO CHANGE TRNSFORMER TRUCK ACESS. SHOWS TO BE A 25 KVA RELEASED BY CREW 077H02 REPLACED TRANSFORMER AND RSTORED POWER AT 1545//COD 1// VER/DBM
11411 | Hazard | 3303902 | LESLIE | WOOTON | 2014-06-18 14:23 | 2014-06-18 17:36 | 3 | 193 | 4107021 | 579 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND VINES RELEASED BY CREW 077S01 REPLACED CUTOUT AND REMOVED VINES , HORNETS --- RESTORED POWER AT 1736 COD-3 ISO TF 37830318B00244 VER/HFP L3/HFP
11412 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2014-05-02 06:57 | 2014-05-02 10:10 | 3 | 193 | 4656681 | 579 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 078S07 POLE 20-6510 6T TRANS, FUSE BROKE REPLACED FUSE VER/SEF
11413 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-01-04 07:17 | 2012-01-04 10:30 | 3 | 193 | 4231551 | 579 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS BAD TRANSFORMER, NEED 25 KVA 7200 TRANSFORMER RELEASED BY CREW 077S05//REPLACE TRANSFORMER VER/KEP IDC XXXX
11414 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-09-30 20:02 | 2012-09-30 23:15 | 3 | 193 | 4101081 | 579 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9, 50 KVA TRANSFORMER, TRUCK ACCESS, NEED 3 MEN, MATERIAL HANDLER. //T. SMITH, W. MELTON & R. RICE TO ASSIST //. ---- POWER RESTORED AT 23:15 //VER/GAH IDC XXXX
11415 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-03-03 21:17 | 2014-03-04 00:30 | 3 | 193 | 4448951 | 579 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TRANSFORMER LEADS BURNT IN TWO, NEED 1 LINEMAN TO HELP... POWER RESTORED. VER/ARN
11416 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-09-24 18:53 | 2018-09-24 22:06 | 3 | 193 | 4152211 | 579 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//NO ANSWER//trans cutout failed on 1081-285.replaced 7200 cutout.restored power at 22;06 L3/HFP
11417 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-07-30 15:57 | 2010-07-30 19:10 | 3 | 193 | 59618-1 | 579 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL HAVE TO CUT VINES OFF OF POLE // BAD 25KVA X-FMR. POWER RESTORED//COD 3// VER/DBM IDCC CDC91 XXXX
11418 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-07-17 17:11 | 2015-07-17 22:00 | 2 | 289 | 4903411 | 578 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANS
11419 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2020-05-24 20:46 | 2020-05-25 01:35 | 2 | 289 | 4900791 | 578 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout
11420 | Whitesburg | 3312901 | JENKINS | KONA | 2018-09-10 10:05 | 2018-09-10 14:54 | 2 | 289 | 4074591 | 578 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | xfmr fuse blown on pole 380-258 due to guywire rusted off at ground & falling into cutout, only2customer affected . Released by crew 077S11
11421 | South Williamson | 3200203 | BARRENSHE | SLATE BRANCH | 2019-10-21 08:11 | 2019-10-21 17:48 | 1 | 577 | 4000901 | 577 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 964316 ¦¦ THIS ORDER REPLACED ORDER 4175471 DUE TO POR FAILOVER¦¦ TIME OFF 0811 10/21/19 NOTES FROM ORIGINAL ORDER"DOL 964316/38821088C00145 POLE TOP ROTTED OFF AND BELL FELL LOOSE ON A VERTICAL 3-PH/OPENED CB AT 1728 TO MAKE SAFE/ (TIME MODIFIED BY DST CHANGE)" BKA STEP 2 DELETED PER MICO.
11422 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-08-15 18:14 | 2008-08-15 19:50 | 6 | 96 | 52427-1 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3314401// LINE FUSE IS OPEN, I AM PATROLLING LINE. I DID NOT FIND ANY TROUBLE. WE DID HAVE A STORM WITH SOME LTNG AND LOTS OF RAIN ROLL THROUGH THIS AREA. FUSE WENT BACK OUT AND I FOUND A BROKEN CUTOUT AT THE END OF LINE ON POLE 449-162//COD 6// VER/DBM IDC XXXX
11423 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-06-03 14:53 | 2016-06-03 18:05 | 3 | 192 | 4292971 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE HOT LEG OF OPEN WIRE SECONDARIES BURNT DOWN UNDER CONNECTION MIDSPAN BETWEEN 1109-19 AND 1109-20 THREE CUSTOMERS AFFECTED FED FROM 25 KVA CSP TRANSFORMER ON POLE 1109-19 I CAN MAKE REPAIRS MADE REPAIRS RESTORED POWER AT 18:05 VER/CRB
11424 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2015-07-02 16:18 | 2015-07-02 17:30 | 8 | 72 | 4711151 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE FUSE OPEN (8 CUSTOMERS)/ TRANSFORMER ON POLE 38830045A10043 ON LOAD SIDE OF LINE FUSE/ MD DONE/ 45-43 LINE FUSE OUT45-43 LINE FUSE OUT BAD CUTOUT REPLACED/ ISO 38830045A10043/ COD 8/ VER/BOW
11425 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-05-27 16:46 | 2008-05-27 19:58 | 3 | 192 | 51839-1 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000801BAD 25 KVA MCCARTY WILL CONTACT ABOUT WHO TO SEND TO/3 CUSTOMERS OUT RELEASED BY CREW 078S03 COMPLTED 1958 VER/HFP IDC XXXX
11426 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2019-10-10 06:49 | 2019-10-10 16:25 | 1 | 576 | 4126471 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 25kva transformer//truck ok//send to bryan ramey Released by crew 078H09///replaced bad 25kva and cutout///closed in at 16:25///complete BR
11427 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-04-29 12:14 | 2015-04-29 21:50 | 1 | 576 | 4376581 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER, CALLING 1 MAN TO COME HELP/CHANGED XFM AND RESTORED POWER AT 21 50// VER/ ADH
11428 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-11-01 08:55 | 2011-11-01 11:19 | 4 | 144 | 4041431 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER OVER LOADED WIRE MELTING OUT ON ONE LEG NEED TO UP-GRSDE TO AN 37.5 NEED NEW RISER. TRUCK OK VOLTAGE OK CREW REQ, POWER RESTORED FOR NOW RELEASED BY CREW 078S09/CREW LOADING XFMR/FETR1530/VEM/OPENED XFMR 1245/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1413/PLEASE CLOSE TICKET/THANKS/VEM//DUPE IN HOIS //COD 4 IDC XXXX
11429 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2011-09-20 13:34 | 2011-09-20 13:43 | 64 | 9 | 4889051 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ROTEN WIRE BROKE WHILE CREW WAS WORKING TO REPLACE POLE IDC XXXX
11430 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-12-12 05:22 | 2010-12-12 05:30 | 72 | 8 | 65487-1 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WHEN TRIED TO CLOSE LINE FUSE AT POLE 249-91 IN POWERON ORDER 65434-1 A BAD CUTOUT CAUSED THE FUSE ON 250-116 TO OPEN UP AGAIN. // OPEN 249-91 TO ISOLATE BAD CUTOUT AND CLOSED IN 250-116 @ 0530 VER/TOM IDC XXXX
11431 | Hazard | 3302703 | HAZARD | HAZARD | 2008-12-22 09:21 | 2008-12-22 10:09 | 12 | 48 | 62380-1 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3302703//FUSE BROKE//REPLACED FUSE RELEASED BY CREW 077H02/VER/CRB L3/KEP IDC XXXX
11432 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2020-05-29 06:15 | 2020-05-29 08:39 | 4 | 144 | 4925971 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER @ 38830070A10092
11433 | South Williamson | 3411401 | DEWEY | INEZ | 2011-02-17 14:12 | 2011-02-17 15:00 | 12 | 48 | 58595-1 | 576 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT UP AT XFMR ON POLE 744-52//GOING TO REPAIR//RESTORED AT 15:00/COMPLETE//EM COD-12 ISO TF 38830744A20052 VER/HFP L3/HFP IDC XXXX
11434 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-11-03 10:57 | 2019-11-03 15:45 | 2 | 288 | 4286891 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout/ power restored 1445
11435 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-12-28 12:36 | 2009-12-28 15:48 | 3 | 192 | 61160-1 | 576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | REPLACED PADMOUNT TRANSFORMER AND RESTORED POWER , CHECKED VOLTAGE JKC
11436 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2018-02-19 13:49 | 2018-02-19 15:44 | 5 | 115 | 4861561 | 575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT OFF
11437 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-01-17 23:13 | 2010-01-18 08:48 | 1 | 575 | 55682-1 | 575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD. R MARCUM WILL WORK IN THE MORNING//COD 1// VER/DBM IDC XXXX
11438 | South Williamson | 3411401 | DEWEY | INEZ | 2011-09-05 07:35 | 2011-09-05 17:10 | 1 | 575 | 4814921 | 575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | XFMER FUSE OPEN CHECKING NOW.INSULATOR BROKE ON RIDE AROUND BRACKET CREW INROUTE RELEASED BY CREW 076H06 VER/HFP L3/HFP IDC XXXX
11439 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-10-25 09:45 | 2010-10-25 11:40 | 5 | 115 | 62891-1 | 575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE ON 356-71 FUSE OUT ON, BAD INSULATOR 356-76 VER/KEP L3/KEP IDC XXXX
11440 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-06-10 06:13 | 2013-06-10 15:47 | 1 | 574 | 4248211 | 574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | TALKED TO CUSTOMER INFORMED THEM TO TURN OFF THE MAIN BREAKER AND WE WOULD GET SOMEONE THERE WHEN THEY COME ON THE MORNING SHIFT 30/6 SEC. POLE ROTTEN AND FELL OVER INTO TREES. NEED 15KVA XFORMER AND ROLL OF 2/3 SERVICE DROP. NEED YARD DOG AND MAN TREE CREW. NO TRUCKS TO POLE. RELEASED BY CREW 078S01 RELEASED BY CREW 078H02 ///VER/CRB L/3 CRB
11441 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-02-23 11:41 | 2019-02-23 21:15 | 1 | 574 | 4848711 | 574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRF IS OUT, WILL REPLACE porcelain CUTOUT AND RE-FUSE////////MADE NECESSARY REPAIRS & RESTORED, ALL OK AFTERWARDS/ restored 2115
11442 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-10-27 11:33 | 2014-10-27 16:20 | 2 | 287 | 4663981 | 574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR. DUTY SUPERVISOR NOTIFIED - CREW IS IN WEST LIBERTY AND WILL START THIS WAY ASAP. RELEASED BY CREW 076S02// REPAIRING NOW// COD 2//VER/ ADH
11443 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-09-20 09:33 | 2018-09-20 14:20 | 2 | 287 | 4134011 | 574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//NO ANSWER// BROKEN CUTOUT ON POLE 794-21.NEED FLAGGING CREW.RESTORED POWER AT 14:20
11444 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-07-26 12:06 | 2012-07-26 21:40 | 1 | 574 | 4832121 | 574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE BLOWN ON MIDDLE TRANSFORMER IN BANK, REPLACED FUSE AND CHECKED VOLTAGE, WAS ONLY GETTING 159 VOLTS 240-480 FOUR BUSHING TRANSFORMER 250 KVA CAN GET TRUCKS TO POLE, LEFT FUSE IN SO THEY COULD RUN AC THEY SHUT 3-PHASE DOWN RELEASED BY CREW 078H18//FETR 21:00 PRT//RISERS WILL NOT WORK IN NEW TRANSFORMER NEW FETR 23:00//POWER RESTORED AT 21:40 SEND COPY TO ENG TO CHECK LOAD ON BANK AND CLOSE TKT PRT///// VER/DBM IDCC PN164 XXXX
11445 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-01-07 19:18 | 2015-01-07 20:40 | 7 | 82 | 4915351 | 574 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY RISER BURNT OUT OF CAN. REPAIRED 38830116A02005 VER/CRB L3/HFP HFPC MCCDL
11446 | Whitesburg | 3401301 | FLEMING | NEON | 2022-12-30 21:05 | 2022-12-30 22:27 | 7 | 82 | 4380241 | 574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral had burnt in two. spliced neutral and redid connections. power restored
11447 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-12-24 08:43 | 2008-12-24 13:30 | 2 | 287 | 63308-1 | 574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR# 27799522 ///POLE FIRE 38830207000101, POLE IS BURNT PRETTY BAD, NEED CREW, 1 CUSTOMER OUT, CORNER OF STINSON RD AND EASTERLING BR. THIS IS RELATED TO ORDER 63349-1 WHICH IS THE OUTAGE TO REPLACE THIS POLE & ISOLATE TROUBLE. OPENED SOLID BLADE ON 207-97 TO ISOLATE TROUBLE....CLOSED IN ON 207-97 @ 13:30 L3/HFP IDC XXXX
11448 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-07-02 09:08 | 2018-07-02 12:19 | 3 | 191 | 4704031 | 573 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired secondary connections,,,only 3 customers affected
11449 | Hazard | 3302704 | HAZARD | KENMONT | 2020-01-12 08:07 | 2020-01-12 17:40 | 1 | 573 | 4281801 | 573 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | secondary connection broken on pole 296d1-73 truck accessible Released by crew 077E02 power restored at 17:40/ ISO 37830296D10073/ COD 1
11450 | Hazard | 3311103 | STINNETT | WENDOVER | 2021-11-30 18:29 | 2021-11-30 21:40 | 3 | 191 | 4136061 | 573 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Cut-out door burned up. Power restored @ 21:40
11451 | Hazard | 3309302 | VICCO | JEFF | 2013-11-30 16:55 | 2013-11-30 19:18 | 4 | 143 | 4089891 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD === REPLACED === POWER OK === OPEN SIDE TAP AT 18:50 CLOSED AT 19:10 (SEE 4090081)//COD 4// VER/DBM
11452 | Hazard | 3308002 | JACKSON | PANBOWL | 2019-01-02 00:45 | 2019-01-02 10:17 | 1 | 572 | 4621531 | 572 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | will work in the am 01/02/19 per latenight guidelines bad splice on trailer pole
11453 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-01-24 20:57 | 2016-01-25 01:43 | 2 | 286 | 4648091 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT HELP COMING
11454 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-02-15 20:07 | 2014-02-15 22:30 | 4 | 143 | 4391561 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK APPEARS TO HAVE BROKEN OR MELTED OUT. CHANGED OLD TYPE CUTOUT AND WILL ATTEMPT TO CLOSE. RESTORED @ 22:30. 25 KVA NEEDS TO BE UPGRADED AND I WILL SEND A JOB TO ENGINEERING. SH VER/ARN
11455 | Paintsville | 3401802 | INDEX | HOSPITAL | 2019-03-18 09:12 | 2019-03-18 11:35 | 4 | 143 | 4996201 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE OUT ON POLE 38830654D00280 COD-4 Fuse link appears to have broke. Restored @ 11:35. oo Please add 25T line fuse on 654-280 to maps oo sh ¦¦ ENTERED MD - HFP
11456 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-03-10 09:54 | 2011-03-10 14:40 | 2 | 286 | 52762-1 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BURNT TOP OF POLE OFF MANUAL VER/KEP IDCC PN253 XXXX
11457 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-05-15 11:32 | 2014-05-15 13:55 | 4 | 143 | 4708261 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR. FUSE BLOWN // WILL REFUSE // CUTOUT BAD ON 37830024B11252// HOT TAP LEAD BURNED OFF L/F ON 37830024B10028 // WILL REPAIR BOTH////REPAIRS MADE/// POWER IS RESTORED @ 13:55 // 5-15-14 VER/SEF
11458 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-09-25 17:54 | 2012-09-25 22:40 | 2 | 286 | 4087301 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE DOOR BURNT OUT ON POLE 37820011B00039 GOING TO REPLACE AND REFUSE POWER RESTORED @ 22:40//COD 1// VER/DBM IDCC FEC49 XXXX
11459 | South Williamson | 3411401 | DEWEY | INEZ | 2011-12-15 16:56 | 2011-12-15 19:19 | 4 | 143 | 4180731 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT. REPLACED CUTOUT. COD-4 ISO PO @ 38830790A00037 VER/HFP L3/HFP IDC XXXX
11460 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-05-02 08:39 | 2015-05-02 13:25 | 2 | 286 | 4383491 | 572 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON UG FROM 206A-2556 TO 2560,NEED LINE CREW TO PLACE POWER TEMP FOR 2 METERS 533582929 & 533516995 UNTIL UG REPAIRS MADE.BT RELEASED BY CREW 078S05 VER/CRB
11461 | Hazard | 3303902 | LESLIE | WOOTON | 2017-12-23 08:02 | 2017-12-23 10:25 | 4 | 143 | 4665971 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | loop on pole 37830366B00171 pulled down close to pole. fixed loop and restored power at 10:25
11462 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-05-30 09:28 | 2015-05-30 19:00 | 1 | 572 | 4484511 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WE HAVE A BAD UNDERGROUND, MEASURED VOLTAGE AT XFMR 125V EACH HOT LEG 250V ACROSS IN BASE 45V AND 125V. NEED 3 MAN CREW BUCKET ACCESSABLE. RELEASED BY CREW 077S08.. UNDERGROUND REPLACED POWER RESTORED 1900.// VER/ ADH
11463 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-03-24 10:19 | 2013-03-24 15:05 | 2 | 286 | 4951341 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN STEP DOWN TRANSFORMER AT 11:20. DUE TO POLE 164-56 BEING ALMOST BURNT INTO AT BRACES. NEED 2 MAN CREW MATERIAL HANDLER BUCKET TRUCK 8 FOOT CROSS ARM CUTOUT AND ARRESTER SMALL BRACES. WE HAVE REPAIRS MADE EVERYTHING OK.//COD 6// VER/DBM IDCC TOF 1120, CDC83, PN460, CNT6 XXXX
11464 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-21 22:08 | 2015-02-22 07:40 | 1 | 572 | 4068151 | 572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OF . NEED LINE CREW , NEED BIG BUCKET , POLE TOP EXT. , INSULATOR , CUTOUT & TBRACKET . 7200 VOLTS . RELEASED BY CREW 075H04. VER/SEF
11465 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2021-09-24 02:00 | 2021-09-24 11:30 | 1 | 570 | 4286071 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines/// Fuse had broke in cutout door, replaced and restored @ 11:30
11466 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2017-08-22 10:51 | 2017-08-22 15:36 | 2 | 285 | 4285831 | 570 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEND BACK RELEASED BY CREW 078S08SEND BACK SERVICE BURNT INTO IN CUST TREES REMOVED 80FT. 4/3 SERVICE INSTALLED 80 FT. 2/3 SERVICE VER/AWD
11467 | Hazard | 3309003 | JEFF | VIPER | 2014-11-14 15:45 | 2014-11-14 16:15 | 19 | 30 | 4728111 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPENED L/F 37830345D00026 @ 1545 TO REPLACE POLE 37830370000013//COD 19 VER/CRB VER/DKG L3/DKGXXXX
11468 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2018-12-11 12:50 | 2018-12-11 14:25 | 6 | 95 | 4552911 | 570 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | customer had 257 volts on 1 leg,ck conection in meter base and top of service pole,found netural connection on transformer pole,repaired netural connection fix the problem,customer states has equiement damage,computer ,stove ect. L3/HFP
11469 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2009-07-04 18:29 | 2009-07-04 20:04 | 6 | 95 | 64881-1 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402204// RISER WIRE FELL OUT OF HOT LINE CLAMP. REPLACED HOT LINE CLAMP EVERYTHING OK.//COD 6//ONLY PHASE A WAS OUT// VER/DBM IDC XXXX
11470 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-09-23 09:43 | 2012-09-23 10:40 | 10 | 57 | 4080081 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP ON POLE 38830070A20605A--ONLY B PHASE OUT COD-10 ISO PO @ 38830070A20605 VER/HFP L3/HFP IDC XXXX
11471 | Hazard | 3303901 | LESLIE | HYDEN | 2015-02-07 11:03 | 2015-02-07 14:13 | 3 | 190 | 4998181 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR C/O BROKE, WILL NEED 1-A AND BIG BUCKET POLE 37830363000118XFMR C/O BROKE, WILL NEED 1-A AND BIG BUCKET//// C/O CHANGED POWER RESTORED VER/CRB L3/HFP XXX
11472 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-06-22 03:13 | 2021-06-22 12:43 | 1 | 570 | 4788311 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | We have a bad Transformer on pole37830047B20592,Crew Required,(25 KVA 12 KV) Truck Accessable. Released by crew 074S01
11473 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2014-12-26 13:10 | 2014-12-26 17:55 | 2 | 285 | 4885841 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR VOLTAGE DROP 113-225 @ XFM 38830207A00141R WHEN CUST TURNS FURN ON,NEED TO REPLACE 25KVA NO TRUCK RELEASED BY CREW 078S05//UPGRADED XFMR 25KVA AND #2RISERS---VOLT 124/124/248---CUST SAID ALL IS GOOD NOW---PWR RESTORED @ 17:55---TBL TKT COMP VER/CRB
11474 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-05-28 18:30 | 2014-05-28 23:15 | 2 | 285 | 4945721 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | BROKEN XFMR FUSE.CHG FUSE..
11475 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-02-19 07:35 | 2015-02-19 10:45 | 3 | 190 | 4041601 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 376-45 RELEASED BY CREW 077S11 REPLACED 15 KVA WITH 24 KVA ALSO CUTOUT 19.9//COD 3 VER/HFP L3/HFP
11476 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-02-29 12:55 | 2012-02-29 14:30 | 6 | 95 | 4518121 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 116-198 BAD LA SEND NOTE TO RAYBURN NO TRUCK POLE 116-762 40T IDC XXXX
11477 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-10-09 17:39 | 2009-10-09 19:33 | 5 | 114 | 52354-1 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/KEP L3/KEP IDC XXXX
11478 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-05-14 04:58 | 2014-05-14 06:33 | 6 | 95 | 4697731 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | G.O.A.B. SWITCH IS BAD @ 37820098000730// OPENED SWITCH & TAGGED /// CLOSED N.O. ON 37820074000190 @ 6:33 AED CREATED SW NEEDS REPLACED ASAP. VER/DP
11479 | Hazard | 3302703 | HAZARD | HAZARD | 2009-09-29 16:15 | 2009-09-29 17:50 | 6 | 95 | 56421-1 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BROKE ON FUSE RISER AT POLE 37830272D20437.//VER/CRB
11480 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2012-12-14 09:02 | 2012-12-14 09:40 | 15 | 38 | 4468981 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 21-6649 15T TRANS FUSE BROKE COD-15 ISO TF 38830021D26649 VER/HFP L3/HFP
11481 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-10-27 07:33 | 2021-10-27 12:18 | 2 | 285 | 4024081 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse had melted out, refused txmf apr at 1218 close ticket
11482 | Hazard | 3308001 | JACKSON | S.JACKSON | 2016-02-29 12:30 | 2016-02-29 14:24 | 5 | 114 | 4788301 | 570 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, UG | BAD SPLICE ON UNDERGROUND/ OPENED TRANSFORMER TO FIX PROBLEM 1409-1428// DUPLICATE IN HOIS/ ISO 38831084A00174/ COD 5
11483 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2020-07-16 12:00 | 2020-07-16 12:57 | 10 | 57 | 4170601 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | door burnt up. replaced. pls close. tre
11484 | Hazard | 3302703 | HAZARD | HAZARD | 2010-08-11 22:55 | 2010-08-11 23:25 | 19 | 30 | H53113-1 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR FAILED ON SECONDARY RISER OPENED XFMR AT 22:55 RESTORED COMPLETE AT 23:25//VER/CRB IDCC DUP TO OPEN TRANSFORMER XXXX
11485 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-04-19 15:15 | 2012-04-19 18:25 | 3 | 190 | 4688241 | 570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED PRC CREW--OPENWIRE SECONDARY DOWN TRUCK TO POLE--#2ACSSR PRIMARY NEUTRAL DOWN AND ONE #4 CU HOT LEG DOWN RELEASED BY CREW 078S07/FETR 19:00 J. HEMLEPP/REPAIRS COMPLETE/POWER REST.@ 18:25//078H05 COD-3 ISO TF 38830093B00027 VER/HFP L3/HFP IDC CHANGED FROM UNKNOWN XXXX
11486 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2022-12-28 12:47 | 2022-12-28 14:41 | 5 | 114 | 4370961 | 570 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 1/0 bad ug/need power temp if available/crew reqd. Released by crew 078S04
11487 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-04-22 18:17 | 2011-04-23 03:45 | 1 | 568 | 62312-1 | 568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR - 39672207 -...FOUND BAD TRANSFORMER WHEN DOING PARTIAL RESTORATION ON PHILLIPS FRK. OUTAGE. //VER/GAH IDC XXXX
11488 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-07-14 16:29 | 2019-07-14 18:51 | 4 | 142 | 4707561 | 568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE
11489 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-07-16 17:43 | 2011-07-16 18:54 | 8 | 71 | 4554291 | 568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//VER/CRB IDC XXXX
11490 | Pikeville | 3421001 | BREAKS | CITY | 2014-07-14 08:34 | 2014-07-14 10:56 | 4 | 142 | 4238481 | 568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ON POLE 220-477, CREW ENROUTE COD 4// VER/ADH
11491 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-03-17 10:37 | 2016-03-17 15:21 | 2 | 284 | 4858501 | 568 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CREW REQUIRED BAD SECTION OF UNDERGROUND SECONDARY BETWEEN ADDRESS 310 AND 523 RELEASED BY CREW 078S03 OPENING SECONDARY LINE FUSE ON 206-2552 1445. WILL NOTIFY CUSTOMERS..OPENED TRANSFORMER AT 14:55, CLOSED IN AT 15:21..NEED WORK ORDER TO REPLACE THE SECONDARY SENT TO PAT STAMPER.ISO 38830206A42552 COD 9 VER/AWD IDCC NEED SECOND OUTAGE CNT9 FP2552 XXXX
11492 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2013-06-12 06:10 | 2013-06-12 10:54 | 2 | 284 | 4261731 | 568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / WILL CHECK AT REGULAR TIME.BROKEN XFMR CUTOUT..CAN REPLACE.//.BAD INSULATOR ON MIDDLE PHASE ALSO.HAS BURNT CROSSARM.WILL NEED CREW.HAVE CALLED J REED.//.OPENED SWITCHES ON POLE 264 (NOT ON MAP).REPLACED CUTOUT & INSULATOR.CLOSED SWITCHES @ 09:47..XFMR ON 941D284 IS BAD.CREW GETTING ONE TO REPLACE.SEND TICKET TO J REED RELEASED BY CREW 080S01.REPLACED TRANSFORMER VER/KEP IDC XXXX
11493 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-01-03 17:21 | 2014-01-03 22:05 | 2 | 284 | 4225781 | 568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA//CREWS GATHERING MATERIALS TO REPLACE//COD 2//CREWS REPLACED XFMR// VER/DBM
11494 | Hazard | 3303902 | LESLIE | WOOTON | 2008-02-14 09:38 | 2008-02-14 12:00 | 4 | 142 | 63151-1 | 568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3303902// UNKNOWN AT THIS TIME 10-T LINE FUSE LOOKED LIKE FUSE BROKE NOT BLOWN//COD 4// VER/DBM IDC XXXX
11495 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-07-11 09:52 | 2017-07-11 10:00 | 71 | 8 | 4104791 | 568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW OPENING (A) PHASE RECLOSER ON POLE 39830901D37011 (COD: 71) FOR APPROXIMATELY 10 MINUTES TO MAKE EMERGENCY REPAIRS AT POLE 39830902B00035.OPENED A PHASE ONLY AT 09:52, CLOSED IN AT 10:00,,,BLR RELEASED BY CREW 078H07 VER/AWD SJG
11496 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-07-31 12:59 | 2012-07-31 14:20 | 7 | 81 | 4870861 | 567 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION BURNT OPEN ON XFMR POLE. WILL HAVE TO OPEN BANK OF XFMRS ON 785-1086 FOR 20 MINUTES TO REPLACE SEC RISER AND MAKE CONNECTION. OPENED XFMRS @ 14:05, MADE REPAIRS AND CLOSED XFMR BANK @ 14:20. SH//COD 7 // ALL CUSTOMERS WERE SINGLE PHASING BEFORE OPENING THE XFMR// VER/DBM IDC XXXX
11497 | Whitesburg | 3312901 | JENKINS | KONA | 2018-09-06 08:18 | 2018-09-06 11:27 | 3 | 189 | 4047741 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | middle phase line fuse cutout bad on pole 403-236, /middle phase line fuse cutout bad on pole 403-236, replaced cutout restored power at 11:27..
11498 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2014-03-10 14:04 | 2014-03-10 15:25 | 7 | 81 | 4465331 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER AT 14:30 TO MAKE REPARS//COD 7// VER/DBM
11499 | Hazard | 3303901 | LESLIE | HYDEN | 2011-10-18 13:54 | 2011-10-18 17:03 | 3 | 189 | 4994831 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA RELEASED BY CREW 077S01 ///VER/CRB IDC XXXX
11500 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-10-13 17:11 | 2018-10-13 20:20 | 3 | 189 | 4249401 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required with yard dog to set anchor to straighten pole 224-61 so can chg cutout Released by crew 078S03,cutout replaced all cust restored @ 2020,send copy to tech for windstream to relocate pole out of slip.bt//SENT TO TECH L3/HFP
11501 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-03-29 13:04 | 2014-03-29 14:25 | 7 | 81 | 4533911 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /FUSE IS OPEN ON 525-161 PATROLLING LINE, ISOLATED BAD 19.9 CUTOUT ON INACTIVE XMF 525-214 APR AT 1425 CLOSE TICKET. VER/CRB
11502 | South Williamson | 3411401 | DEWEY | INEZ | 2014-08-24 00:01 | 2014-08-24 03:10 | 3 | 189 | 4416221 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FUSE DOOR BURNT UP. DONT HAVE ONE ON TRUCK SO IM GOING TO AREA SERVICERS HOUSE TO GET ONE OFF HIS TRUCK. REPLACED CUTOUT AND RESTORED @ 3:10. SH VER/ARN
11503 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2020-08-19 11:12 | 2020-08-19 14:21 | 3 | 189 | 4346721 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Hot leg and neutral burndt into on a service drop coming off pole 48-A3-381, will be replacing drop, will have 3 customers out while making repairs, will keep track of times. Opened 3 customers @1330, replaced drop restored @1421.
11504 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-05-31 01:54 | 2009-05-31 05:03 | 3 | 189 | 52407-1 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE IS BLOWN ON POLE 376-66. I AM NOT SURE OF THE CAUSE BUT THERE ARE SOME TREE LIMBS THAT MAY BLOWN INTO RISER. I AM GOING TRIM TREES AND REFUSE. TRANSFORMER IS BURNED UP. I NEED ONE MAN, MATERIAL HANDLER AND A 25 KVA (19.9) VER/KEP L3/KEP IDC XXXX
11505 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-10-30 11:12 | 2015-10-30 14:21 | 3 | 189 | 4396841 | 567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DISPATCH COULD NOT GET AHOLD OF CUSTOMER XFMR FUSE OUT WILL REFUSE. BAD 25 KVA 7200/ 120/240 SINGLE BUSHING. HAVE CALLED TIM HALL & HE IS TO SEND MATERIAL HANDLER & XFMR./ ISO 37830048C30017/ COD 3/ VER/BOW
11506 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-07-15 04:45 | 2014-07-15 09:28 | 2 | 283 | 4246551 | 566 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PAUL HICKMON OPEN FUSE ON POLE 1062-13 TO SAFELY REMOVE TREES ESTIMATED 3 HRSLOOKE LIKE OLD FUSE JUST BROKE REFUSED XMF APR AT 0928 CLOSE TICKET
11507 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-07-04 13:04 | 2018-07-04 17:47 | 2 | 283 | 4721451 | 566 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | bad 50 kv urd xfm (38830045B20291) truck ok Released by crew 078H01/crew on site/FETR 1830/vem/repairs made and all cust restored 1747/please close ticket/thanks/vem
11508 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-05-06 06:38 | 2013-05-06 16:03 | 1 | 565 | 4077281 | 565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE 42-F-85, BURNING, OPEN UP LINE FUSE ON POLE 42-F-84, GROUNDED AND TAGGED AT THIS POLE, ABOUT 3 FT OF TOP OF POLE 42-85 IS BURNTED ALMOST INTO, HAVE FIRE OUT. WELL NEED TO SEND L/C AND TECH TO WRITE JOB TO REPLACE THIS 402 POLE. NEED NEED CUTOUT AND ARRESTOR, CAN USE TRUCK, HAS A 250 KVA TRANSFORMER ON POLE HOLD TAGS PLACED FOR DDC - CONTACT DDC UPON ARRIVAL COD-1 ISO LF 38830042000084 VER/HFP L3/HFP IDC XXXX
11509 | Pikeville | 3413402 | GARRETT | LACKEY | 2020-05-23 04:10 | 2020-05-23 13:35 | 1 | 565 | 4890211 | 565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25kva csp xfmr bad, need cutout lightning arrester, fiberglass bracket, big bucket, flaggers..25 kva xfmr..3 man line crew.p-135-50.1st pole past pine tree hollow on left.. Released by crew 076S01//all repairs made power restored at 13:35
11510 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-11-24 16:27 | 2008-11-24 18:20 | 5 | 113 | 51692-1 | 565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400301// NOT ABLE TO GET TRUCK TO POLE I WILL BE CHANGING BAD CUTOUT. CHANGED CUTOUT EVERYTHING OK.//VER/CRB IDC XXXX
11511 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-05-29 19:57 | 2021-05-29 21:50 | 5 | 113 | 4648311 | 565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required// fuse link // cod 5
11512 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2021-12-26 23:35 | 2021-12-27 09:00 | 1 | 565 | 4228641 | 565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout at 110-42. power restored 09:00
11513 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-08-25 07:13 | 2018-08-25 09:06 | 5 | 113 | 4998471 | 565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired connections
11514 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-09-26 12:07 | 2014-09-26 13:41 | 6 | 94 | 4530661 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | INSTALLED POLE 1126-55 & SECONDARY 38831126B10027 MAINTENANCE-UPGRADE ELECTRICAL GRID/// 1126-22 REPALCE TRANSFORMER// VER/BOW
11515 | Hazard | 3303901 | LESLIE | HYDEN | 2017-10-25 08:36 | 2017-10-25 10:10 | 6 | 94 | 4496301 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 7200 CUTOUT/ ISO 37830387C00020/ COD 6/ VER/BOW L3/HFP XXXHFP
11516 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-07-01 14:37 | 2010-07-01 17:45 | 3 | 188 | 61327-1 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED CANT REACH WITH MY BUCKET BUT CAN WITH BIG BUCKET ON RIGHT AS YOU GO UP GRAHN HILL/SEND TO P. TOLLIVER RELEASED BY CREW 078S03//REPLACED 2 CUT-OUTS ONE WAS BROKEN AND ONE CRACKED COMPLETE AT 17:45//P TOLLIVER 38830251000121 COD-3 IDC XXXX
11517 | Hazard | 3310502 | HADDIX | CANOE | 2021-04-28 17:48 | 2021-04-28 22:30 | 2 | 282 | 4489991 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout 19.9,truck acess with flaggers Released by crew 077S07 repairs made and line fuse closed at 22:30
11518 | Pikeville | 3402002 | KEYSER | STONECOAL | 2019-11-07 19:18 | 2019-11-07 22:26 | 3 | 188 | 4008611 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse had melted out @1129-C-84, refused @2226.
11519 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-11-11 22:16 | 2019-11-11 23:50 | 6 | 94 | 4021841 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changed cutout & arrester/ ISO 38830117A00202/ COD 6 L3/HFP
11520 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-06-18 06:33 | 2012-06-18 11:15 | 2 | 282 | 4925211 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT STS CANT SEE FUSE FROM GROUND AND BUCKET WONT REACH IT TO REFUSE TRANSFORMER, CALL RIGHT OF WAY CREW TO COME AND CUT OUT CLOSED TRANSFORMER FUSE ON BANK AND STILL NO POWER, GOT CREW COMMING TO TAKE OUT C. L. FUSE TO SEE IF THAT IS BAD ///VER/CRB L/3 CRB IDC XXXX
11521 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2022-01-02 10:57 | 2022-01-02 20:21 | 1 | 564 | 4260511 | 564 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | crew required ,,1/0 secondary pole to pole over creek neutral sleeve pulled out ,,no truck Released by crew 078S05///Complete BR
11522 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2021-09-03 12:18 | 2021-09-03 17:00 | 2 | 282 | 4206881 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Pole 38830118C20015, Bad 15kva 7200, 480 3Ph 3 Wire Delta, Open bank, Grounded hot leg on bad can. Double bushings, three secondary bushings. Trucks to pole, Need flaggers along 23 with sign board. Send to Luke Mccoy Released by crew 078S02 crew on site FETR 16:50 LRM customer exuipment leftxfmr bankopen
11523 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-10-25 12:10 | 2013-10-25 16:52 | 2 | 282 | 4962591 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF, WILL NEED TO REPLACE, CREW ON WAY /// ENTERED MD COD-2 ISO LF 37830204000064 VER/HFP L3/HFP
11524 | Hazard | 3309003 | JEFF | VIPER | 2021-03-16 10:13 | 2021-03-16 11:47 | 6 | 94 | 4339941 | 564 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on pole
11525 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-12-09 11:48 | 2008-12-09 16:30 | 2 | 282 | 55728-1 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SEC. POLE DOWN, 35 CLASS 5. POLE # 37830191D00222 RELEASED BY CREW 074S08 CREW ON SITE R RAY WILL SET NEW POLE EST TIME ON 1800//TIME ON WAS 1630 VER/KEP L3/KEP IDCC FP NULL XXXX
11526 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-04-10 10:22 | 2009-04-10 13:30 | 3 | 188 | 50977-1 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CRFEW REQUIRED REPLACING CUTOUT DOOR//3000201//VER/CRB IDCC FEC49 XXXX
11527 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-07-18 10:03 | 2013-07-18 14:45 | 2 | 282 | 4547391 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830421C10357, WILL NEED BIG BUCKET & FLAGGERS. RELEASED BY CREW 077S11 POWER RESTORED@ 14:45 VER/SEF IDCC PN288 XXXX
11528 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-07-25 12:18 | 2016-07-25 14:39 | 4 | 141 | 4676981 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINEF IS OUT,NOTHING OBVIOUS,WILL RE-FUSE///////////LINE CUTOUT BROKEN,WILL HAVE TO REPLACE IT//////BIG BUCKET ENROUTE TO HELP////////REPLACED CUTOUT&RESTORED/ ISO 38821105C00021/ COD 4/ VER/BOW
11529 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-12-30 08:22 | 2010-12-30 10:43 | 4 | 141 | 56945-1 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 CUTOUT ON BANK BAD WILL CHANGE---CHANGED 2 BAD C/OS VER/KEP L3/KEP IDC XXXX
11530 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-08-22 07:23 | 2013-08-22 10:31 | 3 | 188 | 4692661 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT CREW TO CHANGE CUTOUT AND ARRESTOR VER/KEP
11531 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2022-11-04 02:18 | 2022-11-04 11:42 | 1 | 564 | 4096251 | 564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required ,,bad 25 kva xfr ,,278-207,,truck to pole Released by crew 078S05//arrived RM power on at 11:42 please close tic RM
11532 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-09-08 01:48 | 2018-09-08 11:11 | 1 | 563 | 4056491 | 563 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Crew required Bolt that holds the riser in top of transformer burnt in two. Possible lightning. Need new bolt. Bring new transformer just in case. 25kva 7200 120/240. Small service truck with jib to pole. Released by crew 078H04/crew on site/FETR 1145/vem/repairs made and all cust restored 1111/please close ticket/thanks/vem
11533 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-05-05 03:58 | 2012-05-05 13:20 | 1 | 562 | 4746981 | 562 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 SERVICE NEUTRAL BURNT INTO WILL NEED TO CHANGE SERVICE DROP OUT RELEASED BY CREW 077H142/3 SERVICE NEUTRAL BURNT INTO WILL NEED TO CHANGE SERVICE DROP OUT FOUND NEUTRAL WAS BROKEN AND #12 DD LIGHT WIRE WAS WHAT HAS BEEN MAKING NEUTRAL UP AND IT FINALY BURNT INTO///VER/CRB L/3 CRB IDC XXXX
11534 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2017-02-25 10:09 | 2017-02-25 14:50 | 2 | 281 | 4421201 | 562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830452000029 BAD 7200 C/O-CREW REQ/ ISO 38830452000029/ COD 2 CODC*** MD DONE/ VER/BOW L3/HFP XXXHFP
11535 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-06-24 14:09 | 2011-06-24 18:50 | 2 | 281 | 4410491 | 562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND ROW BAD TOO == CHANGED CUTOUT AND CUT ROW === LINE SIZE NOT ON MAPS IT HAS A 20 T FUSE IN IT NEED TO BE PUT ON MAPS === CUT TREES AND REPAIRED CUTOUT == POWER OK//COD 2//MD FILED/// VER/DBM L3/WDH IDC XXXX
11536 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-03-01 09:34 | 2022-03-01 14:15 | 2 | 281 | 4555371 | 562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Repaired guy. Bad 25 Kva transformer. Replaced xfmr and restored @ 14:15. sh
11537 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-02-09 10:49 | 2018-02-09 15:30 | 2 | 281 | 4820361 | 562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Will address upon completion of switching. bad transformer changed transforer 10 csp to 25 kva
11538 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-06-12 23:13 | 2015-06-13 08:35 | 1 | 562 | 4562231 | 562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ POLE 293-95 NEED LINE CREW TO REPLACE RELEASED BY CREW 078S05//CREW TO WORK 1ST THING DURING DAYLIGHT HOURS//COD 1 VER/SEF
11539 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-07-01 12:03 | 2021-07-01 14:00 | 7 | 117 | 4835261 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester on p-703-84.line back on at 14:00 Released by crew 076S01
11540 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-04-03 09:53 | 2016-04-03 13:00 | 3 | 187 | 4041171 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, BROKE CUTOUT, WILL NEED T-BRK, BIG BUCKET AND ONE MAN AND CUTOUT. 19.9 KV//ARCOSED R.RICE OUT//XFMR FUSE OUT, BROKE CUTOUT, WILL NEED T-BRK, BIG BUCKET AND ONE MAN AND CUTOUT. 19.9 KV. POWER RESTORED VER/CRB
11541 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-12-21 08:36 | 2015-12-21 17:57 | 1 | 561 | 4547521 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFORMER ON POLE 425-69, ALSO TWO SPANS 6A COPPER NEUTRAL DOWN FROM POLE 425-69 TO 425-67 NO TRUCKS TO POLES. NEED LINE CREW. RELEASED BY CREW 078S01/CREW LOADING MATERIAL/DIFFICULT LOCATION/FETR1800/VEM/OPENING LINE FUSE 425-10 @1555/APROX TWO HOUR OUTAGE/VEM/REPAIRS MADE AND ALL CUST RESTORED 1757/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830425000069/ COD 1/ VER/BOW
11542 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-04-06 07:02 | 2016-04-06 10:09 | 3 | 187 | 4056631 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR F IS OUT,WILL RE-FUSE//////////RE-FUSED AND RESTORED,ALL OK .FUSE APPEARS TO HAVE BROKEN VER/CRB
11543 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2018-07-17 06:44 | 2018-07-17 09:51 | 3 | 187 | 4785521 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | tree fell last night 2 spans down and pulled neutral connection into in service. made repaires @ 9:40.//COD 3
11544 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-06-29 19:51 | 2015-06-29 20:42 | 11 | 51 | 4693841 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A/MADE AED/ADH// VER/ ADH
11545 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-09-08 18:35 | 2016-09-08 21:42 | 3 | 187 | 4878481 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 37830397000123 TRANS OPEN//MADE MDC TO SHOW CORRECT TRANS//.. REPLACED 25 KVA XFMR RESTORED POWER AT 21:42. VER/CRB
11546 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-12-26 11:26 | 2010-12-26 20:47 | 1 | 561 | 55789-1 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA 7.2KV TRANSFORMER, WILL BE MANUAL JOB...NEED 2 MEN AND LINETRUCK, 15 KVA TRANSFORMER. RELEASED BY CREW 077H01BAD 10KVA 7.2KV TRANSFORMER, WILL BE MANUAL JOB...NEED 2 MEN AND LINETRUCK, 15 KVA TRANSFORMER. ...ALL POWER RESTORED @ 20:47 HRS..P.HICKS VER/PDP CC 1 IDC XXXX
11547 | Whitesburg | 3312902 | JENKINS | JENKINS | 2014-01-07 11:03 | 2014-01-07 14:10 | 3 | 187 | 4250181 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR MADE OPS TO RELACE TOMORROW, OPS #52205871 RELEASED BY CREW 075H01// VER/DBM
11548 | Pikeville | 3402002 | KEYSER | STONECOAL | 2022-04-24 21:18 | 2022-04-25 00:25 | 3 | 187 | 4795911 | 561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50kva 7200 XFM, Paul Layne coming to help with repairs//cod 3//replace xfmr //
11549 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-12-11 14:38 | 2017-12-11 14:52 | 40 | 14 | 4639561 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | by pass cuout failing on sectionalizer 37820194C00082/ Opening recloser C Phase only to replace c phase cutout/ ISO 37820194C00264/ COD 40/// Opened recloser @14:38 to make repairs/// Repairs made closed recloser in @ 14:52 and restored service
11550 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-06-05 07:55 | 2014-06-05 09:05 | 8 | 70 | 4983201 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CHANGED OUT CUTOUT AND REFUSED LINE VER/CRB
11551 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-05-08 06:43 | 2012-05-08 08:35 | 5 | 112 | 4758351 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 37830201B00030, CHANGED CUTOUT, POWER RESTORED AT 08:35 AM VER/KEP IDC XXXX
11552 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-01-02 07:36 | 2019-01-02 12:16 | 2 | 280 | 4621701 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfm fuse blown will refuse/// Bad 7.2 25 KVA XFM /// No truck Released by crew 074S02 replaced xfmr on at 12:16 d sammons
11553 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2017-02-22 10:01 | 2017-02-22 10:21 | 28 | 20 | 4413801 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE AT POLE 38830331000062 IN BAD SHAPE, WILL NEED TO OPEN RECLOSER TO REPAIR SAFELY// RECL. OPENED AT 10:01 REPAIRS MADE TO CONDUCTOR LINE RESAG ..RECL RE ENERGIZED AT10:21 38830331000027 VER/AWD L3/HFP XXXHFP AJB
11554 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-07-25 11:20 | 2009-07-25 16:00 | 2 | 280 | 56504-1 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT WILL REFUSE AND SEE IF IT STAYS/ TRANSFORMER IS BAD FUSE CAME BACK OUT WILL CALL FOR HELP.//COD 2// VER/DBM IDC XXXX
11555 | Hazard | 3302704 | HAZARD | KENMONT | 2018-11-11 11:00 | 2018-11-11 11:20 | 28 | 20 | 4388911 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED L/F 37830296C20537 TO REPLACE BAD INSULATER//NO OUTAGE TILL L/F OPENED//COD 28//OFF 1100 ON @INSULATOR BROKE CAUSING PHASE TO HANG OUT IN MID AIR, REPLACED INSULATOR OPENED @ 1100 AND CLOSED @ 1120 Released by crew 077S01 L3/HFP
11556 | Hazard | 3420001 | SOFT SHELL | VEST | 2015-11-21 20:25 | 2015-11-21 21:45 | 7 | 80 | 4477351 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 133A-299 , BAD CUTOUT ON POLE 133-77 . CLOSED FUSE ON POLE 133A-299 @ 21:45 . BOTH TAPS ON POLE 133A-299 ARE PROTECTED BY FUSEON POLE 299. RELEASED BY CREW 075H04 MD FILED VER/KEP
11557 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-08-30 23:23 | 2016-08-31 08:43 | 1 | 560 | 4854161 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER CALLOUT GUIDELINES WILL WORK IN THE AM AT START OF NORMAL SHIFT === BAD CUTOUT ON TRANSF POLE REPLACED === POWER OK
11558 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-02-23 15:25 | 2011-02-23 16:45 | 7 | 80 | 60527-1 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE WAS OPENED COD 12//OPEDED A&B AT 1551 //1 PHASE DOWN,WILL REPAIR///////MADE REPAIRS AND RESTORED//VER/CRB IDCC CNT25 PH A INITIALLY OPEN XXXX
11559 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-11-11 19:30 | 2020-11-11 20:50 | 7 | 80 | 4665121 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had line fuse out on pole 37830158000107 and cutout broke on pole 37830158000097
11560 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-12-05 14:40 | 2014-12-05 16:00 | 7 | 80 | 4836301 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG ON UNDERGROUND SERVICE IS BAD1/0 UNDERGROUND //// CALLED TIM HALL AND IS GETTING CREW TOGETHER//NO OUTAGE TILL TRANS OPENED// OPENED TRANSFORMER @ 14:40 INSTALLED ADD-A-PHASE AND RE-DONE CONNECTIONS IN SUB-SURFACE BOX CLOSED TRANSFORMER BACK IN @ 16:00//// WILL COME BACK MONDAY AND DIG UP SERVICE VER/CRB L3/HFP
11561 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2016-06-29 16:33 | 2016-06-29 17:29 | 10 | 56 | 4502971 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OUT @ POLE37830223A00198 ,CLOSED FUSE @ 17:29 . FUSE WAS BROKE .COD 10LINE FUSE OUT ,CLOSED FUSE @ 17:29 . FUSE WAS BROKE . LINE FUSE FEEDING POLE 223-1266 VER/CRB
11562 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-01-15 20:00 | 2015-01-16 00:40 | 2 | 280 | 4938351 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TXMF, NEED TO BRING NEW CUTOUT AND ARRESTER ALSO RELEASED BY CREW 078S11,,,CREW ON SITE,,,UPGRADED XFMR, ALL POWER RESTORED VER/KEP L3/HFP XXX
11563 | Hazard | 3309302 | VICCO | JEFF | 2013-09-10 14:40 | 2013-09-10 15:20 | 14 | 40 | 4835811 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4835321 // CREW OPENED FUSE TO REPLACE BROKEN CUTOUT // COD-14 ISO LF 37830347D00105 VER/SEF L3/HFP IDC XXXX
11564 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-08-11 16:12 | 2015-08-11 18:04 | 5 | 112 | 4124741 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 809-428///GOING TO HAVE TO OPEN XFMER BANK ON POLE 809-428 TO MAKE REPAIRS///OPENED @ 17:50 AND CLOSED AT 18:04///COMPLETE BR// VER/ ADH
11565 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2022-04-17 09:20 | 2022-04-17 10:40 | 7 | 80 | 4771071 | 560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER//VOICEMAIL// Transformer cutout failed. Replaced and restored @ 10:40. sh
11566 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-02-18 12:44 | 2011-02-18 13:27 | 13 | 43 | 58853-1 | 559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SEND TO J HEMLEPP, ROTTEN CROSSARM ,NEED ARM BRACES INSULATOR AND PIN, AND OPEN WIRE SECONDARY SPACER FOR BROKEN MID SPAN TAP RELEASED BY CREW 078S07/ ARM OLD BUT NOT ROTTEN// NO NEED TO REPLACE.// REPLACED PRIMARY ON ARM & SEC. SPREADER. IN OPEN WIRE ////////REPAIRS COMPLETE J. HEMLEPP WR# 38862398 RELEASED BY CREW 078H05//VER/CRB IDC XXXX
11567 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-07-31 23:58 | 2008-08-01 00:11 | 43 | 13 | 63181-1 | 559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3001401//WR#25546665 VER/ARN IDC XXXX
11568 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-06-07 01:36 | 2010-06-07 10:55 | 1 | 559 | 58127-1 | 559 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | SAD, URD CABLE, PART POWER 1/0 CABLE WITH NO,2 BARE NEU, NEED CREW TO FIX CABLE OUR USE POWER TEMP, CAN WAIT UNTILL MORNING CREW TO WORK RELEASED BY CREW 078S09//NOTIFY RAYBURN OR MCCARTY AT STARTING TIME.// VER/DBM IDC XXXX
11569 | Whitesburg | 3312901 | JENKINS | KONA | 2018-11-08 08:13 | 2018-11-08 15:16 | 3 | 423 | 4378831 | 559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | underground service is bad, crew required please send ticket to George Whitaker Released by crew 077S12 set pole install temopary overhead tech to work job to replace underground // Opened xfer @ 1408 taking out the other 2 customers L3/HFP
11570 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-06-11 13:35 | 2014-06-11 22:54 | 1 | 559 | 4050111 | 559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED FUSE VER/KEP AJBC FEC57
11571 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-04-03 08:46 | 2015-04-03 18:05 | 1 | 559 | 4262981 | 559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE ON POLE 38821013A00247 AT THE FOOT OF THE MOUNTAIN IS IN. I TALKED TO SCOTT MCVICAR AND HE IS GOING TO CHECK ON THE COMPUTER TO SEE IF THE POWER IS ON. TRANSFORMER FUSE HAD BROKE, REPLACED THE FUSE AND POWER IS BACK ON./ ISO 38821013A00264/ COD 1 L3/DKGXXX
11572 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-08-19 08:43 | 2012-08-19 09:45 | 9 | 62 | 4951171 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 70-3032 BAD CUT OUT 12T FUSE REPAIRED VER/KEP IDC XXXX
11573 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2021-09-02 16:34 | 2021-09-02 19:40 | 3 | 186 | 4204081 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required no trucks/back upon hillside Released by crew 078S03 crew on site LRM fetr 22:50 all pwr restored19:40 pleasecloseticketLRM
11574 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2010-03-24 14:02 | 2010-03-24 15:35 | 6 | 93 | 53937-1 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER EXPLODED AND TOOK OUT XFMR FUSE. CUT TREES AWAY FROM POLE AND REPLACED CUTOUT AND ARRESTER. RESTORED @ 15:35. CLEANED UP PIECES OF BLOWN ARRESTER BEST I COULD. SH//VER/CRB IDC XXXX
11575 | Hazard | 3311103 | STINNETT | WENDOVER | 2009-06-02 20:51 | 2009-06-02 22:24 | 6 | 93 | H60505-1 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN SECONDARY 1BURNT DOWN OPENED AT 20:51 CLOSED AT 22:24 VER/KEP L3/KEP
11576 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2016-03-31 21:56 | 2016-04-01 02:35 | 2 | 279 | 4012811 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-5577 BAD CUTOUT TRUCK TO POLE SEND TO YOUNGMAN RELEASED BY CREW 078S08.. CREW ON SITE TO CHANGE CUTOUT ETR 300.. CUTOUT CHANGED AND XFMR RESTORED AT 0234.. PLEASE CLOSE TICKET..CY
11577 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-07-24 10:19 | 2010-07-24 13:25 | 3 | 186 | 56298-1 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN, VINES, C/O BROKE, ARRESTOR BAD ON POLE 37830481000021 ALSO LINE FUSE BLOWN ON POLE 481-89/// REPAIRS MADE, POWER RESTORED. VER/KEP L3/KEP IDC XXXX
11578 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-07-09 17:01 | 2015-07-09 21:40 | 2 | 279 | 4756121 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW RQD// 2 MEN, BROKE TRANSFORMER CUTOUT NO TRUCK RELEASED BY CREW 074H02 COMPLETE TICKET
11579 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-02-15 10:54 | 2010-02-15 14:00 | 3 | 186 | 57840-1 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CORRECT TRANSFORMER FOR CUSTOMER IS 38830118D10636--BAD TRANSFORMER TRUCK OK BESIDE FOODLAND PARKING LOT--NEED TO REPLACE WITH 25KVA AN NEW RISERS-SEND TO K BROWN RELEASED BY CREW 078S07//COD 3// VER/DBM IDCC PN634 XXXX
11580 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-12-15 11:58 | 2010-12-15 13:00 | 9 | 62 | H50404-1B | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE OUT ON STEPDOWN TRANS--FLAGERS AND HELP ON WAY //C PHASE STEP DOWN OUT 143 CUSTOMERS - CREW INSTALLING NEW STEPDOWN TR // ISO LF 37830149B00116 // OPENED OTHER STEPDOWN @ A PHASE 1049 & C AT 1158 ALL RESTORED @ 1300 THIS IS THE B PHASE OUTAGE 9 CUST VER/HFP L3/HFP IDC XXXX
11581 | South Williamson | 3411401 | DEWEY | INEZ | 2012-08-03 10:09 | 2012-08-03 14:48 | 2 | 279 | 4888211 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE LEG OF SECONDARY IS OUT//NEIGHBOR HAVING SME PROBLEM///CHECKED BACK TO XFMR///EVERTHING LOOKS GOOD///CREW COMING TO CHANGE OUT CSP XFMR/// RELEASED BY CREW 079S01// OPENED 2 LINE CUTOUTS AT 13:48//CHANGED XFMR// ALL CUSTOMERS RESTORED AT 14:48//COD 2// VER/DBM IDC XXXX
11582 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2017-04-10 17:21 | 2017-04-10 22:00 | 2 | 279 | 4635551 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT . BAD 25KVA 19.9 XFMR . NEED LINE CREW . XFMR IS MANUEL . RELEASED BY CREW 075H04 37830181D00094 VER/AWD L3/HFP XXXHFP
11583 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-10-01 20:28 | 2015-10-01 23:34 | 3 | 186 | 4300461 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS LECKING OIL 37.5 OR 50 KVA TRUCK TO POLE NEED CUTOUT/ ISO 38830116D00162/ COD 3/ 2324/ VER/BOW L3/HFP XXXHFP
11584 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-05-09 10:49 | 2008-05-09 11:51 | 9 | 62 | 59062-1 | 558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | 3MAN CREW L RAYBURN TO CONTACT V MULLINS POLETOP PIN NEEDED RELEASED BY CREW 078H04//3008701//VER/CRB IDC XXXX
11585 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-12-06 09:31 | 2010-12-06 18:48 | 1 | 557 | 63522-1 | 557 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE////////XFR IS BAD,CREW ENROUTE TO REPLACE,NOTE NEW FETR/////////REPLACED XFR,RESTORED,ALL OK AFTERWARDS//VER/CRB L3/SRA IDC XXXX
11586 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-12-12 11:04 | 2009-12-12 15:42 | 2 | 278 | 62693-1 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. WR#33053388 RELEASED BY CREW 076S02BAD 10 KVA XFMR. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. WR#33053388 REPAIRS COMPLETE. CHANGED 10 KVA TO 25 KVA. REPLACED OLD CUTOUT. SH
11587 | Hazard | 3301401 | COMBS | COMBS | 2017-05-03 17:55 | 2017-05-03 20:14 | 4 | 139 | 4741341 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO ANSWER//BAD CUTOUT 37830271C00283 VER/AWD
11588 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-11-28 07:14 | 2011-11-28 09:33 | 4 | 139 | 4118461 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND A BAD HOT TAP AND BROKEN GROUND WIRE, ALSO FOUND ALL CONNECTION TO BE BAD ON THE SECONDARY SIDE OF TRANSFORMER, I HAVE RESQUEEZED ALL CONNECTION AND EVERYTHING IS FINE AT THIS LOC. NOW COD-4 ISO TF 39831000B00101 VER/HFP L3/HFP IDC XXXX
11589 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2022-04-03 14:17 | 2022-04-03 18:55 | 2 | 278 | 4718041 | 556 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva on transformer bank 120 208 bank 7200v truck ok crew required Released by crew 078S09 crew on site FETR 19:45 LRM all pwr restored 18:55 please close ticket LRM
11590 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-03-27 08:47 | 2014-03-27 13:25 | 2 | 278 | 4528001 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD SEC, UNDERGROUND SEND TO BOB R. RELEASED BY CREW 078S08,,,BAD NUET CONNECTION IN SECONDARY BUCKET,,,TWO HOUSES AFFECTED, 110 AND 112 LAUREL COURT...BLR VER/SEF
11591 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-06-10 15:07 | 2019-06-10 19:45 | 2 | 278 | 4475511 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER//COD 2//
11592 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2019-05-28 10:47 | 2019-05-28 14:35 | 4 | 228 | 4353531 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STATION ZONE. pole45-c4-5725, bad 12kv c/o on c ph. old rr bed, 22 and central. to b.reynolds trk to pole//cod 2(+2)//opened other two cutouts on pole 38830045C45806 @ 1345, added 2 B ph cust//MD filed on missing fuses//
11593 | Pikeville | 3402002 | KEYSER | STONECOAL | 2022-06-01 05:17 | 2022-06-01 09:55 | 2 | 278 | 4991001 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout @1152-142, Steve Ray getting a big bucket to come and help change out. Got cutout replaced @0955.
11594 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-07-29 05:34 | 2014-07-29 10:12 | 2 | 278 | 4304531 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING CUTOUT CAN DO WITH RIGGED GUARDS SAFELY VER/CRB
11595 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-02-27 08:07 | 2009-02-27 12:45 | 2 | 278 | 52006-1 | 556 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | WR # 28713078 /// 3000301// BAD CUTOUT BURNT CROSSARM INTO--NEED CREW--3 PHASE DEAD END BANK POLE--NEED 3 CUTOUTS AN ARM--TRUCK OK-M PHELPS TO WORK JOB RELEASED BY CREW 078S07 RESTORED 12:45 M.PHELPS RELEASED BY CREW 078H12//COD 2// VER/DBM IDC XXXX
11596 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-01-10 12:40 | 2016-01-10 17:18 | 2 | 278 | 4601821 | 556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 37830250A00172, CREEK WASHED OUT, CAN SEE BOTTOM OF POLE, NOT SAFE TO CLIMB, NEED YARD DOG AND LINE CREW, 7200 CUTOUT. RELEASED BY CREW 077S04 VER/CRB
11597 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-07-25 18:00 | 2016-07-25 21:05 | 3 | 185 | 4678771 | 555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN TRANSFORMER CUTOUT ON 165-37 CUTOUT IS ON THE CROSSARM BETWEEN THE B AND C PHASES IN THE PRIMARY ZONE NEED CREW TO REPLACE NEED COVER UP AND OBSERVER FRANK BLANKENSHIP IS COMING TO HELP ME REPLACE CUTOUT VER/CRB
11598 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-03-04 01:22 | 2010-03-04 03:13 | 5 | 111 | 62627-1 | 555 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | W/R 34118613 RISER MELTED OFF SEC. ONLY ONE OUTAGE FOR HOIS SECOND OUTAGE WAS MAP ISSUE VER/PDP IDCC CNT10 XXXX
11599 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-11-25 16:20 | 2022-11-25 19:25 | 3 | 185 | 4180731 | 555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew reqd/bad 25kva/can possibly get service bucket material handler to pole. Released by crew 078S04 Repairs made, voltage check good. Closed at 19:25. Ticket complete
11600 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-03-09 06:28 | 2015-03-09 15:43 | 1 | 555 | 4170421 | 555 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS//////////SERV DROP NEEDS REPLACED,SPLICE BURNED INTO,WILL GET HELP////////HAD TO RELEASE,SEND BACK TO ME RELEASED BY CREW 074S06WILL CHECK FOR PROBLEMS//////////SERV DROP NEEDS REPLACED,SPLICE BURNED INTO,WILL GET HELP////////HAD TO RELEASE,SEND BACK TO ME ////REPLACED SERV DROP AND RESTORED,ALL OK AFTERWARDS////////SERVE-IN HEATED UP,BURNED SERV INTO VER/CRB
11601 | Hazard | 3303902 | LESLIE | WOOTON | 2008-07-23 15:25 | 2008-07-23 18:30 | 3 | 185 | 59054-1 | 555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN VER/ARN IDCC PN101 XXXX
11602 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-04-14 15:49 | 2014-04-14 18:54 | 3 | 185 | 4603801 | 555 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWED ON BANK WILL RE-FUSE. CUT-OUT DOOR WAS ALSO BURNT UP REPLACED DOOR AND RE-FUSED TRANSFORMER RESTORED SERVICE//COD 3// VER/DBM
11603 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2009-11-11 08:40 | 2009-11-11 11:45 | 3 | 185 | 60041-1 | 555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP RELATED TO ORDER 57882-1 ... THIS ORDER IS FOR THE OUTAGE REPORTED IN THAT ORDER...REMOVED HOT TAP AT POLE 37830164000196 AT 08:40 , TRANSFORMER ON POLE 196 STILL IN SERVICE ... OPENED TRANSFORMER ON POLE 196 AT 09:40 ... ALL WORK COMPLET / GXJ /// CREATED ORDER 60041-1 & 60062-1 FOR OUTAGES IN THIS ORDER. COD-3 L3/HFP IDC XXXX
11604 | South Williamson | 3200302 | BELFRY | TOLER | 2019-03-18 20:07 | 2019-03-18 23:12 | 3 | 185 | 4998671 | 555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse out on 1015-B-68//25 Scotts Lane//restored power at 23:12//991-B-3 is incorrect pole number.//iso //cod 3
11605 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-05-17 21:50 | 2020-05-18 00:55 | 3 | 185 | 4846781 | 555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva, 7200, 120/240, on pole 20-c2-4559. Has been turned in previously to be changed out, has been leaking. Crew required, trucks to pole. pole sets directly across from New Hampshire Dr Released by crew 078S02/ ISO 38830020C24559/ COD 3
11606 | Whitesburg | 3314401 | MAYKING | ERMINE | 2021-01-25 05:18 | 2021-01-25 09:55 | 2 | 277 | 4888781 | 554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 473-C4-338.. repairs made power restored @ 09:55
11607 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2020-03-25 07:39 | 2020-03-25 08:14 | 24 | 35 | 4508161 | 554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPENED OTHER DIP FUSE (11 CUST) @ 0805 CLOSED BOTH @ 0814 (24 CUST)Arrestor broken off bracket, time off 08:05 time on 08:14 power restored ======= THIS DUPLICATED FOR UNKNOWN REASON ==========
11608 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-03-30 17:53 | 2021-03-30 22:30 | 2 | 277 | 4404871 | 554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT,WILL RE-FUSE//////FUSE BLEW.NEED FOREMAN,2MEN,25 KVA 19.9.IN BACK YARD.NOT TOO SURE WE CAN GET ANYTHING CLOSE ENOUGH TO USE A MAT HANDLER.////////CHANGED XFR & RESTORED POWER,ALL OK AFTERWARDS//cod 2
11609 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-02-01 02:36 | 2013-02-01 11:50 | 1 | 554 | 4779231 | 554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM DUE TO HAZARDOUS ROAD CONDITIONS. TRANS FUSE IS OUT ON POLE 152-8. WE ARE GOING TO REFUSE TRANS. CUTOUT IS BROKEN ON POLE 152-8. WE ARE GOING TO CHANGE CUTOUT. WE CHANGED CUTOUT AND GOT POWER BACK ON. ///VER/CRB L/3 CRB IDCC PN17 CNT3 XXXX
11610 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-27 06:36 | 2008-06-27 15:50 | 1 | 554 | 55757-1 | 554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008702//BAD CUTOUT ANDL.ARRESTOR ONPOLE141-267 19.9 K.V. POLE IN BACKYARD. CAN GET SMALL BUCKET TO POLE. RELEASED BY CREW 078S04 AJBC CDC83 MD FILED ON CUST TO POLE 267 VER/KEP
11611 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-01-05 09:51 | 2017-01-05 19:05 | 1 | 554 | 4271031 | 554 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 1 BAD LEG OF UNDERGROUND OUT ON THIS 3 PHASE SERVICE AT POLE 24-B3-751, HAVE FAULT MACHINE EN ROUTE TO HELP FIND. 1 CUSTOMER IS ALL THATS AFFECTED BY THIS. RELEASED BY CREW 074S05 TEMP REPAIRS MADE ON AT 19:05/ ISO 37830024B30751/ COD 1/ VER/BOW L3/HFP XXXHFP
11612 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-03-08 09:37 | 2008-03-08 14:14 | 2 | 277 | 54951-1 | 554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202//CUTOUT OPEN ON POLE 1115-D-68 (NOT ON MAP, WILL SEND NOTE TO MAPPING)//COD 10//, POLETOP BURNT OFF, POLE#1115-77, CALLEDR MARCUM, HELP ON WAY, CREW ARRIVEDAT 1325//POWER RESTORED 1414// VER/DBM IDCC PN44 XXXX
11613 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-11-13 04:47 | 2019-11-13 08:40 | 3 | 233 | 4028831 | 553 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 Secondary burnt down on pole 166-157/// Opened xfm 37830166000066 @ 06:00 to make safe/// Paul Layne enroute to assist L3/HFP
11614 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2018-02-16 12:04 | 2018-02-16 16:40 | 2 | 276 | 4850571 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout at pole 115-26, opened at pole 115-192 at 15:10 to repair and closed at 16:40 . repairs complete / GXJ Released by crew 074S03/ ISO 37830115000192 & 37830115000206/ COD 2/ no additional customers affected
11615 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-02-14 08:11 | 2022-02-14 11:15 | 3 | 184 | 4479921 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer cutout at pole 164-27 was broke.////// changed out 19.9 cutout and got power restored at 11:15
11616 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-07-25 08:04 | 2012-07-25 11:08 | 3 | 184 | 4822181 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK WAS BROKE//COD 3// VER/DBM
11617 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-11-28 20:40 | 2017-11-28 22:12 | 6 | 92 | 4608161 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | attempted to call customer//no answer at given callback number//replaced broken cutout @ 399-10 all customers retored complete
11618 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2018-02-05 02:16 | 2018-02-05 04:34 | 4 | 138 | 4805051 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 230-93 line fuse open,,,,pole burnt @ 230-343 .replaced insulaters line fuse back in @ 04:34,,complete/md made for line fuse/
11619 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-09-08 00:55 | 2012-09-08 10:07 | 1 | 552 | 4028791 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SATURDAY MAN TO WORK.FUSE LINK BROKE & BURNED UP CUTOUT DOOR. REPLACED FUSE & DOOR. ///VER/CRB L/3 CRB IDC XXXX
11620 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-05-15 20:37 | 2011-05-15 22:55 | 4 | 138 | 4098561 | 552 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST. NEUT. IS IN TWO IN SER WILL REPAIR//NEUT. PULLED OUT OF TENSION SPLICE IN S/D/// CUST. STATED THAT HE HAS DAMAGES// REPAIRED SPLICE ALL BACK TO NORMAL VER/PDP
11621 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-02-27 13:07 | 2014-02-27 16:11 | 3 | 184 | 4438461 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW REQUIRED BROKEN CROSSARM ON 222-17 TRUCKS OK ISOLATED ON 222-15 TAGGED AND GROUNDED IN MULLINS NAME/CROSSARMS AND BRACES REQUIRED RELEASED BY CREW 078S03/CREW ON SITE/FETR1630/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1611/PLEASE CLOSE TICKET/THANKS/VEM//COD 3// VER/DBM
11622 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2015-02-21 19:34 | 2015-02-21 21:06 | 6 | 92 | 4067591 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, CHANGED/ ISO 38830045A10100/ COD 6/ VER/BOW
11623 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2008-04-06 21:38 | 2008-04-06 23:56 | 4 | 138 | 64737-1 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001204 BAD XFMR CALLING OUT D/S FOR CREW. VER/PDP IDC XXXX
11624 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-03-23 13:21 | 2022-03-23 16:25 | 3 | 184 | 4661811 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | pole fire at pole 116-820 needs pole top extension// crew required truck ok// line fuse is open on pole 116-770 Released by crew 078S09,repairs made all cust restored @ 1625 please close ticket thanks.bt
11625 | Hazard | 3309903 | SLEMP | BEECH FORK | 2022-11-27 05:58 | 2022-11-27 09:02 | 3 | 184 | 4182751 | 552 | TRANSMISSION LINE | EQUIPMENT FAILURE | ARRESTER | DOL 1254560/At 0558 SCADA indicated 34kV Bus 2 at Slemp locked out from service/ Personnel en route/ Released by crew 077S04
11626 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-04-08 15:12 | 2010-04-08 19:48 | 2 | 276 | 61030-1 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 080S01, ON SITE, BAD CUTOUT, CALLED R MARCUM FOR HELP//COD 2// VER/DBM IDC XXXX
11627 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-07-19 13:16 | 2014-07-19 16:20 | 3 | 184 | 4263531 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7.2 KV CUTOUT FAILED. NEED ALTEC BUCKET OR THE NEXT BIGGEST ONE. CREW ENROUTE. RELEASED BY CREW 074S02 REPAIRS MADE ON AT 16:20 D SAMMONS//COD 3// VER/DBM
11628 | Pikeville | 3403001 | PIKEVILLE | CITY | 2009-12-10 16:42 | 2009-12-10 19:00 | 4 | 138 | 66333-1 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPEN THE TRANSFORMER FOR ABOUT 15 MINUTE THE 1/0 SEC HERE NEEDS TO BE REPLACED. CONNECTIONS ARE BURNING UP WHERE THE IN INSULATION WILL NOT COME OFF. SEND TO TIM HALL .....DAH VER/KEP L3/KEP IDCC TOF1845 XXXX
11629 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-05-12 06:52 | 2008-05-12 09:10 | 4 | 138 | 62438-1 | 552 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | FOUND ARR. BAD AT POLE 1152-335 STILL PARTROLLING. 1152-186 FUSE POLE BACK TO STA. RT. HAND PHASE OUT 50 T VER/PDP IDCC PN188, FP186, CNT1 ASSUMING PHASE C XXXX
11630 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-12-12 09:56 | 2014-12-12 13:00 | 3 | 184 | 4856231 | 552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT WAS ABLE TO SAFELY REPLACE CUTOUT APR AT 1300 CLOSE TICKET// COD 3//VER/ ADH
11631 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-10-09 21:25 | 2009-10-09 23:15 | 5 | 110 | 53163-1 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BAD == REPLACED == REFUSED == POWER OK //VER/GAH IDC CHANGED COUNT FROM 1 XXXX
11632 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-05-27 03:20 | 2022-05-27 12:30 | 1 | 550 | 4957621 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held for daylight per KPCO late night callout guidelines.// Broke XCO on pole 93-39, Steve Ray is getting one man to come help with repairs
11633 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-08-10 07:50 | 2014-08-10 17:00 | 1 | 550 | 4349991 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORM ER FUSE OUT STS BAD 15 KVA 19.9 TRANSFORMER AND ALSO CUTOUT AND ARRESTOR RELEASED BY CREW 077S05 WAITING ON MEN TO CLEAR UP -UNKNOWN FETR-//COD 1// VER/DBM
11634 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-06-23 02:45 | 2009-06-23 11:55 | 1 | 550 | 63950-1 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 30417459 /// 3311101// BAD XFMR TOLD CUST WOULD BE ABOUT 10:00 A.M. RESTORED //ON SITE CHANGING TRANSFORMER COD-1 ISO 37830505000003 L3/HFP IDC XXXX
11635 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-08-29 09:35 | 2014-08-29 10:00 | 22 | 25 | 4435461 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FUSE BLEW DURING RESTORATION ATTEMPT FOR ORDER 4435291//SEE ORDER4435461 ALSO//COD 22// VER/DBM AJB
11636 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-10-31 11:25 | 2017-10-31 16:00 | 2 | 275 | 4519331 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F IS OUT,WILL RE-FUSE////////BAD 15KVA XFR,NEED 15KVA,MAT HANDLER,2 MEN,1 19.9 CUTOUT FOR SIDE-TAP REPLACEMENT OF PORCELIN CUTOUT RELEASED BY CREW 074S06//POWER RESTORED AT 16:00/ ISO 38831056A00036/ COD 2/ VER/BOW
11637 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2022-02-02 17:31 | 2022-02-02 17:53 | 25 | 22 | 4425271 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Blown arrester repaired and restored at 1753
11638 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-02-08 02:05 | 2017-02-08 11:15 | 1 | 550 | 4370141 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE IS OUT, BROKE 7.2 KV CUTOUT, MANUEL POLE, CALLING FOR HELP/ ISO 37830180000017/ COD 1/ VER/BOW L3/HFP XXXHFP
11639 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2020-07-20 15:17 | 2020-07-20 19:52 | 2 | 275 | 4190021 | 550 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | b phase lead burnt off at cutout. alley behind boyd co. ford. 45-375. trk to pole Released by crew 078S07 on site RM/opened xfm bank @19:35 closed back @19:52 please close tic RM // cod 2
11640 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-03-09 16:35 | 2016-03-09 17:30 | 10 | 55 | 4831641 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | CT METER CABLE BURN UP, REPLACE CABLE AND METER BASE,OPEN TRANSFORMER AT 16:35 AND CLOSE AT 17:30/ ISO 37830230C00166/ COD 10/ VER/BOW
11641 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-10-26 08:40 | 2021-10-26 10:30 | 5 | 110 | 4016341 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Bad cutout gate on pole 519D-27. Power restored at 10:30.
11642 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-03-28 15:20 | 2012-03-28 16:10 | 11 | 50 | 4626181 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WIRE BROKE ON HOT LINE CLAMP ////VER/CRB IDC XXXX
11643 | Hazard | 3310502 | HADDIX | CANOE | 2021-06-21 16:19 | 2021-06-21 20:54 | 2 | 275 | 4783001 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke manual cutout on pole 51-102. need line crew and row crew to cut around pole Released by crew 077S10
11644 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-01-22 07:10 | 2009-01-22 09:00 | 5 | 110 | 59050-1 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WR # 28172688 / TRANSFORMER LUG WAS BURNED OUT I REPLACED LUG//VER/CRB L3/KEP
11645 | Pikeville | 3408103 | SALISBURY | MARTIN | 2018-11-13 12:35 | 2018-11-13 13:25 | 11 | 50 | 4394621 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE UNTIL HOTLINE CLAMP LIFTE // lifted hot line clamp on transformer pole 1089-658 at 12:35 due to bad cutout. will be changing outlifted hot line clamp on transformer pole 1089-658 at 12:35 due to bad cutout. will be changing out. got cutout changed out closed 25t transformer fuse back in at 13:25 COD-11 ISO TF 38831098B00658 OFF 1235 ON 1325
11646 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2011-06-12 10:15 | 2011-06-12 14:50 | 2 | 275 | 4300961 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED NEED FLAGGERS 3 CUTOUT 8FOOT ARM 3 ARRESTERS SET BRACES 2 STEAL PINS 2 INSULATEORS 7200 CAN USE TRUCK. TROUBLE ON POLES 139-373 AND 139-382. RELEASED BY CREW 074S11//CREW ON SITE, WILL NEED TO OPEN OCRS ON POLE 139-429 TO MAKE REPAIRS.//COD 2// VER/DBM IDC XXXX
11647 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-05-22 16:00 | 2012-05-22 17:50 | 5 | 110 | 4818161 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOING TO REPLACE #2 TRIPLEX W 1/0 TRIPLEX AND ALSO REPLACE XFR TO ELIMINATE THE POSSIBILITY OF ITS BEING FAULTY//////PAUL LAYNE ENROUTE RELEASED BY CREW 074S06GOING TO REPLACE #2 TRIPLEX W 1/0 TRIPLEX AND ALSO REPLACE XFR TO ELIMINATE THE POSSIBILITY OF ITS BEING FAULTY//////PAUL LAYNE ENROUTE /////REPLACED SEC AND XFR.XFR OFF AT 1600,ON AT 1730 ///VER/CRB L/3 CRB IDC XXXX
11648 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2013-05-23 05:35 | 2013-05-23 07:25 | 5 | 110 | 4168891 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT INTO SERV TO REPLACE,LINE FUSE IN @0725 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/KEP
11649 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2022-07-17 15:15 | 2022-07-17 17:05 | 5 | 110 | 4503011 | 550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM must be causing problems will have to open to make safe and wait for line crew to change out// opened xfmr @1515 closed @1705
11650 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-07-05 21:42 | 2014-07-06 00:45 | 3 | 183 | 4195901 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 37830198A00152, NEED 1 MAN AND 19.9 CUTOUT ARRESTER AND TEE BRACKET. VER/HFP L3/HFP
11651 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2020-10-23 11:16 | 2020-10-23 20:25 | 1 | 549 | 4578321 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Released by crew 074S03. replaced TR at 20:25 per crews in field 1 CC on this TR
11652 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2015-06-09 10:41 | 2015-06-09 19:50 | 1 | 549 | 4543521 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG OUT ON UNDERGROUND CABLE, WILL NEED LOCATED CAN FIND SEC, BUCKET CREW REQ, TODAY NEED TO INSTALL MACHINE UNTILL REPAIRS MADE RELEASED BY CREW 078S09.. POWER TEMP INSTALLED AND CUST RESTORED.. COMPLETE// VER/ ADH
11653 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-08-18 15:32 | 2014-08-18 18:35 | 3 | 183 | 4380651 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEC. BKT 69C24763 CONNECTIONS AND RUBBER BOOTS. OPEN PAD 69C24762 @ 17:20 TO MAKE REPAIRS.RESTORED @18:35 VER/CRB
11654 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-02-22 05:59 | 2021-02-22 09:02 | 3 | 183 | 4214281 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on 1081-96, repairs made power restored at 9:02
11655 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2018-12-27 08:22 | 2018-12-27 09:23 | 9 | 61 | 4600571 | 549 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | OPENED XFMR BANK TO REPLACE XFMR RISER THAT IS BURNT OF ON PRIMARY SIDE // COD-9 ISO 38830045C14342 OFF @ ON @riser from cutout burnt in clear, cutout may be bad, opening bank to make repairs.riser from cutout burnt in clear, cutout may be bad, opening bank to make repairs. Time off @ 09:00 & back on @ 09:23//WAS PART POWER FROM BEGINNING L3/HFP
11656 | South Williamson | 3411401 | DEWEY | INEZ | 2010-01-22 06:30 | 2010-01-22 09:33 | 3 | 183 | 57674-1 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE//COD 3 IDC XXXX
11657 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-03-16 09:17 | 2016-03-16 12:20 | 3 | 183 | 4853631 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 25T FUSE OUT. LOOKS LIKE THE FUSE BROKE AND TRACKED THROUGH THE DOOR AND BURNT DOOR UP REPLACED DOOR FUSED UP EVERYTHING OK. VER/ARN
11658 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-08-31 17:57 | 2013-08-31 21:00 | 3 | 183 | 4808571 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN//WILL REFUSE// CHANGED BAD 19,900 CUTOUT ALSO// POWER IS RESTORED COD-3 ISO TF 37830143A00249 VER/HFP L3/HFP IDC XXXX
11659 | Hazard | 3303901 | LESLIE | HYDEN | 2022-12-10 16:42 | 2022-12-10 19:45 | 3 | 183 | 4249141 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OPEN ON POLE 388-A-301 /// BAD ARRESTER ON LINE FUSE CUT OUT /// CUT ARRESTER IN CLEAR /// RESTORED POWER @ 19:45 /// SEND TO ROB PIGMAN / JEFF BAKER, TO REPLACE 19.9 ARRESTER
11660 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-08-06 20:11 | 2008-08-07 05:20 | 1 | 549 | 66190-1 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-1319 BURNT OFF 45 CLASS 2 BANK POLE POLE 68-521 3-65T OPEN RELEASED BY CREW 078S08//CREW ON SITE WILL INSTALL HEAVY DUTY POLE TOP EXTENSION AND REPLACE ARM AND 6 CUTOUTS DIFFICULT LOCATION P TOLLIVER//POWER RESTORED AT 05:20 P TOLLIVER VER/KEP IDC XXXX
11661 | Whitesburg | 3409503 | BURDINE | JENKINS | 2012-01-06 12:37 | 2012-01-06 13:38 | 9 | 61 | 4237691 | 549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | THE RISER LEAD BROKE OUT OF THE TOP OF THE CUTOUT, I REPLACED AND REFUSED.//COD 9// VER/DBM IDC XXXX
11662 | Paintsville | 3409302 | KENWOOD | AUXIER | 2011-11-15 14:38 | 2011-11-15 16:55 | 4 | 137 | 4079491 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY LOOP BURNT IN TWO ON 881-38. REPAIRING. LOOP REPAIRED - RESTORED @ 16:55. SH//COD 4//ISO// VER/DBM IDC XXXX
11663 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-08-09 15:40 | 2014-08-09 17:57 | 4 | 137 | 4348061 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 399-116, THIS FEEDS TWO TAPS OFF OF THIS POLE, WILL NEED 1 MAN TO HELP MAKE REPAIRS. MADE REPAIRS, RESTORED POWER AT 1757.//ISO 37830399000116//MD FILED//COD 4// VER/DBM
11664 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-08-14 11:36 | 2011-08-14 16:10 | 2 | 274 | 4707611 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT ON POLE 37830247A00212--- BAD 25 KVA TRANSFORMER, DUTY SUPERVISOR NOTIFIED.--- POWER RESTORED.//COD 2// VER/DBM IDC XXXX
11665 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-06-17 20:58 | 2020-06-17 23:15 | 4 | 137 | 4038301 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IF I CAN REACH IT,CUST HAS WOODEN PALLETS ABT 10FT HIGH ALL AROUND POLE///////COULDNT REACH,1MAN&BUCKET ENROUTE//////MADE REPAIRS&RESTORED//cod 4
11666 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-10-27 13:55 | 2012-10-27 16:12 | 4 | 137 | 4176301 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. SEND COPY TO ENG PIKEVILLE CUTOUT WAS ON ARM BRACKET BURNT 1 ARM JUST ABOUT INTO OTHER ARM IN GOOD SHAPE. I HAVE CUTOUT REPLACED EVERYTHING OK//COD 4// VER/DBM IDC XXXX
11667 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-02-24 06:48 | 2011-02-24 09:05 | 4 | 137 | 60603-1 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 673-47//CHANGING NOW//REPAIRS MADE//RESTORED 9:05//COMPLETE//EM//VER/CRB IDC XXXX
11668 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-02-01 17:33 | 2011-02-01 19:50 | 4 | 137 | 52875-1 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE APPEARS BLOWN COD-4 ISO TF 37830312000187FUSE APPEARS BLOWN---FUSE WAS BLOWN AND DOOR DIDNT DROP DOWN AND WAS TRACKING THRU THE DOOR COD-4 ISO TF 37830312000187 VER/HFP L3/HFP IDC CHANGED FROM CAUSE OTHER XXXX
11669 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-01-08 09:03 | 2015-01-08 11:20 | 4 | 137 | 4918881 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | #4 CU OPEN WIRE SECONDARY FELL AND BLEW XFMR FUSE. CREWS WORKING TO REPAIR. XFMR 38830878000047 IS ALSO OFF AFFECTING ONE ADDITIONAL CUSTOMER. REPAIRS COMPLETE. RESTORED @ 11:20. SH COD 3+1// VER/ ADH
11670 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-10-12 11:39 | 2020-10-12 15:25 | 5 | 226 | 4548241 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 xfm on pole 269-223. truck access Released by crew 077S10 opened line fuse on pole 223 at 14:53 closedback at15:25 transformer replaced and power restored at 15:25
11671 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-04-12 16:10 | 2011-04-12 18:27 | 4 | 137 | 55968-1 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#39542564 POLE 117-320 BAD CUTOUT NO TRUCKS 2-CUST SEND TO VERNON M. RELEASED BY CREW 078S08/CREW ON SITE/FETR1900/VEM/INSTALL 20T LINE FUSE ON POLE # 117-204/CHANGED C/O ON 117-320/POWER RESTORED TO ALL CUST 1827/PLEASE CLOSE TICKET/THANKS/VEM ENTERED MD...HFP VER/HFP L3/HFP
11672 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-03-11 10:23 | 2015-03-11 14:57 | 2 | 274 | 4182601 | 548 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN IN SERVICE @ TRANSFORMER/// WILL REPAIR/// REPAIRED BAD CONNECTION EVERYTHING OK NOW 124/124/248 /////RESTORED SERVICE @ 14:57 ONLY 1 CUSTOMER AFFECTED VER/KEP
11673 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-05-13 17:46 | 2017-05-13 22:20 | 2 | 274 | 4796371 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT - OPENED @ 1930 CLOSED @ 2220
11674 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2013-06-13 14:10 | 2013-06-13 16:27 | 4 | 137 | 4282351 | 548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER AT TOP OF CUT-OUT BURNT OFF ON POLE 468-43 AND FELL ACROSS BOTTOM OF CUT-OUT KEEPING POWER ON. HAD TO OPEN RECLOSER AT POLE 468-179 IN ORDER TO CLEAR RISER AND CHANGE CUT-OUT. OPENED RECLOSER AT 15:50. MADE REPAIRS AND CLOSED RECLOSER; RESTORING POWER AT 16:27 - CAN CLOSE TICKET MWL VER/KEP IDC XXXX
11675 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2012-07-27 10:23 | 2012-07-27 19:30 | 1 | 547 | 4843761 | 547 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6T FUSE OUT DUE TO BAD TRANSFORMER. CALLED ROGER MAYNARD HE WILL BE GETTING 25KVA TRANSFORMER 1 MAN AND MATERIAL HANDLER. CHANGED TRANSFORMER OUT REPLACED CUTOUT EVERYTHING OK VER/KEP
11676 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-02-05 08:24 | 2009-02-05 17:30 | 1 | 546 | 55832-1 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA BAD, 2 TOTAL ELECTRIC HOMES, NEED TO REPLACE WITH 25KVA, 120/240 7.2KV, TRUCK ACCESS, NEED FLAGMEN TO BLOCK 1 LANE OF KY RT 1107 / GXJ RELEASED BY CREW 074S03// CHANGED TO A 25 KVA// COMPLTED AT 17:30//COD 1// VER/DBM
11677 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-06-18 | 2009-06-18 00:13 | 42 | 13 | 51603-1 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SHORT OUTAGE FOR CREW TO MAKE REPAIRS. VER/ARN
11678 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-11-29 20:12 | 2013-11-30 00:45 | 2 | 273 | 4088501 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000802 / WRONG STATION AND CIRCUIT IT IS HAYWARD/LAWTON CREW REQUIRED BAD 25 KVA YARD DOG REQUIRED NO TRUCKS YARD WET SPRING CLOSE TO POLE /DRIVEWAY ON RIGHT AFTER HILLMABN HOLLOW RELEASED BY CREW 078S03// R. VIRGIN & C. YOUNGMAN TO ASSIST // V. MULLINS ALSO TO ASSIST // //VER/GAH IDC XXXX
11679 | Whitesburg | 3401301 | FLEMING | NEON | 2012-12-05 02:32 | 2012-12-05 04:03 | 6 | 91 | 4443151 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED POLE 331-D-63 // OPENED RECL POLE 331-D-229 @ 0343 //REPLACED CUTOUT & CLOSED RECL POLE 331-D-229 @ 0403 // //VER/GAH IDC XXXX
11680 | Hazard | 3303902 | LESLIE | WOOTON | 2008-01-17 10:27 | 2008-01-17 11:45 | 7 | 78 | 57348-1 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303902// SERVICER HAD TO OPEN RECLOSER ON POLE 37830365C00209 TO ISOLATE BURNT SECTION OF LINE CAUSED BY HOT LINE CLAMP FAILURE/ @ POLE 365-45// REPAIRED AND CLOSED RECLOSER BACK @ 1145// VER/TOM IDC XXXX
11681 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-11-04 20:29 | 2009-11-04 22:00 | 6 | 91 | 61962-1 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE, FUSE WAS NEW.// VER/TOM L3/TOM IDC XXXX
11682 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-07-19 21:41 | 2012-07-19 23:12 | 6 | 91 | 4779501 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE VER/KEP
11683 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-07-04 21:45 | 2022-07-05 02:18 | 2 | 273 | 4374541 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout and restored @ 2:18. sh
11684 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-04-01 21:20 | 2010-04-02 01:53 | 2 | 273 | 57259-1 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED, BAD 19.9, 15KVA TRANSFORMER ON POLE 502-69 POLE IS TRUCK ACCESSIBLE NEXT TO ROAD OFF OF 644//STS WR# 34503055//COD 2//\\\\ SHOULD HAVE CALLED FOR FLAGGERS //VER/GAH AJB IDC XXXX
11685 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-06-05 11:54 | 2016-06-05 21:00 | 1 | 546 | 4307651 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED NEED 15 KVA TRUCKS OK RELEASED BY CREW 078S03.. CREW ON SITE .. XFMR CHANGED AND CUST RESTORED AT 2100.. PLEASE CLOSE TICKET VER/KEP
11686 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-05-21 13:01 | 2011-05-21 16:03 | 3 | 182 | 4120321 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 1121-69, CUTOUT VERY CLOSE TO PRIMARY, CAN NOT GET TRUCKS TO THIS, WILL NEED LINE CREW TO MAKE REPAIRS. RELEASED BY CREW 078S06//WR# 40057189 // FETR18.00 RLM //COD 3// VER/DBM IDC XXXX
11687 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-12-15 10:21 | 2020-12-15 11:00 | 14 | 39 | 4770911 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found broke c/o on 1121-2002, which is the l/f, crew is changing it now, power restored at 1100
11688 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-11-06 10:49 | 2018-11-06 15:22 | 2 | 273 | 4370091 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary broke at deadend pole and cutout also broke. 19.9 trucks to pole crew can ground at work location. All repaires made and power restored at 1522 close ticket dwest L3/HFP
11689 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-08-11 15:26 | 2011-08-11 16:57 | 6 | 91 | 4697711 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ONE FUSE OUT IN TRANSFORMER BANK COD-6 ISO TF 38830045C35099 VER/HFP L3/HFP IDC XXXX
11690 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-01-23 15:22 | 2021-01-23 18:24 | 3 | 182 | 4887221 | 546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANS 37830352C00010//COD 3//bad xfmr , we changed it out
11691 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-11-15 09:52 | 2008-11-15 11:41 | 5 | 109 | 65129-1 | 545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202//, , ON SITE, CHECKING TROUBLE, BAD CUTOUT, 2 CUST OUT COD-5 VER/KEP IDC XXXX
11692 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-01-17 04:05 | 2022-01-17 11:30 | 3 | 445 | 4361431 | 545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cust fed from TR 828-128 and found broken cutout (TR 828-281 was never opened--cust mismapped)//Open LF 828-282 to change broken cutout7,200 XFR CUTOUT BROKEN @ POLE 828-128/OPEN LINE FUSE ON 828-282 @ 10;40 TO MAKE REPAIRS/ CLOSED BACK IN @ 11:30 RESTORED.// MDR complete
11693 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-01-24 20:01 | 2013-01-24 21:50 | 5 | 109 | 4738591 | 545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMIT FUSE BURNT OUT. WILL BE OUT OF TRUCK MAKING REPAIR. I HAVE REPAIRS MADE EVERYTHING OK ///VER/CRB L/3 CRB IDC XXXX
11694 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-05-26 15:01 | 2014-05-26 16:50 | 5 | 109 | 4930821 | 545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE BURNT UP CUTOUT DOOR VER/CRB
11695 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-05-10 06:28 | 2015-05-10 11:00 | 2 | 272 | 4407521 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN 12KV CUTOUT BIG BUCKET SHOULD REACH OK, CLEARED HOTTAP, CREW REQUIRED RELEASED BY CREW 078S11/COD 2// VER/ ADH
11696 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-06-29 09:46 | 2008-06-29 10:54 | 8 | 68 | 59216-1 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REPLACED INSULATOR VER/ARN
11697 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-08-10 17:38 | 2022-08-10 22:10 | 2 | 272 | 4718951 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got a broke cutut on the arms at xformer pole 737-217 will be crew required and need big bucket. crew will need a 7200 cutout..sent ticket to austin preese Released by crew 074S03// repairs made restored @ 22:10
11698 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2019-10-27 13:50 | 2019-10-27 16:06 | 4 | 136 | 4207151 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT/////// REPLACED BROKEN CUTOUT AND RESTORED SERVICE..
11699 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-02-22 05:54 | 2022-02-22 08:10 | 4 | 136 | 4526191 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Could Not Reach Customer/ Dispatched in accordance with KYPCo Late Night Callout Guidelines. power restored at 8:10
11700 | Pikeville | 3421001 | BREAKS | CITY | 2021-12-01 14:25 | 2021-12-01 16:41 | 4 | 136 | 4138681 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot tap burnt off on xfm @ pole 243-185 will be making repairs///Replaced hot tap and restored ser vice @ 16:41
11701 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-03-19 10:56 | 2016-03-19 13:12 | 4 | 136 | 4863731 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 6T FUSE BROKE. SEND COPY TO ENG PAINTSVILLE. 4- 200AMP CUST ON 25KVA. CHECK LOAD. FUSED UP EVERTHING OK./EMAILED TECH/ADH// VER/ ADH
11702 | South Williamson | 3411401 | DEWEY | INEZ | 2020-01-29 10:07 | 2020-01-29 11:15 | 8 | 68 | 4346281 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened xfmr on pole 672-276 to replace downed neutral//opened at 10:40//cutout broke//opened line fuse on pole 672-67 to replace cutout @ 1050 //restored all at 1115 // cod 1 (+ 7)
11703 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-10-08 17:38 | 2019-10-08 18:10 | 17 | 32 | 4120731 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | both sets of braces are broke on pole 181-50, arm is being held by extension link on primary tap, opened line at 17:38, closed back in at 18:10
11704 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2014-08-17 00:27 | 2014-08-17 01:01 | 16 | 34 | 4375131 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VERNON MULLINS OPENING FUSES TO MAKE REPAIRS ON HENDRIX CABLE OPENED @ 0027 CLOSED @ 0101. VER/SEF AJBC TOF 08/16 CCSCO FEC57
11705 | Pikeville | 3413402 | GARRETT | LACKEY | 2016-01-14 07:59 | 2016-01-14 10:15 | 4 | 136 | 4618821 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN, ALSO DISCOVERED LOOSE CONNECTION AT TRANSFORMER, REPLACED TRANSFORMER RISER AND ALL CONNECTIONS AT TRANSFORMER, ALL WORK COMPLETE / GXJ VER/CRB L3/GSL
11706 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2010-12-11 14:02 | 2010-12-11 16:18 | 4 | 136 | 65341-1 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38076394 // POLE 1148-328 HOT TAP BROKE TOP OF CUTOUT SEND TO BII F. RELEASED BY CREW 078S08 COD-4 ISO PO 39831148B30710 VER/HFP L3/HFP IDC XXXX
11707 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-07-24 10:43 | 2008-07-24 15:15 | 2 | 272 | 59762-1 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400301//XFMR CUTOUT BROKEN...DIDNT HAVE ONE TO REPLACE....GET BACK TO LATER TODAY...D LEWIS 07-24-08 RELEASED BY CREW 074H08// BILL CAMPBELL AND CREW TO REPLACE // COD 2//VER/CRB IDC XXXX
11708 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2015-12-22 11:36 | 2015-12-22 13:52 | 4 | 136 | 4550271 | 544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PIN INSULATOR BROKE ON POLE#171-93/// NEED LINE CREW AND FLAGGERS//// NEED INSULATOR AND POSSIBLY 8 ARMCUTOUT BROKE ON POLE#171-93/// NEED LINE CREW //// 1352 RESTOREDCUTOUT BROKE ON POLE#171-93/// NEED LINE CREW //// REPAIRS MADE RESTORED SERVICE @ 13:52/ ISO 37820171D00093/ COD 4/ VER/BOW
11709 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-12-20 11:32 | 2017-12-20 14:33 | 3 | 181 | 4660471 | 543 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | found connection almost burnt into on sec. side below xfm. on pole 167-146..opened xfm. @ 14:10 and closed back @ 14:33..
11710 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-10-12 20:44 | 2011-10-12 23:45 | 3 | 181 | 4972501 | 543 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN. RELEASED BY CREW 077S04TRANSFORMER FUSE BLOWN. --- BAD CUTOUT, POWER RESTORED. VER/ARN IDC XXXX
11711 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-12-19 14:16 | 2013-12-19 17:17 | 3 | 181 | 4176881 | 543 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 37.5 NEED LINE CREW TO CHANGE TRUCK OK RELEASED BY CREW 078S05/CREW ON SITE/FETR1800/VEM/REPAIRS MADE AND POWER RESTORED 1717/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L3/HFP
11712 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-06-11 09:59 | 2018-06-11 13:00 | 3 | 181 | 4582481 | 543 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 94-6501 bad 12kv c/o on 3 ph bank, others are silver tops also. Released by crew 078S07/on site RM power on @ 13:00 please close tic RM
11713 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-04-05 11:23 | 2010-04-05 15:54 | 2 | 271 | 58781-1 | 542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER WIRE TOP OF CUTOUT BURNINTO//VER/CRB IDC XXXX
11714 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-08-03 19:09 | 2009-08-03 23:40 | 2 | 271 | 52028-1 | 542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WORK REQ # 31051172 BAD 25 KVA 19.9 NEED 37.5 CUTOUT AND CURRENT LIMING FUSE RELEASED BY CREW 078S08 COD-2 L3/HFP IDCC PN62 XXXX
11715 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-07-12 11:29 | 2013-07-12 16:00 | 2 | 271 | 4512921 | 542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE # 38831108A00469 HAS ROTTED OFF, GOING TO RUN WIRE TO POLE38831108A10685 AND HAVE TO CUT ONE TREE RELEASED BY CREW 077S05 VER/HFP L3/HFP IDC XXXX
11716 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-03-11 04:48 | 2017-03-11 09:19 | 2 | 271 | 4547881 | 542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER ETA 0600// 911 STATES THAT XFMR HAS "BLOWN UP"//SERVICER ETA 0600// 911 STATES THAT XFMR HAS BLOWN UP //25KVA BLOWED LID OFF NEED LINE CREW AND R/W CREW TO CLEAN BLACKTOP FROM OIL RESTORED 0919. 37830483C00029 VER/AWD
11717 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-03-05 08:28 | 2012-03-05 17:30 | 1 | 542 | 4549011 | 542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN AT 169-230. CUTOUT FAILED ON POLE 169-238 AND BURNED TOP OF POLE OFF. WE LIFTED HOTTAP ON POLE 169-77 TO ISOLATE FAULT. I AM GOING TO CLOSE RECLOSER AT 169-230 BACK IN. WE WILL LOWER EQUIP. ON 169-238 TO GET THIS TAP BACK ON. I CLOSED RECLOSER AT 169-230 IN AT 15:58. THIS LEAVES 2 CUSTOMERS OUT UNTIL WE FIX PROBLEM. WE PUT HOT TAP AT 169-77 ON LINE AT 17:30//COD 27// VER/DBM IDC IXXXX
11718 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-04-26 07:56 | 2011-04-26 16:58 | 1 | 542 | 65244-1 | 542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POSSIBLE BAD UNDERGROUND ARE TRANSFORMER BAD 10KVA TRUCKS OK,7200 SINGLE BUSHING 120/240 POLE MIS MAP 524-139 ,PARK AT STORE ON CED-GAP DR. LOOK UP HILL TO TRANSFORMER CREW REQ FIRST DRIVE WAY ON LEFT OFF OF CED GAP //POLE MIS MAP //ISO 38830524000139/./COD 1//MD FILED IDCC PN224, CNT11 XXXX
11719 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-10-31 01:04 | 2016-10-31 10:05 | 1 | 541 | 4064401 | 541 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BULLITT HOLE IN OLD CAN. BAD 7200-15 KVA 120-240. TRK OK, XFMER BAG. RELEASED BY CREW 078S07,REPLACED XFMR ALL CUST RESTORED @ 1005 PLEASE CLOSE TICKET THANKS.BT VER/AWD
11720 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-03-04 00:40 | 2015-03-04 09:41 | 1 | 541 | 4095861 | 541 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK IN THE AM 3-4-15 TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS CUTOUT IS BROKEN. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT 37830190C00095 VER/CRB LE/DKGXXXX
11721 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-05-11 13:45 | 2010-05-11 14:45 | 9 | 60 | H59482-1 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN LINE AT POLE# 244-95 AT 11:45 CUT TREE OFF CLOSED BACK AT 13:30 WHEN CUTOUT BROKE--AT 13:45 OPENED FUSE AT POLE # 244-24 AT 13:45-- 14:45 ALL ON //ISO 37830244000024 //COD 12 IDCC DUP TO OPEN SECOND FUSE, CCTIR XXXX
11722 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-03-27 05:10 | 2009-03-27 05:30 | 27 | 20 | H61993-1 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | JUMPER BROKE ON FUSE POLE 207-46, CC 66 GOING TO OPEN FUSE AT 38830207A00115 TO MAKE REPAIRS. FUSE OPENED AT 05:10, 33 CUSTOMERS FUSE CLOSED AT 05:30, ALL CUSTOMERS RESTORED DUP TICKET MADE TO SHOW OUTAGE. 61993-1 IDCC PN46, CNT33, CDC88 XXXX
11723 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-03-07 07:45 | 2012-03-07 16:45 | 1 | 540 | 4559241 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR FUSE OUT AGAIN,WAS RE-FUSED BY ME YESTERDAY,APPEARS TO BE A JOB OUT TO SET NEW POLE HERE ON UP HILL CLOSER TO WHERE IT NEEDS TO BE,IS ABT 250 FT UNDER HILL AT PRESENT.CREW REQD.CREW IS GOING TO WORK THIS SOME TIME TODAY RELEASED BY CREW 074S06 WE RELOCATED TRANS. POLE UP HILL AND HUNG NEW TRANSFORMER. NEW POLE# IS 216-D4-505 ENTERED MD...HFP VER/HFP L3/HFP IDCC PN213 XXXX
11724 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-09-23 04:30 | 2014-09-23 09:00 | 2 | 270 | 4521151 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNT UP, REPLACED CUTOUT, POWER RESTORED// ISO 37830134C00130/// COD 2// VER/BOW
11725 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-07-07 16:55 | 2016-07-07 17:55 | 9 | 60 | 4558271 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | LINE FUSE OUT ON POLE37830255A00029,PATROLING//FUSE BROKE VER/AWD
11726 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-02-23 10:14 | 2021-02-23 19:14 | 1 | 540 | 4228761 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMER
11727 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2014-01-08 16:30 | 2014-01-08 17:30 | 9 | 60 | H4260791 | 540 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEU. BROKE ON 1/0 LASH CABLE 38830046A20168 REPAIRED NEU. AN 2 HOT LEGS XFORM OFF 16;30 ON 17;30 SEND COPY TO ENG. CHECK SIZE OF SEC. COD-10 VER/HFP L3/HFP IDCC DUP CREATED TO OPEN CAN XXXX
11728 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2015-12-01 19:47 | 2015-12-01 20:05 | 30 | 18 | 4500381 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-10 BAD CUTOUT POLE 45-05 OPEN 40T LINE FUSE NEED CREW/ ALL THREE PHASES ON POLE 45-5 OPENED AT 19:47 TO SAFELY CHANGE BAD CUTOUT/ ETR 20:15/ CUTOUT CHANGED AND LINE FUSES BACK IN AT 20:05 AND TICKET COMPLETE/ CAY SEND NOTE TO ENGINEERING FOR CROSSARM TO BE CHANGED ON POLE 45-10/ ISO 38830045A10005/ COD 30 AJB
11729 | Whitesburg | 3401301 | FLEMING | NEON | 2011-05-13 16:38 | 2011-05-13 18:53 | 4 | 135 | 4086111 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 075H01 FAULT POLE 355-84 IS WRONG. FAULT POLE 355-93 IS CORRECT LOCATION. CUT-OUT GATE IS BLOWN IN-TO. GOING TO CHECK X-FMR TO SEE IF IT IS GOOD, THEN I WILL HAVE TO CHANGE CUT-OUT. X-FMR CHECKED GOOD, REPLACED CUT-OUT AND RESTORED POWER AT 18:53. VER/HFP L3/HFP
11730 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-12-07 11:00 | 2010-12-07 12:00 | 9 | 60 | H63991-1 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TWO OUTSIDE FUSES BLOWN ON POLE 38831027C00604...FOUND TWO CRACKED CUTOUTS ON POLE 38831027C00604...ROGER MAYNARD HAS A CREW IN ROUTE TO CHANGE...WILL HAVE TO OPEN CENTER PHASE WHEN CREW ARRIVES...POWER RESTORED @ 12:00 COD-20 ????? VER/HFP L3/HFP IDCC DUP TO OPEN CENTER PHASE XXXX
11731 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-12-05 22:12 | 2013-12-06 | 5 | 108 | 4103611 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/HFP L3/HFP
11732 | Pikeville | 3414501 | CONSOLIDATE COAL | COAL COMPANY | 2011-03-16 08:36 | 2011-03-16 10:51 | 4 | 135 | 54708-1 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNED LOOSE ON C PHASE, OPENED AND ISOLATED RECLOSER AT POLE 37830088000194 AT 09:30... REPLACED ALL THREE STIRRUPS ON SOURCE SIDE OF POLE 197, CLOSED OCR AT 10:51 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/KEP IDC XXXX
11733 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2021-07-17 11:35 | 2021-07-17 13:50 | 4 | 135 | 4923871 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | isolated broke co @ 330-87 for inactive transformer lf in @ 13:50 on pole 330-14
11734 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2012-10-24 05:25 | 2012-10-24 08:25 | 3 | 180 | 4167301 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND FUSE LINE TO HAVE ROTTED AND BROKE, REPLACED FUSE AND RESTORED POWER AT THIS LOC AT 825 VER/KEP IDC XXXX
11735 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-07-24 08:12 | 2013-07-24 10:00 | 5 | 108 | 4586191 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, POWER RESTORED VER/CRB L/3 CRB IDC XXXX
11736 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-06-30 21:40 | 2020-07-01 02:10 | 2 | 270 | 4096101 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole 39831147C14003 rotted off at ground and leaning over. Wire holding up. 3 phase bank pole 455 , with two runs of underground feeding church. No outage at this time. Need Technician, flaggers, and line crew. Released by crew 078S02,open xfmr @ 2140 repairs made all cust restored @0210 please close ticket thanks.bt
11737 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2018-07-21 17:20 | 2018-07-21 21:50 | 2 | 270 | 4829361 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, I changed it out/ ISO 37830492000036/ COD 2 L3/HFP
11738 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2015-12-23 16:10 | 2015-12-23 16:40 | 18 | 30 | 4553151 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED CONNECTION @ XFMER RISER. CAN OFF @ 16:10, ON @ 16:40//NO OUTAGE TILL TRANSFORMER WAS OPENED VER/CRB
11739 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-06-17 21:51 | 2014-06-18 00:06 | 4 | 135 | 4103961 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD NEUTRAL CONNECTIONS ON THE TRANFORMER POLE THAT WAS MADE UP WITH SPLIT BOLTS.
11740 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2022-03-30 21:15 | 2022-03-31 01:45 | 2 | 270 | 4694711 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 37.5 transformer 7200 120-240 truck ok crew required Released by crew 078S09 Closed at 01:45 Ticket complete.
11741 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-08-03 18:00 | 2013-08-03 18:30 | 18 | 30 | H4619921 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-7034 PRI LOOP BOTTOM OF CUT OUT BURNT OFF INSTALLED ONE NEW CUTOUT REPLACED THE OTHER OPENED CUTOUT 18;00 TO 18;30 30T FUSES BOTH SIDES ORIGINAL 10 CUSTOMER OUT UNTIL 18:00 THEN ALL 28, ALL BACK ON AT 18:30 THIS IS FRON DUPLICATE OF 4619921 VER/SEF
11742 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2009-08-05 09:01 | 2009-08-05 13:31 | 2 | 270 | 61647-1 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, CHECKING FOR TROUBLE, BAD CUTOUT, CALLED FOR HELP, WILLIE ROBINSON SENDING HELP RELEASED BY CREW 080S01 VER/PDP IDC XXXX
11743 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2022-05-05 15:10 | 2022-05-05 19:40 | 2 | 270 | 4841001 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva. 7200 120-240. no trk. side x side,yard dog Released by crew 078S07 Closed at 19:40. Voltage checked good. Ticket complete.
11744 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-08-01 08:05 | 2015-08-01 11:05 | 3 | 180 | 4965551 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE OPEN ON POLE 472-10, SPLICE PULLED OUT IN MID SPAN , MADE REPAIRS RESTORED POWER AT 11:05.// VER/ ADH
11745 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-04-24 09:50 | 2012-04-24 10:10 | 27 | 20 | 4702091 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW TRANSFERING CONDUCTORS TO NEW POLE HAD TO OPEN RECLOSERS TO ALLOW THEM TO REPAIR CONDUCTOR & TRANSFER IT TO NEW POLE // COD-27 ISO OCR @ 38830067A16022 VER/HFP L3/HFP IDC XXXX
11746 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-02-19 10:14 | 2015-02-19 10:50 | 15 | 36 | 4042471 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELATED TO 4041331 // CREW OPENED RECL @ 1014 TO ALLOW THEM TO OPEN FUSE ON POLE 38830905000036//COD 16// VER/HFP L3/HFP
11747 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-07-09 02:30 | 2011-07-09 07:00 | 2 | 270 | 4494971 | 540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 0325 / 3 PHASE TR ISOLATED DUE TO FAILED CUT OUT. POLE WILL NEED TO BE REPLACED. CB OPENED TO ISOLATE TR ON PO ORDER 4494971.MADE TEMP REPAIRS AND CLOSED IN AT 0700. SEND COPY TO CLIFF FREEMAN, POLE NEEDS TO BE CHANGED LATER VER/PDP IDC XXXX
11748 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-10-21 09:53 | 2017-10-21 11:10 | 7 | 77 | 4475121 | 539 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 69-1346 CHGED BAD 1350 INSULATOR AND OID CUTOUT/ ISO 38830069A31346/ COD 7/ VER/BOW L3/HFP XXXHFP
11749 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-07-11 08:26 | 2014-07-11 09:15 | 11 | 49 | 4228531 | 539 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 182-144 6T UNKNOWN MP VER/CRB
11750 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-05-14 14:43 | 2022-05-14 16:00 | 7 | 77 | 4890021 | 539 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew rquired bad cutout 249-174 line fuse on 249-86
11751 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-07-06 14:50 | 2008-07-06 19:19 | 2 | 269 | 63218-1 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SERVICER WORKING ON LARGER OUTAGE (CIRCUIT OUTAGE) WILL WORK THIS NEXT.BROKEN FUSE ON POLE 284-31 20T. VER/HFP IDC XXXX
11752 | Pikeville | 3402002 | KEYSER | STONECOAL | 2016-02-25 07:15 | 2016-02-25 11:44 | 2 | 269 | 4770661 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE BURNED POLE OFF AT T BRACKET . THERE IS A 120/240 XFMR & 240/480 ON THIS POLE . CONTRACTOR JOSEPH SAMMONS WILL BE WORKING THIS. & HE HAS MATERIAL LIST. RELEASED BY CREW 074S04//MADE MDC TO SHOW 15T L/F ON POLE 1152-133// ISO 38831152000133 COD 2 VER/AWD
11753 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-03-26 20:22 | 2013-03-27 05:20 | 1 | 538 | 4960591 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BOTTOM OF CUTOUT BROKE OFF, TOP IS STILL HOT. NEED TWO MEN AND BIG BUCKET. CAN SET UP AND REACH ACROSS THE CREEK AT GREEN MAILBOX WITH #2520 ON IT NEXT TO RED TOCOMA TRUCK ON THE LEFT. WILL WORK ON 3-27-13 CREW CALLED TO A LARGER OUTAGE VER/KEP IDCC PN61 XXXX
11754 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-03-04 08:47 | 2017-03-04 17:45 | 1 | 538 | 4518831 | 538 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY CONNECTION AT POLE 38821137A00580.
11755 | Hazard | 3303901 | LESLIE | HYDEN | 2010-07-25 18:47 | 2010-07-26 03:45 | 1 | 538 | 56973-1 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VINES ON POLE REFUSED XFMR HAS A K MATE IN TOP OF CUTOUT BAD RELEASED BY CREW 077H03---RESTORED AT 0345--K MATE IDC XXXX
11756 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2021-04-16 18:56 | 2021-04-16 23:25 | 2 | 269 | 4457541 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a long span of open wire secondary down from pole 195-3 up to 195-4,Will need Line crew to help make repairs,These poles R Manually poles,Will be opening XFM on 195-3 will keep up with Time.Wire size is #4 solid copper..Opened Trans @ 09:54 Restored @11:25.. LR- First all out call is at 18:56
11757 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-12-31 14:26 | 2011-12-31 18:55 | 2 | 269 | 4218721 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 FUSE OUT ON BANK OF XFMRS, CUTOUT IS BROKE, CALLING FOR BIG BUCKET AND 2 MEN, ( ROAD WILL NEED WATCHED ) ///VER/CRB IDC XXXX
11758 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-09-05 10:22 | 2011-09-05 14:51 | 2 | 269 | 4816691 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN//19.9 CUTOUT BROKEN// CALLED DALE FOR BIG BUCKET RELEASED BY CREW 074H14-WILL CHG CUT-OUT COD-2 ISO TF3883101D20669 VER/HFP L3/HFP IDC XXXX
11759 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2014-12-29 08:41 | 2014-12-29 13:10 | 2 | 269 | 4889181 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED , TAGGED FOR G. JUSTICE, AND GROUNDED AT POLE 38831121D00198 ..REPLACED CROSSARM AND CUTOUT , ALL WORK COMPLETE / GXJ// COD 2// VER/ ADH
11760 | Hazard | 3310502 | HADDIX | CANOE | 2008-01-25 14:21 | 2008-01-25 18:50 | 2 | 269 | 59897-1 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3310502//10KVA CSP BAD//CSP TRANSFORMER TRIPPED OUT-HAD TROUBLE STAYING ON--0N AT 1600--UNKNOWN CREW TO REPLACE WITH 15 KVA-BUCKET JOB -- 2 MEN---WILL NEED CUTOUT--POLE25-80----7.2--TIED IN TO OUTAGE TODAY RELEASED BY CREW 077S06 - COD 2 - ISO/FLT - 37830025000080// VER/TOM IDC XXXX
11761 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-11-16 07:21 | 2016-11-16 11:50 | 2 | 269 | 4104161 | 538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR. IS OPEN AND I CAN NOT GET IT TO RESET OR CLOSE BACK IN , JEFF BAKER IS COMMING TO CHANGE OUT XFMR. RELEASED BY CREW 077S12. POWER RESTORED AT 11:50 VOLTAGE CHECKED GOOD./ ISO 37830445000063/ COD 2/ VER/BOW
11762 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-04-06 13:25 | 2018-04-06 16:24 | 3 | 179 | 4196091 | 537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | meter is blank Hot line clamp failed./ ISO 37830213000002/ COD 3
11763 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-09-01 15:36 | 2020-09-01 18:35 | 3 | 179 | 4414891 | 537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew req, have a broke c/o on 1073-2092, need crew to chg is in 3 phase, can get truck to pole cable co has been to this pole, with truck Released by crew 078S06///complete BR
11764 | Hazard | 3303901 | LESLIE | HYDEN | 2018-04-17 07:31 | 2018-04-17 10:30 | 3 | 179 | 4243531 | 537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cod 3 iso 37830412C00275 BAD 19.9 CUTOUT Restored @ 1030 // POLE 37830412C00275 IS BAD AND IS NEED OF REPLACMENT, MADE SAFE FOR NOW. Sent to Wayne D Christian // JEM
11765 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-10-02 23:03 | 2013-10-03 08:00 | 1 | 537 | 4906321 | 537 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | ONE LEG OF LASH IS DEAD , I CAN NOT GET INTO XFMR FOR VEHICLES I AM GOING TO TRY IN THE MORNING RELEASED BY CREW 077S12//. I REMADE CONNECTIONS BETWEEN THE XFMR AND LASH SECONDARY//COD 1 VER/HFP L3/HFP IDC XXXX
11766 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-01-25 15:01 | 2010-01-25 18:00 | 3 | 179 | 59609-1 | 537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830247D00820 WE HAVE C/O BAD, THIS IS ISOLATING POLE. XFMR POLE IS 37830247D00862 THAT SERVES THIS CUST. CHANGED OUT C/O, POWER RESTORED. ENTERED MD COD-3 ISO LF 37830247D00820 IDCC PN1203 XXXX
11767 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-12-28 09:03 | 2009-12-28 18:00 | 1 | 537 | 60056-1 | 537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | NEED TO REPAIR GUY WIRE, 1500 FOOT SPAN OF OPEN SEEC AND POLE IS PULL OVER. THIS IS AT 1419 STRAY BR. NOT 1429 ON LEFT, RED HOUSE WITH CEDER TREES INFRONT OF POURCH RELEASED BY CREW 077S05
11768 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-05-30 20:01 | 2011-05-30 23:00 | 3 | 179 | 4211441 | 537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 25 KVA TRANS. IS BAD. TIM MCCOY IS SENDING HELP. RELEASED BY CREW 074S01TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 25 KVA TRANS. IS BAD. TIM MCCOY IS SENDING HELP. ERIC MCKINNEY IS BRINGING NEW TRANS.TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 25 KVA TRANS. IS BAD. TIM MCCOY IS SENDING HELP. ERIC MCKINNEY IS BRINGING NEW TRANS. WE CHANGED TRANS. //VER/GAH IDC DCMT XXXX
11769 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-12-10 23:23 | 2011-12-11 02:22 | 3 | 179 | 4168161 | 537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 352-247 WILL NEED ONE MAN BIG BUCKET ,3 CUSTOMERS AFFECTED.. REPLACED XFMR RESTORED POWER AT 02:22. CC 3. VER/SDB IDC XXXX
11770 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-04-22 12:26 | 2015-04-22 15:25 | 3 | 179 | 4353131 | 537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP FELL APART ON TRANS., REPLACED CLAMP AND CLOSED BACK IN AT 1525./COD 3// VER/ ADH
11771 | Pikeville | 3413401 | GARRETT | GARRETT | 2020-05-16 11:02 | 2020-05-16 15:30 | 2 | 268 | 4842011 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 - 15 Kva transformer. Can truck. Crew enroute to replace. Released by crew 076S02//REPAIRSMADE @ 15:30
11772 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-01-04 10:46 | 2022-01-04 13:00 | 4 | 134 | 4298471 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Customer states nothing in home is working, changed all connections on our side, made repairs @1300.
11773 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-03-10 16:45 | 2011-03-10 18:59 | 4 | 134 | 53094-1 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WR# 39122671 // HOT TAP BROKE OFF SEND TO P.T. RELEASED BY CREW 078S08//PRT ON SITE//REPAIRED HOT TAP LEAD ALL POWER RESTORED AT 18:59 PRT//COD 1// VER/DBM IDC CHANGED COUNT FROM 1 XXXX
11774 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2009-10-28 05:58 | 2009-10-28 08:12 | 4 | 134 | 60181-1 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP 3000903// FUSE LINK ROTTENED AND BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC L3/HFP IDC XXXX
11775 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-02-14 21:47 | 2020-02-15 02:15 | 2 | 268 | 4407221 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411802/gaj/2152/all out disp 3542 T FieldsSERV DROP BURNED INTO@A SPLICE,WILL REPAIR, //////////////MADE NECESSARY REPAIRS. SEEMED TO BE OKAY NOBODY CAME TO THE DOOR.
11776 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-11-25 08:22 | 2018-11-25 12:50 | 2 | 268 | 4474911 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Mis-mapped: 533734542 o 38830905000118.190871472 o 38830905B40256. 533735593 o 905-69. ONLY TWO CUST OUT on 905-70. Replaced damaged sec and restored @ 12:50. sh/ ISO 38830905000070/ COD 2/ MD DONE L3/HFP
11777 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-09-25 05:17 | 2012-09-25 09:45 | 2 | 268 | 4084551 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN ON POLE 37820035A00012  APPEARS FUSE BROKE  REPLACED FUSE AND POWER RESTORED @ 09:45 ///VER/CRB L/3 CRB IDC XXXX
11778 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2019-06-17 09:34 | 2019-06-17 18:30 | 1 | 536 | 4522841 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | serv to house burnt into need crew to repair .bt Released by crew 078H02 / restored 18:30, released 078H14 bah
11779 | South Williamson | 3411401 | DEWEY | INEZ | 2017-11-29 14:31 | 2017-11-29 16:45 | 4 | 134 | 4609731 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cust mismapped. Off of 38820745B00136. Broken cutoutcutout broke on pole 745-136//could not reach cutout with my bucket// i cleared up cutout and put hot tap lead from tap to line to get power back on//line crew will install new cutout here in a couple days when they have big bucket over here/restored at 16:45///complete//em
11780 | South Williamson | 3411401 | DEWEY | INEZ | 2017-04-29 18:37 | 2017-04-29 23:05 | 2 | 268 | 4695921 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 19.9 XFMR//TRUCK ACCESS//NEED ONE MAN AND BIG BUCKET//XFMR CHANGED //RESTORED AT 23:05//COMPLETE//EM
11781 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-09-12 13:52 | 2022-09-12 16:06 | 4 | 134 | 4872051 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F open on 38820985000029 // bad c/o on pole 985-30 // repairs made and RESTORED @ 16:06
11782 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2013-07-21 15:46 | 2013-07-21 18:00 | 4 | 134 | 4570911 | 536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN// WILL REFUSE// BAD 50 KVA// CREW ENROUTE// XFMR. REPLACED// POWER IS RESTORED VER/CRB L/3 CRB
11783 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-02-16 17:18 | 2020-02-16 19:05 | 5 | 107 | 4410281 | 535 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | broke cutout on xfm bank pole 38831083C20104.. need one man with big bucket and 2 7200 cutouts.opened other 2 xfmrs at 19:42. restored all at 19:05 L3/HFP
11784 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-07-24 00:51 | 2017-07-24 09:46 | 1 | 535 | 4169151 | 535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST. OLD DOOR FELL APART BACK IN AT 0946. PLS CLOSE. TRE VER/CRB L3/HFP XXXHFP
11785 | Hazard | 3309302 | VICCO | JEFF | 2015-07-19 19:28 | 2015-07-19 21:15 | 5 | 107 | 4912991 | 535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN POLE 251-10, HAVE BAD ARRESTOR ON POLE 251-21///ARRESTOR CHANGED, POWER RESTORED/ ISO 37830251000010/ COD 5
11786 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2019-07-16 18:03 | 2019-07-16 21:01 | 3 | 178 | 4718161 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad Hot line clamp on pole 902C521---made repairs---pwr restored @ 21:01---tbl tkt comp
11787 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-09-27 14:32 | 2008-09-27 16:01 | 6 | 89 | 51428-1 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP LIGHTING ARRESTER BAD ON POLE 38820673D00047 COD - 6 IDC XXXX
11788 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-02-23 15:17 | 2008-02-23 18:15 | 3 | 178 | 66557-1 | 534 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTIONS ON XFMR POLE CUST STILL HAVING PROBLEMS WITH 2 ROOMS IN HOUSE ADVISED TO GET ELECTRICAN TO CHECK RELEASED BY CREW 077S09//3303903//VER/CRB IDCC CCCE, BRIGHT DIM CALL BUT CUST ADVISED TO TURN OFF BREAKER SO LEFT START TIME ALONE XXXX
11789 | Pikeville | 3421001 | BREAKS | CITY | 2015-04-10 15:03 | 2015-04-10 19:30 | 2 | 267 | 4305211 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON TRANSFORMER 243-203, SERVICER CHANGING NOW/COD2/ RELEASED BY CREW 074S02/OPENED RECLSOER 243-46 TO MAKE REPAIRS/RELATED TO OUTAE 43068521// VER/ ADH
11790 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-04-25 07:26 | 2014-04-25 08:55 | 6 | 89 | 4631571 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 50T FUSE OUT B PHASE DUE TO A BAD CUTOUT ON POLE 1098-723. CHANGED CUTOUT FUSED UP EVERYTHING OK//COD 6// VER/DBM
11791 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-03-10 22:27 | 2010-03-10 23:56 | 6 | 89 | 64833-1 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT VER/ARN IDC XXXX
11792 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-10-29 22:26 | 2016-10-30 02:53 | 2 | 267 | 4062781 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA, 7200 120-240, CHANGE CO & ARRESTER TRK OK. RELEASED BY CREW 078S07/CREW ON SITE/FETR0330/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0253/PLEASE CLOSE TICKET/THANKS/VEM VER/TOM L3/TOM
11793 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2018-12-23 12:07 | 2018-12-23 15:05 | 3 | 178 | 4594641 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 37830329000196 service burned down going to church. we put it back up, this needs to go to Doug Christian for a upgrade it needs larger service. COD-3 L3/HFP
11794 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-02-02 03:22 | 2013-02-02 07:49 | 2 | 267 | 4784691 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA, 7200V. TRUCK OK. LINECREW REQUIRED. RELEASED BY CREW 078S11/CREW ON SITE/FETR0815/VEM/XFMR REPLACED AND POWER RESTORED TO ALL CUST 0749/PLEASE CLOSE TICKET/THANKS/VEM //VER/GAH IDC XXXX
11795 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-01 12:20 | 2012-02-01 15:18 | 3 | 178 | 4312721 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. I HAD TO CHANGE CUTOUT. IT WAS NOT BAD BUT OLD AND I COULD NOT REFUSE FROM GROUND, SO I CLIMBED POLE AND CHANGED IT. I HAD TO OPEN CENTER LINE FUSE ON THIS POLE TO GET PROPER CLEARANCE. I OPENED AT 15:05 AND CLOSED IT AT 15:18. ALL POWER IS BACK ON NOW. VER/KEP IDC XXXX
11796 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-08-31 11:12 | 2011-08-31 15:39 | 2 | 267 | 4777871 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE//////BAD XFR ON 9-146,NEED 25KVA 19.9.CAN USE TRUCK RELEASED BY CREW 074S06 //VER/CRB IDC XXXX
11797 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2011-04-07 18:58 | 2011-04-07 23:25 | 2 | 267 | 51556-1 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39486628 // POLE 138-201 BAD 37.5 TRANS NEED 50KVA NO TRUCKS TRACK MACHINE CUTOUT AND T BRECKET RELEASED BY CREW 078S08/CREW ON SITE///REPAIRS COMPLETE POWER RESTORED @ 23:25 J. HEMLEPP & CREW COD-2 ISO TF 38830138C00201 VER/HFP L3/HFP
11798 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-02-28 07:54 | 2018-02-28 10:52 | 3 | 178 | 4889291 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse open on pole 353-233, bad cutout on pole 353-157, made repairs restored power at 10:52..
11799 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-01-26 06:24 | 2018-01-26 09:22 | 3 | 178 | 4774301 | 534 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | restored 0922/ ISO 37830376B00045/ COD 3
11800 | Pikeville | 3413402 | GARRETT | LACKEY | 2014-05-08 17:15 | 2014-05-08 21:42 | 2 | 267 | 4675701 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN WILL RE-FUSE. BAD 25 KVA NEED 1 MAN. REPLACED BAD TRANSFORMER AND REPLACED CUT-OUT. CLOSED TRANSFORMER IN @ 21:42 RESTORING SERVICE THEY WERE 2 CUSTOMERS OUT//COD 2?// VER/DBM
11801 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-06-09 16:26 | 2013-06-10 01:20 | 1 | 534 | 4243521 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE PULL INTO , POWER RESTORED AT 0120 //VER/GAH IDCC CDC83 XXXX
11802 | Whitesburg | 3312901 | JENKINS | KONA | 2010-11-23 20:12 | 2010-11-23 21:41 | 6 | 89 | 59146-1 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP X-FMR KICKED OUT. RESET X-FMR AND RESTORED POWER AT 21:41. J. BAKER//COD 6// VER/DBM IDC XXXX
11803 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-01-03 19:48 | 2010-01-04 00:15 | 2 | 267 | 59239-1 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR# 33287513 // BAD TRANSF == 1MAN & BI8G BUCKET AND NEED 25 KVA TRANSF 19.9 VER/LDA IDC XXXX
11804 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2008-06-16 10:18 | 2008-06-16 14:45 | 2 | 267 | 65470-1 | 534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3004301// HAVE A BAD 25 KVA TRANSFORMER, AT THIS LOCATION, NEED CREW TO CHANGE IT OUT, HAS 2 CUST ON IT CAN USE TRUCK, SINGLE BUSHING, 7200 120/240 ///STS WR# 24798467//CREW ON SITE /FETR1545/VEM/POWER RESTORED 1441/PLEASE CLOSE TICKET/THANKS/VEM // VER/TOM IDCC CNT1 XXXX
11805 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-06-11 07:02 | 2014-06-11 15:55 | 1 | 533 | 4049481 | 533 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED ONE 19.9 15KVA 277-480V XMF AND ALL THREE CURRENT LIMMITING FUSES APR AT 1450 CLOSE TICKET VER/HFP L3/HFP
11806 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-03-04 02:28 | 2014-03-04 11:21 | 1 | 533 | 4449391 | 533 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN WILL REFUSE , BAD XFMR NEED 15KVA 19.9 , CUTOUT AND T BRKT REPLACED TRANSFORMER AND RESTORED POWER AT 1121 VER/CRB
11807 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-04-10 08:07 | 2015-04-10 10:20 | 4 | 133 | 4301741 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830182A00148, CAN REPLACE MYSELF, POWER RESTORED//MADE MDC COD 4// VER/CRB
11808 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2018-03-03 17:21 | 2018-03-03 18:37 | 7 | 76 | 4956041 | 532 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | called customer: flickering ever since wind storm/strong breeze makes lights go out/back on. bad connection. repaired 1837
11809 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-08-27 14:59 | 2009-08-27 16:15 | 7 | 76 | 53942-1 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3311101//REPLACING POLE 625-7 CLOSED @ 1615 - CAUSE CODES OK PER DALE // VER/TOM IDC XXXX
11810 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2011-02-27 07:39 | 2011-02-27 12:05 | 2 | 266 | 63387-1 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. WE HAVE A BAD TRANS. I AM CALLING DALE FOR HELP. WE CHANGED 10 KV TO A 15 KVA. // SENT MAP DISC VER/TOM IDCC PN22 XXXX
11811 | Pikeville | 3408103 | SALISBURY | MARTIN | 2013-06-13 14:02 | 2013-06-13 18:28 | 2 | 266 | 4281311 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED UP WHEN FUSE BLEW ,HAVE REPLACED DOOR, COUSTOMER IS NOW IN SERVICE COD 2 ISO TF 1098C-773 VER/SEF IDC XXXX
11812 | Hazard | 3301401 | COMBS | COMBS | 2017-11-26 04:43 | 2017-11-26 06:56 | 4 | 133 | 4602191 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
11813 | Hazard | 3303902 | LESLIE | WOOTON | 2018-02-14 11:34 | 2018-02-14 16:00 | 2 | 266 | 4839871 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no anwer/// BAD CUTOUT
11814 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2018-05-30 17:24 | 2018-05-30 19:37 | 4 | 133 | 4523321 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CUTOUT GATE
11815 | Hazard | 3309003 | JEFF | VIPER | 2018-04-23 00:08 | 2018-04-23 09:00 | 1 | 532 | 4263221 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer, lights going dim, to off, to dim and then to full brightness. advised customer to turn off main breaker to avoid damage//may have loose connection//please check for unsafe condition//attempted callout but no takers from servicer list, per Jim Mullins, ok to hold until the A.M. restored @ 0900 L3/HFP
11816 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2013-10-11 07:52 | 2013-10-11 10:05 | 4 | 133 | 4929391 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. REFUSED @ 10:05. SH VER/CRB L/3 CRB
11817 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-10-16 09:09 | 2021-10-16 13:35 | 2 | 266 | 4355371 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, on @ 1335
11818 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-12-06 15:17 | 2015-12-06 17:30 | 4 | 133 | 4513921 | 532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE MELTED OUT.REPLACED FUSE// VER/ ADH
11819 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-12-24 18:33 | 2008-12-24 21:30 | 3 | 177 | 63643-1 | 531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3413402// BAD CUTOUT ON ON ARM NOT ABLE TO GET TRUCK TO I SHOULD BE ABLE TO CHANG IT OUT. CHANGED CUTOUT EVERYTHING OK. SEND COPY TO RON RYE PIKEVILLE FRONT CROSS ARM ON A SINGLE PHASE DEAD END POLE IS BURNT ABOUT HALF WAY INTO. NEEDS CHANGED//COD 3//EMAILED TO R RYE// VER/DBM L3/KEP IDC XXXX
11820 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2011-03-21 19:39 | 2011-03-21 22:36 | 3 | 177 | 56511-1 | 531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLING CREW RELEASED BY CREW 078S07///FIXED IT!!!!//VER/CRB IDC XXXX
11821 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-07-12 09:50 | 2009-07-12 12:47 | 3 | 177 | 62603-1 | 531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP FOUND BAD CUTOUT DOOR, HAVE REPLACED AND IS RESTORED AT THIS LOC COD-3 ISO TF 39830901C24598 L3/HFP IDC XXXX
11822 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2013-12-22 01:22 | 2013-12-22 10:13 | 1 | 531 | 4183901 | 531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 45-3699 RISER BROKE ON CUTOUT REPAIRED RELEASED BY CREW 078S08 ****CHANGE ISO POLE 1 CUSTOMER****** VER/SEF L3/HFP
11823 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2008-09-12 15:57 | 2008-09-12 18:54 | 3 | 177 | 61955-1 | 531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3302701//LINE CUTOUT BROKEN REPLACED CUTOUT P HICKMAN//COD 3// VER/DBM IDC XXXX
11824 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-11-25 09:01 | 2013-11-25 10:00 | 9 | 59 | 4071931 | 531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 68-500 CHGED 1301 1350 AND LA 68-498 40T FUSE TREE CREW HERE CUTTING TREES COD-9 ISO LF 38830068D00498 CHECK FOR DUP IN HOIS - THIS WAS IN FOR A TIME AND THEN WENT BACK OUT VER/HFP L3/HFP
11825 | Cannonsburg | 3001401 | LOUISA | CITY | 2009-07-14 07:09 | 2009-07-14 16:00 | 1 | 531 | 54064-1 | 531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ,,8FT CROSSARM BROKE ON A SET OF DOUBLE ARMS, POLE HAS BANK OF TRANSFORMERS ON IT FEEDING WATER TREATMENT PLANT ACROSS FROM LISAS FRONT PORCH. CREW WILL NEED 2 8FT CROSSARMS WITH BRACES,AND 1 CUTOUT FOR 7200V, IT IS TRUCK ACCESSIBLE THROUGH THE WATER PLANT RELEASED BY CREW 078S02...HAVE OUTAGE SCHEDULED FOR 8PM TO MAKE REPAIRS..WILL BE SAFE TILL THEN...BLR IDC XXXX
11826 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-06-25 18:00 | 2016-06-26 02:50 | 1 | 530 | 4475101 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 15KVA TRUCKS OK/METER IS PULLED ON BASE RELEASED BY CREW 078S03,, CREW ON SITE FETR 300.. RESTORED AT 2:50 AND COMPLETE CY VER/ARN
11827 | Hazard | 3309302 | VICCO | JEFF | 2010-06-08 07:12 | 2010-06-08 07:22 | 53 | 10 | H58577-1 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELATED TO 58577-1//OPENED N.C. SWITCHES ON 345-C-369 IN ORDER TO MAKE REPAIRS @ 07:12 INTERRUPTING 53 ADDITIONAL CUSTOMERS//CLOSED BACK AND RESTORE POWER TO ALL CUSTOMERS @ 0722// VER/DBM IDC XXXX
11828 | Hazard | 3420001 | SOFT SHELL | VEST | 2021-05-19 13:05 | 2021-05-19 17:30 | 2 | 265 | 4599991 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 107-6, manuel, calling for help, this is a line fuse cutout, all power restored// off at 1305 on at 1730
11829 | Pikeville | 3120102 | STANVILLE | TRAM | 2022-02-27 13:59 | 2022-02-27 15:45 | 5 | 106 | 4550041 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers service drophad burndt upin 2 spots, I changed it out, only 1 customer was affected. Restored @1545.
11830 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-12-19 08:50 | 2012-12-19 13:15 | 2 | 265 | 4481991 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE PRIMARY UP SOLID.THIS IS PROTECTED BY A LINE FUSE ON POLE #38830955D00160 VER/KEP
11831 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-03-19 09:55 | 2017-03-19 14:20 | 2 | 265 | 4570151 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 227D-82 , CLOSED FUSE BACK AT 14:20/ ISO 37830227D00082/ COD 2/ VER/BOW
11832 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-12-21 16:00 | 2011-12-21 16:53 | 10 | 53 | 4193511 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 472-102 ,OPENED LINE FUSE ON POLE 472-56 TO ISOLATE, REPLACED CUTOUT RESTORED POWER AT 16:53//COD 10 IDC XXXX
11833 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-07-18 09:50 | 2015-07-18 14:15 | 2 | 265 | 4905901 | 530 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL HAS PULLED OUT OF A STRESS SLEEVE IN MID SPAN OF SERVICE DROP. I AM GOING TO LET DROP DOWN AND RESQUEEZE CONNECTIONS, I REPAIRED DROP
11834 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-06-07 20:05 | 2021-06-08 00:30 | 2 | 265 | 4684301 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25kva xfmr bad.. truck access.
11835 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-01-08 01:05 | 2012-01-08 05:30 | 2 | 265 | 4240591 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAVE 1/0 TRIPLEX SECONDARY BURNED DOWN. WILL CLEAN VINES FROM POLE & REPLACE SECONDARY. VER/PDP IDC XXXX
11836 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-08-10 08:24 | 2014-08-10 12:49 | 2 | 265 | 4349771 | 530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 162-73 BAD 25KVA CSP TRUCK TO POLE RELEASED BY CREW 078S08/CREW ON SITE/FETR1245/VEM/NEED TO RELOCATE XFMR ON POLE/NEW FETR1330/VEM/REPAIRS MADE AND ALL CUST RESTORED 1249/PLEASE CLOSE TICKET/THANKS/VEM// COD 2//VER/ ADH
11837 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2009-09-03 09:20 | 2009-09-03 18:09 | 1 | 529 | 62945-1 | 529 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP WORK REQUEST # 31560312 //RELEASED BY CREW 080S01FUSE OUT ON POLE 966-A-642.BAD UNDERGROUND. CREW WILL REPAIR WHEN THEY GET HERE.NEW F.E.T..R. 18:00 COD-1 ISO UGD 38820966A00642 L3/HFP IDC XXXX
11838 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-03-04 08:17 | 2015-03-04 10:29 | 4 | 132 | 4097031 | 528 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830900000027 VER/CRB L3/DKGXXXX
11839 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-03-09 21:57 | 2015-03-09 22:45 | 11 | 48 | 4174871 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP FELL OFF OF STIRRUP 37820150A00104 VER/CRB
11840 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-03-27 11:08 | 2010-03-27 12:36 | 6 | 88 | 54920-1 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN//// REPLACE FUSE ,POWER RESTORED. FUSE BROKE COD=6 VER/HFP L3/HFP IDC XXXX
11841 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2014-07-13 11:45 | 2014-07-13 16:09 | 2 | 264 | 4234021 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 19.9 TRANS. BRING 25KVA 19,9 CURRENT LIMING FUSE TRUCK TO POLE RELEASED BY CREW 078S08/CREW ON SITE/FETR1700/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1609PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
11842 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2012-06-05 12:17 | 2012-06-05 16:41 | 2 | 264 | 4884001 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA NEED 37.5 TRUCK MAYBE TO POLE CALL 3317 HARD PLACE TO FINE RELEASED BY CREW 078S08/CREW ON SITE/FETR 1715/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1641/PLEASE CLOSE TICKET/THANKS/VEM COD-2 ISO TF 38830044D47556 VER/HFP L3/HFP IDC XXXX
11843 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-03-15 04:03 | 2017-03-15 06:15 | 4 | 132 | H4557931 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #6A PRIMARY DOWN ON 905-62. OPENED REC 905-7 @ 4:03. 4CC OUT TO START 4 MORE AT 0403/#6A PRIMARY DOWN ON 905-62. OPENED REC 905-7 @ 4:03. MADE REPAIRS AND CLOSED REC @ 6:15. SH RELEASED BY CREW 076S02 VER/KEP
11844 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-10-02 21:22 | 2013-10-03 01:46 | 2 | 264 | 4906231 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, REPLACED XFMR. VER/KEP L3/HFP IDC XXXX
11845 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-01-09 07:53 | 2021-01-09 10:05 | 4 | 132 | 4857901 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop had burned into and csp xfmr open//i pulled drop back upand repaired connections//restored t 10:05//complete//em
11846 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2022-02-21 09:46 | 2022-02-21 14:10 | 2 | 264 | 4522821 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required on hillside no trucks Released by crew 078S03repairs made all cust restored @ 1410 please close ticket thanks.bt
11847 | Pikeville | 3120102 | STANVILLE | TRAM | 2022-08-02 08:46 | 2022-08-02 13:10 | 2 | 264 | 4661021 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke in 4/0 quad secondary and is about 10ft above roadway, transformer hotleg burnt in 2 at XFM, will have to open XFM bank on 1101-480 to safely make repairs, will keep up with times// off @ 12:36, on @ 13:10
11848 | Whitesburg | 3401301 | FLEMING | NEON | 2008-11-30 07:44 | 2008-11-30 08:50 | 8 | 66 | 53100-1 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK WAS BROKE AND I REPLACED IT//VER/CRB IDC XXXX
11849 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-05-21 03:42 | 2016-05-21 12:30 | 1 | 528 | 4242211 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUES MUST HAVE BROKE// VER/ ADH
11850 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2019-12-30 17:59 | 2019-12-30 19:05 | 8 | 66 | 4197211 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke into , I replaced it
11851 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-05-25 14:21 | 2011-05-25 18:45 | 2 | 264 | 4167751 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN BACK ON HILL// LINE FUSE BLOWN @ 1125-158/// CHANGED CUTOUT// REFUSED LINE FUSE// ALL BACK TO NORMAL VER/KEP
11852 | Pikeville | 3407101 | TOPMOST | DEMA | 2022-11-25 07:24 | 2022-11-25 10:20 | 3 | 176 | 4178931 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Span of secondary down from 210-6 to 210-64 no truck access.//Opened xfm @ 9:33 to make repairs.//Repairs made and restored @ 10:20
11853 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-08-11 19:36 | 2010-08-12 04:24 | 1 | 528 | 53021-1 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1083-1086 IDCC PN736, CNT5 XXXX
11854 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-09-07 09:23 | 2012-09-07 11:35 | 4 | 132 | 4026181 | 528 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | HOT LEAD IN TRANSFORMER { RISER WIRE } BURNED INTO AT BUSHING OF TRANF. I AM GOING TO OPEN TRANS. AND REPLACE RISER WIRE. I REPLACED RISER WIRE. CUSTOMER SAID AC UNIT WOULD NOT KICK BACK ON. I TOLD HIM IT PROBABLY HAD A TIMED RELAY SWITCH. ///VER/CRB L/3 CRB IDC XXXX
11855 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-09-23 07:59 | 2013-09-23 10:55 | 3 | 176 | 4878541 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED TRANSFORMER FUSE.//COD 3// VER/DBM
11856 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-01-17 04:52 | 2009-01-17 06:20 | 6 | 88 | 56739-1 | 528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3409303// WILL REPLACE TRANSFORMER/3409303// BAD CSP XFMR. CREW ENROUTE TO CHANGE.3409303// BAD CSP XFMR. CREW ENROUTE TO CHANGE. RELEASED BY CREW 076S02// CLOSED TRANSFORMER BACK IN.. WILL CHANGE DURING DAYLIGHT VER/KEP L3/KEP
11857 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-03-13 19:09 | 2009-03-13 19:40 | 17 | 31 | 58290-1 | 527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3404302//RELATED TO ORDER 58267-1//OPENED THIS RECLOSER UP TO MAKE LOOP BACK (LOOP HAD FAILED//COD 17// VER/DBM IDC XXXX
11858 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2017-04-21 12:45 | 2017-04-21 13:02 | 31 | 17 | 4664531 | 527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OUTAGE NECESSARY TO SAFELY MAKE REPAIRS TO ELECTRICAL FACILITIES. APPROXIMATELY 15 MINUTE OUTAGE. 1245-1302 OCR 37830139A40429 FAULT 37830139A40071 31LOOP BURNT INTO POLE 139-71. OPENED RECLOSER ON POLE 139-A-429 AT 12:45 CLOSED BACK IN AT 13:02 EVERYTHING OK VER/AWD // PER VOICE REC NO OUTAGE UNTIL RECLS OPENED = L3/HFP XXXHFP AJB
11859 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-10-04 08:55 | 2018-10-04 17:42 | 1 | 527 | 4195691 | 527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | will need to replaced xfmr cutout and arrester, no truck access
11860 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-07-04 14:48 | 2010-07-04 15:05 | 31 | 17 | 62114-1 | 527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOW SIDE STEPDOWN FUSE BLOWN ON 1111-D-178...PATROLLING...FOUND PROBLEM...LOW SIDE FUSE NOT BLOWN...CUT OUT BROKEN...DOOR JUST FELL OPEN....WILL REPLACE...//....ISOLATED STEPDOWN XFMR....REPLACED BAD CUTOUT....CLOSED....POWER ON NOW...JRV...07/04/10//VER/CRB IDC XXXX
11861 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-12-10 19:43 | 2009-12-11 04:30 | 1 | 527 | 54331-1 | 527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED TRANSFORMER VER/KEP L3/KEP IDC XXXX
11862 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-07-14 22:14 | 2020-07-14 22:45 | 17 | 31 | 4165411 | 527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 38830116B00686 arrestor blew on innactive transformer. Lifted hot tap. 40t on 38830116A00250 back in @ 22:45
11863 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-05-31 09:09 | 2010-05-31 17:56 | 1 | 527 | 54130-1 | 527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA XFR.?? TRIED FUSE, FUSE BLEW IMMEDIATELY. MR. GOODALL CELL NUMBER 606-232-1177. HE MAY BE AT WORK WHEN CREW ARRIVES. TRUCK OK. RELEASED BY CREW 078E01//VER/CRB IDC XXXX
11864 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-07-06 19:35 | 2009-07-06 23:58 | 2 | 263 | 54701-1 | 526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3103101//BAD 10KVA XFMR, CONTACTED CREW, NEED TO GO BACK WITH AT LEAST 15KVA, TRUCK OK, PLEASE SEND TICKET TO JIM LINKOUS. RELEASED BY CREW 078S05 WORK REQUEST - 30610670 //VER/GAH IDCC XXXX
11865 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-06-17 02:04 | 2010-06-17 10:50 | 1 | 526 | 50261-1 | 526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK FIRST THING IN MORNING. //REPLACED CUT/OUT DOOR AND REFUSED VOLTAGE CHECKED GOOD ALL CUST. RESTORED AT 10:50 (2 CUSTOMERS) P R TOLLIVER //VER/CRB
11866 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-06-19 20:09 | 2019-06-20 04:55 | 1 | 526 | 4550631 | 526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole 37820126000133, this is on side of hill in difficult location, I cut a good path to the pole but could not get gate to hang, I think ear is broke on the side of cutout. Released by crew 074S05/ all power restored 0455/ ISO 37820126000135/ COD 1
11867 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2021-02-25 14:21 | 2021-02-25 18:44 | 2 | 263 | 4250711 | 526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad severice splice on pole 231-B-65, power restored at 18:30.
11868 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2017-08-03 09:44 | 2017-08-03 14:07 | 2 | 263 | 4219541 | 526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 254-2003 POLE FIRE,,LIFTED HOT TAP @ 254-326,,,SHOULD BE ABLE TO LOWER OR SCAB WITH CROSS ARM NEED CUTOUTAND BRACKET,,,KENTUCKY POWER POLE 404 RELEASED BY CREW 078S05 NO POWER OFF UNTIL 0944 //REPAIRS MADE ALL CUST RESTORED @ 1407 PLEASE CLOSE TICKET THANKS.BT/ ISO 38830254B00326/ COD 2/ VER/BOW
11869 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-08-18 23:49 | 2022-08-19 08:35 | 1 | 526 | 4762761 | 526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | lightning arrester blew on 1126-B1-724 causing line fuse to blow on 1126-B1-517// will be making repairs//MADE A DAE
11870 | Hazard | 3303902 | LESLIE | WOOTON | 2014-07-21 18:17 | 2014-07-21 22:40 | 2 | 263 | 4270391 | 526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT . BAD XFMR NEED 1 MAN & BUCKET TRUCK . 25 KVA 19.9 XFMR . CLOSED XFMR BACK @ 22:40 VER/CRB
11871 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2011-03-09 19:15 | 2011-03-09 21:00 | 5 | 105 | 52506-1 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TBAD TRANSFORMER ON POLE 188B120. OPENED TRANSFORMER UP AT 19:15. I HAVE CREW AND TRANSFORMER ON THE WAY TRANSFORMER CHANGED EVERYTHING OK TIME ON 21:00//COD 5// VER/DBM IDC XXXX
11872 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-02-25 15:00 | 2016-02-25 17:55 | 3 | 175 | 4776231 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT FAILED ON PHASE B. REPLACED ALL THREE LINE FUSE CUTOUTS AND RESTORED @ 17:55. SH VER/CRB
11873 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-11-17 11:00 | 2014-11-17 12:45 | 5 | 105 | H4733771 | 525 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL WORK DURING NORMAL WORK HOURS. POSSIBLE BAD CONNECTION IN UNDERGROUND PEDESTAL, J COMBS AND CREW ENROUTE TO HELP.//ONLY 1 CUSTOMER OUT// OPENED TRANSFORMER AT 11:00 RELEASED BY CREW 077S04 DUP IN HOIS FOR 5 CUST WHEN TR OPENED // COD-6 ISO TF 37830248A00626 DUP OF 4733771 FOR TR OUTAGE // VER/HFP L3/HFP
11874 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-09-30 09:05 | 2020-09-30 10:20 | 7 | 75 | 4512431 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 38830069D47517 hot line clamp burnt off feeding towards 518. repaires mae power restored at 1020. recloser must have operated on 12016 when the clamp fell off basket
11875 | Hazard | 3310502 | HADDIX | CANOE | 2008-10-20 14:00 | 2008-10-20 14:15 | 35 | 15 | 57358-1 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP CREW HAD TO OPEN LINE FUSE TO REPAIR CONDUCTOR THAT THEY FOUND DAMAGED. STRANDS BROKEN OUT OF PRIMARY CONDUCTOR IDC XXXX
11876 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-03-20 18:25 | 2008-03-20 18:32 | 75 | 7 | 59591-1 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | 3307301// CREW OPENED RECLOSER TO BYPASS REGULATOR ON POLE //// ONLY B PHASE OUT 75 CUSTOMERS CCC// VER/HFP L3/DNW IDC XXXX
11877 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-05-30 08:30 | 2012-05-30 09:45 | 7 | 75 | 4847291 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LIFTED HOT TAP ON POLE 177-68 TO REPAIR CONDUCTOR//COD 7// ///VER/CRB L/3 CRB IDC XXXX
11878 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2016-08-02 20:00 | 2016-08-02 21:45 | 5 | 105 | 4725861 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED & RESTORED POWER AT 21:45 VER/AWD
11879 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-09-29 16:30 | 2015-09-29 18:15 | 5 | 105 | 4290521 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 8 CROSSARM, BRACES. 2 CUTOUTS AND ARMMOUNT KITS. PROTECTED BY REC @ 1148 A 53/ LINE FUSE/ ISO 39831147C35019/ COD 5/ OPENED @1630/ REPAIRS MADE ALL CUST RESTORED @ 1815 PLEASE CLOSE TICKET THANKS/ VER/BOW L3/DKG
11880 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-01-30 10:05 | 2011-01-30 13:00 | 3 | 175 | 52241-1 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPLACED XFORMER RISER WIRE.//VER/CRB IDC XXXX
11881 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-05 00:45 | 2011-01-05 02:30 | 5 | 105 | 58759-1 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | C/L FUSE ON FIRE---REPLACED //VER/GAH IDCC PN17 XXXX
11882 | Pikeville | 3409502 | BURDINE | LEVISA | 2008-08-07 21:47 | 2008-08-07 23:32 | 5 | 105 | 50083-1 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409502// A CUTOUT FAILED ON POLE 335-330.// VER/TOM IDCC PN305 XXXX
11883 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2021-12-10 13:49 | 2021-12-10 14:24 | 15 | 35 | 4168651 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 253-246, bad cutout on pole 253-19, cut in clear, main line restored at 14;24
11884 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-07-19 00:39 | 2020-07-19 09:24 | 1 | 525 | 4181521 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout GuidelinesXFRF IS OUT,WILL RE-FUSEXFRF IS OUT,WILL RE-FUSE/////////CUTOUT DOOR HAD BURNED INTO,REPLACED IT&RESTORED POWER
11885 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-02-11 17:45 | 2022-02-11 20:40 | 3 | 175 | 4474941 | 525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans cutout brok at 237-B-32,Will be making repairs.Restored at 20:40..
11886 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2008-06-16 21:11 | 2008-06-17 05:55 | 1 | 524 | 66195-1 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307302/// BAD C/O IDC FUSE MISSING? XXXX
11887 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-06-09 14:08 | 2015-06-09 18:30 | 2 | 262 | 4545281 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BAD---RW NEEDS CUT---CREWS CUTTING FETR 2000// VER/ ADH
11888 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-01-08 13:13 | 2011-01-08 17:35 | 2 | 262 | 59850-1 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT.....FUSE LINK MAY HAVE JUST BROKEN.....//...TRIED FUSE....BAD XFMR....CALLED CREW....PLEASE SEND TO JOEY REED.....THANKS....JRV....01/08/11 RELEASED BY CREW 080S01 //VER/GAH IDC XXXX
11889 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2011-09-05 14:19 | 2011-09-05 16:30 | 4 | 131 | 4819901 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CALLED TREE CREW FOUND BAD LA POLE 1098-663 REPAIRED POLE 1098-207 20T LINE FUSE COD-4 ISO LF 399831098D00207 VER/HFP L3/HFP IDC XXXX
11890 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-11-26 06:19 | 2018-11-26 15:03 | 1 | 524 | 4476371 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout,34.5 kv ,manual,need line crew Released by crew 077S04 repairs made and power restored 1503 L3/HFP
11891 | Hazard | 3310502 | HADDIX | CANOE | 2022-07-21 08:06 | 2022-07-21 16:50 | 1 | 524 | 4539551 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout on pole 51-106 broke but still in. need 19.9 cutout and flaggers to replace. power restored 16:50
11892 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-11-23 20:58 | 2020-11-24 01:20 | 2 | 262 | 4719361 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 10kva need 15 trucks ok Released by crew 078S03 crew on site FETR 02:00 LRM all pwr restored 1:20 LRM//cod 2
11893 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-11-22 07:18 | 2018-11-22 16:02 | 1 | 524 | 4468501 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 7200 cutout squirt bucket can reach it/ white home on right up mudlick saul/ need 1 man and observer L3/HFP
11894 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-11-02 12:58 | 2008-11-02 17:20 | 2 | 262 | 61584-1 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN, BAD XFMR, 10 KVA BURNT UP NEED TO GO BACK WITH 15KVA./// JEFF COMBS AND JEFF BAKER BRING XFMR.//3308401//VER/CRB IDC XXXX
11895 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-01-23 03:26 | 2016-01-23 12:10 | 1 | 524 | 4643191 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | *****SEE H4643191***** NO VOLTAGE @ METER (1 CUST). OTHER METERS CHECK GOOD. RELEASED BY CREW 078S07 OPENED TRANSFORMER 39831147D30806 EFFECTING (2 ADD CUST)// DUPLICATE IN HOIS/ OPENED TRANSFORMER 39831147D30806@ 1110 TO 1210/ ISO 39831147D30806/ COD 3/ VER/BOW
11896 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-11-09 08:01 | 2013-11-09 10:12 | 4 | 131 | 4023591 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR TO RE-FUSE///////CUTOUT DOOR HAD BURNED OUT,REPLACED IT,ALSO RESQUEEZED SEVERAL SERV CONNECTIONS AT SEC RISERS OF XFR.ALL OK AFTERWARDS//COD 4// VER/DBM
11897 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-07-28 21:10 | 2008-07-29 05:54 | 1 | 524 | 61584-1 | 524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501//BAD CUTOUT, GOT RANDY COMMING TO HELP CHANGE IT/ BAD TRANSFORMER / NEED 7200V 15KVA TR AND MATERIAL HANDLER TRUCK// COD-1 // ALSO FOUND BAD SECONDARY VER/LDA IDC XXXX
11898 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-03-26 04:17 | 2014-03-26 13:00 | 1 | 523 | 4525721 | 523 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE HAS BURNED OFF APROX 1 FT.AB XFMR.POLE #37830092000183 40/4-15 KVA- 7200/120/240SINGLE PH. DEADEND HARDWARE. IS ISOLATED ON POLE#37830092000028. I HAVE NOTIFIED T.HALL & HE IIS TO SEND A CREW. IS TRUCK ACCESSIBLE. RELEASED BY CREW 074S04 SEND TO ROW VER/SEF
11899 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-10-15 14:39 | 2020-10-15 23:22 | 1 | 523 | 4559271 | 523 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o crew req--no good place to turn around ..may want to ck out w/ pickup first--ds101520 Released by crew 078S01,repairs made all cust restored @ 2322 please close ticket thanks.bt
11900 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2011-06-09 20:04 | 2011-06-09 20:22 | 29 | 18 | 4280191 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | THERE IS A CROSS ARM BROKEN ON POLE 67-B-174 OPENED RECLOSERS AT POLE 91-A-288 AT 20:04 TO MAKE REPAIRS. WE HAVE MADE REPAIRS AND CLOSED RECLOSERS IN AT 20:22 TIM MCCOY//VER/CRB IDC XXXX
11901 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-04-17 22:59 | 2013-04-17 23:28 | 18 | 29 | H4020291 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OUT DUE TO BAD 6 INCH DISC INSULATOR ON B PHASE RECLOSER LOAD SIDE. CREW ON THE WAY. OPENED A AND C PHASE AT 22:59 CLOSED BACK IN AT 23:28. REPAIRS MADE EVERYTHING BACK ON. VER/ARN IDC XXXX
11902 | South Williamson | 3411401 | DEWEY | INEZ | 2010-05-14 22:18 | 2010-05-15 07:00 | 1 | 522 | 62464-1 | 522 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3411401 CHECKING NOW. HAVE BAD UNDER GROUND.CALLED TIM MILLER ON HIS WAY WITH CREW IDCC CNT3, CCO XXXX
11903 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2016-12-27 01:34 | 2016-12-27 05:55 | 2 | 261 | 4240051 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 954-1176 AND BLEW C PHASE LINE FUSE ON 954-674 OPENED OTHER 2 FUSES AT 0306. REPLACED 4 TRANSFORMER CUTOUTS (2 ON 954-1176 & 2 ON 954-620). CLOSED LINE FUSES ON 954-674 @ 5:55. SH/// VER/DKM
11904 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2012-04-18 17:33 | 2012-04-18 21:54 | 2 | 261 | 4685391 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-2 ISO LF 37830469000226 VER/HFP L3/HFP IDC XXXX
11905 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-08-13 09:23 | 2010-08-13 18:05 | 1 | 522 | 54129-1 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 36430811 // BAD 10KVA 7200 XFMR, TRUCK PROBABLE, NEED TO TAKE DOWN FENCE. TRUCK ENTRY BESIDE POLE 400-18, CREW NOTIFIED RELEASED BY CREW 078S05 // COD-1 VER/HFP L3/HFP
11906 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-12-23 04:06 | 2022-12-23 11:58 | 2 | 472 | 4291241 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Off at 11:08 On at 11:58
11907 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-03-30 09:42 | 2017-03-30 14:03 | 2 | 261 | 4596801 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F IS OUT,WILL RE-FUSE/////////BAD 25KVA 19.9 XFR,NEED MAT HANDLER,CAN GET TRUCK TO POLE XFMR THAT IS BAD IS ON POLE 37820009C00015 NOT 74 XFMR CHANGED ON AT 14:03 D SAMMONS/ ISO 37820009C00015/ COD 2/ VER/BOW
11908 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-01-16 15:38 | 2013-01-16 17:05 | 6 | 87 | 4612511 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE. ///VER/CRB /L/3 CRB IDCC CDC83 XXXX
11909 | South Williamson | 3202201 | LOVELY | LOVELY | 2016-11-08 17:29 | 2016-11-08 20:23 | 3 | 174 | 4085141 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED LOOSE SECONDARY CONNECTIONS ON TRANSFORMER OPENED TRANS AT 20;00 RESTORED POWER AT 20:23/ ISO 38820746B00137/ COD 3
11910 | Paintsville | 3410602 | E.PRESTON | LANCER | 2022-02-21 17:58 | 2022-02-21 19:25 | 6 | 87 | 4525351 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link appears to have broken. Restored @ 19:25. sh
11911 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-05-10 17:34 | 2008-05-10 21:55 | 2 | 261 | 59586-1 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400303 BAD 15KVA XFMR. PIKEVILLE DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. CHANGED XFMR AND CUTOUT. SH IDCC CNT1 XXXX
11912 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2009-01-10 03:39 | 2009-01-10 08:00 | 2 | 261 | 53896-1 | 522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400101///25 KVA CSP XFMR BAD WILL NEED A MATERIAL HANDLER & 1 MAN PLUS XFMR ,T BRACKET & CUTOUT.//WR# 28010183 // VER/LDA L3/KEP IDC XXXX
11913 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-05-11 22:31 | 2011-05-12 00:15 | 5 | 104 | 4069031 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK
11914 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-10-16 08:56 | 2011-10-16 10:40 | 5 | 104 | 4987221 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | APPEARS FUSE LINK BROKE ON XFMR FUSE. RE-FUSED @ 10:40. SH//COD 5// VER/DBM IDC XXXX
11915 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2011-04-11 13:00 | 2011-04-11 15:10 | 4 | 130 | 54745-1 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39518254 //....XFMR LEAKING....50 KVA 7.2 KV.....POLE 1080C62....NEEDS REPLACED & GRASS DUG UP / CLEANED UP....PLEASE SEND TO JOEY REED...THANX...JRV RELEASED BY CREW 080S01 VER/HFP L3/HFP IDC XXXX
11916 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-07-29 22:11 | 2016-07-29 23:55 | 5 | 104 | 4711161 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE PULLED INTO AT POLE 38831150000033, REFUSED @ 2355. VER/CRB
11917 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-03-22 08:47 | 2012-03-22 10:31 | 5 | 104 | 4604821 | 520 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE XFMR FUSE MELTED OUT ON BANK OF 167S/SECONDARY BUG FAILED/SERVICER TO OPEN BANK AND REPAIR CONNECTIONS/FETR1045/VEM/ONLY ON CUST EFFECTED/ISO POLE SHOULD BE 247-327/REPAIRS MADE AND POWER RESTORED 1031/PLEASE CLOSE TICKET/THANKS/VEM COD-5 ISO TF 38830247000019 VER/HFP L3/HFP IDCC PN19 XXXX
11918 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2022-02-10 12:27 | 2022-02-10 12:53 | 20 | 26 | 4464501 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Sleeve pull out on the neutral at pole 273-D-39, I opened the line fuse on pole 273-328 at 12:27 to make repairs and closed back in at 12:53.
11919 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-01-05 15:40 | 2015-01-05 16:45 | 8 | 65 | 4907731 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD SEC. UNDERGROUND SEND CREW RELEASED BY CREW 078S08.. CREW IN PROCESS OF LOCATING BAD UG ETR 17:00.. CAY.. FOUND CONDUCTORS BURNED INTO INSIDE CONDUIT REPAIRING NOW.. OPENED XFMR AT 15:40 ON POLE 115-381 TO MAKE REPAIRS.. REPAIRS COMPLETE.. XFMR BACK IN AT 16:45/ ISO 38830115C00381/ COD 8/ VER/BOW L3/HFP XX
11920 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-10-26 09:37 | 2012-10-26 11:47 | 4 | 130 | 4173501 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// WILL REFUSE// FUSE LINK BROKE// REFUSED // POWER IS RESTORED //VER/GAH IDC XXXX
11921 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-08-29 12:50 | 2014-08-29 15:00 | 4 | 130 | 4435921 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA NEED 37.5 FLAGGERS MARKED POLE OPENED TRANS 12:50 PM RELEASED BY CREW 078S08,,,CREW ON SITE,,UPGRADED XFMR..ALL POWER RESTORED//COD 4// VER/DBM
11922 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-04-13 14:43 | 2022-04-13 15:35 | 10 | 52 | 4757231 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole 737-133 broke at ground line. Emergency ug locate # 2204131051 - 12:15 p.m. Crew to opne sw 737-133 when on site. Opened fuses on 737-133 @ 14:43. Replaced pole and closed fuses on 737-133 @ 15:35. sh
11923 | Hazard | 3309301 | VICCO | REDFOX | 2015-01-14 00:27 | 2015-01-14 02:37 | 4 | 130 | 4934211 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CONNECTION HAD FROZE OUT ON XFMR POLE, REPLACED CONNECTION VER/TOM L3/TOM
11924 | South Williamson | 3411401 | DEWEY | INEZ | 2011-04-18 13:30 | 2011-04-18 15:40 | 4 | 130 | 60263-1 | 520 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE ON SECONDARY AT POLE 768-50 DUE TO TREES AND VINES///GOING TO CUT DOWN WIRE AND REROUTE SERVICE TO NEW SECONDARY POLE BY DRIVEWAY//HAVE POWER RESTORED//CUSTOMER STATES HAS SOME DAMAGE TO SOME APPLIANCES//ADVISED HIM TO CALL IN DAMAGE CLAIM//COMPLETE//EM // EMAILED TO P WYSONG// VER/DBM IDC XXXX
11925 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-03-18 17:36 | 2014-03-18 19:20 | 5 | 104 | H4506641 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN CALLING 1 MAN TO HELP CHANGE AND CREW TO FLAG NEED 1 MAN AND BIG BUCKET ,BAD CUTOUT ON POLE 246B-130 POWER IS BACK ON BUT CUTOUT IS BROKE // 2033 DONNIE SPENCER ON SITE//CUTOUT BROKEN CALLING 1 MAN TO HELP CHANGE AND CREW TO FLAG NEED 1 MAN AND BIG BUCKET ,BAD CUTOUT ON POLE 246B-130 POWER IS BACK ON BUT CUTOUT IS BROKE. OPENED LINE FUSE ON POLE 246B-83 @ 21:10 CLOSED BACK IN @ 21:20 5 CUST // 2ND OUTAGE VER/HFP L3/HFP
11926 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-08-04 05:50 | 2019-08-04 10:10 | 2 | 260 | 4838251 | 520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PR called in-knows specific location/1st house coming down hill to Justiceville on right/n front st. will trim tree & refuse xfmr on pole 37820098A00116.xfmr is bad .will need 1 A man ,material handler ,50 kva 19.9 to 120/240.
11927 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-04-21 12:02 | 2017-04-21 14:55 | 3 | 173 | 4664661 | 519 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE C/O--REPAIRED-DS042117 38830187000141 VER/AWD L3/HFP XXXHFP
11928 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-16 11:07 | 2015-02-16 14:00 | 3 | 173 | 4032551 | 519 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | YELLOW TO RED BARREL CONNECTOR BAD ON XFMR SECONDARY LEAD, REPAIRED/ SERVICER STATED ALL THREE CUSTOMERS ARE OFF SECONDARY/ ISO 37830255A00127/ COD 3 VER/HFP L3/HFP
11929 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-08-19 17:37 | 2013-08-19 20:30 | 3 | 173 | 4680501 | 519 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON THE TRANSFORMER SECONDARY RISER. VER/CRB L/3 CRB
11930 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-02-20 08:02 | 2015-02-20 16:40 | 1 | 518 | 4051791 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFR HERE,NEED A 50KVA 19.9.CAN USE BUCKET///////NEED CREW RELEASED BY CREW 074S06 COD-1 ISO TF 37830263A00265 VER/HFP L3/HFP
11931 | Whitesburg | 3312902 | JENKINS | JENKINS | 2022-07-24 18:41 | 2022-07-24 19:55 | 7 | 74 | 4569431 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutrout on at 1955
11932 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-04-23 08:34 | 2011-04-23 12:53 | 2 | 259 | 62403-1 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ROTTEN FUSE LINK/POWER RESTORED 1253/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
11933 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-10-25 16:22 | 2015-10-25 20:06 | 4 | 224 | 4375341 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BACK IN AT 18:00 ON POLE 165D124 , ISOLATED XFORMER ON POLE 165D142. NEED CUTOUT AND ARRESTER AND MIGHT NEED 15 KVA 7200 XFORMER. TRUCK TO POLE. RELEASED BY CREW 078S01,REPLACE BAD CUTOUT & ARRESTER ALL CUST RESTORED @ 2006 PLEASE CLOSE TICKET THANKS.BT// VER/ ADH L3/HFP XXXHFP
11934 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-02-02 15:08 | 2010-02-02 19:27 | 2 | 259 | 62395-1 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200, NO TRUCK, SEND TO V MULLINS RELEASED BY CREW 078S05 BAD LOCATION CREW GETTING YARD DOG/CREW ON SITE/FETR2045/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1927/PLEASE CLOSE TICKET/THANKS/VEM//COD 2// VER/DBM IDC XXXX
11935 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-01-06 03:51 | 2018-01-06 05:05 | 7 | 74 | 4711221 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER STATES HEARD LOUD NOISE AND NBRS OUT///bad cutout
11936 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-08-06 13:44 | 2016-08-06 18:03 | 2 | 259 | 4742661 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED .BROKE CUTOUT @ 296-135.MAY WINCH SQUIRT BOOM TO POLE RELEASED BY CREW 078H19/CREW ON SITE/WILL NEED TO OPEN XFMR FOR REPAIRS/FETR 1815/VEM/OPENED XFMR AT 1531/REPAIRS MADE AND ALL CUST RESTORED 1803/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
11937 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-12-19 12:31 | 2008-12-19 16:50 | 2 | 259 | 60294-1 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR# 27754435 // 40/5 POLE BURNT OFF CREW REQUIRED FLAGGERS ALSO/2 CUSTOMERS OFF RELEASED BY CREW 078S03 POWER ON @ 16:50 BLR L3/HFP IDC XXXX
11938 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-08-16 09:22 | 2012-08-16 18:00 | 1 | 518 | 4942801 | 518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SDB / BAD CSP TR, EVENING LINE CREW TO REPLACE. NO CUST OUT VER/KEP IDC XXXX
11939 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2018-02-26 07:08 | 2018-02-26 15:45 | 1 | 517 | 4883091 | 517 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew req, have broken c/o on pole 900-134, this is for sperry auto, behind portsmouth school, no trucks to pole. Released by crew 078S06
11940 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-08-27 05:46 | 2022-08-27 10:04 | 2 | 258 | 4801261 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on 220-6 will refuse///19.9 cutout broke on poole 220-6 will be making repairs////Changed bad cutout and restored service @ 10:04
11941 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2013-10-07 10:00 | 2013-10-07 12:09 | 4 | 129 | 4917471 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED POLE 250-23 TO REPLACE CUTOUT 4 CUSTOMER OFF FIRE OUT TRUCK OK NEED TECH TO WRITE POLE TO REPLACE/TURN DOWN FIREHOUSE ROAD AT GRAHN FIRE DEPT. RELEASED BY CREW 078S03/CREW ON SITE/FETR1315/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1209/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L/3 CRB IDCC TOF0925 ESTIMATED TIME OFF XXXX
11942 | Hazard | 3309302 | VICCO | JEFF | 2011-10-19 11:27 | 2011-10-19 15:45 | 2 | 258 | 4998301 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, REPLACED CUTOUT ///VER/CRB IDC XXXX
11943 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-02-14 08:11 | 2010-02-14 10:20 | 4 | 129 | 57526-1 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403302/// CUTOUT DOOR FAILED. REPLACED DOOR AND RE-FUSED XFMR. SH IDC XXXX
11944 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2020-05-30 09:23 | 2020-05-30 11:32 | 4 | 129 | 4932361 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | I think the fuse just broke on this cutout,Will refuse and restore service to these customers,Restored at 11:32.
11945 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-12-31 16:04 | 2009-12-31 17:30 | 6 | 86 | 53690-1 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ON SITE, PATROLLING LINE VER/KEP L3/KEP IDC XXXX
11946 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2021-02-19 12:12 | 2021-02-19 16:30 | 2 | 258 | 4180961 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 200-79 power restored at 16:30
11947 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2020-05-04 15:26 | 2020-05-05 00:02 | 1 | 516 | 4798231 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830333C20165 broke 7200 c/o-crew req-big bucket-ds050420 Released by crew 078S01
11948 | Whitesburg | 3314401 | MAYKING | ERMINE | 2021-09-08 09:39 | 2021-09-08 12:31 | 3 | 172 | 4220411 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cut out, replaced. Opened line at 426B-453 at 11:40 to 12:31 to safely make repairs. Power restored.
11949 | Hazard | 3303902 | LESLIE | WOOTON | 2022-12-15 09:12 | 2022-12-15 13:30 | 2 | 258 | 4262981 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cut arrester in clear. Power restored @ 13:30
11950 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-10-09 16:55 | 2022-10-09 18:21 | 6 | 86 | 4009421 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crrew required 8t
11951 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2012-02-02 15:59 | 2012-02-02 20:17 | 2 | 258 | 4316671 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25KVA TRUCKS OK NO FLAGGERS 2 OR 3 MEN RELEASED BY CREW 078S03/CREW ON SITE/FETR 2115/VEM/XFMR CHANGED AND POWER RESTORED 2017/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB IDC XXXX
11952 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-03-15 13:38 | 2017-03-15 16:30 | 3 | 172 | 4559781 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 7200 XFM..WILL NEED LINEMAN AND BIG BUCKET TO MAKE REPAIRS... 37820097000320 1630 VER/AWD
11953 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2015-09-29 16:58 | 2015-09-29 19:50 | 3 | 172 | 4290561 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, BAD CUTOUT ON POLE 878-98 NO TRUCKS GROUND IS TO WET RELEASED BY CREW 078S06/ 1950CREW REQ, BAD CUTOUT ON POLE 878-98 NO TRUCKS GROUND IS TO WET RELEASED BY CREW 078S06,REPAIRS MADE ALL CUST RESTORED @ 1950 PLEASE CLOSE TICKET THANKS.BT/ ISO 39830878000098/ COD 3/ VER/BOW
11954 | Hazard | 3302703 | HAZARD | HAZARD | 2008-08-29 04:19 | 2008-08-29 05:45 | 6 | 86 | 57181-1 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SERVICER ON SITE TR FUSE OPEN FUSE BROKE.. WILL REFUSE. VER/PDP IDCC FEC57 XXXX
11955 | Hazard | 3303902 | LESLIE | WOOTON | 2009-03-01 15:57 | 2009-03-01 20:15 | 2 | 258 | 52818-1 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 535-30 19.9 NEED CUTOUT T-BRACKET STILL WAITING ON HELP BUMPED TIME UP TO 21:30 VER/KEP L3/KEP IDC XXXX
11956 | Hazard | 3301401 | COMBS | COMBS | 2011-05-16 06:39 | 2011-05-16 08:05 | 6 | 86 | 4098941 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT -- POWER RESTORED.//COD 6// VER/DBM
11957 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2008-01-09 01:19 | 2008-01-09 02:45 | 6 | 86 | 54893-1 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER VER/PDP IDC XXXX
11958 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-01-12 14:17 | 2016-01-12 15:43 | 6 | 86 | H4609571 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | KEVIN BROWN REPORTED UNSAFE CONDITION, OPEN WIRE SECONDARY BETWEEN POLES 38830020D47604 TO 38830020D47610. NEED ROLL 1 AU TWIST./WILL NEED TO OPEN XFMR@20-D4-7617 TO REPLACE TWO SPANS OF WIRE/APROX 1.5 HOUR OUTAGE/FETR 1600/VEM/OPEN XFMR@1417/REPAIRS MADE AND ALL CUST RESTORED 1543/PLEASE CLOSE TICKET/THANKS/VEM// VER/ ADH
11959 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-01-12 10:21 | 2022-01-12 14:39 | 2 | 258 | 4338761 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | got netural broke going to let wire down and fixed it ,got phillip hicks coming to help 1/ 0 sec nerural pull into, cust called five days before and call center told him not aep problem
11960 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-11-06 12:03 | 2013-11-06 14:12 | 4 | 129 | 4015031 | 516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. REPLACED FUSE AND POWER IS BACK ON. VER/CRB L3/HFP IDC XXXX
11961 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-11-05 17:15 | 2014-11-06 01:50 | 1 | 515 | 4702651 | 515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT FIRE IS OUT AND SAFE UNTILL CREW CAN ARRIVE POLE WILL NEED LOWERED, ISOLATED XMF ONLY RELEASED BY CREW 078S11/OPENED TR @ 17:15 11/05/14 /WILL OPEN FUSE ON POLE 595-32,,OPENED AT 00:50,,CLOSED AT 01:50,,ALL REPAIRS MADE, ALL POWER RESTORED RELEASED BY CREW 078H03 VER/ARN // SEE 4703591 FOR FUSE OUTAGE TO REPAIR THIS POLE // L3/HFP
11962 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-02-13 06:25 | 2009-02-13 15:00 | 1 | 515 | 59082-1 | 515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD CONNECTION ON MAST REPAIRED //VER/GAH IDC XXXX
11963 | Hazard | 3310502 | HADDIX | CANOE | 2009-07-15 15:17 | 2009-07-15 17:00 | 5 | 103 | 62467-1 | 515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP 37830027000030 LINE FUSE BLOWN ON RIGHT HAND FORK, LOOKING LINE OVER POLE 37830027000040 WE HAVE PRIMARY OFF POLE, BROKEN INSULATOR AND BENT PIN/// WORK COMPLTED, REFUSED LINE C/O POWER RESTORED L3/HFP IDC XXXX
11964 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2013-08-10 19:54 | 2013-08-10 21:37 | 5 | 103 | 4647831 | 515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS FAILED. & BURNED XARM INTO. WILL CHANGE CUTOUT & ARRESTOR. BACK ON @ 21:37 VER/CRB L/3 CRB
11965 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2021-02-03 23:05 | 2021-02-04 07:40 | 1 | 515 | 4935681 | 515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | crew required bad secondary with bucket tree crew trucks ok with roll of 2/3 Released by crew 078S03/ replaced secondary with new 2/3 service and drop . time restored 740
11966 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-12-25 01:17 | 2013-12-25 03:00 | 5 | 103 | 4199801 | 515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE ON XFMR BROKE OUT.15 KVA XFMR HAS 4 SINGLE WIDE ALL ELECTRIC TRAILORS AND 1 DOUBLE WIDE ALL ELECTRIC..ALL HEAT PUMPS..OFF IT.NEEDS UP GRADED TO AT LEAST 25. VER/PDP
11967 | Hazard | 3309302 | VICCO | JEFF | 2012-10-05 17:27 | 2012-10-05 19:10 | 5 | 103 | 4118481 | 515 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN. BAD ON XFMR. OPENED XFMR AT 18:30 CLOSED BACK IN AT 19:00 ( CLIMED POLE REDONE CONN.) COD-5 ISO TF 37830347D00109 VER/HFP L3/HFP IDC XXXX
11968 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-01-07 19:52 | 2014-01-08 04:27 | 1 | 515 | 4255771 | 515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD MANUAL 25 KVA 7.2KV TRANSFORMER, NEED 3 MEN // COMBS & RICE & MELTONBAD MANUAL 25 KVA 7.2KV TRANSFORMER, NEED 3 MEN POWER RESTORED. VER/SEF IDC XXXX
11969 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-01-11 20:28 | 2022-01-12 00:45 | 2 | 257 | 4337311 | 514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 770-d-67///difficult location//need line crew//19.9 cutout Released by crew 079S01broke cutout on pole 770-d-67///difficult location//need line crew//19.9 cutout//repairs made//restored at 00:45
11970 | Hazard | 3309003 | JEFF | VIPER | 2015-12-18 04:19 | 2015-12-18 08:36 | 2 | 257 | 4541471 | 514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL DISPATCH AT START OF REGULAR SHIFT//TOM REPLACED BAD ARRESTER VER/CRB
11971 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-07-08 08:14 | 2011-07-08 12:31 | 2 | 257 | 4484921 | 514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND HOUSE KNOB PULLED OUT === CHANGED CUTOUT AND REPAIRED HOUSE KNOB COD-2 ISO TF 37830419C00222 VER/HFP L3/HFP IDC XXXX
11972 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-01-26 12:24 | 2019-01-26 16:41 | 2 | 257 | 4724201 | 514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cut out on pole 38830188B02001 cannot reach with my truck will need a big bucket Released by crew 078H01---crew on site---changed both xfmr cutouts---pwr restored @ 16:41---tbl tkt comp--rmv L3/HFP
11973 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2010-05-31 07:41 | 2010-05-31 16:15 | 1 | 514 | 54050-1 | 514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE///REPAIRED////PWR CHECKS OK//VER/CRB IDC XXXX
11974 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-04-18 09:18 | 2022-04-18 13:35 | 2 | 257 | 4773751 | 514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans fuse open on Bank at 144-A-343..Have a Bad Trans spoke with Paul layne and he is getting Trans and is on the way to Make repairs..Trans fuse open on Bank at 144-A-343..Have a Bad Trans, spoke with Paul layne is on the way to Make repairs.. Released by crew 074S01/restored power at 13:35
11975 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-11-04 14:14 | 2013-11-04 17:05 | 3 | 171 | 4008951 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN LINE CUTOUT ON POLE 211-33 NO TRUCKS TO POLE. NEED LINE CREW. RELEASED BY CREW 078S01,, OPENED XFMR AT 16:55, CLOSED AT 17:05,, CHANGED CUTOUT, ALL POWER RESTORED SEE H4008951 FOR 2 ON TR @ 38830211000033 VER/HFP L3/HFP
11976 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2014-08-31 11:34 | 2014-08-31 20:07 | 1 | 513 | 4440841 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND NEED TEP INSTALLED RELEASED BY CREW 078S08// BRING BIGGEST TEMP YOU HAVE/CREW ON SITE/WILL NEED TO OPEN XFMR 20-431/APPROX TWO HOUR OUTAGE/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2007/PLEASE CLOSE TICKET/THANKS/VEM//COD 1 (+ 2 @ 1830)// AJB
11977 | South Williamson | 3411401 | DEWEY | INEZ | 2016-02-25 11:15 | 2016-02-25 14:06 | 3 | 171 | 4771611 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | FOUND SEC. POLE 720-27 FELL OVER LAYING IN TREES//ROTTEN AT GROUND///CREW ENROTE TO REPLACE//OPENED TRANS @ 1115 CLOSED @ 1406 VER/CRB
11978 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-01-31 06:09 | 2018-01-31 09:00 | 3 | 171 | 4785791 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | bad 19.9 current limiting fuse/ ISO 38830092B00609/ COD 3
11979 | South Williamson | 3411401 | DEWEY | INEZ | 2011-11-29 12:29 | 2011-11-29 15:20 | 3 | 171 | 4126711 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE//TREE FELL AND LAYING ON NEUTRAL//NO TRUCK ACCESS//ROGER MAYNARD IS ENROUTE TO HELP//REPAIRS MADE//RESTORED AT 15:20//COMPLETE//EM COD-3 ISO TF 38830791D30242 VER/HFP L3/HFP IDC XXXX
11980 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2019-10-07 00:03 | 2019-10-07 02:54 | 3 | 171 | 4104241 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | no crew required 15t3/ ISO 38830248000093/ COD 3
11981 | Hazard | 3302704 | HAZARD | KENMONT | 2011-10-29 05:17 | 2011-10-29 13:50 | 1 | 513 | 4032601 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN///// 50 KVA 19.9 XFMR BAD ON POLE 37830321D00458, NEED 3MAN LINE CREW AND R/W CREW, MANUAL XFMR.//// XFMR CHANGED OUT POWER RESTORED///VER/CRB IDC XXXX
11982 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-12-15 10:27 | 2010-12-15 19:00 | 1 | 513 | 50576-1 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FUSE OPEN ON PRIMARY UNDERGROUND---37830272B11480 BAD TERMINATION AT TRANSFORMER. DUTY SUPERVISOR NOTIFIED. RELEASED BY CREW 077S04//:: PRIMARY UG WIRE WAS BAD , REPLACED AND RESTORED POWER AT 1900 JKC//COD 1 // SERVICER GETTING W/ENGINEERING TO SUPPLY PADMOUNT INFO TO MAPPING TO ADD IT TO THE MAP // VER/DBM IDC XXXX
11983 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-06-01 12:33 | 2012-06-01 21:06 | 1 | 513 | 4861471 | 513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, WIRE HAS BURNT OFF BOTTOM OF CUTOUT, WILL NEED HELP. XFMR IS BAD, 25 KVA, 19.9 KV RELEASED BY CREW 077S02 REPLACED TRANSFORMER AND RESTORED POWER AT 2106 COD-1 ISO TF 3783015800004437820217D00066 IDC XXXX
11984 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-12-11 08:22 | 2013-12-11 10:30 | 4 | 128 | 4151091 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 271C281 NO TRUCKS/CREW REQUIRED SEND TO FRALEY RELEASED BY CREW 078S03 VER/SEF L3/HFP
11985 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-09-13 05:48 | 2020-09-13 14:20 | 1 | 512 | 4455931 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Held for daylight in accordance with KPCO late night callout guidelines. bad 25kva, 7200 xfm. need row crew and line crew. manual pole. Released by crew 077S10.. repairs made all power restored @ 14:20
11986 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-02-14 14:54 | 2017-02-14 19:10 | 2 | 256 | 4396791 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS CUTOUT ON 1125C797 FAILED LETTING FUSE DROP OPEN DE-ENERGIZING TRAN I REPLACED CUTOUT RESTORED POWER AT 19:10/ ISO 38831125C10797/ COD 2/ VER/BOW L3/HFP XXXHFP
11987 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-12-02 04:40 | 2015-12-02 13:12 | 1 | 512 | 4502051 | 512 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | CALLED CUSTOMER AND SAID WAS OK TO CHECK DURING NORMAL WORK HOURS, MAIN LINE NEUTRAL SPLICE HAS FAILED LETTING SERVICE NEUTRAL COME LOOSE FROM MAIN LINE, WILL NEED HELP TO REPAIR, TURNED CUST BREAKER OFF, ONLY ONE CUST RELEASED BY CREW 077S02 VER/CRB
11988 | Pikeville | 3408103 | SALISBURY | MARTIN | 2017-10-13 12:17 | 2017-10-13 14:25 | 4 | 128 | 4453851 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED XFMER ARRESTER AND POLE GROUND, ALL WORK COMPLETE / GXJ 38831074C00336 VER/AWD L3/HFP XXXHFP
11989 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-07-26 03:37 | 2015-07-26 07:53 | 2 | 256 | 4942861 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED CUTOUT AND BIG BUCKET VER/CRB
11990 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2017-12-21 08:26 | 2017-12-21 10:34 | 4 | 128 | 4661741 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse melted out, refused @1034. // COD-4 ISO TF 38821036B00027
11991 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-05-30 19:56 | 2016-05-31 00:12 | 2 | 256 | 4273321 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 TRANSFORMER VER/TOM L3/TOM
11992 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2017-10-01 18:02 | 2017-10-01 22:18 | 2 | 256 | 4403361 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA CSP XFM/// NO TRUCK/// NEEDLINE CREW AND ROW CREW/// NEED 25KVA 7200 ,CUTOUT AND BRACKET//// CHANGED BAD XFM AND RESTORED SERVICE @ 22:18/// VER/DKM L3/HFP XXXHFP
11993 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-12-23 14:07 | 2013-12-23 16:15 | 4 | 128 | 4197031 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CO POLE 42/86 RESTORED 16:15 MP VER/SEF
11994 | Hazard | 3309003 | JEFF | VIPER | 2017-04-21 20:05 | 2017-04-22 00:21 | 2 | 256 | 4666001 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER ETA APPROX 2035//LID CAME 15 KV TRANSFORMER, NEED 25 KV TRANSFORMER AND 19.9 CUTOUT,OIL IN SWIMMING POOL,PLAY CENTER AND YARD. RELEASED BY CREW 077H07//ISO 37830368000063//COD 2// VER/DBM L3/HFP XXXHFP
11995 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-06-07 07:54 | 2010-06-07 12:10 | 2 | 256 | 58191-1 | 512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//COD 2// VER/DBM IDC XXXX
11996 | South Williamson | 3200301 | BELFRY | BELFRY | 2022-08-22 01:44 | 2022-08-22 10:15 | 1 | 511 | 4776171 | 511 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Stirrup burned off at 38821014A00049.made repairs and got transformer fuse on pole 1014A-49 back in at 10:15
11997 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-10-07 07:19 | 2019-10-07 15:50 | 1 | 511 | 4106471 | 511 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer fuse blowed ::bad 25kva 19.9 on the way to get one
11998 | Whitesburg | 3409503 | BURDINE | JENKINS | 2014-01-29 09:07 | 2014-01-29 10:20 | 7 | 73 | 4322951 | 511 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER ,SECONDARY BURNT INTO , MADE REPAIRS RESTORED POWER AT 10:20 COD-7 VER/HFP L3/HFP
11999 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-04-12 08:59 | 2008-04-12 17:30 | 1 | 511 | 50352-1 | 511 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON TRANSFORMER -- RESTORED AT 17:30 VER/HFP IDC XXXX
12000 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-04-25 19:17 | 2012-04-25 20:30 | 7 | 73 | 4707841 | 511 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONN. BURNED UP AT WEATHER HEAD. POWER BACK ON AT 20:30 ///VER/CRB L/3 CRB IDC XXXX
12001 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-11-29 08:19 | 2016-11-29 16:50 | 1 | 511 | 4141231 | 511 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND NEED TEP, TALKED TO RAYBURN RELEASED BY CREW 078S08/ TEMP RESTORED @1650/ ISO 38830189000128/ COD 1/ VER/BOW
12002 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2022-06-07 20:09 | 2022-06-08 01:40 | 4 | 331 | 4035111 | 511 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failed on pole 212D-33 and burnt top of pole.//Crew required.//Can reach with bigger bucket to lower equipment on pole.//transformer 212-D-33 open/ Opened lat fuse 212-27 @ 00:40.//Repairs made and restored @ 01:40
12003 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-06-27 21:45 | 2015-06-28 02:00 | 2 | 255 | 4682351 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 1065-104, ROTTEN AT GROUNDLEVEL AND FELL OVER, NO POWER OFF AT THIS TIME, 30/6 POLE. CUSTOMER SAID WE COULD DRIVE TRUCK THRU YARD, IF NOT ITS MANUAL.NEED FORMAN AND 3 LINEMEN, A-D./// OPENED XFMR AT 21:45 ON SITERELEASED BY CREW 077S08 ON SITE COMP.J.COMBS VER/ARN
12004 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-10-31 16:40 | 2010-10-31 16:50 | 51 | 10 | H50483-1 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37558637 // OPENED LINE FUSE @ 1640 CLOSED @ 1650 - 51 CUST /// POLE 44-4080 BAD CUTOUT/ON SITE PR TOLLIVER//REPLACED 100AMP CUTOUT ALL CUST. RESTORED AT 19:10 PR TOLLIVER// THIS IS FOR THE FUSE OUTAGE FROM ORDER 50483-1 VER/HFP L3/HFP IDC XXXX
12005 | South Williamson | 3202201 | LOVELY | LOVELY | 2012-08-11 10:45 | 2012-08-11 15:00 | 2 | 255 | 4927971 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 19.9. CAN USE TRUCK ACROSS FROM THE WARFIELD PARK @ OLD COAL PREP PLANT. // J REED &... FAULT WENT THROUGH TRANSFORMER FUSE AND BLOWED A 80 AMP FUSE ON POLE 746C241, NO OTHER CUSTOMERS WAS OFF. "B" PHASE ONLY - 1 CC //VER/GAH IDC XXXX
12006 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-12-05 18:00 | 2018-12-05 22:15 | 2 | 255 | 4510971 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 19.9kv 120/240 Can use truck will need flagging crew. Released by crew 074S07 restored at 22:15 L3/HFP
12007 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-03-30 11:25 | 2014-03-30 12:50 | 6 | 85 | 4541531 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 20 MIN UPDATED FETR// LINE FUSE OUT ON P 182-120 CUTOUT BAD ON POLE SERVICER TO CHANGE// CUTOUT CHANGED ALL PWR RESTORED@ 12:50 & TRAFFIC LIGHTS ARE WORKING PLEASE CLOSE TICKET LRM VER/CRB
12008 | Whitesburg | 3312901 | JENKINS | KONA | 2010-10-04 05:58 | 2010-10-04 08:48 | 3 | 170 | 56537-1 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED FUSE LINK VER/KEP L3/KEP IDC XXXX
12009 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-04-10 20:50 | 2011-04-11 01:05 | 2 | 255 | 54496-1 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE POWER BACK ON //VER/GAH IDC XXXX
12010 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2009-09-26 07:35 | 2009-09-26 11:50 | 2 | 255 | 63543-1 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15KVA TRANSF BAD RELEASED BY CREW 079S01 VER/KEP L3/KEP IDC XXXX
12011 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-06-11 00:55 | 2013-06-11 09:25 | 1 | 510 | 4256191 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / WILL CHECK AT REGULAR TIME FOUND A BAD S&C CUTOUT, HAVE REPAIRS MADED AND POWER IS RESTORED TO THIS CUST AT 0925//COD 1// VER/DBM IDC XXXX
12012 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-05-12 03:15 | 2015-05-12 03:30 | 34 | 15 | 4417361 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED REC TO SAFELY REPLACE CUTOUT ON POLE 38830477C30396 VER/SEF L3/DKGXXX VERIFIED TIME OFF AND ON WITH VOICE RECORDER AJB
12013 | Whitesburg | 3309302 | VICCO | JEFF | 2010-08-11 16:15 | 2010-08-12 00:45 | 1 | 510 | 52636-1 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA NEED 1 MAN& BIG BUCKET RELEASED BY CREW 075H01BAD 25 KVA NEED 1 MAN& BIG BUCKET REPLACED BAD TRANS VER/ARN IDC XXXX
12014 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2018-09-02 18:18 | 2018-09-02 22:33 | 2 | 255 | 4035981 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva trans. on pole 22-48, pole is 200 ft. up on mtn., going to run a temperary secondery from pole 22-244 to take care of till Tuesday, will need a 25/7200, manual r.o.w. crew, and line crew Tuesday, please send a copy of this to Paul Keesee and Cliff Freeman, will also need 1 man tonight to help put in temperary. Got temperary put in @2233, all ok.
12015 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2022-02-23 16:00 | 2022-02-23 17:25 | 6 | 85 | 4537081 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad UG cable, Tommy Goble is coming to assist// openeing XFM on 954-A4-355 will keep up with times// XFM on 954-A4-355 off @ 1600 on@ 17:25
12016 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2022-01-28 09:50 | 2022-01-28 10:45 | 14 | 55 | 4411631 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | serve end melted out. replacing connections 1/0 s/d..opened xfmr on 785-337 at 10:10 back on at 10:45..
12017 | Hazard | 3309301 | VICCO | REDFOX | 2021-06-12 13:55 | 2021-06-12 16:45 | 3 | 170 | 4724341 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse had broke, power restored
12018 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-06-22 15:50 | 2016-06-22 18:40 | 3 | 170 | 4408891 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | I OPENED THE TRANSFORMER CUTOUT AT 15:50. EITHER THE CUTOUT OR ARRESTER IS BREAKING DOWN. I CANNOT REACH IT TO SEE WHAT IS WRONG. NEED A FOREMAN AND B LINEMAN WITH BUCKET TRUCK. ALSO NEED A 19.9 CUTOUT AND ARRESTER.RESTORE 1840// VER/ ADH
12019 | Hazard | 3309301 | VICCO | REDFOX | 2017-02-20 13:48 | 2017-02-20 15:30 | 5 | 102 | 4409581 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | B PHASE ONLY (5 CUST)LIGHTNING ARRESTER HAS WENT BAD ON POLE 300-73, FUSE IS OUT ON 324-251, B PHASE/ ISO 37830324A10251/ COD 5/ VER/BOW L3/HFP XXXHFP
12020 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-02-02 16:20 | 2016-02-02 16:35 | 34 | 15 | 4667741 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF HIGH SIDE OF STEP-DOWN POLE 1126A-14.WILL REPAIR.OPENED @ 16:20.CLOSED BACK IN @ 16:35.// VER/ ADH AJB
12021 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2011-08-24 08:10 | 2011-08-24 11:00 | 3 | 170 | 4749841 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRES GOING TO CITY ST. LIGHT SHORTED OUT VER/KEP IDCC FEC57 XXXX
12022 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2011-04-13 12:12 | 2011-04-13 16:27 | 2 | 255 | 56313-1 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON POLE 263-40 OLD HARTS SANITATION GARAGE NEAR DURBIN RD AND US 23 SOUTH ,CREW REQ,MAY NEED TO OPEN REC, TO CLEAR UP TROUBLE RELEASED BY CREW 078S09/CREW ON SITE/DIFF LOCATION/FETR1700/VEM/REPAIRS MADE AND POWER RESTORED 1627/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP IDC XXXX
12023 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-07-14 22:54 | 2008-07-15 00:19 | 6 | 85 | 52729-1 | 510 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3201001//SERVICER ETA 2330//, ON SITE, SECONDARY BURNT INTO, MAKING REPAIRS, CONNECTOR WHERE SERVICE MAKES UP TO SECONDARYHEATED UP AND BURNT SEC INTO, CUSTS ONLY GETTING 110 VOLTS UNTIL REPAIRS WERE MADE, PULLED XFORMER OFF AT 2338, BACK ON AT0019 IDCC CCMCCDL XXXX
12024 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-05-16 06:03 | 2022-05-16 10:18 | 2 | 255 | 4894351 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced xfr cutout. Complete
12025 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2018-01-02 01:45 | 2018-01-02 04:35 | 3 | 170 | 4694261 | 510 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | wire burned into beside of connector , I replaced connector
12026 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-12-22 17:30 | 2011-12-22 18:55 | 6 | 85 | 4195711 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-2006 BAD CUT SEND NOTE TO CHG. NEXT WEEK NO TRUCK POLE 44-161 25T LINE FUSE OUT // CUST MISMAPPED SHOULD BE ON POLE 44-538 - ENTERED MAP DISC // THIS IS SAME AS 4195801 VER/TOM L3/TOM IDCC PN318 XXXX
12027 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-06-07 08:55 | 2019-06-07 11:45 | 3 | 170 | 4444001 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | l/f out on 1145-31 patrolled found nothing wrong first time, tried l/f came back out, found bad l/a on 1145-129 have cut in the clear, all power is restored at this loc at 1145 by amg
12028 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2016-07-14 14:40 | 2016-07-14 17:30 | 3 | 170 | 4630801 | 510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSURE ON 1124/3041 IS IN. LINE FUSE CUTOUT IS BROKEN (POWER OFF) AT 1124/1554..REPLACING CUTOUT,,,POWER RESTORED AT 1124/1554 AT 17:30.BLR/ ISO 39831124A41554/ COD 3/ VER/BOW
12029 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-07-12 12:20 | 2011-07-12 20:49 | 1 | 509 | 4531461 | 509 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 SERVICE DROP BURNED HOT LEG AND NEUTRAL INTO IN TREE IN MID SPAN. I AM GOING TO CHANGE DROP TO #2. I CHANGED S/DROP.// VER/DBM
12030 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-12-06 05:33 | 2016-12-06 07:40 | 4 | 127 | 4168241 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 472-23, REPLACED CUTOUT , RESTORED POWER AT 07:40.. VER/CRB L3/HFP XXXHFP
12031 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2014-10-14 11:44 | 2014-10-14 15:58 | 2 | 254 | 4619941 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR ON THE TAP FUSE. POWER IS BACK ON.//COD 2// VER/DBM
12032 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-11-09 17:53 | 2014-11-09 20:00 | 4 | 127 | 4715451 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | APPEARS THAT XFMR FUSE LINK FAILED. RESTORED @ 20:00. SH/ ISO 38830834D00210/ COD 4/ VER/BOW
12033 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-05-12 00:34 | 2010-05-12 04:48 | 2 | 254 | 59759-1 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400101// STS 35081122 WILL NEED 50 KVA 7200 PRIMARY 120/240ECONDARY TO REPLACE BAD 50 KVA CSP ALSO CUTOUT & POLE BRACKET . IS TRUCK ACCESSABLE. 1 A LINEMAN & MATERIAL HANDLER IDC XXXX
12034 | Pikeville | 3409502 | BURDINE | LEVISA | 2018-12-10 12:13 | 2018-12-10 16:27 | 2 | 254 | 4544611 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Found porcelain xmer cutout broken and will need replaced. No truck access. ENY Released by crew 074E06 replaced cut out all work complete L3/HFP
12035 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-05-28 10:58 | 2009-05-28 15:12 | 2 | 254 | 59487-1 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT DOOR,,,CUTOUT REPLACED AND POWER RESTORED IDC XXXX
12036 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-04-04 12:10 | 2020-04-04 14:17 | 4 | 127 | 4559771 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr fuse is blown will check// Cutout door is burnt up. This is a old style so will have to change cutout. I replaced cutout and restored customers @ 14:17
12037 | South Williamson | 3200301 | BELFRY | BELFRY | 2020-11-01 08:08 | 2020-11-01 10:15 | 4 | 127 | 4611181 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse open on Trans,Looking it over.Fuse was broke in cutout,Refused and restored at 10:15.
12038 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-11-19 02:44 | 2019-11-19 11:12 | 1 | 508 | 4046031 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONTACTED CUSTOMER/ADVISED TO TRIP MAIN BRK UNTIL A SERVICER CAN RESPOND/CALL DROPPED?TRIED CALLING BACK TO ADVISE SVCR WOULD BE THERE IN MORNING SINCE ABLE TO MAKE IT SAFE-NO ANSWER/40*HAVE TO REPLACE DAMAGED 4/3 SERV DROP W A 2/3HAVE TO REPLACE DAMAGED 4/3 SERV DROP W A 2/3//////REPLACED SERV&RESTORED,ALL OK AFTEWARDS L3/HFP
12039 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-03-19 14:11 | 2022-03-19 18:25 | 2 | 254 | 4647201 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 19.9 xfm. cutout on pole 1105-130.will make repairs..repairs made.restored
12040 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-05 17:08 | 2011-01-05 19:15 | 4 | 127 | 59047-1 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED ... REPLACED CURENT LIMITING FUSE AND REFUSED TRANSFORMER , ALL WORK COMPLETE / GXJ//COD 4// VER/DBM IDC XXXX
12041 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-08-06 12:06 | 2010-08-06 20:34 | 1 | 508 | 50411-1 | 508 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAS PART POWER. CHECKED VOLTAGE HAS 93 VOLTS ON TOP LUGS. CHECKED SECONDARY POLE WERE SERVICE COMES OFF AND ONE LEG OF SERVICE HAS PULLED INTO. NEED A SERVICER TO RE SPLICE SERV IN. RELEASED BY CREW 077F01 RELEASED BY CREW 077S10 VER/HFP L3/HFP
12042 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-04-17 19:12 | 2016-04-18 03:40 | 1 | 508 | 4098261 | 508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR NEED LINE CREW TO REPLACE TRUCK OK RELEASED BY CREW 078S05// RESTORED A@ 0326
12043 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2018-08-04 10:13 | 2018-08-04 18:40 | 1 | 507 | 4907391 | 507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10t fuse out due to bad 50kva transformer Released by crew 074S11..Opened remaining 2 xfmrs @ 17:33 replaced center and outside xfmrs and restored power @ 18:40
12044 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-06-26 00:33 | 2010-06-26 09:00 | 1 | 507 | 57664-1 | 507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THINK K MATE FUSE LINK BAD .BACK TO NORMAL THAY WHERE JUST 1 CUSTOMER ON THIS XFMER //VER/GAH IDC XXXX AJBC FEC57
12045 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-12-28 14:11 | 2022-12-28 17:00 | 3 | 169 | 4371401 | 507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad Transformer on pole 375-2784. Upgrading to bigger size transformer. Bringing 19.9 100KVA xfrm from hazard. Released by crew 077H15 restored @ 17:00
12046 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-05-03 09:06 | 2010-05-03 11:55 | 3 | 169 | 54875-1 | 507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON 38830954A10385. FOUND BROKEN XFMR CUTOUT ON 38830954A10396. ONLY FEEDS STREET LIGHT - ISOLATED AND WILL REPLACE AFTER CUSTOMERS ARE RESTORED. CORRECTION, XFMR @ 396 FEEDS NOTHING. WILL LEAVE ISOLATED. RESTORED CUSTOMERS @ 11:55. SH COD-3 ISO 38830954A10385 VER/HFP L3/HFP IDC XXXX
12047 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-09-24 13:52 | 2011-09-24 18:05 | 2 | 253 | 4912191 | 506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE A BAD 50 KVA TRANSFORMER, SINGLE BUSHING 7200 120/240, CREW REQ, CAN USE TRUCK, LOC LITTLE SANDY STRIP MALL RELEASED BY CREW 078S06 COMPLETE @ 18:05 PLEASE CLOSE TICKET RM//COD 2// VER/DBM IDC XXXX
12048 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-07-04 16:32 | 2008-07-04 20:45 | 2 | 253 | 62176-1 | 506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 45/4 POLE 25 KVA CUTOUT LA 2-CUST OUT RELEASED BY CREW 078S08 VER/HFP IDCC CNT1 XXXX
12049 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2014-08-16 20:48 | 2014-08-17 01:01 | 2 | 253 | 4374931 | 506 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NUMBER 2 WIRE BURNT DOWN TRUCK TO POLE RELEASED BY CREW 078S08/NEED TO OPEN FUSES ON 21-D2-104 FOR REPAIRS APPROX ONE HOUR OUTAGE/FETR0200/VEM/FUSE OPEN@0027/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST@0101/PLEASE CLOSE TICKET/THANKS/VEM VER/SEF IDC XXXX
12050 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2022-06-15 08:27 | 2022-06-15 12:40 | 2 | 253 | 4121961 | 506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10 kva xfr 280-98 Released by crew 078S05 Closed at 12:40. voltage good ticket complete.
12051 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-07-16 13:07 | 2016-07-16 17:20 | 2 | 253 | 4646831 | 506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEC. LEAD CAME LOOSE FROM BUSHING OPENED XFM @ 16:45 AND MADE REPAIRS..PLEASE SEND COPY TO ROW.ROW IS TERRIBLE HERE.AND SEND COPY TO CLIFF FREEMAN SEC. POLE 145-03 NEEDS REPLACED BAD.. VER/CRB
12052 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-06-12 10:47 | 2018-06-12 15:00 | 2 | 253 | 4590421 | 506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
12053 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2012-12-20 14:34 | 2012-12-20 15:20 | 11 | 46 | 4487691 | 506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BURNT POLE OFF OPENED LINE FUSE AT 1434 CLOSED AT 1520 VER/KEP
12054 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-02-22 07:22 | 2022-02-22 11:35 | 2 | 253 | 4526601 | 506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva on pole 1150-62, Austin Hall coming to change to 25kva
12055 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-02-20 18:09 | 2010-02-20 22:22 | 2 | 253 | 59425-1 | 506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// BAD CUTOUT CALLING FOR CREW EST TIME ON 23;30 COMP. 22;22 W.MELTON IDC XXXX
12056 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-05-15 15:29 | 2012-05-15 17:10 | 5 | 101 | 4798081 | 505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830248C00380, CREW ENROUTE.------- REPLACED 2 CUTOUTS, POWER RESTORED. ///VER/CRB L/3 CRB IDC XXXX
12057 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-05-29 13:54 | 2009-05-29 15:35 | 5 | 101 | 66427-1 | 505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP CHECKING TRANSFORMER AT LOCATION POWER RESTORED AT 15:35PM FUSE BROKE COD-5 ISO 37820103B00024 L3/HFP IDCC CCO XXXX
12058 | Whitesburg | 3312902 | JENKINS | JENKINS | 2011-08-14 21:09 | 2011-08-14 22:50 | 5 | 101 | 4711001 | 505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNED OFF AT POLE NO.381-438 . I REPLACED THE CLAMP VER/PDP IDCC PN449 XXXX
12059 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-05-11 12:50 | 2009-05-11 21:15 | 1 | 505 | 60361-1 | 505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICE CONNECTION IS BURN OFF AT TRANSFORMER. I REPAIRED THIS TEMPORARILY BUT TRANSFORMER NEEDS REPLACED AS WELL AS ENCLOSED CUTOUT AND ARRESTOR. CREW WILL NEED A 15 KVA (7.2) TRANSFORMER. THIS IS NOT TRUCK ACCESSIBLE RELEASED BY CREW 077S07
12060 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-01-26 16:47 | 2011-01-27 01:12 | 1 | 505 | 65315-1 | 505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38586467 ///45/4 POLE BURNT OFF BESIDE ROAD 1 CUSTOMER OUT/LOOP CUT ON 292-295 RELEASED BY CREW 078S03//ON SITE PRT//REPLACED POLE AND ANCHOR, POWER RESTORED AT 01:12 P R TOLLIVER IDC XXXX
12061 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2012-07-11 16:50 | 2012-07-11 18:31 | 5 | 101 | 4688811 | 505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTENING ARRESTER BROKE DOWN ON POLE 1127-445 AND BLEW CENTER LINE FUSE ON POLE 1127-268. I CLEARED ARRESTER AND I AM GOING BACK ON HILL TO CLOSE LINE FUSE IN. COD-5 ISO LF 38831127A00268 VER/HFP L3/HFP
12062 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-04-10 20:46 | 2009-04-10 23:34 | 3 | 168 | 51261-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, BROKEN CUTOUT, REPLACING IT VER/KEP L3/KEP IDC XXXX
12063 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-05-26 07:48 | 2009-05-26 12:00 | 2 | 252 | 66343-1 | 504 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3000102// BAD CUTOUT BURNT CROSSARM INTO--LYNCHS CREW TO WORK//COD 2//----CREW ON SITE, WILL ISOLATE AND CHANGE ARM// VER/DBM IDC XXXX
12064 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-06-22 17:34 | 2019-06-22 17:41 | 72 | 7 | 4568801 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | was on trouble ticket 4568501, after restoring this ticket i noticed, that the pri wire had came off ptp, and was floating beside of pole, need l/c to make repairs, no truck to pole, will have to open rec, turn at pig hill rd marked, 2 pole from rec. 1047-6 Released by crew 078S06//tie wire failed//NO OUTAGE TILL RECLOSER 39831047C30100 OPENED @ 1734 closed @ 1741 please close ticket thanks.bt
12065 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-11-04 16:35 | 2010-11-04 17:03 | 18 | 28 | 51855-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD-15OFF TIME 16:35 ON TIME 17:03 VER/HFP L3/HFP IDC XXXX
12066 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-06-02 07:34 | 2009-06-02 10:22 | 3 | 168 | 58500-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT AND ARRESTER BAD ON B PHASE TRANSFORMER. WILL CHANGE BOTH ON ALL THREE PHASES.// WORK COMPLTED AND POWER RESTORED AT 10:22 L3/HFP IDC XXXX
12067 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-10-14 10:41 | 2009-10-14 12:05 | 6 | 84 | 62042-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. REPLACED AND RE-FUSED LINE. SH VER/TOM IDC XXXX
12068 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-09-08 14:53 | 2021-09-08 19:05 | 2 | 252 | 4222171 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kva xfmr in bank. Replaced three cutouts & 15 kva transformer (C phase) on 875-496. Restored @ 19:05. sh
12069 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2020-01-14 12:13 | 2020-01-14 16:25 | 2 | 252 | 4304231 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew reqd, the transformer fuse is blown,,, but the cut out is broken, new cutout needed, truck OK, observer needed Released by crew 078H07crew reqd, the transformer fuse is blown,,, but the cut out is broken, new cutout needed, truck OK, observer needed ...
12070 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-10-10 18:43 | 2011-10-10 22:55 | 2 | 252 | 4963111 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER CREW ENROUTE COD-2 ISO TF 37830024D20158 VER/HFP L3/HFP IDC XXXX
12071 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-12-19 04:32 | 2008-12-19 05:35 | 8 | 63 | 60047-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3007904 // OPENED RECLOSER TO CONNECT TAP, CLOSED RECLOSER AND STAYED IN FOR ABOUT ONE MINUTRE WHEN FLASH OCCURRED DUE TO TROUBLE ON TAP // CHECKING FOR TROUBLE AT THIS TIME// COD-8 // ALSO SEE 60041-1 // VER/LDA L3/KEP IDC XXXX
12072 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-04-11 17:52 | 2022-04-11 18:28 | 14 | 36 | 4748261 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | neutral down not by truck @ 38830355000047. looks like a copper to aluminum sleeve pulled out Released by crew 078S12. crew on site to make repairs. opened lf on pole 356-27 @ 17:52 to make repairs. repairs make lf back in @18:28 on pole 356-27 complete Released by crew 078H31
12073 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-03-15 12:13 | 2017-03-15 16:25 | 2 | 252 | 4559331 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR IS BAD WILL NEED 2 MEN 25 KVA 19.9 / 120- 240 & MATERIAL HANDLER. HAVE CONTACTED STEVE RAY & HE IS GETTING MEN & EQUIPTMENT. 38831125D00815 VER/AWD
12074 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2014-03-14 21:38 | 2014-03-15 01:50 | 2 | 252 | 4494091 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA XFMR ON 738-281 WAS SMOKING SO I OPEND XFMR CUTOUT AT 22:40. CREW ENROUTE TO REPLACE. REPLACED XFMR AND RESTORED @ 1:50. SH VER/ARN
12075 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-02-03 08:11 | 2021-02-03 16:35 | 1 | 504 | 4932891 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | A phase dip fuse blown on pole 144-434 will refuse///Bad 750 KVA pad mount xfm///Storeroom is bringing one from AShland will be here around 13:00///Send to Paul Layne Released by crew 074S02 // repaired and restored @1635
12076 | Hazard | 3303902 | LESLIE | WOOTON | 2008-03-04 16:47 | 2008-03-04 20:59 | 2 | 252 | 52860-1 | 504 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3303902//REPLACED BAD CONNECTION VER/HFP IDC XXXX
12077 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-02-09 22:24 | 2012-02-10 00:30 | 4 | 126 | 4331451 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RED TO RED OUT VER/ARN IDC XXXX
12078 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2014-03-13 18:29 | 2014-03-13 18:38 | 56 | 9 | 4490681 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RETURNING CKTS NORMAL. VER/ARN IDC XXXX
12079 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-07-05 00:53 | 2010-07-05 01:29 | 14 | 36 | 62194-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE //VER/GAH IDC XXXX
12080 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2016-02-21 15:08 | 2016-02-21 16:04 | 9 | 56 | 4744461 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD A PHASE CUTOUT. I OPENED PHASE B & C AT 15:08, AND CLOSED IN AT 16:04. PART OF TICKET 4744241. VER/CRB
12081 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-09-01 08:21 | 2012-09-01 09:03 | 12 | 42 | 4990921 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 1147-4068 BOTTOM RISER ON CUTOUT BURNT OFF CHGED CUTOUT IDC XXXX
12082 | Pikeville | 3409502 | BURDINE | LEVISA | 2009-05-10 15:20 | 2009-05-10 19:32 | 2 | 252 | 56450-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE OUT ON XFMRCUST. BACK ON//VER/CRB
12083 | Paintsville | 3401802 | INDEX | HOSPITAL | 2022-08-07 09:24 | 2022-08-07 13:36 | 2 | 252 | 4698251 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse appears to have broke. Restored @ 13:36. sh
12084 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-10-14 00:24 | 2010-10-14 04:36 | 2 | 252 | 59456-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR FUSE BLOWN ON POLE 519-86 DUE TO BAD ARRESTER... CUT ARRESTER IN CLEAR RESTORED POWER AT 04:36, ONLY SERVED TO METERS, CAN USE TRUCK TO REPLACE ARRESTER RELEASED BY CREW 077S11 //VER/GAH IDCC PN85 XXXX
12085 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-05-30 20:42 | 2017-05-31 00:54 | 2 | 252 | 4884041 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 XFM.NEED B LINEMAN AND BUCKET TO CHANGE OUT..RESTORED..
12086 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-03-21 05:33 | 2019-03-21 13:57 | 1 | 504 | 4004821 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HELD IN ACCORDANCE WITH KPCO CALLOUT GUIDELINES//. cutout broke, making repairs. power restored @ 13:57. pls close. tre
12087 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2019-12-30 11:03 | 2019-12-30 13:51 | 3 | 168 | 4195221 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke. repairs made. pls close tre
12088 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2008-10-20 13:54 | 2008-10-20 16:00 | 4 | 126 | 57359-1 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP ARRESTER WENT BAD == CUT IN CLEAR == REFUSED LINE FUSE POLE 392-12 ENTERED MD TO GET 30T FUSE ADDED TO MAP...HFP IDC XXXX
12089 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-05-04 08:51 | 2012-05-04 17:15 | 1 | 504 | 4742701 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT ON POLE 669-44 NO TRUCKS TO POLE , NEED LINE CREW. RELEASED BY CREW 078S01//CREW ON SITE STARTING REPAIRS TCM// COD 1// VER/DBM IDC XXXX
12090 | Pikeville | 3402002 | KEYSER | STONECOAL | 2020-08-31 16:30 | 2020-08-31 20:42 | 2 | 252 | 4408661 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFR HERE,NEED A 25 7.2 XFR.WINCH JOB HERE Released by crew 074S06 1128-155 changed xfmr installed sec 1/0 to 1128-70//cod 2
12091 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-03-27 22:20 | 2012-03-27 22:32 | 42 | 12 | 4623581 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE (43 CUST) SWITCH ON POLE 38831074C00490 FAILED. CREW HAD TO OPEN RECLOSER TO ALLOW THEM TO SAFELY MAKE REPAIRS /// RELATED TO ORDER 4623471// OPENED RECLOSERS @ 2220 // COD 5 CUST ON A PHASE /28 CUST ON B PHASE / & 3 CUST ON A&B TOTAL CUST 36 // ISO OCR 38831074D00092 VER/HFP L3/HFP IDC CHANGED COUNT FROM 36 XXXX
12092 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-04-03 12:17 | 2014-04-03 15:05 | 3 | 168 | 4559341 | 504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW TO REPLACE CUTOUT RELEASED BY CREW 078S07///REPLACED BROKEN CUTOUT///VOLT CK GOOD///TBL TKT COMPLETE VER/SEF
12093 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-09-08 18:22 | 2009-09-08 22:33 | 2 | 251 | 56625-1 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WORK REQUEST # 31619965 FUSE BLOWN ON HILL TRYING FOR RESTORE//CUTOUT BAD 7200 VOLT AND POLE IS SPLIT AT RIDGE PINS CALLING FOR CREW TO ASSISTFUSE BLOWN ON HILL TRYING FOR RESTORE//CUTOUT BAD 7200 VOLT AND POLE IS SPLIT AT RIDGE PINS CALLING FOR CREW TO ASSIST//OPENED RECLOSERS AT POLE 153-273 AT 22:15 AND RESTORED AT 22:33 L3/HFP IDCC TON2235 XXXX
12094 | Hazard | 3309301 | VICCO | REDFOX | 2015-12-14 10:39 | 2015-12-14 14:50 | 2 | 251 | 4530251 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR AND LINE FUSE HAS BLOWN, POLE #S ARE 325-261 AND 262. BAD 10 KVA XFMR IN 2 POT BANK, WILL NEED CREW. G SHOUSE CREW COMING TO REPLACE RELEASED BY CREW 077S02 // COD-2 ISO TF 37830325C00261 VER/HFP L3/HFP
12095 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-02-20 21:39 | 2011-02-21 01:50 | 2 | 251 | 59544-1 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO REP;ACE 19.9 25 KVA TRANSFORMER VER/HFP IDC XXXX
12096 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-02-07 08:14 | 2014-02-07 12:25 | 2 | 251 | 4365531 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 15 KVA TRANSFORMER ON 782-2. NEED A MATERIAL HANDLER AND 25 KVA TRANSFORMER. CREW ENROUTE TO REPLACE. CREW ON SITE. RESTORED @ 12:25. SH COD-2 VER/HFP L3/HFP
12097 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2012-06-26 17:24 | 2012-06-26 21:35 | 2 | 251 | 4965431 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REFUSED LINE CUTOUT, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03//MADE MDC ///VER/CRB L/3 CRB
12098 | Hazard | 3420001 | SOFT SHELL | VEST | 2022-09-20 13:22 | 2022-09-20 17:33 | 2 | 251 | 4901491 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva 19.9 transformer manual, need ROW crew. send to rick maggard Released by crew 077H05.. restored @ 17:33
12099 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-10-14 08:36 | 2011-10-14 12:47 | 2 | 251 | 4977551 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED, BAD 15 KVA CSP, NEED 15KVA 7200 XFMR AND CUTOUT AND BRACKET, TRUCK OK, WILL HAVE TO SET UP ON ROAD, TRANSFORMER WOULD NOT RESET. RELEASED BY CREW 078S05//COD 2//FETR NEEDED ONCE CREW ARRIVES ON SITE //OPENED LINEFUSE 207-122 @ 12;01 BACK ON @ 12;41////XFMR VOLT CK OK 117/117/246V---//COD 2 IDC XXXX
12100 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-05-28 20:08 | 2010-05-29 04:30 | 1 | 502 | 52812-1 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TR CUTOUT VER/LDA IDC XXXX
12101 | Hazard | 3301401 | COMBS | COMBS | 2017-01-03 20:16 | 2017-01-04 00:27 | 2 | 251 | 4266221 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 271-8, BAD LIGHTNING ARRESTOR ON POLE 271-554, CUTOUT IS BROKE ALSO, WILL NEED HELP VER/KEP L3/HFP HFPC FP37830271C00007
12102 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-01-30 13:00 | 2012-01-30 17:11 | 2 | 251 | 4305781 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND A 25 KVE SINGLE BUSHING, 7200 120/240 LEAKING OIL, HAVE TRANSFORMER OPEN AT 1300, WELL NEED CREW 3 MEN YARD DOG, CAN NOT GET TRUCK TO POLE RELEASED BY CREW 078S06/CREW ON SITE/FETR1830/VEM/XFMR CHANGED AND POWER RESTORED TO ALL CUST 1711/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB IDCC PN NULL XXXX
12103 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2013-01-22 00:59 | 2013-01-22 05:10 | 2 | 251 | 4725751 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY BROKE AT DEADEND CLAMP AND IS HANGING BY XFMR CUTOUT RISER. PRIMARY SAGGED INTO NEUTRAL AND BLEW LINE FUSE. REPAIRING. RESTORED @ 5:10. SH VER/KEP IDC XXXX
12104 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-05-03 07:39 | 2014-05-03 11:50 | 2 | 251 | 4659101 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFOEMER, NEED TO GO BACK WITH 25KVA 7200, X1 BUSHING VOLTAGE 100,X2 VOLTAGE 124 .NEED LINE CREW WITH MATERIAL HANDLER. RELEASED BY CREW 078S01/FETR 12:30 JEH/REPAIRS COMP. @ 11:50/ CLOSE TICKET PLESE VER/SEF
12105 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-04 10:04 | 2015-02-04 14:15 | 2 | 251 | 4990001 | 502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CANNOT GET POWER OUT OF XFMR, MIGHT HAVE PHASE OUT. C PHASE CUTOUT BROKE ON POLE 254-177, WILL NEED HELP/ C PHASE COD 2/ ISO 37830230B00256/ COD 2/ OPENED RECLOSER ON 37830230B00256 FIXED SWITCH 37830254A00177 WHILE OPEN THEN CLOSED RECLOSER AND EVERYTHING WAS RESTORED L3/DKGXXXX
12106 | Hazard | 3303902 | LESLIE | WOOTON | 2014-07-21 08:20 | 2014-07-21 16:41 | 1 | 501 | 4267351 | 501 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER CHECKING PRIMARY METERING. BAD CUTOUT === REPLACED CUTOUT === POWER OK /// COD-1 ISO LF 37830486000189 VER/HFP L3/HFP
12107 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-05-20 10:24 | 2017-05-20 18:45 | 1 | 501 | 4827201 | 501 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | KY OUTAGE/ WILL HAVE KY CREW REPLACE THIS TRANSFORMER/ ISO 38820721D00027/ COD 1/ VER/BOW
12108 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-12-02 09:48 | 2018-12-02 12:35 | 3 | 167 | 4500191 | 501 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout on pole 37830376C00006 // line fuse open on pole 37830376C00112 COD 3 L3/HFP
12109 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2016-12-24 00:53 | 2016-12-24 03:40 | 3 | 167 | 4231771 | 501 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RISER CUTOUT FAILED ON 808-119 (NOT ON MAPS) AND BLEW LINE FUSE ON 808-14. REPLACED CUTOUT AND RESTORED @ 3:40. SH VER/TOM L3/TOM
12110 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2021-05-08 06:01 | 2021-05-08 08:48 | 3 | 167 | 4550111 | 501 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Replaced a broken cutout on pole 199-142. Power restored at 8:48.
12111 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2010-03-30 04:10 | 2010-03-30 05:00 | 10 | 50 | 55837-1 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT FAILED. VER/PDP AJB
12112 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2011-01-26 05:10 | 2011-01-26 09:30 | 3 | 260 | 64334-1 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38577708 //CUTOUT BROKE ON POLE 795-109//TRUCK APPROACH, GOING TO CHANGE NOW//XFMR FUSE ISOLATED//SIDE TAP BACK ON AT 7:10// RELEASED BY CREW 079S01 /// ONLY 1 CUST OUT RESTORED @ 0930 VER/HFP L3/HFP IDC XXXX
12113 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-12-12 05:05 | 2014-12-12 06:45 | 5 | 100 | 4855661 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1.6 TRANS FUSE BROKE ALL PWR RESTORED AT 06:45 PLEASE CLOSE TICKET THANK YOU// COD 5// VER/ ADH
12114 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2021-12-06 11:04 | 2021-12-06 12:44 | 5 | 100 | 4152751 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke lf cutout on pole 400A-151. Made repairs. Power restored at 12:44.
12115 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-03-15 19:15 | 2021-03-15 23:25 | 2 | 250 | 4338471 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required no trucks Released by crew 078S03 crew on site FETR 23 :45 all pwr restored @ 23:25
12116 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2017-03-18 03:00 | 2017-03-18 11:20 | 1 | 500 | 4566461 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL VCHECK IN THE AM 3/18/17//////-///CUTOUT BURNED UP ON 1041-72,WILL REPLACE IF I CAN DO SO SAFELY////////REPLACED CUTOUT&RESTORED.ALSO,THERE WAS A POLE OUT@END OF TAP HAD ROTTED OFF AND FELL.DOESNT APPEAR TO BE MAPPED.I CUT DOWN THE 1 WIRE(PRIM COND)THAT WENT TO THIS POLE,DID NOT SERVE ANYTHING.THIS IS WHAT BURNED THE CUTOUT DOOR OUT./ ISO 38821041B00072/ COD 1/ VER/BOW
12117 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-05-11 10:58 | 2022-05-11 11:48 | 10 | 50 | 4877141 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Open stepdown TR 37820146000194 to replace arrestor and cutout on pole 37820146000125///Off at XXXX -- On at XXXX---DAE 1000058651Open at 10:58 closed at 11:48. Cutout and arrester replaced on pole 146-125.//REMOVED FROM DAE
12118 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-10-29 11:40 | 2012-10-29 12:30 | 10 | 50 | H4181531 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830248A00788, CREW AND FLAGGERS ENROUTE. OPENED FUSE ON POLE 37830248A00788 AT 1140(11 CUSTOMERS) TO REPLACE CUTOUTS ON POLE 37830248A00788BAD CUTOUT ON POLE 37830248A00788, CREW AND FLAGGERS ENROUTE.--- OPENED LINE ON POLE 37830248A00788 AT 11:40, CLOSED AT 12:30 DUP FROM 4181531 FOR 10 CUST VER/HFP L3/HFP IDCC PN4 XXXX
12119 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-09-07 19:08 | 2014-09-07 23:18 | 2 | 250 | 4478371 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 20A41531 BAD 25 KVA, 7200 XFMER, UPGRADE TO 37.5 YARD DOG RELEASED BY CREW 078H12/CREW ON SITE/FETR 0030/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2318/PLEASE CLOSE TICKET/THANKS/VEM VER/DKG L3/DKG
12120 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-10-12 14:55 | 2014-10-12 23:15 | 1 | 500 | 4609161 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | D HAMILTON & P LAYNE & T MCCOWN & E MCKINNEY & CALLED STORE ROOM OUT D MILLER // POSSIBLE U/G FAULT// REPLACING U/G// REPAIRS MADE // POWER RESTORED @ 23:15 VER/SEF
12121 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2020-10-19 09:23 | 2020-10-19 13:33 | 2 | 250 | 4566821 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service burnt down
12122 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2016-03-28 15:38 | 2016-03-28 17:18 | 5 | 100 | 4888931 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANS CUTOUT VER/CRB
12123 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-09-25 07:45 | 2009-09-25 16:05 | 1 | 500 | 61982-1 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE ON POLE 38830185000107 AT 08:30, CREW HAS BEEN NOTIFIED, 45 POLE. TRUCK OK, SHOULD HAVE METERIAL FOR JOB ON TRUCKS RELEASED BY CREW 078S05 COD-7 MADE DUP FOR FUSE MD FILED VER/KEP L3/KEP IDC XXXX
12124 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-02-16 08:35 | 2014-02-16 10:40 | 4 | 125 | 4391831 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10T APPEARS TO HAVE BROKEN OR MELTED OUT ON XFMR 810-306.10T APPEARS TO HAVE BROKEN OR MELTED OUT ON XFMR 810-306. RESTORED @ 10:40. SH // FUSE WAS NEVER OUT HAD TO OPEN IT TO GET ORDER TO RESTORE IN POWERON // ENTERED MD -- COD-4 ISO TF 38830810B00306 VER/HFP L3/HFP
12125 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-04-23 10:48 | 2013-04-23 10:58 | 50 | 10 | 4038671 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TR NEVER OUT FOR HOIS MARSHAL FOUND BROKEN TIE WIRE AT POLE 354-68 - CREW ENROUTE TO MAKE REPAIRS * NO OUTAGE AT THIS TME .. WHEN CREW IS READY THEY WILL OPEN RECLS AT 378-15- TO MAKE REPAIRS. 50 CC.TIE WIRE WAS BAD ON THIS POLE, WE HAD TO RETIE ITTIE WIRE WAS BAD ON THIS POLE, WE HAD TO RETIE IT. WE OPENED THE LINE AT 10:48 AND CLOSED BACK AT 10:58 VER/PDP IDCC PN69 XXXX
12126 | Hazard | 3303902 | LESLIE | WOOTON | 2017-04-25 12:40 | 2017-04-25 14:45 | 4 | 125 | 4681121 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 7200 CUTOUT/ ISO 37830510000128/ COD 4/ VER/BOW L3/HFP XXXHFP
12127 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-10-14 10:35 | 2011-10-14 14:45 | 2 | 250 | 4978171 | 500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT--241-20--PATROLLING NOW //COD 2// ISO 37830241000020 // VER/DBM IDC SWITCH OR FUSE? XXXX
12128 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-06-01 15:56 | 2008-06-02 00:15 | 1 | 499 | 53836-1 | 499 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308502//10 KVA XFMR BAD P HICKMAN WILL WORK AFTER OTHER TROUBLE NEEDS 15 KVA 7200 120/240 COD-1 VER/KEP IDC XXXX
12129 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-04-12 01:03 | 2011-04-12 09:22 | 1 | 499 | 55467-1 | 499 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | HELD TIL AM STS BAD ARRESTOR ON POLE 1039-136 POLE DOES NOT SERV ANYONE SO I REMOVED IT OFF LINE VER/HFP L3/HFP
12130 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-07-25 10:56 | 2011-07-25 19:15 | 1 | 499 | 4617691 | 499 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308401/RELEASED BY CREW 077S02/// LINE FUSE BLOWN POLE 155-51, CHECKING LINE,///// BAD XFMR 15KVA 7200, NEED C/O AND BRKT. //VER/GAH IDC XXXX
12131 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-04-10 18:03 | 2021-04-10 20:00 | 7 | 117 | 4438951 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout// had to open transformer to make repaires opened @1950 closed both line fuse and xfmr @2000 restoring all
12132 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-11-13 12:51 | 2014-11-13 17:00 | 2 | 249 | 4725281 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED TRANSFORMER BANK ON POLE 38831098D00417 . REPLACED 3 CUTOUTS, 3 DEADEND INSULATORS, AND 3 PIN TYPE INSULATORS ON POLE 1098-429 / ALL WORK COMPLETE / GXJ// ISO 38831098D00417/ COD 2/ VER/BOW
12133 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2022-01-04 08:01 | 2022-01-04 12:10 | 2 | 249 | 4297211 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 k v a transformer changing out to a 25 k v a power restored at 12:10
12134 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2022-11-23 10:57 | 2022-11-23 12:20 | 6 | 83 | 4176161 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830834B00445 (COD 6)xformer cutout was broke at pole 834-B-445 and it changed out and power restored at a time of 12:20
12135 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-03-02 07:06 | 2009-03-02 11:15 | 2 | 249 | 53582-1 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307301// BAD CUTOUT, WAITING ON MAINT. TO OK OUTAGE BAD CUOUT ON POLE # 129-178, LINE FUSE OUT ON POLE # 129-28, ONLY 1 PHASE OUT//VER/CRB IDC XXXX
12136 | Pikeville | 3421001 | BREAKS | CITY | 2014-01-14 10:17 | 2014-01-14 11:40 | 6 | 83 | 4280581 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING LEAKING TRANSFORMER /// TIME OFF 10:17 TIME ON 11:40 .XFMR HAS BEEN REPLACED AND SERVICE RESTORED. COD-6 ISO TF 37820220D10157 VER/HFP L3/HFP
12137 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2013-12-10 23:28 | 2013-12-11 00:51 | 6 | 83 | 4150541 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR ON FIREON 37830095000014/// WILL TRY TO REPLACE/ REPLACED DOOR//POWER IS RESTORED VER/TOM L3/TOM
12138 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-05-12 11:05 | 2011-05-12 12:28 | 6 | 83 | 4071981 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLOWN ON POLE 674-313//FOUND BUSTED INSULATOR ON POLE 674-315//CHANGED INSULATOR//RESTORED CUSTOMERS AT 12:28//COMPLETE//EM VER/HFP L3/HFP
12139 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-11-05 04:58 | 2010-11-05 09:07 | 2 | 249 | 53063-1 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE ON THE POLE , NEED CUTOUT AND BRACKET AND CREW M.D.I. RELEASED BY CREW 077S12 OPENED LINE FUSE AT 840 CLOSED LINE FUSE ON PLOE 450-223 AT 907 REPLACED CUTOUT ON POLE 450-212//COD 2//VER/CRB IDC XXXX
12140 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-12-29 23:38 | 2019-12-30 03:47 | 2 | 249 | 4191481 | 498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout // cod 2
12141 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-09-29 21:27 | 2021-09-30 05:45 | 1 | 498 | 4303871 | 498 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad termination in primary underground on pole 37830398D00418 , made repairs restored power at 05:45.
12142 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-02-17 10:13 | 2018-02-17 18:00 | 2 | 467 | 4854121 | 497 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | will need to replace 25 kva xfmr .19.9_120/240.no truck aproach need. 4 men .truck with winch or 3 sheve blocks.can possibally get pickup across bridge/ replaced transformer/ 1 customer out orginally/ opened transformer @ 1730 affecting 1 add. cust/ all power restored @ 1800/ ISO 37820193A00210/ COD 2
12143 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-06-02 15:19 | 2018-06-02 16:30 | 7 | 71 | 4547321 | 497 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Several bad connections at location, repairs made
12144 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2019-04-15 18:40 | 2019-04-15 22:48 | 2 | 248 | 4119321 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | trans hot line clamp on 1088A67 disengaged from primary conductor.reapplied hot line clamp.restored power at 22:48/ ISO 38821088A00067/ COD 2 L3/HFP
12145 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2012-04-21 11:34 | 2012-04-21 19:50 | 1 | 496 | 4692561 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSFORMER. WILL REPLACE IT AFTER THE CASE OF TROUBLE ON OPEN FORK HAS BEEN RESTORED. RELEASED BY CREW 074S02 CREW ON SITE WORKING WORK COMPLTED VOLTAGE CHECK ALL OK//COD 1// VER/DBM IDC XXXX
12146 | Paintsville | 3401102 | FALCON | SALYERSVI | 2011-03-05 13:22 | 2011-03-05 17:30 | 2 | 248 | 50078-1 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR...CUT IN CLEAR AND RE FUSED AT 17.30..BB STS WR # 39051210 // CHECKED HARDWARE AND FOUND NOTHING WRONG. WILL TRY FUSE. FUSE BLEW HARD WHEN I CLOSED LINE FUSE ON 875-613. EITHER CUTOUT, ARRESTER, 6 DISC OR 1301 INSULATOR IS BAD. WILL HAVE TO CLIMB POLE TO DETERMINE WHICH. MUST WALK TO XFMR BANK BEHIND NEW SCHOOL. CREW ENROUTE. RELEASED BY CREW 076S02 COD-2 ISO LF 38830875B00613 VER/HFP L3/HFP IDC XXXX
12147 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-02-06 06:00 | 2015-02-06 07:02 | 8 | 62 | H4995191 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN WIRE SECONDARY DOWN. OPENED XFMR38830834A00576 @ 6:00 TO MAKE REPAIRS. PUT UP WIRE AND CLOSED XFMR @ 7:02. SH VER/CRB // PER SERVICER 2 CUST ORIGINALLY OUT L3/HFP HFPC CNT9
12148 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-10-12 15:45 | 2021-10-12 15:53 | 62 | 8 | 4343721 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary at pole 984-43 has one strand of wire left holding it up, will have to open line fuse on pole 984-48 to safely make repairs, Myles is coming to open fuse to minimize outage time// opened LF 948-48 @ 15:45 closed @ 15:53
12149 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-07-16 13:01 | 2016-07-16 15:05 | 4 | 124 | 4646811 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POWER RESTORED .PLEASE SEND A NOTE TO CLIFF FREEMAN TO HAVE POLE #37830042D00071 CHANGED OUT .IT IS VERY ROTTEN AT THE GROUND LINE.//SENT TO TECH VER/CRB
12150 | Pikeville | 3408101 | SALISBURY | PRINTER | 2018-04-09 09:25 | 2018-04-09 11:29 | 4 | 124 | 4202871 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 6t transformer fuse out due to bad arrester pole 1123-b-7. called line crew is coming out to replace cutout and arrester. arrester and cutout changed everything ok
12151 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-02-27 07:23 | 2014-02-27 09:27 | 4 | 124 | 4437441 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPAN OF PRIMARY DOWN FROM POLE 1073/90 TO POLE 1073/135 CONDUCTOR BROKE AT BASKET SQUEEZE..//COD 4// VER/DBM
12152 | Hazard | 3311103 | STINNETT | WENDOVER | 2010-08-20 14:42 | 2010-08-20 18:50 | 2 | 248 | 58754-1 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR BOTTOM BLOWED AND HIT LEAD TO XFMR VER/KEP L3/KEP IDC XXXX
12153 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-01-22 18:19 | 2012-01-22 22:27 | 2 | 248 | 4282901 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 25 KVA TRANSFORMER, CUTOUT AND BRACKET, RISER WIRE . ADD TRANSFORMER TO POLE 38831098B00310 ( TRUCK ACCESS ) AND CUT EXISTING FAILED TRANSFORMER FROM SECONDARY AT POLE 443 ( DIFFICULT LOCATION ), . ALL WORK COMPLETE / GXJ VER/TOM L3/TOM IDC XXXX
12154 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-01-23 16:12 | 2018-01-23 18:16 | 4 | 124 | 4768341 | 496 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on pole need crew to come back and replace leads in xfmr//SENT TO LINE DEPT // L3/HFP
12155 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2013-11-29 07:16 | 2013-11-29 09:20 | 4 | 124 | 4087081 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR FUSE OPEN ON POLE 449-308, SECONDARY BURNT INTO AT XFMR SECONDARY LUG, MADE REPAIRES RESTORED POWER AT 09:20. VER/CRB
12156 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-10-01 15:53 | 2009-10-02 00:09 | 1 | 496 | 63105-1 | 496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15KVA 19.9 120/240. CAN USE BIG BUCKET RELEASED BY CREW 074S08 // WORK REQUEST 32006227 REPLACED BAD XFORMER AND RESTORED POWER. NEED TO SEND A NOTE TO JASON BRADSHAW TO HAVE R.O.W CUT AT THIS LOCATION. TIM MCCOY. RELEASED BY CREW 074H10 VER/LDA IDCC PN61 XXXX
12157 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-05-26 19:20 | 2020-05-26 22:05 | 3 | 165 | 4911031 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout at 246-311. making repaires. restored 22:05//cod 3
12158 | Hazard | 3303902 | LESLIE | WOOTON | 2008-06-03 17:42 | 2008-06-03 17:57 | 33 | 15 | 55250-1 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELATED TO ORDER 55097-1 CREW OPENED RECL TO REPAIR LOOP THAT BURNT OPEN AT POLE 37830342000085 VER/HFP
12159 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-03-09 09:10 | 2015-03-09 17:25 | 1 | 495 | 4170971 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, 3 BAD CUTOUTS ON BANK POLE, ALSO 8 FT CROSSARM, END BURNTED OFF, CAN USE TRUCK, / 140` UNDERGROUND NEED INSTALLED/ CREW ON SITE/FETR1530/VEM// ISO CREW REQ, 3 BAD CUTOUTS ON BANK POLE, ALSO 8 FT CROSSARM, END BURNTED OFF, CAN USE TRUCK, / 140 UNDERGROUND NEED INSTALLED/ CREW ON SITE/FETR1530/VEM. SERVICE IN CT CABINET FIXED AND POWER RESTORED FOR THIS CUSTOMER AT 17:25 ON 3/9/15.//ISO//COD 1// VER/DBM
12160 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-03-16 21:21 | 2014-03-16 23:00 | 5 | 99 | 4498981 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT. COD-5 ISO TF 38821114C00140 VER/HFP L3/HFP
12161 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-10-16 12:45 | 2012-10-16 13:40 | 9 | 55 | 4145871 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | B PHASE OUT COD 9//BAD ARRESTOR ON POLE 37830248C00352//MADE AED ///VER/CRB L/3 CRB IDC XXXX
12162 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-05-27 14:36 | 2008-05-27 17:21 | 3 | 165 | 51789-1 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3400301//40 T FUSE OUT ON POLE 45-16. I WILL TRY TO FUSE UP. BAD ARRESTER ON POLE 45-257.//COD 3// VER/DBM IDC XXXX
12163 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2008-08-18 08:17 | 2008-08-18 12:20 | 5 | 243 | 52780-1 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 12POLE 70--3667 HAS BROKEN CROSSARM-LIFTED HOTTAPS ON POLE 70-3642-CALLED FOR CREW-A PHASE FUSE BLOWN ON POLE 70-3564//// E MAIL TO OC POLE 70-3641 COVERED IN VINES AN NEEDS SPRAYED//3008003//WR#25809431//POLE 70--3667 HAS BROKEN CROSSARM-LIFTED HOTTAPS ON P//VER/CRB IDC MISSMAPPED CUSTOMER XXXX
12164 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-05-20 09:45 | 2018-05-20 12:30 | 3 | 165 | 4381851 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout door burnt up, transformer back in at 12:30
12165 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-08-02 01:45 | 2015-08-02 02:30 | 11 | 45 | 4966871 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD STIRRUP WHILE WORKING ON PO#4966791 VER/KEP L3/HFP XXXHFP
12166 | South Williamson | 3411401 | DEWEY | INEZ | 2010-06-12 18:55 | 2010-06-13 03:10 | 1 | 495 | 61714-1 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE CHANGING NOW.CHANGED CUTOUT
12167 | Hazard | 3309301 | VICCO | REDFOX | 2008-03-04 06:46 | 2008-03-04 09:31 | 3 | 165 | 52501-1 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309301// XFMR FUSE OUT ON POLE 3, BAD CUTOUT ON POLE # 301-3 RELEASED BY CREW 077S02//MISMAPPED//ONLY 3 CUSTOMERS OUT//VER/CRB IDC XXXX
12168 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-07-09 16:45 | 2015-07-10 01:00 | 1 | 495 | 4755711 | 495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONLY 1 CUSTOMER OUT///NEUTRAL WAS BROKE IN SERVICE DROP///REPAIRS MADE///CUSTOMER BACK ON AT 01:00///COMPLETE BR/ ISO 38830851B00076/ COD 1
12169 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-07-21 10:46 | 2022-07-21 19:00 | 1 | 494 | 4541681 | 494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot seondary on ground. Phillip hicks here working on ticket Released by crew 077M01. Repairs made. Power restored. 19:00. Durell Olinger
12170 | Hazard | 3303902 | LESLIE | WOOTON | 2012-01-13 10:21 | 2012-01-13 14:28 | 2 | 247 | 4257231 | 494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED BURNING 40 FT POLE WILL NEED CREW TRUCK ACCESSABLE ISOLATED ON 509-33 RELEASED BY CREW 077S01 VER/KEP IDC XXXX
12171 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2018-05-10 09:03 | 2018-05-10 13:10 | 2 | 247 | 4330231 | 494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | mismapped xfmer on pole 44-7122, bad 25 kva, 7200. please change co/ arrestor. yard dog, maybe service bkt. // COD-2 ISO TF 38830044D37127.vines, also changed cut out and arr,,,blr
12172 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-05-22 16:14 | 2017-05-22 20:21 | 2 | 247 | 4840151 | 494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 140-2504 BAD 167 19.9 TRANS. 4-SEC. BUSHING TRANS. NEXT TO MAIN ENTRANCE TRUCK TO POLE RELEASED BY CREW 078S08/CREW ON SITE/FETR 2030/VEM/REPAIRS MADE AND ALL CUST RESTORED 2021/PLEASE CLOSE TICKET/THANKS/VEM 38830140B02504 VER/AWD
12173 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-04-20 07:38 | 2013-04-20 15:52 | 1 | 494 | 4031841 | 494 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NEED CREW TO INSTALL POWER TEMP/OR REPAIR BAD UG// DENTIST OFFICE RELEASED BY CREW 078S07/ CREW ON SITE FETR APPROX. 18:30 JEH/LOCATED FAULT MAKING REPAIRS/ REPAIRS COMP. GOOD VOLTAGE POWER REST. @ 15:52 JEH VER/HFP L3/HFP IDC XXXX
12174 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-11-17 11:53 | 2012-11-17 16:00 | 2 | 247 | 4404931 | 494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUTOUT DOOR AND MAYBE CUTOUT ITSELF MAY BE BAD. I AM GOING TO CHANGE CUTOUT. 15 KVA , 12KV. TRANS. IS BAD. I NEED 1 MAN , 25 KVA TRANS. { 12 KV } AND MATERIAL HANDLER. WE CHANGED CUTOUT, ARRESTER. & TRANSFORMER//COD 2// VER/DBM IDC XXXX
12175 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-12-22 09:58 | 2013-12-22 14:05 | 2 | 247 | 4189771 | 494 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEED TO SEND SERVICE TRUCK TO CHK. XFMER CUSTOMER HAS A LOW LEG ON PUMP..CPS RELEASED BY CREW 078E04/NO CREW REQUIRED REPAIRED CONNECTIONS ON POLE 140B428//COD 2//ISO// VER/DBM L3/HFP
12176 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-03-25 08:36 | 2011-03-25 16:50 | 1 | 494 | 59161-1 | 494 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 39307246 // ... WILL NEED TO REPLACE UG SERVICE, LCS HAMILTON NOTIFIED / GXJ RELEASED BY CREW 074S03STS WR # 39307246 // ... WILL NEED TO REPLACE UG SERVICE, LCS HAMILTON NOTIFIED / GXJ ... ALL WORK COMPLETE / GXJ VER/HFP L3/HFP IDC NEEDED A DIGGING CONTRACTOR XXXX
12177 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-02-01 11:13 | 2013-02-01 15:20 | 2 | 247 | 4781611 | 494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 332-101 HAS FALLEN OVER IN THE TIMBER, WE WILL HAVE TO OPEN THE OTHER TWO FUSES ON POLE332-96 TO PULL THE POLE UP AND TEMPERARY GUY IT OFF. WE OPENED THE OTHER TWO AT 14:55 AND CLOSED BACK IN AT 15:20 . PLEASE SEND THIS TICKET TO DOUG CHRISTIAN TO CHANGE OUT POLE ///VER/CRB L/3 CRB IDC XXXX
12178 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-01-20 05:33 | 2014-01-20 09:40 | 2 | 247 | 4294491 | 494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT IS BROKE INTO, I NEED BIG BUCKET AND ONE MAN RELEASED BY CREW 077S12 //VER/GAH
12179 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-05-11 16:12 | 2014-05-11 16:29 | 29 | 17 | 4686091 | 493 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED RECLOSER TO SAFELY MAKE REPAIRS CLOSE TO BIG BLUE DRIVE// OUTAGE SHOULD BE L30 MINUTES// WILL UPDATE FETR IF FIND ADDITIONAL TROUBLE// OPENED @ 1611 CLOSED @ 1629 IDCC TON1631 XXXX
12180 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-02-07 10:38 | 2020-02-07 18:51 | 1 | 493 | 4378461 | 493 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 277/480 25kva 7200 xfm in bank. need new xfm and big bucket Released by crew 077S10.all power restored @ 18:51 hrs p.hicks
12181 | Whitesburg | 3401301 | FLEMING | NEON | 2015-10-20 13:22 | 2015-10-20 15:25 | 4 | 123 | 4364101 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT GONE BAD , I HAVE TO GO TO OFFICE TO GET PARTS// VER/ ADH L3/HFP XXXHFP
12182 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-01-26 16:59 | 2021-01-26 21:05 | 2 | 246 | 4896491 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke Transformer Cut-out,Going to change it out and restore service..Restored service at 21:05.
12183 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-05-31 17:03 | 2008-05-31 18:25 | 6 | 82 | 53515-1 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3314401// NUETRAL WAS BROKE AT SECONDARY POLE// VER/DBM IDC XXXX
12184 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-05-08 10:54 | 2019-05-08 11:00 | 82 | 6 | 4239831 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | Opened Recl long enough to take defective reg offline. reg is stuck in 6 lower Off @ 1054 On @ 1100
12185 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-07-25 10:07 | 2022-07-25 12:10 | 4 | 123 | 4572611 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1021/gaj/Called customer & confirmed they are still out. Reset breakers. Not sure if neighnbors are out or not. Burnt up cutout door, restored
12186 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-11-22 09:12 | 2011-11-22 11:15 | 4 | 123 | 4099711 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREWS OPENED FUSE IN ORDER TO MAKE REPAIRS FOR ORDER 4099301//COD 4// VER/DBM IDC XXXX
12187 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-12-06 05:16 | 2021-12-06 13:28 | 1 | 492 | 4150341 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830234B40238 c/o on arm broke--crew req-ds120621 Released by crew 078S01 crew on site FETR 14:30 LRM pwr restored 13:28
12188 | Hazard | 3302703 | HAZARD | HAZARD | 2019-01-25 08:19 | 2019-01-25 11:03 | 3 | 164 | 4721041 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
12189 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2014-03-03 09:00 | 2014-03-03 17:12 | 1 | 492 | H4445821 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK IN AM HOURS WHEN ROADS ARE SAFE // B PHASE ONLY OUT COD 64 WILL CHECK IN AM HOURS WHEN ROADS ARE SAFE // FAULT POLE 1148-D-6537 OPEN 600 DISS CONN AT PL,1148-6546 AT 9;00 AN RELEASED BY CREW 078S09/CREW ON SITE/HOLD ORDER ISSUED @1054/VEM/JOB GOING WELL/FETR 1745/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1712/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/KEP IDC DUP TO OPEN SWITCH XXXX
12190 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2013-08-12 21:31 | 2013-08-13 00:15 | 3 | 164 | 4657631 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MAYBE BAD CUTOUT RISER BURNT OFF CUTOUT NO TRUCK TO POLE RELEASED BY CREW 078S08------TIME ON 00:15 XMER OUT ON POLE 45A4-1712 COD 3 ****CHANGE ISO POLE ***** VER/SEF
12191 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-11-25 17:08 | 2021-11-25 18:30 | 6 | 82 | 4124501 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hotline clamp failed on pole 397-20. Repaired and power restored at 18:30.
12192 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-11-03 18:00 | 2018-11-03 18:41 | 12 | 41 | 4360791 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke line fuse cutout ,,,20t on 206-120,,complete Cod 12 L3/HFP
12193 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-08-18 17:49 | 2008-08-18 18:30 | 12 | 41 | 53003-1 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3116702// 6T TRANS. FUSE BROKE INSTALLED 8T 37.5 TRANS.//COD 12// VER/DBM IDC XXXX
12194 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-06-04 20:04 | 2011-06-05 00:10 | 2 | 246 | 4232131 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA 480V XFMER ON POLE 771-472/// CREW ENROUTE///BR///CHANGED OUT BAD 50 KVA ON BANK POLE 771-472///BACK ON AT 12:10///CPMPLETE///BR VER/TOM L3/TOM IDC XXXX
12195 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-03-12 15:46 | 2008-03-12 18:30 | 3 | 164 | 56625-1 | 492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701// BROKEN LINE CUTOUT ON POLE 236-33 ( 12 T ) NEEDS LINE CREW. RELEASED BY CREW 078S01//POLE 236-30 NEEDS REPLACED//SENT TO ENG//VER/CRB IDC XXXX
12196 | Hazard | 3303901 | LESLIE | HYDEN | 2014-05-20 08:19 | 2014-05-20 16:30 | 1 | 491 | 4725491 | 491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER COD-1 ISO TF 37830242000131 VER/HFP L3/HFP
12197 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2010-11-26 03:25 | 2010-11-26 11:36 | 1 | 491 | 59709-1 | 491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HARVEY MARTIN ENROUTE TO ASSIST GREG.NEED 25KVA 7.2KV 120/240, LINE TRUCK , 3 MEN... NO TRUCK ACCESS RELEASED BY CREW 074S03//WR#37888713// TOOK TAP OFF AT 10:54 ALL BACK ON AT 11:36 D SAMMONS//VER/CRB IDC XXXX
12198 | Pikeville | 3120102 | STANVILLE | TRAM | 2018-12-13 01:34 | 2018-12-13 09:45 | 1 | 491 | 4560371 | 491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | secondary burned in the clear will need bucket tree crew& 1 lineman . customer ok with waiting till morning. Released by crew 074S04, CREW AUSTIN HALL//all repairs made power restored//COD 1//
12199 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-12-27 10:57 | 2016-12-27 16:35 | 2 | 338 | 4242291 | 491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 37830458000014 BAD CUTOUT ON POLE 37830458000180 NEED LINE CREW TO CHANGE CUTOUT === PUT LINE FUSE IN AT 13:30 1 CUST STILL OUT === CHANGED CUTOUT POWER ON AT 16:35 == VER/CRB
12200 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-02-20 10:30 | 2015-02-20 18:41 | 1 | 491 | 4054701 | 491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | AT POLE 174C2-535 WILL NEED 25 KVA XFMR.(34.5 KV),,XCO,T-BRKT,HLC.,& D.E. INSULATOR (19.9),OIL SPILL CLEANUP KIT,, TRUCK ACCESS-LINE CREW/MAT BUCKET (WILL HAVE TO OPEN LINE FUSE TO REPLACE D.E. INSULATOR AT POLE 174C-295.RGP. //LINE FUSE OPEN FROM 1745 TO 1814AT POLE 174C2-535 SEE H40547 FOR LINE FUSE OUTAGE // VER/HFP L3/HFP
12201 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2017-07-10 17:10 | 2017-07-10 21:15 | 2 | 245 | 4102901 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 89-9 BAD 15KVA TRANS NEED 25KVA LARGE BUCKET TO POLE MAYBE FRIST BRICK HOUSE ON RIGHT PAST SARKS RD. TRANS ON LEFT ON HILL. RELEASED BY CREW 078S08,,CREW ON SITE,,XFMR UPGRADED,,ALL POWER RESTORED..ONLY 2 CUSTOMERS ON THIS XFMR/ ISO 38830089000009/ COD 2***PER COMMENTS/ VER/BOW
12202 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-01-22 09:15 | 2016-01-22 13:20 | 2 | 245 | 4640591 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE 19.9 KVA CAN USE TRUCK POLE 1130-130 CREW ON WAY REPAIRED 13:20 TOM MCCOWN/ ISO 38821130000130/ COD 2/ VER/BOW
12203 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2014-12-04 09:05 | 2014-12-04 10:43 | 5 | 98 | 4832181 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKEN CROSSARM WIRE LAYING ON POLE#903-29 OPENED LINE FUSE 903-2 AT 0905 TO MAKE REPAIRS CLOSED BACK IN AT 1043 VER/KEP
12204 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-07-29 18:22 | 2018-07-29 20:00 | 5 | 98 | 4869171 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse blown on transformer, power restored at 20:00 cod 5 iso 38830020C24568
12205 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-04-01 09:24 | 2010-04-01 10:34 | 7 | 70 | 56805-1 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE HANGING DOWN, FUSE BROKE COD-7 VER/HFP L3/HFP IDC XXXX
12206 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-01-07 01:15 | 2017-01-07 05:20 | 2 | 245 | 4274651 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BD XFMR TRUCK TO POLE BRING 25KVA AND NEW RISERS. CUTOUT AND LA TRUCK TO POLE.. SEND TO BLR RELEASED BY CREW 078H06 VER/KEP L3/HFP XXXHFP
12207 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-06-19 18:51 | 2011-06-19 20:01 | 7 | 70 | 4345871 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOOKS LIKE FUSE ON 38830069C45529 IS OUT--REPLACED BAD CUTOUT COD-7 ISO LF 38830069C45529 VER/HFP L3/HFP
12208 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2020-11-12 03:40 | 2020-11-12 11:50 | 1 | 490 | 4667371 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held for daylight per KPCo late night callout guidelines. need 15 kva xfmr. & cutout. no truck .Have talked with Myles Robinette & gave him material list. Released by crew 074S04 Replaced 15kva xfmr and cutout 11:50
12209 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-03-31 10:05 | 2022-03-31 14:10 | 2 | 245 | 4700991 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cut out on pole 1108-465. Can get big bucket to pole. Will need two (2) 19.9 cut outs. changed cutouts all power restored @ 14:10 p.hicks
12210 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-05-12 10:40 | 2014-05-12 11:50 | 7 | 70 | 4687871 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICER OPENED FUSE TO SAFELY RELACE A BROKEN INSULATOR OPENED FUSE ON 37830272C31664 AT 10:40, CLOSED AT 11:50 VER/KEP
12211 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-09-06 00:45 | 2022-09-06 08:55 | 1 | 490 | 4843501 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke. repairs made
12212 | Cannonsburg | 3000104 | ASHLAND | 25-2-3 | 2019-12-09 19:32 | 2019-12-09 21:10 | 5 | 98 | 4139451 | 490 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | time off 19:32 back on at 21:10//cod 5
12213 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2019-05-30 11:50 | 2019-05-30 20:00 | 1 | 490 | 4386741 | 490 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | splice gone bad in service drop on side of hill..be making reppairs..had a bad serve in. changed out and customers has good voltage.. complete rn
12214 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-06-06 12:44 | 2011-06-06 13:33 | 10 | 49 | 4241171 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 10// VER/DBM IDC XXXX
12215 | Hazard | 3303902 | LESLIE | WOOTON | 2010-02-03 06:50 | 2010-02-03 10:55 | 2 | 245 | 62488-1 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//VER/CRB IDC XXXX
12216 | Pikeville | 3401001 | ELWOOD | DORTON | 2012-09-25 15:47 | 2012-09-25 17:25 | 5 | 98 | 4086671 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT HAS BROKEN INTO. I AM GOING TO REPLACE CUTOUT. I AM GOING TO OPEN UP A LINE FUSE ON POLE 287-105 SERVING 1 MORE CUSTOMER, LONG ENOUGH TO CHANGE CUTOUT.//MADE MDC COD 5 ///VER/CRB L/3 CRB IDC XXXX
12217 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-05-30 18:00 | 2015-05-30 19:10 | 7 | 70 | 4485941 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACE 2/3 SD BECAUSE OPEN NEUT. XFMER OFF @ 18:00, ON @ 19:10// VER/ ADH L3/DKGC TOF1638
12218 | Pikeville | 3408101 | SALISBURY | PRINTER | 2011-02-12 08:45 | 2011-02-12 12:50 | 2 | 245 | 56348-1 | 490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR ON POLE 1123-188//CREW REQUIRED//MANUAL POLE//CREW ENROUTE//XFMR CHANGED OUT//RESTORED AT 12:50//COMPLETE//EM VER/KEP IDC XXXX
12219 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-12-25 14:37 | 2016-12-25 17:20 | 3 | 163 | 4236751 | 489 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TRIED TO CALL CUSTOMER NO ANSWER////BAD PINTOP 19.9 INSULATOR ON POLE 144-07.REPLACED AND RESTORED.../ ISO 37830144A30519/ COD 3/ VER/BOW
12220 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2010-04-29 18:31 | 2010-04-29 21:14 | 3 | 163 | 52903-1 | 489 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN SERVICE NEUTRAL////VER/CRB IDC XXXX
12221 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2021-09-17 12:59 | 2021-09-17 15:42 | 3 | 163 | 4251801 | 489 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Broke secondary neutral, repaired. Power restored.
12222 | Hazard | 3309003 | JEFF | VIPER | 2022-09-28 08:24 | 2022-09-28 11:07 | 3 | 163 | 4932031 | 489 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | No trapped victim/ service line on fire, CAW. Service wire burnt up at weatherhead, repaired. Power restored.
12223 | Hazard | 3303902 | LESLIE | WOOTON | 2011-05-02 09:12 | 2011-05-02 17:21 | 1 | 489 | 53427-1 | 489 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39780639 // BAD 10 KVA 7.2 KV WILL NEED A PICKUP TO GET TO THIS RELEASED BY CREW 077S01 REPLACED TRANSFORMER AND RESTORED POWER AT 1721 JKC COD- 1 ISO TF 37830485000076 VER/HFP L3/HFP IDC XXXX
12224 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-02-11 14:17 | 2022-02-11 17:00 | 3 | 163 | 4470871 | 489 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 19.9 cutout manual pole need cutout and crew Released by crew 077S05
12225 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-04-14 02:51 | 2015-04-14 11:00 | 1 | 489 | 4314581 | 489 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER LATE NIGHT CALL OUT, WILL LOOK AT IN A.M.BAD CUTOUT IN BAD LOCATION.NO TRUCK ACCESS.CHANGING// VER/ ADH
12226 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2021-08-28 01:28 | 2021-08-28 09:36 | 1 | 488 | 4164261 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Power restored at 9:36
12227 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-05 11:52 | 2008-06-05 20:00 | 1 | 488 | 58192-1 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3008702//BAD UNDERGROUND SEND THIS TO DAN.//CANNOT GO BACK WITH A POWER TEMP/ RELEASED BY CREW 078S01 VER/ARN IDC XXXX
12228 | Hazard | 3303902 | LESLIE | WOOTON | 2011-02-22 07:48 | 2011-02-22 09:50 | 4 | 122 | 60047-1 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 413-82 HILLSIDE // COD 4// VER/DBM IDC XXXX
12229 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2008-03-02 07:41 | 2008-03-02 11:45 | 2 | 244 | 51861-1 | 488 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400302 // SPAN OF 2/3 SECONDARY SERVING 2 CUSTOMERS HAS BURNED INTO AT A SPLICE IN MID SPAN. I CALLED DAVE FOR SOME HELP. WE WILL CHANGE SECONDARY TO 1/0. WE CHANGED SECONDARY CONDUCTOR TO 1/0. IDC CNT3 XXXX
12230 | Pikeville | 3403001 | PIKEVILLE | CITY | 2021-02-06 08:08 | 2021-02-06 12:12 | 2 | 244 | 4941291 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke @ 37830024B40745. Will be replacing. Restored @ 12:12
12231 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-02-28 09:56 | 2017-02-28 14:00 | 2 | 244 | 4427791 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITER HAS GONE BAD WILL NEED BIG BUCKET TO REPLACE VER/CRB
12232 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2014-04-21 09:15 | 2014-04-21 11:17 | 4 | 122 | 4620341 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEND TO BREWER - WILL CHECK TRANSFORMER CONNECTIONS// OPENED TRANSFORMER AT 09:15CREW REQUIRED --TRUCK TO POLE --BAD 25 KVA CSP TRANSFORMER NEED NEW CUTOUT INSTALLED--WASTE WATER PLANT ON RIVER ROAD RELEASED BY CREW 078S07/CREW ON SITE/FETR1300/VEM/XFMR REPLACED POWER RESTORED TO ALL CUST 1117/PLEASE CLOSE TICKET/THANKS/VEM//COD 4// VER/DBM
12233 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2008-01-02 23:22 | 2008-01-03 07:30 | 1 | 488 | 53033-1 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 2150501///ON SITE, XFORMER FUSE BLOWN, , REFUSING IT, XFORMER IS BAD, CALLED RANDALL MARCUM AND HE REPORTS WILL CHANGE ON NORMAL WORK, ALSO GETTING TECH TO CHECK LOAD. RELEASED BY CREW 080S01 /CUST DOESN`T USE AN AGREED TO WAIT TIL MORNING/BEING WORK UNDER AN IO////VER/CRB IDCC MCCNI XXXX
12234 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-11-20 09:13 | 2011-11-20 11:15 | 4 | 122 | 4094221 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | # 4 ALUM SERV DROP BURNED INTO /// VER/CRB IDC XXXX
12235 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-09-10 12:16 | 2012-09-10 16:20 | 2 | 244 | 4035671 | 488 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER & ON LASHED CABLE RELEASED BY CREW 077S04 COD-2 ISO TF 37830248A00080 VER/HFP L3/HFP IDC XXXX
12236 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2018-06-17 16:26 | 2018-06-17 20:30 | 2 | 244 | 4611121 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 KVA transformer. Additional crew enroute to replace. Restored @ 20:30. sh
12237 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-01-30 13:13 | 2017-01-30 15:15 | 4 | 122 | 4342321 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNED APART AT TRANSFORMER POLE . REPLACED HOT LINE CLAMP AND STIRRUP , ALL WORK COMPLETE / GXJ/ ISO 38831077A00221/ COD 4/ VER/BOW L3/HFP XXXHFP
12238 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-08-06 20:31 | 2020-08-07 00:35 | 2 | 244 | 4296301 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 15 trucks ok Released by crew 078S03 complted TL
12239 | Hazard | 3309302 | VICCO | JEFF | 2016-03-12 14:47 | 2016-03-12 18:51 | 2 | 244 | 4839241 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER MANUAL NEED 4 MEN,25KV 72 // SMITH, RICE, STRONG & EMBERTON // COD-2 ISO TF 37830322B10338 VER/HFP L3/HFP
12240 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-02-13 18:41 | 2020-02-13 22:45 | 2 | 244 | 4404341 | 488 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva 19.9 xfm single bushing... will need one man with big bucket to make repairs.../ ISO 37830189B00070/ COD 2
12241 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-03-26 02:00 | 2011-03-26 10:08 | 1 | 488 | 59410-1 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CUST IS OK WITH BEING OUT. CREW REQUIRED NEED 25KVA TRANS NEW CUTOUT AND ARRESTER. INSTALL 2/3 DROP THIS WILL BE HAND JOB CAN USE SMALL TRUCK TO WINCH. CUST WILL HAVE CARS MOVED. CUST IS ALSO GOING TO DO UPGRADE AND GET INSPECTED. VOLTAGE CHECKED 168 PHASE TO GROUND ON ONE SIDE 88VOLTS TO GROUND ON THE OTHER SIDE CHANGED 15 TO 25 KVA COD-1 ISO TF 37830092000165 VER/HFP L3/HFP IDC CHANGED OFF TIME FROM 0012 CUSTOMER HAD UPGRADED EQUIPMENT XXXX
12242 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-02-14 02:27 | 2019-02-14 10:35 | 1 | 488 | 4792761 | 488 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | One customer has part power. neutral & one ht leg broke. Service drop is a midspan drop. Linecrew required with service bucket& moe pads to get into ally. Released by crew 078S11 L3/HFP
12243 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-06-20 14:26 | 2014-06-20 18:30 | 2 | 244 | 4123251 | 488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFORMER , NEED LINE CREW TRUCKS TO POLE. RELEASED BY CREW 078S01 VER/CRB
12244 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-08-21 14:08 | 2018-08-21 22:15 | 1 | 487 | 4981821 | 487 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout complete L3/HFP
12245 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2019-07-15 18:34 | 2019-07-15 21:15 | 5 | 161 | 4713021 | 487 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | looks like 1/0 hot conductor and neutral burnt into at sec pole 187-d-251. had transformer on pole 187-d-167 from 20:20 to 21:15 look like conductor got hot at sevend burnt 1 hot conductor into and neutral.
12246 | Paintsville | 3409302 | KENWOOD | AUXIER | 2011-08-02 16:31 | 2011-08-02 17:25 | 9 | 54 | 4656471 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLINE CLAMP BURNT OFF. REPAIRED AND RESTORED @ 17:25. SH//COD 9//ISO// VER/DBM IDC XXXX
12247 | Pikeville | 3407101 | TOPMOST | DEMA | 2020-07-28 02:44 | 2020-07-28 10:50 | 1 | 486 | 4241751 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout Guidelines./ called customer no reading on meter--need 7.2 kv --25 kv need to replace cutout and arrester Released by crew 074M02..replaced transformer and cutout
12248 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-11-27 18:32 | 2022-11-28 02:38 | 1 | 486 | 4192991 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva, 7200 by squirt boom. primery bushing is loose Released by crew 078S12 Repairs made, ticket complete
12249 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-02-15 04:33 | 2022-02-15 07:15 | 3 | 162 | 4482581 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #6 copper secondary burned loose from the xfmr..opened xfmr at 630 back on at 715. re squeezed 3 services directly to the xfmr riser.
12250 | South Williamson | 3411401 | DEWEY | INEZ | 2020-08-23 23:51 | 2020-08-24 01:12 | 6 | 81 | 4362411 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 770-264//broke cutout on pole 770-130//replaced cutout//restored at 1:12//complete//em //cod 6
12251 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2018-08-27 17:53 | 2018-08-27 20:35 | 3 | 162 | 4005631 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200-25 kva, trk to pole Released by crew 078S07/ xfmer on 44-5194 replaced and power restored @ 2035/ please close ticket/ MLH
12252 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-01-25 22:17 | 2010-01-26 02:20 | 2 | 243 | 59847-1 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ABOUT 2-3 FOOT OF POLE BURNT OFF DUE TO BAD CUTOUT. I HAVE HOT LINE CLAMP OFF LINE AT POLE 180-63.ABOUT 2-3 FOOT OF POLE BURNT OFF DUE TO BAD CUTOUT. I HAVE HOT LINE CLAMP OFF LINE AT POLE 180-63. WE HAVE REPAIRS MADE EVERYTHING OK. //VER/GAH IDCC PN76, CNT1 XXXX
12253 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-08-31 18:00 | 2013-08-31 22:03 | 2 | 243 | 4807241 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERV CHECKING VOLTAGE,BAD 50KVA NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05/CREW ON SITE/FER2245/VEM/BOBBY TACKETT OPENED XFMR AROUND 1800 DUE TO HIGH VOLTAGE AT THE RISERS/CHANGED XFMR AND RESTORED POWER AT 2203/ONLY TWO CUST ON THIS XFMR/PLEASE CLOSE TICKET/THANKS/VEM PER VERNON ONLY 2 CUST // ISO TF 38830206C02359 VER/HFP L3/HFP IDC XXXX
12254 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-06-20 15:27 | 2020-06-20 19:30 | 2 | 243 | 4051451 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | tried transformer fused, it kicked back out. bad transformer. crew required need a 7200 25kva transformer and cutout Released by crew 074S09//power restored at19:30
12255 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-01-04 11:39 | 2010-01-04 13:00 | 6 | 81 | 59923-1 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LOOKED LINE OVER CLEARED ONE ARRESTOR MAY BE THE PROBLEM. DONT KNOW FOR SURE. RESTORED AT 1300 COD-6 VER/KEP L3/KEP IDC XXXX
12256 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-01-26 17:30 | 2016-01-26 20:12 | 3 | 162 | 4652221 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-7505 OPENED LINE FUSE 17:30 POLE 45-7302 BURNT OFF CALLED CREW RELEASED BY CREW 078S08,,,CREW ON SITE,,REPAIRS MADE,,ALL POWER RESTORED//COD 3// VER/DBM
12257 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-05-22 09:01 | 2021-05-22 11:25 | 4 | 144 | 4609671 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse stayed on pole 47-B-43 but the customer at the end of the line still has no power// bad XCO on pole 47-B-356, repaired and restored line fuse in @1055 and xfmr on 47-b-356 restored @1125
12258 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-06-23 21:46 | 2008-06-23 22:40 | 9 | 54 | 53282-1 | 486 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | B PHASE FUSE OUT ON POLE 38831083C20103 // RELATED TO ORDER 53258-1 VER/HFP IDC XXXX
12259 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-11-22 15:18 | 2015-11-22 19:21 | 2 | 243 | 4478501 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL BROKE REPLACED XFMR FUSE ALL PWR RESTORED @ 19:21/ ISO 38830597000070/ COD 2/ VER/BOW
12260 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-01-04 09:15 | 2012-01-04 10:36 | 6 | 81 | 4232001 | 486 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFMR. SEC. RISER HAS BURNED IN TWO // WILL REPAIR// REPLACED SEC. RISER // POWER IS RESTORED VER/KEP IDC XXXX
12261 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-04-01 19:59 | 2010-04-01 21:20 | 6 | 81 | 57245-1 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR# 34501981 / HOT TAP FELL OFF//COD 6// VER/DBM IDC XXXX
12262 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2018-06-25 17:57 | 2018-06-25 22:00 | 2 | 243 | 4665731 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout has to be changed Released by crew 077S12 power restored at 22:00
12263 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-07-31 08:13 | 2019-07-31 10:55 | 3 | 162 | 4815301 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Line fuse blown on 986-68 will patrol/// Riser also burnt into @ line fuse/// repairs made closed line fuse in @ 10:55 and restored service
12264 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-08-31 13:22 | 2020-08-31 13:28 | 81 | 6 | 4406971 | 486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | customer claims they have high voltage/ Bad regulator C phase on pole # 490/251/ opened reclosers 37830490A30313 @ 1322 to bypass reg/ closed recloser 37830490A30313 @ 1328/ 81 customers/ DOL 1049964
12265 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-02-23 15:00 | 2014-02-23 23:05 | 1 | 485 | 4428371 | 485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT. BAD 25KVA XFMR NEED 1 MAN & BIG BUCKET RELEASED BY CREW 075H04.ON WAY TO GET TRANSFORMER NOW.P.HICKS.LOADED AND HEADED TO JOB.XFMER CHAGED OUT, ALL POWER RESTORED @ 23:05 HRS.P.HICKS //VER/GAH
12266 | Paintsville | 3401802 | INDEX | HOSPITAL | 2016-11-01 18:03 | 2016-11-01 19:40 | 5 | 97 | 4068871 | 485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT,,,CHANGING/ ISO 38830654D00103/ COD 5/ VER/BOW
12267 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2010-06-01 14:29 | 2010-06-01 22:34 | 1 | 485 | 54892-1 | 485 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLEC K BROWN TO HELP--35356918--SEND TICKET TO L MCCARTY--BAD 10KVA 12KV TRANSFORMER RELEASED BY CREW 078S07/ THIS IS A CARRY IN XFR WAITING ON MULLINS TO RUN YARDDOG/ WIL CHG XFR CUTOUT AND L/A ON THIS POLE AND ALSO CHG CRACKED CUTOUT ON NEXT POLE BACK/ HAVE CUSTOMER BACK ON POLE 140- 559 @ 22:34 NOW CHANGING CUTOUT ON POLE 140-564//COD 1// VER/DBM IDC XXXX
12268 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2019-04-14 15:25 | 2019-04-14 23:30 | 1 | 485 | 4094861 | 485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout and restored @ 23:30. sh
12269 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2020-11-16 15:59 | 2020-11-16 17:36 | 5 | 97 | 4696901 | 485 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced insulinks with squeezons
12270 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-06-26 08:41 | 2015-06-26 16:45 | 1 | 484 | 4661091 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN, PROBABLY FROM LIGHTENING. I AM GOING TO REFUSE TRANS. BAD TRANS. TIM HALL IS GOING TO SEND CREW AS SOON AS ONE GETS AVAILABLE. IT IS A 15 KVA { 19.9 } THAT IS ON POLE NOW. RELEASED BY CREW 074S01 VER/CRB
12271 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-04-24 21:03 | 2022-04-25 01:05 | 2 | 242 | 4795871 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | possible bad xfmr, tried to refuse and it came back out // crew required //25kva 19.9 //truck ok//..transformer and cutout replaced and restored @01:05. ticket complete
12272 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-08-17 18:07 | 2021-08-17 20:08 | 4 | 121 | 4089431 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cuyout broke on 147-476 will be making repairs///Repairs made restored @ 20:08
12273 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-11-15 09:18 | 2014-11-15 13:20 | 2 | 242 | 4729771 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 19.9 JEFF ON THE WAY FETR 1430 //BAD CAN ON POLE 37830293000029BAD 15 KVA 19.9 JEFF ON THE WAY FETR 1430---VOLTAGE OK VER/CRB
12274 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-04-27 15:58 | 2021-04-27 20:00 | 2 | 242 | 4485941 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva xfm on pole 38831098C00787// Crew required// Replaced xfmr and cutout// Restored @ 20:00//cod 2
12275 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-05-19 16:14 | 2013-05-19 20:16 | 2 | 242 | 4134011 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 423-13, THIS IS THE LINE FUSE CUTOUT THAT IS BROKE & IS VERY CLOSE TO BRACKET WILL HAVE TO OPEN RECLOSER ON POLE 423-278 TO ISOLATE CUTOUT. RELEASED BY CREW 077S11BAD CUTOUT ON POLE 423-13, THIS IS THE LINE FUSE CUTOUT THAT IS BROKE & IS VERY CLOSE TO BRACKET WILL HAVE TO OPEN RECLOSER ON POLE 423-278 TO ISOLATE CUTOUT. REPLACED CUTOUT RESTORED POWER AT 20:16//MADE ANOTHER TICKET IDC XXXX
12276 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-12-06 05:18 | 2015-12-06 09:20 | 2 | 242 | 4513101 | 484 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFMR RISER BURNED UP // WILL REPLACE // NEED 1 MAN // BIG BUCKET // LOOSE CONNETCION BURNED SEC. RISER IN TWO // REPLACED XFMR RISERS // POWER RESTORED @ 09:20// VER/ ADH
12277 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-03-07 10:11 | 2009-03-07 12:12 | 4 | 121 | 55923-1 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ;;BIG BUCKET ON THE WAY//VER/CRB IDCC CNT1, MCCDIS XXXX
12278 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2008-07-03 16:59 | 2008-07-03 19:00 | 4 | 121 | 61777-1 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3004301//RE-PLACED// COD 4// NO FETR PROVIDED // VER/TOM IDC XXXX
12279 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2016-07-28 16:21 | 2016-07-29 00:25 | 1 | 484 | 4701281 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA 7200--BAD TRAN--CREW REQ--DS072816 RELEASED BY CREW 078S01.. CREW ON SITE TO REPLACE XFMR FETR 22:30.. XFMR THAT WAS BAD WAS 240/480 VOLT WILL HAVE TO GO BACK TO SHOP TO GET ONE NEW ETR IS 00:30.. XFMR REPLACED AND RESTORED AT 00:25 VER/CRB
12280 | Pikeville | 3120102 | STANVILLE | TRAM | 2022-11-19 05:12 | 2022-11-19 09:14 | 2 | 242 | 4161081 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM fuse open on 1077-703// checking// bad 15kva XFM 7200
12281 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-12-10 09:12 | 2008-12-10 13:14 | 2 | 242 | 56103-1 | 484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404302// RELEASED BY CREW 080S01 REPLACED BAD CUTOUT, AND PUT OUT POLE FIRE.//VER/CRB IDCC CNT21, ESTIMATED TIME OFF XXXX
12282 | Whitesburg | 3312901 | JENKINS | KONA | 2015-03-10 11:27 | 2015-03-10 13:28 | 4 | 121 | 4176931 | 484 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I RESQUEEZED SERVICE TO XFMR LEAD/ ISO 37830404B00098/ COD 1
12283 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-11-15 02:31 | 2014-11-15 10:34 | 1 | 483 | 4729251 | 483 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL WORK DURING NORMAL WORK HOURS 4/3 SERVICE BURNT DOWN REPLACED WITH 2/3 VER/SEF L3/HFP HFPC CNT11
12284 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2012-05-23 21:41 | 2012-05-23 22:50 | 7 | 69 | 4825161 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE TRANSFORMER FUSE WAS BROKEN. CC = 7 VER/SDB IDC XXXX
12285 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-12-03 20:49 | 2011-12-03 23:30 | 3 | 161 | 4139091 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PRC CREW REQUIRED-- NO TRUCKS -37 1/2 CSP TRANSFORMER--HOT TAP LEAD BURNT OFF AT PRIMARY BUSHING-HANGING HOT WAS NOT ABLE TO CLEAR--BUSHING BURNT BAD ON TANSFORMER, NOT SURE IF REPAIRABLE, MIGHT NEED TO CHANGE TRANSFORMER RELEASED BY CREW 078S07 2302 - OPENED LINE FUSE AT POLE 20-1069 FOR SAFETY CLEARANCE - 2330 - RESTORED TO SERVICE //VER/GAH IDC XXXX
12286 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-07-08 06:52 | 2022-07-08 14:55 | 1 | 483 | 4426951 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer/meter blankTrans Cutout broke at 237-C-10,Will be making repairs..Trans Cutout broke at 237-C-10,Will be making repairs..Restored at 14:55..
12287 | Paintsville | 3410602 | E.PRESTON | LANCER | 2018-06-12 15:39 | 2018-06-12 18:20 | 3 | 161 | 4592671 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link appears to have melted out on xfmr. Restored @ 18:20. sh
12288 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-04-03 08:07 | 2015-04-03 16:10 | 1 | 483 | 4262641 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT HAS BROKEN ON POLE 144-296. WE ARE GOING TO CHANGE CUTOUT. WE CHANGED UTOUT./ ISO 37830144B00296/ COD 1 L3/DKGXXX
12289 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-04-09 20:49 | 2015-04-10 04:52 | 1 | 483 | 4300491 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 188-B-414/NEED BIG BUCKET CREW TO FIX/RELEASED BY CREW 078S11 RELEASED BY CREW 078S11 VER/KEP
12290 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-07-09 08:37 | 2022-07-09 16:40 | 1 | 483 | 4441181 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Xfm fuse blown.//Bad current limiting fuse on pole 140d-14.//Can reach with big bucket Released by crew 074S11//restored @16:40
12291 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-02-14 21:35 | 2020-02-15 00:16 | 3 | 161 | 4407201 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3201001/gaj/2144/all out disp 3542 T FieldssSERV DROP BURNED INTO,WILL MAKE REPAIRSsSERV DROP BURNED INTO,WILL MAKE REPAIRS//////////INSULATION FAILURE@A SPLICE,POSSIBLY DAMAGES HERE,NEUTRAL BURNED INTO.MADE NECESSARY REPAIRS&RESTORED 0016
12292 | Whitesburg | 3314401 | MAYKING | ERMINE | 2021-01-11 06:25 | 2021-01-11 09:06 | 3 | 161 | 4860401 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection was burnt up at weatherhead. redid connection.. voltage checks good now
12293 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-11-25 06:03 | 2017-11-25 07:12 | 7 | 69 | 4600751 | 483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned up , I changed it out
12294 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-01-13 19:44 | 2021-01-13 23:45 | 2 | 241 | 4867341 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 10KVA, 7200 on pole 293-7. Not sure if a bucket will reach this pole. Released by crew 077H20/ restored @ 2345
12295 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-03-25 20:29 | 2021-03-26 00:30 | 2 | 241 | 4375631 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout is broke will change// Replaced cutout and restored @ 00:30
12296 | Paintsville | 3401101 | FALCON | FALC-OILS | 2016-01-28 09:29 | 2016-01-28 13:30 | 2 | 241 | 4655901 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE LINK APPEARS TO HAVE BROKEN. RESTORED @ 13:30. SH/ VER/AWD
12297 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2021-06-18 11:38 | 2021-06-18 15:25 | 4 | 227 | 4766991 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout manual need crew to change out Released by crew 077S12 // repaired and restored @ 1525
12298 | Pikeville | 3408101 | SALISBURY | PRINTER | 2020-09-06 12:37 | 2020-09-06 16:38 | 2 | 241 | 4437511 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM cutout door burnt into. Replaced & estored @ 16:38
12299 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2018-07-25 13:19 | 2018-07-25 17:20 | 2 | 241 | 4854761 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Released by crew 076S01//38830954B20291 open 1635-1639//Released by crew 076S01 . replaced 25 kva xfmr with 50 kva xfmr , ALL WORK COMPLETE / GXJ
12300 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2018-07-25 16:48 | 2018-07-26 00:50 | 1 | 482 | 4856521 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 KVA 7200 trans on 1077D295 trk app.need one man and mat handler.replaced trans restored power at 00:50//cod 1
12301 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-05-27 10:32 | 2019-05-27 14:33 | 2 | 241 | 4349041 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED, BROKE 19.9 CUTOUT ON FIBERGLASS BRACKET AT POLE 140-41, CAN USE TRUCK. Released by crew 074E02 Changed c/o, power restored @1433.
12302 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-06-12 13:49 | 2009-06-12 17:50 | 2 | 241 | 56824-1 | 482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL IS BROKEN TEN TO TWELVE FEET FROM THE POLE. WE NEED ADDITIONAL HELP TO LOWER THIS TO THE GROUND AND SPLICE IT OUT #2 SERVICE. RELEASED BY CREW 074S02 NEUTRAL CONDUCTOR OF SERVICE PULLED OUT OF A COMPRESSION TENSION SPLICE CUSTOMER REPORTED DAMAGES . REPAIRED ON AT 17:50 D SAMMONS//VER/CRB
12303 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-01-22 11:21 | 2015-01-22 15:32 | 6 | 251 | 4950721 | 481 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | NO POWER OFF AT THIS TIME FOUND POLE # 37830077000086 BURNED OFF GOT CREW COMMING AND GOING TO OPEN LINE FUSE AT 37830077000037 TO INSTALL SOLID BLADE AT POLE 37830077000133 AND 1 CUST WILL BE OFF UNTIL POLE REPLACED//OPENED L/F @ 1121// CLOSED @ 1207 UPTO POLE 77-133// 37830077000086 BURNED OFF GOT CREW COMMING AND GOING TO OPEN LINE FUSE AT 37 TO INSTALL SOLID BLADE AT POLE 77-133 AND 1 CUST WILL BE OFF UNTIL POLE REPLACED //MADE MD ON SOLID BLADE//PWR REST 1532 VER/CRB L3/HFP XXX AJB
12304 | Hazard | 3302703 | HAZARD | HAZARD | 2016-04-07 14:55 | 2016-04-07 16:15 | 6 | 80 | 4065511 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 144/ 284 AT METERBASE, CHECKED @ DIFFERENT TRANSFORMER ON SAME PHASE AND GOOD VOLTAGE. MANUAL 25 KVA TRANSFORMER. NEED 4 MAN LINE CREW, JIM MULLINS IS AWARE OF THIS/ /POSSIBLE CLAIM SENT TO PEGGY WYSONG/ OPENED LINE AT 1455 RESTORED AT 1615//OPENED FUSE IN ORDER TO REPLACE TRANSFORMER SAFELY//COD 4/ ISO 37830272D20736/ COD 6/ VER/BOW
12305 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2019-10-13 01:53 | 2019-10-13 09:53 | 1 | 480 | 4135601 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replacing bad cutout. all repaires made. apr at 0953 close ticket. dwest
12306 | Hazard | 3310502 | HADDIX | CANOE | 2009-10-07 12:15 | 2009-10-07 14:55 | 3 | 160 | 59403-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUST HAS PART POWER GOING TO OPEN TRANSFORMER AND LOOK FOR THE TROUBLE LEADS ON TRANSFORMER BAD, CHANGE THEM OUT//VER/CRB IDC XXXX
12307 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2015-10-30 09:17 | 2015-10-30 09:47 | 16 | 30 | H4395831 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | KY DDC NOTIFIED APCO DDC// ROANOKE TO DISPATCH - //TOM MAY BE ASSOCIATED WITH APCO OUTAGE/ RISER HAS BURNED OUT OF B PHASE (18 CUST) HOT TAP. WILL NEED TO OPEN A AND C PHASE (82 CUST) TO MAKE REPAIRS.I OPENED ALL THREE PHASES ON POLE 38820917C00383 AT 09:17 (A&C 82 CUST) B WAS ALREADY OUT./ ALL CUST ON 0947/ 80T ON 917-9014 MD DONE/ ISO 38820917C09014/ COD 99/ VER/BOW //SEE ALSO 4395831 - PER B.O. ALL CALLS `A` PHASE ON LY 2 ON `B` - CHANGING CUST COUNT TO 16 L3/HFP HFPC CNT82 TOF0428
12308 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2014-09-05 02:20 | 2014-09-05 03:20 | 8 | 60 | 4466551 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN. REPLACING. REPLACED AND RESTORED @ 3:20. SH VER/TOM L3/TOM
12309 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-06-25 14:30 | 2016-06-25 16:30 | 4 | 120 | 4473641 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POWER RESTORED AT 16:30 VER/CRB
12310 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-08-05 15:30 | 2013-08-05 17:30 | 4 | 120 | 4624441 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST HAS HIGH VOLTAGE DUE TO BAD 25KVA XFMER ON POLE 876-43///OPENED XFMER @ 15:30 DUE TO HIGH VOLTAGE ///CREW ENROUTE TO CHANGE XFMER///INSTALLED NEW 25 KVA///ALL CUST BACK ON @ 17:30///COMPLETE BR VER/CRB L/3 CRB
12311 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-04-23 19:00 | 2012-04-23 23:00 | 2 | 240 | 4700541 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | APPEARS SERVE END HAS BURNT OUT /// GOING TO REPLACE DROP /// WILL HAVE TO OPEN XFMR ON POLE 1057-98 /// POWER RESTORED @ 23:00 ////VER/CRB
12312 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-08-13 22:30 | 2017-08-14 02:30 | 2 | 240 | 4256541 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE--CRACKED C/O,METAL T BRACKET--GETTING C/O, FIBERGLASS T BRACKET AND ARRESTOR TO FACILITATE REPAIRS--OPEN TRAN AT APPROX 22:30--PLEASE FORWARD TO B. PARSONS FOR POLE REPAIRE/REPLACE IN AT 02:30//COD 2// VER/DBM
12313 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2017-06-24 15:55 | 2017-06-24 19:55 | 2 | 240 | 4040731 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD 2 136-51 REPLACING NOW//COD 2// VER/DBM
12314 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-06-08 16:25 | 2011-06-08 17:45 | 6 | 80 | 4270881 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPLACE 4/0 XFMER RISER DUE TO OVERLOAD. XFMER OFF 16:25.//DELETE 1ST STEP ACCIDENTLY RESTORED//REPLACE 4/0 XFMER RISER DUE TO OVERLOAD. XFMER OFF 16:25. RESTORED @ 17:45 M.PHELPS//VER/CRB IDC XXXX
12315 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-09-23 13:25 | 2014-09-23 13:41 | 30 | 16 | 4370041 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HOLD ORDER REQUIRED/CREW REQUIRED POLE 249-30 BROKEN AT TOP ISOLATED AT 249-31 ALSO ISOLATED RECLOSER POLE 273-44 TAGGED TO DDC NO TRUCKS/NEEDS SENT TO TECH TO HAVE POLE REPLACED 249-181 BACK IN AT 1921 HRS NOBODY OFF /LOG ENTRY 8-2-14 @1828/ OUTAGE ON 4322071 AJB TOF15:17 8/14 SEE 4322071 OUTAGE ON 8/2. PER CUST CALLS OUT ON 9/23.
12316 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-03-13 06:45 | 2008-03-13 10:45 | 2 | 240 | 56774-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401801- WILL DISPATCH A SERVCIER AT REG WORK TIME.//....BAD 25 KVA XFMR RELEASED BY CREW 076S01//TCM REPLACED X-FORMER//COD 2// VER/DBM IDC XXXX
12317 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-07-09 19:07 | 2009-07-09 23:07 | 2 | 240 | 51863-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK REQUEST # 30672198 // BAD XFORMER NEED 25KVA 7200. RELEASED BY CREW 078S01/XFMR CHG AND POWER RESTORED 2307/PLEASE CLOSE TICKET/THANKS/VEM VER/TOM L3/TOM IDCC PN33, CNT1 XXXX
12318 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-04-26 20:53 | 2019-04-26 23:33 | 3 | 160 | 4176731 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Gate burndt up on L/F @74-30, checking. Found no trouble on line, changed c/o and closed L/F back in @2333
12319 | Hazard | 3303902 | LESLIE | WOOTON | 2010-05-22 05:20 | 2010-05-22 08:00 | 3 | 160 | 66219-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND FAILED CUTOUT - WILL REPLACE VER/LDA IDC XXXX
12320 | Hazard | 3309302 | VICCO | JEFF | 2016-07-29 12:29 | 2016-07-29 13:17 | 10 | 48 | 4708411 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR === CHANGED === OPEN LINE AT 12:29 CLOSED AT 13:17 POWER OK//COD 10
12321 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-03-01 17:05 | 2009-03-01 17:45 | 12 | 40 | 52773-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3001201//RISERS MEALTING OUT OF TRANSFORMER--NEED 4/0 RISERS--CALLING CREW--SEND TO P TOLLIVER RELEASED BY CREW 078S07//CREW ON SITE PR TOLLIVER//OPENED XFORMER AT 1705 BACK ON AT 17:45 P TOLLIVER VER/KEP L3/KEP IDC XXXX
12322 | Cannonsburg | 3001401 | LOUISA | CITY | 2016-03-09 10:35 | 2016-03-09 11:23 | 10 | 48 | 4830001 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OPENING FUSE TO SAFELY REPLACE ROTTEN CROSSARM/APROX ONE HOUR OUTAGE/VEM/OPEN FUSE AT 1035/VEM/POWER RESTORED TO ALL CUST 1123/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830454A41559/ COD 10/ VER/BOW
12323 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-10-05 17:35 | 2013-10-05 19:35 | 4 | 120 | 4913341 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUTREPLACED BAD CUT-OUT POWER RESTORED VER/SEF L3/HFP IDC XXXX
12324 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2011-11-11 06:43 | 2011-11-11 08:03 | 6 | 80 | 4066961 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHANGE BAD 15 KV XFMR CUTOUT VER/KEP IDCC TOF617 XXXX
12325 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-06-17 21:15 | 2009-06-17 21:30 | 32 | 15 | H50907-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | XFMR POLE 809-319 IS BROKE AND LAYING ACCROSS STREET. OPENED PH C REC ON POLE 809-148 AT 21:15 TO ISOLATE, REMOVED HOT LINE CLAMP ON POLE 809-293 AND CLOSED REC BACK AT 21:30. CREW ENROUTE. CREW ONSITE - REPAIR UNDERWAY. REPAIRS COMPLETE. RESTORED AT 06:10. SH//VER/CRB IDCC DUP TO CUT LOSE XXXX
12326 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-04-11 19:30 | 2022-04-11 20:30 | 8 | 60 | 4750491 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 38830115C00208/probably need big bucket to reach/crew reqd. truck ok. Released by crew 078S04 crew arrived to make repairs. repairs made lf in @ 20:30 on pole 115-208 complete
12327 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-08-04 16:55 | 2017-08-04 18:55 | 4 | 120 | 4226901 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD BROKE CUTOUT ON POLE 37830205D00095 AND HAD LINE FUSE OUT ON POLE37830205D00502/ ISO 37830205D00502/ COD 4/ MAPS WRONG ANOTHER TAP OFF POLE 37830205D00009 FEEDING ONE TRANSFORMER/ SEND TO TECHNICIANS NEED FIELD CHECKED TO GET MAP CORRECTED MD DONE/ VER/BOW
12328 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2010-07-10 14:40 | 2010-07-10 18:40 | 2 | 240 | 64862-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | I REPLACED A RIDGE PIN AND 1301 INSULATOR ON POLE 148-154.//COD 2// VER/DBM IDC XXXX
12329 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-09-05 14:45 | 2012-09-05 16:45 | 4 | 120 | 4018121 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DUTY SUPERVISOR TRYING TO GET CREW TO FIX TRANSFORMER ,NEED SMALL MATERIAL BUCKET BACK YARD JOB ,AND 50 KVA TRANS, 7200 SINGLE BUSHING 120/240 HAVE PERMISSION TO GET IN YARD ON RIGHT OF HOUSE TALK TO CUST HE WILL SHOW YOU WHICH WAY TO GET TRUCK IN YARD RELEASED BY CREW 078S09/FETR 17:00//REPAIRS COMP. POWER REST.@ 16:15/ XFMER OFF @ 14:45 0N @ 16:15 /// JEH ( 4 CUST.) COD-4 ISO TF 39831124B22538 VER/HFP L3/HFP IDCC TOF1159, CNT1 XXXX
12330 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2020-04-06 13:32 | 2020-04-06 15:08 | 5 | 96 | 4564531 | 480 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | C phase line fuse blown on pole 449-152, 2 arresters blown on pole 449-653 & 2 blown on pole 449-1207, arresters are in the clear, restored power at 15:08..
12331 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-04-10 17:00 | 2011-04-10 19:00 | 4 | 120 | 54391-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T TRANSFORMER FUSE OUT DUE TO BAD CUTOUT WILL BE CHANGING. I HAVE CUTOUT CHANGED FUSED UP EVERYTHING OK //VER/GAH IDC XXXX
12332 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-04-27 10:44 | 2017-04-27 11:04 | 24 | 20 | 4686951 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT. OPENED RECLOSER AND TRANSFORMER TO SAFELY DIAGNOSE EQUIPMENT ISSUE.BAD CUTOUT RELEASED BY CREW 077S05 OPENED RECLOSER AND TRANSFORME ON POLE 5-30 AT 10-44 REPLACED CUTOUTS AND REASTORED POWER AT 11-04 RELEASED BY CREW 077H02 COD 24 37830005000030 VER/AWD L3/HFP XXXHFP AJB
12333 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-06-04 18:24 | 2009-06-04 19:12 | 10 | 48 | 61286-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409301// FUSE LINK BROKE. RE-FUSED XFMR. SH VER/KEP L3/KEP IDC XXXX
12334 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-06-14 19:40 | 2009-06-14 21:00 | 6 | 80 | 63686-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 115-246. THIS AT 10672 MEADESPRINGER RD. THIS POLE WILL NEED TO BE CHANGED OUT. SEND NOTE TO S. MARTIN. 12T LINE FUSE BLOWN ON POLE 115-183//COD 6// VER/DBM IDC XXXX
12335 | Hazard | 3309301 | VICCO | REDFOX | 2016-11-06 04:20 | 2016-11-06 07:00 | 3 | 160 | 4079231 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR RISER HAS COME OUT OF CUTOUT, MADE REPAIRS/// VER/DKM
12336 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2020-08-21 14:50 | 2020-08-21 15:30 | 12 | 40 | 4355091 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv door, replaced restored
12337 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-09-13 18:40 | 2020-09-13 20:00 | 6 | 80 | 4459331 | 480 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | secondary connection failed on 1012-C-410.2 customers out ,replaced connections,restored power at 20:00
12338 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-05-19 12:50 | 2010-05-19 13:20 | 16 | 30 | 64941-1 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO-ONE OUT. NEED WIRE TO SPLICE OUT SECONDARY..SEC IS ABOUT BURNED INTO.I WILL HAVE TO TANE XFMRS OFF FOR ABOUT AN HR OFF WHEN I DO JOB.BB RELEASED BY CREW 076S01//VER/CRB IDCC PN83, CNT24 XXXX
12339 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-10-08 11:10 | 2012-10-08 12:10 | 8 | 60 | 4123211 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | OPENED DIP FUSE TO ALLOW CREW TO MAKE REPAIRS ON ORDER 4122211 // COD-8 ISO DF 37830178A00362 VER/HFP L3/HFP IDC XXXX
12340 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-10-09 12:30 | 2019-10-09 14:30 | 4 | 120 | 4124081 | 480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse blown on 842-25//bad arrestor on 842-46//cleared up//restored at 14:30/complete//em L3/HFP
12341 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-04-19 14:41 | 2013-04-19 22:40 | 1 | 479 | 4026821 | 479 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED CREW NO TRUCK RELEASED BY CREW 078S07//PRT ON SITE REPLACING CUTOUT FETR 23:55//REPAIRS COMPLETE AT 22:40 CLOSE TKT PRT// ///VER/CRB L/3 CRB IDC XXXX
12342 | Pikeville | 3413401 | GARRETT | GARRETT | 2010-03-23 03:13 | 2010-03-23 11:12 | 1 | 479 | 53085-1 | 479 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34355878 // 37830017000008, LINE ISOLATED AND GROUNDED, FIRE OUT AND POLE SECURE, NEED TO LOWER TRANSFORMER, INSTALL CUTOUT AND ARRESTER, AND REATTACH PRIMARY ... CREW WILL BE ASSIGNED AT 7:30 AM / GXJ ... ALL WORK COMPLETE / GXJ//VER/CRB IDC CHANGED COUNT FROM 4 XXXX
12343 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-05-13 17:37 | 2015-05-13 21:36 | 2 | 239 | 4427681 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200, 25KVA, PLEASE CHANGE CO & ARRESTER TOO. TRK TO POLE RELEASED BY CREW 078S07 VER/CRB L3/DKGXXX
12344 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2018-01-10 14:13 | 2018-01-10 18:12 | 2 | 239 | 4727341 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer no reading on meter / CSP xfmr bad, will need to replace with 25kva 120/240 / 7.2 kv, crew enroute back1814
12345 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-04-17 09:16 | 2011-04-17 13:15 | 2 | 239 | 59680-1 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39599600 // XFMR FUSE OUT, BAD XFMR, CALLING FOR HELP COD-2 ISO TF 37830231B00018 VER/HFP L3/HFP IDC XXXX
12346 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2018-09-13 15:06 | 2018-09-13 23:04 | 1 | 478 | 4093241 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 75 kva, 240/480v. center can b phase. Released by crew 078S07
12347 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2016-04-30 19:21 | 2016-04-30 23:20 | 2 | 239 | 4145861 | 478 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 110V/30V BOTH HOT LEGS ON URD SERVICE PULLED INTO, WILL HAVE TO CUT CONDUIT AND RESQUEEZE AND POLE IS MANUAL, WILL BE MAKING REPAIRS. CUT OUT WENT BAD AFTER MAKING REPAIRS, WILL BE CHANGING. OPENED TRANS AT 2045, CHANGED CUTOUT AND PUT BACK IN AT 2320. VER/ARN
12348 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-10-22 10:59 | 2018-10-22 14:58 | 2 | 239 | 4308631 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr on pole 398-419, made repairs restored power at 14:58..
12349 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2016-06-15 13:17 | 2016-06-15 17:16 | 2 | 239 | 4350631 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 92-517 BAD 50 KVA NO TRUCKS TO POLE RELEASED BY CREW 078S08 RELEASED BY CREW 078Q04 VER/CRB
12350 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-07-28 18:06 | 2011-07-28 22:05 | 2 | 239 | 4635381 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMER FUSE BLOWN..50KVA , 19.9KV, 120/240V TRANSFORMER IS BAD.NEED ONE MAN AND TRANSFORMER..ONLY 2 CUST OUT..ALL POWER RESTORED @ 22:05.//VER/CRB IDC XXXX
12351 | Hazard | 3308001 | JACKSON | S.JACKSON | 2018-01-14 09:50 | 2018-01-14 13:49 | 2 | 239 | 4746281 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TRANSFORMER//GOING BACK WITH A 25 KVA//got bad transformer need 25 kva 7200
12352 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-11-14 14:36 | 2010-11-14 18:35 | 2 | 239 | 55566-1 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN ON POLE 241-C-120 DUE TO CUTOUT BROKE ON 241-C-20 WILL CHANGE CUTOUT AND REFUSE//COD 2// VER/DBM IDC XXXX
12353 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-06-12 08:51 | 2022-06-12 12:50 | 2 | 239 | 4059751 | 478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM fuse open on 1101-A-222// checking// bad 25KVA 19.9 XFM// need LCS and 2 men
12354 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-10-29 17:52 | 2013-10-29 18:45 | 9 | 53 | 4973881 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD L/A ON POLE 1098-31, HAVE CUT IN THE CLEAR, CAN USE TRUCK TO REPAIR,RESTORED POWER AT THIS LOC AT 1845 TO ALL CUST//AED ENTRY CREATED//COD 9// VER/DBM
12355 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-08-31 07:10 | 2016-08-31 08:03 | 9 | 53 | 4854541 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE INTO// VER/CRB
12356 | Hazard | 3310502 | HADDIX | CANOE | 2021-12-24 10:14 | 2021-12-24 12:53 | 3 | 159 | 4223591 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester at pole 120-65. cleared up and restored power at 12:53
12357 | Paintsville | 3410602 | E.PRESTON | LANCER | 2016-09-12 06:45 | 2016-09-12 14:42 | 1 | 477 | 4886551 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CHANGING FROM UG TO OVER HEAD SERVICE RELEASED BY CREW 076H06CHANGING FROM UG TO OVER HEAD SERVICE .REPAIRS MADE POWER IS BACK ON VER/CRB
12358 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2013-08-09 22:46 | 2013-08-10 01:25 | 3 | 159 | 4642161 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE AND BLEW LINE FUSE. REPLACED CUTOUT AND RESTORED @ 1:25. SH//COD 3// VER/DBM
12359 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-01-07 20:51 | 2009-01-07 23:30 | 3 | 159 | 53094-1 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | VER/HFP COD-3 WIRE CAME OUT OF TRANSFOMER ON HIGH SIDE AND HANGING FROM PRIMARY BY HOT LINE CLAMP. PUT WIRE BACK IN TOP OF HIGH SIDE MADE TRANSFORMER HOT EVERYTHING OK. ISO 37830163A00108 L3/HFP IDC XXXX
12360 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-06-12 15:43 | 2016-06-12 23:40 | 1 | 477 | 4340281 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PROBLEM WITH U/G SERVICE CREW TO WORK ASAP /// OPEN LEG IN UNDERGROUND CUST STILL HAS PARK POWER RUNNING A FAN INSIDE HOUSE. SEND TO B. TACKET LRM..OPEN LEG IN UNDERGROUND CUST STILL HAS PARK POWER RUNNING A FAN INSIDE HOUSE. SEND TO B. TACKET LRM..CREW ON SITE,,POWER TEMP INSTALLED,,PLEASE SEND NOTE TO RAYBURN,,ONLY ONE CUSTOMER WAS PART POWER VER/TOM L3/TOM
12361 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-09-28 15:50 | 2018-09-28 16:43 | 9 | 53 | 4178801 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | complted, opened line at 15:50, closed back in at 16:43 Released by crew 077S02//BUSTED INSULATER
12362 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-08-20 14:59 | 2009-08-20 17:38 | 3 | 159 | 56400-1 | 477 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP PART POWER, CONNECTION AT XFMR WAS BAD L3/HFP IDC XXXX
12363 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-05-28 15:51 | 2021-05-28 18:30 | 3 | 159 | 4638191 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on the arm on 20-a4-1530, Possible big bucket access at 313 buena vista. Spoke with customer. Crew required, send to Kevin Griffith Released by crew 078S02///Complete BR
12364 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2019-12-26 15:16 | 2019-12-26 17:55 | 3 | 159 | 4183661 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tap cutout broke on pole 139-44
12365 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-08-29 07:35 | 2011-08-29 15:32 | 1 | 477 | 4771131 | 477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE FUSE OPEN ON POLE 399-6, STATE DEPT. WORKING UNDER LINE . POLE 400-179 BROKE WIRE DOWN CROSSING HWY 15 RELEASED BY CREW 077S11//COD 1// VER/DBM IDC XXXX
12366 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-02-05 16:42 | 2011-02-05 17:50 | 7 | 68 | 54553-1 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT,6T FUSE HAD BROKEN AT THE WELD VER/KEP IDC XXXX
12367 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2011-12-21 09:06 | 2011-12-21 11:05 | 4 | 119 | 4192521 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE DUE TO BAD CUTOUT I WILL BE REPLACING. I HAVE CUTOUT REPLACED EVERYTHING OK//COD 4 // VER/DBM IDC XXXX
12368 | Pikeville | 3403001 | PIKEVILLE | CITY | 2008-12-18 07:32 | 2008-12-18 08:40 | 7 | 68 | 59777-1 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3403001// FUSE BLOWN--------- 12T FUSE LINK BROKE//COD 7// VER/DBM //L3/WHV// IDC XXXX
12369 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2011-08-13 23:34 | 2011-08-14 07:30 | 1 | 476 | 4705081 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED ONE TRANSFORMER OUT ON POLE 1122-214 NEED 15KVA TRANSFORMER CUTOUT AND ARRESTER CAN USE BUCKET. . HAVE TRANSFORMER CHANGED EVERYTHING OK VER/KEP IDC XXXX
12370 | Hazard | 3303901 | LESLIE | HYDEN | 2009-01-12 22:41 | 2009-01-13 00:40 | 4 | 119 | 54579-1 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3303901// MAY HAVE BAD TRANS// ADD 1 CUST TO COUNT// MISMAPPED COMPLTED DISC// STS WR # 28040042// BROKEN FUSE TAIL // COD 3 + 1 MISMAPPED VER/TOM L3/TOM IDC XXXX
12371 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2022-08-17 11:01 | 2022-08-17 18:57 | 1 | 476 | 4754891 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 38830213B20227 35/5 lift pole broke-by trk through yard- drop down in woods can work tomorrow if so desired-ds081722 Released by crew 078S01 Repairs made, closed on 213-04 at 18:57. Ticket complete.
12372 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-03-10 18:24 | 2012-03-10 18:58 | 14 | 34 | 4569421 | 476 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BROKE NEUTRAL IN SERVICE DROP. OPENED XMF AT 1824 CLOSED AT 1858 ALL POWER RESTORED CLOSE TICKET//COD 14// VER/DBM IDC XXXX
12373 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-03-12 18:17 | 2010-03-12 22:15 | 2 | 238 | 65802-1 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , NEED 2 MEN AND 7.2 CUTOUT, NOT SURE IF BUCKET WILL WORK IT. RELEASED BY CREW 077H01//STS WR# 34238740 //ISO 37830273B00146 // COD 2 // MD FILED ON MISSING FUSE //REPLACED LINE CUTOUT ON POLE #37830273B00146// VER/DBM IDC XXXX
12374 | South Williamson | 3200302 | BELFRY | TOLER | 2018-09-13 00:28 | 2018-09-13 08:24 | 1 | 476 | 4090321 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. I replaced the transformer cutout door that had burned up. Power restored at 08:24. COD-1 ISO TF 38821039B00182
12375 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2013-12-29 11:49 | 2013-12-29 19:45 | 1 | 476 | 4209771 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TAP AT POLE 38831052D00127 @ 1310 POLE FIRE ON 38831052D00351 DUE TO BAD CUTOUT// WILL TRY TO MAKE REPAIRS// WILL NEED 8 CROSSARM //1 MAN// BUCKETPOLE FIRE ON 38831052D00351 DUE TO BAD CUTOUT// WILL TRY TO MAKE REPAIRS// WILL NEED 8 CROSSARM //1 MAN// BUCKET RELEASED BY CREW 074S05 COD-1 ISO PO @ 38831052D00127 VER/HFP L3/HFP IDC XXXX
12376 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-02-29 13:06 | 2016-02-29 15:05 | 4 | 119 | 4788561 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGING ARRESTER ON 38831122C10823/ ISO 38831098D40814/ COD 2 . C PHASE ALREADY OPEN, OPENED A AND B PHASES AT 13:20, REPLACED ARRESTER AND REPAIRED SECONDARY , ALL WORK COMPLETE / GXJ
12377 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2011-05-12 22:30 | 2011-05-12 22:47 | 28 | 17 | 4080041 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HT// VER/DBM
12378 | Pikeville | 3413401 | GARRETT | GARRETT | 2019-06-07 12:22 | 2019-06-07 16:20 | 2 | 238 | 4446271 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Released by crew 074S04guy rusted at anchor & fell in to primary xfmr riser. have secured guy to pole away from primary riser & restored power . we will need to put this in abnormal database.
12379 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-09-30 12:52 | 2012-09-30 16:50 | 2 | 238 | 4100331 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK PULLED INTO == NEW FUSE BEEN PUT ABOUT 2 WEEKS === REFUSED POWER OK ///VER/CRB L/3 CRB IDC XXXX
12380 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-11-27 04:07 | 2017-11-27 08:05 | 2 | 238 | 4603311 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfmer cutout on pole 38831064000012. power restored at 8:05
12381 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2017-08-18 12:59 | 2017-08-18 14:58 | 4 | 119 | 4275801 | 476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE BURNT INTO VER/KEP
12382 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2021-01-08 13:55 | 2021-01-08 15:30 | 5 | 95 | 4856891 | 475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | A span of open wire secondary has pulled out of sleeve,Will have to open Trans on 86-C-403 to sleeve wire back together will keep up with time..Opened at 14:50 made repairs and restored at 15:30.. LR- 1st CC Call of Part out came in at 13:55
12383 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-08-11 22:10 | 2016-08-11 23:45 | 5 | 95 | 4765371 | 475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 44-4612 BAD 37 KVA, 7200-120/240/ ISO 38830044C24612/ COD 5// TRK OK //CEW ON SITE,,ALL REPAIRS MADE,,ALL POWER RESTORED//// VER/DBM
12384 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-01-23 10:30 | 2022-01-23 12:05 | 5 | 95 | 4397981 | 475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced cutout and restored @ 12:05. sh
12385 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-12-01 10:55 | 2008-12-01 12:30 | 5 | 95 | 53511-1 | 475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR# 27479159 // RELATED TO ORDER 53487-1 CREW HAD TO OPEN LINE FUSE TO ISOLATE POLE THAT HAS TOP BURNT OFF// NOTES FROM THAT ORDER=== XFMR POLE 38830762000067 BURNT OFF. OPENED LINE FUSE ON POLE 38830762000002 AT 10:55 TO ISOLATE TROUBLE. CREW EN-ROUTE. REPAIRS UNDERWAY. REPAIRS COMPLETE. CLOSED LINE FUSE AT 12:30. SH L3/KEP IDC XXXX
12386 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2016-06-14 23:44 | 2016-06-15 01:19 | 5 | 95 | 4348191 | 475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | BAD CONN ON 4/3 SERVICE REPLACED 60 FT. 4/3 SERVICE WITH 60 FT. 2/3 SERVICE VER/ARN
12387 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-09-19 15:02 | 2017-09-19 17:40 | 3 | 158 | 4373941 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS CUTOUT DOOR BURNT UP ON 1077A333 REMOVED HOT LINE TAP AT 17:30 REPLACED CUTOUT RESTORED POWER AT 17:40 VER/KEP L3/HFP XXXHFP
12388 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-10-27 14:36 | 2017-10-27 15:55 | 6 | 79 | 4503701 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND AND REPAIRED A STAND BROKEN IN PRIMARY HANGING DOWN INTO NEUTRAL, APR AT 1555 CLOSE TICKET VER/AWD L3/HFP XXXHFP
12389 | Pikeville | 3408401 | KIMPER | LONGFORK | 2009-08-28 11:53 | 2009-08-28 15:50 | 2 | 237 | 55082-1 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WORK REQUEST # 31462953 //CREW WILL CALL FOR TICKET WHEN READY TO REPLACE THIS XFR RELEASED BY CREW 074S06 COD-2 ISO TF 37820005000112 L3/HFP IDC XXXX
12390 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-08-04 16:16 | 2016-08-04 20:13 | 2 | 237 | 4735051 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 25 KVA 7200 TRANSFORMER AND CAN GET BUCKET TO IT RELEASED BY CREW 077S05 2 MEN TO CHANGEOUT. INSTALLED NEW XFMR AND RESTORED POWER 2013 CREW 077H01 VER/AWD
12391 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2019-04-19 15:42 | 2019-04-19 18:20 | 3 | 158 | 4135591 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//CKING BBREAKER///////////XFRF IS OUT,WILL RE-FUSE/////////FUSE HAD ROTTED INTO,RE-FUSED&RESTORED
12392 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-01-21 06:48 | 2014-01-21 10:45 | 2 | 237 | 4297741 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TO REPLACE 3 CUTOUTS . REPLACED 3 CUTOUTS AND 1 ARRESTER , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/CRB
12393 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2009-05-30 21:26 | 2009-05-30 22:45 | 6 | 79 | 52065-1 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 45-5599 BAD LA 10T POLE 45-145 65T CC 6 VER/PDP
12394 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-09-30 05:43 | 2008-09-30 09:40 | 2 | 237 | 52096-1 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000303//BROKE CUTOUT ON POLE 43-175// COD 2//SERVICER OPENED LINE AT POLE 43-160 @ 09:25 TO FIX BROKE CUTOUT//THIS INTERUPTED 27 MORE CUSTOMERS(SEE H52096-1)//ISO 38830043000160// OPENED SB ON POLE 43-160 09;25 ON 09;40//SENT REPORT TO MAPPING DBM// IDC XXXX
12395 | Pikeville | 3402002 | KEYSER | STONECOAL | 2015-03-06 13:31 | 2015-03-06 14:50 | 6 | 79 | 4146941 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE WILL CHANGE/// CHANGED BAD CUTOUT AND RESTORED SERVICE @ 14:50/COD 6// VER/ ADH
12396 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-04-18 11:03 | 2009-04-18 15:00 | 2 | 237 | 57883-1 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/TOM L3/TOM IDC XXXX
12397 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-09-08 10:52 | 2020-09-08 13:30 | 3 | 158 | 4441261 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing.
12398 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-02-16 16:45 | 2015-02-16 20:42 | 2 | 237 | 4034111 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT & XFMR CUTOUT BAD ON POLE 37830376A00102//LINE CUTOUT & XFMR CUTOUT BAD ON POLE 376-102, REPLACECD CUTOUTS RESTORED POWER AT 20:42 VER/CRB L3/HFP XXX
12399 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-06-22 13:33 | 2022-06-22 17:30 | 2 | 237 | 4275881 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken XFMR C/O // Restored @ 17:30
12400 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-01-04 16:46 | 2010-01-04 18:05 | 6 | 79 | 60480-1 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE HAVE XFMR FUSE OUT ON POLE 249-178//// BAD C/O WILL HAVE TO CHANGE IT OUT.//// C/O CHANGED POWER RESTORED VER/KEP L3/KEP IDC XXXX
12401 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-06-02 10:31 | 2022-06-02 14:28 | 2 | 237 | 4997731 | 474 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral and Hot Leg into at secondary pole 215-D-231,Will be making Repairs..Replaced 4-3 service wire with 2-3 and restored service 14:28..
12402 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-01-29 08:02 | 2014-01-29 10:40 | 3 | 158 | 4322191 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ON SITE RM.CREW REQ. RELEASED BY CREW 078H20,, CREW ON SITE, REPLACED 25KVA XFMR, ALL POWER RESTORED COD-3 ISO TF 38830068A00583 VER/HFP L3/HFP
12403 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-12-02 13:13 | 2009-12-02 17:10 | 2 | 237 | 58302-1 | 474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER TO CALL BACK WHEN HAVE GATES UNLOCKED IDCC CDC83 XXXX
12404 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-06-09 22:52 | 2021-06-10 06:45 | 1 | 473 | 4700211 | 473 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer fuse out on pole 819-A-20.cutout was bad.i replaced the cut out and restored the fuse at 06:45
12405 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-11-30 05:42 | 2019-11-30 13:35 | 1 | 473 | 4104301 | 473 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. cutout broke on pole 37830077000044 gonna need 2 men to change. need 7200 cutout t-bracket and arrester pole is manual pole is rotten need send copy to rob pigman asap
12406 | Hazard | 3310502 | HADDIX | CANOE | 2020-06-11 10:19 | 2020-06-11 18:12 | 1 | 473 | 4003431 | 473 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Per Steve Shepard send to rick maggadgot bad 10kva 7200 transformer can back mat hander into pole Released by crew 077S05// repaired and restored @1812
12407 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2009-07-10 08:53 | 2009-07-10 16:45 | 1 | 472 | 53481-1 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WORK REQ # 30680338 // ONE LEG OUT ON UNDER GROUND CABLE NEED CREW TO FIX, CAN NOT INSTALL POWER TEMP IN WAY OF DRIVE THRU ,CHECK ALL CONN IN TRANSFORMER AND METER BASE 43 VOLTS IN ONE LEG OF UNDER GROUND TRYING TO GET CREW NOW RELEASED BY CREW 078S09----CREW ON SITE, NEED TO PULL OUT BAD UG AND INSTALL NEWW SERVICE VER/TOM L3/TOM IDC XXXX
12408 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-03-31 08:57 | 2019-03-31 16:49 | 1 | 472 | 4043881 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew req, bad c/o no trucks, in wet backyard, top of c/o is broken, just sitting on rest of c/o, need to rep c/o Released by crew 078S06,repairs made all cust restored please close ticket thanks.bt
12409 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2022-07-14 23:06 | 2022-07-15 01:04 | 4 | 118 | 4492661 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuse out on pole 38820916B00004.got fuse back in at 01:04.one fuse was in i could hear loud buzzing from deadend bell.its porcelain and has a good size chunk broke off.. send copy to bill johnson so we can get a job wrote up to make repairs
12410 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2021-06-10 13:14 | 2021-06-10 15:36 | 5 | 142 | 4706331 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Center phase trans. cutout busted @48-B1-665, will have to open other 2 phases to make repairs. A phase cutout is busted as well, will need big bucket to make repairs.Will have to open 3 L/Fs @48-B1-178 to isolate. Will keep track of times. Opened all 3 L/F @1513, closed back in @1536.
12411 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2012-10-25 15:42 | 2012-10-25 17:40 | 4 | 118 | 4172251 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING LINE--REPLACED BAD ARRESTOR VER/KEP IDC XXXX
12412 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-02-09 15:25 | 2012-02-09 21:27 | 3 | 362 | 4330641 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | GOT LINE FUSE BACK IN ON 478A4-154 AT 1620, B PHASE CABLE BAD ON POLE 478-20. SLICED CABLE. APR AT 2127 CLOSE TICKET. CABLE IS IN BAD SHAPE PLEASE SEND GREG BELL A COPY OF THIS TICKET TO WRITE JOB FOR REPLACEMENT ASP THANKS.//MD FILED//SENT TO GREG BELL AND STEVE MARTIN//COD 3//ISO// VER/DBM IDC XXXX
12413 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-04-03 12:51 | 2010-04-03 14:49 | 4 | 118 | 57928-1 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD LIGHTNING ARRESTER, LINE FUSE BLOWN ON" A ` PHASE ON POLE 184-35, BAD ARRESTER ON POLE # 184-36 VER/KEP IDC LOOKS LIKE PH C NOT A CHANGED COUNT FROM 2 XXXX
12414 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-01-21 22:11 | 2013-01-22 00:09 | 4 | 118 | 4725481 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | NO CREW REQUIRED 20T ON 271-96 AED CREATED ///VER/CRB L/3 CRB IDC XXXX
12415 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-10-08 08:23 | 2020-10-08 14:00 | 4 | 337 | 4535521 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | one hot leg burnt into on underground service Released by crew 077S10 secondary leg burned into made repairs and restored power at 14:00 opened primary at13:15 closed back at 14:00
12416 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-10-28 07:34 | 2022-10-28 11:30 | 2 | 236 | 4073211 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUST SERVICE DROP BURNT // MAKING REPAIRS // REPLACED 19.9 C/O // RESTORED @ 11:30
12417 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-02-11 10:50 | 2010-02-11 14:46 | 2 | 236 | 56665-1 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | GOT BAD UNDERGROUND SERVICE, CALL JIM MULLINS AND HE IS GOING TO TELL BRUCE AND THEY WILL LET YOU KNOW WHAT THEY COME UP WITH. RELEASED BY CREW 077S05 // VER/TOM L3/TOM IDC XXXX
12418 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-09-12 20:44 | 2011-09-13 00:40 | 2 | 236 | 4862761 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 44-179 BAD 25KVA BRING 37.5 TRUCK TO POLE DO NOT CROSS WOODEN BRIDGE RELEASED BY CREW 078S08//ISO 38830044A00179//COD 3 IDC CHANGED COUNT FROM 4 AND CLEARING POLE FROM 143 XXXX
12419 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-03-09 09:39 | 2008-03-09 13:35 | 2 | 236 | 55638-1 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3314402// REPLACED CUTOUT GATE AND FUSE LINK//COD 2// VER/DBM IDC XXXX
12420 | Pikeville | 3421001 | BREAKS | CITY | 2013-07-13 19:45 | 2013-07-13 21:43 | 4 | 118 | 4519971 | 472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THE NEUTRAL AND ONE PHASE WIRE BURNED APART IN MID SPAN I MADE REPAIRS. VER/PDP IDC XXXX
12421 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-09-02 10:59 | 2009-09-02 18:50 | 1 | 471 | 61104-1 | 471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 31538566 //CHANGED XFR //VOLTAGE STILL 131 / 262 SEND TO G BELL TO CK VOLTAGE AT STATION//COD 1// VER/DBM IDC TRANSF WAS NOT BAD, REGULATOR WAS STUCK IN RAISE POSITION, BUT TRANSFORMER WAS STILL BAD, RISER HAD WELDED TO TANK XXXX
12422 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-03-13 03:01 | 2014-03-13 10:52 | 1 | 471 | 4486911 | 471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD . PLEASE SEND THIS TO TOMMY GOBLE ,HE WILL REPLACE //.CUTOUT REPLACED BACK TO NORMAL COD-1 ISO TF @ 38830956000011 VER/HFP L3/HFP
12423 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-04-26 07:07 | 2011-04-26 14:58 | 1 | 471 | 65219-1 | 471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW TO FIX CALL FOR CREW WAITING ON RESPONSE CREW REQ,669-64 FAULT POLE RELEASED BY CREW 078S09// HIGH WATER WILL GET THIS PM. LMRNEED CREW TO FIX CALL FOR CREW WAITING ON RESPONSE CREW REQ,669-64 FAULT POLE // HIGH WATER WILL GET THIS PM. LMROPEN RECLOSER(IN NEW ORDER) FOR CLEARANCE ISSUE ON BAD CUT-OUT OPENED AT 1400 BACK ON AT 1458 JOB COMP// IDC DCMT XXXX
12424 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-06-15 18:38 | 2014-06-15 21:15 | 3 | 157 | 4094281 | 471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHGING.COMPLETE
12425 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-02-24 08:49 | 2012-02-24 16:40 | 1 | 471 | 4491931 | 471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ACTUAL POLE # 37830117000092, NEED 15KVA TRANSFORMER, NO TRUCK ACCESS, BEWARE: OPEN SEWAGE NEAR POLE, GO TO LAST HSE IN HOLLOW THEN TURN BACK TO THE RIGHT AROUND HILLSIDE RELEASED BY CREW 074S03// CHANGED BAD XFMR AND RESTORED POWER AT 16:40 TIM MCCOY ////VER/CRB IDC XXXX
12426 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2020-06-30 15:23 | 2020-06-30 17:22 | 17 | 119 | 4095511 | 471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 7200 cutout on pole 321-325. need line crew. manual pole. opened step down on 37830321A40568 at 17:00 to safely replace cutout and closed back in at 17:22 Released by crew 077S10
12427 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-01-02 08:40 | 2018-01-02 12:35 | 2 | 235 | 90006953 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 secondary burnt down (3 customers out originally)/ had to open the transformers on pole 38830045D37260/ opened xfmer @ 38830045D37260, @ 08:40 (affected 2 additional customers), 1/0 sec down across 29th st. @bill phillips auto sales crew on site fetr 12:45 replacing 1/0 with 4/0 sec. all pwr restored @ 12:35 plse close ticket lrm/ DUPLICATE IN DOVS
12428 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-12-15 07:20 | 2020-12-15 15:10 | 1 | 470 | 4770091 | 470 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | customer was single phasing, bad UG conductor, will need line crew with 1/0 UG wirecustomer was single phasing, bad UG conductor, will need line crew with 4/0 UG wirecustomer was single phasing, bad UG conductor, will need line crew with 4/0 UG wire Released by crew 074S09//DAE 1000054080 ADIPHASE INSTALLED
12429 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-05-15 06:12 | 2022-05-15 06:59 | 10 | 47 | 4891921 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 37830448B00148 // repairs made and customers restored at 0659
12430 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-11-18 20:34 | 2015-11-19 04:24 | 1 | 470 | 4466671 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 115-493 BAD 25KVA 19.9 120/240 NEED TWO CURRENT LIMBING FUSES A/B TRANS. RELEASED BY CREW 078S08---CREW ON SITE--CHANGED OUT BAD 25KVA AND 3 CURRENT LIMIT FUSES . VER/TOM L3/TOM
12431 | Hazard | 3303901 | LESLIE | HYDEN | 2018-10-13 18:35 | 2018-10-13 22:30 | 2 | 235 | 4249711 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATER ON POLE 37830413A00345 //bad insulator on 413- 431 L3/HFP
12432 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-10-16 11:56 | 2014-10-16 13:30 | 5 | 94 | 4636921 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REMOVED HOT TAP ON 245A97 TO OLD INACTICE LINE HAD BROKEN CUTOUT HAS CLEARENCE ISSUES NEEDS SENT TO TECH TO HAVE LINE REMOVED OR TALLER POLE SET// COD 5// VER/DKG L3/DKGXXXX
12433 | Hazard | 3307301 | BULAN | ARY-HEINE | 2022-10-22 11:10 | 2022-10-22 19:00 | 1 | 470 | 4054211 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken manual cutout on pole 177-D1-391 that is within the minimum approach, crew required. This is a very narrow road leading to this house, I dont think a large truck will be able to turn here. Crew required, 7200 cutout. Released by crew 077S04 restored power at 19:00
12434 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-10-20 15:45 | 2013-10-20 19:40 | 2 | 235 | 4949871 | 470 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTOMER ONLY HAS 120 VOLTS, I NEED ASSISTANCE ONE MAN AND THE BIG BUCKET . WE REDID XFMR LEADS EVERYTHING OK// VER/DBM
12435 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2020-10-13 11:26 | 2020-10-13 13:00 | 5 | 94 | 4551921 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | clamp burnt up on pole 448-B-135. thats what has caused this outage. gonna replace clamp and stirrup. replace burnt items. power restored
12436 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-06-25 12:38 | 2013-06-25 16:33 | 2 | 235 | 4396841 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFORMER . NEED LINE CREW , TRUCKS TO POLE. RELEASED BY CREW 078S01 V, GO BACK WITH A 25KVA//LMR/CREW ON SITE/FETR1730/VEM/REPIRS COMPLETE/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L/3 CRB IDC XXXX
12437 | Hazard | 3301401 | COMBS | COMBS | 2018-01-31 17:09 | 2018-01-31 17:56 | 10 | 47 | 4788121 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called customer meter blank neighbors out broken fuse/ ISO 37830271C00114/ COD 10
12438 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-03-05 13:33 | 2009-03-05 15:07 | 5 | 94 | 55320-1 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404302//, ON SITE, BAD CUTOUT AT XFORMER, REPLACING IT//COD 5// VER/DBM IDC XXXX
12439 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-03-17 10:13 | 2008-03-17 18:03 | 1 | 470 | 57846-1 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3000102// POLE 46-2292 BAD PRI UNDERGROUND IDCC PN2109, CNT4 XXXX
12440 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-09-05 14:23 | 2017-09-05 18:18 | 2 | 235 | 4331601 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED XFR CUTOUT 149-11 COMPLETE 38830149000011 VER/AWD
12441 | Hazard | 3308001 | JACKSON | S.JACKSON | 2016-04-20 01:33 | 2016-04-20 09:23 | 1 | 470 | 4106241 | 470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK ACCORDING TO AFTER HOURS CALLOUT GUIDE LINES BROKE CUTOUT ON POLE 38831083D11185 AND THIS WAS ONE CUST/ ISO 38831083D11185/ COD 1/ VER/BOW
12442 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2018-05-02 11:56 | 2018-05-02 19:45 | 1 | 469 | 4298051 | 469 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | undergr.pad mount xform 75 kva 7200 ,cust has . ct cabinet,checked fuse link in pad mount test good closed back in nothing send to b. tackett Released by crew 078S04,replaced xfmr all cust restored @ 1945 please close ticket thanks.bt/ CD 38830020A17872/ RD 38830020A17875/ COD 1
12443 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-07-13 13:26 | 2012-07-13 21:15 | 1 | 469 | 4712771 | 469 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830249B00089 ALMOST BURNT OFF AT TOP, DUTY SUPERVISOR NOTIFIED.-- OPENED RECLOSERS ON POLE # 37830249B10346 AT 14:10 OUTAGE FOR THIS IN ORDER 4714321 IDC XXXX
12444 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-09-05 00:33 | 2011-09-05 01:40 | 7 | 67 | 4813771 | 469 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 118-4511 6T TRANS FUSE BROKE REPAIRED VER/KEP IDC XXXX
12445 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-02-20 08:27 | 2015-02-20 16:16 | 1 | 469 | 4052591 | 469 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TIM MILLER REPORTS FAILED CUTOUT. REPLACED CUTOUT AND ARRESTOR ADDED FIBERGLASS BRACKET D SAMMONS ON AT 15:55 COD-1 VER/HFP L3/HFP
12446 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-03-11 08:18 | 2016-03-11 15:03 | 3 | 405 | 4836291 | 469 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE H4836291****40/5 POLE, TRACK MACHINE/ POLE FIRE ON POLE 38830115D00436/ LINE FUSE WAS OPEN ON POLE 38830115D00592/ ISOLATED LIFTING HOT TAP ON POLE 38830115D00229 TAGGED TO VERNON MULLINS/ CLOSED IN LINE FUSE ON POLE 38830115D00592 @ 0850//BAD DOGS LOCATED AT ISOLATING POLE 115-D-229, USE CAUTION//CREW ON SITE/WILL NEED TO OPEN FUSE ON 115-D-592 FOR REPAIRS/FETR1500/VEM/OPEN FUSE ON 115-592@1147/REPAIRS MADE AND ALL CUST RESTORED 1503/PLEASE CLOSE TICKET/THANKS/NO ASB WORK ORDER/ VER/BOW
12447 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2019-01-22 07:42 | 2019-01-22 09:00 | 6 | 78 | 4702601 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse link broke. Restored @ 9:00. sh
12448 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2010-04-03 13:22 | 2010-04-03 14:40 | 6 | 78 | 57955-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-378 BAD CUTOUT ALSO 1/0 RISER MELTED OFF POLE VER/KEP IDC XXXX
12449 | Hazard | 3302704 | HAZARD | KENMONT | 2016-12-25 01:33 | 2016-12-25 02:51 | 6 | 78 | 4235831 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 296C-101 OPENED UPON ARRIVAL @ 1:33 POWER RESTORED AT 2:51 JKL VER/TOM L3/TOM
12450 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2014-12-02 11:48 | 2014-12-02 13:45 | 4 | 117 | 4825721 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY RISER HAS BROKE AT TOP OF XFMR CUTOUT. REPAIRING. REPAIRED AND RESTORED XFMR @ 13:45. SH VER/CRB
12451 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2011-04-08 20:45 | 2011-04-09 04:33 | 1 | 468 | 52252-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39503138 // POLE 68-581 BAD 10KVA BRING 15 OR 25KVA TRUCK OK RELEASED BY CREW 078S08/XFMR CHANGED /POWER RESTORED 0433/PLEASE CLOSE TICKET/THANKS/VEM //VER/GAH IDC XXXX
12452 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-12-05 22:39 | 2010-12-06 00:36 | 4 | 117 | 63430-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 329-41... REPLACED CUTOUT RESTORED POWER AT 00:36 VER/ARN IDC XXXX
12453 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2022-01-21 16:32 | 2022-01-21 17:50 | 6 | 78 | 4394041 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Bayonet fuse open on padmount xfmr. Replaced fuse - restored @ 17:50. sh
12454 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-08-10 17:48 | 2015-08-10 19:45 | 4 | 117 | 4118751 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE # 193-20 WILL PATROL/// CUT OUT DOOR BURNT UP ON POLE @ 194-20 WIIL CHANGE/// CHANGED BAD CUT OUT DOOR AND RE-FUSED LINE FUSE @ 19:45 AND RESTORED SERVICE// VER/A DH
12455 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-06-21 09:31 | 2013-06-21 13:25 | 2 | 234 | 4380551 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE IS BLOWN ON POLE 150-50. I AM PATROLLING LINE NOW.I CLOSED LINE FUSE IN AND IT CAME BACK OUT. I AM GOING TO PATROL LINE AGAIN. ARRESTER WAS BAD ON 150-198. I CLEARED ARRESTER AND CLOSED LINE FUSE IN AT 13:25 ENTERED MD COD-2 ISO LF 37820150000050 VER/HFP L3/HFP
12456 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2017-11-02 00:17 | 2017-11-02 08:05 | 1 | 468 | 4523661 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Dispatched in accordance with KYPCo Late Night Callout Guidelines. 4/3 service burnt down
12457 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2020-08-04 08:32 | 2020-08-04 16:20 | 1 | 468 | 4284101 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.5, 75 kva double bushing 240/480 xfmer. need current limiting fuse also. send to T. lewis, truck ok Released by crew 078S04 c phase xfm was bad complete TL
12458 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-05-02 21:34 | 2012-05-03 00:10 | 3 | 156 | 4736921 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 XFORMER ON POLE 165-63 NEED LINE CREW AND TRUCKS TO POLE. RELEASED BY CREW 078S01//COMPLETE AT 00:10 VER/ARN IDC XXXX
12459 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-06-25 16:19 | 2009-06-26 00:07 | 1 | 468 | 60052-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA NO TRUCKS CREW REQUIRED RELEASED BY CREW 078S03/YARD DOG IN ROUTE/XFMR DIFF LOCATION/FETR0130 6-26-09/VEM/XFMR CHANGED AND POWER RESTORED 0007/PLEASE CLOSE TICKET /THANKS/VEM //COD 1// VER/DBM
12460 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-03-05 15:52 | 2018-03-05 19:46 | 2 | 234 | 4968381 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tried to call customer straight to voicemail Bad cutout need 2 men and 19.9 kv cutout. Released by crew 074S07///rreplaced c/o/ Repaired @ 1930 vyt still out due to station outage/ ISO 37830140B00163/ COD 2/ 1552-1946
12461 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-04-28 09:25 | 2009-04-28 17:13 | 1 | 468 | 53361-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | VER/HFP WR # 29556329 //// OPENED TRANSFORMER AT 09:25 TO MAKE REPAIRS--RAYBURN AN MARTIN ENROUTE--B FRALEY TO WORK RELEASED BY CREW 078S07 COD-2 L3/HFP IDC XXXX
12462 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-05-16 15:27 | 2009-05-16 23:15 | 1 | 468 | 58705-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP BAD URD WILL NEED TO LOCATE AND MAKE REPAIRS. CARL TOLIVER RELEASED JOB CREW REQ POWER ON AT 23:15//VER/CRB L3/HFP
12463 | Whitesburg | 3312902 | JENKINS | JENKINS | 2018-10-17 16:33 | 2018-10-17 18:30 | 4 | 117 | 4263581 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned into I installed a new cutout and arrestor L3/HFP
12464 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-08-30 02:41 | 2008-08-30 06:35 | 2 | 234 | 57617-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | COD-2 / BAD 15KVA NEED 25 KVA RELEASED BY CREW 078S08, COMPLTED CHANGE OUTFROM 15 TO 25 VER/LDA IDC XXXX
12465 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2016-12-03 07:26 | 2016-12-03 10:02 | 3 | 156 | 4162341 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-6081 BAD CUTOUT DOOR BURNT UP OLD CUTOUT NO PARTS NO TRUCK/ ISO 38830069D16081/ COD 3 REPLACED CUTOUT, CLOSED AT 10:02 TICKET COMPLETE/ VER/BOW L3/HFP XXXHFP
12466 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-06-13 19:59 | 2014-06-13 22:35 | 3 | 156 | 4089131 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BROKE DOWN CATCHING GREEN POLE ON FIRE. PT OUT FIRE AND RELACED CUT-OUT. RESTORED POWER AT 22:35. 6/13/2014. PLEASE SEND TO DOUG CHRISTIAN. MAY NEED TO REPLACE POLE. HAS A LARGE HOLE TROUGH IT. VER/CRB
12467 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2016-08-02 13:31 | 2016-08-02 16:07 | 3 | 156 | 4723941 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ON 991=D2-152 TOOK OUT LINE FUSE ON 991-D2-101 NTA BUT I CAN MAKE REPAIRS// REPLACED CUTOUT AND STANDOFF BRACKET RESTORED POWER AT 16:07 COD-3 ISO LF @ 38820991D20101 VER/HFP L3/HFP
12468 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-06-05 15:46 | 2011-06-05 19:40 | 2 | 234 | 4237191 | 468 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY BOLT BROKE ON NEW 15KVA TRANSFORMER SEND TO B FRALEY--IA SPAN OF 4/2 IS ON THE GROUND AT POLE 38830069C35157AND NEEDS CUT DOWN--E MAIL TO MARTIN GUY STUB POLE IS BROKE AND NEEDS REPLACED--NEED TRAFFIC CONTROL RELEASED BY CREW 078S07//VER/CRB IDC XXXX
12469 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-12-06 11:26 | 2010-12-06 15:20 | 2 | 234 | 63575-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURN-UP REPLACE BAD CUTOUT COD-2 ISO TF 38831103000333 VER/HFP L3/HFP IDC XXXX
12470 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2019-07-14 20:41 | 2019-07-15 00:35 | 2 | 234 | 4708031 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50 KVA xfmr (two bushing in 120/208 bank). Crew enroute to replace. Replaced xfmr and restored @ 00:35. sh//cod 2
12471 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-08-29 10:19 | 2013-08-29 14:13 | 2 | 234 | 4718591 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT SERV TO TRY,BAD XFMR ON POLE 140B-372 100KVA 19.9,NO TRUCK RELEASED BY CREW 078S05XFMR FUSE OUT SERV TO TRY,BAD XFMR ON POLE 140B-372 100KVA 19.9,NO TRUCK RELEASED BY CREW (REPLACED 100 KVA XFMER AND TWO 19.9 CUTOUTS POWERED RESTORED AT 14:13) VER/SEF IDC XXXX
12472 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-01-12 14:53 | 2020-01-12 22:41 | 1 | 468 | 4290881 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 249-26 has rotted off at the ground and leaned over towards a garage. Map shows that its a 35-5, needs replaced. Truck access, flaggers. 12kv double dead end, cutout, #2 aluminum and reuse transformer. Released by crew 077H20//RESTORED @ 2241 ON 01-12-2020//COD 1
12473 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2009-08-22 15:33 | 2009-08-22 17:30 | 4 | 117 | 60752-1 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE IS NOT BLOWN. HOT-LINE CLAMP CAME OFF ON POLE 38830809000219. CUSTOMER COUNT IS SAME. DIFFICULT LOCATION. REPAIRED. RESTORED AT 1730. SH VER/KEP L3/KEP IDC XXXX
12474 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2019-02-08 17:56 | 2019-02-08 19:53 | 4 | 117 | 4772231 | 468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse failed on 148-42 refused cutout.restored power at 19:53 L3/HFP
12475 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-08-22 04:51 | 2018-08-22 12:38 | 1 | 467 | 4986451 | 467 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | : Dispatched in accordance with KYPCo Late Night Callout Guidelines./////bad 15kva 19.9 single bushing xfm.////will need one man and big bucket to replace.
12476 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-10-15 09:13 | 2022-10-15 13:06 | 2 | 233 | 4029771 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 13:06. sh
12477 | Paintsville | 3401101 | FALCON | FALC-OILS | 2010-11-22 09:31 | 2010-11-22 13:24 | 2 | 233 | 58612-1 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHECKING TRANSFORMER CUSTOMER HAS NO 240V// BAD TRANSFORMER GIONG TO GET ONE AND COME BACK// RELEASED BY CREW 076H04//CHANGING POT NOW TCM// OPENED POT AT 12:55, CLOSED NEW ONE IN AT 13:24 TCM//VER/CRB IDC XXXX
12478 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-06-04 09:42 | 2008-06-04 17:28 | 1 | 466 | 55889-1 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3110902// FOUND A BAD 25 KVA CSP TRANSFORMER, CAN NOT GET TRUCK TO POLE, ONE CUST, LAST HOUSE AT THE END OF THE HOLLOW //COD 1////VER/CRB IDC XXXX
12479 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-01-25 14:52 | 2013-01-25 18:45 | 2 | 233 | 4740681 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 37820050000177// J. HAWKINS IS ON THE WAY TO HELP RELEASED BY CREW 074S05 ///VER/CRB L/3 CRB IDC XXXX
12480 | Hazard | 3302704 | HAZARD | KENMONT | 2015-02-16 08:32 | 2015-02-16 12:25 | 2 | 233 | 4031981 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSF === NEED 50 KVA 19.9 TRANSF AND BUCKET TRUCK === CALLED FOR LINE CREW ==== RELEASED BY CREW 077S03/ ISO 37830320C00301/ COD 2 VER/HFP L3/HFP
12481 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-07-26 18:34 | 2015-07-26 22:27 | 2 | 233 | 4944451 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200-75 KVA 2 BUSHING. RELEASED BY CREW 078S07/ON SITE RM ALL POWER BACK ON PLEASE CLOSE TIC RMTIME ON 22:27//COD 2// VER/DBM
12482 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-08-09 11:44 | 2012-08-09 19:30 | 1 | 466 | 4915501 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD 4/0 UG--BOTH LEGS OUT--NEEDS REPAIRED--CAN USE SMALL SERVICE BUCKET RELEASED BY CREW 078S07///UG APPX. 6 DEEP, WOULD REQUIRE SHURRING. GONNA INSTALL TEMP OH AND REPLACE WITH NEW UG AT LATER DATE..HOTROD LINKOUS ///VER/CRB L/3 CRB IDC XXXX
12483 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-05-12 17:47 | 2019-05-12 18:52 | 10 | 65 | 4259421 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot tapburnt off on pole 289-54/// will have to open line fuse 289-53 to make repairs//COD 6 FROM BEGINNING OF OUTAGE//OPENED L/F 37820289A00053 @ 1833//P/U ALL CUSTS @ 1852 L3/HFP
12484 | Pikeville | 3407101 | TOPMOST | DEMA | 2008-02-22 21:24 | 2008-02-23 05:10 | 1 | 466 | 66397-1 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN ON POLE 37830162000001. POLE TOP BURNED OFF ON POLE 37830162000096. RELEASED BY CREW 074S08//VER/CRB IDC XXXX
12485 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-09-15 08:19 | 2016-09-15 16:05 | 1 | 466 | 4895171 | 466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BAD PADMOUNT XFMR AT 398-303.ISOLATED AT 398-418 RELEASED BY CREW 077S11 RELEASED BY CREW 077H17. RESTORED POWER AT 1605/ ISO 37830398D00418/ COD 1/ VER/BOW
12486 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2009-03-15 06:07 | 2009-03-15 07:40 | 5 | 93 | 58701-1 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000901 - BROKEN FUSE LI NK //VER/GAH IDCC CNT1 XXXX
12487 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-09-03 12:30 | 2022-09-03 15:05 | 3 | 155 | 4833321 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced and restored @ 15:05. sh
12488 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-01-23 10:57 | 2018-01-23 12:30 | 5 | 93 | 4766451 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830092B00912 has broken cutout on three phase tap Released by crew 078H01,,,
12489 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-11-19 09:15 | 2020-11-19 11:50 | 3 | 155 | 4707661 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Opened customers up @ 09:15 closed @ 11:50
12490 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-08-20 19:57 | 2020-08-20 21:30 | 5 | 93 | 4352501 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM fuse is Blown,Will be looking it over..Cutout was broke,Got it changed and restored service at 21:30.
12491 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-05-18 16:50 | 2021-05-18 19:25 | 3 | 155 | 4597171 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | primary lead burned out of top of xfmr.replaced with new clamp
12492 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2011-02-11 21:22 | 2011-02-11 22:55 | 5 | 93 | 56315-1 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE A BAD CONNECTION ON SECONDARY SIDE OF XFMR RISER....WILL HAVE TO OPEN XFMR TO REPAIR...//OPENED XFMR @ 22:35....REPLACED BAD CONNECTION....CLOSED XFMR @ 22:55....VOLTAGE GOOD NOW...JRV...02/11/11//VER/CRB IDC XXXX
12493 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-12-14 12:02 | 2008-12-14 12:17 | 31 | 15 | H58201-1 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402002//STS WR 27671844//HIGH SIDE STEPDOWN FUSE OPEN ON CENTER PHASE (PHASE A) ON POLE 1080-157A (NOT ON MAP YET, THIS SECTION OF LINE IS BEING REWORKED) //WILL OPEN OTHER TWO PHASES IN ORDER TO MAKE REPAIRS TO FUSE... WHICH WILL INTERRUPT 31 MORE CUST//CURRENT COD 17//OPENED OTHER 2 PHASES @ 1202//CLOSED AND ALL CUST RESTORED @ 1217//LEAD OUT OF HOT-TAP @ STEPDOWN BANK POLE 1080-157,WILL MAKE REPAIRS VER/KEP L3/KEP IDC XXXX
12494 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-02-18 09:50 | 2017-02-18 12:25 | 3 | 155 | H4405781 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CALLED 911 WITH ETA: 0945, SERVICE DROP BURNT DN MIDSPAN, REPLACED SERVICE APR CLOSE TICKET. OPENED XMF AT 0950 CLOSED AT 1225 CLOSE TICKET 38830453000183 VER/AWD L3/HFP XXXHFP
12495 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2017-04-03 20:16 | 2017-04-03 22:51 | 3 | 155 | 4610441 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEND TO RON. RELEASED BY CREW 078S08//BAD 25KVA//SEND TO RON. RELEASED BY CREW 078S08---CREW ON SITESEND TO RON. RELEASED BY CREW 078S08---CREW ON SITE--UPGRADED TO 37.5KVA--ALL NEW CONNECTIONS AND RISERS AT POLE--VOLT CK GOOD--PWR RESTORED AT 22:51--TBL TKT COMP---RMV VER/CRB L3/HFP XXXHFP
12496 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-11-05 21:30 | 2014-11-06 05:15 | 1 | 465 | 4703361 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOTTAP TO CLEARUP BROKEN 7200 CUTOUT, POLE IS NOT ON FIRE, CREW REQUIRED NO TRUCKS TO POLE.CREW ON SITE, ALL POWER RESTORED VER/ARN
12497 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-05-12 21:17 | 2015-05-12 22:50 | 5 | 93 | 4423611 | 465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE37830472000001, REPLACED CUTOUT RESTORED POWER AT 22:50. VER/CRB
12498 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-09-15 20:49 | 2018-09-15 22:45 | 4 | 116 | 4103221 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | clamp burnt into on pole 351-35, opened line fuse on pole 351-34 to isolate ..made repairs restored power at 22:45..
12499 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-07-28 14:03 | 2011-07-28 17:55 | 2 | 232 | 4634341 | 464 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEC RISER HAS BURNED IN TWO// WILL REPAIR//REWORKED SEC//POWER IS RESTORED//COD 2 AJB
12500 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2012-04-26 08:28 | 2012-04-26 16:12 | 1 | 464 | 4710181 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | APPALACHIAN WIRELESS IS HERE AND STATES XFMR FUSE IS BLOWN AT TOWER /// THEY ARE GOING TO TAKE ME UP THE HILL TO REFUSE /// XFMR IS BAD /// WILL NEED 25KVA 19.9KV /// CAN GET PICKUP TO POLE /// PLEASE CALL APPALACHIAN WHEN WE RESTORE POWER @ 1-800-438-2355 RELEASED BY CREW 074H18//REPLACED BAD TRANSFORMER AND RESTORED POWER AT 16:12 TIM MCCOY VER/KEP IDCC CCU XXXX
12501 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-01-03 23:24 | 2014-01-04 01:20 | 4 | 116 | 4226651 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR FUSE BLOWN DUE TO BAD CONNECTION IN SECONDARY WIRE, MADE REPAIRS RESTORED POWER AT 01:20 VER/PDP
12502 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-03-20 11:53 | 2021-03-20 15:45 | 2 | 232 | 4357651 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout..
12503 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2015-02-20 15:17 | 2015-02-20 23:01 | 1 | 464 | 4057531 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER 15 KVA NEED 25 CREW REQUIREDCAN GET TRUCK TO HAVE TO BACK UP HILL NO PLACE TO TURN AROUND NEED CHAINS/38830248B30379//RELEASED BY CREW 078S03/CREW ON SITE/FETR2315/VEM/ONLY TWO CUST OUT/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2301/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
12504 | Whitesburg | 3312901 | JENKINS | KONA | 2008-03-19 13:34 | 2008-03-19 17:26 | 2 | 232 | 58607-1 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE CECIL IS BRINGING BIG BUCKETT /// RELATED TO ORDER 58778-1 THIS (58778-1) WAS CREATED WHEN CREW OPENED LINE FUSE TO REPLACE CUTOUT VER/HFP IDC XXXX
12505 | Hazard | 3309302 | VICCO | JEFF | 2013-08-22 10:35 | 2013-08-22 12:31 | 4 | 116 | 4693931 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOLID BLADE CUTOUT WENT BAD REPLACED CUTOUT === POWER OK VER/KEP
12506 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-09-26 09:37 | 2015-09-26 10:35 | 8 | 58 | 4272591 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | OPENED LINE FUSE AT 09:37. DUE TO LINE FUSE CUTOUT BREAKING DOWN . SHOULD HAVE BACK ON AROUND 10:45 REPAIRS MADE CLOSED LINE FUSE BACK IN AT 10:35 EVERYTHING OK // NOTE ALSO OPENED TR FUSE TO REPLACE CUTOUT 8 CUST TOTAL // COD-8 ISO LF 38830784D00226 VER/HFP L3/HFP
12507 | Hazard | 3302704 | HAZARD | KENMONT | 2013-10-08 01:31 | 2013-10-08 09:15 | 1 | 464 | 4920321 | 464 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL WORK DURING NORMAL WORK HOURS------ SERVICE NEUTRAL BROKEN. REPAIRED NEUTRAL, POWER RESTORED. VER/HFP L3/HFP IDC XXXX
12508 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2012-03-15 22:56 | 2012-03-16 06:40 | 1 | 464 | 4586751 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PRC CREW ALSO WILL NEED SOMEONE TO OPERATE TRACK BUCKET,, HILL IS VERY STEEP AND SLICK, BAD 50KVA TRANSFORMER 7.2KW 120/240V SHOT WITHAND WITHOUT LIGHTING ARRESTER RELEASED BY CREW 078H08//REPLACED BAD TRANSFORMER POWER RESTORED AT 0640 PLEASE CLOSE TKT PRT COD-1 ISO TF 38830190A46023 VER/HFP L3/HFP IDCC FEC57 XXXX
12509 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2018-02-27 11:32 | 2018-02-27 18:12 | 3 | 400 | 4887401 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o..big bucket (septic tank)--crew req-ds022718 Released by crew 078S01/on site RM also opening line fuse on pole 262-236 to safel climb pole/ 1812 all power restored/ opened line fuse 1740 2 add customer MD DONE/ ISO 38830262000236/ COD 2/ COD 1 38830262000274
12510 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-07-14 18:44 | 2022-07-14 22:36 | 2 | 232 | 4491881 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15kva trans 7200 cutout and t bracket. truck accessible replaced transformer power restored at 22 :36
12511 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-06-15 15:52 | 2020-06-15 19:44 | 2 | 232 | 4023491 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200- 120-240, 25kva. trk to pole. Released by crew 078S07/on site RM xfm fuse in @19:44 please close tic RM
12512 | South Williamson | 3411401 | DEWEY | INEZ | 2017-12-23 05:03 | 2017-12-23 08:55 | 2 | 232 | 4665521 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 745-30//cant get truck to pole//need one man//repairs made//restored at 8:55//complete//em
12513 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2021-04-11 15:13 | 2021-04-11 19:05 | 2 | 232 | 4442471 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad c/o & arrestor pole 68-257. trk ok Released by crew 078S07,,,
12514 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-11-30 00:13 | 2015-11-30 02:09 | 4 | 116 | 4493231 | 464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT IS BAD ON POLE 37820008B00061. I NEED TO OPEN THE TRANSFROMER TO REPLACE THE CUTOUT. I OPENED THE TRANSFORMER AT 01:30, AND CLOSED BACK IN AT 02:09.
12515 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-08-18 07:08 | 2014-08-18 14:51 | 1 | 463 | 4377471 | 463 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 277/480 CAN 7200 VOLT TRUCKS OK/B PHASE SEND TO MULLINS RELEASED BY CREW 078S03/CREW ON SITE/FETR 1330/VEM/XFMR CHANGED BVOLTAGE TO HIGH /MAY HAVE REG PROBLEM/VEM/B PHASE REG ON 222-293 BAD TAGGED FOE DDC/MRO CONTACTED/VEM VER/CRB
12516 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-11-11 16:07 | 2011-11-11 23:50 | 1 | 463 | 4068351 | 463 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 3KVA SINGLE BUSH 7200 GO BACK WITH 10 OR 15 KVA TR TO POLE RELEASED BY CREW 078S04. CC = 1. REST AT 2350. VER/SDB IDC XXXX
12517 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2015-07-10 07:04 | 2015-07-10 14:47 | 1 | 463 | 4761471 | 463 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CREW REQUIRED, NEED 12 KV C/O, BKT & ARR..NTA RELEASED BY CREW 074E11CHANGE TX CUTOUT AND ARRESTER VER/SEF
12518 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-12-15 00:34 | 2021-12-15 08:16 | 1 | 462 | 4196961 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.,,replaced xfr cutout ,,complete
12519 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2022-03-06 20:05 | 2022-03-06 23:56 | 2 | 231 | 4572491 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required trucks ok need to change all 3 Released by crew 078S03//arrived RM open @ 23:30 closed @ 23:56 please close tic RM
12520 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-01-17 10:59 | 2017-01-17 12:05 | 7 | 66 | 4305261 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE BLOWN ON POLE 178-16, PATROLLING LINE, FOUND BAD LIGHTNING ARRESTOR ON POLE 178-230, CUT IN CLEAR//MADE AED VER/CRB L3/HFP HFP
12521 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2017-11-01 17:01 | 2017-11-01 19:35 | 3 | 154 | 4523221 | 462 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | need line crew SMALL BUCKET 3-CUTOUTS AND LA B PHASE OUT Released by crew 078S08/crew on site/FETR2000/vem/repairs complete and all cust restored 1935/please close ticket/thanks/vem COD-3 ISO TF 38830045C14243
12522 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-06-13 15:40 | 2010-06-13 16:57 | 6 | 77 | 62927-1 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT,WILL INVESTIGATE.WILL RE-FUSE,CUTOUT WAS BROKEN,OPENED FUSE AT 1105-25 AT 1618,CLOSED AT 1657 AFTER I REPLACED CUTOUT//COD 1 + 5
12523 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-01-13 13:22 | 2021-01-13 17:13 | 2 | 231 | 4866491 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 7200 cutout on pole 356/45 not by truck Released by crew 078H03arrived RMarrived RM cutout replaced power on @ 17:13 please close tic RM
12524 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-05-12 06:18 | 2008-05-12 14:00 | 1 | 462 | 62425-1 | 462 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SER DROP IS BROKE PULLED OUT OF SLEEVE DUE TO AN POLE THAT IS A LOCATIONIN A HILL-SLIDE POLE IS BOWED SEVERLY NEED TO GIVE ACOPY TO TECH TO RELOCOLATE POLE 165-920 REPAIRED FOR NOW POLE MAY BREAK ANY TIME SOON IDC XXXX
12525 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-08-14 11:27 | 2011-08-14 15:18 | 2 | 231 | 4707581 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON E-CORNER POLE IS UP ABOVE BOTTOM PHASE,NEED 7.2 CUTOUT,BUCKET TRUCK,1 MAN///REPLACED CUTOUT AND RESTORED// VER/DBM IDC XXXX
12526 | Hazard | 3309302 | VICCO | JEFF | 2015-02-16 10:19 | 2015-02-16 14:10 | 2 | 231 | 4032441 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830323D00212 === NEED LINE CREW MANUAL UP ON HILL 19.9 CUTOUT == RELEASED BY CREW 077S03 CUTOUT REPLACED POWER RESTORED AT 14;10/ ISO 37830323D00212/ COD 2 VER/HFP L3/HFP
12527 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-05-07 17:32 | 2010-05-07 20:06 | 3 | 154 | 57118-1 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE 937-2 IS OUT,BELIEVE A BAD ARRESTOR TOOK IT OUT.WILL REPLACE ARRESTOR AND RE-FUSE//REPLACED ARRESTOR,RE-FUSED AND RESTORED//COD 3// ISO 38820937000002 // VER/DBM IDC XXXX
12528 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-10-16 19:10 | 2013-10-16 20:27 | 6 | 77 | 4941371 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN MADE REPAIRS SERVICE ON FIRE AND BURNING 4 TO 5 FEET FROM POLE NO SPLICES VER/SEF IDCC CCU XXXX
12529 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-10-14 15:32 | 2009-10-14 16:49 | 6 | 77 | 63041-1 | 462 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION BURNED INTO, MADE REPAIRS RESTORED FULL POWER AT 16:49 VER/TOM IDC XXXX
12530 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-01-02 13:06 | 2019-01-02 14:23 | 6 | 77 | 4623011 | 462 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired neut. broke in two
12531 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2017-11-19 18:21 | 2017-11-19 18:54 | 14 | 33 | 4586571 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEE 4585201/ opening al three phase switch pole 37820197000027 to repair burnt loop 37820197000028/ opened @ 1821 closed @ 1854/ ISO 37820197000027 COD 14
12532 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-11-27 08:36 | 2015-11-27 12:27 | 2 | 231 | 4487651 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR VER/CRB
12533 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-05-24 18:41 | 2020-05-24 22:32 | 2 | 231 | 4899211 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830110B20171//COD 2//PREDICTED WRONG TRANSChuck said to release this due to wrong pole changed cutout power on 22:32 Released by crew 077S03
12534 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-05-29 15:25 | 2009-05-29 17:59 | 3 | 154 | 50201-1 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP BAD CURRENT LIMITING FUSE. L3/HFP IDC XXXX
12535 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-03-19 07:11 | 2008-03-19 07:32 | 22 | 21 | 58407-1 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3309103// THIS OUTAGE CREATED TO ALLOW CREW TO MAKE UP LOOPS AFTER REPAIRS MADE ON ORDER 58375-1 VER/HFP IDC XXXX
12536 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-09-02 07:17 | 2015-09-02 11:08 | 2 | 231 | H4189611 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEE 4189611.... PART POWER, LOOKING FOR PROBLEM REPAIRS MADE NEW S.D & REPAIRED NEUT. N SEC. XFMER OFF @ 10:45, ON @ 11:08 (2 ADD. CUST) DUPLICATE IN HOIS/ ISO 38830069D37131/ COD 3/ VER/BOW
12537 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-06-02 06:48 | 2015-06-02 09:22 | 3 | 154 | 4499071 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED INTO. I AM GOING TO REPLACE DOOR. I CHANGED DOOR./ ISO 37820097000175/ COD 3/ VER/BOW
12538 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-06-19 11:18 | 2019-06-19 12:35 | 6 | 77 | 4546221 | 462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1126-B1-42, checking. refused @1235.
12539 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-08-29 18:13 | 2008-08-30 01:54 | 1 | 461 | 57486-1 | 461 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074S08XFR TO RE-FUSEXFR IS BAD,WILL HAVE TO REPLACE IT,NOTE FETR CHANGEREPLACED BAD XFR,RESTORED.ALL OK AFTERWARDS VER/PDP IDC XXXX
12540 | Hazard | 3301401 | COMBS | COMBS | 2017-10-29 00:31 | 2017-10-29 02:03 | 5 | 92 | 4507391 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE/// VER/DKM L3/HFP XXXHFP
12541 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-06-10 09:10 | 2008-06-10 13:00 | 2 | 230 | 61413-1 | 460 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3000202// XFMR SECONDARY LUG BOLT BROKE, REPLACED RISER AND BOLT//VER/CRB IDC XXXX
12542 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-04-01 17:04 | 2011-04-01 18:36 | 5 | 92 | 61206-1 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | NO CREW REQUIRED REPAIRED GUY THEN SECONDARY//VER/CRB IDC XXXX
12543 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2021-12-22 16:40 | 2021-12-22 20:30 | 2 | 230 | 4220971 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad UG wire in conduit @ pole 91-115, need secondary bucket, 45ft of 4/0 wire, and 4 sticks of conduit, and clamps. Crew required, trucks to pole Released by crew 078S02crew on site FETR 21:00 LRM
12544 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2020-10-23 15:20 | 2020-10-23 16:06 | 10 | 46 | 4578671 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulator on pole 304-52, changed and restored power at 1606 no outage until line fuse opened @ 1520
12545 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-12-24 11:35 | 2009-12-24 15:25 | 2 | 230 | 54844-1 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER
12546 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-07-25 08:25 | 2008-07-25 12:15 | 2 | 230 | 60057-1 | 460 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3310501//\\\ SERV-IN CONNECTOR PULLED OUT, REPLACE WITH SQUEEZ-ON, POWER RESTORED//COD 2// VER/DBM IDC XXXX
12547 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-12-13 20:58 | 2019-12-13 22:30 | 5 | 92 | 4151921 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout on 37830030000006//ISO//Opened xfmr fuse @ 2209 // Closed @ 2230 //cod 5//
12548 | Pikeville | 3421001 | BREAKS | CITY | 2019-07-01 10:26 | 2019-07-01 18:06 | 1 | 460 | 4626751 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK FOR PROBLEMS/////////BROKEN CUTOUT 200-145,CREW ENROUTE TO HELP////////REPLACED BROKEN CUTOUT&RESTORED POWER
12549 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-03-03 20:55 | 2009-03-04 00:45 | 2 | 230 | 54751-1 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR # 28770215 // STS GOT 2 / 3 SERVICVE BURNED DOWN TO TWO METERS ON SAME SERVICE POLE CALL FOR SOME WIRE REPLACED SERVICE VER/LDA IDC XXXX
12550 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-04-04 15:15 | 2009-04-04 19:05 | 2 | 230 | 65159-1 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD TRANSFORMER CALLED FOR ONE AND RONNIE RICE IS BRINGING ONE TO US.//BAD TRANSFORMER CALLED FOR ONE AND RONNIE RICE IS BRINGING ONE TO US. FOUND BAD CONNECTION AT TRANSFORMER REPAIRED AND RESTORED POWER AT 1905. JKC & TS//COD 2// VER/DBM IDC XXXX
12551 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2021-11-03 10:28 | 2021-11-03 14:18 | 2 | 230 | 4052591 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | An old cutout gate burnt apart on pole 152-13. I dont have a like kind gate that will fit this cutout and I have spoken with the Hazard office about getting help to replace this equipment. Replaced this cutout.
12552 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-04-14 15:55 | 2015-04-14 19:45 | 2 | 230 | 4318051 | 460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WAITING ON CREW TIME OFF 18:40 ON @ 19:45. SD NEUT SQUEZED TO MAIN LINE NEUT. EXPECT DAMAGE COMP/EMAILED PEGGY/ADH// NEUTRAL BAD IN METER, HAD TO OPEN LINE FUSE FOUND BAD INSULATOR ON LINEFUST ON POLE 52 WHILE OUT THERE EVERYONE ON @ 1945// VER/ ADH
12553 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-06-10 15:39 | 2012-06-10 18:12 | 3 | 153 | 4898631 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUTOUT DOOR COD-3 ISO TF 37830024C01649 VER/HFP L3/HFP IDC XXXX
12554 | Hazard | 3309301 | VICCO | REDFOX | 2017-03-23 17:57 | 2017-03-23 20:30 | 3 | 153 | 4581101 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, WILL NEED 25 KVA 19.9 KV XFMR, CAN WORK WITH BIG BUCKET, POWER RESTORED VER/KEP
12555 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-12-08 14:45 | 2011-12-08 17:18 | 3 | 153 | 4160901 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 66-95 BAD 25KVA NEED 50KVA 4/0 RISERS TRUCK TO POLE OPENED TRANS 14;45 NO ONE HOME 2-CUST. OUT ADDRESS 4822 ON MAIL BOX RELEASED BY CREW 078S08.. REPLACED XFORMER.VOLTAGE IS 124-124/248..BLR COD-3 ISO TF 38830066000095 VER/HFP L3/HFP IDCC TOF1331 XXXX
12556 | Pikeville | 3402002 | KEYSER | STONECOAL | 2018-01-11 08:48 | 2018-01-11 09:39 | 9 | 51 | 4728931 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT-TAP STIRRUP BURNED INTO AT TAKE-OFF POLE,CREW ENROUTE TO HELP REPAIR STIRRUP,MAY REPLACE CUTOUT WHILE AT SITE//////REPLACED CUTOUT&STIRRUP,RESTORED./ ISO 38831127D00657/ COD 9
12557 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2020-07-23 16:30 | 2020-07-23 17:21 | 9 | 51 | 4219441 | 459 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | complete. pls close. tre
12558 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-10-16 09:47 | 2019-10-16 12:20 | 3 | 153 | 4146371 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutout was broken on pole 191-210..made repairs.restored. L3/HFP
12559 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-07-28 11:37 | 2012-07-28 14:10 | 3 | 153 | 4856691 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1147-4532 6T CHANCE FUSE BROKE VER/KEP
12560 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-12-24 22:31 | 2014-12-25 06:10 | 1 | 459 | 4883111 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF @ 206B-2627 NEED LINE CREW TO REPAIR NO TRUCK,LINE FUSE OPEN @ 206B-2353,WILL NEED TRACK EQUIP TO REPLACE 404 DEAD END RELEASED BY CREW 078S05 LOWED XFOMER C/O @ PRIMARY CUT TREES OUT VER/ARN
12561 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-12-02 10:35 | 2022-12-02 11:02 | 17 | 27 | 4220361 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Open Switch 38820673C00233 to reconnect Tap at 38820673C00074 (COD 17) /opened at 10:35//closed at 11:02//complete//em
12562 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-10-27 07:26 | 2010-10-27 15:05 | 1 | 459 | 65450-1 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURN OFF MANUAL, NEED 3 MAN CREW,//LIFTED HOT TAP ON POLE #37830109000006 NOT GROUNDED,CAN LOWER ON POLE WITH GOOD CLEARANCE, FIRE DEPT. WILL PUT FIRE OUT WITH FOAM,NEED NEW CUT OUT AND ARRESTER COMPLETE AND DEAD END AND GUY ATTACH. //COD 1// VER/DBM IDC 911 CALL FULL POWER BUT ASSUMING IT WENT OUT SOON AFTER XXXX
12563 | Hazard | 3307301 | BULAN | ARY-HEINE | 2019-07-26 18:46 | 2019-07-26 20:57 | 6 | 131 | 4797221 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | to close to change without cover up COD 3 FROM THE BEGINNING//LIFTED CLAMP ON POLE 37830200D00344 TO CHANGE CUTOUT,//THIS OUTED 3 MORE CUSTS//to close to change without cover uplifted hot tap on pole37830200D00344 at 20:35,put hot tap back on pole37830200D00344 at 20:57//replace 72 kv cutout Released by crew 077S04 L3/HFP
12564 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-11-23 00:19 | 2021-11-23 07:58 | 1 | 459 | 4117381 | 459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out, melted out, power restored
12565 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-07-07 08:23 | 2022-07-07 16:01 | 1 | 458 | 4416931 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required with flaggers bad 25 kva trucks ok change cutout while there take guard off old transformer install on arrestor bad bird area Released by crew 078S03
12566 | South Williamson | 3411401 | DEWEY | INEZ | 2011-04-12 10:31 | 2011-04-12 14:20 | 2 | 229 | 55731-1 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39536177 /// BAD 25 KVA XFMR ON POLE 601-6// NO TRUCK APPROACH//CREW ENROUTE//WILL CHANGE AFTER CLEAR UP AT PHOEBE TRACE//CREW ON SITE CHANGING NOW TCM// COD-2 ISO TF 38820601D00006 VER/HFP L3/HFP
12567 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-01-18 11:21 | 2009-01-18 15:10 | 2 | 229 | 58040-1 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-2 RELATED TO ORDER 58018-1 ADDED 1 CUSTOMER TO THIS ORDER AND ENTERED MD FOR CUSTOMER IN THAT ORDER L3/HFP
12568 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-01-30 13:31 | 2012-01-30 17:20 | 2 | 229 | 4306001 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA XFMR ON 794-103//CREW ENROUTE//HAVE XFMR CHANGED//RESTORED AT 17:20//COMPLETE//EM ///VER/CRB IDC XXXX
12569 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-04-05 19:40 | 2010-04-05 23:29 | 2 | 229 | 59094-1 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR RELEASED BY CREW 077S11BAD 25 KVA XFMR ... REPLACED XFMR RESTORED POWER AT 23:29 VER/LDA IDC XXXX
12570 | Paintsville | 3410602 | E.PRESTON | LANCER | 2015-12-26 10:36 | 2015-12-26 14:10 | 3 | 214 | 4561711 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 955-103. CLOSED LINE FUSE 955-95 @ 12:38 RESTORING ALL BUT XFMR 955-103. REPLACING CUTOUT. REPLACED CUTOUT AND CLOSED XFMR 955-103 @ 14:10 RESTORING REMAINING OUTAGED CUSTOMERS. SH// VER/ ADH
12571 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-12-12 13:41 | 2008-12-12 17:30 | 2 | 229 | 57732-1 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | VER/HFP HOT SEC. DOWN #4 CU.......COMP COD-2 L3/HFP IDC XXXX
12572 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-01-14 15:15 | 2010-01-14 19:04 | 2 | 229 | 54241-1 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN, BAD XFMR, NEED 25 KVA 7200 3 MEN & LINE TRUCKXFMR FUSE BLOWN, BAD XFMR, NEED 25 KVA 7200 3 MEN & LINE TRUCK.... REPLACED XFMR RESTORED POWER AT 19:04//COD 2// VER/DBM IDC XXXX
12573 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-06-02 17:42 | 2008-06-02 21:31 | 2 | 229 | 54658-1 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLING CREW/B REYNOLDS TO WORK RELEASED BY CREW 078S07//3000902//COD2 PER CREW//VER/CRB IDC XXXX
12574 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-04-20 09:41 | 2011-04-20 13:30 | 2 | 229 | 61090-1 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39644639 // XFMR CUTOUT BROKE...WILL REPLACE...POWER RESTORED @ 13:30 VER/KEP IDC XXXX
12575 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2016-01-16 20:38 | 2016-01-17 00:27 | 2 | 229 | 4626231 | 458 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE SEC. BURNT OPEN NEED CREW RELEASED BY CREW 078S08/OPENING XFMR ON 1148-590 FOR REPAIRS/LOOP BURNT OPEN 1148-589/APROX ONE HOUR OUTAGE/VEM/OPENED XFMR @1153/REPAIRS MADE AND ALL CUST RESTORED 0027/PLEASECLOSE TICKET/THANKS/VEM VER/KEP AJB CNT7
12576 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2021-06-10 10:52 | 2021-06-10 16:00 | 6 | 308 | 4704711 | 458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug 120 on one leg & 0 on the other/crew reqd. direct bury cable/4/0 Released by crew 078S04 // opened xfmr @1530 closed @1600
12577 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2009-06-09 23:53 | 2009-06-10 07:30 | 1 | 457 | 63740-1 | 457 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 30221325 //BAD 15KVA XFMR. CUSTOMER OK TO WAIT UNTIL 1ST THING IN THE MORNING. PLEASE HOLD AND MILLER OR ROGER WILL CALL FOR IT WHEN THEY COME IN. BRING XFMR BAG. RELEASED BY CREW 076S02 BAD 15KVA XFMR. CUSTOMER OK TO WAIT UNTIL 1ST THING IN THE MORNING. PLEASE HOLD AND MILLER OR ROGER WILL CALL FOR IT WHEN THEY COME IN. BRING XFMR BAG. CREW ON SITE - REPLACEMENT OF XFMR UNDERWAY.BAD 15KVA XFMR. CUSTOMER OK TO WAIT UNTIL 1ST THING IN THE MORNING. PLEASE HOLD AND MILLER OR ROGER WILL IDC XXXX
12578 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-05-26 15:08 | 2013-05-26 22:45 | 1 | 457 | 4186551 | 457 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN, 1 CUST HAD PART POWER. TR OUTAGED AT THE FOLLOWING TIMES... 1752-1805 1958-2007 2207-2245. CC 4. ORIGINAL OUTAGE 4186551. DUPLICATE OUTAGES H1181075-1, H1181076-1 & H1181077-1. VER/SDB IDCC TON1752 XXXX
12579 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2018-06-22 15:20 | 2018-06-22 22:57 | 1 | 457 | 4645871 | 457 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | have bad c/o on pole 1122-414, behind house, no trucks to pole, need crew req, to make repairs, lifted htsp on pole 1122-304, no grds or tgs placed at this loc, Released by crew 078S06 Released by crew 078H22--crew on site--G&T to rmv--made repairs--pwr restored at 22:57--tbl tkt comp--rmv
12580 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-08-29 08:28 | 2014-08-29 11:00 | 3 | 152 | 4435481 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 138-261 BAD LA SEND NOTE TO RAYBURN POLE 138-53 50T LINE FUSE//COD 3//AED CREATED// VER/DBM
12581 | Hazard | 3309302 | VICCO | JEFF | 2018-06-12 12:57 | 2018-06-12 16:45 | 2 | 228 | 4591201 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Need 19.9 cutoout and arss. and t bracket Released by crew 077S03
12582 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-09-22 00:26 | 2022-09-22 02:20 | 4 | 114 | 4907031 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout broke. Replaced cutout and restored @ 2:20. sh
12583 | Hazard | 3310502 | HADDIX | CANOE | 2015-10-13 08:41 | 2015-10-13 12:29 | 2 | 228 | 4343531 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 169A-369 , BAD CUTOUT ON POLE 169A-371 . FUSE SIZE ON POLE 169A-369 IS A 20T .//MADE MDC TO SHOW L/F ON POLE 369 AND L/F REMOVED ON 145 VER/CRB
12584 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2012-09-17 17:52 | 2012-09-17 18:30 | 12 | 38 | 4054841 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKEN..DETERIORATED..//..REPLACED & RE-FUSED XFMR.JRV..09/17/12//MADE MDC//COD 12 ///VER/CRB L/3 CRB IDC XXXX
12585 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-07-14 15:27 | 2017-07-14 23:03 | 1 | 456 | 4122011 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA NEED MATERIAL HANDLER AND 2 MEN/ ISO 38821081D00235/ COD 1/////////REPLACED XFR&RESTORED,ALL OK AFTERWARDS/ ISO 38821081D00235/ COD 1/ VER/BOW
12586 | South Williamson | 3411401 | DEWEY | INEZ | 2011-08-10 23:06 | 2011-08-11 01:00 | 4 | 114 | 4695031 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 647-2//GOING TO CLIMB AND CHANGE//CUTOUT CHANGED RESTORED AT 1:00//COMPLETE//EM VER/SDB IDCC PN502 XXXX
12587 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-02-05 19:28 | 2009-02-05 22:00 | 3 | 152 | 56040-1 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307302// LIGHTS BLINKING AT 2 HOUSES, PATROLING NOW. FOUND BAD LINE CUT-OUT, WILL HAVE TO OPEN RECLOSER TO REPLACE CUT-OUT. PAUL HICKMAN ON WAY TO LEND A HAND, SO AS TO KEEP OUTAGE TO MIN. P. HICKS. CHANGE OF PLANS...... WILL MACK OUT BAD C/O AND TAKE OFF LINE. AND COME BACK TOMAROW AND REPLACE WHEN LIGHT IS BETTER. HOT WORK REQUIRED. SHOULD NOT HAVE OUTAGE. P.HICKS.//COD 3// VER/DBM
12588 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-12-28 14:59 | 2010-12-28 17:31 | 3 | 152 | 56555-1 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38224442 // JOE MORELAND FOUND TRANSFORMER FUSE BLOWN AND DISCOVERED BAD 15KVA TR // TRUCK ACCESSABLE UPGRADED TO A 25 KVA POWER RESTORED AT 17:31 ENTERED MD..HFP // COD-3 ISO TF 38830269D06014 IDC XXXX
12589 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2017-12-13 20:58 | 2017-12-13 23:30 | 3 | 152 | 4647251 | 456 | PARTIAL POWER | EQUIPMENT FAILURE | INSULATOR | CALLED CUST//PART POWER//SERVICERS COMPUTER NOT WORKING//WORKING ORDER IN OFFICE//on at 1130
12590 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-07-27 09:19 | 2009-07-27 10:35 | 6 | 76 | 60082-1 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKE IDC XXXX
12591 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2016-07-07 07:21 | 2016-07-07 09:15 | 4 | 114 | 4553361 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 679-73..CHANGING.CHANGED XFMR CUTOUT..
12592 | Whitesburg | 3409503 | BURDINE | JENKINS | 2015-02-02 19:52 | 2015-02-02 23:40 | 2 | 228 | 4987091 | 456 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S11 BAD CONNECTIONS BURNT SECONDARY LEAD INTO AT POLE 382-143, WILL OPEN XFMR ON POLE 382-144 TO ISOLATE, OPENED AT 23:12 MADE REPAIRS RESTORED POWER AT 23:40. VER/KEP L3/HFP XXX AJBC CNT7 SEE H4987091
12593 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-09-23 12:44 | 2018-09-23 14:00 | 6 | 76 | 4144871 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 117-345, grounding and tagging tap to myself. Cutout changed all power restored at 14:00 L3/HFP
12594 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2021-01-07 16:26 | 2021-01-07 18:20 | 4 | 114 | 4854991 | 456 | DISTRIBUTION STATION | EQUIPMENT FAILURE | FUSE | Cutout fuse was broken. Customer stated that someone replaced this pole today and when I re-fused this cutout I noticed that someone had used a 1.6 amp fuse where a 6 should have been used. Fuse was broken, not blown.
12595 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2009-12-12 07:57 | 2009-12-12 11:45 | 2 | 228 | 60819-1 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR WILL NEED 10 KVA 7200 XFMR & BIG BUCKET,, REPLACED XFMR RESTORED POWER AT 11:45 TO 2 CUSTOMERS MAP SHOWS 1 CUST SERVICER SAID 2 VER/KEP L3/KEP
12596 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-05-03 17:27 | 2020-05-03 21:15 | 2 | 228 | 4791241 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 25 kva txmf truck ok bring txmf bag. Linecrew required. Released by crew 078S11 trsfmer changed and back in at 21:15
12597 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-05-31 13:39 | 2022-05-31 15:33 | 4 | 114 | 4988511 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke XCO on pole 1127-D1-824, Jason Hawkins is coming to help with repairs
12598 | Pikeville | 3409502 | BURDINE | LEVISA | 2021-02-09 09:10 | 2021-02-09 11:42 | 3 | 152 | 4951091 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a lead coming out of Trans Bushing that has Melted into,Going to open Trans and climb pole to make repairs will keep up with time..Opened Trans at 10:55 Restored at 11:42.Send copy to RyanThornsbury about getting a job to change out pole 311-113.
12599 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-03-26 09:24 | 2011-03-26 11:18 | 4 | 114 | 59431-1 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 248-626 WE HAVE A BAD XFMR C/O, WILL HAVE TO OPEN TAP OFF POLE 626 TO BE ABLE TO CHANGE C/O. TAP OFF FROM 10:45 TO 11:12. C/O CHANGED OUT POWER RESTORED. SEE 59455-1 FOR OUTAGE TO REPLACE CUTOUT /// COD-4 ISO TF 37830248A00626 VER/HFP L3/HFP IDC XXXX
12600 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-12-21 17:42 | 2011-12-21 21:30 | 2 | 228 | 4193981 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT..CUST SAYS HAPPENED AT 1 PM.THEY WAIT TIL DARK TO CALL IN THE NO POWER..NON TRUCK ACCESS..NEED ON A MAN TO ASSIST..3RD POLE PAST THE VULCAN BRIDGE, GOING TOWARD MAJESTIC.LIFTED HOT LINE CLAMP WITH LONG STICK..SEND TO JOEY REED.THANX.JRV.12/21/11 RELEASED BY CREW 080S01 ///VER/CRB IDC XXXX
12601 | Hazard | 3303901 | LESLIE | HYDEN | 2008-12-06 08:13 | 2008-12-06 10:45 | 3 | 152 | 54852-1 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3303901//XFMR FUSE BLOWN, LOOKS LIKE FUSE BROKE. REFUSED XFMR POWER RESTORED // COD 3 VER/TOM L3/TOM IDC XXXX
12602 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-01-13 14:34 | 2015-01-13 15:50 | 6 | 76 | 4933421 | 456 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY RISER BURNT UP ON ONE SIDE OF THE TRANSFORMER/// WILL REPLACE RISER//// REPLACED SECONDARY RISER AND RESTORED SERVICE @ 15:50//// VER/CRB L3/HFP XXX
12603 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-01-12 02:44 | 2021-01-12 06:32 | 2 | 228 | 4862761 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | Hot tap has come loose on 38830476000054, no trucks linecrew required. Released by crew 078S11/on site RM power back on @ 06:32 please close tic RM
12604 | Hazard | 3420001 | SOFT SHELL | VEST | 2014-05-28 09:11 | 2014-05-28 09:35 | 19 | 24 | H4941681 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO AT 107-77 COD-71/ OPENED RECL 108-116 AT 0911 TO REPAIR COD-19/ VER/KEP IDC XXXX
12605 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-07-08 15:29 | 2008-07-08 18:01 | 3 | 152 | 64618-1 | 456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410501// CUTOUT BROKE INTO. TIM IS SENDING LARGE BUCKET TO CHANGE CUTOUT. WE ALSO HAVE A LINE FUSE OUT ON POLE 48-46. THIS HAS 1 OTHER CUSTOMER WITH PARTIAL POWER. WE WILL REFUSE IT WHEN WE GET CUTOUT CHANGED. RELEASED BY CREW 074S01 - // COD 3 WILL NEED TO CHANGE FLT POLE 37830048A40026// VER/TOM IDC XXXX
12606 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-02-24 08:40 | 2022-02-24 10:11 | 5 | 91 | 4538991 | 455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DA SCHEME RESTORED 749 CUSTOMERS AUTO ///POLE 1083-92,DEAD-END INS BROKEN,TING PHASE LAY ON ARM///////.ELLIOT CREW ON SITE TO REPLACE INSULATOR//////MADE NECESSARY REPAIRS&RESTORED@10:11
12607 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-07-06 11:20 | 2012-07-06 18:55 | 1 | 455 | 4539431 | 455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 15KVA TRANSFORMER, NEED MATERIAL HANDLDER, NO RUSH (GARAGE) REPLACED TRANSFORMER, POWER RESTORED AT 18:55 --CAN CLOSE TICKET MWL
12608 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-08-04 17:56 | 2019-08-04 19:27 | 5 | 91 | 4839631 | 455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST// XFMR fuse blown will check and refuse// Fuse link pulled apart inside of cutout door. I refused and restored power @ 19:27
12609 | South Williamson | 3411401 | DEWEY | INEZ | 2008-05-18 15:44 | 2008-05-18 17:15 | 5 | 91 | 65539-1 | 455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT BAD ON POLE 743-C-2 CUT LOOP ON POLE 743-C-1 DELETE REST STEP FOR 1 CUSTOMER ALL BACK ON @ 1715 --- REMOVED CUTOUT UNTIL POLE IS REPLACED AT LATER DATE. SAM GOING TO TURN IN JOB TO HAVE POLE REPLACED. VER/HFP IDC XXXX
12610 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2012-07-06 07:09 | 2012-07-06 08:40 | 5 | 91 | 4530001 | 455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-48 BAD CUTOUT 20T
12611 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-02-13 17:45 | 2008-02-13 19:16 | 5 | 91 | 62825-1 | 455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3404302//LOOPS BURNT OPEN ON B PHASE OF POLE 1012-392//COD 5, OPENED 3 UNDERARM DISC. ON POLE# 1012-A-393 AT1904, CLOSED BACK AT1916// NO ADDITIONAL CUSTOMERS OUT WHEN DISC OPENED - CUSTOMERS ALREADY OUT FROM BURNT LOOPS// ISO - 38821012A00393 // VER/TOM IDC XXXX
12612 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-09-18 14:59 | 2015-09-18 18:46 | 2 | 227 | 4249321 | 454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA XFMER ON POLE 906-76///NEED 1 MAN AND BIG BUCKET///REPLACED BAD XFMER///REFUSED AT 18:46///COMPLETE BR VER/CRB
12613 | Hazard | 3307301 | BULAN | ARY-HEINE | 2017-10-26 00:26 | 2017-10-26 08:00 | 1 | 454 | 4499021 | 454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | UNLOCATED WITH VALID ACCOUNT NUMBER//PER CSC, THIS WAS A NEW INSTALL AS OF 10/23/17 // CALLED CUSTOMER AND CUSTOMER CAN SEE FUSE HANGING DOWN // CUSTOMER HAVING WORK DONE AT THIS ADDRESS EARLY IN THE MORNING, WANTS IT LOOKED AT FIRST THING, WISHES TO BE CALLED BEFORE WE COME OUT// // FUSE HAD BROKE, POWER RESTORED COD-1 ISO TF37830130000027 VER/HFP L3/HFP
12614 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-09-24 12:03 | 2018-09-24 15:50 | 2 | 227 | 4150221 | 454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door broken..changing L3/HFP
12615 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-09-14 04:31 | 2018-09-14 08:18 | 2 | 227 | 4094791 | 454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines.//fuse link broke
12616 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-12-23 18:05 | 2018-12-23 21:52 | 2 | 227 | 4595311 | 454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200 50kva, trk to pole. xfmer bag Released by crew 078S07/Arrived RM power on @ 21:52 please close tic RM L3/HFP
12617 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-11-16 08:12 | 2019-11-16 15:46 | 1 | 454 | 4039371 | 454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr, contacted P Hicks to get xfmr.. comp power restored
12618 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-11-09 19:37 | 2012-11-09 23:24 | 2 | 227 | 4378211 | 454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED A 25 KVA 19.9-120/240. MATERIAL HANDLER & 1 A LINEMAN COD-2 1 MISMAPPED TO #429 MD FILED VER/KEP IDC XXXX
12619 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-01-30 17:50 | 2021-01-30 21:15 | 7 | 205 | 4921171 | 454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | line fuse restored at 1849, XFM on pole 1125-D-601 is bad will need line crew with 25KVA 19.9 XFM// had to open line fuse on pole 1125-D-191 to safely change XCO on pole 115-D-601// line fuse on 191 off @ 20:30 on @ 20:54// XFM on 601 on @ 21:15
12620 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-01-24 22:14 | 2010-01-25 00:45 | 3 | 151 | 59021-1 | 453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON POLE 473-51... REPLACED DEADEND BELL & CUTOUT ON POLE 473-142 RESTORED POWER AT 00:45 COD-3 VER/KEP L3/KEP IDC XXXX
12621 | Cannonsburg | 3001401 | LOUISA | CITY | 2016-02-15 18:44 | 2016-02-15 21:15 | 3 | 151 | 4698421 | 453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XMF CUTOUT BROKE HANGING IN THE CLEAR, CUTOUT ON ARM AND IS LINECREW REQUIRED RELEASED BY CREW 078S11--SECOND BAD CUTOUT FEEDING SIDETAP TOWARD POLE 454-1801--OPENED AT 21:05---BOTH 30T LF AND XFMR FUSES-BACK IN AT 21:15---TBL TKT COMP RELEASED BY CREW 078H16// VER/ ADH
12622 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2021-12-11 14:02 | 2021-12-11 21:35 | 1 | 453 | 4178191 | 453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew reqd. bad 7200-25kva xfmer. no trk. yard dog or side by side w/winch. road cone marks driveway Released by crew 078S07
12623 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-08-07 08:44 | 2017-08-07 11:15 | 3 | 151 | 4233101 | 453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT ON POLE402-15 IS BROKEN. WE CHANGED OUT AND REFUSED COD-3 ISO LF 37830402D00015 VER/HFP L3/HFP
12624 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-01-26 06:14 | 2011-01-26 08:45 | 3 | 151 | 64339-1 | 453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN,WILL REPLACE IT////////REPLACED XFR CUTOUT AND RESTORED,ALL OK AFTERWARDS COD-3 ISO TF 37820004000039 VER/HFP L3/HFP IDC XXXX
12625 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-12-19 10:24 | 2020-12-19 12:55 | 3 | 151 | 4786581 | 453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed at transformer. {3 customers affected} Made repairs and restored @ 12:55. sh
12626 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2022-07-01 13:54 | 2022-07-01 16:25 | 3 | 151 | 4356241 | 453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required. bad 7200 25kva transformer. trucks to pole. Released by crew 078H33,repairs made all cust restored @ 1625 please close ticket thanks.bt
12627 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-04-17 01:05 | 2014-04-17 08:38 | 1 | 453 | 4613571 | 453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK AT REGULAR WORK TIME AS PER SET GUIDELINES // STS CUTOUT GATE BURNED UP COD-1 ISO TF 38831015000053 VER/HFP L3/HFP
12628 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-06-20 19:04 | 2020-06-20 22:50 | 2 | 226 | 4052311 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad transformer, putting out bad voltage. crew required 7200 25KVA transformer and cutout and bracket.
12629 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-08-02 07:52 | 2009-08-02 09:45 | 4 | 113 | 59413-1 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NEED TREE CREW TO CLEAR RIGHTAWAY --BROKEN FUSE LINK // VER/TOM L3/TOM IDC XXXX
12630 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-02-13 20:22 | 2010-02-14 00:08 | 2 | 226 | 57507-1 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRANSFORMER NEED TO REPLACED WITH AN 25 KVA 7200 VER/PDP IDC XXXX
12631 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2016-02-21 12:17 | 2016-02-21 14:10 | 4 | 113 | 4743621 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 48B-502..MADE REPAIRS AND CLOSED BACK IN @ 14:10.. VER/CRB
12632 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-07-28 07:44 | 2011-07-28 11:30 | 2 | 226 | 4631991 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFORMER. TRUCKS TO POLE. RELEASED BY CREW 078S01//COD 2 IDC XXXX
12633 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2022-12-19 09:19 | 2022-12-19 16:51 | 1 | 452 | 4275331 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Power temp @ location. Other hot leg burnt in two. need crew to repair or replace.//DAE# 1000075547//Power temp @ location. Other hot leg burnt in two. need crew to repair or replace. Released by crew 078S02Power temp @ location. Other hot leg burnt in two. need crew to repair or replace.//DAE# 1000075547///Repairs made///back on @ 16:51///Complete BR//CLOSED DAE
12634 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-01-01 20:12 | 2016-01-01 22:05 | 4 | 113 | 4580531 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKE. RESTORED @ 22:05. SH//COD 4// VER/DBM
12635 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-02-05 15:19 | 2015-02-05 17:12 | 4 | 113 | 4993531 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 37830179C00082, MANUEL, CALLING FOR HELP. OPENED RECLOSER 37830179C00232 AT 16:46, CLOSED BACK IN AT 17:12. ALL POWER RESTORED/ ISO 37830179C00232/ COD 4/ VER/BOW L3/DKGXXXX
12636 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-09-17 15:24 | 2020-09-17 19:10 | 2 | 226 | 4472621 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | need 25 kva 7200 and cutout and arrestor Released by crew 077S05.all power restored @ 19:10 hrs.p.hicks
12637 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2016-10-21 16:15 | 2016-10-21 23:47 | 1 | 452 | 4040651 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQ, BAD 25 KVA SINGLE BUSHING 120/240, CAN NOT GET TRUCK TO POLE I DO NOT THINK YOU CAN, RELEASED BY CREW 078S06/CREW ON SITE/FETR0030/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2347/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP L3/HFP XXXHFP
12638 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-06-07 19:34 | 2018-06-07 23:20 | 2 | 226 | 4567161 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced tran c/o.tran fuse in at 23:20--allgood-ds060718
12639 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-04-15 05:52 | 2019-04-15 09:38 | 2 | 226 | 4112771 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap broke @ pole38830070B43570. will make repairshot tap broke @ pole 70-3570. will make repairs Released by crew 078S07. Repairs made, ticket complete. COD-2 ISO TF 38830070B43570
12640 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2009-08-07 11:28 | 2009-08-07 19:00 | 1 | 452 | 58602-1 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP REPLACED CUTOUT L3/HFP IDC XXXX
12641 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2017-07-28 22:58 | 2017-07-29 06:30 | 1 | 452 | 4199681 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CREW REQ, NEUTRAL BROKEN ON #2 UNDERGROUND, FEEDING WHITE HOUSE, I PUT UP THE SEC, AT THIS LOC, AND FOUND NEUTRAL BROKEN GOING DOWN IN METAL CONDUIT, COULD NOT FIND THE END OF WIRE, WILL NEED TO MAKE REPAIRS OR INSTALL POWER TEMP, AS EARLY AS POSSIBLE TOMMORROW, CUST HAVE FAMILY REUNION RELEASED BY CREW 078S06/CREW ON SITE/FETR 0600/VEM/REPAIRS MADE/POWER RESTORED 0630/PLEASE CLOSE TICKET/THANKS/VEM/ONLY ONE CUST OFF/VEM SJGC CNT2
12642 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-02-19 07:01 | 2013-02-19 08:54 | 4 | 113 | 4828931 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE ///VER/CRB L/3 CRB IDC XXXX
12643 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-02-18 08:31 | 2009-02-18 12:17 | 2 | 226 | 63908-1 | 452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#28571014// BAD 15KVA NEED 25KVA TRUCK OK. 2-CUSTS. RELEASED BY CREW 078S08/CREW ON SITE /FETR1245/VEM/REPAIRS MADE AND ALL CUST RESTORED 1217 02-18-09/PLEASE CLOSE TICKET /THANKS/VEM//COD 2// VER/DBM
12644 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2019-01-29 03:26 | 2019-01-29 10:57 | 1 | 451 | 4730141 | 451 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout Guidelines./ Bad Transofrmer crew enroute to replace/ ISO 38831149000010/ COD 1Dispatched in accordance with KYPCo Late Night Callout Guidelines.xfmr bad .have called for crew to change out
12645 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2015-06-21 18:01 | 2015-06-22 01:32 | 1 | 451 | 4631671 | 451 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRUCK TO POLE RELEASED BY CREW 078S08///CREW ON SITE////REPLACED BAD 25KVA///VOLT CK GOOD///TBL TKT COMP//COD 1// VER/DBM
12646 | South Williamson | 3411401 | DEWEY | INEZ | 2018-05-07 16:12 | 2018-05-07 17:05 | 25 | 53 | 4321151 | 451 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | right hand line fuse blown on pole 743-199//cutout broke on 743-200///opened other two xfmrs to make repairs @ 1650//repairs made//restored all at 17:05//complete//em//COD 2 FROM THE BEGINNING OF OUTAGE
12647 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2011-07-23 16:30 | 2011-07-23 18:00 | 5 | 90 | 4597621 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GOING BAD POWER ON NOW NEED 1 MAN BIG BUCKET OPEN@1630 ON@1800 RPLACED CUTOUT VER/KEP
12648 | Pikeville | 3401001 | ELWOOD | DORTON | 2010-09-29 07:35 | 2010-09-29 10:05 | 3 | 150 | 55017-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE BROKE OUT OF HOT TAP FROM TOP OF LINE FUSE CUTOUT. I REPLACED HOT TAP. VER/KEP L3/KEP IDC XXXX
12649 | South Williamson | 3411401 | DEWEY | INEZ | 2021-04-12 07:35 | 2021-04-12 15:05 | 1 | 450 | 4443341 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | riser fuse out on pole 861-c-89//tried fuse and came back out//crew enroute to assist//OPENED RECLOSER 38830861A40174 @ 1151 CLOSED @ 1152//riser fuse out on pole 861-c-89//tried fuse and came back out//crew enroute to assist//found bad arrestor in padmount 861-95//have arrestor in clear//riser fuse out on pole 861-c-89//tried fuse and came back out//crew enroute to assist//found bad arrestor in padmount 861-95//have arrestor in clear//restored at 15:05//crew will come back to replace arrestor
12650 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-06-03 10:08 | 2009-06-03 13:53 | 2 | 225 | 65268-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED CUTOUT//COD 2// VER/DBM IDC XXXX
12651 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-10-31 11:20 | 2013-10-31 11:50 | 15 | 30 | 4977961 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RICK RAY OPENING LINE TO CHANGE CRACKED BYPASS FUSE VER/SEF IDC XXXX
12652 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-01-01 09:10 | 2022-01-01 16:40 | 1 | 450 | 4244381 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 15 kva trucks ok customer at last house up hill has the key togate Released by crew 078S03///Complete BR
12653 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-04-23 16:05 | 2018-04-23 17:35 | 5 | 90 | 4267621 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o, restored L3/HFP
12654 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-12-15 08:06 | 2020-12-15 10:36 | 3 | 150 | 4770161 | 450 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | crew req, have broken c/o, can use truck, also might as well change the other two c/o, as well, Released by crew 078S06/ all cutouts changed and xfmr bank restored 1036/ MLH
12655 | Hazard | 3310502 | HADDIX | CANOE | 2011-04-01 15:30 | 2011-04-01 16:45 | 6 | 75 | H61022-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER// WR#39398409BAD TRANSFORMER--//REC OPEN ON MAIN LINE OFF FROM 1530 TILL 1645 // VER/KEP IDCC CDC92 XXXX
12656 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2016-07-12 16:48 | 2016-07-12 18:18 | 5 | 90 | 4618331 | 450 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY NEUTRAL BROKE. I SPLICED IT BACK VER/AWD
12657 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2009-08-09 22:10 | 2009-08-09 22:40 | 15 | 30 | H51100-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICER ETA 20:10 (4 CUSTOMERS WITHOUT POWER) NO INTERRUPTION ON OTHER 15. 1/0 TWIST SECONDARY BURNT DOWN. APPROX 130 FT OF WIRE DAMAGED - WILL HAVE TO REPLACE ENTIRE SPAN. GOING TO PAINTSVILLE OFFICE TO GET WIRE. OPENED XFMR ON 978-177 AT 22:10. RESTORED AT 22:40 PICKING UP ALL CUSTOMERS. HAD TO LEAVE SECONDARY SLACK DUE TO TREES IN PRIMARY AT 978-177. PLEASE SEND TO J. BRADSHAW. SH IDCC DUP TO OPEN TRANSF XXXX
12658 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-02-09 06:28 | 2009-02-09 10:13 | 2 | 225 | 56831-1 | 450 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED RISER WIRE ON TRANSFORMER//COD 2// VER/DBM IDC XXXX
12659 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-02-20 15:13 | 2018-02-20 18:58 | 2 | 225 | 4865321 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout big bucket required. Released by crew 074S07//ENERGIZED 1858//PAUL LAYNE
12660 | Hazard | 3309301 | VICCO | REDFOX | 2009-04-10 12:10 | 2009-04-10 14:40 | 3 | 150 | 51024-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEVICER FOUND BROKE CUTOUT. MANUAL CLIMB CHANGED BAD CUTOUT//VER/CRB IDCC MCCDIS XXXX
12661 | Paintsville | 3401802 | INDEX | HOSPITAL | 2017-02-09 06:25 | 2017-02-09 10:10 | 2 | 225 | 4374691 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER/ TRANSFORMER FUSE APPEARS TO HAVE BROKEN. OOONLY TWO CUSTOMERS AFFECTEDOO RESTORED @ 10:10. SH/ ISO 38830654B00049/ COD 2 PER SERVICE CUSTOMER COUNT*****/ VER/BOW L3/HFP XXXHFP
12662 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-07-05 10:04 | 2016-07-05 11:34 | 5 | 90 | 4536971 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DUPLICATE OUTAGE; POWER WAS RESTORED AROUND 11:00
12663 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-07-14 17:45 | 2012-07-14 18:30 | 10 | 45 | 4726001 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TRANSFORMER TO MAKE SAFE @ 1745 // DONT SEE WHAT TOOK LINE DOWN // VER/ARN
12664 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-09-27 10:50 | 2009-09-27 18:20 | 1 | 450 | 65467-1 | 450 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ALL CONNECTIONS AT POLE AND METER CHECK OK, BEAST NEUTRAL TESTER SHOWS BAD NEUTRAL, CREW NOTIFIED, 1 CUST OUT, # ABOVE IS GOOD OR ALSO 316-9757, MAIN BREAKER IN HOUSE IS OFF, URD DIECT BURIED 1/0 #2 NEUTRAL RELEASED BY CREW 078S05 VER/KEP L3/KEP
12665 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-10-25 10:15 | 2009-10-25 13:27 | 3 | 192 | 52778-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WORK REQ # 32360206 // SOME KIND OF ANIMAL ON CUTOUT, BAD CUTOUT ON POLE 255-91. LINE FUSE BACK IN ON POLE 45. FETR ON 255-91 IS 13:30 COD-3 ISO LF 37830255D00045 L3/HFP IDC XXXX
12666 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-09-18 11:30 | 2012-09-18 13:00 | 5 | 90 | 4061071 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW LIFTED HOT TAP AT POLE 37830530000012 TO ALLOW THEM TO REPLACE CUTOUT OPENED LINE @ 1130 AND CLOSED @ 1300 CUTOUT FAILED LOWERED MATERIAL ON POLE COD-5 ISO PO @ 37830530000012 VER/HFP L3/HFP IDC XXXX
12667 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-06-03 08:47 | 2009-06-03 16:17 | 1 | 450 | 64561-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3307302//XFMR FUSE IS OUT DUE TO TREES GROWN INTO RISER CALLING FOR TREE CREW TO CUT PATH TO POLE//15 KVA XFMR IS BAD SEND TO P HICKMAN CREW RELEASED BY CREW 077S04 REPLACED XFMR RESTORED POWER AT 1617//COD 1// VER/DBM IDC XXXX
12668 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2012-12-31 17:12 | 2012-12-31 20:57 | 2 | 225 | 4560821 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED 2 LINEMAN FOREMAN , AUTO XFMR & POSSIBALLY 4/0 UG SERVICE WIRE. WILL SPEAK TO COUSTOMER & SEE IF HE KNOWS IF THE UG IS IN CONDUIT OR NOT. // HAMILTON, GARRETT & LAYNE//REPLACED TRANS VER/CRB L/3 CRB
12669 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-01-17 17:30 | 2010-01-17 20:00 | 3 | 150 | 55617-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRYING TO ISOLATE CUTOUT ON 204-150 VER/TOM IDC XXXX
12670 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2010-05-20 10:15 | 2010-05-20 11:45 | 5 | 90 | 65399-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NO OUTAGE AT THIS TIME XFMR LEAKING OIL , WILL NEED CREW TO REPLACE 50 KVA 7200 RELEASED BY CREW 077S11 RPLACE 50KVA OPENAT 10:15 ON AT11:45;//VER/CRB IDC XXXX
12671 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-01-09 14:24 | 2020-01-09 14:49 | 18 | 25 | 4228531 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened @14:24 closed @ closed @14:49 changed broke coutout ///
12672 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-05-13 08:10 | 2010-05-13 10:40 | 3 | 150 | 61207-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND FUSE LINK, HAD ROTTEN AND BROKEN, ALSO CUTOUT DOOR WAS BAD, REPLACED DOOR AND POWER IS RESTORED AT THIS LOC VER/KEP L3/KEP IDC XXXX
12673 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-12-19 21:25 | 2008-12-19 22:40 | 6 | 75 | H61018-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003// POLE FIRE AT 38830230000279, ISOLATED AT 239-155, 6 CUST RESTORED AT 22:40, REMOVED INACTIVE PRIMARY AND NEUTRAL FROM POLE 38830230000278, NEED TO RETURN WHEN GROUND IS FROZEN TO REMOVE POLE 230-279 AND XFMR, PLEASE SEND COPY OF TICKET TO LLOYD RAYBURN, FINAL RESTORATION 23:45 VER/LDA L3/KEP IDC XXXX
12674 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-05-09 13:40 | 2012-05-09 16:10 | 3 | 150 | 4763991 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | TRANSFORMER LEADS--NEED BIG BUCKET--OPEN TRANSFORMER 13:40--CLOSED16:10 ///VER/CRB L/3 CRB IDC XXXX
12675 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-07-13 08:36 | 2009-07-13 10:06 | 5 | 90 | 65443-1 | 450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411801//APPEARS LINE FUSE FOR THIS HOLLOW IS OUT,WILL PATROLAPPEARS LINE FUSE FOR THIS HOLLOW IS OUT,WILL PATROL/CUTOUT DOOR HAD BURNED OUT,REPLACED AND RE-FUSED AND RESTORED POWER - DID MAP DISC - VER/TOM L3/TOM IDCC CNT1 XXXX
12676 | Pikeville | 3403001 | PIKEVILLE | CITY | 2009-11-06 15:56 | 2009-11-06 23:25 | 1 | 449 | 66067-1 | 449 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP RELEASED BY CREW 074S08 L3/HFP IDC XXXX
12677 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-10-03 07:04 | 2018-10-03 14:33 | 1 | 449 | 4191861 | 449 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | heated up con on open wire #4 copper--replaced--tree crew clearing up tree at sec pole--beast of burden not all twitchy now--allgood-ds100318/ ISO 38830142A00154/ COD 1 L3/HFP
12678 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-07-25 19:58 | 2011-07-25 21:50 | 4 | 112 | 4621901 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 1 SEC. RISER HAS BURNED IN TWO AT XFMR//REPAIRED RISER// POWER IS RESTORED//VER/CRB IDC XXXX
12679 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-07-07 10:01 | 2010-07-07 13:45 | 2 | 224 | 62934-1 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#35881388 BAD 50KVA 19.9 TRANS. NEED 75 KVA 19.9 SEND TO BILL FRALEY TRANS. IS ON POLE 92-117 NOT 422 RELEASED BY CREW 078S08 IDCC CNT5, PN422 XXXX
12680 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2010-12-11 22:31 | 2010-12-12 00:23 | 4 | 112 | 65431-1 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE FUSED TRANSFORMER UP EVERTYHING OK VER/TOM IDCC PN192 XXXX
12681 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-02-20 17:45 | 2015-02-20 18:41 | 8 | 56 | H4054701 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | AT POLE 174C2-535 WILL NEED 25 KVA XFMR.(34.5 KV),,XCO,T-BRKT,HLC.,& D.E. INSULATOR (19.9),OIL SPILL CLEANUP KIT,, TRUCK ACCESS-LINE CREW/MATERIAL HANDLER BUCKET (WILL HAVE TO OPEN LINE FUSE TO REPLACE D.E. INSULATOR AT POLE 174C-295.RGP. //LINE FUSE OPEN FROM 1745 TO 1814 DUP OF 4054701 FOR FUSE OUTAGE // VER/HFP L3/HFP
12682 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-06-17 13:27 | 2015-06-17 20:55 | 1 | 448 | 4587111 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NEED 45/5 POLE TRUCKS TO POLE ISOLATED LINE FUSE ON POLE 185-28 AND PLACED GROUNDS AND TAGES TO DDC. NEED LINE CREW , RELEASED BY CREW 078S01//1535 GAVE BOBBY REYNOLDS PERMISSION TO REPLACE KYDDC TAGS AND GRNDS WITH HIS OWN BY PHONE// ISO 38830185000028/ COD 1/ VER/BOW
12683 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-10-31 12:56 | 2016-10-31 16:40 | 2 | 224 | 4065581 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 139-4002 BAD 7200, 277-480 2 SEC BUSHING CAN. ROADSIDE CAN SUPER QUICK CARWASH. RELEASED BY CREW 078S07,REPLACED BAD XFMR ALL CUST RESTORED @ 1640 PLEASE CLOSE TICKET THANKS.BT 38830139C00135 VER/AWD
12684 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-11-21 12:31 | 2011-11-21 16:15 | 2 | 224 | 4097341 | 448 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY BUSHING BROKE ON XFMR, NEED CREW TO CHANGE RELEASED BY CREW 077S12. CHANGED X-FMR AND CUT-OUT RESTORING POWER AT 16:15. 11-21-2011. J.S.B.//COD 2// VER/DBM IDC XXXX
12685 | Pikeville | 3421001 | BREAKS | CITY | 2009-06-13 11:32 | 2009-06-13 19:00 | 1 | 448 | 60505-1 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER. VOLTAGE IS 7200/120/240/. CANNOT USE TRUCK. RELEASED BY CREW 074S02 COD-1 VER/KEP L3/KEP
12686 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-04-14 06:31 | 2008-04-14 10:15 | 2 | 224 | 50911-1 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401302//ISOLATED TROUBLE CECIL SEXTONS CREW WILL MAKE REPAIRS RELEASED BY CREW 074S07//VER/CRB IDC XXXX
12687 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-11-11 12:14 | 2016-11-11 12:42 | 16 | 28 | 4093591 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENING LINE FUSE TO CHANGE BAD INSULATOR ON POLE 38821132000135/ ISO 38821132000022/ COD 16// OPENED LINE AT 12:14 CLOSED BACK IN AT 12:42 TIM MCCOY/ VER/BOW L3/HFP XXXHFP
12688 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-02-27 10:43 | 2020-02-27 14:27 | 2 | 224 | 4436441 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 19.9 trans on 8-D-139 trk app.need 2 men and mat handler. Released by crew 079S03 L3/HFP
12689 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-07-08 18:37 | 2018-07-08 22:21 | 2 | 224 | 4751701 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | C phase cutout busted on pole 24-D2-475, will have to open other 2 cutouts on bank to make repairs, will keep track of times.C phase cutout busted on pole 24-D2-475, will have to open other 2 cutouts on bank to make repairs, also bad 15 kva 7200 trans. / cut over to 208, will need 1 man and material handler bucket to help change out.C phase cutout busted on pole 24-D2-475, will have to open other 2 cutouts on bank to make repairs, also bad 15 kva 7200 trans. / cut over to 208, will need 2 men a
12690 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-02-01 23:53 | 2016-02-02 01:45 | 4 | 112 | 4665711 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BROKEN LINE FUSE VER/KEP
12691 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2015-09-13 10:20 | 2015-09-13 11:24 | 7 | 64 | H4234081 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE @ 271-194 .OPENED LINE FUSE @ 272-73 @ 10:20///REPAIRS MADE LINE FUSE 272-73 IN @ 11:24// VER/ ADH L3/HFP XXXHFP
12692 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-09-30 23:51 | 2011-10-01 00:55 | 7 | 64 | 4936301 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// FUSE BROKE//REFUSED//POWER IS RESTORED //VER/GAH IDC XXXX
12693 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-04-16 20:35 | 2022-04-16 20:43 | 56 | 8 | 4770311 | 448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | Emergency outage to bypass regulator//123V Ph-G/DOL 1198711Released by crew 077S05
12694 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-01-24 22:53 | 2014-01-25 00:45 | 4 | 112 | 4311141 | 448 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEC CABLE DOWN,WILL SEE IF I CAN REPAIR////////MADE NECESSARY REPAIRS.SERVE-IN BURNED NEUTRAL INTO,ALSO 1 LEG.POSSIBLY DAMAGES HERE.OK WHEN I LEFT //VER/GAH
12695 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-12-04 16:46 | 2022-12-04 19:15 | 3 | 149 | 4227401 | 447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on 828-100. replacing..
12696 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-10-01 12:46 | 2022-10-01 15:15 | 3 | 149 | 4959161 | 447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C ph line fuse blown on 875-185. Cutout failed on bank pole 875-322. Replaced all three cutouts on 875-322 and one arrester.Restored @ 15:15. sh
12697 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2018-02-10 10:31 | 2018-02-10 13:00 | 3 | 149 | 4822761 | 447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT@147-319 BROKE DOWN,WILL REPLCE IT.OPENED F@147-55 TO ISOLATE POLE 147-319@11:24 Opened line fuse on 37820147B00055 to safely isolate pole fire on 37820147B00319. CUTOUT@147-319 BROKE DOWN,WILL REPLCE IT.OPENED F@147-55 TO ISOLATE POLE 147-319@11:24//////REPLACED CUTOUT&RESTORED
12698 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2009-08-12 06:38 | 2009-08-12 14:05 | 1 | 447 | 61082-1 | 447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR BAD//COD 1//ISO 37820196000021// VER/DBM IDC XXXX
12699 | Pikeville | 3409502 | BURDINE | LEVISA | 2009-04-25 09:57 | 2009-04-25 12:26 | 3 | 149 | 59771-1 | 447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACE TRANSFORMER FUSE BROKE //COD 3// VER/DBM IDC XXXX
12700 | Hazard | 3302704 | HAZARD | KENMONT | 2014-02-17 13:34 | 2014-02-17 16:03 | 3 | 149 | 4394421 | 447 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER, OPENED TRANSFORMER AT 15:15, REPLACED ALL CONNECTIONS, POWER RESTORED AT 16:03//COD 2 + 1
12701 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-07-30 23:46 | 2017-07-31 02:15 | 3 | 149 | 4208471 | 447 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION ON XFM. LEAD...REPAIRED...
12702 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-04-03 16:20 | 2014-04-03 20:27 | 3 | 247 | 4560661 | 447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PARTAILLY RESTORE HAVE BAD 15 KVA, ON POLE 18-174, CAN USE TRUCKS CREW REQ, RESTORED LINE FUSE AT 1800, TO ALL BUT ONE CUST AT OLD BALL FIELD BEHIND FIRE DEPT, RELEASED BY CREW 078S06/CREW ON SITE/FETR2045/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2027/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
12703 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-02-14 09:16 | 2009-02-14 11:45 | 3 | 149 | 61031-1 | 447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830183B00180 //VER/GAH
12704 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-04-25 20:22 | 2013-04-26 00:05 | 2 | 223 | 4048701 | 446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER IS BAD AND LEAKING OIL, FUSE WON.T OPEN ON TRANSFORMER BLOWING LINE FUSE NEED CREW CAN UP-GRADE TRANSFORMER TO BIGGER SIZE 10 KVA BAD 7200 120/240 LINE FUSE NOT ON FUSEIS AN 20-T PRI IS HOT GIVE TO JOE RELEASED BY CREW 078S09/ FETR 01:00 // JEH/ REPAIRS COMP. POWER REST. @ 00:05 JEH VER/ARN IDCC PN5662 XXXX
12705 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-11-21 06:08 | 2011-11-21 13:34 | 1 | 446 | 4096001 | 446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT ON POLE 6-50 STS BAD 15 KVA 19.9 CALL JIM MULLINS AND HE IS GETTING CREW RELEASED BY CREW 077S05//COD 1// VER/DBM IDCC PN53 XXXX
12706 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-06-10 18:49 | 2011-06-11 02:15 | 1 | 446 | 4287841 | 446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE CKING TROUBLE///BAD CUT OUT NEED 2 MEN MANUAL WILL REQUIRE AND OUTAGE TO CHANGE . PER DUTY SUPV WILL WORK TOMORROW REPLACED CUTOUT AND RESTORED POWER AT 0215 //VER/GAH IDC XXXX
12707 | Pikeville | 3409502 | BURDINE | LEVISA | 2021-08-09 11:41 | 2021-08-09 15:24 | 2 | 223 | 4021691 | 446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | On pole 358-430 Primary Metering we have a broke stirup,Customer has dropped load so i can replace Hottap and screw on stirup..Made repairs and restored at 15:24.
12708 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-08-22 04:54 | 2011-08-22 12:20 | 1 | 446 | 4740621 | 446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK IN THE MORNING--- TRANSFORMER FUSE BLOWN.--- BAD 25KVA-19.9 TRANSFORMER. RELEASED BY CREW 077S04//VER/CRB IDC XXXX
12709 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2018-07-24 23:12 | 2018-07-25 02:55 | 2 | 223 | 4852011 | 446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva, 7200 transformer. Truck to pole. Transformer open at 12:35 Released by crew 078H04/crew on site/FETR 033-/vem/repairs made and all cust restored 0255/please close ticket/thanks/vem//cod 1
12710 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-06-11 06:32 | 2013-06-11 10:15 | 2 | 223 | 4256901 | 446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ROTTEN FUSE LINK AND ALSO A BAD L/A ON THIS POLE SEND TO MR. RAYBURN TO HAVE L/A REPLACED, CUST IS RESTORED AT THIS LOC AT 1015//COD 2//AED CREATED// VER/DBM IDC XXXX
12711 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-10-30 06:33 | 2018-10-30 13:59 | 1 | 446 | 4341351 | 446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 70-3578 bad 7200-25kva, no trk, need 6 wheeler. can open fuse on 3575 to deenergize line. Released by crew 078S07 arrived RM opening line fuse to safly change xfm // NO ADDITIONAL CUST INTERRUPTED/// COD-1 ISO TF 38830070B43578
12712 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2018-01-01 21:42 | 2018-01-02 01:25 | 2 | 223 | 4693881 | 446 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva,7200-120/240, split windings to 120/208 Released by crew 078S07--crew on site--will need to open other 2 xfrms to change--informed cust---opened @ 00:49--changed bad 50 kva xmfr in bank---closed in @ 01:25---volt ck good---tbl tkt comp..rmv
12713 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2022-01-31 15:26 | 2022-01-31 16:55 | 5 | 89 | 4419531 | 445 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Fault on unused UG service blew xfmr fuse. Isolated unused svc and restored customers at 16:55. sh
12714 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-03-12 13:20 | 2008-03-12 20:45 | 1 | 445 | 56570-1 | 445 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308502// BAD XFMR MANUEL RELEASED BY CREW 077S09//VER/CRB IDC XXXX
12715 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-03-08 23:00 | 2017-03-09 00:29 | 5 | 89 | 4539721 | 445 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 1077A326 REPLACED CUTOUT RESTORED POWER AT 00:29 VER/KEP
12716 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-04-07 14:25 | 2022-04-07 21:50 | 1 | 445 | 4737491 | 445 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service nuetral broke midspan.// Released by crew 074S11
12717 | Pikeville | 3413401 | GARRETT | GARRETT | 2020-08-08 09:44 | 2020-08-08 13:29 | 6 | 225 | 4301261 | 445 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout changing.open up line on p-16-31 at 1245.// repairs made and restored @1329
12718 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2022-10-31 07:12 | 2022-10-31 09:40 | 3 | 148 | 4079941 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer fuse out on pole 1038D-235 due to broke cutout.i replaced cutout and got fuse on pole 1038D-235 back in at 09:40
12719 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2011-06-17 11:59 | 2011-06-17 14:27 | 3 | 148 | 4333771 | 444 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BROKEN HOT TAP COD-3 ISO PO 38830021D20399
12720 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-11-18 17:05 | 2015-11-19 00:29 | 1 | 444 | 4464481 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 67-219 BAD CUTOUT NEEDS LARGE BUCKET AND BUCKET TREE CREW TREES ON POLE BAD BOTH POLES FLAGGERS/ROW ISSUE OPENED LINE FUSE 38830067D00218 STILL SAME AMOUNT OF CUSTOMERS/ ---CREW ON SITE---SEND NOTE TO FORESTRY (J BRADSHAW) TO HAVE TREES TRIMMED, WILL NEED CHIPPER FOR CLEANUP--3PH POLE 67-D-218 AND DE XFMR POLE 67D-219---REPAIRED CUTOUT--LF IN ON PL 67D218 AT 00:29/ ISO 38830067D00218/ COD 1/2 LINE FUSES ON POLE 38830067D00218 ONE FEEDING EACH WAY MD DONE EMAIL SENT/ VER/BOW
12721 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-02-11 14:54 | 2008-02-11 16:45 | 4 | 111 | 59926-1 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409301/// FUSE BROKE VER/HFP IDC XXXX
12722 | Hazard | 3311103 | STINNETT | WENDOVER | 2010-11-06 13:56 | 2010-11-06 15:47 | 4 | 111 | 53535-1 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WR#37653107/// XFMR FUSE BLOWNCUT ARRESTOR IN CLEAR. POWER RESTORED. //VER/CRB IDC XXXX
12723 | South Williamson | 3200301 | BELFRY | BELFRY | 2009-08-04 18:55 | 2009-08-04 20:46 | 4 | 111 | 58715-1 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BRAND HATFIELD ( STATION DEPT REPORTS POLE TOP ON FIRE # 1014-A-49 LINE COULD BE HOT.CUTOUT BROKEN DOWN,NEARLY BURNED POLE INTO.RANDALL COMING TO SEE IF REPAIRS R NECESSARYCUTOUT BROKEN DOWN,NEARLY BURNED POLE INTO.RANDALL COMING TO SEE IF REPAIRS R NECESSARY. TOOK XFR OFF-LINE TO CLEAR UP CUTOUTCUTOUT BROKEN DOWN,NEARLY BURNED POLE INTO.RANDALL COMING TO SEE IF REPAIRS R NECESSARY. TOOK XFR OFF-LINE TO CLEAR UP CUTOUT RELEASED BY CREW 074S06/// COD-8 L3/HFP IDC XXXX
12724 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-12-01 15:30 | 2014-12-01 17:21 | 4 | 111 | 4822381 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHANGING.CHG OUT CUTOUT RE FUSED 38830876C00263 VER/CRB
12725 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-10-12 15:44 | 2013-10-12 17:35 | 4 | 111 | 4932421 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP APPEARS TO HAVE FALLEN OFF// WILL REPAIR// SOMEONE HAS BEEN CUTTING BRUSH WITH A BUSHHOG AND APPEARED TO HAVE HIT THE POLE KNOCKING OFF THE HOT TAP// POWER IS RESTORED VER/CRB L/3 CRB
12726 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2016-06-29 17:15 | 2016-06-29 19:43 | 3 | 148 | 4503941 | 444 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SHE CALLED IN AND SAID SHE THOUGHT THE NEIGHBORS WERE STEALING POWER. COULD NOT LOCATE EXACT RESIDENCE. I CHECKED THE FIRST DUPLEX AS YOU ENTER NUMBER 6 HOLLOW. BOT METERS HAVE A FORT KNOX LOCK ON THEM. DID NOT SEE ANYTHING SUSPICIOUS. NOT SURE IF THIS IS THE CORRRECT PALCE. I TRIED TO CALL MS. BLANKENSHIP SEVERAL TIMES BUT NEVER DID GET AN ANSWER. SQUEEZE ON BURNT INTO AT POLE 381-299. OPENED AT 19:35 CLOSED AT 19:43 COD-3 ISO TF 37830381C00299 VER/HFP L3/HFP
12727 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-08-03 07:32 | 2022-08-03 10:00 | 3 | 148 | 4667081 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | wire had come loose from hot line clamp, power restored
12728 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-02-18 12:13 | 2022-02-18 15:55 | 2 | 222 | 4511401 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on 228/143 will need big bucket send to C.Williams Released by crew 077S03bad cutout.replaced c/o
12729 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2015-01-26 14:25 | 2015-01-26 18:07 | 2 | 222 | 4965281 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIKE LIFTED HOT TAP AT 1425 COD 2//POLE 39831147A00801 HT LIFTED TO 1147 A 992 RELEASED BY CREW 078H12/CREW LOADING MATERIAL/FOREMAN ON SITE/FETR1900/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1807/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
12730 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-12-20 06:30 | 2013-12-20 08:21 | 4 | 111 | 4178221 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT ON POLE 1108-621 FUSE PULL INTO//COD 4 PER SERVICER// VER/DBM L3/HFP
12731 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-09-01 09:59 | 2018-09-01 11:50 | 4 | 111 | 4028941 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | I patroled and refused the line L3/HFP
12732 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-09-17 23:15 | 2012-09-18 00:09 | 9 | 54 | 4055711 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN AND CAUGHT POLE 98-590 ON FIRE. I OPENED UP LINE FUSE ON 98-585 AT 23:15 SO I CAN PUT POLE FIRE OUT. I PUT FIRE OUT AND CUT A LOOP ON POLE 98-586 TO ISOLATE 98-590. I CLOSED LINE FUSE IN AT 98-585 AT 00:03. THIS GOT EVERYONE ON BUT A CHURCH AND A DD LIGHT. WE CAN FIX THIS TOMORROW. EMAIL TO TIM HALL. RELEASED BY CREW 074S01//WILL BE WORKED ON OPS ORDER///VER/CRB L/3 CRB IDC XXXX
12733 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-06-30 23:57 | 2015-07-01 02:25 | 3 | 148 | 4702181 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON ONE OF THEIR PRI. METERINGS HAS BROKEN. I CHANGED CUTOUT
12734 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-10-23 18:33 | 2020-10-23 20:24 | 4 | 111 | 4579341 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans fuse is blown 37820098C00576Going to refuse and try .Fuse had broke in Trans cutout replaced and restored at 20:24. (4 CC)
12735 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-04-08 12:52 | 2008-04-08 15:20 | 3 | 148 | 65201-1 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION IS BURNED UP ON TRANS. POLE. I AM GOING TO CLIMB POLE AND REPLACE CONNECTION. I CHANGED CONNECTION. VER/HFP IDCC CNT1 XXXX
12736 | Pikeville | 3451201 | BEEFHIDE | BEEFHIDE | 2018-05-03 20:42 | 2018-05-04 04:06 | 1 | 444 | 4304401 | 444 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | FAILED PHASE 2 34KV BUS ARRESTOR /// VERIFIED TIMES PER SCADA & DOL = L3/HFP
12737 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2022-01-13 15:17 | 2022-01-13 17:45 | 3 | 148 | 4344391 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | no crew required replaced door
12738 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-04-25 09:02 | 2021-04-25 11:30 | 3 | 148 | 4478121 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connections at service// Repairs made and restored @ 11:30
12739 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-05-27 16:16 | 2011-05-27 17:30 | 6 | 74 | 4196601 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 40152158 //PRT ON SITE//REPLACED 15KVA WITH 25KVA ALL POWER RESTORED P TOLLIVER AT 17:30/// COD-6 ISO TF 39831147A00402 VER/HFP L3/HFP IDC XXXX
12740 | Pikeville | 3402002 | KEYSER | STONECOAL | 2012-02-26 16:27 | 2012-02-26 18:55 | 3 | 148 | 4509121 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 LINE CUTOUT HAS BROKEN INTO ON POLE 1152-196. THIS POLE IS IN A FENCED ARE AT A LOCAL BUSINESS. I CALLED AND THEY ARE TRYING TO FIND SOMEONE TO COME AND OPEN GATE. I WILL CHANGE CUTOUT WHEN I CAN GET TO POLE. I CHANGED CUTOUT AND RESTORED POWER AT 18:55. COD-3 ISO LF 38831152000196 VER/HFP L3/HFP IDCC TON1857 XXXX
12741 | Hazard | 3310502 | HADDIX | CANOE | 2011-01-09 17:18 | 2011-01-09 21:00 | 2 | 222 | 60214-1 | 444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE OUT BROKE CUTOUT ON TRANSFORMER VER/TOM IDC XXXX
12742 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-11-03 09:08 | 2018-11-03 15:09 | 2 | 361 | 4359441 | 443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Line fuse blown on pole 215-502 /// Bad 15 kv 19.9 xfm/// got line fuse back in @ 10:30 but xfm on pole215-502 is bad/// may be able to get truck through bottom /// Released by crew 074S02 xfmr replaced on at 15:09 d sammons L3/HFP
12743 | Hazard | 3303901 | LESLIE | HYDEN | 2020-07-25 09:02 | 2020-07-25 16:25 | 1 | 443 | 4230611 | 443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRANSFORMER 7200 /NEED CUTOUT AND BRACKET.comp
12744 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-10-10 17:58 | 2014-10-11 01:21 | 1 | 443 | 4603721 | 443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE HOT LEG OUT, WILL CLIMB POLE AND CHECK AT XFMR/ GOT OIL LEAKING// 4 MAN CREW // RANDY SAYS 15KVA IS ALL HE THINKS HAZARD HAS RIGHT NOW MAPS SHOW 5KVA// NO TRUCK ACCESS// TRANSFORMER IS STILL HOT/ NEED TRANSFORMER TIME OFF-ON TIMESONE HOT LEG OUT, WILL CLIMB POLE AND CHECK AT XFMR/ GOT OIL LEAKING// 4 MAN CREW // RANDY SAYS 15KVA IS ALL HE THINKS / NO TRUCK ACCESS// TRANSFORMER IS STILL HOT CHANGED TRANSFORMER OPENED AT 1100 AND CLOSED BACK IN AT 0121 VER/SEF
12745 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-04-08 17:07 | 2011-04-09 00:30 | 1 | 443 | 51948-1 | 443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39501766 // BAD CUTOUT 6T XFORM. POWER RESTORED 00:30 //VER/GAH IDC XXXX
12746 | Hazard | 3303901 | LESLIE | HYDEN | 2014-10-07 03:52 | 2014-10-07 11:15 | 1 | 443 | 4562251 | 443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT COD-1 ISO TF 37830267000132 VER/HFP L3/HFP
12747 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-05-31 08:16 | 2009-05-31 15:39 | 1 | 443 | 53107-1 | 443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3103101// SERVICER ENROUTE/CREW REQUIRED BAD 25 KVA NO TRUCKS/MAYBE TRACK BUCKET/SEND TO MULLINS RELEASED BY CREW 078S03/CREW GETTING TRACK BUCKET ON SITE/FETR1700/VEM/REPAIRS MADE /CUST RESTORED 1539/PLEASE CLOSE TICKET/THANKS/VEM//COD 1// VER/DBM IDC XXXX
12748 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-10-08 16:04 | 2008-10-08 16:38 | 13 | 34 | 54298-1 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | GOT BAD NETURAL IN SEC PEDESTAL, GOT JEFF COMBS CREW COMMING TO HELP OPEN TRANSFORMER AT 1604 AND CLOSED IT AT 1638//3308002//VER/CRB IDCC TOF1215, CNT1 XXXX
12749 | Hazard | 3303901 | LESLIE | HYDEN | 2009-04-29 12:52 | 2009-04-29 20:14 | 1 | 442 | 58360-1 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303901//ISOLATED POLE FIRE BY LIFTING TAP ON POLE 37830290000018//CREW ON THE WAY WITH POLE//COD 1//ISOCREW ON THE WAY WITH POLE POLE 290 18 HAS A10T FUSE ON IT MD FILED COD-1 VER/KEP L3/KEP IDC XXXX
12750 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-06-27 08:59 | 2009-06-27 16:21 | 1 | 442 | 64435-1 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED SEND TO MULLINS BAD 25 KVA TRUCKS OK 4 WHEEL DRIVE BUCKET MATERIAL HANDLER RELEASED BY CREW 078S03 WR 30493555CREW REQUIRED SEND TO MULLINS BAD 25 KVA TRUCKS OK 4 WHEEL DRIVE BUCKET MATERIAL HANDLER RELEASED BY CREW 078S03/CREW ON SITE/FETR1715/VEMCREW REQUIRED SEND TO MULLINS BAD 25 KVA TRUCKS OK 4 WHEEL DRIVE BUCKET MATERIAL HANDLER RELEASED BY CREW 078S03/CREW ON SITE/FETR1715/VEM/POWER RESTORED 1621/PLEASE CLOSE TICKET/VEM
12751 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-04-02 16:17 | 2010-04-02 19:58 | 2 | 221 | 57600-1 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER; CREW REQUIRED; NEED 10KVA 19.9 TRANSFORMER; ARRESTER, CUTOUT AND BRACKET; TRUCK ACCESSABLE; RELEASE TO LINE CREW RELEASED BY CREW 078S12 //VER/GAH IDCC PN269 XXXX
12752 | Hazard | 3309302 | VICCO | JEFF | 2010-05-15 06:39 | 2010-05-15 14:01 | 1 | 442 | 62665-1 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309302//19.9 CUTOUT BAD AT POLE 37830323C30057 PHASE CLOSEST TO STATION IS BAD WONT STAY IN //DAMAGED AT TOP OF CUTOUT //..ON SITE PREPAIRING TO WORK. P.HICKS...C/O REPLACED AND ALL POWER RESTORED @ 14:01 HRS. P.HICKS//COD 1// VER/DBM IDCC PN157 XXXX
12753 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-08-24 11:49 | 2021-08-24 15:30 | 2 | 221 | 4144081 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout on pole 148-116. restored power at 15:30 Released by crew 077S10
12754 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-03-13 21:09 | 2013-03-14 00:50 | 2 | 221 | 4904821 | 442 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER REPLACED TRANSFORMER SERVICE CONNECTIONS VER/KEP IDC XXXX
12755 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-07-02 18:46 | 2018-07-02 22:27 | 2 | 221 | 4709791 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200 25kvA on 165-155/ line crew required/ truck ok/ xfmr fuse has been refused/ MLH Released by crew 078H08/crew on site/FETR 2300/vem/repairs complete all cust restored 2227/please close ticket/thanks/vem
12756 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2009-08-20 16:29 | 2009-08-20 20:10 | 2 | 221 | 56806-1 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 31335278 // NEED 50 KVA TRANFORMER AND NEW RISERS--MATERIAL HANDLER OK--L MCCARTY TO WORK RELEASED BY CREW 078S07//INSIDE FAIR GROUNDS XFR RISER NOT MADE UP TO PRIMARY NEUTRAL//COD 2// VER/DBM IDCC PN358 XXXX
12757 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-05-06 12:47 | 2022-05-06 16:28 | 2 | 221 | 4845151 | 442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B and C phase LF blown on 1126-C-537// bad dead end insulator on 1126-C-511// will have to open A phase when big bucket gets here to safely make repairs
12758 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2017-08-23 13:34 | 2017-08-23 17:15 | 2 | 221 | 4293441 | 442 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER NO ANSWER POLE 21-2058 6T TRANS FUSE OUT/ ISO 38830021B12058/ COD 2/ VER/BOW
12759 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2021-11-12 17:51 | 2021-11-12 18:40 | 9 | 49 | 4086841 | 441 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Repaired bad connection @ pole
12760 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-07-13 13:33 | 2012-07-13 14:22 | 9 | 49 | 4712861 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT 115-169,,, CHANGED CUTOUT ON POLE 115610 ONLY THING SEEN DAMAGED, CLSED IN AT 1622, HOLDING//COD 9 //
12761 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-04-11 18:33 | 2016-04-11 21:00 | 3 | 147 | 4082091 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT DOOR BURNT UP REPLACED DOOR RESTORED POWER AT 21:00 VER/CRB
12762 | Hazard | 3303901 | LESLIE | HYDEN | 2021-08-17 17:33 | 2021-08-17 20:00 | 3 | 147 | 4088911 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT
12763 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-03-05 14:46 | 2016-03-05 15:35 | 9 | 49 | 4819781 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RESTORED VER/KEP
12764 | Hazard | 3303902 | LESLIE | WOOTON | 2008-03-07 07:48 | 2008-03-07 10:15 | 3 | 147 | 54466-1 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303902//REPLACED BAD CUTOUT VER/KEP IDC XXXX
12765 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-03-09 12:18 | 2015-03-09 14:45 | 3 | 147 | 4172291 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | POLE 67 C 64 1/0 LASH SEC. & #2 AL. NEUT DAMAGED, RISER BURNT OFF @ XMFER. LINE CREW, NO TRK CREW ON SITE,,REPAIRS MADE,,REMOVE LASH,,ALL POWER RESTORED/ ISO 38830067C00064/ COD 3/ VER/BOW
12766 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-11-05 05:36 | 2010-11-05 08:03 | 3 | 147 | 53061-1 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#37639350//FAILED CUTOUT//VER/CRB IDC NOT SURE WHEN POWER ACTUALLY WENT OUT LEFT AS IS XXXX
12767 | Hazard | 3309003 | JEFF | VIPER | 2019-06-01 09:07 | 2019-06-01 11:34 | 3 | 147 | 4406171 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate brunt up changsd gate power ok
12768 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-06-28 08:54 | 2010-06-28 16:15 | 1 | 441 | 58795-1 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 93-389 TRUCK TO POLE. RELEASED BY CREW 078S01/CREW ON SITE J. HEMLEPP O78H05/CUTOUT CHANGED CUST RESTORED @ 16:15 J. HEMLEPP//COD 1// VER/DBM IDC XXXX
12769 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2014-11-17 09:07 | 2014-11-17 10:10 | 7 | 63 | 4734321 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP ON POLE 38820966A30629. GOING TO TRY AND REPLACE THE DOOR. REPLACED CUTOUT AND POWER IS BACK ON//COD 6 +1 MAP DESPREANCY// VER/ ADH L3/DKG MAP DISCREPANCY ENTERED BY DISPATCHER
12770 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-02-15 12:57 | 2020-02-15 15:24 | 3 | 147 | 4408581 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 19.9 cutout repairs mae and power restored at 1524
12771 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-02-25 08:33 | 2012-02-25 11:00 | 3 | 147 | 4503351 | 441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | TIE WIRE BROKE AND PHASE WIRE JUMPED OFF INSULATOR AND SLAPPED NEUTRAL, BLOWING FUSE LINE FUSE ON POLE 145-38. I AM GOING TO TIE PHASE WIRE BACK TO INSULATOR AND REFUSE LINE FUSE. COD-3 ISO LF 37820145000038 VER/HFP L3/HFP IDC XXXX
12772 | Paintsville | 3401102 | FALCON | SALYERSVI | 2021-08-07 12:20 | 2021-08-07 14:10 | 4 | 110 | 4014731 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke cutout on pole 875-A-285,Going to make repairs and restored at 14:10.
12773 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-05-11 12:10 | 2008-05-11 19:30 | 1 | 440 | 60831-1 | 440 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3410502SERVICE CONNECTION BURN=INTO//VER/CRB IDC XXXX
12774 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-06-16 19:55 | 2022-06-16 21:45 | 4 | 110 | 4142541 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans open at 99-11,Will be trying to get back in..Fuse had broke in Trans cutout restored at 21:45..
12775 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-11-15 22:02 | 2021-11-15 23:30 | 5 | 88 | 4096871 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse brokein line cutout
12776 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-04-16 20:35 | 2022-04-16 20:43 | 55 | 8 | 4770311 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | Emergency outage to bypass regulator//123V Ph-G/DOL 1198711Released by crew 077S05
12777 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-09-01 13:55 | 2014-09-01 14:50 | 8 | 55 | 4444011 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 45-1043 6T TRANS. FUSE BROKE/// TRANSFORMER WAS OUT ON POLE 38830045A31043 NOT THE FUSE. CUSTOMER MUST HAVE BEEN MISMAPPED// VER/BOW VER/DKG L3/DKG
12778 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2020-03-02 13:05 | 2020-03-02 16:45 | 2 | 220 | 4444331 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout failed on 1111--C-182.i replaced cutout,restored power at 16:45 one customer mismapped // MD made
12779 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-03-14 14:13 | 2016-03-14 14:57 | 10 | 44 | 4841931 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 188-311 35/5 ROTTEN AT GROUND . NEED LINE CREW AND TECH,, DOG NO TRUCKS TO POLE. RELEASED BY CREW 078S01--CREW ON SITE--REPLACED POLE 40CL5---INSTALLED 50T LF ON POLE 188-147----TIME OFF AT 14:13--TIME ON AT 14:57---TBL TKT COMP RELEASED BY CREW 078H16/ ISO 38830188A00147/ COD 10/ VER/BOW
12780 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-01-30 17:12 | 2015-01-30 20:52 | 2 | 220 | 4976321 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074H17/// BAD 15 KVA 19.9 TRANSFORMER @ POLE 37830167B00369 NEED 1 MAN///// COD 2//MIS-MAPPED CUST MADE MDC//RELEASED BY CREW 074H17/// BAD 15 KVA 19.9 TRANSFORMER @ POLE 37830167B00369 NEED 1 MAN///// COD 3// CHANGED BAD TRANSFORMER AND RESTORED SERVICE @ 20:52 //// ONLY 2 CUSTOMERS AFFECTED VER/CRB
12781 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-04-04 22:30 | 2012-04-04 23:10 | 11 | 40 | 4648501 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW OPENED FUSE TO SAFELY REPLACE BAD TRANSFORMER ON ORDER 4647161 IDC XXXX
12782 | Hazard | 3302704 | HAZARD | KENMONT | 2014-04-04 09:10 | 2014-04-04 11:00 | 4 | 110 | H4571051 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER AFTER HOURS GUIDE LINES THIS TROUBLE WILL BE CHECKED ASAP 04/04/14 === STEPDOWN TRANSF BAD ===- 333 KVA STEPDOWN BAD === NEED LINE CREW AND FLAGERS AND 333 KVA STEPDOWN //ONLY CENTER PHASE OPEN//OPENED OTHER 2 PHASES @ 0901//COD 3 + 43// IDCC DUP TO OPEN OTHER PHASES XXXX
12783 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-08-09 10:20 | 2014-08-09 14:00 | 2 | 220 | 4346601 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 550-162 PATROLLING LINE, FOUND BAD CUTOUT ON 549-72 NO TRUCKS TO POLE, LINECREW REQUIRED ISOLATED GROUNDED&TAGGED TO V MULLINS ON 549-162. RELEASED BY CREW 078S11// PWR RESTORED @ 14:00 PLEASE CLOSE TICKET LRM// COD 2 ISO POLE 38830549D40162// VER/ ADH
12784 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2022-12-25 04:52 | 2022-12-25 06:20 | 5 | 88 | 4353171 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse burned out on 1110C-110..back in at 06:20
12785 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2008-06-02 21:26 | 2008-06-02 22:54 | 5 | 88 | 54737-1 | 440 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | POLE HARDWARE | CC428//STATION OUT DUE TO LOVELY/WOLF CRK CKT OUT. VER/CWH L3/CWH IDC XXXX
12786 | Hazard | 3303902 | LESLIE | WOOTON | 2013-02-02 19:54 | 2013-02-02 21:22 | 5 | 88 | H4787191 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE WIRE BURN,T INTO LAYING IN CREEK WILL OPEN XFMR AND SPLICE SERVICE AND TRY TO GET IT ACROSS CRK//// XFMR OPENED 19:54 CLOSED 21:22. RE-PULLED SERVICE POWER RESTORED. COD-6 VER/KEP IDC XXXX
12787 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2010-05-11 18:02 | 2010-05-11 18:42 | 11 | 40 | 59645-1 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 35070045 // LOOKS LIKE BAD CUTOUT SEND TO VERNON M. RELEASED BY CREW 078S08/CREW ON SITE/WILL OUTAGE XFMR BANK AT 1800/30 MIN OUTAGE/REPLACE CO &LA/REMOVE ARMS/VEM COD-11 VER/HFP L3/HFP IDC XXXX
12788 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-11-12 15:20 | 2012-11-12 16:00 | 11 | 40 | 4387571 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, OPENED LINE AT 15:20, REPLACED CUTOUT, POWER RESTORED AT 16:00 HRS//COD 11// VER/DBM IDCC CDC92 XXXX
12789 | Hazard | 3303902 | LESLIE | WOOTON | 2018-06-10 03:53 | 2018-06-10 07:33 | 2 | 220 | 4575091 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrester on pole 414-33 line fuse out on pole 414-32
12790 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-12-26 14:10 | 2018-12-26 16:00 | 4 | 110 | 4599581 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required burnt fuse L3/HFP
12791 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-02-24 08:15 | 2017-02-24 10:05 | 4 | 110 | 4418031 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ***SEE 4417301***/ OPENING LINE FUSE TO PUT WIRE BACK UP/ ISO 37830173B00217/ COD 4/ 0815 TO 1005/ VER/BOW L3/HFP XXXHFP
12792 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-01-28 14:45 | 2013-01-28 15:05 | 22 | 20 | 4747751 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE ON POLE 39831099D16009 AT 14:45 TO MAKE REPAIRS ///VER/CRB L/3 CRB IDC XXXX
12793 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2011-04-26 09:30 | 2011-04-26 10:10 | 11 | 40 | 65333-1 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED RECLOSER TO MAKE UP LOOPS ON ORDER 65071-1 VER/KEP IDC XXXX
12794 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2016-04-23 04:45 | 2016-04-23 06:35 | 4 | 110 | 4118801 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT DOOR REPLACED DOOR FUSED UP EVERYTHING OK VER/KEP
12795 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-10-19 14:10 | 2011-10-19 16:00 | 4 | 110 | 4999261 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT..BURNING POLE..J REED LIFTED HOT LINE CLAMP @ 14:30..WILL EXTINGUISH FIRE & REPLACE CUTOUT..//.REPLACED CUTOUT...BAYONETTED POLE..ALL CUSTS RESTORED @ 16:00//COD 4// VER/DBM IDC XXXX
12796 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-03-07 10:55 | 2015-03-07 11:15 | 22 | 20 | 4142861 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY BROKEN AND POLE LEANING POLE #211-84. IS OLD GUY GOING TO NEED TO REPLACE. POLE IS A 1947 MODEL LOOKS OK IT IS NOT BROKEN A 405, NEED TO REPLACE GUY CAN REACH TOP OF POLE WITH A BUCKET B. . NO POWER OUT. NEED BUCKET TRUCK CANNOT CLIMB POLE . P.THOVSON,,POLE STRAIGHT,,DOES NOT NEED CHANGED,,OPENED 211-73 AT 10:55..CLOSED AT 11:15,,,CLOSE TICKET RELEASED BY CREW 078H03/ COD 22// VER/ ADH AJB
12797 | Hazard | 3302703 | HAZARD | HAZARD | 2009-12-01 14:47 | 2009-12-01 16:15 | 5 | 88 | 54201-1 | 440 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LEAD BURNT INTO ON XFMR///// SPLICED LEAD POWER RESTORED//COD 5// VER/DBM IDC XXXX
12798 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-10-01 08:25 | 2011-10-01 10:15 | 4 | 110 | 4936941 | 440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I REMOVED HOT LINE CLAMP ON B PHASE AT 08:25 AT POLE 117-85 DUE TO B PHASE BEING BURNT OUT OF HOT LINE CLAMP AND FELL DOWN ON TRANSFORMER RISER AND BURNING. I HAVE CREW ON THE WAY. WE HAVE REPAIRS MADE. SEND COPY TO ROW PIKEVILLE EVERYTHING NEEDS CUT FROM POLE 117-85 TO END OF LINE SINGLE PHASE FROM FUSE POLE 118-26 IS COVERED UP NEEDS CUT BAD. COD-4 ISO PO 37830117000085 VER/HFP L3/HFP IDC XXXX
12799 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-03-10 11:23 | 2008-03-10 18:42 | 1 | 439 | 55873-1 | 439 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | CABLE CONNECTOR BURNT INTO CUST HAD PART POWER.//3403201//VER/CRB IDC XXXX
12800 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-05-13 11:56 | 2011-05-13 19:15 | 1 | 439 | 4083251 | 439 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA XFMR, CREW IN ROUTE. XFMR CHANGED VER/HFP L3/HFP
12801 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2011-10-12 08:16 | 2011-10-12 11:55 | 2 | 219 | 4969191 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CONNECTED LOAD TO TRANSFORMER AT POLE 37830212A00100 TEMPORARILY, ON AT 11:55 . OPENED AT 14:25 AND RESTORED AT 14:45 , REPLACED 25KVA TRANSFORMER WITH SAME AND REPLACED 4/3 SD WITH 2/3 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 ///VER/CRB IDC XXXX
12802 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2021-05-25 18:15 | 2021-05-25 21:54 | 2 | 219 | 4621701 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT,WILL RE-FUSE//////////XFR IS BAD,WILL REPLACE IT//////NEED A 25KVA,7.2.CAN USE MAT HANDLER&AN A LINEMAN////////REPLACED XFR,RESTORED@21:54 // cod 2
12803 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2020-04-11 10:39 | 2020-04-11 13:05 | 3 | 146 | 4620891 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required ,,,replace xfr cutout ,,no truck Released by crew 078S05,repairs made all cust restored @ 1305 please close ticket thanks.bt
12804 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-08-24 23:50 | 2011-08-25 01:03 | 6 | 73 | 4753671 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE IDCC PN12 XXXX
12805 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-09-29 19:19 | 2013-09-29 21:45 | 3 | 146 | 4897331 | 438 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICEDROP HOTLEG AND NEUTRAL BURNT INTO, APR CLOSE TICKET IDC XXXX
12806 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-06-25 15:10 | 2021-06-25 22:28 | 1 | 438 | 4807031 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, GROUNDING | 136-38 crew required , bad 25 kva xfr ,service truck material handler to pole Released by crew 078S05. xfr changed and back on at 22:28//cod 1
12807 | Hazard | 3309302 | VICCO | JEFF | 2017-11-19 00:54 | 2017-11-19 08:12 | 1 | 438 | 4578051 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | customers service laying on roof, wire damaged at weatherhead, advised customer to turn off main breaker untill repairs are made,,he turned breaker off, will require servicer,,jdm Released by crew 077E01 repaired serv neut === hot connection got into the neut of serv === repaired neut === power ok
12808 | Hazard | 3303902 | LESLIE | WOOTON | 2009-05-04 01:46 | 2009-05-04 05:25 | 2 | 219 | 64807-1 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE #389-308...CLOSED LINE FUSE IN AT 03;50.....REPLACED CUTOUT RESTORED POWER AT 05:25 VER/ARN
12809 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-07-26 16:30 | 2009-07-26 23:48 | 1 | 438 | 53393-1 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ,,,BAD TRANSFORMER,, 7200 VOLT 25KVA TRANSFORMER BIG TRUCK CAN REACH POLE ,,,CREW MAY WANT TO BACK THERE BIG BUCKET UP DRIVEWAY THERE IS NOT MUCH ROOM TO TURN AROUND UP THERE. RELEASED BY CREW 078S02 VER/TOM L3/TOM IDC XXXX
12810 | Hazard | 3303901 | LESLIE | HYDEN | 2009-03-11 08:22 | 2009-03-11 15:40 | 1 | 438 | 57141-1 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28879410 // BAD LEAKING XFMR 37830242000094 COD-1 CREW WILL CHANGE OUT 5KVA RELEASED BY CREW 077S01 L3/HFP IDC XXXX
12811 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-10-02 13:46 | 2016-10-02 17:25 | 2 | 219 | 4954591 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAD XFMR OUT THIS MORNING . XFMR BACK OUT . BAD XFMR . NEED 4 MAN LINE CREW & ROW CREW . RELEASED BY CREW 075H04/ ISO 37830223B00042/ COD 2/ VER/BOW L3/HFP XXXHFP
12812 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2019-05-03 16:17 | 2019-05-03 17:30 | 6 | 73 | 4211801 | 438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Found and replacing bad cutout on 38830453D40440. Found and replacing bad cutout on 38830477000148.//REPLACED L/F AND TRANSFORMER CUTOUT L3/HFP
12813 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-08-13 21:43 | 2008-08-14 05:00 | 1 | 437 | 51863-1 | 437 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3001002 CREW REQUIRED SEND TO FRALEY BAD 5 KVA NO TRUCKS RELEASED BY CREW 078S03 VER/JHM IDC XXXX
12814 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2013-02-03 11:46 | 2013-02-03 12:11 | 29 | 25 | 4787831 | 437 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT POLE#45-1717/WILL NEED TO OPEN LINE FUSE ON POLE# 45-4665 TO ISOLATE CUTOUT/FETR FOR CUST ON LINE FUSE 1200/FETR FOR CUST FED FROM XFMR ON 45-1717 1300/VEM/LINE FUSE OPEN AT 1146/LINE FUSE BACK IN AT 1155/XFMR CUTOUT CHANGED AND POWER RESTORED TO REMAINING 11 CUST 1211/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB L/3 CRB IDCC PN1717 XXXX
12815 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-08-03 19:41 | 2014-08-03 21:30 | 4 | 109 | 4328211 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT ON BANK OF 2 TRANSFORMERS BROKE DOWN. IT BLEW FUSE ON SECOND TRANS. ALSO. I WILL NEED ONE MAN AND BIG BUCKET TRUCK TO CHANGE TRANS. ERIC HAS CUTOUT CHANGED.. VER/KEP
12816 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2015-07-08 19:31 | 2015-07-08 21:20 | 4 | 109 | 4747881 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT IS BROKEN ON POLE 1151-724. I AM GOING TO CHANGE CUTOUT/ ISO 38831151C00724/ COD 4/ VER/BOW
12817 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-01-13 22:56 | 2008-01-14 00:45 | 4 | 109 | 56473-1 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401103/CHG CUTOUT.../COD-4 / VER/LDA IDC XXXX
12818 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-01-03 20:41 | 2012-01-03 22:30 | 4 | 109 | 4230651 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN. COD-4 ISO TF 38830737000024 VER/HFP L3/HFP IDC XXXX
12819 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-09-17 08:22 | 2020-09-17 12:00 | 2 | 218 | 4470661 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required.failed19.9 cutout on 746-D1-85,nta.need 19.9 cutout and standoff bracket. Released by crew 079S03//all repairs made power restored at 12:00
12820 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-12-28 15:52 | 2016-12-28 17:41 | 4 | 109 | 4246511 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT// CHANGED CUTOUT POWER RESTORED 1741// COMPLETE TT 38830901000011 VER/AWD
12821 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-12-17 18:56 | 2012-12-17 20:45 | 4 | 109 | 4476311 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE, WILL NEED TO CHANGE//// REPLACED CUTOUT, POWER RESTORED// COD 4 // VER/DBM
12822 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-09-19 13:51 | 2012-09-19 17:29 | 2 | 218 | 4069451 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 15KVA 7200 TRANSFORMER (POWER RESTORED AT 17:29) ///VER/CRB L/3 CRB IDC XXXX
12823 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-10-09 20:13 | 2012-10-09 23:51 | 2 | 218 | 4127331 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD SEC. UNDERGROUND NEED TWO TEMP.SEND TO VERNON M. RELEASED BY CREW 078S08/CREW ON SITE/INSTALLING TEMP XFMRS/FETR0030/VEM/INSTALLED TWO TEMP XFMRS AT LOT 27&28/CUST HAVE FULL POWER 2351/UG BAD FROM XFMR 140-587 TO PED 140-626/4/0SEC/ISOLATED BAD LEG IN 140-626/PLEASE COPY L RAYBURN/VEM VER/KEP IDC XXXX
12824 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2019-12-03 09:22 | 2019-12-03 13:00 | 2 | 218 | 4119081 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BURNED UP,WILL REPLACE IT WITH POLYMER TYPE/////////REPLACED&RESTORED POWER
12825 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-05-09 11:57 | 2008-05-09 15:35 | 2 | 218 | 59106-1 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3311101 / BAD TRANSFORMER - NEED CONV TR, 7200V CUTOUT AND BRACKET, MATERIAL TRUCK. TRUCK ACCESSABLE BUT WILL NEED FLAGMEN. COD-2 VER/LDA IDC XXXX
12826 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-01-03 17:47 | 2014-01-03 21:25 | 2 | 218 | 4225861 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 10KVA CSP NEED 15KVA TRUCKS OK WORK FROM DRIVEWAY/POLE 181C52/SEND TO REYNOLDS RELEASED BY CREW 078S03//COD 2// VER/DBM
12827 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-03-29 08:09 | 2021-03-29 09:58 | 4 | 109 | 4397751 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Broken fuse feeding a 100KVA on pole 203-22. Power restored at 9:58.
12828 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-05-11 14:09 | 2013-05-11 15:58 | 4 | 109 | 4104501 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUT-OUT ON POLE 472-48 POLE IS MANUAL, WILL NEED ONE MAN TO HELP CLEAR UP CUT-OUT AND REPLACE. RESTORED POWER AT 15:58. 5/11/13. J.S.B. COD-4 ISO TF 37830472000048 VER/HFP L3/HFP IDC XXXX
12829 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-11-12 09:46 | 2013-11-12 11:35 | 4 | 109 | 4031141 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 172-167. BAD CUTOUT ON POLE 172-516. CLEARED CUTOUT UP , XFMR DOSE NOT SERVE ANYTHING , LEFT OF LINE. CLOSED CUTOUT @ 11:35. VER/SEF L3/HFP
12830 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-11-11 08:03 | 2018-11-11 11:41 | 2 | 218 | 4388371 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL HAVE TO ISOLATE UG SERVICE&RE-FUSE UG XFR,NEED 1MAN&UG XFR FUSE//BAD fuse THAT IS NOT ON THE MAP//SENT TO CLIFF FREEMAN TO HAVE A TECH TO GO OUT AND WRITE THIS INFO UP//the new transformer is next to 37830047A00360//cod 2 L3/HFP
12831 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2015-02-21 11:52 | 2015-02-21 15:30 | 2 | 218 | 4063361 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. GOING IN TO PAINTSVILLE SERVICE CENTER TO GET A CUTOUT. REPLACED CUTOUT AND RESTORED @ 15:30. SH//COD 2// VER/DBM
12832 | Whitesburg | 3314401 | MAYKING | ERMINE | 2016-07-03 13:00 | 2016-07-03 14:49 | 4 | 109 | 4518171 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 37830449D10089. BAD CUTOUT ON POLE 449-89, OPENED B PHASE LINE FUSE ON POLE 449-92 AT 14:33 TO ISOLATE, REPLACED CUTOUT RESTORED POWER AT 14:49.. VER/AWD
12833 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2012-10-29 16:31 | 2012-10-29 18:20 | 4 | 109 | 4185351 | 436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT POLE 18-20 DUE TO BAD CUTOUT POLE 18-28. NOT ABLE TO GET TRUCK TO I WILL BE CHANGING OUT. I HAVE CUTOUT REPLACED FUSED UP EVERYTHING OK. COD-4 ISO LF 37830018D00020 VER/HFP L3/HFP IDC XXXX
12834 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-12-30 08:33 | 2010-12-30 15:48 | 1 | 435 | 56948-1 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT.....NEW INSTALLATION....DONT SEE REASON WHY....FUSE MAY HAVE JUST BROKEN....WILL RE-FUSE...//...FUSE BLEW.....BAD XFMR.....NEED TO REPLACE A 25KVA 19.9 KV WITH A 50KVA....CUST HAS INCREASED LOAD HERE.....NEED CREW...TALKED TO DAVE SAMMONS & JOEY REED....THEY WITH BOTH CALL DDC....CREW WILL GET TO THIS IN AFTERNOON....THANKS...JRV RELEASED BY CREW 080S01 VER/KEP L3/KEP IDC XXXX
12835 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-01-21 09:13 | 2008-01-21 11:38 | 3 | 145 | 58367-1 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3409301// 15 KVA XFMR BAD. CREW EN-ROUTE TO CHANGE TO 25 KVA.//COD 3//REPLACE 15 KVA WITH 25 KVA TC MILLER//VER/CRB IDC XXXX
12836 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-04-02 22:47 | 2008-04-03 00:14 | 5 | 87 | 63285-1 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3403201 TRANSFORMER FUSE BROKE AT POLE 139C124. THIS 25 KVA HAS 5 CUST ON IT . LINE WORK IS GOING ON IN THIS AREA AT THIS TIME. SEND COPY OF THIS TO RON RYE PIKEVILLE TO CHECK LOAD ON THIS TRANSFORMER. MAY BE A GOOD TIME TO GET IT CHANGED IF NEED BE. VER/JHM IDCC CCU XXXX
12837 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-06-05 07:45 | 2010-06-05 15:00 | 1 | 435 | 57117-1 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830400000056, ISOLATED AT 38830400000055, 1 CUSTOMER OUT, RESTORATION 1 AT 10:00, POLE BURNT IS 45 WITH NO PHONE, SHOULD BE ABLE TO LOWER, BAD ROAD NEED SMALL TRUCK. RELEASED BY CREW 078S05//VER/CRB IDC XXXX
12838 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-11-06 06:20 | 2011-11-06 08:45 | 3 | 145 | 4054651 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | I FOUND A STRAND BROKEN IN THE #2 PRIMARY THAT HAD UNRAVELED AND HAD WELDED ITSELF TO THE NEUTRAL. I CLEARED THIS UP. THIS IS BETWEEN POLE 289-84 AND 289-85. SDB / EMAIL SENT TO TIM HALL FOR FOLLOW UP WORK ON RWS. CC=3. VER/SDB IDC XXXX
12839 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-06-10 20:28 | 2020-06-11 03:43 | 1 | 435 | 4994511 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | burnt up hotleg and nuetrul repairs made and back in at 03:43
12840 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2013-01-21 18:03 | 2013-01-21 19:30 | 5 | 87 | 4723961 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUST. HAD BAD CONNECTION ON XFMR POLE, REMADE ALL CONNECTIONS, POWER RESTORED. ///VER/CRB L/3 CRB IDC XXXX
12841 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-03-11 17:19 | 2020-03-11 19:44 | 3 | 145 | 4469951 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout need 19,9 cutout and arrestor and tee brkt Released by crew 077S05replaced cutout arr, and brkt all power restored @19:44 p.hicks
12842 | Paintsville | 3401102 | FALCON | SALYERSVI | 2021-11-29 08:47 | 2021-11-29 11:12 | 3 | 145 | 4131001 | 435 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection got water inside , froze open,,, replaced 6 connections.
12843 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2013-06-19 08:45 | 2013-06-19 16:00 | 1 | 435 | 4370641 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6T FUSE OUT DUE TO BAD CUTOUT. WILL BE CHANGING OUT. BAD 25KVA TRANSFORMER CAN USE TRUCK. GOT UP WITH DENNIS CREW WILL BE ON THE WAY. RELEASED BY CREW 074S11 VER/KEP IDC XXXX
12844 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-05-12 04:30 | 2008-05-12 11:45 | 1 | 435 | 62353-1 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001203// CROSS ARM BURNT OFF POLE 69-673 HOT TAP OFF POLE 69-588 NEED 6-CUTOUTS CROSS ARM STATION ZONE RELEASED BY CREW 078S08//VER/CRB IDCC IDC TOF0332 XXXX
12845 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2017-01-30 15:31 | 2017-01-30 16:00 | 15 | 29 | 4342701 | 435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ISO 38830046B12136/ COD 15/ 1/0 BURNT INTO/ VER/BOW L3/HFP XXXHFP
12846 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-12-03 05:23 | 2010-12-03 09:00 | 2 | 217 | 62629-1 | 434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT, LOOKED LIKE FUSE JUST BROKE//COD 2// VER/DBM IDC XXXX
12847 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-07-31 11:25 | 2009-07-31 15:02 | 2 | 217 | 65541-1 | 434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT POWER BACK ON RELEASED BY CREW 078S11 VER/PDP IDC XXXX
12848 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-10-01 09:20 | 2011-10-01 12:57 | 2 | 217 | 4937061 | 434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE 38831149000071 BURNED OFF//FUSE AT POLE 1149-24 BLOWN//CREW ON SITE TOP OF POLE 38831149000071 BURNED OFF//FUSE AT POLE 1149-24 BLOWN//CREW ON SITE//REPAIRED DAMAGES//POWER IS RESTORED COD-2 ISO LF 38831149000024 VER/HFP L3/HFP IDC NOT SURE WHEN POWER WENT OUT LEFT AS IS XXXX
12849 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-09-09 20:29 | 2015-09-10 00:06 | 2 | 217 | 4219791 | 434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, NEED LINE CREW, 7200 CUTOUT AND ARRESTOR AND TEE BRACKET. RELEASED BY CREW 077S04 VER/ARN
12850 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-05-25 05:48 | 2021-05-25 09:25 | 2 | 217 | 4618461 | 434 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Dispatched in accordance with KYPCo Late Night Callout Guidelines,,replaced secondary connections ,,complete
12851 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-09-04 06:51 | 2013-09-04 14:05 | 1 | 434 | 4818301 | 434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7.2KV 25KVA, 120/240 CAN READING HIGH VOLTAGE 163/320 3 MAN CREW CAN SET UP IN DRIVE WAY TO CHANGE CAN, METER PULLED, TRANSFORMER FUSE OPENED UP RELEASED BY CREW 078H08///CHANGED OUT XFMR///VOLT CK 123/123/246V/// VER/CRB L/3 CRB IDC XXXX
12852 | Hazard | 3309003 | JEFF | VIPER | 2018-09-03 16:21 | 2018-09-03 23:35 | 1 | 434 | 4038591 | 434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | long span of 1/0 secondary down on pole 417-146. Need 2 men and a bucket, 1/0 wire and splices. power restored at 23:35
12853 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-12-04 18:48 | 2013-12-04 22:25 | 2 | 217 | 4099551 | 434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 15 KVA 19.9 TRANS IS BAD ON POLE 167-296. I AM CALLING FOR HELP. WE CHANGED TRANS. VER/CRB L3/HFP
12854 | Hazard | 3310502 | HADDIX | CANOE | 2022-01-04 11:07 | 2022-01-04 18:20 | 1 | 433 | 4298721 | 433 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout. replaced and restored power 18:20
12855 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-05-07 03:37 | 2015-05-07 10:50 | 1 | 433 | 4399161 | 433 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE SERVICER CHECK AT START OF REGULAR SHIFT//TOM,BROKE CUTOUT NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05 VER/CRB
12856 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2015-07-17 08:17 | 2015-07-17 15:30 | 1 | 433 | 4898531 | 433 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | IDC RISER MISSING NOT SURE WHY
12857 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-02-02 09:32 | 2010-02-02 16:45 | 1 | 433 | 62275-1 | 433 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND PEDESTAL ONLY HAS PARTIAL POWER COMING INTO IT. I AM CHECKING NOW. I MAY NEED HELP. WE PUT IN A TEMP. SERVICE OVERHEAD TO CUSTOMER. WE OPENED TRANS. ON POLE 98-338 AND LEFT IT OPEN UNTIL THEY CAN COME BACK AND FIND TROUBLE. COD-1 VER/KEP L3/KEP IDCC PN338 XXXX
12858 | Whitesburg | 3314401 | MAYKING | ERMINE | 2019-05-05 16:03 | 2019-05-05 18:27 | 3 | 144 | 4227471 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer lug bad on pole 426-382.. replaced lug.. cutout also bad. replacing cutout on 382. open line fuse on 426-294 to replace cutout.. cutout replaced on 426-382.. power restored @ 18:27
12859 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-06-05 17:36 | 2021-06-05 20:00 | 3 | 144 | 4672841 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out broke into , I replaced it
12860 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-05-27 21:03 | 2008-05-27 22:15 | 6 | 72 | 51923-1 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409303//FUSE LINK BROKE. RE-FUSED XFMR. SH VER/HFP IDC XXXX
12861 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2011-07-20 13:39 | 2011-07-20 14:15 | 12 | 36 | 4568221 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LA POLE 46-2333 LINE FUSE OUT 40T 46-2021//SENT MESSAGE TO MR MARTIN ABOUT LINE FUSE COD 12//VER/CRB
12862 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-07-20 17:26 | 2012-07-20 19:50 | 3 | 144 | 4787651 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD XFMR, CALLED FOR CREW. POWER RESTORED COD-3 ISO TF 37830206000183 VER/HFP L3/HFP
12863 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-07-14 11:40 | 2008-07-14 14:04 | 3 | 144 | 52439-1 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501// STS CUTOUT GATE IS BURNED UP , GOING TO SEE IF THE ONE I HAVE WILL WORK, CHANGE GATE ON CUTOUT IDCC CNT1 XXXX
12864 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2017-07-26 14:02 | 2017-07-26 14:50 | 9 | 48 | 4182131 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-2096 30T LINE FUSE BAD TRANS. 45-2262 TOOK LINE FUSE OUT/ ISO 38830045B12096/ COD 9/ VER/BOW
12865 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-05-27 11:39 | 2019-05-27 15:15 | 2 | 216 | 4349431 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Bad arrestor on pole 117-142, got changed out and repairs made @1515.
12866 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2016-03-12 13:13 | 2016-03-12 14:07 | 8 | 54 | 4839081 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 380-27. GOING TO CUT IN THE CLEAR. POWER RESTORED AT 14:07 /// COD-8 ISO TF 37830380A00027 VER/HFP L3/HFP
12867 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-03-16 18:10 | 2014-03-16 18:58 | 9 | 48 | H4497501 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XARM BURNED HALF INTO,MUST HAVE A CUTOUT BRKNG DOWN,NEED BIG BUCKET,1 MAN,3 CUTOUTS W STAND-OFF MOUNTS.WILL GET CUTOUTS OFF ARM & ONTO INSULATED MOUNTS.WILL TAKE OUTAGE WHEN NEEDED//COD 33 (+9 MORE @ 1810 WHEN OPENED 38821105D00150)//ISO 38821105C00082//MADE REPAIRS AND RESTORED RELEASED BY CREW 074S06 IDC DUP TO OPNE SWITCH XXXX
12868 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-06-19 02:38 | 2012-06-19 09:50 | 1 | 432 | 4929891 | 432 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL DISPATCH AT REG WK TIME TODAY.BAD CONN SERV TO FIX.ALL CUST BACK ON PLEASE COMPLET TICKET THANKS.BT ///VER/CRB L/3 CRB IDC XXXX
12869 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2011-01-19 04:49 | 2011-01-19 08:25 | 2 | 216 | 62542-1 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 38494659 // POLE 137-109 BAD CUTOUT//COD 2// VER/DBM IDC XXXX
12870 | Pikeville | 3409502 | BURDINE | LEVISA | 2018-04-01 23:04 | 2018-04-01 23:58 | 8 | 54 | 4163051 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on line fuse /// will make repairs/// Changed bad cutout and closed line fuse in @ 23:58 and restored service
12871 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-08-21 16:21 | 2011-08-21 18:45 | 3 | 144 | 4736521 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 140-113 BAD 25KVA TRUCK TO POLE RIBBON ON POLE RELEASED BY CREW 078S08 COMP. 16:45 M.P. COD-3 ISO TF 38830140C00113 IDC XXXX
12872 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-07-31 17:17 | 2014-07-31 19:05 | 4 | 108 | 4314861 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE OPEN ON 644-28, FOUND BAD ARRESTER ON 644-70 APR AT 1905 CLOSE TICKET COD 4//VER/ ADH
12873 | Hazard | 3308001 | JACKSON | S.JACKSON | 2022-09-06 10:36 | 2022-09-06 13:00 | 3 | 144 | 4845941 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | had bad connections on customers service pole got connections fixed and voltage good to both meter bases.
12874 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-02-24 13:16 | 2014-02-24 13:28 | 36 | 12 | 4430981 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENING RECLOSERS TO REPAIR LOOPS @746-14 OPENED AT 13:16 CLOSED @ 13:28 VER/SEF IDC XXXX
12875 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-08-10 17:28 | 2019-08-10 18:40 | 6 | 72 | 4870071 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout has failed .i will replace. complted
12876 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2015-09-12 19:27 | 2015-09-12 20:15 | 9 | 48 | 4232811 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-1548 BAD CUTOUT DOOR REPAIRED 10T TRANS FUSE/// VER/ ADH L3/DKG TIMES WERE NOT MENTIONED ON VOICE RECORDER
12877 | Pikeville | 3408103 | SALISBURY | MARTIN | 2010-07-23 13:36 | 2010-07-23 16:00 | 3 | 144 | 55986-1 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ACTUAL OUTAGE ON POLE 38831098C00502, FUSE LINK BROKEN ... REFUSED TRANSFORMER, ALL WORK COMPLETE / GXJ VER/KEP L3/KEP IDC XXXX
12878 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-01-09 10:13 | 2014-01-09 11:25 | 6 | 72 | 4264491 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN WIRE SEC. HAS BURNED DOWN// WILL CLEAR SEC. AND REWORK SER. ON 24-75 TO RESTORE ALL CUST// REMOVED 1 SEC. WIRE FROM POLE 24-75 -24-76// POWER IS RESTORED // OPEN WIRE NEEDS TO BE REMOVED FROM 24-74 TO 24-76// SEND TO C. FREEMAN VER/CRB
12879 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-02-26 04:31 | 2010-02-26 06:55 | 3 | 144 | 61152-1 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308602// BAD CUTOUT, ALSO CHECK XFMR CHECKED GOOD..REPLACED CUTOUT RESTORED POWER AT 06:55, ONLY HAD 2 CUSTOMERS OUT OF POWER CCC COD-3 ISO VER/HFP L3/HFP IDC XXXX
12880 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-09-21 09:00 | 2021-09-21 12:36 | 2 | 216 | 4262111 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke Trans Cutout on 215-D-82,This is a Manually pole have help on the way..Made repairs and restored at 12:36.
12881 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-04-25 16:20 | 2010-04-25 19:56 | 2 | 216 | 50953-1 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34819300 // TRANSFORMER FUSE OUTTRANSFORMER FUSE OUT. BAD TRANSFORMER 15 KVA 7200 2 BUSHING VER/HFP L3/HFP IDC XXXX
12882 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-08-17 21:21 | 2020-08-17 23:45 | 3 | 144 | 4341111 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Tested good at meter base but reworked weatherhead due to connection heating up. Also found bad sec neutral connection at xfmr. Opened xfmr @ 23:15, made repairs and closed @ 23:45. sh // cod 3
12883 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2011-07-09 11:36 | 2011-07-09 13:24 | 4 | 108 | 4496631 | 432 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 SECONDARY BROKEN ON POLE 37830296B31158. WILL OPEN XFMR AND TO REPAIR LINE. SPLICED SECONDARY, POWER RESTORED COD-4 ISO TF 37830296B31158 VER/HFP L3/HFP IDC XXXX
12884 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-03-05 16:09 | 2014-03-05 18:33 | 3 | 144 | 4454881 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE BACK ON HILL//GOING TO CLIMB AND CHANGE//REPAIRS MADE////OPENED TAP AT 17:43//CLOSED BACK AT 18:25 RESTORING ALL CUST//COMPLETE//EM /// COD-3 ISO TF 38820673D00195 VER/HFP L3/HFP
12885 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2013-04-24 20:37 | 2013-04-24 22:25 | 4 | 108 | 4045811 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN ON POLE 771-314//REPLACED CUTOUT ON THIS POLE//RESTORED AT 22:25//COMPLETE//EM//COD 4// VER/DBM IDC XXXX
12886 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2022-09-15 10:44 | 2022-09-15 14:20 | 2 | 216 | 4885431 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required
12887 | Paintsville | 3410602 | E.PRESTON | LANCER | 2018-10-22 07:25 | 2018-10-22 09:49 | 3 | 144 | 4307041 | 432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link appears to have broke. Restored @ 9:49. sh L3/HFP
12888 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-03-04 11:34 | 2012-03-04 18:45 | 1 | 431 | 4543931 | 431 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | XMF HAD BARE XL RISERS. ONE HOT LEG HAD COME IN CONTACT WITH NEUTRAL BURNNING HOTLEG INTO. ALL REPAIRES MADE APR AT 1845 CLOSE TICKET //VER/CRB
12889 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2019-05-29 22:33 | 2019-05-30 05:49 | 1 | 435 | 4382651 | 431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED RECLOSER 37830296D11616 //COD 293//TO MAKE REPAIRS ON PRIMARY METERING CONNECTION ON OUR SIDE 37830320C10451 //OFF @ 0545 ON @ 0549Waiting on coal co. to run line out Released by crew 077S03 L3/HFP
12890 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-07-01 07:54 | 2021-07-01 15:05 | 1 | 431 | 4833121 | 431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva xfmr, need new cutout---NO Truck--all manual---maybe ATV??---line crew required--assign to B Tackett Released by crew 078H16// installing dead end blivett between pole 260 and 261bad 25kva xfmr, need new cutout---NO Truck--all manual---maybe ATV??---line crew required--assign to B Tackett Released by crew 078H16 Repairs made ticket complete. Closed at 15:05
12891 | Pikeville | 3407102 | TOPMOST | CANEY | 2010-02-03 21:29 | 2010-02-04 04:40 | 1 | 431 | 62823-1 | 431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | CONTACTED TIM HALL DUTY SUPERVISOR .. WILLL DETERMINE IF POSSIBLE TO SEND CREW TONIGHT OR MAY HAVE TO WAIT UNTIL DAYLIGHT TO PATROL LINE FOR SAFETY CONCERNS. * TIM HALL IS SENDING PAUL LAYNE AND GREG JUSTICE TO PATROL LINE AND TRY FUSE. * AT 0200 , CREW REPORTS CUST DROPPED LOAD , FUSE WAS TRIED BUT DID NOT HOLD. CREW TO CONTINUE FOOT . AT 0345 CREW FOUND BAD P/T & ISOLATED. IDC XXXX & RESTORE LINE.CONTACTED TIM HALL DUTY SUPERVISOR .. VER/PDP
12892 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-19 18:09 | 2008-06-20 01:20 | 1 | 431 | 50943-1 | 431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008702// BAD 19.9 15 KVA XFORMER, I CHANGED CURRENT FUSE , XFORMER FUSE BLEW WHEN I CLOSED IT IN. NO TRUCKS TO POLE. RELEASED BY CREW 078S01/CREW IN ROUTE RELEASED BY CREW 078H05 COD-1 VER/LDA IDC XXXX
12893 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2011-10-31 09:40 | 2011-10-31 16:50 | 1 | 430 | 4038711 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000903 - ERIC BAIER, DHE, REPORTED APPEARS TR IS BAD, NEED TO HAVE SERVICER CHECK // BAD 50KVA NO TRUCKS MIT GET YARD DOG TO POLE CALLED TREE CREWS TO CLEAN VINES OFF POLE RELEASED BY CREW 078S08//COD 1// VER/DBM IDC EXTENDED FOR TREE REMOVAL XXXX
12894 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2010-08-06 10:50 | 2010-08-06 18:00 | 1 | 430 | 50294-1 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 490/105///BUCKET ACCESS NEED FIBERGLASS T BRKT 12 CUTOUT AND ARRESTOR,,19.9///JDM RELEASED BY CREW 077E01 === REPLACED CUTOUT GATE === AND CUT TREES AROUND TRANSF POLE == REFUSED POWER OK ===
12895 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-02-17 21:06 | 2010-02-17 22:32 | 5 | 86 | 58811-1 | 430 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RICK... MIGHT WANT TO CHECK THE VOLTAGE AT THE REGULATORS ON POLE 37830375A00387 FIRST... SECONDARY SPLICE BURNED INTO.. MADE REPAIRS RESTORED POWER AT 22:32 VER/HFP L3/HFP IDC XXXX
12896 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-02-27 12:02 | 2018-02-27 19:12 | 1 | 430 | 4887531 | 430 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Repairing bad connection that failed due to all 3 conductors being wrapped in tape. one customer only affected./ ISO 37830069000074/ COD 1
12897 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-24 04:01 | 2016-02-24 09:21 | 2 | 320 | 4752841 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 117-43 BAD 19.9 CUTOUT NEED LINE CREW TRUCK TO POLE RELEASED BY CREW 078S08 RESTORED AT 0921. COD 1 VER/AWD
12898 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-12-04 10:09 | 2009-12-04 17:19 | 1 | 430 | 52981-1 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA ONE CUST, THIS IS RIGHT ACROSS FROM THE OLD CAR LOT, AT THE TOP OF HILL, IF YOU PASS THE LAKE YOU HAVE WHEN TO FAR, WELL NEED CREW, CAN US TRUCK ON THIS ONE. RELEASED BY CREW 078S06//COD 1// VER/DBM IDC XXXX
12899 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-11-06 17:25 | 2016-11-06 21:00 | 2 | 215 | 4080221 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | METER BLANK BAD 25 KVA TRANSFORMER. REPLACED XFMR AND RESTORED @ 21:00. SH//COD 2
12900 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-08-04 16:00 | 2010-08-04 19:35 | 2 | 215 | 61450-1 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT == REPLACED == POWER OK VER/HFP L3/HFP IDC XXXX
12901 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-01-14 09:03 | 2015-01-14 09:13 | 43 | 10 | 4934651 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE BAD CUTOUT ON 38830044C14064/ CHANGING CUTOUT/ OPENED RECLOSER 38830044C24509 TO ISOLATE LINE FUSE 38830044C14064/ POLE 44-4509 REC. BACK ON 09:07/ BAD CUTOUT CHGED 30T BACK ON 09:13/ RECLOSER 38830044C24509 9:03 TO 9:07 (COD 147)// LINE FUSE 38830044C14064 9:03 TO 9:13 (COD 43)//// ISO 38830044C14064/ COD 43// CHANGE IN HOIS /// VER TIME VIA VOICE RECD // VER/HFP L3/HFP AJB
12902 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-02-10 11:22 | 2010-02-10 18:32 | 1 | 430 | 55084-1 | 430 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | SEND TO B LYNCH RELEASED BY CREW 078S07//COD 1 IDC XXXX
12903 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-02-15 04:55 | 2019-02-15 08:30 | 2 | 215 | 4796021 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE # 37830402B00519//COD 2//
12904 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-02-26 11:27 | 2009-02-26 15:02 | 2 | 215 | 51703-1 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT , CALLING FOR HELP. G SHOUSE CREW COMING TO HELP RELEASED BY CREW 077S02//COD 2// IDC XXXX
12905 | Hazard | 3307301 | BULAN | ARY-HEINE | 2016-01-02 22:55 | 2016-01-03 02:30 | 2 | 215 | 4581931 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | UNABLE TO CONTACT CUSTOMER,,, LINE HAS BEEN DISCONNECTED// BAD CSP XFMR, WILL NEED CREW, 25 KVA XFMR, 7.2 KV, AND CUTOUT, CAN REACH WITH BIG BUCKET//COD 2// VER/DBM
12906 | Hazard | 3309301 | VICCO | REDFOX | 2011-08-03 01:25 | 2011-08-03 05:00 | 2 | 215 | H4657141 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | PRIM METERING ON POLE 324-257 HAS GONE BAD, 1 BY-PASS CUTOUT IS ALSO BAD, WILL NEED TO REPLACE BY-PASS CUTOUT BEFORE RESTO`G POWER, 2 FUSES ARE BLOWN ON POLE 323-430. REPLACED 2 BY-PASS CUTOUTS AND REMOVED CLAMPS FROM METERING VER/PDP STC, CRT`D 2ND TT, PER PHONE CONF & CALLS - A&C PHSES OUT, CREW OP`D B PHSE @ 01:25(2ND TT W/2), ALL REST @ 05:00, 1 OF 2 TT`S
12907 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2015-06-13 19:30 | 2015-06-13 23:05 | 2 | 215 | 4566411 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 6 T TRANS FUSE//COD 2//AED ENTRY CREATED// VER/DBM
12908 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-10-02 08:05 | 2013-10-02 15:15 | 1 | 430 | 4903911 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074S04 BAD XFMR 167/KVA/277/480-19.9 HAVE A CREW ON THE WAY VER/CRB L/3 CRB IDC XXXX
12909 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-01-23 19:02 | 2021-01-23 20:28 | 5 | 86 | 4887481 | 430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
12910 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-02-22 05:55 | 2022-02-22 13:04 | 1 | 429 | 4526201 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout Guidelines./crew requird no big trucks small material handler only very steep narrow long nmud driveway 15 kva Released by crew 078S03//arrived RM removed fines power back on @13:04 please close tic RM
12911 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2008-07-07 18:21 | 2008-07-07 19:00 | 11 | 39 | 63936-1 | 429 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3002103//4/0 RISER MELTED OFF SEC // VER/TOM IDC XXXX
12912 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-08-27 19:57 | 2008-08-27 22:20 | 3 | 143 | 56617-1 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38821105C00216. REPLACED.....DAH//3411802//VER/CRB IDC XXXX
12913 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-06-01 00:32 | 2014-06-01 02:55 | 3 | 143 | 4957901 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SERVICER PATROLLING . FUSE LINK BROKEN, REFUSED TRANSFORMER CUTOUT, ALL WORK COMPLETE / GXJ
12914 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-02-27 07:47 | 2009-02-27 10:10 | 3 | 143 | 51997-1 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008702//NEED BIG BUCKET//MAY NEED TO OPEN UP LINE, BROKE CUTOUT ALMOST LAYING ON TOP OF TRANSFORMER//COD 3// VER/DBM IDC XXXX
12915 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2017-12-31 19:28 | 2017-12-31 21:51 | 3 | 143 | 4690691 | 429 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | called customer no answer,,,replaced split bolt connections complete
12916 | Hazard | 3308001 | JACKSON | S.JACKSON | 2017-03-14 14:07 | 2017-03-14 16:30 | 3 | 143 | 4556471 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEC BUSHING IN TRANSORMER R BAD NEED 25 KVA 7200 AND #2 CU LEADS, CAN USE MAT HANDLER BUCKET. OPEN TRANSFORMER AT 1439 AND THIS ON POLE 38831083D30252 NOT 1084-6/ ISO 38831083D30252/ COD 3 CODC***PER SERVICER***/ 1630/ VER/BOW
12917 | Hazard | 3420001 | SOFT SHELL | VEST | 2021-03-13 00:51 | 2021-03-13 08:00 | 1 | 429 | 4333101 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines.0800
12918 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-01-31 15:52 | 2014-01-31 18:15 | 3 | 143 | 4333441 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA XFMR FAILED ON 882-324.//TOMMY GOBLE TO ASSIST15 KVA XFMR FAILED ON 882-324. CREW ENROUTE TO CHANGE.15 KVA XFMR FAILED ON 882-324. CREW ENROUTE TO CHANGE. CHANGED TO NEW 25 KVA AND RESTORED @ 18:15. SH VER/SEF
12919 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-03-12 12:47 | 2015-03-12 19:56 | 1 | 429 | 4187121 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DHE CREW WAS IN AREA WORKING ON RECLOSER ABOVE THIS TICKET, CHECKED AND SAID THE CURRENT LIMITING FUSE IS BURNT UP, OPENED THE TRANSFORMER FUSE, NEED BUCKET TO GET TO//// WILL REPLACE CURRENT LIMITING FUSE///REPLACED BAD CURRENT LIMITING FUSE AND RESTORE SERVICE @ 19:56//COD 1// VER/DBM
12920 | South Williamson | 3411401 | DEWEY | INEZ | 2009-06-20 08:53 | 2009-06-20 11:16 | 3 | 143 | 61686-1 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD//VER/CRB
12921 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2020-12-14 23:38 | 2020-12-15 02:01 | 3 | 143 | 4769881 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 2:01. sh
12922 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-02-22 19:11 | 2008-02-22 19:50 | 11 | 39 | 66389-1 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308503// BAD CUTOUT - WILL NEED CREW AND BIG BUCKET// CUTOUT ON FIRE WILL TRY AND LOWER //ASSOCIATED WITH OUTAGE 66364-1//OPENED LINE AT 1911 CLOSED AT 1950.// VER/TOM IDC XXXX
12923 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2022-02-18 13:34 | 2022-02-18 14:13 | 11 | 39 | 4512141 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Broken fuse, restored @ 14:13
12924 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-06-02 13:58 | 2018-06-02 16:21 | 3 | 143 | 4546961 | 429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broken on pole 263-35..will make repairs.restored..
12925 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-06-05 17:16 | 2021-06-05 20:50 | 2 | 214 | 4672771 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm door open @ 37830140B00250Cutout broke @ 37830140B00250 /Restored @ 20:50
12926 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-02-25 19:13 | 2017-02-25 21:00 | 4 | 107 | 4423001 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT ON P 925-136.CHANGING.//COD 4// VER/DBM L3/HFP HFPC FP
12927 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-08-04 13:35 | 2009-08-04 17:09 | 2 | 214 | 55908-1 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP LINE FUSE OUT ON POLE 398-183, BAD CUTOUT ON POLE 398-442, REPLACED CUTOUT ,RESTORED POWER AT17:09 COD-3 L3/HFP IDC CHANGED FROM COUNT 3 XXXX
12928 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2015-12-17 09:27 | 2015-12-17 16:35 | 1 | 428 | 4539311 | 428 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG OF THE SECONDARY UNDERGROUND IS BAD. TECHNICIAN IS EN-ROUTE TO LOCATE THE FAULT. THIS SERVICE IS OFF OF UNDERGROUND TRANSFORMER #38820966A32769. RELEASED BY CREW 079S02 811 CALLED @12:10 TICKET # 1512170574 THIS A DOP BACKON AT 16:35 VER/HFP L3/HFP
12929 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-04-25 16:57 | 2017-04-25 18:44 | 4 | 107 | 4681991 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE37830343D00025 . REPLACED CUTOUT . VER/CRB L3/HFP XXXHFP
12930 | Pikeville | 3413402 | GARRETT | LACKEY | 2014-04-16 21:11 | 2014-04-17 00:45 | 2 | 214 | 4613451 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD POLE 73, LARGE TREE GROWN AROUND POLE TO PRIMARY, FLAGGING CREW REQUIRED . REPLACED CUTOUT AND ARRESTER, ALL WORK COMPLETE / GXJ //VER/GAH
12931 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-11-01 06:27 | 2009-11-01 08:14 | 4 | 107 | 54466-1 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408303// BAD CUTOUT ON POLE 9-C-223. //VER/GAH IDCC PN223 XXXX
12932 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-06-18 18:47 | 2015-06-19 01:55 | 1 | 428 | 4602311 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ** SEE H460231** POLE 38831077D00667 IS BROKE. MAP SHOWES IT TO BE 38831077D00655 WILL NEED 35 CLASS 5 LINE CREW LINE TRUCK & MATERIAL HANDLER. 1 MANUAL TREE CREW RELEASED BY CREW 074S04/ 1 CUSTOMER OUT ORIGINALLY/ OPENED TRANSFORMER 38831077D00164 @ 23:12 (2 CUSTOMERS) CLOSED @ 01:55 (3 CUSTOMERS)/ ISO 38831077D00164/ COD 3/ DUPLICATE IN HOIS/ VER/BOW
12933 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2011-05-23 12:42 | 2011-05-23 16:16 | 2 | 214 | 4143341 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURN OPEN ON POLE 25-30 ???????????????????????????????
12934 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-05-31 17:22 | 2017-06-01 00:30 | 1 | 428 | 4890311 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT./// VER/DKM
12935 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2013-08-19 15:48 | 2013-08-19 19:35 | 4 | 227 | 4680211 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | C PHASE LF BLOWN ON 37830048B30081// WILL PATROL// BAD XFMR ON 37830048B31083//CLOSED LF AT 16:55// 48-1083 IS ONLY ONE OFF// REPLACED XFMR//2 CUTOUTS/LAS// POWER IS RESTORED VER/CRB L/3 CRB
12936 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-11-15 06:26 | 2018-11-15 10:00 | 2 | 214 | 4400931 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout pole 44-A-305 crew required, Bobby Tackett, Lifting hottap at 44-A-108crew reqd. broke cutout on pole 38830044A00305. no trucks.. tagged to B. tackett & hot tap lifted @ pole 44a108 Released by crew 078H17 RESTORED @ 1000
12937 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-11-29 14:26 | 2010-11-29 18:00 | 2 | 214 | 60694-1 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 37909066 // BAD 50 KVA TRANSF 19.9 KV == NEED LINE CREW == CALLED FOR LINE CREW RELEASED BY CREW 077S03 CREW ON SITE WILL BE WORKING POWER ON W.MELTON // COD-2 VER/HFP L3/HFP IDC XXXX
12938 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-04-01 15:39 | 2014-04-01 19:13 | 2 | 214 | 4552611 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQ BAD 25 KVA NEED 37.5 TO REPLACE SEND TO VEM RELEASED BY CREW 078H06/CREW ON SITE/FETR1915/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST@1913/PLEASE CLOSE TICKET/THANKS/VEM COD-2 ISO TF 38830206D02057 VER/HFP L3/HFP IDC XXXX
12939 | South Williamson | 3411401 | DEWEY | INEZ | 2012-02-21 10:23 | 2012-02-21 12:10 | 4 | 107 | 4459241 | 428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP HAD BROKE AND RISER WAS HANGING DOWN//MADE REPAIRS//RESTORED AT 12:10//COMPLETE//EM VER/HFP
12940 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-01-21 05:38 | 2019-01-21 12:45 | 1 | 427 | 4697991 | 427 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 39831099A20204 b phase xfmer bad 277/480 single pri bush, 2 sec bush,trk to pole. open other fuses @ 09:30 contact adam poplin 606-254-6172 upon arrival. ONLY 1 CUSTOMER OUT ON THIS ORDER///
12941 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-02-19 23:13 | 2015-02-20 06:20 | 1 | 427 | 4045791 | 427 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP IS BURNT INTO AT SECONDARY POLE ///// THIS IS UP ON A ROCK CLIFF CANT HARDLY GET UP TO SEC. POLE/// NEED A CREW TO REPLACE SERVICE#2 ABOUT 75 FT./// TALKED TO CUSTOMER AND TOLD HIM THAT IT REQUIRED ADDITIONAL HELP HE SAID THAT WOULD BE FINE RELEASED BY CREW 074H10//// REPLACED BURNT SERVICE DROP AND RESTORED SERVICE @ 6:20/// ONE CUSTOMER AFFECTED VER/CRB L3/HFP XXX
12942 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2014-01-14 13:34 | 2014-01-14 14:35 | 7 | 61 | 4281511 | 427 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT DOOR. COD-7 ISO TF 37820081D00109 VER/HFP L3/HFP
12943 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-05-11 21:54 | 2020-05-11 22:55 | 7 | 61 | 4826501 | 427 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Changed cutout, door burnt up/ ISO 38830019D00016/ COD 7
12944 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-04-13 16:58 | 2013-04-14 00:05 | 1 | 427 | 4007061 | 427 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XMFR NEED 10 KV 7200 & CUTOUT / T BRACKET. SMALL BUCKET & LINE TRUCK MAY GET TRUCK TO POLE BUT ITS ?. BRING MUD BOARD TRAILER. 3 MEN VER/PDP IDC XXXX
12945 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-11-21 11:47 | 2017-11-21 18:54 | 1 | 427 | 4592521 | 427 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | called customer voicemail/ line crew req/ Bad hot leg in 4/0 underground svc/ MTR #533588963 only customer affected/ Line crew try to locate with fault finder for repair or install new svc/ MLH Released by crew 078H08/on site RM couldnt locate faut installed power temp repair at later date ,please close tic RM/ ISO 39830925000089/ COD 1
12946 | Hazard | 3303901 | LESLIE | HYDEN | 2010-07-13 08:06 | 2010-07-13 15:12 | 1 | 426 | 65808-1 | 426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 19.9 120/240 RELEASED BY CREW 077S01 POWER RESTORED--- G FUGATE COD-1 VER/HFP L3/HFP IDC XXXX
12947 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-08-15 17:56 | 2018-08-15 20:18 | 3 | 142 | 4957871 | 426 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Secondary splice burndt into on customers service drop, 1 cust out while making repairs. Replaced service @2018.
12948 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-11-03 06:47 | 2014-11-03 09:09 | 3 | 142 | 4694751 | 426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE///////////RE-FUSED AND RESTORED,FUSE APPEARED TO HAVE MELTED OUT/ ISO 37820005000004/ COD 3// VER/BOW
12949 | Hazard | 3303901 | LESLIE | HYDEN | 2009-10-29 20:23 | 2009-10-29 22:45 | 3 | 142 | 51902-1 | 426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT UP ON THE SIDE OF THE HILL./// POWER RESTORED. G FUGATE IDC XXXX
12950 | South Williamson | 3411401 | DEWEY | INEZ | 2011-01-11 12:03 | 2011-01-11 14:25 | 3 | 142 | 60624-1 | 426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RUDY VASS REPORTS CUTOUT IS BROKE ON POLE 742-B-35//CHANGING NOW///RESTORED AT 14:25//EM // COD 3// VER/DBM IDC XXXX
12951 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-05-27 16:48 | 2009-05-27 20:21 | 2 | 213 | 57023-1 | 426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 30004680 // BAD 12KV CUTOUT POLE 140-7015 RESTORED @ 20:34 RELEASED BY CREW 078H12 COD-2 ISO 38830140D07015 L3/HFP IDC XXXX
12952 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-07-11 10:10 | 2009-07-11 12:32 | 3 | 142 | 58187-1 | 426 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | VER/HFP RELEASED BY CREW 074S06 FUSE BROKE COD-3 38831125C40091 L3/HFP IDC XXXX
12953 | Hazard | 3302703 | HAZARD | HAZARD | 2010-01-06 10:11 | 2010-01-06 12:33 | 3 | 142 | 63234-1 | 426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TR ANSF BAD == SECONDARY LUG BURNED UP == NEED TO REPLACE WITH 50 KVA 7200 KV == RELEASED BY CREW 077S03 REPLACED TRANSFORMER RESTORED POWER AT 1233 077H01 COD-11 VER/HFP L3/HFP IDC CHANGED COUNT AND POLE NUMBER PER THE FAULT POLE XXXX
12954 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2021-08-14 16:23 | 2021-08-14 23:29 | 1 | 426 | 4064461 | 426 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | crew required 1 leg bad 4/0 ug/may need add a phase Released by crew 078S03///Only 1 cust was out///repairs made cust back on @23:29///Complete BR
12955 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-07-17 22:17 | 2021-07-18 00:39 | 3 | 142 | 4928741 | 426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a Broke Trans Cutout at pole 190-B-114,Will have to Climb pole to make repairs..Restored at 00:39.
12956 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-09-23 16:57 | 2020-09-23 20:30 | 2 | 213 | 4489771 | 426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | opened xfmer @ 16:57. bad 25kva. truck ok, crew & flaggers reqd. cust getting 150 volts on each leg. Released by crew 078S04 crew on site FETR 21:00 ALL pwrrestored 20:30 pleasecloseticket LRM (2 CC)
12957 | Paintsville | 3401802 | INDEX | HOSPITAL | 2019-05-23 21:45 | 2019-05-23 23:10 | 5 | 85 | 4323141 | 425 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | having bright an dim problems voltage is droping when air comes on// we have an auto transformer on this house due to bad underground // crew on there way// changed transformer on 654-168 opened transformer and tap at 2145 closed at 2310 // complete tt//cod 5
12958 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-03-20 11:30 | 2017-03-20 11:55 | 17 | 25 | H4571651 | 425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LREPLACED CUTOUT//RESTORED ALL CUSTOMERS AT 11:55//COMPLETE//INE CUTOUT BROKE ON POLE 890-3//OPENED SWITCH ON POLE 866-84 TO SAFELY MAKE REPAIRS//OPENED AT 11:30//REPAIRS MADE//RESTORED ALL CUSTOMERS AT 11:55//COMPLETE//EM DUP ******* VER/HFP L3/HFP
12959 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-04-20 03:24 | 2019-04-20 10:29 | 1 | 425 | 4139361 | 425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ./ called customer: didnt hear anything was asleep, looks like eighbors have power, no reading on meter/xfmr fuse open/servicer to try/vem/broken fuse link/power restored to all cust 1029/please close ticket/thanks/vem
12960 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-07 07:01 | 2008-12-07 08:26 | 5 | 85 | 55061-1A | 425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308401/// BAD CSP XFMR *** 1 CC UNTIL ***** AT 0701 SEVICER OPENED LF AT POLE 227-52 TO SAFELY REPLACE TR. ALLL CUST RESTORED AT 08:26 VER/KEP L3/KEP IDCC PN94 CHANGED FROM SCHEDULED XXXX
12961 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-11-29 21:18 | 2013-11-30 00:50 | 2 | 212 | 4088541 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 400-232 //J.BAKER TO ASSIST //BAD XFMR ON POLE 400-232, REPLACED XFMR RESTORED POWER AT 12:50 //VER/GAH IDC XXXX
12962 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-01-14 13:28 | 2019-01-14 17:00 | 2 | 212 | 4672291 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | trans reiser burnt in two at trans.repaired riser.restored at 17;00 L3/HFP
12963 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-05-07 03:36 | 2009-05-07 10:40 | 1 | 424 | 62162-1 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001203 -OPENED TRANSFORMMER AT 07:10--HIGH VOLTAGE ON TRANSFORMER--132/275 CALLING CREW RELEASED BY CREW 078S07 IDC CREATED DUPLICATE TO OPEN TRANSFORMER THIS CUSTOMER WAS ADVISED TO TURN OFF MAIN. XXXX
12964 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2019-06-20 11:54 | 2019-06-20 13:40 | 4 | 106 | 4552281 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOLD ORDER//DOL 932274//PRIM MTR FUSE OUT@79-72,WILL RE-FUSE////////2 HOTTAP CONNECTIONS@79-63BURNED INTO///////NEED CREW&ALSO A TREE CREW(MANUAL)//cod 4//
12965 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2016-05-08 09:22 | 2016-05-08 10:15 | 8 | 53 | 4187081 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-2262 75KVA TRANS. OUT 12T CHGED BAD CUTOUT INSTALLED ANIMAL GUARD/ ISO 38830045B12262/ COD 8/ VER/BOW
12966 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-01-08 04:31 | 2015-01-08 08:03 | 2 | 212 | 4917141 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRS MADE, POWER RESTORED. ORGINAL 2 OFF, OPENED THE OTHER 5 LATER/ OPENED TRANSFORMER AT 07:38.CLOSED AT 08:03/COD2+5// VER/ ADH
12967 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2020-03-12 19:41 | 2020-03-13 02:45 | 1 | 424 | 4472851 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout 12kv crew required Released by crew 078S11,repairs made all cust restored @ 0245 please close ticket thanks.bt // cod 1//
12968 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2015-06-15 18:32 | 2015-06-15 22:04 | 2 | 212 | 4576011 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANS ON POLE 378300A21195 NEED ONE MAN AND MATERIAL HANDLER ITS A 10 KV TRANS BUT BRING 15 OR 25 KV TRANS TRK APPROACH RELEASED BY CREW 079H03BAD TRANS ON POLE 378300A21195 NEED ONE MAN AND MATERIAL HANDLER ITS A 10 KV TRANS BUT BRING 15 OR 25 KV TRANS TRK APPROACH REPLACED 10 KVA WITH 15 KVA RESTORED POWER AT 22:04/ ISO 37830024A21195/ COD 2/ VER/BOW
12969 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-09-09 14:38 | 2013-09-09 18:10 | 2 | 212 | 4831991 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 20-3550 BAD 25 KVA TRANS. NEED 3-CUTOUTS AND LA. TRUCK TO POLE RELEASED BY CREW 078S08,, CREW ON SITE, CHANGED XFMR AND CUTOUTS ARRESTERS, ALL POWER RESTORED VER/CRB L/3 CRB
12970 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2021-05-23 20:13 | 2021-05-23 23:45 | 2 | 212 | 4613461 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva can get small bucket to pole Released by crew 078S06 crew on site FETR 11:45 LRM
12971 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-04-27 23:00 | 2011-04-27 23:53 | 8 | 53 | 50217-1 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN ARRESTER PULLED IN THE CLEAR REFUSED TRANSFORMER APR AT 2353 CLOSE TICKET IDC XXXX
12972 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2013-01-04 10:01 | 2013-01-04 17:05 | 1 | 424 | 4568211 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR FROZE OPEN ON 954-763. NEUTRAL IS BROKE ON 954-762 ALSO. REPAIRING. REPAIRS COMPLETE. <<ONLY ONE CUSTOMER AFFECTED>> RESTORED @ 17:05. SH VER/HFP L3/HFP IDC XXXX
12973 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-05-12 13:51 | 2015-05-12 17:23 | 2 | 212 | 4421171 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA ,7200 XFMER, NO TRK. RELEASED BY CREW 078S07 NEIGHBOR SAID THE LAND OWNER WOULD NOT CARE IF WE TOOK THE PICKUP INTO THE TRANSFORMER LOCATION..NEW SERIAL # HI 1506421115.25 KVA..OLD # M&E 78ZN095018..15 KVA TIME ON 17:23/ ISO 38830090000028/ COD 2/ VER/BOW
12974 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-02-22 02:56 | 2011-02-22 10:00 | 1 | 424 | 60032-1 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKE, TREES ALL OVER POLE. WILL NEED BIG BUCKET AND R-O-W CREW //COD 1// VER/DBM IDC XXXX
12975 | South Williamson | 3200302 | BELFRY | TOLER | 2009-06-18 15:46 | 2009-06-18 19:18 | 2 | 212 | 61169-1 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, XFORMER FUSE BLOWN, REFUSING IT, BAD CUTOUT, CALLED R MARCUM FOR CUTOUT AND HELP.//VER/CRB IDC XXXX
12976 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-01-01 06:32 | 2011-01-01 08:18 | 4 | 106 | 57501-1 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 472-120... REPLACED CUTOUT RESTORED POWER AT 08:18 COD-4 ISO LF 37830472000005 VER/HFP L3/HFP IDC XXXX
12977 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-01-04 11:37 | 2014-01-04 15:09 | 2 | 212 | 4228171 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED. VER/CRB IDC XXXX
12978 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-02-28 17:28 | 2019-03-01 00:32 | 1 | 424 | 4939281 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR fuse blown will check.Bad 25 KVA 7200 will need one man and big bucket to change.Replace XFMR and restored power @ 00:32
12979 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-08-31 03:14 | 2014-08-31 10:18 | 1 | 424 | 4439941 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN// WILL REFUSE// CUTOUT BROKE //REPAIRS MADE // POWER RESTORED @ 10:18 VER/TOM L3/TOM
12980 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-06-22 11:56 | 2010-06-22 19:00 | 1 | 424 | 54491-1 | 424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 92-833 BAD 75KVA 277/480 VOLT 2-BUSHING SEC. TRUCK TO POLE ALSO NEED 3-12KV CUTOUTS CUST IS OUT OFF POWER RELEASED BY CREW 078S08/ CREW ON SITE MAKING REPAIRS/RESTORED @ 19:00 J. HEMLEPP //VER/GAH IDC XXXX
12981 | Hazard | 3310502 | HADDIX | CANOE | 2013-01-22 22:54 | 2013-01-23 01:15 | 3 | 141 | 4731151 | 423 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK VER/KEP IDC XXXX
12982 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-07-14 10:09 | 2010-07-14 12:30 | 3 | 141 | 50078-1 | 423 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD ARRESTOR ON POLE 1122-170, CAN NOT GET TRUCK TO POLE, HAVE CUT IN THE CLEAR AND HAVE POWER RESTORED AT THIS LOC, SEND A COPY TO MR. RAYBURN TO HAVE CREWS TO REPLACE THIS ARRESTOR AT A LATER DATE//VER/CRB IDC XXXX
12983 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2018-12-13 01:57 | 2018-12-13 09:00 | 1 | 423 | 4560381 | 423 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout nbt L3/HFP
12984 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2013-06-26 16:15 | 2013-06-26 18:36 | 3 | 141 | 4404631 | 423 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKEN INTO FUSED UP EVERYTHING OK COD 3 ISO TF 160-48 VER/SEF IDC XXXX
12985 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2019-05-29 02:13 | 2019-05-29 03:00 | 9 | 47 | 4357921 | 423 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Associated with 4357551/ bad transformer on pole 38821065D20145/ secondary runs from 38821065D20145 to pole 38821065D40240/ ned to open 38821065D40240 to get over top of the it to remove transformer 1065-145/ ISO 38821065D40240/ cOD 9/ 0213 to 0300
12986 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2013-01-26 07:04 | 2013-01-26 09:25 | 3 | 141 | 4742351 | 423 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED @ 9:25. SH VER/KEP IDC XXXX
12987 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-09-10 09:58 | 2013-09-10 17:00 | 1 | 422 | 4833981 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | COLLEGE TO BRING ATV TO ACCESS SITE, BAD XFMR, CREW ON WAY TO REPLACE XFMR RELEASED BY CREW 077S02 VER/CRB L/3 CRB
12988 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-05-03 12:02 | 2009-05-03 15:33 | 2 | 211 | 64100-1 | 422 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP UG SERVICE IN TROUBLE,WILL MAKE TEMPORARY REPAIR.MASSEY IS COMING TO HELPREPLACED UG SERV WITH TEMPORARY OVRHD COD-1 L3/HFP
12989 | Hazard | 3309302 | VICCO | JEFF | 2008-11-19 04:09 | 2008-11-19 07:40 | 2 | 211 | 66448-1 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR 27354530 TRANSF FUSE OUT == BAD TRANSF 19.9 = 10KVA == NEED 25 KVA == CHANGED TRANSF == POWER OK VER/KEP IDC XXXX
12990 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-02-11 04:10 | 2013-02-11 11:12 | 1 | 422 | 4807751 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL CHECK AT REGULAR WORKTIME AS PER SET GUIDELINES // FUSE IS OPEN ON 526-65 15T VER/KEP IDC XXXX
12991 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-09-17 08:54 | 2013-09-17 12:25 | 2 | 211 | 4859711 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED--BAD 75 KVA TRANSFORMER--NEED NEW CUTOUT AND BRACKET -NEED BIGER MATERIAL HANDLER--TRANSFORMER LEAKING OIL--LOCATED BEHIND CATTLESBURG ELEMENTARY SCHOOL--TRANSFORMER FOR SCHOOL RELEASED BY CREW 078S07POWER BACK ON AT 1225...NEW TRANSFORMER NUMBERS 1308270813..HOWARD IND..JOB COMPLETE VER/CRB L/3 CRB
12992 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2017-05-12 11:16 | 2017-05-12 18:18 | 1 | 422 | 4786391 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FAILED, 25 KVA , 19.9 / 120/240, 1 MAN , MATERIAL HANDLER REQUIRED . REPLACED XFMR, ALL WORK COMPLETE / GXJ 37830068000209/ VER/BOW
12993 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-07-14 05:19 | 2014-07-14 08:50 | 2 | 211 | 4237641 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VERY OLD FUSE FAILED REPLACED WITH NEW DOOR AND CLOSED BACK IN AT 08:50. COMPLETE COD 2// VER/ADH
12994 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-04-25 17:14 | 2009-04-25 20:45 | 2 | 211 | 61125-1 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3409303//BLOWN FUSE ON POLE 3883085700283//COD 2//ISO//FOUND BLOWN ARRESTOR, WILL CLEAR IT AND RESTORE FUSE// VER/DBM IDC XXXX
12995 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2019-05-07 13:49 | 2019-05-07 15:35 | 4 | 106 | 4235151 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad transformer cutout. No truck access. Need three man crew, cutout, arrester and bracket, eight foot crossarm, arm braces, two angle pins and insulators for 7200. Service neutral is also burned into, kwh meter is pulled and three phase is still hot. Will need to open the three phase at pole 38821065D10016 to make repairs. Line opened at 13:49 Released by crew 079S02//NO OUTAGE TILL L/F OPENED @ 1349//HAD TO OPEN TRANS FUSE ON POLE 38821065D10016 ALSO
12996 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-08-18 18:23 | 2017-08-18 21:54 | 2 | 211 | 4277161 | 422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LINE FUSE BLEW AT POLE 1072-139///POLE 1072-97 IS ROTTEN AND FELL OVER///NO LIVES PAST XFMER POLE 1072-96///GOING TO CUT DEAD END ON POLE 1072-96 TO GET ALL CUST BACK ON AND HAVE TECH WRITE JOB TO FIC BROKE POLE AT LAER DATE 39831072000139 39831072000096LINE FUSE BLEW AT POLE 1072-139///POLE 1072-97 IS ROTTEN AND FELL OVER///NO LIVES PAST XFMER POLE 1072-96///GOING TO CUT DEAD END ON POLE 1072-96 TO GET ALL CUST BACK ON AND HAVE TECH WRITE JOB TO FIC BROKE POLE AT LATER DATE///MADE SAFE AND CLO VER/AWD
12997 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-02-23 07:04 | 2020-02-23 10:35 | 2 | 211 | 4425331 | 422 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | open wire sec. has burnt down and caught phone or tv cable on fire..due to sec. sagging into cable.will make repairs..sec. down from poles 191-22 to 191-21..will need one man to help make repairs with #2 alum. wire..please send copy to tech to have job written up to move xfm. from pole 191-22 to 191-21.
12998 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-06-27 05:32 | 2008-06-27 12:33 | 1 | 421 | 55740-1 | 421 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 27KV CUTOUT GATE BURNED UP ON POLE 306-130 TRUCK ACCESSIBLE 60 FT POLE RELEASED BY CREW 077E02 VER/KEP IDC XXXX
12999 | South Williamson | 3411401 | DEWEY | INEZ | 2011-10-16 16:29 | 2011-10-16 23:30 | 1 | 421 | 4988441 | 421 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 15 KVA XFMR ON POLE 649-80//TIM MILLER GETTING CREW//CREW ON SITE//XFMR REPLACED// RESTORED AT 2330//COMPLETE//EM. CC = 1. VER/SDB IDC XXXX
13000 | Hazard | 3303902 | LESLIE | WOOTON | 2014-04-01 16:19 | 2014-04-01 23:20 | 1 | 421 | 4552821 | 421 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 535-54 . NEED LINE CREW & 10KVA XFMR & CUTOUT / T - BRACKET 7200 VOLTS . ALSO NEED 6 WHEELER . COD-1 ISO TF 37830535000054 VER/HFP L3/HFP IDC XXXX
13001 | Whitesburg | 3401301 | FLEMING | NEON | 2012-05-14 02:04 | 2012-05-14 09:05 | 1 | 421 | 4788671 | 421 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT VER/KEP IDC XXXX
13002 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-05-11 04:50 | 2015-05-11 11:51 | 1 | 421 | 4409411 | 421 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | COUSTOMER HAS A BAD MAIN BREAKER BUT VOLTAGE ON THIS XFMR IS 133/ 131-264. T.HALL TO HAVE XFMR CHANGED OR RUN SECONDARY FROM POLE#37830095000209 RELEASED BY CREW 074S04/ ISO 37830095000200/ COD 1/ VER/BOW
13003 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-07-18 11:04 | 2019-07-18 12:04 | 7 | 60 | 4727511 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING LEAKING TRANSFORMER 37830387B20654//COD 7//OFF @11:04 ON @12:04
13004 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-07-04 22:24 | 2022-07-04 23:24 | 7 | 60 | 4374601 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout gate on pole 271-C-114, power restored at 23:24.
13005 | Hazard | 3302704 | HAZARD | KENMONT | 2020-01-24 14:54 | 2020-01-24 16:04 | 6 | 70 | 4335951 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | pole is slabing and a chunk of pole layed over on transformer, removed wood and refused transformer//cod 6 L3/HFP
13006 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2008-03-21 17:50 | 2008-03-21 20:10 | 3 | 140 | 59714-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3309902// PRIMARY HITING SPAN GUY == REWORKING POLE 513-145 == OPEN TAP LINE UP TO MAQKE REPAIRS AT 1750 BACK ON 2005//COD 3// VER/DBM IDCC TOF1110 XXXX
13007 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-04-08 15:00 | 2018-04-08 16:45 | 4 | 105 | 4196671 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Secondary going between padmount 38830045D16212, and pedestal 38830045D16213, on oposite side of road is bad. No power only at 2307 hillcrest. Released by crew 078H04--crew on site investigating--open padmount bayonet fuse 38830045D16212 @ 20:15 to safely dig conductor --Located fault under Road--will have to come back and repair at later date--only 1 cust out and house is vacant--- OPENED TRANS @ 1500 ON 04-08-2018 CLOSED 1645
13008 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-06-08 10:14 | 2011-06-08 12:34 | 3 | 140 | 4267621 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED FUSE AT 1220HOT LINE CLAMP HAS PULL OFF TOP OF CUTOUT ON LINE FUSE, GOING TO OPEN OTHER LINE FUSE TO MAKE REPAIRS//VER/CRB IDC XXXX
13009 | Pikeville | 3408103 | SALISBURY | MARTIN | 2019-12-01 09:40 | 2019-12-01 10:50 | 6 | 70 | 4109021 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NC SERVICER REQ/ Dispatched in accordance with KYPCo Late Night Callout Guidelines. Broke cutout on pole 38831074A00182 // manual // opened line fuse on pole 38831074A00371 to climb safely Off @ 0940 on @ 1050
13010 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-01-17 04:06 | 2010-01-17 05:30 | 5 | 84 | 55190-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OPEN ON 251-143/PATROLING/12T LINE FUSE 5 CUSTOMERS VER/ARN IDCC PN146 XXXX
13011 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2011-09-05 11:41 | 2011-09-05 18:41 | 1 | 420 | 4817801 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SEC BURNED DOWN,WILL REPLACE/REPAIR IT////////////MADE NECESSARY REPAIRS AND RESTORED VER/HFP L3/HFP IDC XXXX
13012 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-09-29 16:30 | 2015-09-29 18:15 | 4 | 105 | 4289981 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 8 CROSSARM, BRACES. 2 CUTOUTS AND ARMMOUNT KITS. PROTECTED BY REC @ 1148 A 53/ XFRM FUSE/ ISO 39831147C35019/ COD 4/ OPENED @ 16308 CROSSARM, BRACES. 2 CUTOUTS AND ARMMOUNT KITS. PROTECTED BY REC @ 1148 A 53,REPAIRS MADE ALL CUST RESTORED @ 1815 PLEASE CLOSE TICKET THANKS/ VER/BOW L3/DKG
13013 | Hazard | 3302704 | HAZARD | KENMONT | 2011-01-25 23:50 | 2011-01-26 01:35 | 4 | 105 | 64316-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR- TRANSFORMER FUSE BLOWN --- CUT ARRESTOR IN CLEAR. POWER RESTORED. IDCC CNT1 XXXX
13014 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-04-26 13:45 | 2019-04-26 14:55 | 6 | 70 | 4164351 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Found a broke neutral in customers service drop, going to change out drop while customer is disconnected at her request. Will have to open trans. @167-B-144 to make repairs, will keep track of times. Opened @1345 Closed @1455. L3/HFP
13015 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-04-03 12:55 | 2018-04-03 14:40 | 4 | 105 | 4168771 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Tryed line fuse came back out//MADE MD ON POLE 37830223C00471 S/B HAS BEEN REPLACED 40T L/F//COD 4//Tryed line fuse came back out pole ground on middle phase at 37830223C00560
13016 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-06-07 12:41 | 2019-06-07 13:11 | 14 | 30 | 4446361 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | EMERGENCY OUTAGE OFF 1241 ON 1311 Released by crew 079H07
13017 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2013-11-06 15:21 | 2013-11-06 16:45 | 5 | 84 | 4016221 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 45-159 HOT TAP BROKE OFF CUTOUT 25T OUT SEND TO CREWS NEED BIG BUCKET RELEASED BY CREW 078S08. RESTORED @ 16:45 MP VER/CRB
13018 | Cannonsburg | 3001401 | LOUISA | CITY | 2016-07-29 13:11 | 2016-07-29 16:41 | 2 | 210 | 4708611 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED- TRUCK OK--CUT-OUT ON ARM BROKE ON THREE PHASE POLE MIDDLE CUT-OUT LOOKS CRACKED OPENED THIRD CUT-OUT ON ARRIVAL, RELEASED BY CREW 078S02/CREW ON SITE/FETR1715/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1641/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830454A41673/ COD 2/ VER/BOW
13019 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-07-25 20:35 | 2010-07-25 22:55 | 3 | 140 | 57074-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND LINE FUSE OUT, PATROLLED FOUND TREES IN PRIMARY, I CUT THEM OUT, THEN I FOUND A BAD CUTOUT ON POLE 1122-140, HAVE IT REPLACED AND POWER IS RESTORED AT THIS LOC IDC XXXX
13020 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2016-07-01 11:09 | 2016-07-01 14:39 | 2 | 210 | 4509931 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CORNER OF WALKER RD AND LINCOLN AVE, 15 KVA BAD, CR, CAN USE TRUCK, NEED NEW C/O ALSO RELEASED BY CREW 078S06--CREW ON SITE--CHANGED OUT BAD CAN, NEW CUTOUT AND BRACKET---VOLT CK GOOD---TBL TKT COMP-RMV VER/AWD
13021 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2011-03-17 16:55 | 2011-03-17 17:15 | 21 | 20 | 55277-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND LA POWER WAS ON OPENED TRANS 16;55 BACK ON 17;15 10T TRANS FUSE VER/KEP IDC XXXX
13022 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-07-15 21:25 | 2011-07-15 23:45 | 3 | 140 | 4552131 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT IS BROKEN INTO. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT.//COD 3// VER/DBM IDC XXXX
13023 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-11-11 19:48 | 2015-11-11 20:30 | 10 | 42 | 4429491 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE IN XFMER FUSE ON POLE 809-77///REFUSED AT 20:30///COMPLETE BR/ ISO 38830809C10077/ COD 10/ VER/BOW L3/HFP XXXHFP
13024 | Whitesburg | 3401301 | FLEMING | NEON | 2016-01-16 11:10 | 2016-01-16 12:10 | 7 | 60 | 4625381 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE MELTED OUT, REFUSED AT 1210.// VER/ ADH
13025 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2014-12-21 12:41 | 2014-12-21 13:11 | 14 | 30 | 4873091 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | C PHASE/DUE TO BAD PRIMARY RISER ON 1148-B2-865/SWITCHING BAD CABLE OUT/APPROX ONE HOUR OUTAGE/VEM/OPENED C PHASE 1241/RESTORED C PHASE CUST @1311 IN XFMR 1148-B2-625/DDC TO CREATE ABNORMAL/VEM VER/HFP L3/HFP
13026 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-06-05 18:06 | 2016-06-05 19:30 | 5 | 84 | 4310721 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHANGING.. VER/CRB
13027 | Hazard | 3307301 | BULAN | ARY-HEINE | 2019-10-16 21:22 | 2019-10-17 00:52 | 2 | 210 | 4154361 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | attempted to contact customer but no response // ,lead burnt out of bottom of cutout , cutout mounted on arm between phases manual on hill side, talked to cust ok to leave untill tomorrow cust has generator will need crew and cutout , also talked to Greg Shouse OPS # 032292234// one cust living here, other trailer is vacant //cod 2//
13028 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-10-23 14:33 | 2017-10-23 18:03 | 2 | 210 | 4481521 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 38830501000423.--CREW ON SITE---CHANGED 19.9 CUTOUT---PWR RESTORED AT 18:03--TBL TKT COMP--RMV VER/AWD L3/HFP XXXHFP
13029 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-06-21 16:55 | 2013-06-21 17:55 | 7 | 60 | 4383021 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE PULLED INTO AT POLE 375-340, REFUSED AT 17:55. VER/CRB L/3 CRB IDC XXXX
13030 | Hazard | 3309301 | VICCO | REDFOX | 2008-01-29 21:05 | 2008-01-29 22:15 | 6 | 70 | 60794-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3309301// XFMR FUSE OUT, FUSE LINK BROKE//COD 6// VER/DBM IDC XXXX
13031 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-08-17 06:45 | 2009-08-17 08:30 | 4 | 105 | 59982-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR#31257716BAD CUTOUT DOOR, REPLACED DOOR POWER BACK ON. VER/KEP L3/KEP IDC XXXX
13032 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-03-10 16:17 | 2013-03-10 17:17 | 7 | 60 | 4895411 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUT BAD ARRESTER IN THE CLEAR. COD-7 ISO LF 38820990A00031 VER/HFP L3/HFP IDC XXXX
13033 | Hazard | 3309301 | VICCO | REDFOX | 2008-11-24 10:09 | 2008-11-24 11:09 | 7 | 60 | 51548-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR, LINE FUSE HAD BLOWN ON POLE # 324-244, RESTORED POWER AT 11:09 ON LINE FUSE. XFMR BAD ON 154//3309301//VER/CRB IDCC PN205 XXXX
13034 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-02-05 09:23 | 2018-02-05 12:53 | 2 | 210 | 4805971 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
13035 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2017-07-27 23:53 | 2017-07-28 00:35 | 10 | 42 | H4191131 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 445-130,WILL HAVE TO OPEN LINE FUSE ON POLE 445-50 TO ISOLATE. OPENED AT 23:53 MADE REPAIRS RESTORED POWER AT 00:28.. 37830445000130 VER/AWD
13036 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2010-09-02 11:55 | 2010-09-02 12:37 | 10 | 42 | 62883-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT VER/KEP L3/KEP IDCC FP NULL XXXX
13037 | Hazard | 3308001 | JACKSON | S.JACKSON | 2021-12-20 05:53 | 2021-12-20 07:38 | 4 | 105 | 4213041 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pull in two // cod 4
13038 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2018-09-11 13:30 | 2018-09-11 17:00 | 2 | 210 | 4083991 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Viper reclosures on pole 162-6141 open, second time today. no visable problems on line. Having meter electricians check controls to be correct settings. Crew required to bypass reclosures on pole 162-6141, Beside pole 38830162C00366. 60-1 pole, cant get service truck close enough. Big bucket will reach. Reclosure bypassed, and tagged to ddc.
13039 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2022-11-01 14:15 | 2022-11-01 15:15 | 7 | 60 | 4086061 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Replacing Bad TR 38831003D00099 ( 0 COD)//// Per Nathan Goble request ticket is sent to Shawn Goble for replacement./// Found crossarm to be bad and have opened L/Fs on 1003-97 @14:15 to safely replace./// Replaced arm and xfmr Reastored @ 15:15
13040 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-03-10 18:25 | 2017-03-10 20:45 | 3 | 140 | H1256285-1 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830430B00004 TO 38830430B09003 NEU AND HOT LEG OF OPEN WIRE SEC DOWN (1 CUST ORIG)--OPEN TRAN 83-430B/4 AT 18:25 OPEN TRAN (3 CUST) ---TEMPREPAIRS MADE--TRAN IN AT 20:45 (4 CUST)--ALLGOOD--DS031017--WILL NEED TEC TO REPLACE OPEN WIRE W/TWIST/ ISO 38830430B00004/ COD 4/ DUPLICAT IN HOIS/ VER/BOW
13041 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-03-07 09:20 | 2021-03-07 12:50 | 2 | 210 | 4311441 | 420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout , replaced , power back on @ 12:50
13042 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-06-24 13:36 | 2015-06-24 20:35 | 1 | 419 | 4651421 | 419 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | UNDERGROUND CREW REQUIRED SEC WILL NEED TRACED TO FIND, NO VOLTAGE INSIDE METERBASE RELEASED BY CREW 078S11//BAD SEC CONNECTIONS//OPENED TRANS @ 1900//REPAIRED @ 2035UNDERGROUND CREW REQUIRED SEC WILL NEED TRACED TO FIND, NO VOLTAGE INSIDE METERBASE RELEASED BY CREW 078S11..1 .BAD HOT LEG FEEDING 1043 PANSY LANE. REPAIRED..BLR VER/CRB
13043 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-09-27 07:16 | 2021-09-27 14:15 | 1 | 419 | 4293421 | 419 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Line fuse open @74-16, checking. Bad cutout and dead end bell @74-150, will be changing out. Got cutout and dead end replaced, closed L/F back in @1415.
13044 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-12-23 09:31 | 2008-12-23 16:30 | 1 | 419 | 63013-1 | 419 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411802//SERVICE SHORTED OUT,BURNED UP.GOING TO HAVE TO UPGRADE SERV.HAVE CONTACTED PVILLE AND CREW WILL BE HERE SOON WITH BIGGER DROP,ETC REPLACED 2/0 4-COND. WITH 4/0 4COND. AND RE-ENERGIZED BANK . RBW// VER/DBM L3/KEP IDC XXXX
13045 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-08-22 03:46 | 2018-08-22 10:45 | 1 | 419 | 4986271 | 419 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | : Dispatched in accordance with KYPCo Late Night Callout Guidelines./no crew required 6t fuse L3/HFP
13046 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2021-12-11 08:46 | 2021-12-11 15:15 | 3 | 389 | 4172671 | 419 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV NEUTRAL&1 LEG BROKEN,WILL REPAIR////////WHERE POLE WAS JERKED EARLIER,MUST HAVE CAUSED THE PROBLEMS WITH THE SERVICE//////////made repairs&restored,all ok afterwards/ opened transformer 1500 to 1515/// **Per Servicers nots "where pole was jerked earlier" I assume he is referring to order 4170491 where the service drop broke. it was jerked at pole 38820966D00074 on that order***-BOW
13047 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-09-15 22:01 | 2022-09-16 05:00 | 1 | 419 | 4887711 | 419 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | pole 180-140 bad 15kvs 7200 xfmer. no trk. side of hill in pasture. Released by crew 078S07//cod 1
13048 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-12-12 08:12 | 2009-12-12 15:10 | 1 | 418 | 60991-1 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OPEN ON 747-220, 15 KVA TRANSFORMER BAD ON POLE 747-332, CUSTOMER HAS ADDED 5 TON ELECTRIC HEAT PUMP / WILL NEED FLAGMEN / TRUCK ACCESS RELEASED BY CREW 074S03 VER/KEP L3/KEP
13049 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2015-09-26 08:13 | 2015-09-26 11:42 | 2 | 209 | 4273231 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW,FOREMAN,2MEN,BUCKET,BELIEVE ALL CAN BE LOWERED ON POLE & BE OK////////TOP OF POLE,ABT 2FT,BURNED OFF COD-2 ISO LF 38820868D00042 VER/HFP L3/HFP
13050 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-10-27 17:06 | 2009-10-27 20:35 | 2 | 209 | 58903-1 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN. I HAVE TO CALL TO HAVE SOMEONE BRING ME ONE. BILLY CHANGED CUTOUT. IDC XXXX
13051 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-02-17 10:45 | 2022-02-17 14:14 | 2 | 209 | 4490941 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans Cutout broke at 165-183,Will be making repairs..Restored at 14:14.
13052 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2014-11-02 09:16 | 2014-11-02 12:45 | 2 | 209 | 4692331 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. WILL BE CHANGING OUT. CHANGED BAD CUTOUT FUSED UP EVERYTHING OK// COD 2//VER/ ADH
13053 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-01-07 20:30 | 2019-01-08 03:28 | 1 | 418 | 4638741 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required 117-67 bad transformer 1 customer/19.9 25kva/trucks ok Released by crew 078S03,repairs made all cust restored please close ticket thanks.bt//cod 1//iso 38830117B00067
13054 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2022-06-05 06:16 | 2022-06-05 09:45 | 2 | 209 | 4019941 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout door, changing
13055 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-04-06 11:49 | 2015-04-06 15:18 | 2 | 209 | 4280211 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERV DROP TO REPAIR////BAD XFR,BUSHING BROKEN,CREW ENROUTE TO CHANGE XFR RELEASED BY CREW 074S06 REPLACED XFMR ON AT 15:18 D SAMMONS VER/CRB
13056 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-12-15 19:25 | 2008-12-15 22:54 | 2 | 209 | 58734-1 | 418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001002//POLE FIRE AT 38830279000217, ISOLATED AT 38830279000024, 1 CUSTOMER OUT, LIFTED HOT TAP AT 19:25, NO CUST OUT UNTIL THEN. BILL FRALEY HAS BEEN NOTIFIED AND IS LOADING METERIAL. RELEASED BY CREW 078S05//COD 2//ISO 38830279000024// VER/DBM L3/KEP IDC XXXX
13057 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-01-13 05:26 | 2011-01-13 08:55 | 2 | 209 | 60992-1 | 418 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | XFMR SECONDARY LEAD BURNED UP, WE REPLACED IT M.D.I.//VER/CRB IDC XXXX
13058 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-29 20:41 | 2014-01-29 23:00 | 3 | 139 | 4326081 | 417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKE. RESTORED @ 23:00. SH VER/KEP IDC XXXX
13059 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-06-14 16:51 | 2019-06-14 19:10 | 3 | 139 | 4508121 | 417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout
13060 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-11-15 07:16 | 2008-11-15 09:35 | 3 | 139 | 65059-1 | 417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401702LINE FUSE OUT LIGHTNING ARRESTOR BLOWN ON SIDE TAP, THEIR WERE ONLY 4 CUSTOMER OUT. LINE FUSE ON POLE 74-16 AND THE TRANS FUSE ON POLE 16 ALSO OUT VER/KEP IDC XXXX
13061 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2017-11-11 10:05 | 2017-11-11 12:24 | 3 | 139 | 4549181 | 417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I replaced bad cutout
13062 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-02-19 13:20 | 2011-02-19 15:39 | 3 | 139 | 59278-1 | 417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WR#38870218 FOUND NOTHING SERVICE ONWR#38870218 POLE 1147-791WR#38870218 SEND TO WRONG PLACE POLE IS 1147-491 OPENED TRANS. 13;20 PM SEC. UNDERGROUND SHORTED OUTWR#38870218 ISOLATED SEC. PED. WHICH FEEDS MTR#435943567// CUST IS OK WITH MAKING REPAIRS 02-21-11 OPS ORDER #35989106// CUST IS OK WITH MAKING REPAIRS 02-21-11 OPS ORDER #35989106// POWER RESTORED @ 15:39 J. HEMLEPP RELEASED BY CREW 078H05//VER/CRB IDCC PN4566 XXXX
13063 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-11-03 15:16 | 2019-11-03 22:13 | 1 | 417 | 4287541 | 417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 7200 c/o nbt--crew req-ds110319 Released by crew 078S01///replaced bad cutout///complete BR//cod 1
13064 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2014-09-01 21:16 | 2014-09-01 23:35 | 3 | 139 | 4446361 | 417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 80T LINE FUSE OUT ON POLE 42-C-184. B PHASE OPENEN A&C PHASE AT 22:38. ALSO HAD 2 -6T TRANSFORMER FUSE OUT ON POLW 42-C-196 I HAVE REPAIRS MADE ON POLE 42-C-196 COD 3 CHANGE ISO POLE VER/SEF
13065 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-06-05 23:22 | 2009-06-06 00:14 | 8 | 52 | 66661-1 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK-INSTALLED 12T FUSE COD-8 VER/KEP L3/KEP IDC XXXX
13066 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-07-28 13:12 | 2021-07-28 16:40 | 2 | 208 | 4971561 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse out, bad 25 kva, 19.9 truck access, power restored, only two customers
13067 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-01-01 15:30 | 2009-01-01 17:14 | 4 | 104 | 50606-1 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308603//REPLACED TRANSFORMER//VER/CRB L3/KEP IDCC TOF1416 ESTIMATED TIME OFF XXXX
13068 | Hazard | 3309301 | VICCO | REDFOX | 2015-02-05 08:17 | 2015-02-05 11:45 | 2 | 208 | 4991881 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2/3 SECONDARY IS BAD BETWEEN POLES, CALLING FOR ROLL OF 1/0 SERVICE WIRE, HELP COMING, CONNECTIONS FAILED IN SECONDARY. POWER RESTORED/ ISO 37830253000067/ COD 2/ VER/BOW L3/HFP XXX
13069 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2017-09-27 09:02 | 2017-09-27 12:30 | 2 | 208 | 4392811 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEE H4392811 39831072C45564 2 CUSTOMER OUT ORIGINALLY/ FOUND NEUTRAL AND HOTLEGS BURNTED INTO ON POLE 1072-5564, 1/0 SEC, NO CREW REQ TOOK CARE OF IT MYSELF, ALL REPAIRS ARE MADED AT THIS LOC AND EVERYONE IS BACK ON, OPENED XFMR 39831072C45564 TIME OFF WAS 1200 TIME ON WAS 1230 (7 ADD CUST) BY AMG/ DUPLICATE IN HOIS/ VER/BOW
13070 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-12-03 12:09 | 2022-12-03 13:53 | 4 | 104 | 4224381 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cracked 19/9 cut out, replaced.
13071 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-09-20 19:01 | 2009-09-20 20:45 | 4 | 104 | 55824-1 | 416 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP PART POWER ON LASH SECONDARY, BAD CONNECTION AT XFMR, RESTORED POWER AT 20:45 L3/HFP IDCC CNT1 XXXX
13072 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2022-11-21 13:11 | 2022-11-21 14:55 | 4 | 104 | 4169061 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse on 38830576D00131 open, door burned up, power restored at 1455
13073 | Whitesburg | 3401301 | FLEMING | NEON | 2012-04-17 10:47 | 2012-04-17 14:15 | 2 | 208 | 4679601 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WE HAVE A BAD XFMR, CREW WILL HAVE TO CHANGE. XFMR IS A 25 KVA 7200 LOCATED AT JRS. BARBER SHOP IN NEON RELEASED BY CREW 077S12//COD 2// VER/DBM IDC XXXX
13074 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2016-02-05 20:37 | 2016-02-05 22:21 | 4 | 104 | 4679971 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..CHANGING/ ISO 38830801000024/ COD 4/ VER/BOW
13075 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-11-28 06:22 | 2012-11-28 09:50 | 2 | 208 | 4427121 | 416 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP SHORTED OUT AT SPLICE. SERVE-END FAILED AND BURNED NEUTRAL AND 1 HOT LEG INTO IN SERVICE DROP. I RESPLICED DROP. THERE ARE 2 CUSTOMERS SERVED OFF THIS ONE SERVICE DROP. NO ONE HOME AT 1 RESIDENT AND THE OTHER CUSTOMER DID NOTSEEM TO HAVE DAMAGES. VER/HFP L3/HFP IDC XXXX
13076 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-05-22 16:41 | 2018-05-22 19:57 | 4 | 196 | 4395141 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 115-94, bad 19.9 c/o . trk to pole. crew reqd. station zone/ ISO 38830115D00094/ COD 4--crew on site--made repairs--pwr restored at 19:57---tbl tkt comp---rmv/ 38830115D00094 @ 1957 (4 cust)/ 38830115D00094 1945 to 1957 (2 cust)
13077 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-12-28 15:42 | 2021-12-28 19:10 | 2 | 208 | 4233031 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Clamp failed on pole 398C-185. Need one man. Manual. Power restored at 19:10.
13078 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-02-03 09:25 | 2018-02-03 11:33 | 7 | 128 | 4797471 | 416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | found connection burnt into on one sec. conductor...repairs made...opened @ 10:45 and closed back @ 11:33...//COD 1 FROM THE BEGINNING
13079 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2021-03-11 20:35 | 2021-03-12 01:25 | 6 | 290 | 4328391 | 415 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | hot leg going bad on UG/crew reqd. send to B Reynolds. // Opened trans at 01:00 closed trans at 01:25 // cod 1 (+5) //
13080 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-01-28 22:17 | 2014-01-28 23:40 | 5 | 83 | 4320731 | 415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE EITHER BROKE OR MELTED OUT ON 25KVA 810-212. RE-FUSED @ 23:40. SH VER/KEP IDC XXXX
13081 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2015-02-25 07:42 | 2015-02-25 09:05 | 5 | 83 | 4079591 | 415 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | POLE 45-7260 8T FUSE BROKE SEND NOTE TO TEC. TO WRITE JOB ALL CUTOUTS AND LA NEED CHGED ASAP/ ISO 38830045D37260/ COD 5/ VER/BOW
13082 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-09-12 23:44 | 2008-09-13 06:39 | 1 | 415 | 62024-1 | 415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3007904//BAD TRANSFORMER,,,ON POLE 574-139 15KVA 7200V IT IS TRUCK ACCESIBLE FROM DRIVEWAY RELEASED BY CREW 078S02/CREW ON SITE/FETR0700/VEM/XFMR CHANGED AND POWER RESTORED AT 0639/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN IDC XXXX
13083 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-11-30 17:25 | 2008-12-01 00:20 | 1 | 415 | 53292-1 | 415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR - DIFFICULT LOCATION. DUTY SUPERVISOR NOTIFIED, CREW EN-ROUTE.//3401801. REPAIRS COMPLETE. HAD FUSE ON POLE 38830655B00028 OPEN FROM 11:00 TO 12:20 INTERRUPTING 2 CUSTOMERS. SH //VER/GAH IDC XXXX
13084 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-09-20 00:35 | 2008-09-20 07:30 | 1 | 415 | 65690-1 | 415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR FUSE ON MTN IS OUT,VERY DIFFICULT LOCATION TO GET TO.HAVE CALLED DALE TO GET ME ONE MAN OUT TO HELP ME TO HOLD LITE ETC.ALSO KILLED COPPERHEAD BACK THERE LAST WEEK WHEN WE HAD TROUBLE HERE,PRIM WIRE WAS DOWN HEREXFR IS BAD,CREW ENROUTE WITH REPLACEMENT,NOTE FETR CHANGE RELEASED BY CREW 074S06CREW 074H03 REPLACE XFMR, COMPLTED 07:30. DEH. VER/PDP IDC XXXX
13085 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2021-07-02 09:26 | 2021-07-02 10:49 | 5 | 83 | 4846911 | 415 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad secondary connection at TR--opened TR at 1024 to make repairs Bad secondary connection on pole 272-A3-235. Power off at 10:30 restored at 10:49.
13086 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-08-17 23:22 | 2009-08-18 00:45 | 5 | 83 | 63467-1 | 415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3003701//BROKEN FUSE ON POLE 38830160000114, PLEASE ADD FUSE TO MAP, 10T FEEDING TO POLE 160-189 ONLY. MADE A MAP DISCREPANCY ON THIS FUSE... IDCC PN189 XXXX
13087 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-08-28 18:06 | 2008-08-28 20:24 | 3 | 138 | 57119-1 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202201// TRANSF FUSE BLOWED//1957 OPENED C PHASE ON REC 746/243//COD 753202201// TRANSF FUSE BLOWED. CUTOUT BAD//VER/CRB IDC DID WE OPEN OR WAS IT OPEN IDCC CNT75 XXXX
13088 | South Williamson | 3411401 | DEWEY | INEZ | 2015-07-06 18:43 | 2015-07-06 22:10 | 2 | 207 | 4734411 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMER FUSE BLEW ON POLE 742-66///FUSE BROKE IN XFMER CUTOUT///REFUSED AT 22:10///COMPLETE BR/ ISO 38830742D00066/ COD 2/ VER/BOW
13089 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-11-11 18:03 | 2010-11-11 21:30 | 2 | 207 | 55006-1 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAYONET FUSE BAD..EN ROUTE TO OFFICE TO PICK ONE UP.. RE FUSED EVERY ONE BACK ON..BB VER/HFP L3/HFP IDC XXXX
13090 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-01-22 08:27 | 2020-01-22 10:45 | 3 | 138 | 4327981 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRF IS OUT,WILL RE-FUSE////////////RE-FUSED&RESTORED,APPEARED TO HAVE SIMPLY BROKEN
13091 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2017-03-04 09:21 | 2017-03-04 16:15 | 1 | 414 | 4519071 | 414 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NEW FENCE, BAD HOT LEG ON UG SERVICE. POWER TEMP & CREW REQD RELEASED BY CREW 078S07--BAD SECONDARY FEEDING 2 TRAILERS---INSTALLED POWER TEMP---BOTH TRL VOLT CK OK---RMV RELEASED BY CREW 078H16////MADE AED FOR POWER TEMP VER/CRB
13092 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-04-12 04:33 | 2008-04-12 08:00 | 2 | 207 | 50306-1 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED DRT TO HELP// REPLACED BAD CUTOUT//3008702//VER/CRB IDC XXXX
13093 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2011-09-01 10:15 | 2011-09-01 13:42 | 2 | 207 | 4780321 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUS IS OUT,ALSO XFR ON THAT PHASE NEXT POLE OUT,MAY HAVE BEEN VINES,WILL RE-FUSE///////BAD 15KVA XFR ON POLE 1113-201,7.2KV,CAN USE TRUCK RELEASED BY CREW 074S06 //VER/CRB IDC XXXX
13094 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-02-01 20:15 | 2011-02-01 23:42 | 2 | 207 | 52907-1 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38656095 //XFR CUTOUT BURNED XARM IN TWO,MASSEY SAID P LAYNE AND BIG BUCKET WILL BE HERE SHORTLY TO HELP REPAIR,SEND TO TIM HALL TO REPAIR COD-2 ISO TF 37830071000235 VER/HFP L3/HFP IDC XXXX
13095 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-03-04 17:47 | 2021-03-04 20:05 | 3 | 138 | 4304271 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke cutout on 265-D-137,Going to change it and restore service.Made repairs and restored at 20:05
13096 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-04-04 11:08 | 2017-04-04 14:35 | 2 | 207 | 4612331 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 19.9 XFMR//CUSTOMER SAID FIRE WAS COMING OUT OF TOP OF XFMR//IT IS BLACK AROUND SIDE BY PRESSURE VALVE///NEED LINE CREW WITH MATERIAL HANDLER AND XFMR//REPAIRS MADE//RESTORED AT 14:35//COMPLETE//EM/ ISO 38820794D00026/ COD 2/ VER/BOW L3/HFP XXXHFP
13097 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2019-07-20 12:09 | 2019-07-20 12:55 | 9 | 46 | 4737441 | 414 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | opened xfr @ 12:45 closed @ 12:55 to replace xfr connections complete L3/HFP
13098 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-12-11 18:33 | 2013-12-11 22:00 | 2 | 207 | 4154661 | 414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 3 MAN PRC CREW--TRUCK TO POLE RELEASED BY CREW 078S07FETR// 22:15//JEH/ REPAIRS COMPLETE POWER RESTORED @ 22:00// JEH //VOD 2// VER/DBM L3/HFP
13099 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-01-08 01:07 | 2012-01-08 08:00 | 1 | 413 | 4240581 | 413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL DISPATCH AT DAYLIGHT . 6T FUSE BROKE VER/ARN IDC XXXX
13100 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-06-30 08:37 | 2008-06-30 15:30 | 1 | 413 | 59962-1 | 413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S03/BAD CUTOUT DOOR COD-1 VER/HFP IDC XXXX
13101 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-06-13 12:22 | 2013-06-13 19:15 | 1 | 413 | 4274631 | 413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED R BONDS CREW GOING ON IT RELEASED BY CREW 078S03//LR SAYS THIS HAS BEEN COMPLETED. CLOSE TICKET//GAB IDC XXXX
13102 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2019-10-08 20:58 | 2019-10-08 21:57 | 7 | 59 | 4121841 | 413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Earlier fault on xfmr 760-304 melted line fuse out and finished off failing cutout door. Replaced door and restored @ 21:57. sh L3/HFP
13103 | Pikeville | 3421001 | BREAKS | CITY | 2020-09-21 08:47 | 2020-09-21 15:40 | 1 | 413 | 4481491 | 413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Underground going to parsonage one leg is about burnt into ///Cut open @ xfm to make safe will need crew to make repairs//Send to Rick Ray Released by crew 074S02 CREW ON SITE, WAITING FOR A SPLICE FROM PIKEVILLE; OPENED X-FMR AT 15:36 CLOSED BACK IN AT 15:40
13104 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2010-07-13 08:22 | 2010-07-13 15:15 | 1 | 413 | 65817-1 | 413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 35960668 // CONNECTOR FAILED ON 4/3 SERVICE AND BURNED SERVICE DOWN CALLING FOR CREW TO ADD POLE AND SECONDARY RELEASED BY CREW 077S04 SET POLE AND REPLACED WIRE , RESTORED POWER AT 1515 JKC // COD-6 VER/HFP L3/HFP IDC XXXX
13105 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-08-17 00:52 | 2009-08-17 02:35 | 4 | 103 | H59824-1 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001202//TRANSFORMR FUSE OUT ON POLE 38830069A31251--CALLING TREE CREW-OPENED LINE FUSE ON POLE 38830069A31059 AT 12:52 BACK ON AT 02:35-- BAD 25KVA TRANSFORMER ON POLE 38830069A31251 WITH 8 CUSTOMERS OM IT-TRUCK OK-CALLING CREW RELEASED BY CREW 078S07 //VER/GAH IDCC DUP TO OPEN FUSE XXXX
13106 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2022-05-27 11:49 | 2022-05-27 15:15 | 2 | 206 | 4965521 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN 7.2 XFMR C/O // MAKING REPAIRS // RESTORED @ 15:15
13107 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-11-28 21:38 | 2016-11-28 23:21 | 4 | 103 | 4137311 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT VER/CRB
13108 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2009-12-13 14:30 | 2009-12-13 16:13 | 4 | 103 | 51994-1 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 25KVA TRANS. RELEASED BY CREW 078S08/CREW ON SITE/FETR1645/VEM/XFMR CHANGED AND POWER RESTORED/1613/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/KEP L3/KEP
13109 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-12-09 14:31 | 2012-12-09 16:14 | 4 | 103 | 4454311 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT//COD 4// VER/DBM IDC XXXX
13110 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-01-17 08:22 | 2009-01-17 11:48 | 2 | 206 | 57069-1 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD 2 WR# 28105408 /// TRANS. FUSE HAS BLOWN. I AM GOING TO REFUSE TRANS. COD 2 - 38821011B000163411801// TRANS. FUSE HAS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. IS BAD ON POLE 1011-16. ITS A 10 KVA TRANS. 19.9 VOLTAGE. WE NEED TO CHANGE TO A 25KVA. RELEASED BY CREW 074S01 L3/HFP
13111 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2022-08-07 17:34 | 2022-08-07 21:00 | 2 | 206 | 4700261 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout //cod 2
13112 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-10-07 06:11 | 2019-10-07 09:37 | 2 | 206 | 4105971 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broken. no truck.changing.
13113 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-07-27 08:11 | 2010-07-27 09:54 | 4 | 103 | 57720-1 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 2 XFR FUSES OUT,POLES 1056-116 AND 1056-242,ALSO 1 LINE FUSE ON 1056-33,WILL REPAIR ALL//////////////////MADE NECESSARY REPAIRS AND RESTORED COD-4 VER/HFP L3/HFP IDCC CNT2 XXXX
13114 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-05-15 13:59 | 2020-05-15 17:25 | 2 | 206 | 4839071 | 412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse on pole 1076-109 is out. refused and restored at 1725
13115 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-06-17 21:05 | 2021-06-17 23:22 | 3 | 137 | 4765451 | 411 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Power restored @ 23:22
13116 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-08-16 21:07 | 2018-08-16 23:24 | 3 | 137 | 4962691 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced failed cutout//cod 3
13117 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2021-08-27 18:13 | 2021-08-27 20:30 | 3 | 137 | 4163341 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout apr at 2030 close ticket
13118 | South Williamson | 3411401 | DEWEY | INEZ | 2015-05-01 16:43 | 2015-05-01 19:00 | 3 | 137 | 4382441 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 548-A-16 NTA CHANGED CUTOUT OUT// VER/ ADH
13119 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-05-07 11:55 | 2012-05-07 14:12 | 3 | 137 | 4755031 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN TRANSFORMER FUSE//COD 3// VER/DBM IDC XXXX
13120 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-10-11 11:36 | 2014-10-11 18:27 | 1 | 411 | 4606721 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THIS REPLACES ORDER 4606051 //POLE TOP BURNT OFF NEED 3 MEN & FLAGGING CREW & 4` FIBERGLASS POLE EXTENSION & CUTOUT // OPENED STEPDOWN @ 1336 //R VIRGIN & YOUNGMAN & CANTRELL & SIMMONS // LINE OPENED & GR & TAG TO RON V AT 429D-67 R FLAGGERS TO MEET @ BIRDHOUSE 1CUST INITALLY OUT // INTERRUPTED 71 @ 1336 COD-72 ISO LF 38830429D00067 SEE DUP IN HOIS H4606721 FOR 71 CUST // VER/HFP L3/HFP AJB
13121 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2021-12-02 10:23 | 2021-12-02 12:40 | 3 | 137 | 4141091 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout apr at 1240 close ticket
13122 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2012-09-01 15:58 | 2012-09-01 18:15 | 3 | 137 | 4991951 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT WAS BROKEN TOOK IT OFF LINE AT 1558 - NEED CREW TO REPLACE CUT-OUT TRUCK SHOULD BE OK TO USE CUST SAID IT WOULD BE OK // TOLLIVER, PHILLIP & MULLINS, VERNON & MCCANN, NICK CUT-OUT WAS BROKEN TOOK IT OFF LINE-NEED CREW TO REPLACE CUT-OUT TRUCK SHOULD BE OK TO USE CUST SAID IT WOULD BE OK // TOLLIVER, PHILLIP & MCCANN, NICK//COMPLETE POWER RESTORED AT 18:15 PRT COD-3 ISO TF 38830211000022 VER/HFP L3/HFP
13123 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-05-13 22:39 | 2011-05-14 00:56 | 3 | 137 | 4088581 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER ON 429-323 APR AT 056 CLOSE TICKET VER/PDP
13124 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-03-23 08:58 | 2015-03-23 11:15 | 3 | 137 | 4218381 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED 19.9 CUTOUT/COD 3// VER/ ADH L3/DKGXXXX
13125 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-12-23 14:18 | 2011-12-23 16:35 | 3 | 137 | 4199041 | 411 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WATER HAS JUNCTION BOX FULL OF WATER AND CONNECTIONS HAVE BURNED INTO. I AM GOING TO TRY TO FIX TEMP. I BAILED WATER OUT OF JUNCTION AND SPLICED CONDUCTORS TEMPORARILY. TIM HALL IS SUPPOSE TO GET WITH LANDLORD TUESDAY AND WORK OUT A SOLUTION TO THIS PROBLEM. VER/HFP L3/HFP IDC XXXX
13126 | Whitesburg | 3312901 | JENKINS | KONA | 2015-09-30 00:23 | 2015-09-30 02:40 | 3 | 137 | 4292751 | 411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CHANGED BAD INSULATOR ON POLE 304-136 VER/SEF
13127 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-10-01 11:47 | 2013-10-01 15:12 | 2 | 205 | 4901771 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN ON POLE 37830247C00276, BAD 25 KVA, 7.2KV TRANSFORMER. RELEASED BY CREW 077S04TRANSFORMER FUSE BLOWN ON POLE 37830247C00276, BAD 25 KVA, 7.2KV TRANSFORMER. ==== REPLACED TRANSFORMER, POWER RESTORED. COD-2 ISO TF 37830247C00276 VER/HFP L3/HFP IDC XXXX
13128 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-01-09 11:18 | 2010-01-09 18:08 | 1 | 410 | 51111-1 | 410 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | WR 33371681 BAD UNDERGROUND 1/0 WIRE RELEASED BY CREW 078S08 IDC XXXX
13129 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-04-06 07:45 | 2022-04-06 08:26 | 10 | 41 | 4728081 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | outage here per levi grayson // all pwr restored 08:26 please close LRM
13130 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-04-23 19:15 | 2020-04-24 02:05 | 1 | 410 | 4742741 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | crew required can cut poleoff fire is out trucks ok/tagged fuse to reynolds Released by crew 078S03
13131 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-10-14 17:56 | 2009-10-14 21:21 | 2 | 205 | 63402-1 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS BROKE CUTOUT//VER/CRB IDC XXXX
13132 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-05-10 18:13 | 2010-05-10 21:38 | 2 | 205 | 59261-1 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA XFMR. DUTY SUPERVISOR NOTIFIED AND CREW IS ENROUTE. XFMR REPLACED. RESTORED @ 21:38. SH COD-2 VER/HFP L3/HFP IDC XXXX
13133 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-12-20 10:00 | 2017-12-20 13:25 | 2 | 205 | 4660141 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 8ft cross arms burnt off @ 182-3518,, lifted hot taps @ 182-6163 to get load off of building ,,need 2 8ft crossarms and 6 12kv cutouts
13134 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-10-21 09:15 | 2008-10-21 12:40 | 2 | 205 | 57551-1 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP 3008702//RESEND RELEASED BY CREW 078S073008702//RESEND // BROKEN FUSE LINK BURNT UP CUTOUT DOOR PER SERVICER THIS ONLY FEEDS 1 CUSTOMER IDC XXXX
13135 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-10-09 22:25 | 2010-10-10 05:15 | 1 | 410 | 58381-1 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 75KVA 7200 120/240 2 BUSHING XFMR, CREW REQUIRED, NEED NEW XFMR AND 500MCM COPPER, OPENED OTHER 2 XFMRS AT 22:25, ONLY 1 CUSTOMER OUT. PLEASE SEND TO B REYNOLDS RELEASED BY CREW 078S05 VER/ARN IDCC PN91, XXXX
13136 | Hazard | 3303901 | LESLIE | HYDEN | 2009-02-09 19:01 | 2009-02-09 19:42 | 10 | 41 | 57194-1 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP RELATED TO ORDER 57205-1 CREW HAD TO OPEN LINE FUSE TO ALLOW THEM TO SAFELY REPAIR PRIMARY CONDUCTOR THAT IS LAYING ON A CROSS ARM L3/HFP
13137 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-01-06 08:15 | 2009-01-06 15:05 | 1 | 410 | 51813-1 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3301701 - BAD TRANSF == 5 KVA TRANSF == NEED LINE CREW == CALLED GEN COMBS TO GET CREW == RELEASED BY CREW 077S03 JAMES SUMNFERS , DHE IS WORKING THIS JOB... ALL NO TRUCK.. VER/KEP L3/KEP IDC XXXX
13138 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-05-01 16:43 | 2018-05-01 20:08 | 2 | 205 | 4295001 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Called customer: no answer . Bad CSP xfmr, will need 25 kva 7200 xfmr,,, restored power at 20:08..
13139 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-03-13 07:02 | 2014-03-13 13:52 | 1 | 410 | 4487271 | 410 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK AT REGULAR TIME. PART POWER DUE TO BAD CONNECTION IN SERVICE DROP MADE REPAIRS RESTORED POWER AT 13:52 VER/HFP L3/HFP
13140 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-07-13 11:07 | 2009-07-13 14:32 | 2 | 205 | 50042-1 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3301701// BAD TRANSF == NEED LINE CREW AND BIG BUCKET === NEED A 15 KVA TRANSF 7200 KV == RELEASED BY CREW 077S03 // 1432 VER/TOM L3/TOM IDC XXXX
13141 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-06-05 13:53 | 2019-06-05 15:15 | 5 | 82 | 4431841 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | off at 15:00 back in @ 15:15. informed cust they need to make arrangements to remove all the vegetation on their service drop. bad spot in service, spliced hot leg. send to forestry to cut out sec between pole 38830020C14030 & pole 38830020C14031.
13142 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2021-07-13 09:46 | 2021-07-13 13:11 | 2 | 205 | 4904891 | 410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | cust had hotlead burn in too..i opened transformer on pole 34D-35 @ 12:30 made repairs and transformer back in at 13:11..
13143 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-02-10 13:36 | 2019-02-10 20:25 | 1 | 409 | 4774911 | 409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad neutral/ underground. Wire spliced before on pole. Conduit busted at ground level also, bring three new sticks of conduit. Mopads needed, trucks to pole. Send to bob reynolds Released by crew 078H04
13144 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2010-12-12 00:26 | 2010-12-12 07:15 | 1 | 409 | 65448-1 | 409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUST MAPPED WRONG....BROKEN XFRMR CUTOUT ON 988-B-110....NON TRUCK ACCESS....NEED 2 MEN TO CHANGE....CALLED CREW....RELEASING TICKET TO GO ON OTHER TROUBLE...JRV...// RELEASED BY CREW 080S01// WILL BE OUT TO WORK AT 0700 //VER/GAH IDCC PN13, CNT8 XXXX
13145 | Hazard | 3303902 | LESLIE | WOOTON | 2010-12-20 03:18 | 2010-12-20 10:07 | 1 | 409 | 54422-1 | 409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS FUSE BLOWN....BAD TRANSFORMER, NEED 19.9KV, 25 KVA, 120/240V TRANSFORMER, 2 MEN AND LINE TRUCK.....ALL POWER RESTORED @ 10:07 HRS. P.HICKS//COD 1// VER/DBM IDC XXXX
13146 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-07-10 14:44 | 2015-07-10 21:33 | 1 | 409 | 4764991 | 409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SVCR OR 2 MAN CREW REQUIRED, NEED 12 KV C/O, ARR AND BKT, TRUCK ACCESS RELEASED BY CREW 074E11 RELEASED BY CREW 079H01SVCR OR 2 MAN CREW REQUIRED, NEED 12 KV C/O, ARR AND BKT, TRUCK ACCESS RELEASED BY CREW 079H01/REPLACED CUTOUT, ARRESTOR & BRACKET, RESTORED POWER @ 21:33..MTH/ ISO 38830912D00018/ COD 1/ VER/BOW
13147 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-08-12 11:45 | 2021-08-12 18:34 | 1 | 409 | 4043841 | 409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad Ug service, bad hot leg isolated in meter base, and transformer open @ 11:45. Send to Rick Morgan to place power temp, or repair. New fence, and metal conduit slid down about 6 inches @ meter base. Splice in meterbase good. Customer requests to knock or call before showing up for dogs. If customer not home, dogs will be up. Released by crew 078S02 // replaired and restored @1834
13148 | Hazard | 3420001 | SOFT SHELL | VEST | 2015-02-20 08:35 | 2015-02-20 15:24 | 1 | 409 | 4052801 | 409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT,BAD XFMR, WILL NEED 25 KVA, 19.9 KV. MANUEL, SNOW COVERED DRIVEWAY RELEASED BY CREW 077S02 REPLACED TRANSFORMER AND RESTORED POWER AT 1524/ ISO 37830110000141/ COD 1/ VER/BOW L3/DKGXXXX
13149 | Hazard | 3309302 | VICCO | JEFF | 2009-01-01 10:56 | 2009-01-01 17:45 | 1 | 409 | 50487-1 | 409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3309302//BAD UNDERGROUND == WENT OVERHEAD WITH SERV == WILL WORK ON UNDERGROUND LATER == ALL CUST HAS POWER//1 OUTAGE//VER/CRB L3/KEP IDC XXXX
13150 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-10-07 10:36 | 2013-10-07 17:25 | 1 | 409 | 4917801 | 409 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD HOT LEG. THIRD PARTY SAID HE WAS PULLING STAKE AND GOT SHOCKED BESIDE XMF POLE. LINECREW REQUIRED TO INSTALL POWER TEMP RELEASED BY CREW 078S11 VER/CRB L/3 CRB IDC XXXX
13151 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-06-09 08:20 | 2008-06-09 15:09 | 1 | 409 | 60373-1 | 409 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3116702//BAD UNDERGROUND //VER/CRB IDC XXXX
13152 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-04-01 10:11 | 2019-04-01 12:27 | 3 | 136 | 4047221 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on pole 215-226..repairs made.restored.. COD 3
13153 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2013-07-10 18:28 | 2013-07-10 20:10 | 4 | 102 | 4500541 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY CONNECTION ON POLE 38820991D40213. PLEASE SEND TO CLIFF FREEMAN TO HAVE THIS POLE REPLACED. IT IS VERY BAD AND NO TRUCK ACCESS. VER/CRB L/3 CRB IDC XXXX
13154 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-08-04 16:53 | 2021-08-04 18:35 | 4 | 102 | 4005101 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout/replaced cutout & arrestor. pls close. tre
13155 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-08-05 14:14 | 2018-08-05 16:30 | 3 | 136 | 4910901 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//NEIGHBOR OUT ALSO//fuse on xfmr broke.changing
13156 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-08-22 18:18 | 2014-08-22 20:00 | 4 | 102 | 4405951 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 39831024A00186 TRANSFORMER IS BAD ,FEED ING TWO CUST FROM POLE39831024A00187 CAN FIX TRANSFORMER NXT WEEK GIVE TO LINE TO WORK POWER ON FOR NOW NO OUTAGE KWB//COD 4//EMAILED TO TECH AND LINE CREWS
13157 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2022-05-31 09:56 | 2022-05-31 13:20 | 2 | 204 | 4987021 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Theres a bad secondary connection on pole 175-89. I have a manual ROW crew coming to help and a line crew.
13158 | South Williamson | 3200302 | BELFRY | TOLER | 2013-03-25 15:14 | 2013-03-25 16:05 | 8 | 51 | 4957441 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TROUBLE TICKET ENTERED ON WRONG ACCOUNT. TRANSFORMER SECONDARY RISER BURNED OUT OF THE LUG. THIS IS ON THE BELFRY TOLER CIRCUIT. COD-8 ISO TF 38821039C00107 & 3200302 VER/HFP L3/HFP IDC XXXX
13159 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-03-19 17:34 | 2008-03-19 19:50 | 3 | 136 | 58801-1 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701// POLE 116-176 BAD CUT 6T POLE 116-8 25T// VER/TOM IDCC PN176 XXXX
13160 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-05-14 08:42 | 2015-05-14 09:50 | 6 | 68 | 4428651 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 078S07 SINGLE TRANS, OUT BACK -YARD POWER RESTORED KWB COD-6 ISO TF 38830045B22627 VER/HFP L3/HFP
13161 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-08-15 20:27 | 2009-08-16 03:15 | 1 | 408 | 59185-1 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3001002//OPEN WIRE SECONDARY DOWN AT POLE 38830278000104, CRE REQUIRED, #4 SOLID COPPER RELEASED BY CREW 078S05 //VER/GAH IDC XXXX
13162 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-12-09 08:36 | 2013-12-09 12:00 | 2 | 204 | 4132621 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON ARM// WILL REPLACE// REPAIRS MADE/POWER IS RESTORED VER/CRB L3/HFP
13163 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-05-20 14:17 | 2020-05-20 14:51 | 12 | 34 | 4869731 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE 1081-177 TO REPLACE BAD CUTOUT//////////REPLACED 2 XFR CUTOUTS WHILE OUTAGE WAS RUNNING,RESTORED,ALL OK AFTERWARDS
13164 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2013-06-18 11:19 | 2013-06-18 12:10 | 8 | 51 | 4364701 | 408 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 6T TRANS FUSE BROKE COD-8 ISO TF 38830045C45781 VER/HFP L3/HFP IDC XXXX
13165 | Hazard | 3309301 | VICCO | REDFOX | 2020-09-02 13:54 | 2020-09-02 16:10 | 3 | 136 | 4419991 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke on pole 323-200. restored 16:10
13166 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2016-01-19 15:19 | 2016-01-19 17:35 | 3 | 136 | 4633161 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV 7200 XFM NEED ONE MAN AND BIG BUCKET..CHANGED XFM ON POLE 37830024B40232 CLOSED IN @ 17:35.. VER/CRB
13167 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-09-24 15:52 | 2012-09-24 22:40 | 1 | 408 | 4083841 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 25KVA 240---480V HIGHSIDE HAS TWO BUSHINGS. ALSO NEED XMF BAG AND ALL NEW RISER WIRE #2 COPPER WITH NEW 19.9 CUTOUT AND ARRESTER, AND 2 CURRENT LIMMITTING FUSES. WATCH FOR DOGS THEY ARE TIED. RELEASED BY CREW 078S11//COD 2// VER/DBM IDCC PN22 XXXX
13168 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-05-28 03:32 | 2009-05-28 05:14 | 4 | 102 | 58365-1 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3001204//PATROLING LINE NOW LINEFUSE OUY ON POLE 93-141 25-T PTP PIN OFF POLE AT 93-402
13169 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-02-17 17:44 | 2008-02-17 20:00 | 3 | 136 | 64318-1 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308002 LOOSE CONNECTION IN HOT CLAMP VER/JHM IDCC CNT1 XXXX
13170 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-11-23 11:32 | 2021-11-23 12:40 | 6 | 68 | 4118791 | 408 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Opened transformer on 68-515 from 12:30 to 12:40 to repair bad connection on secondary. Restored @ 12:40
13171 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-11-18 20:41 | 2022-11-19 00:05 | 2 | 204 | 4160671 | 408 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer // large appliances not working //25kva, 19.9 has oil running down the outside and only has 60 volts on one of the secondary bushings. by truck //,repairs made all cust restored please close ticket thanks.bt // cod 2
13172 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-06-21 11:11 | 2011-06-21 14:35 | 2 | 204 | 4362011 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 673-72///NO TRUCK ACCESS// PAUL MUNCY BRINGING CREW TO HELP CHANGE// RELEASED BY CREW 079S01 ** AT 1411 , PAUL MUNCY ON SITE TO BEGIN REPAIRS. PAUL MUNCY REPAIRS ARE COMPLETED. IDC XXXX
13173 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-06-23 07:14 | 2010-06-23 09:30 | 3 | 136 | 55453-1 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND LINE FUSE OUT, HAD LEAD OUT OF THE BOTTOM OF CUTOUT THAT HAD BROKEN, ALSO PATROLLED LINE FOUND LOW PRI NEUTRAL ON POLE 1097-180, NEEDS TO BE SENT TO LINE CREWS, TO BE REPAIRED LATER ON, CAN NOT GET TRUCK TO THIS POLE RUNS THRU THE WOODS, BUT POWER IS RESTORED AT THIS LOC AT THIS TIME//COD 3// VER/DBM IDC XXXX
13174 | Hazard | 3309301 | VICCO | REDFOX | 2013-01-21 11:16 | 2013-01-21 12:58 | 4 | 102 | 4718541 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT COD-4 ISO TF 37830326B00042 VER/HFP L3/HFP IDCC FP NULL XXXX
13175 | South Williamson | 3411401 | DEWEY | INEZ | 2022-02-22 09:22 | 2022-02-22 12:46 | 2 | 204 | 4527141 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | middle phase blown on pole 744-a-398//cutout broke on pole 744-400//crew enroute//will have to open other two phases to make repairs//repairs made//restored at 12:46 Released by crew 079S01
13176 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2022-02-07 14:13 | 2022-02-07 16:29 | 3 | 136 | 4454531 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Kenny Coleman from tele-com reports outage at Wheelwright tower. Confirmed blank meter./////// Had a broke 19.9 cutout on pole 115-192.///// changed out cutout on pole 115-192 and got power restored at 16:29.
13177 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2021-08-31 11:59 | 2021-08-31 18:47 | 1 | 408 | 4184631 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 447-207.. need crew to replace.. manual pole. 19.9 cutout Released by crew 077S11
13178 | South Williamson | 3411401 | DEWEY | INEZ | 2010-04-30 15:18 | 2010-04-30 17:34 | 3 | 136 | 53188-1 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLOWN COUGHT THE HILLS ON FIRE. CLEARD ARRESTER UP VER/KEP L3/KEP IDC XXXX
13179 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-03-08 10:02 | 2017-03-08 11:44 | 4 | 102 | 4535101 | 408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR WAS NOT CLOSED ALL THE WAY DURING LAST WEEKS STORM DUE TO THE LOOSE BRACKET AND IT FELL OPEN. PLEASE SEND TO CLIFF FREEMAN TO HAVE THE CUTOUT AND THE STEEL BRACKET REPLACED. NO TRUCK ACCESS TO THIS POLE.
13180 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-04-25 18:58 | 2011-04-26 01:45 | 1 | 407 | 64817-1 | 407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39694023 //HAVE A BAD 25 KVA DOUBLE BUSHING TRANSFORMER, IS BAD, ROADSIDE, CAN USE TRUCKS, 120/240 WYE/DELTA, NEED CREW TO CHANGE, SEND TO MR. FRALEY.HAVE A BAD 25 KVA DOUBLE BUSHING TRANSFORMER, IS BAD, ROADSIDE, CAN USE TRUCKS, 120/240 WYE/DELTA, NEED CREW TO CHANGE, SEND TO MR. FRALEY. RELEASED BY CREW 078S06 COD-1 ISO TF 39830902A00101 VER/HFP L3/HFP IDC XXXX
13181 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2011-04-22 07:13 | 2011-04-22 14:00 | 1 | 407 | 61885-1 | 407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQ 39668051 // RELEASED BY CREW 078H14WORK REQ 39668051 // BROKEN CUTOUT ON POLE 329-153 NEED LINE CREW NO TRUCKS TO POLE.WORK REQ 39668051 // BROKEN CUTOUT ON POLE 329-153 NEED LINE CREW NO TRUCKS TO POLE. RELEASED BY CREW 078S01//FUSE PL #329-111 OPEN @ 13:45 CLOSED 14:00 REPAIRS COMPLETE @ 14:00 J. HEMLEPP - SECOND OUTAGE CREATED TO REFLECT OPEN LINE FUSE VER/TOM L3/TOM IDC XXXX
13182 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2010-09-20 16:13 | 2010-09-20 16:50 | 11 | 37 | 51636-1 | 407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE DOOR BROKE. REPLACED DOOR AND RE-FUSED @ 16:50. SH// COD 11// VER/DBM IDC XXXX
13183 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2020-05-01 20:00 | 2020-05-01 20:37 | 11 | 37 | 4786481 | 407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout. repairs made. pls close. tre/ 38830140A20581 cod11
13184 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-02-08 05:51 | 2017-02-08 12:38 | 1 | 407 | 4370171 | 407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 37830272B21230 TOP OF POLE BURNED OFF NEED LINE CREW AND SIDE BY SIDE TO GET TO POLE === PLACED GROUND ON POLE 37830272B21230 === RELEASED BY CREW 077S03. POWER RESTORED/ ISO 37830272B21230/ COD 1/ VER/BOW L3/HFP XXXHFP
13185 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-02-24 11:37 | 2015-02-24 15:00 | 2 | 203 | 4078191 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE BAD TRANAFORMER 7200, SINGLE BUSHING, MAP SHOW TO BE A 3 KVA, BUT LOOK LIKE A 15KVA, NEED CREW TO REPLACE TRANSFORMER, ALSO NEED AWP, CAN NOT USE TRUCKS, BUT MAYBE ABLE TO WINCH FROM ROAD, RELEASED BY CREW 078S06//COD 2//MD FILED// VER/DBM
13186 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-04-25 01:14 | 2018-04-25 08:00 | 1 | 406 | 4275781 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trnsfrmr 178-114 was never open--Ken Napier opened line fuse 178-161 due to line doiwn going to cell tower///top of pole 178-488 is gone, pole is still smouldering, difficult location, if we wait untill worktime im afraid we wont have enough pole left, will need line crew, dead-end and cutout with bracket/ ISO 37830178000161/ COD 1
13187 | Hazard | 3303902 | LESLIE | WOOTON | 2021-03-20 11:44 | 2021-03-20 18:30 | 1 | 406 | 4357621 | 406 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | splice failed in service drop Released by crew 077S07
13188 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-04-28 13:28 | 2011-04-28 16:51 | 2 | 203 | 51558-1 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DONT SEE ANY DAMAGE,XFR TO RE-FUSE//////XFR MUST BE DAMAGED INTERNALLY,FUSE CAME BACK OUT,WILL GET CREW & XFR////NOTE NEW FETR//////////////////////REPLACED AND RESTORED VER/KEP IDC XXXX
13189 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-07-21 11:16 | 2015-07-21 18:02 | 1 | 406 | 4925571 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM FUSE BLOWN WILL RE-FUSE R WORRIX & S GOBLEXFM FUSE BLOWN WILL RE-FUSE/// BAD 25 KVA 19.9 //// CAN USE BUCKET NEEDS TO BE 4 WHEEL DRIVE RELEASED BY CREW 074H17XFM FUSE BLOWN WILL RE-FUSE R WORRIX & S GOBLE/// ON SITE WAITING ON CREW. TIM MCCOYXFM FUSE BLOWN WILL RE-FUSE R WORRIX & S GOBLE/// ON SITE WAITING ON CREW./// CHANGED TRANSFORMER AND RESTORED POWER AT 18:02. TIM MCCOY RELEASED BY CREW 074H10 VER/CRB
13190 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-06-08 16:45 | 2021-06-08 20:08 | 2 | 203 | 4690451 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke Trans Cutout on 216-143,Going to get it changed and restore service..Restored @ 20:08.
13191 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-12-01 08:37 | 2016-12-01 09:35 | 7 | 58 | 4156941 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE INTO, I WILL CHANGE IT OUT 37830426D00016 VER/AWD L3/HFP HFPC CDC83 FP37830426D00315
13192 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-04-03 14:30 | 2019-04-03 15:28 | 7 | 58 | 4054331 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LIFTED TAP ON POLE 39831024B00088 TO REPLACE INSULATER ON SAME POLE//COD 7//OFF @ 1430 ON @ 1528 L3/HFP sjg
13193 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2012-07-09 14:34 | 2012-07-09 21:20 | 1 | 406 | 4647731 | 406 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | CREW REQUIRED, LEAD CAME OUT OF XFORMER. RELEASED BY CREW 078M03/CREW ON SITE.RM/MADE REPARIRS ON SEC. RISER CHECK VOLATGE,VOLTAGE OKTHERE IS NOT 33 CUSTOMERS OUT ONLY 1 OPENED BANKAT 21:00 CLOSED BACK IN AT 21:20 PLEASE CLOSE TICKET RM/CALLED CUSTOMER LEFT MESSAGE SO HE CAN TURN GENERATOR OFF VER/HFP L3/HFP IDC XXXX
13194 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2012-01-23 13:54 | 2012-01-23 17:17 | 2 | 203 | 4285941 | 406 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEND TO CREWS HOT TAP BROKE OFF 3 PHASE NEED BIG BUCKET RELEASED BY CREW 078S08/CREW ON SITE/FETR 1745/VEM/REPAIRS MADE AND POWER RESTORED 1717/PLEAE CLOSE TICKET/THANKS/VEM //VER/GAH IDC XXXX
13195 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-01-14 20:47 | 2010-01-15 03:33 | 1 | 406 | 54353-1 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR RELEASED BY CREW 077H03 VER/ARN IDC XXXX
13196 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-08-27 14:37 | 2008-08-27 18:00 | 2 | 203 | 56358-1 | 406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3314401//BAD CUTOUT AND ARRS. ALSO OING TO HAVE TO CUT SOME R-O-W//COD 2 IDC XXXX
13197 | Hazard | 3303902 | LESLIE | WOOTON | 2010-12-12 14:29 | 2010-12-12 21:15 | 1 | 406 | 65624-1 | 406 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38077808 // SPLICE BAD ON TRANSF == REPAIRED === POWER OK COD-1 ISO TF 37830342000202 VER/HFP L3/HFP IDC XXXX
13198 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-04-14 18:25 | 2022-04-15 01:10 | 1 | 405 | 4765091 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad 4/0 underground customer said it is all in conduit. cre required. talked to Levi G Released by crew 078S11. crew on site to make repairs put power temp on for a temporary fix power restored @ 01:10 complete. please send copy of ticket to vernon mullins//emailed to v mullins
13199 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-10-01 14:15 | 2015-10-01 15:36 | 5 | 81 | H4298121 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 250 STEPDOWN XFMR ON C PHASE AT POLE 376-18. WILL NEED FLAGGERS//OPENING OTHER PHASES @ 1415//COD 6 VER/CRB // PER VOICE RECORDER B PHASE STEPDOWN BAD & BUSINESS OBJECTS ALSO INDICATES B PHASE (66%) SCADA NO HELP = L3/HFP HFPC CDC92
13200 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-09-30 09:25 | 2008-09-30 09:40 | 27 | 15 | H52096-1 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000303//PART OF 52096-1//BROKE CUTOUT ON POLE 43-175// COD 2//SERVICER OPENED LINE AT POLE 43-160 @ 09:25 TO FIX BROKE CUTOUT//THIS INTERUPTED 27 MORE CUSTOMERS//ISO 38830043000160// OPENED SB ON POLE 43-160 09;25 ON 09;40//SENT REPORT TO MAPPING DBM// VER/DBM IDC XXXX
13201 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2018-11-02 18:20 | 2018-11-03 01:05 | 1 | 405 | 4358281 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke -- door burnt up--replaced-allgood-ds110318 L3/HFP
13202 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-10-01 03:25 | 2020-10-01 10:10 | 1 | 405 | 4516301 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Held in accordance with KPCO late night callout guidelines.door split out and fail open got door replaced and power restored 10:10
13203 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2019-01-18 09:55 | 2019-01-18 12:10 | 3 | 135 | 4684701 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke @ 761-241 calling crew now. Repairs made back to normal L3/HFP
13204 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-07-26 03:30 | 2016-07-26 10:15 | 1 | 405 | 4680231 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HAD BURNED INTO AT XFMR///REPAIRED CONNECTIONS///CUSTOMER HAD TURNED OFF MAIN BREAKER AND IT WILL NOT CLOSE BACK///HE IS GOING TO REPLACE BREAKER///I HAVE CUSTOMER DISCONNECTED//HE WILL CALL BACK FOR RECONNECT WHEN REPAIRS ARE MADE/ ISO 38820771B10470/ COD 1/ VER/BOW
13205 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-06-12 17:12 | 2015-06-12 19:27 | 3 | 135 | 4560851 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE WILL CHANGE//CHANGED BAD CUTOUT AND RESTORED SERVICE @ 19:27// VER/ ADH
13206 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-03-02 13:30 | 2018-03-02 14:15 | 9 | 45 | 4927831 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Ellis McKnight reports cutout on pole 158-23 is broken and re-energized from top of cutout and tail blowing on pole---no outage currently. all power restored /// SENT EMAIL ON TIMES OFF & ON = HFP
13207 | South Williamson | 3411401 | DEWEY | INEZ | 2009-08-04 12:24 | 2009-08-04 12:39 | 27 | 15 | 55308-1 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411401//OPENED C PHASE RECLOSER HERE TO ALLOW CREWS TO WORK ON STEPDOWN TRANSFORMER (SUSPECT IS BAD STPDWN XFRMR) IN ORDER 54331-1//COD 27// VER/DBM IDC XXXX
13208 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-12-16 22:05 | 2021-12-17 04:50 | 1 | 405 | 4203551 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad underground 1 hot leg went bad 2 days ago had power temp installed other hot leg failed// crew required to repair underground service///made repairs to UG///Complete BR
13209 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-04-04 04:45 | 2015-04-04 11:30 | 1 | 405 | 4271701 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED LINE CREW BAD TRANS. NEED 25KVA TRUCK TO POLE RELEASED BY CREW 078S08,,CREW ON SITE,,UPGRADED TO 25KVA,,,ALL POWER RESTORED L3/DKGXXXX
13210 | South Williamson | 3200301 | BELFRY | BELFRY | 2018-02-26 16:55 | 2018-02-28 23:20 | 2 | 405 | 4885151 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Part power here per Mike Hatfield//739 Forest Hills, Goody/mtr 533650103/ bad UG low voltage on one leg i think UG is in conduit need 160 ft of 1/0 UG creek bank has settled so conduit may be pulled in two or bring the add a phase over temporarily Released by crew 079H03/crew on siteop/xf 23:00 cl/xf 23:20. need to replace bad 1/0 ug ser./ ISO 38820990A00037/ COD 2
13211 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2022-01-27 04:36 | 2022-01-27 05:57 | 5 | 81 | 4407891 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse broke. Restored @ 5:57. sh
13212 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-08-05 16:10 | 2018-08-05 17:31 | 5 | 81 | 4911051 | 405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | xform risers & sec.loops burn into , cutout opened to easy need line crew& flaggers bad location on rd send to v. mullins Released by crew 078S04//opened trans @ 1610//closed 1731//no outage till transformer opened
13213 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-05-17 13:03 | 2008-05-17 16:25 | 2 | 202 | 65108-1 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3308502//XFMR FUSE OUT, BAD ARRESTOR TOOK OUT XFMR FUSE VER/HFP IDC XXXX
13214 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-12-02 01:49 | 2014-12-02 05:11 | 2 | 202 | 4824151 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ POLE 184-55 BURNT POLE NEED LINE CREW TO MAKE REPAIRS TO POLE RELEASED BY CREW 078S05/WILL NEED TO OPEN FUSE @184-C-30 FOR REPAIRS/APPROX TWO HOUR OUTAGE/ONLY TWO CUST OUT AT THIS TIME/OPEN FUSE@0407/VEM/REPAIRS MADE AND ALL CUST RESTORED 0511/PLEASE CLOSE TICKET/THANKS/VEM SHOWED LINE FUSE OUTAGE ON TICKET 4824501 VER/ARN
13215 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-03-05 16:53 | 2014-03-05 20:15 | 2 | 202 | 4454991 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830184B00260 H.AS A BROKEN LINE CUTOUT 19.9, ON BYPASS ON LEFT ON CLIFF. NEED CREW. JEFF COMBS CREW STANDING BY IN OFFICE. RELEASED BY CREW 077S08 REPLACED CUTOUT AND RESTORED POWER AT 2015//COD 2//ISO// VER/DBM
13216 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-05-23 10:46 | 2011-05-23 17:30 | 1 | 404 | 4141401 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON TRANSFORMER POLE. NEED R / W CREW TO CUT IT AROUND TRANSFORMER, NEED BOAT TO PUT LINE FUSE BACK IN WHEN CUTOUT IS REPLACED ON TRANS RELEASED BY CREW 077S05 COD-1 ISO LF 37830030000087 VER/HFP L3/HFP
13217 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-12-06 08:49 | 2014-12-06 10:30 | 4 | 101 | 4839441 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ON POLE 38830044B00374POLE 44-374 BAD CUTOUT REPLACED VER/CRB
13218 | Hazard | 3309301 | VICCO | REDFOX | 2010-04-12 13:37 | 2010-04-12 20:21 | 1 | 404 | 62430-1 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN///// BAD 7200 3KV XFMR, NEED XFMR AND MATERIAL HANDLER BUCKET. 1 LINEMAN WILL BE ENOUGH//// REPLACED XFMR, POWER RESTORED. // COD-1 VER/HFP L3/HFP IDC XXXX
13219 | Hazard | 3309302 | VICCO | JEFF | 2018-10-27 22:20 | 2018-10-28 01:42 | 2 | 202 | 4333871 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 348-110 power restored at 1:42
13220 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-09-19 23:04 | 2011-09-20 00:45 | 4 | 101 | 4886341 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED RELEASED BY CREW 078S07/ REPAIRS COMPLETE POWER RESTORED @ 12:45 J. HEMLEPP //VER/GAH IDC XXXX
13221 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-06-11 11:19 | 2009-06-11 13:00 | 4 | 101 | 58953-1 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN TRANSFORMER FUSE..CHG. TRANSFORMER FUSE...BB IDC XXXX
13222 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-04-17 22:43 | 2020-04-18 05:27 | 1 | 404 | 4714561 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | arrived RM broken cutout repairs made fuse in @05:27 please close tic RM
13223 | Whitesburg | 3401301 | FLEMING | NEON | 2015-09-12 13:20 | 2015-09-12 16:42 | 2 | 202 | 4231761 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O ON POLE 355-321, WILL HAVE TO OPEN 3 L/F AT POLE 355-27 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED L/F AT 1523. MADE REPAIRS AND CLOSED LINE FUSES AT 1642.// VER/ ADH
13224 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2016-05-26 22:23 | 2016-05-27 01:45 | 2 | 202 | 4263291 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON ARM, MANUAL, NEED 3 MAN LINE CREW AND 7200 KV. CUTOUT. RELEASED BY CREW 077S04REPAIRS MADE AND POWER RESTORED AT 0145
13225 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2016-05-01 20:48 | 2016-05-02 00:10 | 2 | 202 | 4154311 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CREW REQUIRED NEED TWO MEN 7.2KV NEED HARD COVERUP. NO TRUCK RELEASED BY CREW 074S02// VER/ ADH
13226 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-04-10 08:03 | 2015-04-10 11:25 | 2 | 202 | 4301711 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. COD-2 ISO TF 38830425000095 L3/DKGXXX
13227 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2009-01-17 00:08 | 2009-01-17 01:49 | 4 | 101 | 56524-1 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3201001//, ON SITE, BURNT UP XFORMER, CALLED R MARCUM FOR HELP / COD-4 / VER/LDA L3/HFP
13228 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-07-27 13:31 | 2010-07-27 15:12 | 4 | 101 | 57976-1 | 404 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION COD-4 VER/HFP L3/HFP IDC XXXX
13229 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-05-11 19:57 | 2010-05-11 23:19 | 2 | 202 | 59735-1 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35074166 // BAD 25 KVA NEED 37.5 OR 50 KVA TRUCK TO POLE RELEASED BY CREW 078S08/CREW ON SITE/FETR2300/VEM VER/HFP L3/HFP IDCC FP NULL XXXX
13230 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-05-12 09:48 | 2015-05-12 16:32 | 1 | 404 | 4419351 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT == NEED LINE CREW NEED 19.9 CUTOUT AND T BRACKET RELEASED BY CREW 077S03/ ISO 37830514B00159/ COD 1/ VER/BOW
13231 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-09-16 11:46 | 2012-09-16 18:30 | 1 | 404 | 4051461 | 404 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | FOUND BURNTED UP METERBASE, 200 AMP UNDERGROUND, ALSO FOUND BAD 4/0 UNDERGROUND WIRE IN METERBASE, WELL BE CREW REQ, TO REPAIR UNDERGROUND WIRE, SHOULD JUST NEED A SHORT PIECE OF 4/0 UNDERGROUND WIRE, ALSO NEED TO BRING A 200 AMP UNDERGROUND METERBASE RELEASED BY CREW 078S06 (MADE TEMP. REPAIRS ;CUSTOMER WILL HAVE ELECTRICAN MONDAY 09/17/12 TO REPLACE METER BASE//COD 1//EMAILED RAYBURN// VER/DBM IDC XXXX
13232 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-04-29 14:28 | 2016-04-29 16:09 | 4 | 101 | 4142591 | 404 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTIONS IN THE SERVICE DROP ONLY ONE CUSTOMER AFFECTED. VER/AWD
13233 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-07-02 14:17 | 2016-07-02 17:39 | 2 | 202 | 4514961 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK FOR PROBLEMS/////////CUTOUT DOOR BURNED INTO,REPLACED W NEW DOOR,RESTORED,ALL OK AFTERWARDS VER/AWD
13234 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-02-02 11:01 | 2013-02-02 17:45 | 1 | 404 | 4785801 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 RED TO REDS FROZE OUT ON SERVICE, RESQUEEZED, CLOSED BACK IN AT 17:45. ///VER/CRB L/3 CRB IDC XXXX
13235 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-12-14 19:21 | 2015-12-14 21:02 | 4 | 101 | 4532891 | 404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, ON POLE 426-539, ONLY ONE CUSTOMER AFFECTED REPLACED CUTOUT RESTORED POWER AT 21:02..// VER/ ADH
13236 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2017-05-19 11:11 | 2017-05-19 17:54 | 1 | 403 | 4818331 | 403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 167 TRANSFORMER. RELEASED BY CREW 076S01// ON SITE, REPAIRING NOW.// REPAIRS COMPLETE, RESTORED AT 17:54 VER/CRB
13237 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2014-06-15 04:34 | 2014-06-15 11:17 | 1 | 403 | 4092511 | 403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. LOOKS LIKE A LIGHTENING ARRESTER BROKE DOWN AND BLEW TRANS. FUSE. I REFUSED TRANS. AND IT STAYED. I DID NOT HAVE ANOTHER ARRESTER TO REPLACE DAMAGED ONE. /// ENTERED AED COD-1 ISO TF 3782012500008338830067D00116
13238 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2022-05-27 08:16 | 2022-05-27 10:40 | 3 | 144 | 4961791 | 403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire on pole 448-C3-569. lifted clamp on pole 448-C3-410. line crew coming to help make repairs on pole open @ 08:45. repairs made. closed @ 10:40
13239 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-12-23 11:22 | 2022-12-23 18:05 | 1 | 403 | 4316901 | 403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | refused xfmr fuse blew bad xfmr on pole 198-209 need line crew steep icy driveway probablky need chains Released by crew 077E02 Released by crew 077H13///restored at 1805
13240 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2022-08-09 06:34 | 2022-08-09 09:55 | 2 | 201 | 4707671 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout back in at 0955
13241 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-07-19 11:43 | 2014-07-19 13:57 | 3 | 134 | 4263121 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT . FOUND BAD CUTOUT ON POLE 269C-12 . REPLACED CUTOUT ,CLOSED FUSE BACK @ 13:57//COD 3// VER/DBM
13242 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-07-06 19:48 | 2015-07-07 02:30 | 1 | 402 | 4734671 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200, 25 KVA./ ALSO NEED YELLOW GUY PROTECTORS.. CREW ON SITE WILL TAKE A LITTLE TIME GETTING FLAGGERS SET UP ETR 3:00.. TRANSFORMER CHANGED AND RESTORED AT 2:30.. COMPLETE VER/SEF
13243 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2021-10-27 11:58 | 2021-10-27 14:12 | 3 | 134 | 4025481 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | splice failed in secondary
13244 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-08-31 20:06 | 2015-08-31 22:20 | 3 | 134 | 4186631 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP. 7200, NEED 25 KVA. TRUCK OK. RELEASED BY CREW 078S07REPAIRS MADE PLEASE CLOSE TICKET THANKS.BT VER/CRB
13245 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-12-22 23:16 | 2017-12-23 01:30 | 3 | 134 | 4665061 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout
13246 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2015-01-28 18:58 | 2015-01-28 20:05 | 6 | 67 | 4971241 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 39831123B00248 BAD CUTOUT AND LA 6T TRANS DOOR BURNT UP CHGED CUTOUT AND LAPOLE 1123-248 BAD CUTOUT AND LA 6T TRANS DOOR BURNT UP CHGED CUTOUT AND LA VER/CRB L3/HFP XXX
13247 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-03-28 17:31 | 2021-03-28 20:52 | 2 | 201 | 4394401 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Primary and nuetral down one span from 38831099000020. Fuse blown @ 38831098C00101. Repairs made and restored @ 20:52
13248 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-08-28 13:18 | 2019-08-28 20:00 | 1 | 402 | 4957121 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva, 7200. no trk Released by crew 078S07
13249 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-05-03 17:33 | 2021-05-03 18:40 | 6 | 67 | 4518271 | 402 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection part power/ power restored at a18:40
13250 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2015-04-10 10:55 | 2015-04-10 17:37 | 1 | 402 | 4303661 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED FULL ROLL FO #2 / 3 SERVICE DROP , LINE CREW AND MAN TREE CREW. TREES RUBED SERVICE DROP INTO/T.MORRIS ARRIVED ON SITE/ //IDC SETTING POLE ROCK HOLE/CREW OPENING TRANSFORMER454-B4-2586 TO MAKE REPAIRS/OPENED 1725 CLOSED 1737/ WORKING ON POLE 454-7623, SHOUDLN`T HAVE TO OUTAGE/ VER/KEP
13251 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-09-13 14:56 | 2020-09-13 16:03 | 6 | 67 | 4458041 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 54-51 didnt serv anyone and took off line
13252 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-05-15 15:02 | 2009-05-15 18:23 | 2 | 201 | 57362-1 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#29847400//PATROLING LINE--CALLED CREW-BAD TRANSFORMER//MADE MD FOR LINE FUSE ON POLE 92-701////VER/CRB
13253 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-04-14 17:39 | 2015-04-14 21:00 | 2 | 201 | 4318971 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 793-93//ALSO WHEN I TRIED XFMR THE LINE FUSE CUTOUT ON POLE 793-92 BROKE//CREW ENROUTE//REPAIRS MADE//RESTORED AT 21:00//COMPLETE//EM// MD DONE/ ISO IS A LINE FUSE NOT SHOWN ON POLE 38820793D00092/ COD 2
13254 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-29 02:31 | 2014-01-29 04:45 | 3 | 134 | 4321051 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | AFFECTS 5 CUSTOMERS SECONDARY CONNECTION FAILED ON XFMR POLE. REPAIRED AND RESTORED @ 4:45. HAD XFMR OPEN FROM 4:10 TO 4:45. SH 3 ON SEC VER/KEP
13255 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2011-04-26 19:18 | 2011-04-26 21:32 | 3 | 134 | 65818-1 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR FUSE OUT,WILL RE-FUSE///////REPLACED BROKEN CUTOUT AND RESTORED COD-3 ISO TF 38820989A00121 VER/HFP L3/HFP IDC XXXX
13256 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-01-13 02:16 | 2019-01-13 08:58 | 1 | 402 | 4662881 | 402 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power , bad connection at trl pole , made repairs restored power at 08:58..only one customer affected.. L3/HFP
13257 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-02-21 21:36 | 2018-02-21 23:50 | 3 | 134 | 4870521 | 402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout not by truck on pole 69-1597 Released by crew 078H01,,crew on site..replaced cutout,,all power restored
13258 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-13 14:59 | 2011-05-13 21:40 | 1 | 401 | 4084611 | 401 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRING JUMPER BURNED IN-TO ON TAKE-OFF POLE; OPENED XFMR FUSE ON POLE 93/56 AT 2105HRS AND BACK IN AT 2140HRS TO MAKE REPAIRS ON TAKE-OFF POLE; PWR RESTORED AT 2140 HRS; CLOSE TICKET VER/HFP L3/HFP
13259 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-12-21 12:09 | 2014-12-21 18:50 | 1 | 401 | 4873221 | 401 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TREE WAS CUT ONTO THE SERVICE DROP AND HAS BURNED A SECONDARY LEAD INTO. IM GOING TO REPLACE THE SERVICE DROP. TRIED THE TRANSFORMER AND IT IS BAD. NEED 15KVA 7200,FOUR MEN AND AWP. NO TRUCK ACCESS./ ISO 38821090D00098/ COD 1/ VER/BOW
13260 | Hazard | 3303902 | LESLIE | WOOTON | 2019-06-30 13:24 | 2019-06-30 20:05 | 1 | 401 | 4621921 | 401 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cut out on pole 37830390000005. power restored at 20:05
13261 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2011-10-06 12:00 | 2011-10-06 15:20 | 2 | 200 | 4952451 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN LINK VER/KEP IDCC FP NULL XXXX
13262 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-08-14 20:20 | 2009-08-14 22:00 | 4 | 100 | 58575-1 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 760-177. ISOLATED IT AND WILL TRY TO RE-FUSE. 20T FUSE NOT ON MAP MD FILED VER/KEP L3/KEP IDC XXXX
13263 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-02-18 18:40 | 2014-02-18 20:00 | 5 | 80 | 4399161 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 205C-237. B PHASE STEPDOWN OUT ON POLE 205C-375 . CLOSED FUSE BACK IN @ 20.00//COD 5//AED ENTRY CREATED// VER/DBM
13264 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2015-01-09 00:30 | 2015-01-09 01:10 | 10 | 40 | 4922501 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-7191 10T BAD CUTOUT DOOR VER/HFP L3/HFP
13265 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-09-02 21:10 | 2014-09-03 00:30 | 2 | 200 | 4453891 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. REPLACED CUTOUT FUSED UP EVERYTHING OK VER/CRB
13266 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-11-12 16:40 | 2015-11-12 17:05 | 16 | 25 | 4438491 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE XFMER CUTOUT ON POLE 809-368///OPENED XFMER BANK UP AT 16:40 TO MAKE REPAIRS///CLOSED BACK IN AT 17:05///COMPLETE BR VER/CRB
13267 | South Williamson | 3200302 | BELFRY | TOLER | 2008-03-30 13:15 | 2008-03-30 13:55 | 10 | 40 | 62141-1 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200302//, ON SITE, CHECKING TROUBLE, POLETOP BURNT OFF AT POLE#990-D3-517, CUT LOOP AT POLE#993-D3-517 TO CLEAR TROUBLE// + 1 COD DUE TO MISMAPPED CUSTOMER// 10 COD // MAP DISC ISSUED// / / VER/TOM IDC XXXX
13268 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2009-02-22 13:26 | 2009-02-22 15:06 | 4 | 100 | 50341-1 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE, XFORMER FUSE BLOWN, POLE# 1113-B-113, REFUSING IT, FUSE BROKE//3200201//VER/CRB IDC XXXX
13269 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-02-27 19:55 | 2015-02-27 23:15 | 2 | 200 | 4086541 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANS. AT POLE 470-22, WILL NEED 1 MAN, BIG BUCKET, AND A 15KVA, 34 TRANS./COD 2/BAD TRANS. AT POLE 470-22, WILL NEED 1 MAN, BIG BUCKET, AND A 15KVA, 34 TRANS. CHANGED TRANS. CLOSED BACK IN AT 23:15. VER/SEF
13270 | Hazard | 3302704 | HAZARD | KENMONT | 2010-05-08 08:10 | 2010-05-08 11:30 | 2 | 200 | 57565-1 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREES AROUND TRANSF == CALLED ROW CREW == ALSO BAD CUTOUT & ARRESTER == CUT TREES AND CHANGED CUTOUT & ARRESTER == REFUSED TRANSF == VER/ARN IDC XXXX
13271 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-04-28 03:20 | 2021-04-28 10:00 | 1 | 400 | 4487121 | 400 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Dispatched in accordance with KYPCo Late Night Callout Guidelines//connection had burned almost into on secondry pole//repairs made//restored at 10:00//complete//em
13272 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-04-15 08:20 | 2019-04-15 15:00 | 1 | 400 | 4114121 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | not showing on map, bank of 167 kva xfmrs has a broke cutout, need to replace all 3, xfmrs are also covered in vines, will need big bucket, 3 cutout and arrestors, 3 t-brkts. power restored//MADE MD
13273 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2021-11-22 09:40 | 2021-11-22 13:00 | 2 | 200 | 4114781 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required repplaced broke fuse
13274 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2016-07-17 17:10 | 2016-07-17 18:30 | 5 | 80 | 4650481 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPAN OF 6A COPPER DOWN ,, MAN SAID HE PULLED OUT OF ROAD THINKING HE GOT IT INTO XFER SECONDARY BUSHING KNOCKING FUSE ..NEED 300 FT 6A COPPER FOR POLES 1122-41 TO 1122-248 NEUTRAL DOWN CAN FIX AT LATER DATE//MADE AED VER/CRB
13275 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2019-10-03 19:50 | 2019-10-03 20:10 | 20 | 20 | 4092831 | 400 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection failed at weatherhead..opened transformer at 19:50..closed back at 20:10
13276 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-08-22 21:30 | 2016-08-23 00:50 | 2 | 200 | 4826981 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 19.9 TRANSFORMER. NEED BIG BUCKET/1 MAN.BAD 15 KVA 19.9 XFMR ..BAD 15 KVA 19.9 XFMR ..REPLACED XFMR RESTORED POWER AT12:50.. VER/TOM L3/TOM
13277 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2015-11-07 22:15 | 2015-11-07 23:35 | 5 | 80 | 4418951 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED FUSE//COD 5// VER/DBM
13278 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-06-13 15:15 | 2013-06-13 15:35 | 20 | 20 | H4274891 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ROTTED OFF POLE 56-35-ALL MANUEL---STR LINE 12KV -1ARM ,BRACES,3 PIN ,3 INS 1 CLEVIS ,-6A AND 4 COPPER-OPEN AT POLE56-102---OPENED 55-223 AT 1515-CLOSE UP TO 102 AT 1535--WILL NEED RW CREW ALSO---JIM RELEASED BY CREW 077S06 CANNOT COMPLETE TONIGHT DUE TO DIFFICULT LOCATION, CREWS WLLL RETURN FIRST THING FRIDAY MORNING TO REPLACE POLE - GLEN COMBS //COD 22// VER/DBM IDCC DUP TO OPEN RECLOSER XXXX
13279 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2015-08-04 02:02 | 2015-08-04 08:42 | 1 | 400 | 4973101 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | HELD PER AFTER HRS GUIDELINES// LIGHTENING ARRESTER HAS GONE BAD. ILL REPLACE THE ARRESTER. ARRESTER REPLACED, POWER IS BACK ON./ ISO 38820991D20053/ COD 1/ VER/BOW
13280 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-11-16 10:00 | 2011-11-16 10:20 | 20 | 20 | 4080331 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE YET.WIRE LOOSE IN CUTOUT LUG..GLOWING.ON HILLSIDE.POLE 1113C30..NO TRUCK ACCESS..POWER IS ON..WILL HOLD UNTIL DAYLIGHT, & WILL WORK WITH S WMSON CREW..JRV RELEASED BY CREW 080S01 // OPENED LINE FUSE @ 1000 TO REPLACE BAD CUTOUT COD-19 ISO LF 38821114A00005NO OUTAGE YET.WIRE LOOSE IN CUTOUT LUG..GLOWING.ON HILLSIDE.POLE 1113C30..NO TRUCK ACCESS..POWER IS ON..WILL HOLD UNTIL DAYLIGHT, & WILL WORK WITH S WMSON CREW..JRV VER/KEP IDC XXXX
13281 | Hazard | 3303902 | LESLIE | WOOTON | 2012-12-29 04:18 | 2012-12-29 07:38 | 2 | 200 | 4547781 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7.2 CUTOUT, WILL NEED ONE MAN AND BIG BUCKET, 7.2 CUTOUT/ ARRESTER AND FIBERGLASS BRKT..P.HICKS.OPEN ONE POLE TAP, AND TRANSFORMER CUTOUT ON POLE 366D-104 AT 07:22, AND CLOSED IT BACK IN AT 07:38HRS.ALL POWER RESTORED.P.HICKS///VER/CRB L/3 CRB
13282 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-02-04 14:25 | 2019-02-04 15:15 | 8 | 50 | 4753201 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Repaired faulty connection L3/HFP
13283 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-01-02 21:05 | 2011-01-02 22:25 | 5 | 80 | 58054-1 | 400 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE-END HAD BURNED OPEN ON A HOT LEG IN SERVICE DROP AT SECONDARY POLE. I REDONE ALL CONNECTIONS. VER/ARN IDC XXXX
13284 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-07-09 15:30 | 2008-07-09 16:50 | 5 | 80 | 65844-1 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3110902//F BROKEN 10-T FUSE LINK RE-PLACED 10-T FUSE 39831073B43530 VER/HFP IDC XXXX
13285 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-05-30 19:10 | 2011-05-30 22:30 | 2 | 200 | 4211201 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN// WILL REFUSE// BAD XFMR//CALLED T. MCCOY FOR 1 MAN & BUCKET//REPLACED XFMR BACK TO NORMAL //VER/GAH IDC XXXX
13286 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2018-11-26 21:10 | 2018-11-26 21:50 | 10 | 40 | 4482111 | 400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv door, restored/ ISO 38830045C24559/ COD 10 L3/HFP
13287 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-01-03 16:39 | 2014-01-03 17:59 | 5 | 80 | 4225671 | 400 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | RISER WIRE BURNT INTO,REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT//COD 5// VER/DBM
13288 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2020-06-23 18:37 | 2020-06-23 20:50 | 3 | 133 | 4066321 | 399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | changed customers service drop, pole 38830067B00149, possible transformer issues. 25kva 7200. Talked to bryan ramey. Going to change transformer to try and correct issue//NO OUTAGE TILL TRANSFORMER OPENED @changed customers service drop, pole 38830067B00149, possible transformer issues. 25kva 7200. Talked to bryan ramey. Going to change transformer to try and correct issue/ crew on site
13289 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-08-08 20:42 | 2022-08-08 22:55 | 3 | 133 | 4706911 | 399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse pulled into. restored 22:55
13290 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-12-27 11:36 | 2019-12-27 15:15 | 5 | 219 | 4185301 | 399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connections--open tran 14:30 made repairs--tran back in at 15:15--allgood-ds122719
13291 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2011-04-07 09:45 | 2011-04-07 10:42 | 7 | 57 | 50963-1 | 399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39469053 // 50 KVA IS SLIGHTLY LEAKING ON POLE 1086-D-333....NEEDS REPLACED....CALLED JOEY REED....CUSTS ARE OK WITH US CHANGING XFMR TOMORROW (04/07/11)....VERY MINIMAL CLEANUP NEEDED....PLEASE HOLD FOR JOEY...THANX...// RELEASED BY CREW 080S01. CHANGING TRANSFORMER . OPENED TRANSFORMER AT 9:45//VER/CRB
13292 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-03-04 12:44 | 2014-03-04 12:51 | 57 | 7 | 4450911 | 399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER TO MAKE REPAIRS ON TICKET 4450581 VER/CRB IDCC CCSCO CNT59 XXXX
13293 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-07-13 18:55 | 2008-07-13 21:08 | 3 | 133 | 51950-1 | 399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311401// FOUND 19.9 CUTOUT BROKEN ACROSS CREEK AND AT LOWER END OF BOTTOME. CALLING FOR ONE MAN AND CUTOUT RELEASED BY CREW 077S07 IDC CHANGED START TIME FROM 1615 XXXX
13294 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-08-28 02:05 | 2020-08-28 08:44 | 1 | 399 | 4391401 | 399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines /no crew required replacing cutout/MADE MD TO SHOW L/F ON POLE 38830269B00097 ONLY FEEDS ONE POLE TAP TOWARDS 38830269B00408
13295 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-06-22 17:39 | 2018-06-22 20:58 | 2 | 199 | 4647721 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Released by crew 079H03//FUSE BROKE
13296 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-06-10 05:11 | 2010-06-10 08:30 | 2 | 199 | 59558-1 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401801// WILL DISPATCH IN THE A.M. CUTOUT BURNED UP..CHANGED CUTOUT VER/KEP L3/KEP
13297 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-08-17 11:12 | 2021-08-17 17:50 | 1 | 398 | 4086061 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required 15kva truck ok/put in rameys name Released by crew 078S03/// Complete BR
13298 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-09-30 06:26 | 2008-09-30 09:45 | 2 | 199 | 52107-1 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S05 CHANGED OUT BAD CUTOUT.//3003701//VER/CRB IDC XXXX
13299 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2021-08-19 19:01 | 2021-08-19 22:20 | 2 | 199 | 4123331 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 1111C-39..broke cutout.i made repairs and restored line fuse on pole 1111C-39 at 22:20
13300 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2022-06-14 10:10 | 2022-06-14 16:48 | 1 | 398 | 4103291 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 bring transformer and cut out no truck access will be manual change out Released by crew 079S02xfmr bad 25kva NTA/// Crew onsite to repairxfmr bad 25kva NTA/// Crew onsite to repair/// Replaced can and broken cutout. Power restored @16:48
13301 | Pikeville | 3413402 | GARRETT | LACKEY | 2016-12-21 16:32 | 2016-12-21 19:51 | 2 | 199 | 4227701 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE ON 87-D-29 FAILED REFUSED CUTOUT RESTORED POWER AT 19;51 VER/CRB
13302 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-05-18 09:32 | 2015-05-18 16:10 | 1 | 398 | 4440911 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FIRST CALL @ 09:32 05/18/2015 FROM ORDER 4440151 // POLE 141-198 BAD 15KVA,7200 C/O & ARR. CREW REQD.TK OK SEVERAL POLES MISTAGGED. RELEASED BY CREW 078S07///CREW ON SITE///CHANGED 15KVA XFMR & NEW CUTOUT///CUST MTR BASE HAS CORRODED NEUTRAL LUGS, CUST MAY NEED TO CHANGE IF ANY MORE ISSUES///OUR SIDE 124/124/248V THERE SIDE READING TO NEUTRAL 110/110/220V/// TBL TKT COMP///RMV/ON @1610
13303 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2012-08-10 02:22 | 2012-08-10 09:00 | 1 | 398 | 4921541 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL CHECK AT REGULAR TIME ARRESTER BLEW UP AND GROUND WIRE CONTACTED XFMR PRIMARY RISER. PULLED WIRE IN THE CLEAR AND RE-FUSED XFMR @ 9:00. SH COD-1 ISO TF 38830714000013 VER/HFP L3/HFP IDC XXXX
13304 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-11-16 18:35 | 2014-11-16 20:29 | 4 | 114 | 4732781 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT 248-21 TRYING TO ISOLATE ROTTEN POLE//ISO POLE L/F 38830248000016//COD 4//ISOLATED POLE 38830248000021AND TRIED L/F BACK @ 2000BROKEN CUTOUT 248-21 TRYING TO ISOLATE ROTTEN POLE/LINE FUSE IN AT 2000 HRS2 CUSTOMER STILL OFFBROKEN CUTOUT VER/CRB
13305 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2013-11-29 10:52 | 2013-11-29 17:30 | 1 | 398 | 4087631 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED FUSE ON 277/480 V BANK, CLOSED IN C PHASE IT STAY, THEN CLOSED IN B PHASE IT BLEW, AND SO DID C PHASE, NEED 3 25 KVA SINGLE BUSHING 277/480 V TRANSFORMER, WELL NEED AWP FOR TRAFFIC CONTROL ALSO, WELL BE CREW REQ RELEASED BY CREW 078S06CHANGED OUT XFORMER BANK, PERFECT VOLTAGE, OUR FUSE DROPS OUT WHEN CUST SWITCH IS CLOSED, TRANS BANK IS NOT OVERLOADED (TLM BY GREG BELL) CUST TROUBLE.BLR VER/CRB IDC XXXX
13306 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2011-02-21 11:11 | 2011-02-21 14:30 | 2 | 199 | 59708-1 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 077S05--BAD 15 KVA -7.2---POLE 148-80---RW CREW IN RT-OK TO TRIM--ON LEFT-MANUAL POLE IN LEVEL YARD--MAYBE BUCKET----ASK OWNER -- JUST B4 STIDHAM SIGN -JIM RELEASED BY CREW 077S06 REPLACEDXFMR AND TRIMMED TREE RESTORED POWER AT 1430 CREW 077H01//COD 2// VER/DBM IDC XXXX
13307 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-06-17 09:02 | 2008-06-17 15:40 | 1 | 398 | 66481-1 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUTOUT // VER/TOM IDC XXXX
13308 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2016-09-23 18:11 | 2016-09-23 21:30 | 2 | 199 | 4921791 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV TRANSFORMER 72 KV, NEED LINE CREW AND A TREE CREW TO FLAGG, NEED BIG BUCKET RELEASED BY CREW 077H07POWER RESTORED AT 21:30//// ISO 37830272C40855/ COD 2/ VER/BOW
13309 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-07-23 07:16 | 2018-07-23 10:35 | 2 | 199 | 4838901 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing
13310 | Hazard | 3303902 | LESLIE | WOOTON | 2013-07-16 12:11 | 2013-07-16 15:30 | 2 | 199 | 4529491 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE RUSTED OFF AND CONTACTED TRANSFORMER RISER, BLOWING TRANSFORMER FUSE, TREES ALSO IN R/W IN PRIMARY...HAVE R/W CREW ON THEIR WAY.P.HICKS..RESTORED POWER TO TRANSFORMER @15:30 HRS VER/CRB L/3 CRB IDCC PN86, CNT1 XXXX
13311 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-08-03 10:41 | 2009-08-03 14:00 | 2 | 199 | 65128-1 | 398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA XFMR, DONNIE GENT WILL BE CHANGING XFMR. //COD 2// VER/DBM IDC XXXX
13312 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2016-07-27 14:06 | 2016-07-27 20:43 | 1 | 397 | 4690241 | 397 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7200 TRAN.. CREW REQ--NOTE: CELL TOWER .NEED TRAN, SQUIRTBOOM, PICKUP W/WINCH--DS072716 RELEASED BY CREW 078S01--CREW ON SITE--CHANGED BAD 25KVA---VOLT CK GOOD--PWR RESTORED AT 20:43---TBL TKT COMP---RMV VER/CRB
13313 | Pikeville | 3407101 | TOPMOST | DEMA | 2009-12-07 17:42 | 2009-12-07 21:00 | 2 | 198 | 52724-1 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNED OPEN UNDER A PIECE OF TAPE....DAH//COD 2// VER/DBM IDC XXXX
13314 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-10-07 09:58 | 2014-10-07 12:10 | 3 | 132 | 4564111 | 396 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | THIS WAS ACTUALLY ON POLE # 38831099000055 HAD BAD CONNECTION AT SECONDARY RISER CCC COD-3 ISO SO @ 38831099000055 VER/HFP L3/HFP
13315 | Hazard | 3302703 | HAZARD | HAZARD | 2012-08-03 16:18 | 2012-08-03 18:30 | 3 | 132 | 4890491 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR, CUT IN CLEAR. ---- 37830272D21077 ROTTEN POLE BAD ARRESTOR, PLEASE SEND A COPY TO D. CHRISTIAN//AED CREATED FOR ARRESTER//COD 3// 37830272D20727// VER/DBM IDC XXXX
13316 | Hazard | 3309302 | VICCO | JEFF | 2012-05-19 16:00 | 2012-05-19 16:36 | 11 | 36 | 4809711 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE TO MAKE REPAIRS ON 4809371 VER/KEP IDC XXXX
13317 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-03-28 10:21 | 2008-03-28 13:39 | 2 | 198 | 61548-1H | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001002// 1AND 3/4 MILE OUT RT. 5 FROM US 60 YELLOW TRL. ON RIGHT JUST PASS WILLIAMS CK. CHURCH POLE ON HILL ON LEFT 114-12 2- CUST RELEASED BY CREW 078S08// HAD TO OPEN SOLID BLADE @ POLE 90-357 TO SAFELY CHAGE CUTOUT// OPENED SOLID BLADE @ 1250 AND CLOSED BACK IN @ 1339 //// VER/TOM IDCC DUP FOR EARLIER 2 CUSTOMERS OUT XXXX
13318 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-02-05 08:52 | 2011-02-05 12:10 | 2 | 198 | 54162-1 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 XFORMER, NEED LINE CREW TRUCKS TO POLE OK.//COD 2//WR# 38704529 // VER/DBM IDC XXXX
13319 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-06-09 01:23 | 2015-06-09 03:35 | 3 | 132 | 4540781 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SINGLE TRANS, OUT CHECKING BROKEN FUSE LINK REPAIRED POWER RESTORED KWB/ ISO 38830067B00035/ COD 3/ VER/BOW
13320 | Pikeville | 3407103 | TOPMOST | KITE | 2012-09-23 17:17 | 2012-09-23 20:35 | 2 | 198 | 4080841 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT . ALL WORK COMPLETE / GXJ COD-2 ISO TF 37830185000032 VER/HFP L3/HFP IDC XXXX
13321 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-08-30 22:49 | 2008-08-30 23:25 | 11 | 36 | 57919-1 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WRONG FUSE INSTALLED 8T FUSE BROKE INSTALLED 10T 50KVA VER/PDP IDC XXXX
13322 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-03-06 15:13 | 2010-03-06 17:25 | 3 | 132 | 63394-1 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OPEN AT POLE 38830352000010, BROKEN INSULATOR AT POLE 38830352000052 COD-3 VER/KEP L3/KEP IDC XXXX
13323 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-01-01 06:46 | 2018-01-01 10:04 | 2 | 198 | 4691601 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kv 7200 xfm by truck should go back with a 37 1/2 Released by crew 078H01/ Transformer changed, all power restored at 10:04
13324 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-08-23 22:42 | 2016-08-24 00:21 | 4 | 99 | 4830461 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 079S02 TRANSFORMER FUSE HAD BROKE, REPLACED THE FUSE AND POWER IS RESTORED. VER/TOM L3/TOM
13325 | South Williamson | 3200301 | BELFRY | BELFRY | 2014-11-16 15:31 | 2014-11-16 15:49 | 22 | 18 | 4732031 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CANNOT TELL BUT IT LOOKS LIKE A BAD TRANSFORMER CUTOUT ON POLE 38821014C10081. IM GOING TO REPLACE IT.//BAD CUT OUT ON L/F OPENED 38821014C10081 I REPLACED BAD C PHASE CUTOUT ON THE SIDE TAP ON POLE 38821014C10081. OPENED AT 15:31 AND CLOSED ALL BACK IN AT 15:49//ALL 3 CUTOUTS WERE OPENED AT 1531 VER/CRB L3/HFP AJB
13326 | Pikeville | 3413402 | GARRETT | LACKEY | 2020-04-17 13:02 | 2020-04-17 16:20 | 2 | 198 | 4710851 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3413402; LF assembly failure at pole 87-D-8 is causing fuse cutout door to track across, shorting the A-phase primary on the Garrett/Lackey ckt; tap line is de-energized with 2cc out; restored 2cc at 1620; per S. Garrido (circuit coordinator), we can check for hazards and let R. Quick close these sws when he's ready;
13327 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2012-06-25 19:04 | 2012-06-25 19:48 | 9 | 44 | 4962191 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPAIRED BROKEN HOTTAP LEAD ///VER/CRB L/3 CRB
13328 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-03-09 15:59 | 2022-03-09 22:35 | 1 | 396 | 4594591 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Released by crew 077H05 bad 10kva xfmr
13329 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2013-01-23 10:22 | 2013-01-23 13:40 | 2 | 198 | 4732551 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON POLE 38831077B00134REPLACED PIIMARY INSULATOR //VER/GAH IDC XXXX
13330 | Hazard | 3303901 | LESLIE | HYDEN | 2015-04-14 11:07 | 2015-04-14 14:25 | 2 | 198 | 4316551 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR/COD 2/BAD INSULATOR ON 413-345 AND 389-496// VER/ ADH
13331 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2017-06-19 13:04 | 2017-06-19 19:40 | 1 | 396 | 4000251 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKEN . REPLACED CUTOUT AND REFUSED XFMR, ALL WORK COMPLETE / GXJ/ ISO 37830160000031/ COD 1/ VER/BOW
13332 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-12-18 10:07 | 2012-12-18 13:25 | 2 | 198 | 4479141 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED IN APPROACH DISTANCE CAN USE BIG BUCKET ON IT RELEASED BY CREW 078S03
13333 | Pikeville | 3407101 | TOPMOST | DEMA | 2019-06-05 11:53 | 2019-06-05 14:05 | 3 | 132 | 4430721 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t transformer fuse out due to bad coutout broken hanging down pole. i will not be able to get truck to this. changed cutout everything ok
13334 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-06-18 13:21 | 2011-06-18 15:00 | 4 | 99 | 4337791 | 396 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 1 BROKEN CUTOUT,HAVE TO OPEN THE OTHER TWO CUTOUTS TO CHANGE..CHANGED CUTOUT.SERVICE BACK ON 15.00 COD-4 ISO TF 38830875C00359 VER/HFP L3/HFP
13335 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-12-25 00:30 | 2010-12-25 03:48 | 2 | 198 | 55597-1 | 396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | D/S CALLING OUT SERVICE. LINE FUSE OUT ON 379-352, BAD CUTOUT ON 379-540... REPLACED CUTOUT RESTORED POWER AT 03:48 VER/PDP IDC XXXX
13336 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2017-08-18 00:55 | 2017-08-18 01:39 | 9 | 44 | H4273371 | 396 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART OF 4273371//OPENED XFMR AT 00:55--BACK ON AT 01:39---TBL TKT COMP---RMV//COD 9// VER/DBM
13337 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-06-22 07:50 | 2021-06-22 14:25 | 1 | 395 | 4789501 | 395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | power restored at 14:25
13338 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2017-11-21 10:28 | 2017-11-21 17:03 | 1 | 395 | 4591881 | 395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer meter is blank === cutout bad === need line crew this is manual up on hill side === called for line crew/ ISO 37830442000077/ COD 1
13339 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2021-05-13 11:55 | 2021-05-13 18:30 | 1 | 395 | 4583471 | 395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Center phase riser fuse was blown on 1052-C-974. Tried fuse and it came back out. Opened remaining 2 fuses @ 12:28 to isolate and check cable. Crew enroute with testing equipment/// Primary UG cable is bad crew on sight to replace// restored @1830 Released by crew 076S03
13340 | Hazard | 3302703 | HAZARD | HAZARD | 2011-07-21 16:00 | 2011-07-21 22:35 | 1 | 395 | 4575271 | 395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR NEED 25 KVA 7.2 KV XFMR CUTOUT ,T BRKT HOT LINE CLAMP & RISER MANUEL WILL NEED DOLLY TO GET XFMR AROUND HOUSE RELEASED BY CREW 077E02 VER/ARN
13341 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-05-21 16:26 | 2009-05-21 17:45 | 5 | 79 | 57967-1 | 395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER WENT BAD == CUT IN CLEAR == REFUSED TRANSF//COD 5// VER/DBM IDC XXXX
13342 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-02-20 08:01 | 2009-02-20 09:20 | 5 | 79 | 65795-1 | 395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP COD-7 OPEN WIRE SECONDARY DOWN--OPENED TRANSFORMER AT 08:01--CALLING CREW--#2 CU SECONDARY--NEED 4/0 RISERS FOR 50 KVA TRANSFORMER--B FRALEY TO WORK RELEASED BY CREW 078S07 L3/HFP IDCC DUP FOR FIRST 2 CUSTOMER OUT WITH PART POWER XXXX
13343 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-07-03 22:02 | 2011-07-03 23:21 | 5 | 79 | 4452061 | 395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUST HAS PART POWER/HOT LEG IN TROUBLE/SERVICER TO MAKE REPAIRS/VEM/WILL HAVE TO OPEN XFMR ON 39831073B43530 FOR REPAIRS/FETR 2330/VEM/OPEN XFMR 2259/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2311/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
13344 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2016-02-15 15:41 | 2016-02-15 17:00 | 5 | 79 | 4697721 | 395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ON POLE 1113B17 REPLACED CUTOUT RESTORED POWER AT 17:00 VER/CRB L/3 CRB
13345 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-05-25 16:32 | 2009-05-25 19:49 | 2 | 197 | 64262-1 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND 15 KVA TRANSFORMER BURNED UP. GEORGE WHITAKER IS ENROUTE TO HELP ME ON THIS//COD 2// VER/DBM IDC XXXX
13346 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2017-08-14 05:47 | 2017-08-14 09:04 | 2 | 197 | 4256921 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DISPATCHED IN ACCORDANCE WITH KYPCO LATE NIGHT CALLOUT GUIDELINES POLE 1148-143 BAD CUTOUT AND LA VER/HFP L3/HFP
13347 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-02-02 01:53 | 2019-02-02 05:10 | 2 | 197 | 4748051 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, repaired connections on pole L3/HFP
13348 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-02-02 10:33 | 2019-02-02 13:50 | 2 | 197 | 4748471 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t fuse out due to bad cutout. will be away from the truck while changing out. coutout changed out everything ok // Cod 2 Iso 37830213000026 customer was mismapped MD made
13349 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-06-28 09:48 | 2017-06-28 13:05 | 2 | 197 | 4053561 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 076S01 ISOLATED XFMR LIGHTNING ARRESTER AND RESTORED LINE FUSE 38830853000077 @ 13:05. SH COD 2 VER/AWD
13350 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-07-24 10:39 | 2015-07-24 17:13 | 1 | 394 | 4938061 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-4387 BAD 75KVA TRUCK TO POLE OTHER TRANS STILL ON RELEASED BY CREW 078S08/CREW ON SITE/FETR 1745/VEM/REPAIRS MADE AND ALL CUST RESTORED 1713/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
13351 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-11-01 06:03 | 2012-11-01 09:20 | 2 | 197 | 4311531 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TAP FUSE IS BLOWN ON POLE 1062-B-172. TAP FUSE HAD BROKE. REPLACED FUSE, POWER RESTORED. //VER/GAH IDCC PN174 XXXX
13352 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2008-02-13 08:21 | 2008-02-13 14:55 | 1 | 394 | 62211-1 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008003// CALLED CREW/ SEND TO P TOLLIVER //COMPLETE AT 14:55//REPLACED 3-50KVA WITH 3-75KVA TRANSFORMERS REPLACED 4/0 RISERS WITH 500MCM REPLACED 1 CUT-OUT AND REFUSED WITH 12T TRANSFORMER FUSES VOLTAGE CHECKED GOOD 120/208// VER/DBM IDC XXXX
13353 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2016-05-01 07:56 | 2016-05-01 14:30 | 1 | 394 | 4148231 | 394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER. NEED 15 KVA 7200 TRANSFORMER, CUTOUT AND BRACKET. FOREMAN AND ONE LINEMAN WITH A MATERIAL HANDLER. POWER RESTORED AT 14:30, ONLY ONE CUSTOMER WAS OFF. RELEASED BY CREW 079S02// VER/ ADH
13354 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-02-27 06:39 | 2020-02-27 08:50 | 3 | 131 | 4435441 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 8:50. sh L3/HFP
13355 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-06-21 08:54 | 2022-06-21 11:05 | 3 | 131 | 4267271 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Loop burnt open on pole 141-92, opened C phase on 141-72 @ 09:40. Tagged to luke mccoy Released by crew 078S02 crew on site FETr 11:30
13356 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-02-20 08:04 | 2015-02-20 10:15 | 3 | 131 | 4051861 | 393 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS @ XFMER. OFF @ 9:45, ON @10:15. RESTORED MP VER/HFP L3/HFP
13357 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-09-04 10:04 | 2019-09-04 12:15 | 3 | 131 | 4978611 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout. apr at 1215 close ticket. dwest
13358 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-05-05 11:29 | 2009-05-05 13:40 | 3 | 131 | 55120-1 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830151000213 XFMR CUTOUT BAD 7200 CUT OUT ALSO BAD ON POLE 37830151000028 // RESTORED COMPLETE 13:40 COD-3 VER/KEP L3/KEP
13359 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-01-25 23:09 | 2022-01-26 01:20 | 3 | 131 | 4404881 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke @ 37830117A40298.// Replaced and restored @ 01:20
13360 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-12-31 15:49 | 2012-12-31 18:00 | 3 | 131 | 4560631 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT UP DOOR/NO CREW REQUIRED COD-3 ISO TF 38830326000033 VER/CRB L/3 CRB
13361 | Hazard | 3310502 | HADDIX | CANOE | 2010-01-01 16:22 | 2010-01-01 18:33 | 3 | 131 | 55889-1 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT IN PROCESS OF REPLACING , REPLACED CUTOUT AND RESTORED POWER AT 1833 JKC VER/HFP L3/HFP IDC XXXX
13362 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-07-31 10:07 | 2022-07-31 16:40 | 1 | 393 | 4641831 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TR 38820841B00139 open upon arrival-tried to close TR in and cutout failed-lifted tap at 38820841B00053 to isolateXfmr cutout broke.Xfmr cutout broke. Replaced cutout and restored @ 16:40
13363 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-12-27 11:19 | 2009-12-27 13:30 | 3 | 131 | 55086-1 | 393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK
13364 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2016-07-27 15:44 | 2016-07-27 19:00 | 2 | 196 | 4691181 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. POLE IS IN A DIFFICULT LOCATION. REPLACED CUTOUT AND RESTORED @ 19:00. SH VER/CRB
13365 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-10-07 11:19 | 2021-10-07 14:35 | 2 | 196 | 4326971 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 19.9 cutout. got tim smith crew coming to help
13366 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2010-05-18 14:27 | 2010-05-18 16:05 | 4 | 98 | 64750-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FUSE OUT68-C-923 CHECKING NOW ISO- LATED URD CABLE FROM TRANSFORMER FUSE IS IN BLOWED FIRST TIME ATTEMPTED TO RESTORE CREW WIL BE NEEDED TO MAKE REPAIRS CAN WAIT UNTILL MORNING HAVE TO FIX BY THURSDAY ,FUNERAL SERVICE ON THIS DAY KEVIN BROWNN CREATED IO ORDER TO REPAIR THIS TOMORROW VER/HFP L3/HFP IDCC CNT1 XXXX
13367 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-03-11 11:47 | 2016-03-11 15:03 | 2 | 196 | 4836831 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN THE LINE FUSE BACK UP ON POLE 38830115D00592 TO MAKE REPAIRS IN ORDER 4836291/ OPENED @1147/ ISO 38830115D00592/ COD 2/ 1503 ALL POWER RESTORED/ VER/BOW
13368 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-11-06 22:07 | 2009-11-06 23:45 | 4 | 98 | 66340-1 | 392 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BAD AT XFMR WILL HAVE TO OPEN XFMR TO MAKE REPAIRS...OPENED XFMR AT 23:35&RESTORED POWER AT 23:45 IDC XXXX
13369 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-11-19 15:07 | 2008-11-19 16:45 | 4 | 98 | 50035-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000301//BROKEN FUSE VER/KEP IDC XXXX
13370 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-01-04 05:50 | 2012-01-04 07:28 | 4 | 98 | 4231471 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | "C" PHASE ONLY COD-4 FUSE BROKEN VER/KEP IDC XXXX
13371 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-09-27 18:53 | 2009-09-28 01:25 | 1 | 392 | 66082-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANS IDC XXXX
13372 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2018-06-18 08:15 | 2018-06-18 09:53 | 4 | 98 | 4614971 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | power restored @ 09:53. pls close. tre/ ISO 38830046B10171/ COD 4
13373 | South Williamson | 3411401 | DEWEY | INEZ | 2013-07-04 12:42 | 2013-07-04 14:20 | 4 | 98 | 4462451 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE.. GOING TO CHANGE.. CHANGED CUTOUT AND GOT TRANSFORMER BACK ON AT 14:20.. POLE NEEDS CUT AROUND. THE REST OF LINE IN GOOD SHAPE BUT AROUND POLE IS BAD.. PLEASE SEND TO ROW.. COMPLETE RN VER/CRB L/3 CRB
13374 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-03-11 11:47 | 2016-03-11 15:03 | 2 | 196 | H4836291 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4836291****40/5 POLE, TRACK MACHINE/ POLE FIRE ON POLE 38830115D00436/ LINE FUSE WAS OPEN ON POLE 38830115D00592/ ISOLATED LIFTING HOT TAP ON POLE 38830115D00229 TAGGED TO VERNON MULLINS/ CLOSED IN LINE FUSE ON POLE 38830115D00592 @ 0850//BAD DOGS LOCATED AT ISOLATING POLE 115-D-229, USE CAUTION//CREW ON SITE/WILL NEED TO OPEN FUSE ON 115-D-592 FOR REPAIRS/FETR1500/VEM/OPEN FUSE ON 115-592@1147/REPAIRS MADE AND ALL CUST RESTORED 1503/PLEASE CLOSE TICKET/THANKS/NO ASB WORK ORDER/ VER/BOW
13375 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2017-12-02 19:27 | 2017-12-02 21:05 | 4 | 98 | 4617291 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse link broke. Restored @ 21:05. sh//cod 4
13376 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2019-02-07 15:57 | 2019-02-07 17:35 | 4 | 98 | 4764681 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Arrester failed - ground wire blown off. Resulting arc blew transformer fuse. Restored @ 17:35. sh Iso 38830785D21120 this was the only Xfer out L3/HFP
13377 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2011-11-15 06:47 | 2011-11-15 08:25 | 4 | 98 | 4077621 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED TRANSFORMER CUTOUT OPENED LINE FUSE AT 0815 CLOSED AT 0825.//MADE MDC /// VER/CRB IDC XXXX
13378 | Hazard | 3303902 | LESLIE | WOOTON | 2009-11-29 16:06 | 2009-11-29 17:44 | 4 | 98 | 50703-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 32853537 //BAD CUTOUT GATE /// COD-4 ISO TF 37830340000041 L3/HFP IDC XXXX
13379 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-07-21 11:58 | 2021-07-21 18:30 | 1 | 392 | 4942161 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad UG @ location, power temp installed. Last hot leg burnt in two. Customer going from Ug to over head, but we have to set new pole. Job should already be written. Pole is staked. Customer going to be working on Switching there stuff over, inspection required. We can get pole and service drop in, in the mean time. Crew Required. Send to bobby tackett Released by crew 078S02,repairs made all cust restored please close ticket thanks.bt
13380 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-05-17 13:59 | 2021-05-17 17:15 | 2 | 196 | 4593171 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | pad mount xfmr fuse blown..
13381 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2008-04-19 06:11 | 2008-04-19 07:00 | 8 | 49 | 52257-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 68-142 CUTOUT FELL APART VER/LDA IDCC TOF0613 SEE 52256-1 XXXX AJBC
13382 | South Williamson | 3200302 | BELFRY | TOLER | 2009-01-10 20:09 | 2009-01-10 23:25 | 2 | 196 | 54097-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200302//, ON SITE, CHECKING TROUBLE, BAD CUTOUT, CALLED R MARCUM FOR HELP COD-2 VER/KEP L3/KEP IDC XXXX
13383 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-01-24 18:02 | 2022-01-24 19:40 | 4 | 98 | 4401801 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on xformer pole 139-C-94.
13384 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2008-01-21 10:24 | 2008-01-21 13:40 | 2 | 196 | 58508-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3451202//TRANSFORMER IS BAD WILL NEED TO BE REPLACED WITH A 25KVA//COD 2// RELEASED BY CREW 074S07//VER/CRB IDC XXXX
13385 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-10-06 18:37 | 2014-10-06 20:15 | 4 | 98 | 4560001 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON POLE 237-A-23 WILL PATROL/// BAD INSULATER ON POLE #237-B-57 WILL CHANGE/// CHANGED BAD INSULATOR ON POLE 237-B-57 AND CLOSED LINE FUSE IN ON POLE #237-A-23 @20:15 AND RESTORED SERVICE// ISO 37830237A00023/// COD 4 CCC*****/// TRANSFORMER 37830237A00248 AND TRANSFORMER 37830237B00057 ARE BOTH UNDER FUSE 37830237A00023// VER/BOW
13386 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2009-04-03 08:12 | 2009-04-03 11:28 | 2 | 196 | 64469-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, BAD CUTOUT , CALLED R MARCUM FOR HELP, SEND TICKET TO JOEY REED RELEASED BY CREW 080S01//COD 2// VER/DBM IDC XXXX
13387 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2019-02-05 17:09 | 2019-02-05 20:25 | 2 | 196 | 4756711 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad transformer on pole 139-352. 10 kva, 120/240, 19.9, 2 bushing transformer. Crew required. Send to bobby tackett Released by crew 078H04 ,repairs made all cust restored @ 2025 please close ticket thanks.bt
13388 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-08-27 22:19 | 2020-08-28 01:35 | 2 | 196 | 4391201 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service drop burnt down due to bad connections at weather head insulink heated up burning 1/0 drop down made repair to conductor and new connections at weather head everything ok. send copy of this to dmage claims cust could possibly call in.//emailed to d lemaster //
13389 | Pikeville | 3408401 | KIMPER | LONGFORK | 2009-01-14 22:16 | 2009-01-14 23:54 | 4 | 98 | 55107-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408401//XFR TO RE-FUSECUTOUT DOOR HAD BURNED OUT OF CUTOUT,REPLACED IT,CLOSED,RESTORED POWER //VER/GAH L3/KEP IDC XXXX
13390 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2008-12-20 10:38 | 2008-12-20 17:10 | 1 | 392 | 61189-1 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 27764356 DE-ENERGIZED SECTION OF UNUSED PRIMARY U.G. GOT POWER ON TO CUST. AT 17:10 //VER/GAH L3/KEP IDC XXXX
13391 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2017-03-29 11:09 | 2017-03-29 11:37 | 14 | 28 | 4594351 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | OUTAGE NECESSARY TO ALLOW CREW TO REPLACE CRACKED CUT OUT THAT THEY FOUND // COD-14 ISO LF & TF 37820073C00173 OFF @ 1109 ON @ 1137. VER/HFP L3/HFP
13392 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-08-17 19:04 | 2022-08-17 22:20 | 2 | 196 | 4757771 | 392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 15 KVA transformer on pole 424-259. Bucket access. Need cutout and T bracket. Linecrew req. Released by crew 077H15.. restored power @ 22:20
13393 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-08-19 06:44 | 2010-08-19 13:15 | 1 | 391 | 57995-1 | 391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIED,,,NEUTRAL HAS ONE STRAND HOLDING IT UP,,,HOT LINE CLAMP MAY HAVE DAMAGED PRIMARY IT IS ENDANGER OF FALLING IF TAKEN OFF,, AND TRANSFORMER HAS FRESH OIL DOWN THE SIDE OF IT NEEDS TO BE CHANGED OUT FOR A 25 KVA 7200V AND A CUTOUT NEEDS TO BE INSTALLED. RELEASED BY CREW 078S02078H05 INROUTE078H05 INROUTE/ ON SITE@11:20078H05 INROUTE/ ON SITE@11:20/ REPAIRED #2 PRIMARY&NEUT. REPLACED C/O& L/A REPLACED 5KVA WITH 25KVA INST. NEW GRND. ROD AND GRND. WIRE.CUST REST.@ 13:15// VER/DBM IDC XXXX
13394 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-12-06 08:19 | 2010-12-06 14:50 | 1 | 391 | 63496-1 | 391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE LINK BROKEN...ONLY ONE CUSTOMER OFF THIS TRANSFORMER..RE-FUSED TRANSFORMER 6 T FUSE... COD-1 TF 38830876C00082 VER/HFP L3/HFP IDC XXXX
13395 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-03-27 06:49 | 2019-03-27 13:20 | 1 | 391 | 4028971 | 391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10 kva transformer replaced transformer an cutout power restored at 13:20
13396 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-12-23 10:44 | 2018-12-23 17:15 | 1 | 391 | 4594461 | 391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10 kva 7.2 120/240 cutout & bracket no truck accessible restored at 17:15 L3/HFP
13397 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-04-28 08:34 | 2015-04-28 15:05 | 1 | 391 | 4371651 | 391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON PRIMARY METERING ON POLE 37830176000167, NEED TO REPLACE ALL 3 CUTOUTS, CAN WORK WITH BIG BUCKET. 7200 KV. RELEASED BY CREW 077S04 VER/CRB
13398 | Pikeville | 3413401 | GARRETT | GARRETT | 2014-11-18 11:13 | 2014-11-18 11:52 | 10 | 39 | 4741441 | 390 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REPLACING TRANSFORMER - OPENED TR @ CLOSED @ REPLACED BAD TRANSFORMER ON POLE 65-237 TOOK IT OFF AT 11:13 ON AT 11:52 COD-10 ISO TF 37830065D00237 VER/HFP L3/HFP
13399 | Hazard | 3309301 | VICCO | REDFOX | 2010-02-28 12:35 | 2010-02-28 13:05 | 13 | 30 | H61643-1 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR# 34050585 //PATROLLING LINE, RESTORED POWER BUT HAVE BAD ARRESTER, WILL NEED BIG BUCKET AND 1 MAN // TOOK LINE BACK OFF AT 1235 ON AT 1305 DUPLICATE OF 61643-1 DUPLICATING FOR OUTAGE TO REPLACE ARRESTOR. VER/HFP L3/HFP IDC XXXX
13400 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-10-12 11:35 | 2011-10-12 13:45 | 3 | 130 | 4970291 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED POLE BURNT OFF BACK YARD/MIGHT BE ABLE TO LOWER 19.9 SPACING/POLE 247-32 30T LINE FUSE BLOWN ///VER/CRB IDC NOT SURE WHAT TIME FUSE BLEW XXXX
13401 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2019-07-16 03:30 | 2019-07-16 06:45 | 2 | 195 | 4714851 | 390 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | Part out/unable to reach customer/address is 488/clamp burnt off on 174-357Part out/unable to reach customer/address is 488 lead burned off primary meter
13402 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2021-05-25 08:40 | 2021-05-25 09:58 | 5 | 78 | 4618961 | 390 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neut broke in sec/repairs made. pls close. tre
13403 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-01-15 12:48 | 2019-01-15 19:18 | 1 | 390 | 4675481 | 390 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced burnt connection at weatherhead L3/HFP
13404 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-04-03 14:57 | 2015-04-03 16:15 | 5 | 78 | 4265351 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD CUTOUT 37830401B00064/ ISO 37830401B00064/ COD 5/ VER/BOW
13405 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-11-18 07:16 | 2019-11-18 10:31 | 2 | 195 | 4043021 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST TWICE & NO ANSWER, Broken 19.9 cutout on pole 141-280 in backyard. Crew required/no trucks Released by crew 078H04 crew on site FETR 11:00 ALL PWR restored @ 10:31 please close ticket LRM
13406 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2018-03-23 09:00 | 2018-03-23 15:30 | 1 | 390 | 4044871 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Opened fuses on pole 39830879B04663 at 0900.480v meter and base burnted and control cable, all repairs are made all good at this loc time on was 1530 by amg
13407 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-05-14 16:55 | 2009-05-14 23:25 | 1 | 390 | 55648-1 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TRANSFORMER. I HAVE CALLED DINNIS HE IS GOING TO GET CREW HEADED THIS WAY. RELEASED BY CREW 074S11 IDC XXXX
13408 | Pikeville | 3408101 | SALISBURY | PRINTER | 2018-03-16 08:27 | 2018-03-16 11:17 | 6 | 170 | 4019241 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line cutout ( not shown on map ) on pole 58 broken . xfmr pole 58 opened @ 10:22 and closed @ 11:06 . line fuse pole 58 closed @ 11:17 / ALL WORK COMPLETE / GXJ Released by crew 074S03 cod 1 iso 38831146C00058 entered MD (5 cust on xfmr)
13409 | South Williamson | 3202201 | LOVELY | LOVELY | 2021-05-21 12:30 | 2021-05-21 15:45 | 2 | 195 | 4607221 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA transformer. Replaced xfmr, cutout and arrester. Restored @ 15:45. sh
13410 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-07-21 05:25 | 2011-07-21 08:40 | 2 | 195 | 4571041 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT. NO TRUCKS TO POLE.BAD CUTOUT. REPLACED BAD CUTOUT//VER/CRB
13411 | South Williamson | 3411401 | DEWEY | INEZ | 2018-10-04 13:10 | 2018-10-04 19:40 | 1 | 390 | 4197051 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse on 38820769D00078 is blown due to bad trans cutout on 38820769D30133 .this is one span tap feeding meter 435943439 and trans on pole 78 iis under this line fuse also.changed 19,9 cutout.restored power at 19:40/ ISO 38820769D00078/ COD 1 L3/HFP
13412 | Cannonsburg | 3000101 | ASHLAND | 25-25STREET | 2015-06-30 06:42 | 2015-06-30 08:00 | 5 | 78 | 4695001 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830045C45674 BAD CUTOUT DOOR 10T REPLACED DOOR VER/CRB
13413 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-12-31 07:45 | 2017-12-31 11:00 | 2 | 195 | 4689841 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fuse blown on p-851-219. patrolling..line cutout broken on 851-219.changing cutout.
13414 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-02-15 11:00 | 2016-02-15 14:15 | 2 | 195 | 4697161 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT RELEASED BY CREW 077S05 VER/CRB L/3 CRB
13415 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-12-10 12:20 | 2018-12-10 15:35 | 2 | 195 | 4544691 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o 140-563, to bob tackett Released by crew 078S07,repairs made all cust restored @ 1535 please close ticket thanks.bt L3/HFP
13416 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-07-09 10:30 | 2015-07-09 17:00 | 1 | 390 | 4750261 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR NEEDS NEW LEADS AND CUTOUT AND ARRESTOR , WILL TAKE LINE CREW AND TREE CREW. ASPLUNDH CREW AND GEORGE WHITAKER ARE COMMING. RELEASED BY CREW 077S12 REBUILT SECONDARY SIDE OF XFM ALSO REPLACED CUTOUT VER/CRB
13417 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2018-02-04 11:25 | 2018-02-04 13:35 | 3 | 130 | 4799291 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout or deadend insulater failed/// Lifted hot tap on pole #37820151000030 to isolate truoble @ 11:25/// Need 1 man to assist//NO OUTAGE TILL HT LIFTED @ 1125//Changed bad cutout and lowered primary and neutral// Put hoy tap back on @ 13:35 and restored service
13418 | Hazard | 3309302 | VICCO | JEFF | 2022-01-26 15:50 | 2022-01-26 18:00 | 3 | 130 | 4407061 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | got servin froze out in sec up on slde of , got crew coming to help let wire down and made repairs will have to open transformer when crew get here
13419 | Hazard | 3309302 | VICCO | JEFF | 2021-03-20 11:50 | 2021-03-20 18:20 | 1 | 390 | 4357661 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 KVA csp need line crew 7200V cutout and t/bracket calling help// power on//cod 1
13420 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-23 13:36 | 2011-05-23 16:51 | 2 | 195 | 4144201 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 LINE CUTOUT ( B PHASE ) NO TRUCKS TO POLE. NEED LINE CREW. RELEASED BY CREW 078S01//REPLACED 19.9 KV CUTOUT S&C BRAND CUSTOMERS RESTORED PRTOLLIVER AT 16:50 (OPENED LINE VIA SCADA TO SAFELY CLIMB POLE)// RELEASED BY CREW 078H03 //VER/GAH
13421 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-11-05 16:45 | 2010-11-05 18:55 | 3 | 130 | 53199-1 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT POLE FIRE-//COD 3 ISO 37840288000076 // VER/DBM IDC CHANGED START TIME FROM 1303 CUSTOMER CALL WAS FULL POWER XXXX
13422 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-03-06 09:15 | 2010-03-06 12:30 | 2 | 195 | 63317-1 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE HAVE LINE C/O BROKEN,NEED OTHER SATURDAY MAN AND 12KV C/O/////// REPLACED C/O POWER RESTORED VER/KEP L3/KEP IDC XXXX
13423 | Hazard | 3301401 | COMBS | COMBS | 2011-07-12 13:45 | 2011-07-12 20:15 | 1 | 390 | 4532961 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN TRUCK ACCESSIBLE POLE 271C-179 RELEASED BY CREW 077E02,REPLACED CUTOUT,ARR.& BRKT.,POWER RESTORED @ 20:15.RGP.
13424 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2016-10-06 16:26 | 2016-10-06 17:05 | 10 | 39 | 4964381 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED LINE CREW PLEASE RESEND RELEASED BY CREW 078H11 BAD XFMR 50 KVA 18:30 FETR LRM ALL PWR RESTORED @ 17:05 PLEASE CLOSE TIKET 38830045C24683 VER/AWD L3/HFP XXXHFP
13425 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-04-08 20:55 | 2014-04-09 00:10 | 2 | 195 | 4587691 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 93-212 BAD 25KVA BRING 37.5 YARD BUCKET NO TRUCKS TO POLE RELEASED BY CREW 078S08.. CHANGED BAD ARRESTER ON XFMR, ALL POWER RESTORED VER/TOM L3/TOM
13426 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-12-11 07:18 | 2018-12-11 13:48 | 1 | 390 | 4550821 | 390 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug cable, 160v 1 leg, 80v 1 leg. good @ xfmer and connections on pole, send to r.virgin Released by crew 078S07---Crew on site--installing ADD-A-PHASE--PWR restored (124-124-248V) w Pwr Temp--tbl tkt comp---RMV--Send note to Trouble Crew to make perm. Repairs L3/HFP
13427 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-08-15 10:13 | 2017-08-15 10:43 | 13 | 30 | H4260331 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DISPATCHED IN ACCORDANCE WITH KYPCO LATE NIGHT CALLOUT GUIDELINES. B PHASE COD-19/ L/F OPEN @25-A-328, PATROLLING. BAD POLE TOP INSULATOR ON POLE 25-A-29, TIM HALL GETTING A BIG BUCKET TO COME HELP, WILL HAVE TO OPEN A AND C PHASE TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED A AND C PHASE @1013, CLOSED ALL BACK IN @1043. VER/KEP SJG
13428 | South Williamson | 3411401 | DEWEY | INEZ | 2009-12-13 10:32 | 2009-12-13 13:47 | 2 | 195 | 50440-1 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, CHECKING TROUBLE, BAD CUTOUT, POLE# 696-A-68, CALLED R MARCUM FOR HELP, TWO CUST OUT VER/KEP L3/KEP
13429 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2015-04-15 11:00 | 2015-04-15 13:10 | 3 | 130 | 4321861 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPEN LINE FUSE POLE 183-121AT 11:00 BECAUSE OF BROKEN WINDSTREAM POLE IN PROCESS OF RESTORING ALL CUSTOMERS UNTIL WINDSTREAM CAN SET POLE.. SECONDARY BREAKERS AT POLE 183-120 AND GROUNDS PLACED MID SPAN BETWEEN POLES 183-121 AND 183-120 TAGGED TO DDC TO ISOLATE BROKEN POLE.. PAT STAMPER TO WRITE JOB TO DO AWAY WITH LINE SAID HE WILL CONTACT CABLE AND PHONE COMPANY.. TRANSFORMER IN AT 13:10 AND CUSTOMERS RESTORED//COD 3//AED CREATED//MD FILED// VER/DBM
13430 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-06-13 12:50 | 2008-06-13 19:20 | 1 | 390 | 63876-1 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116701// TRY TO BRING TREE CREW SAT. CUTOUT BROKE CREW NEEDED WILL NEED PICKUP TO GET UP TO HOUSE RELEASED BY CREW 078S08/CREW ON SITE/FETR1930/VEM/COMPLETE/PLEASE CLOSE TICKET/POWER RESTORED 1920/VEM RELEASED BY CREW 078H14 VER/TOM IDCC CNT2 XXXX
13431 | Pikeville | 3413402 | GARRETT | LACKEY | 2016-06-01 11:45 | 2016-06-01 18:15 | 1 | 390 | 4279401 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOUG HALL REPORTS FUSE TO PRIMARY METERGING POLE 64-180 IS OUT/ C PHASE FUSE OPEN AT PRIMARY METERING . REPLACED ALL 3 CUTOUTS AT PRIMARY METERING , ALL WORK COMPLETE / GXJ VER/AWD
13432 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2009-10-23 13:59 | 2009-10-23 16:09 | 3 | 130 | 66583-1 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 32349227 //WR/ 32349227 POLE 45-7502 BAD 25KVA BRING 37.5 4-CUST TRUCK TO POLE RIBBON ON POLE FIRST TRANS. ON LEFT OFF 29TH. ST.WR/ 32349227 POLE 45-7502 BAD 25KVA BRING 37.5 4-CUST TRUCK TO POLE RIBBON ON POLE FIRST TRANS. ON LEFT OFF 29TH. ST. RELEASED BY CREW 078S08/CREW ON SITE/FETR1700/VEM/XFMR CHG ALL CUST RESTORED 1609/PLEASE CLOSE TICKET/THANKS/VEM ISO TF 38830045D47302 COD-3 L3/HFP IDC XXXX
13433 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-11-21 09:55 | 2015-11-21 11:00 | 6 | 65 | 4475901 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKE FUSE/ ISO 39831123D37064/ COD 6/ VER/BOW
13434 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-06-24 05:45 | 2009-06-24 12:15 | 1 | 390 | 53447-1 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3411801// THIS WELL BE DISPATCHED DOING NORMAL WORKING HOURSXFR TO RE-FUSE25 KVA XFR IS BAD,NEED TO REPLACE IT.CALLED T HALL,CREW ENROUTE SHORTLY.NOTE FETR RELEASED BY CREW 074S06 COD-1 ISO 38831056A00321 L3/HFP IDC XXXX
13435 | South Williamson | 3411401 | DEWEY | INEZ | 2011-05-19 09:25 | 2011-05-19 11:35 | 3 | 130 | 4112681 | 390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLOSED FUSES ON POLE 861-137 10:52//STAYED IN// BLEW CENTER PHASE FUSE ON POLE 861-164//FOUND BAD ARRESTOR ON POLE 861-166//REPAIRED//RESTORED AT 11:35//COMPLETE//EM//PLEASE SEND TO ENGINEERING TO HAVE FUSES COORDINATED//EM VER/KEP IDC XXXX
13436 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-05-10 14:49 | 2021-05-10 21:18 | 1 | 389 | 4572151 | 389 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a broke Neutral in service drop,Going to pull METER and climb pole to make Repairs..Restored service at 21:18.
13437 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-09-12 09:41 | 2013-09-12 16:10 | 1 | 389 | 4841561 | 389 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SECONDARY POLE ROTTEN AT GROUND AND FALL OVER, 355 POLE, #4 CU SEC. 100W DTOD, 4/3 SERVICE DROP, DOWN GUY, PHONE CO POLE, NEED TECH TO WRITE A JOB, WELL BE CREW REQ,, HAVE SEC LOOP CUT ON TRANSFORMER POLE, 1071-61 CAN USE TRUCKS RELEASED BY CREW 078S06,,CREW ON SITE,,REPAIRS MADE, ALL POWER RESTORED VER/CRB L/3 CRB
13438 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-08-24 05:26 | 2020-08-24 11:55 | 1 | 389 | 4362651 | 389 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout Guidelineschanged out XFM and got customers restored
13439 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2018-11-19 06:01 | 2018-11-19 12:30 | 1 | 389 | 4457501 | 389 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | // No structure fire, voltage is good going to the house. Neutral connection is broke at the house knob. The porch is very slick where the ladder needs set up. Need pickup, ladder and two men to make repairs. Released by crew 079S02//COD 1//ON 1230 L3/HFP
13440 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2018-07-10 07:41 | 2018-07-10 14:10 | 1 | 389 | 4756421 | 389 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad hot leg on URD service coming from 24-B2-1089, crew coming to help make repairs. Found fault on urd cable, spliced and made back hot @1410. Only 1 customer was out of power.
13441 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2011-08-26 13:51 | 2011-08-26 20:20 | 1 | 389 | 4762291 | 389 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 10 KVA TRUCKS OK/SEND TO FRALEY RELEASED BY CREW 078S03//COD 1. VER/CRB IDC XXXX
13442 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2010-03-10 08:01 | 2010-03-10 11:15 | 2 | 194 | 64510-1 | 388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED A FAILED CHROME TOP CUTOUT. VER/KEP L3/KEP IDC XXXX
13443 | Hazard | 3309302 | VICCO | JEFF | 2019-01-20 12:55 | 2019-01-20 16:09 | 2 | 194 | 4695421 | 388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 19.9 CUTOUT/ replaced cutout and restored power at 1609/ ISO 37830346C00303/ COD 2
13444 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-07-28 13:47 | 2011-07-28 15:24 | 4 | 97 | 4634301 | 388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | NEED CREW TO REPLACE ARRESTOR AND CUTOUT RELEASED BY CREW 078S07//COD 4// VER/DBM IDC XXXX
13445 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-04-07 10:53 | 2020-04-07 12:30 | 4 | 97 | 4567121 | 388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | csp xfmr kicked out under load, may need to send to ryan newsome, need to add xfmr, split load..back on at 12:30. ¦¦¦ sent email as requested. hfp
13446 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-04-07 08:45 | 2012-04-07 15:13 | 1 | 388 | 4653561 | 388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA 7.2KV 120/240V NEED SMALL 4X4 MAT HANDLER,, CUST SAY OK TO GET TO POLE,, CUST ASK TO LOCK GATE WHEN WE LEAVE IIF HE IS NOT THERE,, PRC CREW REQUIRED CREW = B. REYNOLDS & V. MULLINS/CREW ON SITE/FETR1530/VEM/REPAIRS MADE AND POWER RESTORED 1513/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 COD-1 ISO TF 38830548000041 VER/HFP L3/HFP IDC XXXX
13447 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-02-18 08:58 | 2022-02-18 12:12 | 2 | 194 | 4509031 | 388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
13448 | Hazard | 3303901 | LESLIE | HYDEN | 2020-04-20 09:16 | 2020-04-20 12:30 | 2 | 194 | 4722051 | 388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout help on its way
13449 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-05-12 12:58 | 2015-05-12 14:35 | 4 | 97 | 4420721 | 388 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | OPS 035166486---WILL TALK TO BRUCE TO REPAIR LATTER--HOUSE FOR SALE NOBODY LIVING HERE--FOUND BY METER MAN BILL COMBS RELEASED BY CREW 077S06/ BAD UNDERGROUND
13450 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-12-12 21:11 | 2014-12-13 00:25 | 2 | 194 | 4857831 | 388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ETA 20 MINUTES POLE 69C24750 25KVA 7200, C/O & ARRESTOR XFMER BAG OIL CLEANUP. RELEASED BY CREW 078H12 VER/ARN
13451 | Hazard | 3420001 | SOFT SHELL | VEST | 2011-12-10 12:13 | 2011-12-10 18:40 | 1 | 387 | 4167091 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NEED FORMAN AND TWO LINEMAN, BAD UNDERGROUND, 150FT 1/0 UNDERGROUND, BIG BUCKET, 4 YRD PADS. NEED TO CALL STORE ROOM PERSON OUT RELEASED BY CREW 077S08 CHANGED UG CONDUCTOR REPLACED CSP XFMR WITH NEW CONVENTIONAL XFMR POWER RESTORED AT 1840 CREW 077H01 ///VER/CRB IDC XXXX
13452 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-22 03:51 | 2011-01-22 10:18 | 1 | 387 | 63527-1 | 387 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 074S06WILL CHECK FOR PROBLEMS,THIS IS A UG SERVICEWILL CHECK FOR PROBLEMS,THIS IS A UG SERVICE.SERVE-IN FROZE OUT ON XFR POLE,WILL REPAIR/////MADE REPAIRS AND RESTORED,ALL OK AFTERWARDS VER/HFP L3/HFP IDC XXXX
13453 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-07-20 14:37 | 2014-07-20 15:20 | 9 | 43 | 4265111 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER, SHE SAID IT HAS BEEN DOING IT FOR OVER A WEEK, WILL LOOK AT IF SVCR GETS CALLED OUT ON SOMETHING ELSE, XMER THAT IS ARCING IS 248A-431, BROKEN CUTOUT ON POLE 37830248A00845, OPENED LINE FUSE ON POLE 37830248A00369 AT 14:37, REPLACED CUTOUT AND ARRESTER, POWER RESTORED AT 15:20//COD 9// VER/DBM
13454 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-01-09 02:03 | 2015-01-09 08:30 | 1 | 387 | 4922581 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HOT TAP LEAD BURNT OFF WILL REPLACE,,, REPLACED HOT TAP POWER BACK ON AT 8:30/ ISO 38830832000028/ COD 1/ VER/BOW
13455 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-01-02 14:11 | 2011-01-02 14:54 | 9 | 43 | 57970-1 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 38259871 // BROKEN FUSE LINK COD-9 ISO TF 38830045B43633 VER/HFP L3/HFP IDC XXXX
13456 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-07-30 17:28 | 2018-07-30 23:55 | 1 | 387 | 4873501 | 387 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 1OF3 LINEFS OUT@1107-2.GOING TO REPLACE MTRNG CUTOUTS@1107-92 AS THEY ARE IN BAD SHAPE AND POWER IS ALREADY OFF ALSO///REPLACED CUTOUTS&RESTORED POWER,ALL OK AFTERWARDS//////CUTOUTS APPEARED OK
13457 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2022-01-12 22:42 | 2022-01-13 00:51 | 3 | 129 | 4341301 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | servicer ETA approx 0020 // failed cutout // cod 3
13458 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-11-10 07:26 | 2016-11-10 09:35 | 3 | 129 | 4089071 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE VER/CRB
13459 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-07-17 14:44 | 2011-07-17 16:53 | 3 | 129 | 4555861 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LOW SIDE FUSE ON STEPDOWN BLOWN @ 1126-958// THIS IS RIGHT HAND PHASE WITH BACK TO STATION // PATROLING// INS. BAD ON POLE 1126-308// WILL REPAIR///CHANGED INS.// POWER RESTORED//VER/CRB IDC XXXX
13460 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-05-11 15:23 | 2009-05-11 21:50 | 1 | 387 | 61441-1 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | XFMR FUSE OUT ON 3PHASE BANK BAD XFMR RELEASED BY CREW 077H14.......ON SIGHT CHANGEING XFMR.P. HICKS
13461 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-06-26 20:32 | 2009-06-26 21:15 | 9 | 43 | 63839-1 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE//COD 9// VER/DBM IDC XXXX
13462 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-04-04 00:10 | 2008-04-04 00:53 | 9 | 43 | 63651-1 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT CREW REQUIRED TO FIX POLE OPENED LINE FUSE 182-236 AT 0010 HRS BACK ON AT 0053 HRS SENT TO MCCARTY TRUCKS OK 40/4 POLE NOBODY OFF AS PER LLYOD MCCARTY .. OPS ORDER CREATED AND SENT TO ENGR. OK TO CLOSE TICKET. VER/PDP IDC XXXX
13463 | Hazard | 3303902 | LESLIE | WOOTON | 2014-01-25 16:33 | 2014-01-25 18:42 | 3 | 129 | 4312791 | 387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830463000053 BROKEN XFMR CUTOUT, MIGHT HAVE TO REMOVE TAP TO REPLACE/// REPLACED C/O, POWER RESTORED COD-3 ISO TF 37830463000053 VER/HFP L3/HFP
13464 | South Williamson | 3411401 | DEWEY | INEZ | 2010-12-09 04:34 | 2010-12-09 11:00 | 1 | 386 | 64595-1 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON POLE 769-139XFMR FUSE BLOWN ON POLE 769-126//BAD XFMR ON POLE 126/// NEED 25KVA 19.9 XFMR//MANUAL POLE DUE TO SEPTIC SYSTEM//TIM MILLER BRINGING CREW TO CHANGE// RELEASED BY CREW 079S01// WRONG POLE NUMBER, BAD TRANSFORMER IS ON 769-126 , CHANGING NOW TCM//ISO//COD 1// VER/DBM IDC XXXX
13465 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2012-10-14 14:54 | 2012-10-14 21:20 | 1 | 386 | 4139651 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A/B UNDERGROUND FUSE OUT 40T RELEASED BY CREW 078S08 // MULLINS & BAD ARRESTOR VER/KEP IDCC CDC83 XXXX
13466 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2021-08-08 09:55 | 2021-08-08 13:27 | 7 | 212 | 4018271 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout, need 1 man help.//LIFTED A CLAMP ON POLE 37830333B00019 TO BE ABLE TO SAFELY REPLACE CUTOUT ON POLE 37830333B00020//OFF @ 1258 ON @ 1327
13467 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-03-29 10:20 | 2018-03-29 13:33 | 2 | 193 | 4146431 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replaced transformer on pole 37830265000029, customer states that other customers in neighborhood are experiencing the same problems.
13468 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2015-05-04 17:34 | 2015-05-04 20:47 | 2 | 193 | 4390111 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CLAMP ON XFM IS BURNT OFF WILL REPLACE/ OPENED XFM @ 19:50 MADE REPAIRS AND CLOSED BACK IN @ 20:47 AND RESTORED SERVICE//// BOTH CUSTOMERS WERE PART OUT TO BEGIN WITH/ SEND COPY TO CLIFF FREEMAN/// NEED TO CHANGE AND UPGRADE XFM/// BUSHINGS ARE ABOUT BURNT OFF XFM/ ISO 37820149000048/ COD 2/ VER/BOW
13469 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-06-09 22:02 | 2009-06-10 01:15 | 2 | 193 | 63484-1 | 386 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | RISER BAD COMING DOWN POLE NEED CREW TO MAKE REPAIRS TWO CUST, PART POWER CALLED DUTY RELEASED BY CREW 078S09 CREW HAS INSTALLED TWO AUTO TRS. AT THESE LOCATIONS PLEASE SEND L MCCARTY COPY . VER/PDP
13470 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-05-14 13:08 | 2012-05-14 16:21 | 2 | 193 | 4792141 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FEED LIGHTS ON STRUCTURE FOR AVIATION , REPAIRED AND RESTORED POWER AT 1621 VER/KEP IDC XXXX
13471 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-08-01 17:43 | 2010-08-02 00:09 | 1 | 386 | 60241-1 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE,TREES ALL AROUND POLE///////BAD XFR,TIM HALL IS GETTING CREW,NOTE NEW FETR //VER/GAH IDC XXXX
13472 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-03-29 10:47 | 2022-03-29 14:00 | 2 | 193 | 4686791 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Linda Bevins states road crew stopped her saying fuse is blown here and people out of power
13473 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2022-01-20 17:37 | 2022-01-20 20:50 | 2 | 193 | 4392211 | 386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | cust meter base was bad.meter melted out of it and base was arcing.opened transformer fuse on pole 1064B-235 at 20:26 for cust to make repairs.got transformer fuse back in at 20:50
13474 | Hazard | 3308002 | JACKSON | PANBOWL | 2017-06-14 11:08 | 2017-06-14 17:33 | 1 | 385 | 4966741 | 385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA XFMR . RELEASED BY CREW 075H04..REPLACED XFMR., POWER RESTORED38831083C31086 VER/AWD
13475 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-01-14 22:23 | 2018-01-14 23:40 | 5 | 77 | 4747441 | 385 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | one leg of service drop came apart at splice//repairs made//restored to normal at 23:40//complete//em
13476 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-06-10 20:39 | 2009-06-11 03:04 | 1 | 385 | 55040-1 | 385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHG BAD 25 KVA XFMR..BB VER/PDP IDC XXXX
13477 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2020-11-02 08:43 | 2020-11-02 10:00 | 5 | 77 | 4631891 | 385 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole. opened xfmr at 9:45 closed back in at 10:00 power restored
13478 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-11-02 13:20 | 2013-11-02 19:45 | 1 | 385 | 4004081 | 385 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED SERVEND WENT BAD & GOT INTO SERVICE NEUTRAL& BURNED INTO. POWER BACK ON @ 19:45. VER/CRB
13479 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-04-26 08:09 | 2015-04-26 09:26 | 5 | 77 | 4366671 | 385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BROKE ON POLE 401D-26. REPLACED CUT-OUT AND RESTORED POWER AT 09:26. 4/26/2015/ ISO 37830401D00026/ COD 5/ VER/BOW
13480 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-02-22 02:33 | 2011-02-22 08:58 | 1 | 385 | 60031-1 | 385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 424-85... REPLACED CUTOUT RESTORED POWER AT 08:58 // COD 1// VER/DBM IDCC PN181 XXXX
13481 | Cannonsburg | 3001401 | LOUISA | CITY | 2019-07-16 19:58 | 2019-07-16 20:33 | 11 | 35 | 4718351 | 385 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | Opened txmf at 1958 to repairee bad connection. Closed at 2033 apr close ticket
13482 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-02-10 19:22 | 2012-02-10 19:57 | 11 | 35 | 4333221 | 385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 11// VER/DBM IDC XXXX
13483 | Hazard | 3303901 | LESLIE | HYDEN | 2016-06-25 12:52 | 2016-06-25 15:00 | 3 | 128 | 4472951 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT, WILL REPLACE/ POWER ON AT 1500 CAN CLOSE MWL// VER/ ADH
13484 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-06-03 17:07 | 2010-06-03 19:15 | 3 | 128 | 56040-1 | 384 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | TRANSFORMER LEAD GOT INTO MAIN LINE NETURAL AND BURNED BOTH INTO .., REPAIRED BOTH// VER/DBM IDC XXXX
13485 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2011-03-22 07:34 | 2011-03-22 09:10 | 4 | 96 | 56563-1 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ALL POWER ON AT 09:10 COD-4 ISO TF 38830045C30375 VER/HFP L3/HFP IDC XXXX
13486 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-06-22 22:22 | 2018-06-23 00:30 | 3 | 128 | 4650461 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout power restored@00:30
13487 | Hazard | 3302704 | HAZARD | KENMONT | 2009-05-12 09:29 | 2009-05-12 11:05 | 4 | 96 | 63841-1 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP WIRE DOWN ACROSS ROADWAY == NEED LINE CREW & FLAGGERS == ONE WIRE OF A 3 WIRE OPEN SECONDARY # 2 AL == L3/HFP IDC XXXX
13488 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2017-07-19 22:08 | 2017-07-20 01:20 | 2 | 192 | 4144721 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-5016, BROKEN CUTOUT. CUTOUT CHANGED, AND POWER RESTORED 1:20 VER/ARN
13489 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-01-03 18:40 | 2009-01-03 20:16 | 4 | 96 | 51104-1 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | 3001204// POLE WAS CHANGED OUT ABOUT 2 MO AGO BAD VOLTAGE ON U G SER 196 VOLTS ON ONE LEG 16 VOLTS OTHER LEG DIGGING DOWN CHECKING SPLICE// FOUND BAD SPLICE ON NEUTRAL - SENT COPY TO PEGGY VER/TOM L3/TOM IDC XXXX
13490 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-04-23 07:42 | 2012-04-23 09:50 | 3 | 128 | 4695691 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN..NO TREES..MIGHT BE BAD CURRENT LIMITING FUSE..WILL RE-FUSE.//..REMOVED BAD CURRENT LIMITING FUSE..RE-FUSED XFMR..POWER ON NOW..JRV..04/23/12 // COD-3 ISO TF 38821058A00339 VER/HFP L3/HFP
13491 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-12-01 05:58 | 2022-12-01 08:06 | 3 | 128 | 4215851 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole 37830022000015// restored @ 08:06
13492 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-04-18 20:39 | 2012-04-18 22:15 | 4 | 96 | 4685801 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY PREFORM BROKE, REPULLED GUY AND REFUSED LINE COD-4 ISO LF 37830329000012 VER/HFP L3/HFP IDC XXXX
13493 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2009-08-30 21:31 | 2009-08-30 22:35 | 6 | 64 | 56666-1 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3002103/// BAD CONNECTION AT CUTOUT VER/JHM IDCC CCO XXXX
13494 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-04-20 09:42 | 2020-04-20 16:06 | 1 | 384 | 4722161 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse out, broke cutout, 19.9, will need big bucket and flagging crew Released by crew 077S02xfmr fuse out, broke cutout, 19.9, will need big bucket and flagging crew power restored
13495 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-08-19 13:09 | 2022-08-19 16:21 | 2 | 192 | 4764641 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | opened L/F on 983-7 @ 13:09 // 38830983000076 broke @ ground // crew enroute // REPAIRS MADE & RESTORED @ 16:21
13496 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2010-12-24 11:00 | 2010-12-24 13:08 | 3 | 128 | 55529-1 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON BANK POLE 449-275... REPLACED CUTOUT RESTORED POWER AT 13:08//COD 3// VER/DBM IDC XXXX
13497 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-11-20 06:33 | 2008-11-20 09:45 | 2 | 192 | 50138-1 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308402/ BAD LEAD ON XFMR, LOOSE CONNECTION AT BUSHING CAUSED LEAD TO BURN INTO VER/KEP IDC XXXX
13498 | Paintsville | 3401802 | INDEX | HOSPITAL | 2011-07-17 15:56 | 2011-07-17 22:20 | 1 | 384 | 4555981 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANFORMER BAD ON POLE 655-262. 15 KVA NO TRUCK.. 3 MEN CREW CLOSED FUSE IN AT 22:30 COMPLETE RN VER/PDP
13499 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2013-08-06 16:36 | 2013-08-06 17:40 | 6 | 64 | 4629091 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE WAS NOT OUT, HAD TRANSFORMER OUT ON POLE 902-362, CAUSE WAS BAD CUTOUT, I HAVE CHANGED AND POWER IS RESTORED AT THIS LOC AT 1740, TURN IN FOR MAP DIS, TO DRAFTING//MADE MDC VER/CRB L/3 CRB
13500 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2013-07-20 05:08 | 2013-07-20 08:20 | 2 | 192 | 4559971 | 384 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SDB / WILL DISP AT DAYLIGHT BAD CONNECTION ON ONE OF THE PHASE WIRES ON THE TRANSFORMER. VER/TOM L3/TOM
13501 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-02-20 10:52 | 2014-02-20 13:00 | 3 | 128 | 4404111 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEM//////1/0 SEC CABLE DAMAGED,CABLE SQEEZEON BAD ENROUTE///REPAIRS WERE COMPLTED OPEN XMER @10:52 CLOSED @1300 VER/SEF
13502 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-05-30 16:27 | 2012-05-30 19:39 | 2 | 192 | 4850641 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN PLUS LINE FUSE, DIDNT SEE ANYTHING THAT WOULD HAVE CAUSED IT. //// WE HAVE A BAD 15KV 19.9 XFMR. THIS NEEDS A LARGER XFMR. RELEASED BY CREW 077S08 REPLACED WITH A 25 KVA AND REPLACED CUTOUT ,RESTORED POWER AT 1939 COD-2 ISO TF 37830272B21408 VER/HFP L3/HFP IDCC PN1408 XXXX
13503 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-09-07 20:01 | 2021-09-07 23:13 | 2 | 192 | 4219111 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke Xfmr cutout, replaced. Power restored.
13504 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-05-08 14:24 | 2012-05-08 16:00 | 4 | 96 | 4760681 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NOT LINE FUSE OUT TRANS, POLE 902-A-362 7 CUST POWER RESTORED FUSE LINK BROKE//ISO//COD 4// VER/DBM IDC XXXX
13505 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-03-10 12:42 | 2019-03-10 19:06 | 1 | 384 | 4967611 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | XFR RISER HAS COME OUT OF HOTTAP,WILL REPAIR///////////MADE NECESSARY REPAIRS&RESTORED,ALL OK AFTERWARDS
13506 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-03-31 12:45 | 2008-03-31 15:57 | 2 | 192 | 62433-1 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3401002/CUST HAVING VOLTAGE PROBLEMS// CURRENT LIMITING FUSE IS BAD ON TRANS. I AM GOING TO BYPASS IT. I CHANGED CURRENT FUSE. IDC XXXX
13507 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-12-15 12:00 | 2022-12-15 15:12 | 2 | 192 | 4264901 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lifting Hot Line Tap at 37830579B00036 to replace cutout (confirmed outage) at 37830579B00111///Open at - ////Close at -Lifte clamp to replace cutout @ 14:44. Power restored @ 15:12//COD DID NOT CHANGE STILL 2
13508 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-12-27 10:58 | 2009-12-27 14:10 | 2 | 192 | 54839-1 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED LIGHTING ARRESTER & RESTORED POWER AT 12-27-09 AT 14:10 THIS IS SAME OUTAGE TICKET AS 55207 RELEASED BY CREW 074M02
13509 | Hazard | 3302703 | HAZARD | HAZARD | 2022-12-20 09:50 | 2022-12-20 11:26 | 4 | 96 | 4279241 | 384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | STATIC WIRE | off @ 0950 on @ 1126
13510 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-04-10 17:16 | 2015-04-10 23:39 | 1 | 383 | 4306101 | 383 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F IS OUT,WILL RE-FUSE////////////BAD XFR,NEED 15 KVA 7.2,MATERIAL HANDLER,1 MAN/////////////REPLACED XFR AND RESTORED,ALL OK AFTERWARDS VER/KEP
13511 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-06-30 09:37 | 2008-06-30 16:00 | 1 | 383 | 60026-1 | 383 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 19.9 CUTOUT & BIG BUCKET - @ SAW MILL ON RT 3 STS WR# 25027169 //COD-1 VER/HFP IDC XXXX
13512 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-05-04 12:32 | 2020-05-04 18:55 | 1 | 383 | 4796891 | 383 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutoutbad manuel pole need cutout arrester and t-bracket, need couple men Released by crew 077S07
13513 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-08-04 08:19 | 2014-08-04 11:30 | 2 | 191 | 4328801 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR.CUST SAYS WE CAN CHG TOMORROW.OLD BLOCK GARAGE BLD.NO HURRY. MADE OPS ORDER AND SENT TO TIM MILLER..# 033549974... RELEASED BY CREW 076S01//COD 1
13514 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-06-10 14:51 | 2018-06-10 18:02 | 2 | 191 | 4577271 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | current limiting fuse is bad will make repairs
13515 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2008-10-31 13:04 | 2008-10-31 16:15 | 2 | 191 | 61146-1 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400602//WILL REPLACE CUTOUT AND ARRESTER ... REPLACED CUTOUT AND ARRESTER, ALL WORK COMPLETE / GXJ//VER/CRB IDC XXXX
13516 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-05-01 16:34 | 2011-05-01 19:45 | 2 | 191 | 53277-1 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT///////REPLACED BROKEN CUTOUT AND RESTORED//COD 2// VER/DBM IDC XXXX
13517 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-10-15 17:07 | 2018-10-15 20:18 | 2 | 191 | 4256191 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke on transformer cutout.. refused and closed in at 20:18 L3/HFP
13518 | Hazard | 3303902 | LESLIE | WOOTON | 2021-03-12 14:04 | 2021-03-12 17:15 | 2 | 191 | 4331911 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout manuel , need 2 cutouts and t brackets 1 arrester, row crew to cut path Released by crew 077S07 // repaired and restored @1715
13519 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-04-08 15:22 | 2019-04-08 18:33 | 2 | 191 | 4071021 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE OUT ON 38821057D00018B//phase line fuse open on 1057-D-18.Bbhase trans cutout bad on 1057-D-291.NTA//MADE MD TO SHOW B PHASE HAS 2 CUSTOMERS ON IT//B phase line fuse open on 1057-D-18.B b phase trans cutout bad on 1057-D-291.NTA replaced cutout. restoored power at 18:33
13520 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-05-15 08:01 | 2022-05-15 13:05 | 3 | 304 | 4892151 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on transformer, need two man line crew and two man tree crew cut path to pole Released by crew 077S05 . opened cutout on pole 1038-22 @ 12:26 , closed back @ 13:05 Released by crew 075H04
13521 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-11-03 16:18 | 2011-11-03 22:40 | 1 | 382 | 4048001 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA, 7200, TRANSFORMER, ..NEED 2 MEN AND TRANSF, 7.2 KV C/O AND FIBERGLASS T BRKT.CAN WRK WITH MATERIAL HANDLER. PAUL HICKMAN & VIRGIL HURT REPLACED XFMR RESTORED POWER AT 2240 CREW 077H01 COD-1 ISO TF 37830159000055 VER/HFP L3/HFP IDC XXXX
13522 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-11-25 16:24 | 2013-11-25 19:35 | 2 | 191 | 4073551 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 380-51 ***CHANGE ISO POLE****BAD CUTOUT ON POLE 380-51 , TIP OF CROSSARM BURNT OFF SAFE FOR NOW, ONLY 2 CUSTOMERS AFFECTED REPLACED CUTOUT RESTORED POWER AT 19:35. ARM CAN REPLACED LATER. VER/SEF
13523 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2010-07-16 18:52 | 2010-07-17 01:14 | 1 | 382 | 51150-1 | 382 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3010602 ONE WIRE OF 1/0 OPEN WIRE SECONDARY BURNT DOWN AT THE TRANSFORMER POLE BECAUSE OF A BAD CONNECTION CALLING CREW--OPENED TRANSFORMER AT 19:23-- B REYNOLDS RELEASED BY CREW 078S07 IDCC PN NULL XXXX
13524 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-07-21 03:08 | 2022-07-21 09:30 | 1 | 382 | 4535521 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.BAD CURRENT LIMITING FUSE // REMOVED AND RESTORED XFMR @ 09:30//cod 1
13525 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2020-04-27 05:49 | 2020-04-27 09:00 | 2 | 191 | 4755781 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | D.wired down @ 38830186000198, pole 186000166 has roted and fallen over, this section of line is inactive, i cut the trouble in the clear at pole 198 to reenergize line, the inactive tap needs removed at a later time. 20t on pole 124 in at 0900//SENT TO TECH AND LINE
13526 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-06-30 16:04 | 2021-06-30 19:15 | 2 | 191 | 4829151 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50kva xfmr here have called for 1 man and big bucket to replace/// Replaced xfmr and restored @ 19:15
13527 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-09-01 08:34 | 2013-09-01 11:45 | 2 | 191 | 4810541 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..CHG CUTOUT... VER/CRB L/3 CRB IDC XXXX
13528 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-05-19 15:04 | 2017-05-19 18:15 | 2 | 191 | 4820261 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED,206-2210 BROKE XFR CUTOUT ,,NO TRUCKS ,CLOSE SPACING RELEASED BY CREW 078S05 VER/CRB
13529 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2020-08-22 20:56 | 2020-08-23 00:07 | 2 | 191 | 4359111 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Crew req, have broke c/o in alley can use truck, Released by crew 078S06/arrived RM cutout replaced power on @00:07 please close tic RM//cod 2
13530 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-10-01 10:49 | 2012-10-01 14:00 | 2 | 191 | 4102651 | 382 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER, CREW ENROUTE.--- POWER RESTORED AT 14:00 VER/KEP IDC XXXX
13531 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-15 07:34 | 2011-05-15 10:45 | 2 | 191 | 4096071 | 382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 116-160 BAD 25KVA NEED 37.5 TRUCK TO POLE RELEASED BY CREW 078S08/J. HEMLEPP & CREW ON SITE/// REPAIRS COMPLETE POWER RESTORED @ 10:45 078H05//VER/CRB
13532 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-03-20 07:14 | 2015-03-20 09:21 | 3 | 127 | 4212151 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED INTO === REFUSE TRANSF POWER OK COD=3 ISO 37830200B00154 VER/HFP L3/HFP
13533 | Hazard | 3309302 | VICCO | JEFF | 2020-07-18 13:59 | 2020-07-18 20:20 | 1 | 381 | 4179781 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA need crew cust. said could back thru yard 7200V Released by crew 077S03. changed xfmr, all powe restored @ 20:20
13534 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2011-11-22 09:35 | 2011-11-22 11:42 | 3 | 127 | 4099791 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE ISOLATED REPAIRING CUTOUT/273-51 30T// COD 3// VER/DBM IDC XXXX
13535 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2022-02-18 11:35 | 2022-02-18 13:42 | 3 | 127 | 4510901 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout. We replaced three cutouts on pole 272-A4-640
13536 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-08-30 14:54 | 2013-08-30 17:01 | 3 | 127 | 4802361 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE BAD 25KVA 19.9 TRANS. TRUCK TO POLE NEED 19.9 CURRENT LIMMING FUSE ALSO RELEASED BY CREW 078S08/CREW ON SITE/FETR1730/VEM/CHANGED XFMR AND POWER RESTORED TO ALL CUST 1701/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L/3 CRB IDC XXXX
13537 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2015-02-07 05:34 | 2015-02-07 11:55 | 1 | 381 | 4997901 | 381 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | UG SERVICE IN TROUBLE CREW ENROUTE. ONLY ONE CUSTOMER AFFECTED WE INSTALLED THE ADD-A-PHASE TRANSFORMER. THE UG CREW WILL REPAIR THE UG SERVICE ON REGULAR HOURS. VER/KEP L3/HFP XXX
13538 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2019-11-10 02:19 | 2019-11-10 08:40 | 1 | 381 | 4016191 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | // Xfmr cutout failed. cutout and restored @ 8:40. sh
13539 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2010-12-09 09:13 | 2010-12-09 11:20 | 3 | 127 | 64730-1 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY LEAD ON TRANS. HAS BURNED INTO. I AM GOING TO OPEN TRANS. AND SPLICE WIRE. I SPLICED TRANS. LEAD.//COD 3// VER/DBM IDC XXXX
13540 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2015-10-02 12:54 | 2015-10-02 19:15 | 1 | 381 | 4303021 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | PEDESTAL BURNT UP///TIM HALL HAS CREW ENROUTE TO REPLACE RELEASED BY CREW 074H17/ ISO 38831150000096/ COD 1/ VER/BOW L3/HFP XXXHFP
13541 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2021-10-26 00:38 | 2021-10-26 02:45 | 3 | 127 | 4014631 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout burnt top of pole off @ 37830042C00317.// Opened hot tap and xfm on pole 37830042C00262 to make repairs.//Opened @ 00:38Line fuse open @ 37830042C41071.//Bad cutout burnt top of pole off @ 37830042C00317.// Repairs made repairs and restored @ 02:45
13542 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2018-06-20 15:47 | 2018-06-20 17:54 | 3 | 127 | 4629581 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 90-56 broken xform cutout ,replace, refuse power restored
13543 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-08-01 15:44 | 2014-08-01 17:51 | 3 | 127 | 4317661 | 381 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD JOB TO REPLACE GUY ON P#271/ 674, THIS IS FEED OFF OF TRANSFORMER BANK ON P#271/ 481 WHICH HAD BROKE CUTOUT LAYING ON TRANSFORMER ,CHANGING ALL CUTOUTS AND FIXING GUY. VER/CRB
13544 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-01-17 15:52 | 2020-01-17 19:02 | 2 | 190 | 4316541 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse is out will refuse. bad xfmr will need 1 man material handler 15 kva 120/240- 7200 ,t bracket,cutout & lightning arrestor,changed xfmr . power is restored
13545 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-08-21 17:01 | 2012-08-21 18:17 | 5 | 76 | 4959661 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/KEP IDC XXXX
13546 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2012-02-12 09:24 | 2012-02-12 10:40 | 5 | 76 | 4341401 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 448-48.. REPLACED CUTOUT RESTORED POWER AT 10:40///VER/CRB IDC XXXX
13547 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2018-01-13 16:18 | 2018-01-13 16:37 | 20 | 19 | 4744601 | 380 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connections on xfmr pole opened at 16:18 closed at 16:37//WAS PART POWER TILL TRANSFORMER OPENED
13548 | Whitesburg | 3401301 | FLEMING | NEON | 2020-08-13 21:00 | 2020-08-13 22:35 | 4 | 95 | 4322531 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Called Customer No Reading On Meter. cut out is broke in half, it will have to be changed./ ISO 37830355D30366/ COD 4
13549 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2015-03-10 15:21 | 2015-03-10 21:41 | 1 | 380 | 4178791 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B PHASE WAS BLOWN OPENED OTHER TWO PHASES 1613/CREW ON SITE/FETR2200/VEM/REPLACED ARMS @38830021A20532 /REPAIRS MADE AND ALL CUST RESTORED 2141/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
13550 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-03-12 10:48 | 2008-03-12 10:58 | 38 | 10 | 56472-1 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001203//BILL FRALEY OPENED FUSE ON POLE 69-254 TO ISOLATE LINE SO CREWS CAN SAFELY MAKE REPAIRS ON POLE 45-2783, WILL TIE THIS SECTION AT NO POINT POLE 69-118 TO HOWARD COLLINS/13TH ST TO RESTORE ALL CUST WHILE REPAIRS ARE IN PROGRESS CLOSED TIE POINT AT 1058 * @ 1630 OPENED N.O. SW CC 38- CLOSED SWS AT POLE 69-A-254 AT 1630 IDCC TON1056 XXXX
13551 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-11-19 12:02 | 2021-11-19 13:37 | 4 | 95 | 4108641 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a Broke Trans cutout at pole 237-B-80,Going to make repairs and restore service..Restored at 13:37.
13552 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-12-02 13:55 | 2009-12-02 17:05 | 2 | 190 | 56602-1 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 140-141 BURNT OFF WR/ 32905186 40/5 NO TRUCKS RELEASED BY CREW 078S08---CREW ON SITE ,TIME WILL DEPEND IF CUST WILL ALLOW TRUCK IN YARD IDCC TOF1317, PN141, CNT1 XXXX
13553 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-06-05 20:04 | 2016-06-05 21:20 | 5 | 76 | 4311591 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED CUST THEY REPORT POWER SURGES// SERVICE HAD BEEN SPLICED .PHASE CONDUCTOR HEATED UP & BURNED NETURAL INTWO VER/KEP
13554 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-07-15 18:15 | 2015-07-15 18:35 | 19 | 20 | 4884231 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED BAD ARRESTOR 0N 38831053D00030. CLOSED @38831053D00025 @18:23 CLOSED @38831053D00028 @1835/ ISO 38831053D00025/ COD 19
13555 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-01-22 20:32 | 2013-01-22 22:07 | 4 | 95 | 4730811 | 380 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S09//CONNECTION AT TRANS BURNT ///VER/CRB L/3 CRB IDCC FP NULL XXXX
13556 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-09-20 03:39 | 2016-09-20 09:59 | 1 | 380 | 4910521 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLD FOR LINE CREW. TRANSFORMER POLE IS ON THE SIDE OF HILL AND IS NO TRUCK. BAD 7200 CUTOUT IS ON THE ARM NEXT TO THE PRIMARY CONDUCTOR. WILL NEED LINE GUARD. RELEASED BY CREW 079S02 37820005000183 VER/AWD
13557 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2016-03-06 12:45 | 2016-03-06 14:20 | 4 | 95 | 4821271 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TRANSFOMER 37830188B00091 @ 1245OPENED TRANSFORMER CUTOUT POLE 91 AT 12:45/ POWER RESTORED 1420, REPLACED TRANSFORMER CUTOUT AND ARRESTER AND LINE CUTOUT, CREATED OPS ORDER # 033957854 FOR T. HALL TO REPLACE 8 FT ARM AND REMOVE OLD COUTOUT / ALL WORK COMPLETE / GXJ/ ISO 37830188B00091/ COD 4/ VER/BOW
13558 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-12-04 15:27 | 2008-12-04 16:43 | 5 | 76 | 54520-1 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401302// CUTOUT IS BAD AND HAS X ARM ALMOST BURNED INTO REPLACED CUTOUT//VER/CRB L3/KEP IDC XXXX
13559 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-02-03 15:40 | 2016-02-03 17:15 | 4 | 95 | 4673241 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACE CUTOUT VER/CRB
13560 | Whitesburg | 3401301 | FLEMING | NEON | 2011-01-12 10:22 | 2011-01-12 11:00 | 10 | 38 | 60850-1 | 380 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | XFMR SECONDARY LEADS BURNED UP,. WE REPLACED IT. M.D.I.//VER/CRB IDC CHANGED START TIME FROM 0952 XXXX
13561 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-01-03 11:44 | 2010-01-03 13:00 | 5 | 76 | 58645-1 | 380 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTIONS ON TRANSFORMER I OPENED TRANSFORMER AT 1235 AND CLOSED AT 1300 COD-5 VER/HFP L3/HFP IDC XXXX
13562 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-06-24 19:00 | 2015-06-24 20:35 | 4 | 95 | H4651421 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | UNDERGROUND CREW REQUIRED SEC WILL NEED TRACED TO FIND, NO VOLTAGE INSIDE METERBASE RELEASED BY CREW 078S11//BAD SEC CONNECTIONS//OPENED TRANS @ 1900//REPAIRED @ 2035UNDERGROUND CREW REQUIRED SEC WILL NEED TRACED TO FIND, NO VOLTAGE INSIDE METERBASE RELEASED BY CREW 078S11..1 .BAD HOT LEG FEEDING 1043 PANSY LANE. REPAIRED..BLR VER/CRB
13563 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2015-02-04 21:08 | 2015-02-05 00:18 | 2 | 190 | 4991511 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 KVA TRUCKS OK RELEASED BY CREW 078S03///REPLACED XFMR (25KVA) & CUTOUT///PWR RESTORED @ 00:18///VOLT CK GOOD///TBL TKT COMP///RMV VER/KEP L3/HFP XXX
13564 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-03-26 18:35 | 2018-03-26 21:45 | 2 | 190 | 4122011 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed de-energizing 2 customers on 37830092000010 NTA climbed pole replaced cutout restored power at 21:45//made md to show trans on load side of l/f
13565 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2016-04-28 05:50 | 2016-04-28 09:00 | 2 | 190 | 4135961 | 380 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD CONNECTION
13566 | South Williamson | 3411401 | DEWEY | INEZ | 2012-06-08 18:55 | 2012-06-09 01:15 | 1 | 380 | 4895001 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON 648-560///NEED 3 MAN CREW//NO TRUCK//NEED TO REPLACE WITH 25KVA 7200 XFMR//RAY, STEPHEN D & BOWERSOCK, BOBBY D & BAD XFMR ON 648-560///NEED 3 MAN CREW//NO TRUCK//NEED TO REPLACE WITH 25KVA 7200 XFMR//ONLY ONE CUSTOMER OUT//REPAIRS MADE//RESTORED AT 1:15//COMPLETE//EM VER/ARN IDC XXXX
13567 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-03-17 18:52 | 2016-03-17 22:02 | 2 | 190 | 4860191 | 380 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 079H03BAD CONNECTION ON 1082-181 LEAVING CUSTOMER WITH ONLY 120 VOLTS REPAIRED CONNECTION RESTORED POWER AT 21:48 38821082000181 COD 2 VER/AWD
13568 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-11-15 09:28 | 2011-11-15 11:03 | 4 | 95 | 4078251 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | LINE FUSE BLOWN ON 904-15. PATROLLING. GUY WIRE RUSTED OFF AT GROUND ALLOWING GUY TO FALL AGAINST CSP XFMR RISER. REMOVED GUY AS IT IS NOT NEEDED AND RE-FUSED 15T ON 904-15 @ 11:03. SH ///VER/CRB IDC XXXX
13569 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-10-08 20:22 | 2021-10-08 21:00 | 10 | 38 | 4333171 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | At pole 73-B-18 Tie wire has broke and Primary is floating,Going to open Line fuse at 73-B-11 and ground line and make repairs,Will keep up with Time..Opened line fuse at 20:25 made repairs restored at 21:00..
13570 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2016-07-27 19:30 | 2016-07-28 01:50 | 1 | 380 | 4694091 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | K MATE FUSE BLOWED ON POLE 266-212, GOT CHANGED OUT @ 0150. VER/KEP
13571 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-03-10 18:42 | 2020-03-10 20:17 | 4 | 95 | 4467091 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout failed on 8-D-26.i can make repairs but will have too deenergized 1 span tap off of8-D-26,replaced cutout.restored power at 20:17.did not open 1span tap on 8-D-26 Released by crew 079S03 // DID NOT OPEN 1 SPAN TAP ONLY 4 CUSTOMERS AFFECTED //
13572 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-04-10 23:20 | 2014-04-11 05:40 | 1 | 380 | 4594041 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT VER/ARN
13573 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-11-30 07:20 | 2013-11-30 08:55 | 4 | 95 | 4088761 | 380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS IN SECONDARY, MADE REPAIRS RESTORED POWER AT 08:55 VER/PDP
13574 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-07-17 08:41 | 2015-07-17 15:00 | 1 | 379 | 4898691 | 379 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | U/G ONE LEG IS BAD.MILLER IS SENDING THE AUTO TRANSFORMER..CREW REQUIRED.. RELEASED BY CREW 076S01
13575 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-07-16 02:56 | 2014-07-16 09:15 | 1 | 379 | 4252171 | 379 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK DURING NORMAL WORK HOURS. I CHANGED CUTOUT AND REFUSED XFMR COD 1// VER/ADH
13576 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-06-21 19:11 | 2013-06-22 01:30 | 1 | 379 | 4383611 | 379 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR IS BAD,NEED CREW,25KVA 7.2////////////REPLACED XFR AND RESTORED,ALL OK AFTERWARDS VER/ARN
13577 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-11-02 11:07 | 2011-11-02 12:10 | 6 | 63 | 4043441 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER NEEDS UPGRADED TO A 50KVA/120/240V IS CHECKED VOLTAGE WITH BEAST GETTING 5 VOLT DROP ACCROSS LEGS VOLTAGE IS 121/242 AT METERBASE LIGHTS DEEMING WHEN HEAT PUMP STARTS, CHANGED NEUT CONNECTIONS AT MAST, SECVICE SLEEVE, AT SEC POLE AND TRANS POLE, CLEANED TRANSFORMER CONECTIONS AT TRANSFORMER, 3 HOUSES ON TRANSFOMER, CREW REQUIRED 3MEN ,BESIDE OF ROAD ,MATERIAL HANDLER,WILL ALSO REQUIRE NEW RISER RELEASED BY CREW 078H08//VEM/NOROOMLEFT RELEASED BY CREW 078H14 ///VER /CRB IDC XXXX
13578 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-08-26 18:15 | 2020-08-26 19:18 | 6 | 63 | 4384041 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CABLE CO CALLED JEFF BAKER AND REPORTS CONDUCTOR IN TROUBLE AT POLE 37830220000071 // WIRE ALMOST BURNT INTO AT POLE 37830221000086, OPENED LINE FUSE 37830220000016 TO MAKE REPAIRS @ 1815 CLOSED IN @ 1918
13579 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-07-04 16:01 | 2008-07-04 17:04 | 6 | 63 | 62181-1 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE ON 38830206C01250, OPENED UP BANK AND CHANGED CUTOUT, PLEASE SEND COPY TO TECHS, DOUBLE XARMS, 1 NEEDS REPLACED SENT EMAIL TO STEVE MARTIN & LLOYD RAYBURN VER/HFP IDCC TOF1535 XXXX
13580 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-03-05 17:43 | 2014-03-05 18:25 | 9 | 42 | 4455081 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 44544881 // SERVICER OPENED LINE FUSE TO ALLOW HIM TO SAFELY CLIMB POLE & REPLACE BAD CUTOUT // COD-6 VER/HFP L3/HFP
13581 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-01-07 08:56 | 2015-01-07 09:50 | 7 | 54 | 4912381 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830248A00163, POWER RESTORED.// COD 7// VER/ ADH L3/HFP XXX
13582 | Pikeville | 3402003 | KEYSER | MULLINS | 2018-01-06 09:15 | 2018-01-06 11:21 | 3 | 126 | 4712171 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | A phase l/f open @1127-B-500, checking. Fuse melted out, closed back in @1121./ ISO 38831127B00500/ COD 3
13583 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-07-15 12:42 | 2010-07-15 19:00 | 1 | 378 | 50566-1 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CALLED TREE CREW AND LINE CREW RELEASED BY CREW 078S07 BAD CONNECTION AT POLE 141-161 VER/KEP L3/KEP IDC CHANGED EQUIPMENT FROM CONN/CLAMP PER CONF CALL XXXX
13584 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2014-12-23 08:09 | 2014-12-23 10:15 | 3 | 126 | 4876131 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BROKE TRANSFORMER FUSE.//ISO POLE 37820053000194 //COD 3//MADE MD TO SHOW RIGHT COD VER/CRB
13585 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-11-18 12:06 | 2010-11-18 12:24 | 21 | 18 | 57893-1 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED FUSE TO SAFELY REPLACE A BROKEN CUTOUT POLE 273-38//COD 21// VER/DBM IDC XXXX
13586 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-07-18 13:32 | 2021-07-18 15:38 | 3 | 126 | 4930991 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Removed broke cut-out on 38831030000131. Power restored @ 15:38
13587 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-07-26 12:21 | 2018-07-26 15:30 | 2 | 189 | 4859451 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout chng.. COD-2 ISO TF 38830877000046
13588 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-07-28 11:29 | 2012-07-28 13:35 | 3 | 126 | 4856621 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHECKING.CUT-OUT FAILED AT POLE 351-301, OPENED AT 13:10, WILL BE MAKING REPAIRS.MADE REPAIRS, CLOSED TRANS. FUSE BACK IN AT 13:35.
13589 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2021-04-26 17:37 | 2021-04-26 18:40 | 6 | 63 | 4482201 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 377-256.. cutout replaced power restored
13590 | Hazard | 3311103 | STINNETT | WENDOVER | 2013-03-03 00:40 | 2013-03-03 03:49 | 2 | 189 | 4867471 | 378 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED-RED CONN. AT XFMR ONLY ONE CUST. ON THIS XFMR VER/ARN IDC XXXX
13591 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-02-27 00:15 | 2008-02-27 03:24 | 2 | 189 | 50737-1 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408303// COD-2 /, ON SITE, CHECKING TROUBLE, BAD CUTOUT, NEED BIG BUCKET, R MARCUM SENDING HELP VER/LDA IDCC TOF2257 XXXX
13592 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2008-04-03 10:59 | 2008-04-03 13:05 | 3 | 126 | 63363-1 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3301701//7200 VOLT ARRESTOR FAILED ON XFMR - CUT MISMAPPED - ISSUED MAP DISC// VER/TOM IDC XXXX
13593 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-06-01 07:52 | 2022-06-01 14:10 | 1 | 378 | 4991261 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 xfmr on bank//middle xfmr//need 25 kva xmfr and big bucket//xfmr replaced//restored at 14:10
13594 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-02-07 15:45 | 2018-02-07 22:03 | 1 | 378 | 4813931 | 378 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad urd cable at 2614 cumberland ave will need temp. xfm best access from right side Released by crew 078H01/crew on site/FETR 2230/vem/cust full power at 2203/please close ticket/thanks/vem/ ISO 38830045B22628/ COD 1
13595 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-12-20 14:54 | 2015-12-20 17:00 | 3 | 126 | 4547151 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OUT ON POLE 265-11 , PATROLLED LINE , WAS CLEAR . FOUND FUSE WAS BROKE . VER/CRB
13596 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-12-21 11:57 | 2013-12-21 14:03 | 3 | 126 | 4181151 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. REPLACED THE FUSE AND POWER IS BACK ON.//COD 3// VER/DBM L3/HFP
13597 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2020-11-18 13:09 | 2020-11-18 16:18 | 2 | 189 | 4705711 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 19.9 25 kva trans. @991-C-54, Rick Ray crew coming to help change out. Got trans. changed out @1618.
13598 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-07-07 19:02 | 2015-07-07 21:08 | 3 | 126 | 4740361 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 HOT SECONDARY RISER HAD CAME OUT OF BUSHING ON XFMER///MADE REPAIRS///COMPLETE BR/ ISO 38830835B00193/ COD 3/ VER/BOW
13599 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-11-28 14:15 | 2012-11-28 15:09 | 7 | 54 | 4428651 | 378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REFUSED LINE CUTOUT, ALL WORK COMPLETE / GXJ COD-7 ISO LF 38831099000031 VER/HFP L3/HFP IDC XXXX
13600 | Hazard | 3307301 | BULAN | ARY-HEINE | 2010-09-16 10:53 | 2010-09-16 17:10 | 1 | 377 | 50398-1 | 377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S02, XFMR FUSE OUT, BROKE CUTOUT, NEEDS CREW, PLEASE FAX COPY TO BRUCESO THIS CAN BE WORKED ON 9-17-10 RELEASED BY CREW 077S02 COD-1 IDC XXXX
13601 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2017-08-04 07:38 | 2017-08-04 13:55 | 1 | 377 | 4223151 | 377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | P.T. BAD ON PRIMARY METERING REPAIRED ON AT 13:55 D SAMMONS37820219000011 VER/AWD
13602 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-01-08 03:18 | 2010-01-08 09:35 | 1 | 377 | 66151-1 | 377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF. NOT TRUCK APROCH RELEASED BY CREW 079S01.ON SITE IDC XXXX
13603 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-10-29 07:12 | 2012-10-29 13:29 | 1 | 377 | 4180681 | 377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE 1121-309, TO HAVE TOP BURNTED OFF, I OPEN UP SOLID BLADE ON POLE 1121-102 AT 0830, WELL NEED A CREW TO MAKE REPAIRS, 405 POLE, BUT MAY BE ABLE TO USE A POLE EXTEND ON THIS, WELL NEED NEW CUTOUT AND POLE TOP PIN, EVERYTHING ELSE WILL WORK BACK, IS IN FIELD MAY BE ABLE TO GET TRUCKS TO POLE. CREW REQ, HAVE LINE GROUNDED AND TAGGED AT POLE 1121-102 RELEASED BY CREW 078S06 TOTAL COD 31 ISO PO @ 39831121B00102 SEE DUP FOR 30 CUST IN RECORD # H4180681 VER/HFP L3/HFP IDC XXXX
13604 | Hazard | 3310502 | HADDIX | CANOE | 2015-07-21 07:45 | 2015-07-21 14:02 | 1 | 377 | 4923571 | 377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF WILL OPEN SWITCH AT 240/54 WHEN CREW GET S HERE VER/CRB
13605 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-03-13 15:53 | 2015-03-13 19:19 | 4 | 206 | 4190921 | 377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-695 BAD 19.9 CUTOUT NO TRUCK TO POLE COOKSEY LN 1ST. A FRAME ON RIGHT WHEEL WILL BESIDE ROAD POLE 92-329 40T ON 16:50 RELEASED BY CREW 078S08 RELEASED BY CREW 078Q04//COD 4 // VER/DBM
13606 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-08-09 20:02 | 2014-08-09 23:10 | 2 | 188 | 4348891 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED A - LINEMAN 25 KVA XFMR 7200-120/240 & MATERIAL HANDLER
13607 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-09-02 09:52 | 2008-09-02 13:00 | 2 | 188 | 58456-1 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3410501//BILL JOHNSON WORKING WITH WITH NEW RIVER ELECTRIC////VER/CRB IDC XXXX
13608 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-09-28 17:50 | 2015-09-28 20:58 | 2 | 188 | 4283671 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR . REPLACED 25 KVA XFMR RESTORED POWER AT 20:58./ ISO 37830426B00251/ COD 2/ VER/BOW
13609 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-01-25 08:51 | 2009-01-25 10:25 | 4 | 94 | 59723-1 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008702//TRANSFORMER OUTAGE//COD 4//XFORM. FUSE OLD AND BROKE. REFUSED POWER OK// VER/DBM L3/KEP
13610 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-10-09 02:44 | 2022-10-09 09:00 | 1 | 376 | 4007751 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1127-A-182, checking. Trans. fuse melted out, refused @0900. Released by crew 074S05
13611 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-06-21 17:37 | 2011-06-21 20:45 | 2 | 188 | 4367101 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING LINE NOW FOUND ARRESTER BLOWN INTO CLEAR UP, BACK TO FUSE POLE 1147-503 15 T//COD 2//AED CREATED // VER/DBM IDC XXXX
13612 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-03-27 17:52 | 2022-03-27 21:00 | 2 | 188 | 4681491 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout on 478-2004///// No trucks crew required. No outage untill 1840 lifted H.T Released by crew 078S11 Closed at 21:00 Ticket complete.
13613 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2022-07-14 20:02 | 2022-07-14 23:10 | 2 | 188 | 4492211 | 376 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad hot leg on underground. their xfmr is on pole 38830213009001 Released by crew 078S12 Installed Power Temp. Ticket complete
13614 | Hazard | 3303902 | LESLIE | WOOTON | 2008-12-24 15:19 | 2008-12-24 18:27 | 2 | 188 | 63533-1 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH SERVICER ASAP.//7200 CUTOUT BREAKING DOWN... SERVICER THINKS HE CAN REPAIR THIS ON HIS OWN...//WILL DISPATCH SERVICER ASAP. FOUND BAD C/O. WILL REPLACE//COD 2// VER/DBM L3/KEP IDC XXXX
13615 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2012-07-17 16:22 | 2012-07-17 19:30 | 2 | 188 | 4750721 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS FAILED ON POLE 37820125000144 GOING TO REPLACE REPAIRS COMPLETE & POWER RESTORED @ 19:30 COD-2 37820125000144
13616 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2016-03-01 19:36 | 2016-03-01 22:44 | 2 | 188 | 4794441 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REFUSED TRANSFORMER, CAME BACK OUT. BAD 25 KVA TRANSFORMER 7.2 KV, TRUCK ACCESS WITH FLAGGERS. ISOLATED TRANSFORMER. RELEASED BY CREW 077S04 VER/KEP
13617 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2018-10-04 11:56 | 2018-10-04 13:30 | 4 | 94 | 4196731 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke..replaced-ds100418 L3/HFP
13618 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2019-06-20 12:11 | 2019-06-20 13:45 | 4 | 94 | 4555401 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse blown on side & cutout door is burnt up.Will patrol line
13619 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-10-31 16:02 | 2010-10-31 19:10 | 2 | 188 | 50483-1 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37558637 // OPENED LINE FUSE @ 1640 CLOSED @ 1650 - 51 CUST /// POLE 44-4080 BAD CUTOUT/ON SITE PR TOLLIVER//REPLACED 100AMP CUTOUT ALL CUST. RESTORED AT 19:10 PR TOLLIVER// SEE RECORD H1144135-1 FOR THE FUSE OUTAGE. VER/HFP L3/HFP IDC XXXX
13620 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2022-01-08 13:44 | 2022-01-08 20:00 | 1 | 376 | 4325131 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 1113A-211.i got the old transformer removed and a new one in route.made repairs and got transformer fuse on pole 1113A-211 back in at 20:00
13621 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-08-29 22:27 | 2017-08-30 01:35 | 2 | 188 | 4309021 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE A BAD CUT OUT . WILL REPLACE & RESTORE POWER. PRIMARY BUSHING IS BAD . WILL NEED TO REPLACE XFMR . IT IS 15 KVA -19.9/120240. NEED 1 A MAN & MATERIAL HANDLER. VER/KEP L3/HFP XXXHFP
13622 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-08-09 17:59 | 2022-08-10 00:15 | 1 | 376 | 4711481 | 376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad xfmr // crew enroute to make repairsCUST GETTING BAD VOLTAGES // BAD XFMR // OPENED C/O @ 23:15 CLOSED @ 00:15
13623 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-11-20 09:55 | 2021-11-20 12:00 | 3 | 125 | 4110581 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 374-33 restored power at 12:00
13624 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-10-07 19:40 | 2008-10-07 20:05 | 15 | 25 | 53980-1 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308603//LINE CUTOUT FAILING//OPENED LINEFUSE AND TRANSFORMER ON POLE 494-35 @ 1940 TO MAKE REPAIRS//COD 15//3308603//HOT LINE CLAMP BURNT OF RISER OPEN FUSE ON POLE 494-35// VER/DBM IDC XXXX
13625 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-12-12 09:50 | 2014-12-12 10:15 | 15 | 25 | 4855751 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED ON 978-124. OPENED XFMR 38830978C10008 @ 9:50. MADE REPAIRS AND RESTORED XFMR @ 10:15. SH RELEASED BY CREW 076S02 ISOLATION POLE 38830978C10124//COD15// VER/ ADH
13626 | Hazard | 3310502 | HADDIX | CANOE | 2013-01-30 09:24 | 2013-01-30 15:39 | 1 | 375 | 4755031 | 375 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | HOT WIRE ON TRANSFORMER, GOING TO OPEN TRANSFORMER AND CLIMB POLE AND TO REPAIR ///VER/CRB L/3 CRB IDC XXXX
13627 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-03-24 17:55 | 2013-03-24 20:00 | 3 | 125 | 4952201 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN INTO. I AM GOING TO REPLACE CUTOUT. I CHANGED CUTOUT//COD 3// VER/DBM IDC XXXX
13628 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-08-29 20:03 | 2009-08-29 22:08 | 3 | 125 | 56251-1 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402001//REPLACE BAD CUTOUT VER/DKG L3/DKG IDCC CNT20 CREATED OUTAGE TO OPEN FUSE, CHANGED TIME ON FROM 2211 XXXX
13629 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2012-04-26 11:55 | 2012-04-26 14:00 | 3 | 125 | 4712531 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LIGHTNING ARRESTOR ON POLE 37830318D00323, REPLACED ARRESTOR, POWER RESTORED. VER/KEP IDC XXXX
13630 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-04-07 06:30 | 2009-04-07 12:45 | 1 | 375 | 50106-1 | 375 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL DISPATCH SERV AT REG WORK TIME TODAY.WR# 29265745 CALLED CTOLLIVER TO HELP--RESQUEZED ALL TRANSFORMER CONNECTIONS//VER/CRB IDC XXXX
13631 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-06-24 13:52 | 2010-06-24 15:07 | 5 | 75 | 56461-1 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | I HAVE A LINE DOWN JUST BEFORE THE LINE WE HAD THE LAST TIME WE WILL BE WORKING THE SAME POLE 37830185000113 ///PHASE B WAS THE ONLY ONE BLOWN. PULLED OTHER 2 OFF AT 13:52. I ALSO HAD 2-BLOWN FUSES ON POLE 37830185000176 1-6T FUSE FOR BANK AND 1-30T FUSE THAT FEEDS SINGLE PHASE LINE. I WILL PATROL THE LINE TO MAKE SURE NOTHING IS ON SINGLE PHASE./// REPLACED DOWNED CONDUCTOR AND RESTORED POWER AT 15:05 TIM MCCOY //COD 17 IDC ADDED PH B CUSTOMERS TO OUTAGE 56254-1 USE THIS FOR OPEN PH A AND C XXXX
13632 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-12-12 15:10 | 2022-12-12 21:25 | 1 | 375 | 4252891 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Fiber caused pole 359-9 to lay over due to Ground being soft,Lift Hot Tap at pole 359-8 to isolate Trouble,Have Crew bringing Yard Dog to Straighten pole. Released by crew 074S01//LIFTED HT @ 1510Fiber caused pole 359-9 to lay over due to Ground being soft,Lift Hot Tap at pole 359-8 to isolate Trouble,Have Crew bringing Yard Dog to Straighten pole. Released by crew 074S01. Repairs made. Restored at 21:25
13633 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2018-05-08 18:15 | 2018-05-08 19:30 | 5 | 75 | 4325551 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER BURNT OFF//OPENED TRANS @ 1815 CLOSED 1930//38830045C35042 COD 5
13634 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-07-22 10:18 | 2009-07-22 11:33 | 5 | 75 | 58928-1 | 375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP LINE FUSE IS OUT AT MOUTH,WILL PATROLCUTOUT ON INACTIVE XFR AT FUSE POLE AT MOUTH HAD BROKEN,CLEARED IT UP,RE-FUSED AND RESTORED /// COD-5 IS LF 38830983000049 L3/HFP IDCC PN51 XXXX
13635 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-10-07 12:23 | 2014-10-07 15:30 | 2 | 187 | 4564991 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE, POWER RESTORED COD-2 ISO TF 37830130000094 VER/HFP L3/HFP
13636 | Hazard | 3309003 | JEFF | VIPER | 2015-04-29 10:28 | 2015-04-29 16:42 | 1 | 374 | 4375401 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WRONG POLE NO SHOULD BE 37830393B20155 === TRANSF BURN UP NEED LINE CREW AND 15 KVA 7200 === GET TRUCK TO POLE ===// ISO 37830393B20155/ COD 1 CCC*****/ MD DONE/ VER/BOW
13637 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-04-20 18:48 | 2011-04-20 21:55 | 2 | 187 | 61512-1 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OPEN/SERVICER TO TRY FUSE/FETR2230/VEM/ROTTEN FUSE LINK/POWER RESTORED TO ALL CUST 2155/PLEASE CLOSE TICKET/THANKS/VEM//COD 2// VER/DBM IDC XXXX
13638 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-10-30 08:06 | 2022-10-30 14:20 | 1 | 374 | 4078101 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 15KVA TRANSFORMER /// TRUCK ACCESS /// POLE 199-A-186 /// NEED NEW 19.9 CUTOUT // NEED LINECREW /// Released by crew 077H12 power restored at 14:20//cod 1//
13639 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-11-01 13:18 | 2019-11-01 16:25 | 2 | 187 | 4276851 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will replace/// Replaced bad cutout and restored service @ 16:25/ ISO 37830312000088/ COD 2
13640 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-08-25 06:08 | 2016-08-25 09:15 | 2 | 187 | 4833601 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT DOOR BROKE CAUSING FUSE TO BREAK. REPLACED CUTOUT AND RESTORED @ 9:15. SH COD-2 ISO TF 38830905000185 VER/HFP L3/HFP
13641 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-03-20 21:59 | 2014-03-20 22:10 | 34 | 11 | 4514581 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OUTAGE NECESSARY TO BYPASS A DEFECTIVE REGULATOR COD-34 ISO OCR 38830306000024 VER/HFP L3/HFP IDCC FEC57 XXXX
13642 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-11-19 07:38 | 2014-11-19 10:45 | 2 | 187 | 4744661 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD SQUEEZON ON 38830502000029 MAY HAVE A DAMAGE COMPLAINT//BAD SQUEEZON ON 38830502000029MAY HAVE A DAMAGE COMPLAINT INSU-LINK BAD FROM RISER TO SERVICE MTR #190408026 ALL PWR RESTORED PLEASE CLOSE TICKET THANK YOU LRM VER/CRB
13643 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-02-23 08:33 | 2020-02-23 11:40 | 2 | 187 | 4425441 | 374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT,WILL RE-FUSE///////BAD XFR,NEED 25KVA 19.9,1 MAN W MATERIAL HANDLER // restored @ 1140 L3/HFP
13644 | South Williamson | 3411401 | DEWEY | INEZ | 2013-09-26 20:52 | 2013-09-27 03:05 | 1 | 373 | 4891161 | 373 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VINES AND TREES HAVE XFMR COVERED//FUSE BLOWN//GOING TO TRY TO CLEAR UP//CLEARED VINES AND FUSE CAME BACK OUT HARD//NEED 3 MEN AND BIG BUCKET//ANS 25 KVA 19.9 XFMR// MILLER,NEWSOME,GOBLE TO ASSISTVINES AND TREES HAVE XFMR COVERED//FUSE BLOWN//GOING TO TRY TO CLEAR UP//CLEARED VINES AND FUSE CAME BACK OUT HARD//NEED 3 MEN AND BIG BUCKET//ANS 25 KVA 19.9 XFMR/HAVE XFMR REPLACED//RESTORED AT 3:05//COMPLETE//EM IDC XXXX
13645 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2010-12-20 04:02 | 2010-12-20 10:15 | 1 | 373 | 54428-1 | 373 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 7200 XFMR, PROBABLY NO TRUCK, CREW REQUIRED RELEASED BY CREW 078S05//ON SITE NO TRUCKS PT//POWER RESTORED AT 10:15 P R TOLLIVER//COD 1// VER/DBM IDC XXXX
13646 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2021-07-21 17:58 | 2021-07-21 20:02 | 3 | 124 | 4943671 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3 bad lf cutouts on pole 118-4022. trk to pole. alley way near parking lot of new courthouse and floodwall. Released by crew 078S07repairs made all cust restored @ 2002 please close ticket thanks.bt
13647 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-04-26 14:08 | 2015-04-26 16:12 | 3 | 124 | 4367641 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT TO SINGLE PHASE XFMR IS BROKEN ON 833-571.CHANGING./ ISO 38830833D00571/ COD 3/ VER/BOW
13648 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-04-28 17:53 | 2014-04-28 19:57 | 3 | 124 | 4643351 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOOK BEST GUESS AT POLE LOCTION REPLACED BAD TRANSFORMER CUTOUT. VER/CRB
13649 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-10-08 18:04 | 2013-10-08 18:10 | 62 | 6 | 4923341 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | HANDLE DROPPED DOWN ON RECLOSER WHEN CREW WAS TAKING IT OFF NON-RECLOSE /// COD-132 ISO OCR 37830381D40692 ON @ 1810 // CONTRACTOR TO TALK TO GLEN ABOUT RECLOSER - MAY NEED REPLACED VER/HFP L3/HFP IDCC CNT133, CCO, PHASE B ONLY XXXX
13650 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2008-09-17 11:13 | 2008-09-17 11:25 | 31 | 12 | H64819-1 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3008003// FOUND LOOP BURNT OPEN @ POLE 94-6510 / OPENED C PHASE RECLOSER TO ISOLATE AND MAKE REPAIRS - OPENED @ 1113 AND CLOSED @ 1125// COD 69 REPLACED RISER AND HOT TAP// 41 CUSTOMER OFF ENTIRE TIME FROM LOOP THAT BURNT ON SOLID BLADE - THEN ADDITIONAL 28 OFF WHEN OPENED C PHASE RECLOASE IDCC DUP TO OPEN RECLOSER XXXX
13651 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-12-26 12:31 | 2022-12-26 13:25 | 10 | 54 | 4359441 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed mid span in service. Bad connection in 1/0 secondary. Will have to let it down to repair. // XFMR 38830858B00172 OPEN @1231 // HAVE TO OPEN LF ON 38830858B00163 TO SAFLEY MAKE REPAIRS // LF OFF@1255 RESTORED ALL @1325
13652 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-10-22 09:25 | 2019-10-22 12:31 | 2 | 186 | 4180461 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED FOR CREW TO REPLACE CUTOUT COD-2 ISO TF 37830178B00332 L3/HFP
13653 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2013-12-29 12:48 | 2013-12-29 19:00 | 1 | 372 | 4209941 | 372 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL IN SERVICE DROP HAS PULLED OUT OF A SLEEVE. I AM GOING TO SPLICE DROP. I SPLICED DROP. VER/HFP L3/HFP
13654 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-09-28 06:49 | 2012-09-28 09:55 | 2 | 186 | 4094511 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. IS BAD. I AM CALLING FOR A CREW. RELEASED BY CREW 074S01 S.RAY CREW ONSITE ///VER/CRB L/3 CRB IDC XXXX
13655 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2015-11-30 09:52 | 2015-11-30 12:58 | 2 | 186 | 4494481 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 796-218 BURNED OFF AT TOP//LINE FUSE BLOWN ON POLE 796-110//NO TRUCK//CREW ON SITE //REPAIRS MADE//RESTORED AT 12:57//COMPLETE//EM /// XFMR ON THIS POLE NEVER OUT PER SERVICER // COD-2 ISO LF 38820796B00110 VER/HFP L3/HFP
13656 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-12-21 08:05 | 2022-12-21 10:09 | 3 | 124 | 4282501 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans open at 237-A-158,Will be trying to get it back in.Trans open at 237-A-158,Broke Trans Cutout,Will be making repairs.Trans open at 237-A-158,Broke Trans Cutout,Will be making repairs.Restored at 10:09.
13657 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-10-15 13:29 | 2012-10-15 16:35 | 2 | 186 | 4143211 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN// WILL REFUSE// BAD CUTOUT // T. HALL SENDING HELP RELEASED BY CREW 074S05 IDC XXXX
13658 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-09-29 09:38 | 2020-09-29 15:50 | 1 | 372 | 4507491 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke manual cutout on pole 269-30. restored 15:50
13659 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2018-02-22 15:55 | 2018-02-22 17:47 | 6 | 112 | 4873531 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout 160-9 cleared up cutout crew will have to lower Released by crew 078S05.opened and tagged 38830160000005 @1655,,repairs complted,,closed fuse @1747 Released by crew 078H03/
13660 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-12-11 08:02 | 2012-12-11 10:06 | 3 | 124 | 4459871 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, REPLACED COD-3 ISO PO 37830256000161 VER/HFP L3/HFP
13661 | Hazard | 3310502 | HADDIX | CANOE | 2015-06-18 08:48 | 2015-06-18 15:00 | 1 | 372 | 4593671 | 372 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 37830169C00262 WE HAVE 15KV, 7200 XFMR WITH BUSHING BURNT OFF, PROBABLY NEED XFMR CHANGED OUT. ITS THE MIDDLE XFMR. NEEDS CREW, ALERTED JIM HE GETTING CREW RELEASED BY CREW 077S08 VER/CRB
13662 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-06-13 16:54 | 2014-06-13 20:00 | 2 | 186 | 4087921 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA XFMR.TRUCK ACCESS.NEED 1 MAN AND MATERIAL HANDLER. // COD-2 ISO TF 38830900000247 VER/CRB
13663 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-07-19 21:47 | 2013-07-19 23:20 | 4 | 93 | 4559141 | 372 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LEAD APPEARS IN TWO ON POLE BACK ON THE HILL// XFMR SEC. RISER FELL OUT OF BUSHING// REPLACED RISER// POWER IS RESTORED// TREES IN THIS SPAN ARE 5 OVER THE PRI. NEEDS CUT BAD//SEND TO R/W // COD 4// VER/DBM
13664 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2019-07-07 19:32 | 2019-07-08 01:44 | 1 | 372 | 4675211 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link appears to have broke. Restored @ 1:44. sh
13665 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-03-09 09:42 | 2015-03-09 11:15 | 4 | 93 | 4171211 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE, REPLACED POWER RESTORED AT THIS LOC AT 1115/ ISO 39831122C00181/ COD 4/ VER/BOW
13666 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-06-27 13:14 | 2016-06-27 15:18 | 3 | 124 | 4484181 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # IS ACTUALLY 38830906000107 // 2 CUSTOMERS // BAD CUTOUT. GOING TO CHANGE.// RESTORED AT 15:18 VER/KEP
13667 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-12-10 06:21 | 2012-12-10 08:25 | 3 | 124 | 4455481 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED, NO DAMAGE TO THE POLE. COD-3 ISO TF 37820099000089 VER/HFP L3/HFP
13668 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2012-12-21 07:53 | 2012-12-21 10:59 | 2 | 186 | 4497801 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LINE FUSE RISER BROKEN POLE#45-43/B PHASE OUT/SERVICER TO MAKE REPAIRS/FETR 1130/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1059/PLEASE CLOSE TICKET/THANKS/VEM ////VER/CRB L/3 CRB
13669 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-11-13 15:08 | 2010-11-13 21:20 | 1 | 372 | 55444-1 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | BAD 25KVA 7200 XFMR, TRUCK OK, POLE HAS PRIMARY JUMPER ABOUT 1 FROM POLE, PLEASE CORRECT. SEND TICKET TO J LINKOUS. RELEASED BY CREW 078S05//WR# 37749115 // RELEASED BY CREW 078H02 // BACK ON AT 2120 VER/TOM IDC XXXX
13670 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-03-04 19:34 | 2010-03-04 22:40 | 2 | 186 | 62947-1 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BROKE RELEASED BY CREW 079S01. ON SITE TO CHANGE CTOUT.THERE WAS TWO CUSTOMERS ON THIS TAP.//COD 2// VER/DBM IDCC PN86 XXXX
13671 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2016-10-08 08:06 | 2016-10-08 14:18 | 1 | 372 | 4970381 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RESET MAIN/TRANSFORMER MAKING LOUD NOISE/---TRAN QUIET NOW-W/MTR 120/0---NO MTR 120/105--SUSPEC BAD UG--NEED AUTO TRAN--CREW REQ--DS100816 RELEASED BY CREW 078S01---INSTALLED ADD-A-PHASE--VOLT CK 124-124-248---TBL TKT COMP--ONLY 1 CUST--- VER/CRB L3/HFP XXXHFP
13672 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-07-09 10:03 | 2013-07-09 16:15 | 1 | 372 | 4491331 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VINES AND TREES HAVE POLE COVERED. RELEASED BY CREW 077S04VINES AND TREES HAVE POLE COVERED. ---- CUTOUT BROKEN. COD-1 ISO TF 37830246A00148 VER/HFP L3/HFP IDC XXXX
13673 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-06-07 17:57 | 2011-06-07 19:30 | 4 | 93 | 4259041 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACE CURRENT FUSE COD-4 ISO TF 38831100000051 VER/HFP L3/HFP IDC XXXX
13674 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-12-22 08:17 | 2012-12-22 09:50 | 4 | 93 | 4506051 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT, FUSE TAIL BROKE, POWER RESTORED ////VER/CRB L/3 CRB
13675 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-12-08 11:34 | 2013-12-08 14:40 | 2 | 186 | 4115781 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 CUTOUT BAD RELEASED BY CREW 077S01 ONLY 2 CUST. ON THIS XFMR.. VER/SEF L3/HFP
13676 | Pikeville | 3407101 | TOPMOST | DEMA | 2014-04-25 12:10 | 2014-04-25 14:14 | 3 | 124 | 4633481 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 10T LINE FUSE OUT DUE TO BAD CUTOUT POLE 113-169. WILL BE OUT OF TRUCK MAKING REPAIRS. REPAIRS MADE FUSE UP EVERYTHING OK//COD 3// VER/DBM
13677 | Whitesburg | 3312901 | JENKINS | KONA | 2020-07-20 12:34 | 2020-07-20 15:40 | 2 | 186 | 4187541 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester failed causing it to burn top side of transformer. will need 25 kva 7200 and cutout Released by crew 077S11 replaced transformer installed new cutout power restored at 15:40
13678 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-04-30 14:50 | 2019-04-30 16:23 | 4 | 93 | 4188101 | 372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | rotten windstream pole 1147c3 5059, line truck holding is safe. crew reqd. NO OUTAGE AT THIS TIME,open xfmr @ 1450,repairs made all cust restored @ 1623 please close ticket thanks.bt/ ISO 39831147C35059/ COD 4 L3/HFP
13679 | Hazard | 3309302 | VICCO | JEFF | 2011-06-20 13:00 | 2011-06-20 19:11 | 1 | 371 | 4353101 | 371 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRANSF === NEED 1 MAN AND BIG BUCKET == RELEASED BY CREW 077S03CHANGED XFMR RESTORED POWER AT 1911 CREW 077H01//COD 1// VER/DBM IDC XXXX
13680 | Pikeville | 3409502 | BURDINE | LEVISA | 2010-03-13 15:24 | 2010-03-13 21:35 | 1 | 371 | 66469-1 | 371 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. BAD TRANS. WILLIE IS SENDING HELP. WE CHANGED TRANS. IDC XXXX
13681 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-01-09 01:30 | 2019-01-09 02:44 | 5 | 74 | 4648231 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | related to 4644071//opened line fuse @ 0130///closed @ 0244//cod 5/high side came out of xfr cutout,manual work on hill
13682 | Hazard | 3307301 | BULAN | ARY-HEINE | 2013-10-21 09:17 | 2013-10-21 15:27 | 1 | 370 | 4950781 | 370 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OLD FARM SERVICE . WIRE BURNT AT METERBASE , WILL HAVE TO REPLACE WIRE AND METERBASE. RELEASED BY CREW 077S04OLD FARM SERVICE . WIRE BURNT AT METERBASE , WILL HAVE TO REPLACE WIRE AND METERBASE. ONLY 1 CUST OUT. REBUILT FARM SERVICE. POWER RESTORED. (AEP OWNED EQUIPMENT) VER/HFP L3/HFP IDC XXXX
13683 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2015-02-27 21:01 | 2015-02-27 22:15 | 5 | 74 | 4086611 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE REPLACED POWER IS RESTORED AT THIS LOC AT 2215/COD 5// VER/ ADH
13684 | Hazard | 3303902 | LESLIE | WOOTON | 2016-06-21 17:46 | 2016-06-21 19:00 | 5 | 74 | 4400081 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT REPLACED CUTOUT & CLOSED XFMR @ 19:00 VER/AWD
13685 | Hazard | 3303901 | LESLIE | HYDEN | 2008-10-12 16:20 | 2008-10-12 22:30 | 1 | 370 | 55250-1 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303901//REPLACED 10KVA 7.2KV 120/240 VER/JHM IDC XXXX
13686 | Hazard | 3309302 | VICCO | JEFF | 2011-01-17 21:30 | 2011-01-18 00:35 | 2 | 185 | 62031-1 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 100 FT OF 4/3 SERVICE BURNT DOWN, NEED 1 MAN AND WILL REPLACE WITH 2/3. DUTY SUPERVISOR NOTIFIED. IDC XXXX
13687 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-11-27 08:35 | 2020-11-27 11:40 | 2 | 185 | 4725181 | 370 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CALLED CUST NO RDG ON MTR//. was here last night & everything checked good, voltage & beast checked good. all connections look good & everything tight in meter base. voltage test this morning showed nothing on one hot leg. crew reqd. 4/0 ug. Released by crew 078S04 power temp installed LRM//DAE # 1000053687//SENT TO LINE
13688 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-05-07 07:46 | 2012-05-07 09:00 | 5 | 74 | 4753651 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN.CHG FUSE.. VER/KEP L3/GDK IDC XXXX
13689 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-01-29 10:40 | 2014-01-29 13:45 | 2 | 185 | 4323581 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | THE FAULT POLE IS 478-1030 LINEVREW REQUIRED NEED 12KV 37.5 XMF TRUCK OK,,PLEASE SEND TO BRENT T RELEASED BY CREW 078S11, CREW ON SITE, REPLACED XFMR AND CUTOUT, ALL POWER RESTORED COD-2 ISO TF 38830478001030 VER/HFP L3/HFP
13690 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-03-11 19:51 | 2014-03-11 22:56 | 2 | 185 | 4469391 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT DOOR. CUTOUT WILL NEED BE REPLACED. NO BUCKET TO POLE RELEASED BY CREW 078H25 //VER/GAH
13691 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-04-05 18:31 | 2021-04-05 21:36 | 2 | 185 | 4421311 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SINGLE PHASE SIDE TAP DOWN,ROAD XING.NEED #4,CREW,FLAGGERS,//cod 1
13692 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-07 06:50 | 2011-01-07 09:55 | 2 | 185 | 59402-1 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMIT FUSE. ALSO 1T TRANSFORMER FUSE OUT. I HAVE REPAIR MADE FUSED UIP EVERYTHING OK. SEND COPY OF THIS TO BOB SHURTLEFF AND ENG PIKEVILLE. THIS IS SOMETHING THAT HAS CAUSED PROBLEMS FOR A WHILE NOW.//VER/CRB IDC THIS IS NOT THE CORRECT POLE NUMBER ACCORDING TO THE NOTES XXXX
13693 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2016-06-02 13:55 | 2016-06-02 17:00 | 2 | 185 | 4285671 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 37830248B00180, CAN PROBABLY WORK WITH BIG BUCKET, NEED LINE CREW AND 7200 CUTOUT. RELEASED BY CREW 077S04 POWER RESTORED AT 17 00/ ISO 37830248B00180/ COD 2/ VER/BOW
13694 | South Williamson | 3411401 | DEWEY | INEZ | 2017-02-28 13:05 | 2017-02-28 16:10 | 2 | 185 | 4428521 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 768-196///XFMR CUTOUT BROKE ON POLE 768-329///THIS XFMR ONLY FEEDS SOME 2 LIGHTS HERE AT SCRAPYARD//I CAN ISOLATE WITH LONG STICK///TALKED TO SCRAP YARD OWNER HE IS GOING TO CLEAR ME APATH TO POLE AND I CAN REPLACE CUTOUT TOMORROW TO RESTORE LIGHTS//RESTORED CUSTOMERS AT16:10//LIGHTS ONLY THING STILL OUT WILL REPAIR TOMRROW WHEN HE MOVES OLD CARS OUT OF THE WAY// L/F SHOWS ZERO CUST BUT 2 HSES PER SERVICER VER/CRB
13695 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-06-04 21:30 | 2011-06-05 00:35 | 2 | 185 | 4231791 | 370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 35 FT SECONDARY POLE BROKE DUE TO GROUNDLINE ROT AND A RUSTED OFF GUY WIRE BACKING UP 1/0 LASH. POLE 979-104. RELEASED BY CREW 076S0235 FT SECONDARY POLE BROKE DUE TO GROUNDLINE ROT AND A RUSTED OFF GUY WIRE BACKING UP 1/0 LASH. POLE 979-104. OPENED SECONDARY LOOPS ON 38830979D00039 @ 21:30 (HAD METER 533743267 OUT), MADE REPAIRS AND CLOSED LOOPS @ 00:35 RESTORING THE ONE CUSTOMER. SH VER/TOM L3/TOM IDC XXXX
13696 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-29 13:46 | 2008-03-29 19:55 | 1 | 369 | 61968-1 | 369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// REPLACE POLE DUE TO BAD CUTOUT RELEASED BY CREW 077S09 // VER/TOM IDC XXXX
13697 | Paintsville | 3410602 | E.PRESTON | LANCER | 2022-09-07 09:32 | 2022-09-07 11:35 | 3 | 123 | 4850531 | 369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | had a broke nutral at xformer pole 955-C-45 had to open xformer at 11:20 and splice service drop neutral and got xformer 955-C-45 restored at a time of 11:35
13698 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2019-12-12 07:57 | 2019-12-12 10:00 | 3 | 123 | 4146731 | 369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced old cutout door
13699 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-03-01 20:00 | 2011-03-01 20:09 | 41 | 9 | H65340-1 | 369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | STS WR # 38986441 // MAIN LINE POLE IS BROKE IN MIDDLE, WILL HAVE TO HAVE OUTAGE TO REPLACE, CALLING FOR HELP. NO POWER OFF AT THIS TIME RELEASED BY CREW 077S02 DUE TO OUT OF PHASE SWITCHING TOOK INTERRUPTION FROM 2000 TO 2009 (41 CUST) //VER/GAH SEE DISPATCH LOG FOR SWITCHING DETAILS. IDC CHANGED FROM SCHEDULED XXXX
13700 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-09-13 18:01 | 2013-09-14 00:10 | 1 | 369 | 4852681 | 369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 596-88 NO TRUCKS TO POLE, LINECREW REQUIRED RELEASED BY CREW 078S11//SWITCH AT 2215 17 COD//BROKEN CUTOUT ON 596-88 NO TRUCKS TO POLE, LINECREW REQUIRED RELEASED BY CREW 078S11 (BAD POLE HAD TO GUY IT OFF TO MAKE IN SAFE TO CLIMB ;SEND TROUBLE TICKET TO TECH TO BE CHANGED OUT AT LATER: ; DATE TRACK EQUIPTMENT REQUIRED VER/KEP SEE H4852681 FOR OUTAGE TO REPLACE CUTOUT L3/HFP IDC XXXX
13701 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-05-25 17:36 | 2019-05-25 23:45 | 1 | 369 | 4332801 | 369 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power, 200 span of 2/3 secondary has bad splice in mid span, need big bucket and 2 men. some 2/3 to splice with. Released by crew 077H09 power restored at 23:45
13702 | Pikeville | 3407101 | TOPMOST | DEMA | 2009-02-05 09:41 | 2009-02-05 15:50 | 1 | 369 | 55858-1 | 369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3407101// CUST SAID LINE CREW WAS DOING WORK IN THE AREA REPAIRING POLE AND ARMS AND AND HE SAID ALL THE POLE WERE SHAKING AND MOVING NOT SHURE IF IT BROKE SEC DOWN POLE TO POLE OR NOT. I WILL HAVE TRANSFORMER OFF AT POLE 114A17. THIS WAS A 4-3 SEC DROP SERV VER/KEP L3/KEP
13703 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-03-12 12:41 | 2014-03-12 18:50 | 1 | 369 | 4471081 | 369 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RELEASED BY CREW 077S03--CUST HAS PART POWER CHECKED WITH VOLT MTR, NEED SERVICER TO CHECK THIS-077M01-BK RELEASED BY CREW 077M01 HAD RED/RED SERVE END BAD ON POLE 342-193 ONLY 1 CUST. WITH PART POWER VER/HFP L3/HFP
13704 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-02-05 02:41 | 2019-02-05 08:50 | 1 | 369 | 4754491 | 369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER REPLACING BROKEN CUTOUT ¦¦¦ COD-1 38830405000175bad cutout on p# 405-175 made repairs all pwr restored @ 8:50 please close ticket LRM
13705 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-06-22 06:15 | 2009-06-22 12:24 | 1 | 369 | 57606-1 | 369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP XFMR FUSE APPEARS BLOWN ,XFMR IS BACK ON HILL---CUTOUT BAD WILL HAVE TO CLIMB AND CHANGE-----CHANGED BAD CUTOUT L3/HFP IDC XXXX
13706 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2017-12-05 06:03 | 2017-12-05 07:35 | 4 | 184 | 4621391 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 796-176///repairs made//restored at 7:35//complete//em
13707 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-02-09 17:50 | 2022-02-09 20:54 | 2 | 184 | 4463071 | 368 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad conn. on transformer
13708 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-02-24 07:22 | 2011-02-24 13:30 | 1 | 368 | 60609-1 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | LINE FUSE IS OUT ON UNDERGROUND PRIMARY AT POLE 144-338. I AM GOING TO REFUSE LINE FUSE. FUSE CAME BACK OUT. I AM GOING TO CHECK THE TRANSFORMER. POTHEAD IN TRANSFORMER IS BAD. DALE HAMILTON AND CREW IS GOING TO CHANGE IT. WE CHANGED POTHEAD AND MADE TRANS HOT AT 13:30//MADE A MD//VER/CRB IDCC PN524, CDC83, FP338, CCO XXXX
13709 | Pikeville | 3408103 | SALISBURY | MARTIN | 2017-05-25 22:32 | 2017-05-26 04:40 | 1 | 368 | 4863901 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED, TAGGED FOR G. JUSTICE AND GROUNDED AT POLE 38831098D00620,. REPLACED CUTOUT AN ARRESTER AND ADDED CROSSARM TO PLOLE FOR SUPPORT , ALL WORK COMPLETE / GXJ VER/ARN
13710 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-12-31 13:44 | 2017-12-31 16:48 | 2 | 184 | 4690251 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, calling for big bucket and one man, will need flaggers
13711 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-10-02 03:03 | 2010-10-02 04:35 | 4 | 92 | 56167-1 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830182B43588, REPLACED CUTOUT //VER/GAH IDC XXXX
13712 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-09-01 21:29 | 2011-09-01 22:15 | 8 | 46 | 4783141 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DONT SEE FUSE OUT ON GATE, GOING UP IN BUCKET TO SEE WHATS WRONG FUSE BROKE IN TWO VER/KEP IDC XXXX
13713 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2012-08-16 20:23 | 2012-08-16 21:55 | 4 | 92 | 4945261 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 4 IDC XXXX
13714 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-10-14 16:51 | 2012-10-14 19:55 | 2 | 184 | 4139371 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRIMARY NEUTRAL AND 1 HOT OPEN WIRE SECONDARY HAS BURNT DOWN, CUTOUT ON XFMR HAS ALSO BURNT UP, CALLING FOR HELP // MULLINS & SHOUSE ****CREW OPENED SWS AT POLE 130-135 TO MAKE REPAIR..PRIMARY NEUTRAL AND 1 HOT OPEN WIRE SECONDARY HAS BURNT DOWN, CUTOUT ON XFMR HAS ALSO BURNT UP, CALLING FOR HELP, OPENED MAIN LINE TO MAKE REPAIRS. ALL POWER RESTORED VER/HFP L3/HFP IDCC CCO, TOF1425, CNT73 XXXX
13715 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-11-29 16:41 | 2019-11-29 19:45 | 2 | 184 | 4103551 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva xfmr on 850-297, took xfmr off line and made up customers off open sec on pole fed from xfmr on p 850-97.we can chg xfmr at later date. only 2 customers on outage
13716 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-06-27 11:04 | 2012-06-27 17:12 | 1 | 368 | 4967521 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGED 4/3 SERVICE TO 2/3, REMADE ALL CONNECTIONS AT HOUSE AND POLE, BAD TRANSFORMER, NEED 15KVA, 7200, 3 MEN AND BUCKET TRUCK. RELEASED BY CREW 077S04//CUTOUT AND ARRESTER NEEDED REPLACED TRANSFORMER AND RESTORED POWER VOLTAGE CHECKED GOOD JKC //VER/CRB L/3 CRB
13717 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-11-06 11:58 | 2015-11-06 15:02 | 2 | 184 | 4415331 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BESIDE OF ROAD , IHAVE FLAGGERS COMMING// VER/ ADH
13718 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-12-22 03:40 | 2013-12-22 05:12 | 4 | 92 | 4185921 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 374-57, MADE REPAIRS RESTORED POWER AT 05:12 VER/KEP L3/HFP
13719 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-02-09 10:52 | 2015-02-09 17:00 | 1 | 368 | 4002391 | 368 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | LOW VOLTAGE 1 LEG UG, NEIGHBOR GOOD VOLTAGE. RELEASED BY CREW 078S07.INSTALLED POWER TEMP, WILL MAKE PERMANENT REPAIRS ON TUESDAY..BLR// VER/ ADH L3/HFP HFPC MCCDL
13720 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-10-21 19:55 | 2016-10-22 02:03 | 1 | 368 | 4041591 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1146-348 ON FIRE OPENED HOT TAP 19;55 PM POLE 1146-146 MAYBE SMALL TRUCK RELEASED BY CREW 078S08/CREW ON SITE/FETR 0330/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST0203/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP L3/HFP HFPC LCD39831146D00348
13721 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-02-03 15:47 | 2022-02-03 17:19 | 4 | 92 | 4429341 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole37830225B00031
13722 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-08-30 13:09 | 2012-08-30 13:55 | 8 | 46 | 4986391 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 44-4185 8T TRANS FUSE BROKE REFUSED VER/KEP IDC XXXX
13723 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-05-31 07:55 | 2009-05-31 14:03 | 1 | 368 | 53026-1 | 368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POSSIBLE BAD XFMR BAD 25KVA 19.9//COD 1// VER/DBM IDC XXXX
13724 | Hazard | 3303901 | LESLIE | HYDEN | 2009-06-01 00:13 | 2009-06-01 06:20 | 1 | 367 | 55343-1 | 367 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303901/// BAD XFMR VER/JHM IDCC PN42 XXXX
13725 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-06-20 11:23 | 2014-06-20 17:30 | 1 | 367 | 4121791 | 367 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSF 10 KVA 7200 ==== NEED 15 KVA 7200 === MANUAL UP ON HILLSIDE ==== NEED LINE CREW === LARRY LAWSON CREW IS GOING TO CHANGE TRANST RELEASED BY CREW 077S03 VER/CRB
13726 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-09-21 07:58 | 2009-09-21 14:05 | 1 | 367 | 56184-1 | 367 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED POLE CUTOFF REQUIRED NO CHANGEOUT NEED TRACK BUCKET 1 CUSTOMER OUT RELEASED BY CREW 078S03//COD 1// VER/DBM IDCC PN179 XXXX
13727 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-12-29 18:21 | 2014-12-30 00:28 | 1 | 367 | 4890641 | 367 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9, 25KVA TXMF NO TRUCKS SIX WHEELER & MANUAL TREECREW REQUIRED RELEASED BY CREW 078S11--CHANGED 25KVA XFMR AND SERV DROP---CK VOLT 125-125-250----TBL TKT COMP VER/ARN
13728 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2014-08-06 08:06 | 2014-08-06 14:12 | 1 | 366 | 4335321 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY LEAD BURNT INTO MADE REPAIRS RESTORED POWER AT 14:12// ISO 37830352C00034// COD 1 CCC*******************
13729 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-12-12 12:54 | 2010-12-12 19:00 | 1 | 366 | 65631-1 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38077829 //RELATED TO ORDER 65596-1// CREATED THIS ORDER FOR REPAIR CREW @ THEIR REQUEST & ADJUSTED TIME OFF TO 1254 OF ORIGINAL ORDER VER/HFP L3/HFP IDC XXXX
13730 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-08-06 16:09 | 2010-08-06 22:15 | 1 | 366 | 50682-1 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 12KV TRANSFORMER C/O BURNED UP. TRUCK ACCESSIBLE.. BJ RELEASED BY CREW 074E04, 25KVA TRANSFORMER BURNED UP NEED CREW WITH MATERIAL HANDLER BUCKET M.D.I. VER/HFP L3/HFP
13731 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-09-27 09:10 | 2010-09-27 11:12 | 3 | 122 | 54056-1 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE, REPLACE BAD CUTOUT//COD 3// VER/DBM IDC XXXX
13732 | Whitesburg | 3401301 | FLEMING | NEON | 2014-06-14 11:39 | 2014-06-14 17:45 | 1 | 366 | 4091031 | 366 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CENTER PHASE TRANS. BAD ON A 50 KVA 7200 120/208 BANK. WILL NEED NEW TRANS. AND 85 FT. OF 4/0 QUADRAPLEX, CUSTOMER SAID IT WAS FINE TO DO MONDAY MORNING, OPS. ORDER # 039896156. NO ONE USING THIS BUILDING AT THIS TIME. //// COD-1 ISO TF 37830355D30327 VER/HFP L3/HFP
13733 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-04-24 14:32 | 2011-04-24 17:35 | 2 | 183 | 63699-1 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUT OUT ON 477-177 WAITING ON FLAGGING CREW;; REPLACED CUTOUT ALL POWER RESTORED AT 1735 CLOSE TICKET IDC XXXX
13734 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2018-02-14 13:48 | 2018-02-14 15:50 | 3 | 122 | 4840651 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 30t line fuse out on pole 1145-c-8 due to bad arrester on pole 1145-c-144. cleared arrester up closed in 30t t fuse everything ok. i will also get order to replace arrester 1550
13735 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-05-15 12:48 | 2020-05-15 14:50 | 3 | 122 | 4838851 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutral on customers transformer pole burnt up.. pole number 421-93. need to open transformer long enough to make repairs. open @ 13:20 closed @ 14:50
13736 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-10-04 08:09 | 2017-10-04 09:10 | 6 | 61 | 4408601 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKE. RESTORED @ 9:10. SH 38830882D00155 VER/AWD L3/HFP XXXHFP
13737 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-05-27 10:09 | 2018-05-27 11:10 | 6 | 61 | 4503771 | 366 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | a tention splice on the neutral in the service pulled apart. I replaced it
13738 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-06-13 00:09 | 2011-06-13 03:12 | 2 | 183 | 4307921 | 366 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 4/0 COPPER LEAD,BURNT OFF,LOOKS LIKE 4/0 ALU 3 PHASE SERVICE-BIG BUCKET,NEW LEAD,,WILL HAVE TO OPEN REST OF BANK,SERVES LARGE COOLERS FULL-- $$$$$----JIM //VER/GAH IDC XXXX
13739 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2013-03-10 15:48 | 2013-03-10 17:50 | 3 | 122 | 4895371 | 366 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 079S02 REPLACED BAD CONNECTION AT TRANSFORMER POLE. COD-3 ISO SO 38820941D00292 VER/HFP L3/HFP IDC XXXX
13740 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2012-07-30 09:49 | 2012-07-30 15:55 | 1 | 366 | 4864371 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | <<ONLY ONE CUSTOMER AFFECTED>> ONE HOT CONDUCTOR BURNT OPEN IN SECONDARY. REPLACED 4/3 SERVICE WITH 2/3 AND RE-WORKED SECONDARY CONNECTIONS. RESTORED @ 15:55. SH//COD 1// VER/DBM
13741 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-01-14 10:42 | 2018-01-14 13:45 | 2 | 183 | 4746371 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | span of open wire burnt down between pole 142-154 and midspan tap #4 copper will need some to splice with by truck Released by crew 078H01,repairs made all cust restored please close ticket thanks.bt
13742 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-12-31 14:43 | 2015-12-31 17:46 | 2 | 183 | 4578881 | 366 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON WEATHERHEAD// VER/ ADH
13743 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2013-10-20 08:14 | 2013-10-20 09:15 | 6 | 61 | 4949181 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP, I CHANGED IT OUT//COD 6// VER/DBM
13744 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-07-13 16:49 | 2008-07-13 18:51 | 3 | 122 | 51969-1 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3404302, ON SITE, LINE FUSE OUT ON POLE#1012-24, REFUSING IT//VER/CRB IDC XXXX
13745 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-03-08 10:34 | 2018-03-08 12:36 | 3 | 122 | 4978551 | 366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | replaced the transformer fuse that had broke. Power is restored. cod 3 iso 38820989B00272
13746 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-11-26 11:45 | 2010-11-26 17:50 | 1 | 365 | 59839-1 | 365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1130-316 BURNED OFF,ISOLATED AT 1130-225.WILL CALL FOR CREW AND MATERIALS.HOLD TICKET FOR CREW RELEASED BY CREW 074S06 RELEASED BY CREW 074H02POLE 1130-316 BURNED OFF,ISOLATED AT 1130-225.WILL CALL FOR CREW AND MATERIALS.HOLD TICKET FOR CREW RELEASED BY CREW 074S06 REPAIRS MADE ON AT 17:50//VER/CRB IDC DCMT, CHANGED TIME OFF FROM 1045 ESTIMATED XXXX
13747 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2011-09-20 09:02 | 2011-09-20 10:15 | 5 | 73 | 4887541 | 365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | <<AFFECTS ONE CUSTOMER ONLY>> XFMR CUTOUT BROKE ON BANK POLE 38830954B40620.//ISO //COD 1// REPLACED CUTOUT AND RESTORED @ 10:15. SH IDCC PN93 XXXX
13748 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2022-11-05 20:52 | 2022-11-06 02:57 | 1 | 365 | 4104531 | 365 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | (TIME MODIFIED BY DST CHANGE) (TIME MODIFIED BY DST CHANGE)Connection burnt into going to power supply///Replaced bad connection and restored service @ 02:57
13749 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-08-19 22:27 | 2015-08-19 23:40 | 5 | 73 | 4155301 | 365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV DOOR/ ISO 38830045B33090/ COD 5/ VER/BOW
13750 | South Williamson | 3200302 | BELFRY | TOLER | 2008-07-07 14:15 | 2008-07-07 20:20 | 1 | 365 | 63792-1 | 365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3200302//, ON SITE, CHECKING TROUBLE, HAVING TO REPLACE UNDERGROUND SERVICE, SERVICE BURNT UP// 1 COD// // VER/TOM IDC XXXX
13751 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-02-22 08:35 | 2022-02-22 14:40 | 1 | 365 | 4527811 | 365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva 7200 -- bt --crew req-ds022222 Released by crew 078S01 Repairs made closed at 14:40. Ticket complete
13752 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-04-20 16:15 | 2021-04-20 22:20 | 1 | 365 | 4465691 | 365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 2.8 miles out bolts fork to arnett ln--bad 5kva per fieldview--nbt--feeding pump and electric fence--gate dummy locked and cows behind gate--can get sxs to pole (through gate past house,past black shed right up hill keep right around to pole)--crew req-(call duane co radio 7019 for more info)-ds042021 Released by crew 078S01 crewon site FETR23:00
13753 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2009-06-03 09:00 | 2009-06-03 09:52 | 7 | 52 | H62821-1 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED, R MARCUM KNOWS WHAT HE NEEDS, WILL WORK TOMORROW RELEASED BY CREW 080S01. A&B PHASE IS OPEN. WE WILL OPEN C PHASE TO MAKE REPAIRS. IDC XXXX
13754 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-04-15 07:30 | 2014-04-15 07:37 | 52 | 7 | H4605201 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | FOUND HOT TAP ON SOURCE SIDE OF RECLOSER WAS BAD, REPLACED AND ALL CUST RESTORED AT THIS TIME OF 0730 AT THIS LOC VER/KEP IDC APPEARS THAT WE OPENED PH A TO MAKE REPAIRS XXXX
13755 | Whitesburg | 3314401 | MAYKING | ERMINE | 2021-04-08 13:23 | 2021-04-08 14:54 | 4 | 91 | 4431041 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loose neutral connection in padmount transformer 449-D3-1576.. opened primary fuse on pole 449-D3-1575 to make repairs safely. open @ 14:15 closed back @ 14:45 tightened all connections in padmount..
13756 | Whitesburg | 3312902 | JENKINS | JENKINS | 2011-06-20 13:46 | 2011-06-20 19:50 | 1 | 364 | 4354061 | 364 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFMR SECONDARY LEAD TO SERVICE DROP CONNECTION IS BURNED UP , I CALLED FOR CREW WITH BIG BUCKET AND NEW SECONDARY LEAD AND CONNECTOR IDC XXXX
13757 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-09-27 09:54 | 2015-09-27 11:25 | 4 | 91 | 4277901 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMIT FUSE , REMOVED FUSE RESTORED POWER AT 11:25 COD-4 ISO TF 3783035100256 VER/HFP L3/HFP
13758 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-06-04 09:49 | 2015-06-04 09:56 | 52 | 7 | H4509261 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE IS NOT BLOWN ON POLE 38820989A00139, THE A PHASE IS OUT BACK TOWARDS THE RECLOSER ON POLE 38820964B00153, PATROLLING THE LINE. BAD PIN INSULATOR ON POLE 38820989A00131. I WILL NEED TO OPEN THE OTHER TWO PHASES TO REPLACE IT. SWITCHES OPENED ON POLE 38820964C00099 AND TAGGED FOR MATNEY. RECLOSER ON POLE 38820964B00153 OPENED AT 09:49 AND CLOSED BACK IN AT 09:56.RESTORED FINAL CUSTOMERS AT 1114/ L3/DKG SEE 4509261 FOR ORIGINAL OUTAGE AJB
13759 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2018-11-14 22:57 | 2018-11-15 00:28 | 4 | 91 | 4400051 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse blown on pole 123-34 will patroll/// Bad cutout on pole# 123-120///will make repairs/// Changed bad cutout and refused line fuse @ 00:28 and restored service L3/HFP
13760 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-04-29 06:23 | 2013-04-29 09:25 | 2 | 182 | 4055171 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP HAD COME OFF MAIN LINE, MADE REPAIRS//COD 2// VER/DBM IDC XXXX
13761 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-08-11 16:07 | 2012-08-11 16:33 | 14 | 26 | 4928661 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FUSE BLEW WHEN TRYING TO RESTORE ORDER 4927181 // VER/HFP L3/HFP IDC XXXX
13762 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-06-29 08:36 | 2008-06-29 10:07 | 4 | 91 | 59134-1 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOT TAP BROKEN OUT OF TOP OF CUTOUT ON 3 PHASE POLE// NEED BIG BUCKET TO REPLACE CUTOUT/NO WIRE DOWN/ LOCATED AT FAIRVIEW HIGH SCHOOL BUS PARKING LOT/ SEND TO MIKE PHELPS RELEASED BY CREW 078S07 BACK ON AT 1007 VER/ARN IDCC PN XXXX
13763 | Hazard | 3303902 | LESLIE | WOOTON | 2021-06-11 15:26 | 2021-06-11 21:30 | 1 | 364 | 4716501 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 341-121, need big bucket 19.9 cutout t bracket arrester Released by crew 077S07. Power restored at 21:30
13764 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-09-02 13:31 | 2015-09-02 19:35 | 1 | 364 | 4191621 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEND TO OLLIE ADKINS/BURNT SERVICE AT SHREDDER RELEASED BY CREW 078S03 REPAIRED DAMAGE CONDUCTORS AND CHECKED ROTATION AND VOLTAGE CUSTOMER IS BACK IN OPERATION// VER/ ADH
13765 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-11-05 11:43 | 2018-11-05 17:47 | 1 | 364 | 4364431 | 364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 75 KVA Released by crew 078H04--crew on site--changing 1-75kva in a Wye Bank---changed out 75kva---also found load side of LF cutout on 38830020D47584 open--made repairs---volt ck good on new xfmr--changed neutral buss risers---closed xfmr bank 20-7729 @ 17:47---tbl tkt comp---rmv L3/HFP
13766 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-01-16 06:27 | 2009-01-16 12:30 | 1 | 363 | 55527-1 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308503// XFMR BAD NEED TO REPLACE WITH A 25 KVA 7200 TRUCK ACESSIBLE RELEASED BY CREW 077S04 REPLACED XFMR P HICKMAN T SMITH COD-1 VER/KEP L3/KEP
13767 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-09-04 14:59 | 2009-09-04 17:00 | 3 | 121 | 65780-1 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR BLOWN IN CLEAR REPLACED 6-T FUSE GIVE COPY OF TICKET TO LLOYD RAYBURN TO REPLACED ARRESTOR TRUCK TO POLE//MD FILED ON MISSMAPPED CUST PREMISE//COD 3//ISO 38830206A22120// VER/DBM IDC XXXX
13768 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2021-05-06 12:49 | 2021-05-06 14:50 | 3 | 121 | 4544791 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Xfmr riser connection failed. Replaced connections and restored @ 14:50. sh
13769 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-03-03 10:32 | 2018-03-03 16:35 | 1 | 363 | 4950711 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED 349-41 BROKE xfr cutout no trucks Released by crew 078S05/on site RM power on at 16:35 please close tic RM
13770 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-06-10 08:07 | 2015-06-10 14:10 | 1 | 363 | 4548211 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CREW BAD 12KV C/O. CORNER OF LONG %26 HALLS CT. 1147 C4 5584 RELEASED BY CREW 078S07/ ISO 39831147C45584/ COD 1// CREW SHOULD ARRIVE SOON, TRUCK TROUBLE//LMR. CUTOUT TYPE WAS ABB, CRACKED AT THE MOUNTING BRACKET. RELEASED BY CREW 078Q12 VER/ARN
13771 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-12-27 13:40 | 2009-12-27 15:41 | 3 | 121 | 56190-1 | 363 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED CONNECTOR ON SERVICE AT XFMR 122709 SC CLOSE TICKET MWL
13772 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-06-18 16:27 | 2015-06-18 22:30 | 1 | 363 | H4597231 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ** SEE 4597231** VEHICLE ACCIDENT WIRE DOWN/POLE 116-738 REMOVED 80FT. 4/0 4 CONDUCTOR WIRE SERVICE AT 8136 US 60/ ALSO SERVICE OFF 8136 AND 8140 US 60 CUST TO CALL FRIDAY IF REPAIRES MADE/ LINE GREW NEEDS TO COME FIX BAD 19.9 CUTOUT POLE 116-815 TONIGHT/ TRUCK TO POLE OPENED OTHER DOORS ON CUTOUTS/ DUPLICATE IN HOIS/ BAD CUTOUT : ISO 38830116A00815 COD 1/ VEHICLE ACCIDENT: ISO 38830116A00738/ COD 2/ VER/BOW
13773 | Hazard | 3310502 | HADDIX | CANOE | 2015-06-28 14:42 | 2015-06-28 20:45 | 1 | 363 | 4687581 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR . NEED 1 MAN & BUCKET TRUCK . 50KVAXFMR &CUTOUT & FIBERGLASS TBRACKET . 19.9 VOLTS . CLOSED XFMR @ 20:45/ ISO 37830075000148/ COD 1/ VER/BOW
13774 | Hazard | 3309003 | JEFF | VIPER | 2022-07-23 14:57 | 2022-07-23 21:00 | 1 | 363 | 4556221 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout.manual need 7.2 kv cutout /bracket. Released by crew 077H18
13775 | Pikeville | 3407103 | TOPMOST | KITE | 2022-06-14 20:29 | 2022-06-14 22:30 | 3 | 121 | 4118321 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfm fuse blown.//Restored @ 22:30
13776 | Pikeville | 3403001 | PIKEVILLE | CITY | 2022-05-04 07:38 | 2022-05-04 09:39 | 3 | 121 | 4834441 | 363 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a broke Neutral in secondary coming off pole 48-C3-17,will be making repairs..Restored at 09:39..
13777 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-01-30 18:54 | 2020-01-30 20:55 | 3 | 121 | 4350271 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Bad spot in secondary has caused wire to burn down on pole 832-130. I will be making repairs. Repaired conductor and restored power at 20:55
13778 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-09-06 15:39 | 2013-09-06 21:42 | 1 | 363 | 4825981 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON POLE # 38831084A00309 GOT CONNECTIONS ON TRANSFORMER HOT. GOING TO OPEN BANK AND FIX IT OPEN TRANSFORMERBANK AT 2110 AND CLOSED AT 2142 RELEASED BY CREW 077S05 ****CHANGE ISO POLE*** VER/SEF IDCC TOF2110 XXXX
13779 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-03-14 14:34 | 2009-03-14 16:35 | 3 | 121 | 58512-1 | 363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309103// CUTOUT IS BROKEN ON POLE 472-148. CECIL SEXTON IS ENROUTE TO HELP ME ON THIS // COD 3 // VER/TOM L3/TOM IDC XXXX
13780 | South Williamson | 3411401 | DEWEY | INEZ | 2011-07-13 09:18 | 2011-07-13 15:20 | 1 | 362 | 4539861 | 362 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE SECONDARY LEG BURNED ALMOST INTO AT CONNECTION//REPAIRS MADE//COMPLETE//EM VER/HFP L3/HFP IDC XXXX
13781 | Pikeville | 3407103 | TOPMOST | KITE | 2013-10-03 12:26 | 2013-10-03 15:27 | 2 | 181 | 4907721 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED TRANSFORMER CUTOUT , ALL WORK COMPLETE / GXJ//COD 2 VER/HFP L3/HFP IDC XXXX
13782 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-01-25 12:44 | 2008-01-25 15:45 | 2 | 181 | 59862-1 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400301//X FMR BAD RELEASED BY CREW 074S04//VER/CRB IDC XXXX
13783 | Hazard | 3303901 | LESLIE | HYDEN | 2020-04-18 08:39 | 2020-04-18 11:40 | 2 | 181 | 4716231 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LRS - TRUCK 1907 - 4/18/2020 11:00 ; CUTOUT IN @ 37830339000039, NEEDS ROLLED TO LARGER TICKET; CUTOUT BROKE @ 37830339000038 - REPLACE CUTOUT, NO DOWN WIRE Released by crew 055E01
13784 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-05-28 07:59 | 2018-05-28 11:00 | 2 | 181 | 4508141 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o
13785 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-03-26 17:47 | 2012-03-26 20:48 | 2 | 181 | 4619901 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE COD-2 ISO TF 37820027000004 VER/HFP L3/HFP IDC XXXX
13786 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-04-03 10:43 | 2016-04-03 16:45 | 1 | 362 | 4041811 | 362 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN SERVICE DROP BROKE , DIDNT SEE ANYTHING CAUSED IT TO BREAK, MADE REPAIRS RESTORED POWER AT 16:45.ONLY ONE CUSTOMER AFFECTED.. VER/CRB
13787 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-05-31 19:48 | 2010-06-01 01:50 | 1 | 362 | 54495-1 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 116-316 BAD 25KVA BAD LA POLE LOOKS ROTTEN NO TRUCKS MAYBE TRACK REAL WET RELEASED BY CREW 078S08REPLACED CUT OUT & XFORMER POWER ON AT 13:50 IDC XXXX
13788 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-08-29 19:02 | 2022-08-30 01:04 | 1 | 362 | 4810141 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required///// bad xformer at pole 67-423///// crew will need a 25 kva xformer 7200///// will be a manual pole no truck.. Released by crew 074S03. Repairs made. Restored at 01:04.
13789 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-01-02 08:59 | 2011-01-02 12:00 | 2 | 181 | 57918-1 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38259533 // CUTOUT BAD ON POLE 379-145 LINE FUSE OPEN ON 379-144 NEED 1 MAN AN BIG BUCKET POWER ON AT 1200 COD-2 ISO LF 37830379D00144 VER/HFP L3/HFP IDC XXXX
13790 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-06-17 11:09 | 2011-06-17 14:10 | 2 | 181 | 4333541 | 362 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER. COD-2 ISO SO 37830286000214 VER/HFP L3/HFP
13791 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-11-17 06:43 | 2014-11-17 12:45 | 1 | 362 | 4733771 | 362 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL WORK DURING NORMAL WORK HOURS. POSSIBLE BAD CONNECTION IN UNDERGROUND PEDESTAL, J COMBS AND CREW ENROUTE TO HELP.//ONLY 1 CUSTOMER OUT// OPENED TRANSFORMER AT 11:00 RELEASED BY CREW 077S04 DUP IN HOIS FOR 5 CUST WHEN TR OPENED // COD-6 ISO TF 37830248A00626 SEE H4733771 FOR TR OUTAGE // VER/HFP L3/HFP
13792 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2022-08-04 12:38 | 2022-08-04 18:40 | 1 | 362 | 4674151 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad xfmr 15kva no truck access//restored at 18:40
13793 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2017-01-13 13:38 | 2017-01-13 16:39 | 2 | 181 | 4295191 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN DOWN CUTOUT HAS BURNED POLE ABT HALFWAY INTO,NEED CREW,2XARMS,7.2 CUTOUTS,LAS,INSULATED BRACKETS FOR CUTOUTS/////POLE APPEARS 2B 966-628////TIMMCCOY ENROUTE/ ISO 38820966B00628/ COD 2 MD DONE/ GREG BOWEN APCO LOGGED ON 1:38PM AND OPENED TRANSFORMER BACK ON 1639/ VER/BOW
13794 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-02-05 23:09 | 2011-02-06 02:10 | 2 | 181 | 54759-1 | 362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN---BAD 50 KVA TRANSFORMER. // VER/TOM IDC XXXX
13795 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-02-20 16:09 | 2014-02-20 22:10 | 1 | 361 | 4406781 | 361 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 078S04 NOTHING FOUND REFUSED OLD FUSE APR AT 2210 CLOSE TICKET. DEW //VER/GAH
13796 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-01-09 09:29 | 2011-01-09 15:30 | 1 | 361 | 60088-1 | 361 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BLOWN 6T FUSE,, NEED A 25KVA TO REPLACE A 10KVA HAS #2 RISERS IN TRANS,, CUST TO MOVE STOCK TRAILER FOR ACESS TO POLE BY TRUCK,, 3 MEN REQUIRED RELEASED BY CREW 078H08 //VER/GAH IDC XXXX
13797 | South Williamson | 3411401 | DEWEY | INEZ | 2009-03-22 10:14 | 2009-03-22 16:15 | 1 | 361 | 60660-1 | 361 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411401//SUSPECT THIS IS A BAD TRANSFORMER//CALLING DUTY SUPERVISOR//.CREW ON THERE WAY WITH XFMER AND 6WHEELER *** UPDATE AT 1545 - SERV REST OUTAGE BY ACCIDENT. OUTAGE TIME IS FROM 1014 UNTIL WORK IS COMPLETE.//COD 1// VER/DBM IDC XXXX
13798 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-09-06 09:59 | 2013-09-06 16:00 | 1 | 361 | 4824901 | 361 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE TOP BUSTED OUT,NEED 30/6 POLE 3 CLEVISES AND SPOOLS GUY ATTACH AND WIRE, AND 6A WIRE FOR SPLICING, VOLTAGE AT METER 246 PHASE TO NEUT WHEN ARRIVED, OPENED TRANS FUSE ON HILL, AND PULLED METER, MAY LOWER ON POLE BUT WILL NEED SOME MINOR RIGHT-AWAY CLEARING RELEASED BY CREW 078H08,,,CREW ON SITE,LOWERED WIRE ON POLE, VOLTAGE 120-120-245, ALL POWER RESTORED//COD 1// VER/DBM
13799 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-09-24 23:47 | 2011-09-25 01:17 | 4 | 90 | H4912701 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG SEND TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE/VEM/ORIGINAL CALL 4 CUST PART POWER/OPEN XFMR 1148-650 AT 2347 TO ISOLATE BAD UG/XFMR BACK IN AT 0019/ 4 CUST OUT FOR REPAIRS/REPAIRS MADE AND POWER RESTORED TO 4 CUST AT 0117/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
13800 | Pikeville | 3410602 | E.PRESTON | LANCER | 2010-12-20 04:10 | 2010-12-20 05:10 | 6 | 60 | 54417-1 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | NEED TO REPAIR BAD CONNECTION //VER/GAH IDC CHANGED TIME OFF FROM 0254 CUSTOMER HAD BRIGHT DIM XXXX
13801 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-08-20 20:10 | 2011-08-20 21:10 | 6 | 60 | 4734361 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TR @ 2010, BAD CONN ON POLE, RESTORED AT 2110. CC = 6. IDC XXXX
13802 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-04-12 06:04 | 2014-04-12 12:04 | 1 | 360 | 4597531 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUT-OUT ON POLE 516-37. GOING TO CHANGE CUT-OUT. POWER RESTORED AT 12:04. J.S.B. COD-1 ISO TF 37830516A40037 VER/HFP L3/HFP
13803 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-06-21 20:15 | 2015-06-21 22:15 | 3 | 120 | 4634341 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | LINE FUSE DID NOT DROP OUT FROM EARLIER CASE OF TROUBLE , POWER FEEDING THROUGH OTHER XFMR BANKS. I REFUSED LINE FUSE ON POLE 448-69//COD 3//A PHASE ONLY// VER/DBM
13804 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2015-05-23 17:30 | 2015-05-23 18:42 | 5 | 72 | 4459551 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830254A00163 LINE FUSE BROKEN NO CREW REQUIRED VER/CRB
13805 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-02-27 09:50 | 2020-02-27 10:50 | 6 | 60 | 4436151 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse on pole 220-16 broke. restored power at 10:50 L3/HFP
13806 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2021-09-13 10:14 | 2021-09-13 11:44 | 4 | 90 | 4235291 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Padmount trans. fuse open @24-B2-1081, checking. Fuse had melted, refused @1144.
13807 | Pikeville | 3413402 | GARRETT | LACKEY | 2012-08-24 08:35 | 2012-08-24 10:35 | 3 | 120 | 4967821 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER PER GREG JUSTICE//OPENED UP @ 0835// . REPLACED TRANSFORMER, ALL WORK COMPLETE / GXJ//COD 3// VER/DBM IDC XXXX
13808 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-09-15 09:21 | 2014-09-15 12:21 | 2 | 180 | 4499701 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SERVICER REPAIRING B PHASE ON URD SERVICE// WILL REPLACE BAD U.G. TO MAKE REPAIRS FOR THE CUSTOMER. // FOUND FAULT AND MADE REPAIRS AND RESTORED SERVICE AT 12:21 TIM MCCOY RELEASED BY CREW 074H10// COD 2// VER/ ADH
13809 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-02-15 10:05 | 2009-02-15 11:35 | 4 | 90 | 61970-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BROKE//3202201//VER/CRB
13810 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-03-15 03:43 | 2010-03-15 03:55 | 30 | 12 | 50063-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AT 0350 SERVICER OPEND " C" PHASE FUSE TO MAKE REPAIRS TO FAILED CUTOUT ON ORDER 50057-1 32 CC FROM 0350-0358 IDCC CNT41 TOF0350, FP130 XXXX
13811 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-01-08 08:00 | 2015-01-08 10:00 | 3 | 120 | 4918431 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | LEAD BURNT OFF BUSHING, OPENING TRANSFORMER 239-6/COD3/SECONDARY RISER IN TRANSFORMER HAD BURNED INTO. I AM GOINGTO REPLACE RISER.SECONDARY RISER IN TRANSFORMER HAD BURNED INTO. I AM GOINGTO REPLACE RISER. I OPENED TRANS. ON POLE 37830239000006 AT 09:30 AND CLOSED IT BACK IN AT 10:00// COD 3// VER/ ADH
13812 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-03-17 09:32 | 2014-03-17 15:32 | 1 | 360 | 4500991 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE BAD IN SERV REPAIRED === POWER OK VER/SEF
13813 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-12-12 10:30 | 2009-12-12 12:30 | 3 | 120 | H60310-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 1/0 SECONDARY CONDUCTOR GOT HOT AT A SPLICE IN MID SPAN AND SHORTED OUT AND THEN BURNED INTO IN 3 PLACES. I CALLED DALE AND HE IS SENDING CREW TO REPLACE SEC. COND. WE JUST HAVE 3 CUSTOMERS OUT RIGHT NOW. WHEN CREW GETS HERE WE WILL HAVE TO OPEN TRANS. AND THIS WILL HAVE 2 MORE CUSTOMERS OUT. I HAVE INFORMED THEM THEY WOULD BE OUT FOR ABOUT AN HOUR AND A HALF. I CAUGHT WIRE WITH BOOM OF MY TRUCK AND JERKED PHONE AND TV CABLE OFF CUSTOMERS HOUSE. IT TORE CORNER MOLDING O VER/KEP L3/KEP
13814 | Whitesburg | 3312902 | JENKINS | JENKINS | 2019-06-27 18:20 | 2019-06-28 00:20 | 1 | 360 | 4608521 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kv xfmr 7200, restored power at 00:20
13815 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2013-05-17 08:08 | 2013-05-17 10:08 | 3 | 120 | 4125691 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE A FUSE BLOWN AT POLE #38821065D20162. BAD CUTOUT ON POLE 1065-D2-308. WILL REPLACE CUTOUT AND CLOSE FUSE BACK IN.// COD 3 VER/SEF IDC XXXX
13816 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-06-28 22:31 | 2010-06-28 23:11 | 9 | 40 | 60042-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 9// VER/DBM
13817 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2014-03-02 16:25 | 2014-03-02 17:10 | 8 | 45 | 4444331 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE OUT ON BANK OF TRANS, B PH FUSE OUT BROKEN FUSE LINK POWER RESTORED KWB. VER/CRB IDC XXXX
13818 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-06-19 18:20 | 2009-06-19 21:20 | 2 | 180 | 58926-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 30382258 // SEND TO LYNCH-BAD 15KVA NEED 25 KVA--12KV--MATERIAL HANDLER OK RELEASED BY CREW 078S07 //VER/GAH IDC XXXX
13819 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-07-05 14:20 | 2016-07-05 17:20 | 2 | 180 | 4540421 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED
13820 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2008-06-01 16:55 | 2008-06-01 18:55 | 3 | 120 | 53931-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200204//, ON SITE, BAD CUTOUT, R MARCUM COMING TO HELP, 3 CUST OUT//COD 3// VER/DBM IDC XXXX
13821 | South Williamson | 3200301 | BELFRY | BELFRY | 2012-10-02 07:33 | 2012-10-02 08:45 | 5 | 72 | 4106271 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT UP XFMR CUTOUT...WILL REPLACE..//..REPLACED CUTOUT & OLD ARRESTER..JRV & RST ...10/02/12//COD 5// VER/DBM IDC XXXX
13822 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-06-10 09:40 | 2018-06-10 11:10 | 4 | 90 | 4575911 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Side tap cutout on pole 38820941B00414 that feeds towards to pole 38820941B00418 had broke, and the transformer fuse was also under it.//MADE MD//COD 4
13823 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-11-18 21:20 | 2011-11-18 21:40 | 18 | 20 | 4091641 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CREW REQUIRED-NEED 3 MAN CREW-BUCKET TRUCK TO POLE-BAD HOT TAP ON LINE FUSE NEEDS REPLACED RELEASED BY CREW 078S07---- POWER OFF @ 21:20 --- ON @ 21:40 REPLACED HOT TAP VER/ARN IDCC MCCNI XXXX
13824 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-02-19 16:15 | 2014-02-19 17:45 | 4 | 90 | 4402531 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 98-258 HAS ROTTED AND ABOUT TO FALL. WE ARE GOING TO CHANGE POLE. WE WILL HAVE TO OPEN TRANS. ON POLE 98-45 WHEN WE GET READY TO TRANSFER SEC. CONDUCTORS. I WILL KEEP OPEN AND CLOSE WE CUT SECONDARY . AT ROTTED POLE AT 16:15 AND MADE SERVICES BACK UP AT 17:45. WE DID NOT OPEN TRANSFORMER. RELEASED BY CREW 074S01 VER/SEF
13825 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2013-11-20 09:30 | 2013-11-20 11:30 | 3 | 120 | 4058401 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 0715 ETA 911 HOUSE FIRE CALL BACK. PART POWER ON CSP TRANSFORMER// BAD CSP TRANSFORMER CONTACTING CREW// NEED 25 KVA CUTOUT AND BRACKET /// RELEASED BY CREW 076H04// CREW ON SITE, TCM// VER/SEF
13826 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-01-25 18:03 | 2013-01-25 19:15 | 5 | 72 | 4741151 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PRC CREW REQUIRED--BAD 12KV 25KVA TRANSFORMER--TRUCK TO POLE--SMALL OIL SPILL NEEDS CLEANED UP--LEAKING TRANSFORMER IS NEW RELEASED BY CREW 078S07/ FETR 19:45 JEH// REPAIRS COMP. POWER RESTORED @ 19:15//JEH(5 CUST.) ///VER/CRB L/3 CRB IDCC TOF1633 XXXX
13827 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-01-27 09:15 | 2011-01-27 12:15 | 2 | 180 | 66147-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 225-125, CREW ENROUTE. COD-2 VER/KEP IDCC TOF0739, ESTIMATED TIME OFF XXXX
13828 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-06-16 20:30 | 2010-06-16 21:10 | 9 | 40 | 50110-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND TRANSF FUSE BROKE - REPLACED AND IS OKAY. VER/LDA AJBC FEC57
13829 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-04-23 19:35 | 2011-04-23 21:05 | 4 | 90 | 63167-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING CUTOUT DOOR //VER/GAH IDCC FEC49 XXXX
13830 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-11-05 16:00 | 2010-11-05 16:40 | 9 | 40 | 53243-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE DID NOT START TIL 1600 EVEN THOUGH 1 TIX SHOWS EARLIER THEY WERE CALLING IN THE FIRE//REPLACED CUTOUT / GXJ RELEASED BY CREW 074S03//VER/CRB IDCC PN24 , CNT11 XXXX
13831 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-12-03 15:30 | 2010-12-03 17:00 | 4 | 90 | H62768-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 62768-1 // SERVICE DROP BURNT DOWN....WILL HAVE TO OPEN XFMR TO REPLACE...4/3 DROP WAS UNDERSIZED AND BURNT DOWN...CUSTOMER HAD A 200AMP METERBASE...SEND A COPY OF THIS TO PEGGY WAYSON...POWER RESTORED @ 17:00//COD 4// VER/DBM IDC XXXX
13832 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-07-07 20:25 | 2017-07-07 21:25 | 6 | 60 | 4090221 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE ON POLE 1-13, ITS ON SIDE OF HILL, WILL HAVE TO OPEN TRANS. ON POLE 1-12 AND 1-14 TO SAFELY CLIMB AND MAKE REPAIRS, WILL KEEP TRACK OF TIMES. ATTEMPTED TO CONTACT CUSTOMERS. TFO OFF 2025-2125. 39830879B34699 OFF ONLY/ COD: 6 VER/AWD
13833 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2022-01-28 15:30 | 2022-01-28 16:10 | 9 | 40 | 4411971 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | customer has open neutral on our side. hooked up the add a phase machine to correct problem. crew will be back first thing monday to try and find problem with underground service. open line fuse @ 15:30 closed @ 16:10
13834 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-03-04 05:15 | 2019-03-04 11:15 | 1 | 360 | 4948831 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | //BAD CONNECTION@ XFR RISER TO SERVICE CONNECTIONS.MADE NECESSARY REPAIRS&RESTORED POWER L3/HFP
13835 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-05-14 14:09 | 2009-05-14 14:54 | 8 | 45 | 55344-1 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEC. BUSHING IN XFMR LOOSE ..NEED TO SEND A COPY TO DENZIL, SMITH..,TO CHG XFMR...MAY NEED TO GO BACK WITH 50 KVA..AND CHG OUT DROP TO MARSHAS BEAUTY SHOPP..BB VER/KEP L3/KEP
13836 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-12-22 16:10 | 2008-12-22 16:25 | 24 | 15 | 62718-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411801//HOT TAP IS ALMOST BURNT INTO REPLACED HOT ----OFF AT 16:10 BACK ON AT 16:25//VER/CRB L3/KEP IDC XXXX
13837 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-01-08 22:00 | 2019-01-08 22:30 | 12 | 30 | 4646921 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg bad @ xfmer. repaired off @ 22:00 on @ 22:30
13838 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2015-12-14 12:15 | 2015-12-14 12:55 | 9 | 40 | 4530741 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELATED TO ORDER 4529921 - CREW HAD TO OPEN LINE FUSE TO SAFELY REPLACE BROKE INSULATOR OFF @ 1215 - ON @ 1255 // SEE OTHER OUTAGE FOR INITAL SERVICE OUTAGE VER/HFP L3/HFP
13839 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2015-03-21 19:55 | 2015-03-21 22:55 | 2 | 180 | 4216861 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KV CSP XFMR, 12KV, SWITCH ON THE SIDE WOULDNT PICK UP. BELIEVE BIG BUCKET WILL WORK, NOT SURE?//// MATERIAL 50KV, 7200 XFMR, C/O AND BRKT. CREW REQUIRED RELEASED BY CREW 077S08 VER/TOM L3/TOM
13840 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-01-08 14:33 | 2015-01-08 17:33 | 2 | 180 | 4921211 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE A BAD 25 KVA SINGLE BUSHING NEED CREW TO REPLACE CAN USE TRUCK 2 TRANSFORMER UP ROAD GOING TO DAM, ON THE RIGHT RELEASED BY CREW 078S06/CREW ON SITE/FETR 1830/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1733/PLEASE CLOSE TICKET/THANKS/VEM/COD 2// VER/ ADH
13841 | Paintsville | 3401101 | FALCON | FALC-OILS | 2012-02-16 18:00 | 2012-02-16 19:30 | 4 | 90 | 4354111 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE, CUTOUT BROKEN.PUT POLE OUT.CHG CUTOUT COD-4 ISO TF 38830805000052 VER/HFP L3/HFP IDC XXXX
13842 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-10-20 14:12 | 2015-10-20 14:52 | 9 | 40 | 4364261 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING STEP DOWN 538-72 TO REPLACE BAD CUT OUT ON POLE 562-17/OPENED 1412 CLOSED 1452// VER/ ADH L3/DKG
13843 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-02-01 16:45 | 2010-02-01 22:45 | 1 | 360 | 62115-1 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 37830295A30310, WE HAVE BAD UNDERGROUND. CREW REQUIRED. SEND TO JEFF COMBS RELEASED BY CREW 077S08 REPAIRED UG SERVICE AND RESTORED POWER TO CUSTOMER AT 2245 JKC//VER/CRB IDC XXXX
13844 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-07-28 14:04 | 2014-07-28 17:04 | 2 | 180 | 4302261 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ELECTRICIAN CALLED HIGH VOLTAGE COMPLAINTS// GONNA HAVE TO CHANGE TRANSFORMER// ISO 38830478A10247// COD 2. BAD 7200 25 KVA SERVICE BUCKET TO POLE AND PICKUP ONLY. RELEASED BY CREW 078S11///CHANGED BAD CAN///VOLT CK GOOD///BACK ON @ 17:04///TBL TKT COMP VER/CRB
13845 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-06-02 15:40 | 2015-06-02 17:10 | 4 | 90 | 4502501 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE37830195000024 . REPLACED CUTOUT . CLOSED FUSE @ 17:10 VER/CRB
13846 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-01-25 11:45 | 2018-01-25 11:51 | 60 | 6 | 4772601 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Emergency outage required to safely replace broken cutout on 38830092C00619. Opened recloser on 38830068D00286 at . opened at 11:45 power restored at 11:51
13847 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-11-05 17:30 | 2013-11-05 17:50 | 18 | 20 | H4012541 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "C" PHASE FUSE ONLY//COD 4//ARRRIVED FOUND C PHASE LINE FUSE OUT, PATROLLED FOUND BAD L/A ON POLE 1098-3144, OPENED OTHER 2 PHASES 18 @ 1730 ON @ 1750 DUP OF 4012541 FOR 18 // VER/HFP L3/HFP IDC XXXX
13848 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-02-24 13:39 | 2014-02-24 13:49 | 36 | 10 | 4431151 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENING RECLOSER TO CLOSE SWITCHES AND PICK UP LOAD WITH RECLOSER OPENED @1339 CLOSED @1349 COD-36 VER/HFP L3/HFP IDC XXXX
13849 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-03-02 13:15 | 2020-03-02 14:35 | 15 | 80 | 4444301 | 360 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Bad secondary leg. Transformer on pole 248-616 off at 14:15 to 14:35.
13850 | Cannonsburg | 3110901 | WURTLAND | WURTLAND | 2022-02-03 00:17 | 2022-02-03 00:35 | 20 | 18 | 4425861 | 360 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | DOL 1180514 // SCADA indicates station l/o @ 0017 // cod 20
13851 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-05-10 14:10 | 2020-05-10 17:10 | 2 | 180 | 4819721 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200-25kva csp. beside road,truck to pole Released by crew 078S07//arrived RM power on @ 17:10 please close tic RM
13852 | South Williamson | 3202201 | LOVELY | LOVELY | 2013-06-29 09:15 | 2013-06-29 15:15 | 1 | 360 | 4426251 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR.PUTTING OUT 148/148/296 VOLTS..OPENED XMFR CUTOUT @ 12:00..NEED 2 MEN & MATERIAL HANDLER BUCKET & 25KVA 19.9 KV XFMR. RELEASED BY CREW 080S01 XFMR CHANGED ON AT 15:15 D SAMMONS VER/CRB L/3 CRB
13853 | Pikeville | 3414901 | FISHTRAP | DISTRIBUTION | 2015-06-26 20:06 | 2015-06-26 21:18 | 5 | 72 | 4664231 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 77-34 SOLID BLADE CUTOUT BROKEN,NEED CREW.WILL OPEN @77-183&77-174 WHEN CREW ARRIVES,NO NEED TO OUTAGE ANYONE ELSE TILL THEN//OPENED BLADE ON POLE 37820077000183 @2006 COD 5//CLOSED 2118 VER/CRB
13854 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-03-10 08:50 | 2011-03-10 10:50 | 3 | 120 | 52726-1 | 360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS ON TRANSFORMER VER/KEP IDC XXXX
13855 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-11-16 10:19 | 2020-11-16 16:18 | 1 | 359 | 4694871 | 359 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 197 -248 bad 15 kva trucks ok/crew required Released by crew 078S03//arrived RM power on @ 16:18 please close tic RM
13856 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-11-21 17:11 | 2008-11-21 23:10 | 1 | 359 | H50735-1 | 359 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 3400303// BAD 25KVA PAD MOUNT TRANSFORMER. I CALLED WILLIE HE IS CALLING A CREW TO HEAD THIS WAY // OPEN @ RISER POLE 1126-823 TO ISOLATE AND CHANGE PAD MOUNT// OPENED @ 2200 AND CLOSED @ 2310 // VER/TOM IDCC DUP FOR ORIGINAL OUTAGE XXXX
13857 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-12-29 11:21 | 2013-12-29 17:20 | 1 | 359 | 4209691 | 359 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 293-53 NEED BIG BUCKET & 7200 CUTOUT . VIRGIL HURT COMMING TO HELP. POWER BACK ON @ 17:20. COD-1 ISO 37830293000053 VER/HFP L3/HFP
13858 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2013-01-30 11:31 | 2013-01-30 14:30 | 2 | 179 | 4757801 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CREW ENROUTE COD-2 ISO TF 37820147D00151 VER/HFP L3/HFP IDC XXXX
13859 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-12-07 10:14 | 2011-12-07 16:12 | 1 | 358 | 4147811 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD XFMR, 15 KVA 19.9KV. WILL NEED CREW RELEASED BY CREW 077S02 CHANGED XFMR AND RESTORED POWER AT1612 CREW 077H01 COD-1 ISO TF 37830181D00332 VER/HFP L3/HFP IDC XXXX
13860 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-06-20 18:24 | 2018-06-21 00:22 | 1 | 358 | 4631781 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | per terry fields, this has been this way for a while, he is making himself an ops order to dome back on this tomorrow ///// there was 1 customer transferred from outage 4630901. the customer was out at 1824.
13861 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-01-08 18:42 | 2019-01-09 00:40 | 1 | 358 | 4643601 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 247-541,need line crew.19.9kv Released by crew 077S04
13862 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-10-17 10:51 | 2018-10-17 13:50 | 2 | 179 | 4261691 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connection
13863 | Hazard | 3309302 | VICCO | JEFF | 2022-11-01 07:36 | 2022-11-01 10:35 | 2 | 179 | 4084541 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke changed cutout power restored at 10:35
13864 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-04-22 19:21 | 2011-04-22 22:20 | 2 | 179 | 62221-1 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AS A RESULT OF BAD CUTOUT.....POLE 1111D160.....LATERAL FUSE BLOWN ON 1111D14.....CALLED CREW....NEED BUCKET & CROSARM TO BAYONET POLE TOP....PLEASE SEND TO JOEY REED....THANX.....JRV RELEASED BY CREW 080S01//MADE MAP DISC//COD 2. SEND TO R/W . 1 SPAN NEEDS TREES TRIMMED //VER/GAH IDCC PN160 XXXX
13865 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-10-02 06:22 | 2012-10-02 09:21 | 2 | 179 | 4106161 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOIUND C PHASE LINE FUSE BLOWN ON POLE 1097-DH-22, PATROLLED AND FOUND BAD L/A ON POLE 1097-278, PLEASE BUT IN ABNORMAL DATABASE, I HAVE IT CUT IN THE CLEAR, I CLOSED IN LINE FUSE AT 0921 RESTORING POWER AT THIS LOC//ISO 1097-C-1262 <-- SERVICERS TRUCK WAS AT THIS POLE WHEN RESTORING//COD 2//AED CREATED// VER/DBM IDC XXXX
13866 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-07-14 08:22 | 2014-07-14 14:20 | 1 | 358 | 4238421 | 358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT NO TRUCKS TO POLE. NEED LINE CREW. RELEASED BY CREW 078S01-----BAD 25KVA--POLE 309-46-- REPLCED 25KVA WITH 15KVA FEEDS ONE CUST.----//COD 1//ISO 38830309000046// VER/DBM
13867 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-02-16 02:01 | 2014-02-16 04:00 | 3 | 119 | 4391701 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN NOT BLOWN VER/ARN
13868 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-10-03 08:51 | 2015-10-03 09:08 | 21 | 17 | 4308011 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | EDDIE OPENING RECLOSER TO ISOLATE TROUBLE ON TICKET #4307751 OPENED AT _0851_ CLOSED AT _0908___. VER/SEF // VERFIED PER VOICE RECORDER = L3/HFP XXXHFP AJB
13869 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-10-24 14:50 | 2016-10-24 20:47 | 1 | 357 | 4049551 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ORIGINAL TICKET WORKED FROM OPS, VOLTAGE WAS 285 PHASE TO PHASE AND 141 PHASE TO GROUND, BAD 25 7200, TRUCK OK, CREW REQUIRED RELEASED BY CREW 078S11/CREW ON SITE/FETR 2100/VEM/REPAIRS MADE AND ALL CUST RESTORED 2047/PLEASE CLOSE TICKET/THANKS/VEM VER/AWD L3/HFP XXXHFP
13870 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-02-24 19:14 | 2015-02-24 20:05 | 7 | 51 | 4079151 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE WILL REPLACE/// REPLACED BAD CUTOUT AND RESTORED SERVICE @ 20:05/COD 7// VER/ ADH
13871 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-07-25 17:09 | 2010-07-25 23:06 | 1 | 357 | 56888-1 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE/////BAD XFR,WILL BE REPLACING IT.DALE H IS GETTING CREW,NOTE NEW FETR//////RE-LOCATED XFR TO POLE 986-3 VER/ARN IDC XXXX
13872 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2015-03-31 17:57 | 2015-03-31 19:56 | 3 | 119 | 4252121 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD-3 VER/HFP L3/HFP
13873 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2019-05-02 20:29 | 2019-05-02 22:28 | 3 | 119 | 4203671 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on pole 217-52////will make repairs .restored. L3/HFP
13874 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-08-13 20:41 | 2010-08-13 22:40 | 3 | 119 | 54497-1 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN..RE FUSED TRANSFORMER...BB.//VER/CRB
13875 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-08-02 14:02 | 2015-08-02 16:01 | 3 | 119 | 4967591 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LA SERVICER TO CHANGE LINE FUSE ON P 05 IN @ 16:01 ALL PWR RESTORED PLEASE CLOSE TICKET LRM// VER/ ADH
13876 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-01-21 01:58 | 2012-01-21 07:55 | 1 | 357 | 4279131 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 190-108 //VER/GAH IDC XXXX
13877 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-08-06 07:01 | 2011-08-06 09:00 | 3 | 119 | 4670591 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT 7200, SILVER TOP.//VER/CRB IDC XXXX
13878 | Pikeville | 3407101 | TOPMOST | DEMA | 2013-12-29 13:17 | 2013-12-29 15:16 | 3 | 119 | 4209891 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TAP AT POLE 35 AT 13:17 (3 CUST), OPENED AT POLE 37830113000099 AT 13:30 (10 CUST)OPENED TAP AT POLE 35 AT 13:17, OPENED AT POLE 37830113000099 AT 13:30 . EXTINGUISHED FIRE AND REPLACED CUTOUT AT POLE 35, RESTORED ALL CUSTOMERS AT POLE 99 AT 15:16 , ALL WORK COMPLETE / GXJ SEE H4209891 VER/HFP L3/HFP
13879 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-05-13 13:16 | 2009-05-13 15:15 | 3 | 119 | 52240-1 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | THE CURRENT LIMITING FUSE FAILED. VER/ARN IDC XXXX
13880 | Pikeville | 3421001 | BREAKS | CITY | 2016-11-01 09:48 | 2016-11-01 11:47 | 3 | 119 | 4067321 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE REPAIRS TO CUTOUT VER/AWD
13881 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-06-07 12:17 | 2013-06-07 14:16 | 3 | 119 | 4236121 | 357 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS ON XFMR, PART POWER, COMPLTED VER/KEP IDC XXXX
13882 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-01-06 16:57 | 2009-01-06 19:45 | 4 | 168 | 52025-1 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27949071 //3000802//CALLED FOR CREW WITH BIG BUCKET/271-140 15T BACK IN AT 1800 HRS SEND TO MCCARTY/1 CUSTOMER STILL OUT RELEASED BY CREW 078S03/ LAST CUSTOMER BACK ON @ 19:45 L3/HFP IDC XXXX
13883 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2011-03-03 17:51 | 2011-03-03 19:50 | 3 | 119 | 66280-1 | 357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#39033159////VER/CRB IDC XXXX
13884 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2008-12-19 15:07 | 2008-12-19 21:03 | 1 | 356 | 60603-1 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED NO TRUCKS SMALLEST 10 OR 15 KVA YOU CAN GET/LIMITED SPACE ON TURN AROUND WITH TRUCKS RELEASED BY CREW 078S03 VER/TOM L3/TOM IDC XXXX
13885 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-07-10 09:34 | 2010-07-10 15:30 | 1 | 356 | 64719-1 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BROKEN XFRMER CUTOUT.....& DE-ENERGIZE LATERAL (AGAIN) THAT FEEDS OFF THIS POLE...(IT SERVES NO CUSTS NOW).....//....XFRMER CUTOUT REPLACED....TAP DE-ENERGIZED AGAIN....POWER ON FOR 2 CUSTS FED OFF THIS XFMR ON POLE 794B107....JRV...07/10/10 // COD 1 IDC XXXX
13886 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2011-12-22 10:31 | 2011-12-22 12:00 | 4 | 89 | 4194871 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND 4/3 SECONDARY BURNTED DOWN, I REPLACED IT WITH 2/3 SECONDARY, ALL POWER IS RESTORED AT THIS LOC//COD 4// VER/DBM IDC XXXX
13887 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-12-17 16:06 | 2017-12-17 17:35 | 4 | 89 | 4654841 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout/ ISO 37820032C00004/ COD 4***map shows 3 servicer says 4
13888 | Pikeville | 3407101 | TOPMOST | DEMA | 2009-05-04 11:14 | 2009-05-04 14:12 | 2 | 178 | 50363-1 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 50T LINE FUSE OPEN ON POLE 37830162000020 ( NOT ON MAP ), TRANSFORMER CUTOUT BAD POLE 177 MD FILED COS-2 ... RPLACED CUTOUT AND ARRESTER, ALL WORK COMPLETE / GXJ VER/KEP L3/KEP
13889 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-05-24 10:43 | 2013-05-24 16:39 | 1 | 356 | 4178891 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1126-205 HAS 50KVA 19900 277-480 TRANSFORMER BAD.ONLY FEEDS PUMP FOR PONDS.CUSTOMER SAID CAN WAIT TILL TUESDAY MORNING.SEND TO TIM HALL TO SCHEDULE FOR TUESDAY MORNING.. VER/HFP L3/HFP IDC XXXX
13890 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-07-11 15:11 | 2022-07-11 18:09 | 2 | 178 | 4461391 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans cutout broke at pole 261-10,Will be making repairs..Restored at 18:09.
13891 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-12-05 23:13 | 2008-12-06 00:42 | 4 | 89 | 54814-1 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411802//XFR TO RE-FUSEXFR CUTOUT BROKEN INTO,REPLACED IT AND RESTORED POWER VER/JHM L3/KEP IDC XXXX
13892 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-07-18 16:56 | 2012-07-18 18:25 | 4 | 89 | 4760931 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP, I GOT OLD ONE GOING TO TRY TO REFUSED TRANSFORMER VER/KEP
13893 | Pikeville | 3308404 | BECKHAM | PIPPA PASSES | 2020-04-22 17:54 | 2020-04-22 23:50 | 1 | 356 | 4737951 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva i talked to paul lane he will be bringing 1 send to paul lane Released by crew 074S03
13894 | Pikeville | 3403001 | PIKEVILLE | CITY | 2008-10-26 13:01 | 2008-10-26 14:30 | 4 | 89 | 59200-1 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP LEAD MELTED AT TRANSFORMER, OPEN TRANSFORMER AT 14:15. TOTAL 4 CUSTOMER WITH PART POWER IDCC TOF1415 XXXX
13895 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2011-11-05 17:14 | 2011-11-05 23:10 | 1 | 356 | 4054111 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 100KVA 277 / 480 TRANSFORMER , 2 MEN , LINE TRUCK, NO BUCKET REQUIRED, CAN USE MY SEVICE BUCKET TO CHANGE TRANSFORMER / GXJ .. CALL STEVEN AT 791-1078 WHEN REPAIREDNEED 100KVA 277 / 480 TRANSFORMER , 2 MEN , LINE TRUCK, NO BUCKET REQUIRED, CAN USE MY SEVICE BUCKET TO CHANGE TRANSFORMER / GXJ . REPLACED TRANSFORMER, ALL WORK COMPLETE / GXJ VER/PDP IDC XXXX
13896 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-09-22 18:11 | 2021-09-22 21:09 | 2 | 178 | 4279151 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Have a broke Trans Cutout at 189-D-142,Will be making repairs..Restored at 21:09.
13897 | Paintsville | 3401802 | INDEX | HOSPITAL | 2017-02-15 12:04 | 2017-02-15 18:00 | 1 | 356 | 4399691 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR..NEED XFMR 1 MAN AND MATERIAL HANDLER.. VER/CRB L3/HFP XXXHFP
13898 | Hazard | 3420001 | SOFT SHELL | VEST | 2011-05-29 21:17 | 2011-05-30 03:13 | 1 | 356 | 4207981 | 356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA, CSP XFMR. NEED 7200 15 KV XFMR AND C/O AND BRKT. MATERIAL HANDLER BUCKET.//// XFMR CHANGED, POWER RESTORED IDCC PN23 XXXX
13899 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-02-28 07:54 | 2008-02-28 09:05 | 5 | 71 | 51158-1 | 355 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK IN TRANSFORMER BANK VER/HFP L3/DEBBIE IDC XXXX
13900 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-01-06 07:40 | 2014-01-06 13:35 | 1 | 355 | 4235021 | 355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED CREW OPENWIRE SECONDARY DOWN/ 6A WIRE SHOULD BE ABLE TO GET TRUCK TO POLE--OPENED TRANSFORMER ON POLE 38830090000077 AT 11:20 RELEASED BY CREW 078S07, CREW ON SITE,,REPAIRS MADE, ALL POWER RESTORED//COD 1//ISO// VER/DBM
13901 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-10-15 06:40 | 2015-10-15 12:35 | 1 | 355 | 4350171 | 355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 PHASE OF SERVICE DROP OPEN. WILL GET R/W CUT & REPAIR SERVICE. BAD 25 KVA .ONE PHASE OPEN IN XFMR.WILL NEED 25,120/240. 19.9. CREW IS ON WAY. LINE FUSE TIMES (OPENED PRIMARY TAP ON POLE 36 @ 11:00 BACK ON @11:20)/ ISO 38831100000036/ COD 1/ VER/BOW
13902 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-09-03 21:18 | 2010-09-04 03:13 | 1 | 355 | 63456-1 | 355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR.. REPLACED 15 KVA BACK ON AT 3:13 .. C YOUNGMAN VER/PDP IDC XXXX
13903 | South Williamson | 3411401 | DEWEY | INEZ | 2008-05-12 06:00 | 2008-05-12 11:55 | 1 | 355 | 62417-1 | 355 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BURNT OPEN AT SPLICE. REPAIRED. SH//3411401//VER/CRB IDC XXXX
13904 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-04-12 08:35 | 2008-04-12 14:30 | 1 | 355 | 50348-1 | 355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT-WILL NEED 1 MAN %26 BUCKET-THIS IS TRUCK ACCESSIBLE VER/HFP MLR OK
13905 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-12-23 08:49 | 2010-12-23 10:00 | 5 | 71 | 55255-1 | 355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#38194258// BAD CUTOUT 10T FUSE//VER/CRB IDC XXXX
13906 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-06-04 18:36 | 2021-06-05 00:31 | 1 | 355 | 4670331 | 355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 19.9 25kva txmf, truck ok crew required Released by crew 078S11///Complete BR
13907 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-05-16 20:33 | 2015-05-16 23:30 | 2 | 177 | 4436721 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT
13908 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-01-18 02:06 | 2011-01-18 08:00 | 1 | 354 | 62060-1 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK AT NORMAL START TIME PER CALL OUT GUIDE LINES FOUND FUSE LINK HAD ROTTEN AND BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC // COD-1 ISO TF 39831024A00228 VER/HFP L3/HFP IDC XXXX
13909 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-04-15 15:20 | 2020-04-15 18:17 | 2 | 177 | 4700441 | 354 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connectionson pole. repaired
13910 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-04-17 08:27 | 2010-04-17 10:25 | 3 | 118 | 64345-1 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE #S ARE WRONG,206-2700 IS THIS CUST TRANSFORMER POLE #//MD FILED//COD 1//ISO 38830182B30120 // VER/DBM IDC XXXX
13911 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-02-24 14:22 | 2010-02-24 16:20 | 3 | 118 | 60621-1 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I WILL BE CHANGING BAD CUTOUT. CUTOUT CHANGED FUSE UP 10T FUSE EVERYTHING OK.//COD 3// VER/DBM IDC XXXX
13912 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-05-14 09:02 | 2014-05-14 11:59 | 2 | 177 | 4698951 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE#1062-C-244 BURNT OFF FAILED CUTOUT. FUSE IS BLOWN ON POLE 38821062C00312. RELEASED BY CREW 079S02.GOING TO LOWER EQUIPMENT. R/W CREW ENROUTE. ** CUSTOMERS RESTORED AT 1159 CREW STILL ON SITE WORKING ALL POWER ON. VER/KEP
13913 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2021-10-17 07:53 | 2021-10-17 10:50 | 2 | 177 | 4358681 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | bad UG elbow, made repairs and customer restored
13914 | South Williamson | 3411401 | DEWEY | INEZ | 2010-04-10 14:52 | 2010-04-10 16:50 | 3 | 118 | 61952-1 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT...CHG CUTOUT..BB//VER/CRB IDC XXXX
13915 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-08-28 03:55 | 2016-08-28 06:52 | 2 | 177 | 4843661 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED APART @ 38821058D00117, REFUSED @ 0652.
13916 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-04-08 18:48 | 2015-04-08 21:45 | 2 | 177 | 4292071 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT/COD 2// VER/ ADH
13917 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-03-18 16:40 | 2018-03-18 18:38 | 3 | 118 | 4024931 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cod 3 iso 37830261000016 cutout broke willl replace
13918 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2020-10-25 13:16 | 2020-10-25 14:15 | 6 | 59 | 4583371 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer restored @ 14:15
13919 | Hazard | 3303902 | LESLIE | WOOTON | 2020-05-26 12:49 | 2020-05-26 14:47 | 3 | 118 | 4909131 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | replaced arrester
13920 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-12-07 07:06 | 2011-12-07 13:00 | 1 | 354 | 4146951 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHG CUTOUT COD-1 ISO TF 38830655B00284 VER/HFP L3/HFP IDC XXXX
13921 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-07-18 15:51 | 2020-07-18 21:45 | 1 | 354 | 4180071 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr 25 kva 19.9 Released by crew 077S12
13922 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-10-14 14:02 | 2020-10-14 19:56 | 1 | 354 | 4555821 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva 7200 not by truck unless you have a really long boom. will need flaggers Released by crew 078H03,repairsmade all cust restored @ 1956 please close ticket thanks.bt
13923 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2019-09-04 19:29 | 2019-09-05 01:23 | 1 | 354 | 4981961 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connections on pole, 45-c4-5903, meter blanked at dr office. Send to Rick Morgan Released by crew 078H04/arrived RM fixed connection &checked volatge all good please close tic RM
13924 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-01-17 09:02 | 2010-01-17 11:00 | 3 | 118 | 55318-1 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN,WILL REPLACE///REPLACED CUTOUT AND RESTORED,ALL OK AFTERWARDS IDC XXXX
13925 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-11-06 07:15 | 2018-11-06 10:12 | 2 | 177 | 4369221 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuse blown on pole 215-17//////dead insulator is bad on pole 37830215B00372.wil make repairs.// L3/HFP
13926 | Pikeville | 3413402 | GARRETT | LACKEY | 2016-06-26 13:00 | 2016-06-26 18:54 | 1 | 354 | 4478571 | 354 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL OPEN SD SERVICE POLE 37830087D00063 REPAIRED 18:54 TOM MCCOWN VER/CRB
13927 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2008-12-01 09:17 | 2008-12-01 11:15 | 3 | 118 | 53448-1 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3400702// - WR#27476771 CUTOUT FAILURE COD-3 L3/KEP IDC XXXX
13928 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-06-26 12:52 | 2011-06-26 14:50 | 3 | 118 | 4416301 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT ON POLE 254-434.. FUSE WAS NOT BLOWN, METAL FUSE TAIL WAS BROKE WHICH OPENED DOOR. REFUSED DOOR AND CUST RESTORED AT 14:50.. CAY//VER/CRB IDC XXXX
13929 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-02-21 11:58 | 2018-02-21 13:55 | 5 | 117 | 4868221 | 354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout 37830422000127 manual/ had to open hot tap 1315 on pole 37830398B00250 to change/ ISO 37830398B00250 COD 3/ ISO 37830422000127 COD 1
13930 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-06-02 23:22 | 2009-06-03 05:15 | 1 | 353 | 63221-1 | 353 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25KVA TRUCKS OK AT CEMETARY ON TOP OF TRUMBO HILL TURN BESIDE CEM. TRAILOR OUT ROAD ON RIGHT RELEASED BY CREW 078S03//VER/CRB IDC XXXX
13931 | Pikeville | 3421001 | BREAKS | CITY | 2011-05-12 10:17 | 2011-05-12 16:10 | 1 | 353 | 4071521 | 353 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT//COD 1// VER/DBM
13932 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-02-06 01:37 | 2009-02-06 07:30 | 1 | 353 | 56066-1 | 353 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3301402/// BAD XFMR, SIDE OF HILL, MANUEL JOB // VER/TOM L3/TOM IDC XXXX
13933 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-04-12 05:05 | 2011-04-12 10:58 | 1 | 353 | 55528-1 | 353 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / WILL DISP IN AM FOUND BAD CUTOUT, WELL BE CREW REQUIRED, IN BEHIND SECOND HOUSE ON BILLUP FORK, NONE TRUCK ACCESIBLE RELEASED BY CREW 078S06// WILL NEED TO OPEN RECLOSER ON POLE 1024-32 TO REPLACE CUTOUT//TIMEOFF ON RECL.10:16 TIMEON 10:58 ALL CUST. RESTORED PTOLLIVER VER/HFP L3/HFP IDC XXXX
13934 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-07-05 18:34 | 2022-07-05 21:30 | 2 | 176 | 4389961 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout on pole - 900-36 broken.changing
13935 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2015-08-18 08:54 | 2015-08-18 11:50 | 2 | 176 | 4146951 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7200 CUTOUT ON POLE 262-101// VER/ ADH
13936 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-12-22 16:50 | 2011-12-22 19:12 | 4 | 142 | 4195601 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED ON 247-266 1 CUSTOMER OFF 247-19 30T BACK IN AT 1800HRS/NO CREW REQUIRED ///VER/CRB IDCC STP MISSING XXXX
13937 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2019-08-30 18:43 | 2019-08-31 00:35 | 1 | 352 | 4966421 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmer changed out/ back in @ 0035/ please close ticket/ MLH
13938 | Hazard | 3310502 | HADDIX | CANOE | 2008-07-18 19:44 | 2008-07-18 20:16 | 11 | 32 | 54035-1 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3310502// RESAGED NET OPEN AT 1944 CLOSED AT 2016 G. SHOUSE//COD 11//ISO 37830170000045// VER/DBM IDC XXXX
13939 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2019-04-09 16:02 | 2019-04-09 18:58 | 2 | 176 | 4075231 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke on xfmr cutout. Restored @ 18:58. sh
13940 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2015-08-14 15:38 | 2015-08-14 21:30 | 1 | 352 | 4135531 | 352 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED ALL CONNECTIONS & REFUSED XFMRS.50 KVA IS NOW BAD. HAVE CALLED FOR 50 KVA 7200/120/240 2 BUSHING.& MATERIALHANDLER.// VER/ ADH
13941 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-10-12 21:05 | 2009-10-12 22:33 | 4 | 88 | 60444-1 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT INTO WILL HAVE TO OPEN XFMR TO MAKE REPAIRS... REPAIRED SERVICE RESTORED POWER AT 22:33 //VER/CRB IDC XXXX
13942 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-05-11 11:59 | 2020-05-11 14:55 | 2 | 176 | 4824131 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 37830055000240 and got line fuse out on pole37830055000239 cut vines off fuse pole 25t
13943 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-08-27 11:53 | 2012-08-27 17:45 | 1 | 352 | 4976171 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND TALKED TO CUST CAN WAIT TILL TUESDAY // SENT EMAIL TO LLOYD RAYBURN & LLOYD MCCARTY ON THIS TO HAVE IT FIXED TOMORROW 08/28/12 VER/HFP L3/HFP IDC XXXX
13944 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-04-15 09:33 | 2018-04-15 12:29 | 2 | 176 | 4226821 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ser drop & sec. almost burn into splice out sec. resqueeze connections at xform power restored
13945 | Hazard | 3310502 | HADDIX | CANOE | 2010-12-21 16:19 | 2010-12-21 19:15 | 2 | 176 | 54900-1 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | WIRE OFF INSLATOR--NEED BIG BUCKET,ONE MAN--OFF AT 16:19--HELP IS ON THE WAY--ON 19:15 COD-2 ISO LF 37840144000027 VER/HFP L3/HFP IDC XXXX
13946 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-07-15 15:32 | 2015-07-15 17:00 | 4 | 88 | 4881801 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA POLE 1147-C1-4228, NEW 50KVA INSTALLED SER# HI1948622015
13947 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-11-29 10:24 | 2013-11-29 16:16 | 1 | 352 | H4087561 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SECONDARY HAS BURNED DOWN AGAIN BETWEEN POLE 38821014C20332 AND THE CHURCH BUILDING. WE ARE GOING TO REPLACE THE 1/0 CONDUCTOR WITH 4/0. TRANSFORMER FUSE DID NOT BLOW, BUT WE WILL OPEN IT TO REPLACE THE SECONDARY CONDUCTOR WHEN WE GET READY. OPENED TRANSFORMER UP AT 15:39, AND CLOSED BACK IN AT 16:16. VER/CRB IDC XXXX
13948 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-07-01 20:21 | 2019-07-02 02:13 | 1 | 352 | 4630041 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad transformer pole # 1110/30
13949 | Whitesburg | 3314401 | MAYKING | ERMINE | 2018-02-02 21:54 | 2018-02-03 00:50 | 2 | 176 | 4796851 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 7200 xfmr on pole 449-204, replaced xfmr restored power at 00:50.
13950 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-05-02 18:31 | 2011-05-02 19:03 | 11 | 32 | 53808-1 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO ORDER 53780-1 CREW OPENED RECLOSER AT ???? TO MAKE REPAIRS TO LOOP BURNT OPEN AT POLE 401-13//VER/CRB IDC XXXX
13951 | Pikeville | 3402002 | KEYSER | STONECOAL | 2012-07-06 14:24 | 2012-07-06 17:20 | 2 | 176 | 4547061 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH
13952 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2017-04-17 18:05 | 2017-04-17 18:21 | 22 | 16 | 4652821 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED RECLOSER ON POLE 38830190000146 TO SAFELY MAKE REPAIRS TO FACILITIES. P190-146 REPAIRED HOT TAP ON B PHASE . ALL REPAIRS MADE PLEASE CLOSE TICKET LRM OPENED @ 18:05 RESTORED @ 18:21/ ISO 38830190000146/ 22/ VER/BOW L3/HFP XXXHFP AJB
13953 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2012-04-26 08:58 | 2012-04-26 14:50 | 1 | 352 | 4710411 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 5 KVA ON HILLSIDE NO TRUCKS CAN RELOCATE TO 296-115 TRUCKS TO IT NEED 10 KVA COMPLETE/CREW REQUIRED RELEASED BY CREW 078S03.. RELOCATED TRANSFORMER TO POLE 296-115 WORK ORDER (WITH MAP CHANGES TO FOLLOW) VER/KEP IDC XXXX
13954 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-03-15 14:10 | 2010-03-15 14:42 | 11 | 32 | 50317-1 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | CREW OPENED TO SAFELY STAIGHTEN POLE 453-155 VER/KEP L3/KEP IDC XXXX
13955 | Pikeville | 3413402 | GARRETT | LACKEY | 2010-03-05 10:52 | 2010-03-05 12:20 | 4 | 88 | 63116-1 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED TRANSFORMER CUTOUT ... ALL WORK COMPLETE / GXJ COD-4 VER/KEP L3/KEP IDC XXXX
13956 | Whitesburg | 3401301 | FLEMING | NEON | 2008-07-08 17:04 | 2008-07-08 20:00 | 2 | 176 | 64877-1 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER AND CUSTOMER ALSO HAS A BAD 200 BREAKER HE IS GOING TO CALL BACK IN TO BE DISCONNECTED SO HE CAN CHANGE HIS BREAKER OPENED TRANSFORMER AT 1912 CLOSED IT AT 2000//3401301//VER/CRB IDCC CNT1 XXXX
13957 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-02-04 01:43 | 2010-02-04 04:39 | 2 | 176 | 62846-1 | 352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TR OUT AGAIN (CSP) . SERVICER WILL CONTACT D/S.BAD 15 KVA, CREW REQUIRED, NEED TO UPGRADE TO 25 KVA 7200, TRUCK OK BESIDE ROAD.RESET CSP EARLIER, TRIPPED AGAIN,BAD 15 KVA, CREW REQUIRED, NEED TO UPGRADE TO 25 KVA 7200, TRUCK OK BESIDE ROAD. V MULLINS HAS BEEN CONTACTED, PLEASE SEND TICKET TO HIM.RESET CSP EARLIER, . V MULLINS HAS BEEN CONTACTED, PLEASE SEND TICKET TO HIM. RELEASED BY CREW 078S05 IDC XXXX
13958 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-01-21 12:44 | 2021-01-21 18:35 | 1 | 351 | 4883101 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva 19.9kv transformer, please send to mr. phillip hicks Released by crew 077S05, crew on site,, all power restored @18:35 p.hicks
13959 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-01-18 03:23 | 2014-01-18 05:20 | 3 | 117 | 4291421 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 05:20 VER/HFP L3/HFP
13960 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-02-06 12:57 | 2010-02-06 14:54 | 3 | 117 | 50262-1 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, XFORMER FUSE BLOWN REFUSING IT,POLE#941-281, 3 CUST OFF MD FILED IDC XXXX
13961 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-01-04 23:53 | 2013-01-05 01:50 | 3 | 117 | 4569831 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S08REPLACED BAD CUTOUT DOOR. POWER BACK ON. IDC XXXX
13962 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-11-18 18:41 | 2015-11-18 20:38 | 3 | 117 | 4466681 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830278A00038/ ISO 37830278A00038/ COD 3 CCC**** MD DONE/ VER/BOW
13963 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2018-07-07 13:28 | 2018-07-07 13:55 | 13 | 27 | 4748031 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened transformer pole 211-c-353 at 13:28 to replace cutout and arrester. closed 10t transformer fuse back in at 13:55
13964 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-12-12 09:06 | 2021-12-12 11:03 | 3 | 117 | 4187191 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 2 FUSES OUT HERE,THE LINE FUSE AND THE XFR FUSE UNDER IT/////////RE-FUSED BOTH AND RESTORED ALL////////POSSIBLY THE ARRESTOR ON THE XFR WENT BAD
13965 | Hazard | 3309301 | VICCO | REDFOX | 2022-12-06 23:03 | 2022-12-07 01:00 | 3 | 117 | 4236251 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service netural splice bad made repairs everything checked good at meter
13966 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-11-24 15:38 | 2015-11-24 17:35 | 3 | 117 | 4483811 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ONLY 3 CUSTOMERS AFFECTED STIRRUP BURNT OFF ON38830882B00037. REPLACED AND RESTORED @ 17:35. SH RELEASED BY CREW 076S02//CHANGED TO 3 CUSTS PER SERVICER VER/CRB
13967 | South Williamson | 3200302 | BELFRY | TOLER | 2016-01-03 21:18 | 2016-01-03 23:15 | 3 | 117 | 4582851 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT UP CUTOUT//COD 3// VER/DBM
13968 | Hazard | 3302703 | HAZARD | HAZARD | 2012-11-08 09:01 | 2012-11-08 09:28 | 13 | 27 | 4373291 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE., POWER RESTORED. COD-13 ISO TF 37830272B40012 VER/HFP L3/HFP IDC XXXX
13969 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-01-01 12:14 | 2011-01-01 18:05 | 1 | 351 | 57691-1 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38258802 // BAD 15 KVA TRANSFORMER. COD-1 VER/HFP L3/HFP IDC XXXX
13970 | South Williamson | 3411401 | DEWEY | INEZ | 2016-06-20 16:00 | 2016-06-20 17:57 | 3 | 117 | 4392201 | 351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN ON 770-A-21 I CAN MAKE REPAIRS REPLACED CUTOUT RESTORED POWER AT 17:42 VER/CRB
13971 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-01-08 07:54 | 2015-01-08 10:49 | 2 | 175 | 4918371 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT// COD 2// VER/ ADH
13972 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-07-26 11:40 | 2009-07-26 12:15 | 10 | 35 | 66261-1 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408101 // MANUALLY OPENED RECL POLE 1123-133 TO REPLACE BURNT UP CUTOUT AT POLE 1147-101.ASSOCIATED TICKETS 63950 66253 COMPLTED. IDC XXXX
13973 | South Williamson | 3411401 | DEWEY | INEZ | 2018-05-15 13:55 | 2018-05-15 15:05 | 5 | 70 | 4349071 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Released by crew 079H03 50 kva on 744-B-313 is sizzling and looks like has been getting hot. Contacted Tim Hall and they will change it out tomorrow. plz send copy to Tim Hall..//replaced xfmr and cutout and brkt// at 13:55//closed back at 15:05//complete//em Released by crew 079S01
13974 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2009-12-06 10:27 | 2009-12-06 16:17 | 1 | 350 | 61985-1 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP TRANSFORMER IS BAD WILL NEED TRANSFORMER AND BIG BUCKETT COD-1 ISO TF 37830282000027 L3/HFP IDC XXXX
13975 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2022-12-21 15:45 | 2022-12-21 21:35 | 1 | 350 | 4284721 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required. bad 7200 10kva transformer on pole 453-165. Released by crew 078H33///Complete BR
13976 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-08-21 08:27 | 2009-08-21 11:22 | 2 | 175 | 58060-1 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN, BROKE CUTOUT, REPLACED CUTOUT. PULLED LINE FUSE AT 11:02 AND PUT BACK AT 11:22 VER/KEP L3/KEP IDCC TON1128 XXXX
13977 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-12-24 11:11 | 2008-12-24 14:06 | 2 | 175 | 63364-1 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS POLE 38830069A10267 BAD CUTOUT TALKED TO LLOYD WILL SEND CREW LATER NEED ALL THREE CUTOUTS CHGED RELEASED BY CREW 078S08 CARL DAVIS IS ON THIS JOB HELPING TOLIVER. VER/PDP L3/KEP IDC XXXX
13978 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-07-07 14:14 | 2012-07-07 15:24 | 5 | 70 | 4576321 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER
13979 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-03-07 09:50 | 2021-03-07 12:20 | 11 | 150 | 4311491 | 350 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on secondary from riser, Transformer off from 12:00 to 12:20. Repaired//1 CUST FROM BEGINNING
13980 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-09-27 20:46 | 2010-09-27 20:56 | 35 | 10 | H54278-1 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER POLE 429/364 OPEN; PATROLLING LINES; BURNT TOP OUT OF POLE 405/53; CREW REQUIRED; ISOLATED BETWEEN POLES 405/51 AND 405/49; PARTCIAL PWR RESTORED AT 1706 HRS; OPENED RECLOSER AT 2046HRS TO MAKE UP LOOPS; FULL RESTORATION AT 2056HRS; CLOSE TICKET//VER/CRB IDCC DUP TO OPEN RECLOSER BACK UP XXXX
13981 | Pikeville | 3421001 | BREAKS | CITY | 2018-01-16 06:15 | 2018-01-16 09:10 | 2 | 175 | 4750461 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva xfm 7200// Can use truck Released by crew 074S02--- CHANGED X-FMR, GOOD VOLTAGE ON AT 09:10 R RAY
13982 | South Williamson | 3411401 | DEWEY | INEZ | 2021-08-18 14:10 | 2021-08-18 17:05 | 2 | 175 | 4109381 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | customer said we were here earlier and it stayed on about 20 minute//bottom was blown on arrestor//i replaced arrestor and restored at 17:05//complete//em
13983 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-05-12 05:31 | 2008-05-12 11:21 | 1 | 350 | 62395-1 | 350 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE ON SERVICE DROP,, I MADE REPAIRES IDCC CDC94 XXXX
13984 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-06-18 22:49 | 2008-06-18 23:59 | 5 | 70 | 50588-1 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409303// CUTOUT DOOR BURNT-UP. REPLACED DOOR AND RE-FUSED XFMR CUTOUT. SH VER/JHM
13985 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2019-11-26 19:45 | 2019-11-26 20:55 | 5 | 70 | 4071021 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR cutout had broke down and was arcing causing flickering lights. Had to open cutout to isolate and make safe @ 19:45 This is no truck approach but I should be able to safely make repairs///Replaced cutout and restored power @ 20:55/ ISO 38830834A00448/ cOD 5
13986 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-05-01 19:10 | 2008-05-01 20:20 | 5 | 70 | 56165-1 | 350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3000303 BAD LA ON CSP TRANS. 20-3531 20-3509 20T LINE FUSE VER/HFP IDC XXXX
13987 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2011-08-08 03:11 | 2011-08-08 09:00 | 1 | 349 | 4677391 | 349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, HAVE CHANGED AND POWER IS RESTORED AT THIS LOC VER/KEP IDC XXXX
13988 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2015-11-12 16:26 | 2015-11-12 22:15 | 1 | 349 | 4439091 | 349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STEP DOWN ON POLE # 7-121 IS BAD ///LID HAS BLOWN OFF NEED 333 KVA STEP DOWN //// LINE CREW AND FLAGGER//DONNIE BARTLEY (TRANSMISSION) IS BRING LG LINE TRUCK TO PUT OFF STEP-DOWN// WE ARE ALL ON SITE AND SETTING UP TO GET READY TO CHANGE XFMR.// REPLACED BAD TRANSFORMER AND RESTORED POWER AT 22:15 TIM MCCOY/ ISO 37820007B00121/ COD 1/ VER/BOW
13989 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2021-06-02 14:08 | 2021-06-02 19:57 | 1 | 349 | 4659551 | 349 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug/crew reqd. Released by crew 078S04 Installed power temp. Ticket complete.//DAE 1000057999//
13990 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2019-06-20 12:21 | 2019-06-20 18:10 | 1 | 349 | 4555481 | 349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO POWER ON SIDE TAP, WILL BE CHECKING LOOP BURNED INTO AT POLE 147B168 WILL CLIMB AND MAKE REPAIRS COMPLETED R RAY
13991 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-06-19 09:11 | 2018-06-19 15:00 | 1 | 349 | 4619991 | 349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMRBAD 10KVA 7200BAD 10KVA 7200 Released by crew 077S01 power restored @ 15:00 JKL/ ISO 37840384000136/ COD 1
13992 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-02-16 07:19 | 2011-02-16 09:15 | 3 | 116 | 58029-1 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK TALL BROKE OFF FROM TIP REPLACED 6-T FUSE JOB IS COMP // COD-3 ISO TF 39831147D10441 // VER/HFP L3/HFP IDC XXXX
13993 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-04-19 08:55 | 2008-04-19 10:51 | 3 | 116 | 52270-1 | 348 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | HOT LEG ON XFORMER BURNT INTO RELEASED BY CREW 078H04//3002001//VER/CRB IDC XXXX
13994 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-06-15 21:37 | 2011-06-16 03:25 | 1 | 348 | 4324911 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFORM POLE COMPLETLY COVERED WITH TREES AND VINES CANNOT SEE XFORM OR CUTOUT NEED LINE CREW BUCKET AND TREE CREW BUCKET RELEASED BY CREW 078S04/ TREETRIMMERS CUTTING @ 2:33 BROKEN CUTOUT VER/ARN IDC XXXX
13995 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-03-28 11:33 | 2010-03-28 14:27 | 2 | 174 | 55168-1 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 LINE CUTOUT BAD ON POLE 37830223B00015 AND XFMR FUSE ALSO WAS BLOWN RESTORED FOR NOW WILL HAVE CREW RETURN TOMORROW TO REPLACE LINE CUTOUT COD-2 VER/HFP L3/HFP AJB
13996 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-03-12 20:44 | 2020-03-12 22:40 | 3 | 116 | 4473051 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 19.9 cutout on pole 117-384. No trucks, crew required. Lifted tap on 38830117B00381 to isolate, Grounded and tagged to Bobby Tackett at pole 38830117B00381. (Transmission overhead) Released by crew 078S02,repairs made all cust restored @ 2240 please close ticket thanks.bt
13997 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-04-26 13:26 | 2021-04-26 16:20 | 2 | 174 | 4481241 | 348 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Repaired a bad secondary connection.
13998 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-04-07 17:36 | 2022-04-07 20:30 | 2 | 174 | 4738541 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | b phase 80t lf @ 1024-4 open. 1024-248 b phase tie wire broke. wire off pin and laying on arm. trk ok Released by crew 078S07 crew on site FETR 21:00
13999 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2019-07-14 18:07 | 2019-07-14 23:55 | 1 | 348 | 4707691 | 348 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse out on pole 37830048A31360. will refuse, will need a 100KVA xfmr 7200 to 120-208. 3 cutouts & arrestors ,material handler ,2 linemen & a NE//cod 1//ISO
14000 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-08-08 21:02 | 2008-08-09 02:50 | 1 | 348 | 50425-1 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3403003// HAD TO OPEN LINE FUSE TO REPLACE TRANSFORMER. WILL HAVE OFF FOR ABOUT ONE AND A HALF HOURS // COD-17 // SEE OUTAGE 50410-1 // VER/LDA IDCC CNT17 XXXX
14001 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-08-07 17:03 | 2010-08-07 18:30 | 4 | 87 | 51126-1 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 1730 // CUTOUT DOOR FAILED AND WAS TRACKING. REPLACED CUTOUT. SH//COD 4// VER/DBM
14002 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-05-04 23:33 | 2012-05-05 00:31 | 6 | 58 | 4745371 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 195 -102 (NO OUTAGE UPON ARRIVAL) ISOLATED CUTOUT (1 CUST OUT OF POWER) PUT OUT FIRE, TOP OF POLE 2/3 GONE, NEED CREW TO LOWER CONDUCTORS AND TRANSFORMER.. BLR RELEASED BY CREW 078H07/CREW ON SITE/WILL NEED TO OPEN FUSE ON POLE#195-11 FOR REPAIRS/FETR 0200/OPENED FUSE AT 2333/REPAIRS MADE AND POWER RESTORED 0031 5-5-12/PLEASE CLOSE TICKET/THANKS/VEM //COD 1 + 5// IDCC PN102, CNT1959 XXXX
14003 | South Williamson | 3411401 | DEWEY | INEZ | 2022-06-26 14:06 | 2022-06-26 17:00 | 2 | 174 | 4323611 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral burned into on secondary//making repairs//going to have to replace span//several bad places//had to replace secondary and service drop//restored at 17:00//complete//em
14004 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2011-03-06 11:52 | 2011-03-06 12:50 | 6 | 58 | 50568-1 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39052535 // BROKE CUTOUT REPAIRING NOW. VER/HFP L3/HFP IDCC CDC92 XXXX
14005 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-01-21 19:53 | 2020-01-21 22:47 | 2 | 174 | 4327041 | 348 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVE-IN FROZEN OUT ON XFR POLE.MADE NECESSARY REPAIRS,ALL OK AFTERWARDS L3/HFP
14006 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-02-03 17:38 | 2014-02-03 19:05 | 4 | 87 | 4345361 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL CONNECTION BAD ON XFMR POLE. OPENED XFMR ON 834-37 @ 17:38. RE-WORKED XFMR CONNECTIONS AND CLOSED XFMR @ 19:05. SH VER/HFP L3/HFP
14007 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-01-24 08:56 | 2009-01-24 09:54 | 6 | 58 | 59576-1 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED SECTIONALIZER SO CREWS COULD SAFELY MAKE REPAIRS ON TICKET 59564-1 3411902 - WIRE BURN-INTO. POLE 143-15 OPEN LINE AT 08:56 VER/ARN L3/KEP
14008 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-11-14 16:18 | 2012-11-14 17:45 | 4 | 87 | 4398061 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLEW AND THE GATE DID NOT DROP OUT AND THE FUSE CONTINUED TO BURN. I CUT THE SERVICE LOOSE THAT WENT TO THE AFFECTED HOUSE AND REFUSED THE XFMR AND CHECKED THE VOLTAGE . THE POWER WAS OFF WHEN I ARRIVED BUT I HAD TO OPEN THE CUTOUT GATE. M.D.I. 11-14-12 VER/KEP IDC XXXX
14009 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-07-01 17:16 | 2015-07-01 20:10 | 2 | 174 | 4706321 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE WILL CHANGE/// OPENED LINE FUSE @ 19:44 AND ALSO REPLACED BROKEN CUTOUT ON POLE # 1057-76 AND CHANGED XFM CUTOUT/// RESTORED SERVICE @ 20:10 ON XFM AND LINE FUSE// VER/ ADH
14010 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-08-07 08:09 | 2015-08-07 09:36 | 4 | 87 | 4108141 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON TRANSFORMER. ISO 38831108C00056/ COD 4/ VER/BOW
14011 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-09-20 09:30 | 2013-09-20 12:24 | 2 | 174 | 4869741 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PATROLLING LINE AND FUSE BLEW WHILE I WAS PATROLLING. TIM MCCOY RELEASED BY CREW 074H10PATROLLING LINE AND FUSE BLEW WHILE I WAS PATROLLING.// FOUND CABLE GOING TO GROUND AT PAD 72-C-506 I HAVE THE TROUBLE ISOLATED AND TAGGED WILL HAVE TO MAKE SOME REPAIRS CUSTOMER RESTORED AT 12:24 TIM MCCOY//MAP DESC ALREADY MADEPATROLLING LINE AND FUSE BLEW WHILE I WAS PATROLLING.// VER/CRB L/3 CRB
14012 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-09-08 07:44 | 2020-09-08 08:42 | 6 | 58 | 4440231 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT/////////REPLACED XFR CUTOUT&RESTORED POWER,ALL OK AFTERWARDS
14013 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-01-16 07:24 | 2019-01-16 08:51 | 4 | 87 | 4677241 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 222b14 broke cutout L3/HFP
14014 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2020-09-25 09:38 | 2020-09-25 11:05 | 4 | 87 | 4494591 | 348 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | stirrup burnt into repaired and back on at 11:05
14015 | Paintsville | 3410602 | E.PRESTON | LANCER | 2018-09-10 16:49 | 2018-09-10 18:45 | 3 | 116 | 4078731 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 kva on pole # 38830955D00391 is bad serves a housr that is disconnected. massey wants to wait till tomorrow to replace.//SENT TO LINE DEPT
14016 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2021-06-16 08:52 | 2021-06-16 14:40 | 1 | 348 | 4757941 | 348 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | secondary hot leg and neutral burnt into, mid span in a tree. no truck power fully restored at 14:40
14017 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-01-22 04:27 | 2016-01-22 10:15 | 1 | 348 | 4639691 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUST//WILL DISPATCH @ START OF SHIFT// REPLACED SERVICE DROP. ONLY ONE CUSTOMER OUT// VER/ ADH
14018 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-12-12 11:48 | 2008-12-12 13:15 | 4 | 87 | 57644-1 | 348 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED TO RED FROZE OUT//3310501 VER/KEP L3/KEP IDCC FEC44 XXXX
14019 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-12-18 09:47 | 2018-12-18 15:35 | 1 | 348 | 4576731 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10kv 7200 xfm. Will need big bucket to replace. L3/HFP
14020 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-12-27 14:24 | 2020-12-27 20:12 | 1 | 348 | 4828191 | 348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Bare spot in hotleg had burnt service neutral n2 at sec. pole 900-63. I de-energived service at pole @ 10:25 and made repairs to service. Restored @20:12 and customer now has good voltage
14021 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-08-09 11:48 | 2020-08-09 16:35 | 2 | 287 | 4303521 | 347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 by truck Released by crew 078H03 Released by crew 078H07 // had to lift tap and de energize 1 additional customer opened at 1535 closed at 1635
14022 | Hazard | 3303902 | LESLIE | WOOTON | 2009-06-11 08:28 | 2009-06-11 14:15 | 1 | 347 | 58812-1 | 347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 30247030 //RELEASED BY CREW 077S01WR # 30247030 // COMP.W.MELTON//COD 1// VER/DBM IDC XXXX
14023 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-12-21 05:58 | 2018-12-21 11:45 | 1 | 347 | 4584841 | 347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad 19.9 deadend insulator on pole 169-37.will need line crew to make repairs..non-truck access..restored L3/HFP
14024 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-08-28 09:13 | 2012-08-28 15:00 | 1 | 347 | 4979571 | 347 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND SERVICE POWER TEMP INSTALLED. WILL REPLACE THE WHOLE SERVICE ON TUESDAY, 9-4-12 // PLACED IN AED DATABASE VER/HFP L3/HFP IDC XXXX
14025 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-11-13 08:37 | 2019-11-13 14:24 | 1 | 347 | 4029871 | 347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15kva 7200 xfmr on pole 924-51. This is no truck approach. Have contaced crew and Robie Blair will be coming to replace//Repaced xfmr and restored power @ 14:24 L3/HFP
14026 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-10-06 05:21 | 2014-10-06 11:08 | 1 | 347 | 4556201 | 347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT START TIME, BAD 19.9 KV CUTOUT AND ARRESTER, RELEASED BY CREW 077S04// SERVICER OPENING TAP ON POLE 343-A-44 TO MAKE REPAIRS//WILL WORK AT START TIME, BAD 19.9 KV CUTOUT AND ARRESTER, RELEASED BY CREW 077S04 OPEN AT 1023 CLOSED AT 1108 RELEASED BY CREW 077H04 // 1 OUT INITALLY THEN OPENED TAP @ 1023 INTERRUPTING 2 MORE CUSTOMERS /// SEE DUP H4556201 FOR ADDITIONAL INTERRUPTION OF 2 CUST VER/HFP L3/HFP
14027 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-05-14 20:54 | 2011-05-15 02:40 | 1 | 346 | 4094661 | 346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA CSP(7200) XFMR ON POLE 936-29//FEEDS VACANT TRAILER BUT CUSTOMER WOULD LIKE CHANGED TONIGHT BECAUSE HE HAS FREEZERS INSIDE// TRUCK APPROACH// NEED 15KVA XFMR AND CUTOUT//JOEY REED WILL BE COMING TO CHANGE OUT// RELEASED BY CREW 079S01. CHANGED TRANSFORMER AND REPAIRED SERVICE.CUSTOMER RESTORED EXCEPT FOR DD LIGHT. 100 FT OF DUPLEX BURNED UP. WILL REPLACE THIS WEEK. SOMEONE DAMAGED SERVICE PRUNING TREE. VER/PDP
14028 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2019-01-31 18:40 | 2019-01-31 21:33 | 2 | 173 | 4744991 | 346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPAN OF WIRE DOWN/// R VIRGIN AND CREW ENROUTEno crew required 6a copper trucks okno crew required 6a copper trucks ok Released by crew 078S03---crew on site---repaired 1 span 6A Open wire---pwr restored @ 21:33---tbl tkt comp---rmv
14029 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-04-23 11:14 | 2015-04-23 17:00 | 1 | 346 | 4358481 | 346 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CONNECTION BURNED IN TWO // REPLACED 4/3 S/D WITH 2/3// VER/ ADH
14030 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2020-09-26 08:42 | 2020-09-26 11:35 | 2 | 173 | 4497731 | 346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke @ 37820243B00007. Changed cutout and restored @ 11:35. Send copy to tech due to deadend bells broken down.
14031 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-05-28 02:56 | 2018-05-28 05:49 | 2 | 173 | 4507521 | 346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
14032 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2020-05-23 21:21 | 2020-05-24 00:14 | 2 | 173 | 4894251 | 346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service burnt into, got it repaired and power restored at 00:14
14033 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-08-29 11:44 | 2010-08-29 17:30 | 1 | 346 | 61635-1 | 346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 19-01 NEED 25KVA NO TRUCKS NEED FLAGMAN RELEASED BY CREW 078S08 VER/KEP L3/KEP IDC XXXX
14034 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-08-22 14:17 | 2018-08-22 17:10 | 2 | 173 | 4989451 | 346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken transformer fuse L3/HFP
14035 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2017-12-28 10:19 | 2017-12-28 13:41 | 3 | 202 | 4684891 | 346 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | crew req, have hot leg on 1/0 sec, burnted into, diffuctly loc, runs up hill side, will need to bring small srv bucket, to get up driveway Released by crew 078S06/crew on site/open xfmr at 1229/FETR 1315/vem/repairs made and power restored to all cust 1341/please close ticket/thanks/vem
14036 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-05-23 08:07 | 2014-05-23 11:00 | 2 | 173 | 4743851 | 346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BURNT UP CUTOUT DOOR FROM BAD FUSE /// COD-2 ISO TF 38830015B02010 VER/HFP L3/HFP
14037 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-10-22 11:09 | 2019-10-22 16:54 | 1 | 345 | 4181061 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR
14038 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2011-01-21 08:30 | 2011-01-21 10:25 | 3 | 115 | 63257-1 | 345 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN FAILED AT TRANSFORMER.. REPLACED ALL CONNECTIONS AT TRANSFORMER, ALL WORK COMPLETE / GXJ COD-3 37830160000048 VER/HFP L3/HFP IDC XXXX
14039 | Pikeville | 3421001 | BREAKS | CITY | 2019-01-21 09:45 | 2019-01-21 11:40 | 3 | 115 | 4699371 | 345 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open @ xfm on pole 220-113 will make repairs/// Repairs made and restored service @ 11:40
14040 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-11-07 10:30 | 2021-11-07 12:25 | 3 | 115 | 4064141 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | servicer on site replacing broken cutout ,,replaced complete
14041 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-11-29 21:10 | 2015-11-29 23:05 | 3 | 115 | 4493051 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED XFMR @21:50 TO CHG CUTOUT & TBRACKET .HAVE MATERIAL ON THE WAY.COMPLETED VER/TOM//L3/TOM
14042 | South Williamson | 3411401 | DEWEY | INEZ | 2020-06-03 16:30 | 2020-06-03 18:25 | 3 | 115 | 4950941 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout on 743-C-2, opened hot tap on 743-C-1 to isolate trbl at .made repairs,restored power at 18:25//COD 3 FROM BEGINNING
14043 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-04-05 14:25 | 2015-04-05 16:20 | 3 | 115 | 4278081 | 345 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE A SERVE END HAS BURNED LOOSE ON ONE HOT LEG ON SERVICE DROP AT TRANS. POLE. I AM GOING TOREPLACE CONNECTION. IT WAS ACTUALLY A SQUEZZE-ON THAT GOT HOT AND MELTED A HOT LEG IN SERVICE DROP INTO. I REPAIRED SERVICE./ ISO 37820145000049/ COD 3
14044 | Hazard | 3301101 | CHAVIES | CHAVIES | 2021-02-09 13:00 | 2021-02-09 14:55 | 3 | 115 | 4951941 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | red to red burnt out. opened xfm 172-337 from 14:35 to 14:55 to make repaires
14045 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-05-09 18:25 | 2015-05-09 20:20 | 3 | 115 | 4406901 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT AND BAD R/W//MADE MD FOR TAP ON POLE 134-143 TO BE UNDER LINE FUSE/ADH//COD3/EMAILED ROW/ADH// VER/ ADH
14046 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-06-08 14:41 | 2017-06-08 16:36 | 3 | 115 | 4924021 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TRANS FUSE BLOWN ON 32A48 1/0 SECONDARY NUUETRAL BROKEN ALLOWING WIRE TO SAG DOWN INTO OPEN WIRE SECONNDARIES REPAIRED SECONDARY NUETRAL RESTORED POWER AT 16:36 VER/CRB
14047 | Paintsville | 3401802 | INDEX | HOSPITAL | 2012-05-01 15:36 | 2012-05-01 16:45 | 5 | 69 | 4731481 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN.RE FUSED. ///VER/CRB L/3 CRB IDC XXXX
14048 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-08-30 10:36 | 2021-08-30 16:21 | 1 | 345 | 4175511 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout at 285-99,Will make repairs and restore service..Restored @ 16:21.
14049 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-01-14 07:25 | 2013-01-14 09:20 | 3 | 115 | 4601781 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, CUTOUT BROKE/OPENED FUSE ON POLE#26 TO ISOLATE AT XFMR FUSE OUT, CUTOUT BROKE. OPENED LINE FUSE ON POLE 134-26 AT 08:55, REPLACED CUTOUT, CLOSED FUSE BACK AT 09:20. ALL POWER RESTORED COD-3 ON TRANS AND 1 MORE ON FUSE VER/KEP IDC XXXX
14050 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2011-09-06 11:35 | 2011-09-06 13:30 | 3 | 115 | 4833801 | 345 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | FUSE BROKE ON CENTER PHASE XFMER///REFUSED @ 13:30///COMPLETE BR //// COD-3 ISO 38830785D20590 VER/HFP L3/HFP IDC XXXX
14051 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2017-11-01 11:06 | 2017-11-01 12:15 | 5 | 69 | 4522301 | 345 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 138-139 1/0 SERVICE BURNT INTO REPAIRED
14052 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2019-11-13 23:19 | 2019-11-14 01:14 | 3 | 115 | 4032361 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Power ok fuse 6T broke
14053 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-02-09 07:05 | 2018-02-09 12:50 | 1 | 345 | 4819591 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout broke on 655-5580. Replaced cutout and restored @ 12:50. One customer was out. sh
14054 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-06-19 08:00 | 2015-06-19 13:45 | 1 | 345 | 4607961 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 35-6 STRAIGHT LINE PRIMARY POLE ROTTED OFF AT GROUND LEVEL AND FELL OVER. OPENED HOT-LINE CLAMP ON 810-422 TO ISOLATE AT 8:00 OUTAGING ONE METER (656780915). TEMP GROUND AND TAG PLACED TO STEVE HALL ON SAME POLE. OOREPLACED TAG WITH DDC TAGOO 811 NOTIFIED @ 8:20. RELEASED BY CREW 076S02/// I HAVE MADE REPAIRS AND RESTORED POWER AT 13:45 TIM MCCOY RELEASED BY CREW 074H10 VER/KEP
14055 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-04-12 14:37 | 2018-04-12 16:32 | 3 | 115 | 4215211 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broken on 39831148A00300, changed out and all power restored at 16:32/ ISO 39831148A00300/ COD 3
14056 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-10-08 09:50 | 2008-10-08 11:45 | 3 | 115 | 54155-1 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WE HAVE LINE FUSE OUT ON POLE 328-167.GOT LINE FUSE BACK IN AT 11:45 POLE 328-144 WILL NEED R/W CREW TO CUT AROUND XFMR POLE.//3311401//VER/CRB IDCC PN331 XXXX
14057 | Pikeville | 3407103 | TOPMOST | KITE | 2016-11-30 05:05 | 2016-11-30 10:50 | 1 | 345 | 4147281 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED LINE CUTOUT POLE 208 AND XFMR CUTOUT AND ARRESTER POLE 209, ALL WORK COMPLETE / GXJ 37830209000208 VER/AWD L3/HFP XXXHFP
14058 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-03-04 11:40 | 2020-03-04 12:49 | 5 | 69 | 4451611 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Bad lightning arrestor on pole 248-293. Power restored at 12:49//MADE A DAE ON L/A
14059 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-02-27 04:22 | 2013-02-27 10:07 | 1 | 345 | 4857051 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK AT REGULAR WORKTIME // JEH ON SITE FETR 10:30/ BRKN C/O // NO TRUCK// REPAIRS COMPLETE POWER RESTORED @ 10:07 JEH ///VER/CRB L/3 CRB IDC XXXX
14060 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-06-23 18:36 | 2019-06-24 00:21 | 1 | 345 | 4571671 | 345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | tree in primary will need manual R/W crew. bad 15 kva xfme will need forman 3 linemen 15 kva 7200to 120/240 . & manual tree crew to cut tree off primary Released by crew 074S04//OUTAGE STARTED @ 1836
14061 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-06-20 21:54 | 2014-06-20 23:20 | 4 | 86 | 4131501 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON 37820098A00121// WILL CHANGE// CUTOUT CHANGED// POWER RESTORED 23:20//6-20-14//COD 4// VER/DBM
14062 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-03-07 21:21 | 2017-03-08 03:05 | 1 | 344 | 4532821 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER CUTOUT DOOR BURNED OUT ON POLE 830-22///OLD CUTOUT AND DONT HAVE DOOR TO FIT GOING TO REPLACE CUT///CUTOUT REPLACED///CLOSED IN AT 03:05///COMPLETE BR//COD 1
14063 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-04-08 03:46 | 2016-04-08 09:30 | 1 | 344 | 4070111 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT START TIME 4-8-16/NO CREW REQUIRED CUTOUT DOOR VER/AWD
14064 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-03-09 09:29 | 2011-03-09 15:13 | 1 | 344 | 52038-1 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 167KVA RELEASED BY CREW 077S01 VER/KEP IDCC PN299 XXXX
14065 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-07-30 11:26 | 2021-07-30 14:18 | 2 | 172 | 4982801 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout failed..replaced.restored..
14066 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-10-01 07:41 | 2009-10-01 13:25 | 1 | 344 | 60702-1 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL INVESTIGATE1/0 PRIM COND DOWN,NEED CREW,WIRE.CUTOUT BURNED UP AT FUSE LOCATION ALSO1/0 PRIM COND DOWN,NEED CREW,WIRE.CUTOUT BURNED UP AT FUSE LOCATION ALSO RELEASED BY CREW 074S06 VER/KEP L3/KEP IDC XXXX
14067 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-06-13 14:08 | 2017-06-13 17:00 | 2 | 172 | 4959681 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RESAGGED OPEN WIRE XFR FUSE BACK IN @ 17:00 COMPLETE VER/CRB
14068 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-01-23 18:23 | 2013-01-23 21:15 | 2 | 172 | 4734861 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WE MAY HAVE BAD UNDERGROUND OR XFMR//// REFUSED SHE BLEW. BAD 50KV XFMR, 19.9. AIKMAN GONE TO GET BUCKET AND XFMR.///// CHANGED XFMR, POWER RESTORED! ///VER/CRB L/3 CRB IDC XXXX
14069 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-04-07 08:46 | 2020-04-07 14:30 | 1 | 344 | 4566321 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva 19.9 xfmr on pole 841-a-42///feeds railroad signal//dry enough that can get bucket to pole// Released by crew 079S01
14070 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-11-15 14:47 | 2013-11-15 17:39 | 2 | 172 | 4041851 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 CUST OUT INITIALLY // OPENED XFMR ON POLE 1039-13 @ 16:45 (4 CUST - IN H4041851) CLOSED BACK IN @ 17:39 SECONDARY BURNED DOWN GOING TO POLE 1039-62 . VER/HFP L3/HFP
14071 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-07-11 17:43 | 2013-07-11 23:27 | 1 | 344 | 4509501 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/CRB L/3 CRB IDC XXXX
14072 | Paintsville | 3401101 | FALCON | FALC-OILS | 2011-01-29 17:18 | 2011-01-29 20:10 | 2 | 172 | 52085-1 | 344 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END FROZEN AND LOOSENED UP...REPLACED 3 SERVE ENDS..//VER/CRB IDCC MCCNI XXXX
14073 | Pikeville | 3401001 | ELWOOD | DORTON | 2010-04-16 13:24 | 2010-04-16 14:50 | 4 | 86 | 63819-1 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOKS LIKE HOTTAP HAS BURNED OFF BELL. I AM GOING TO REPLACE HOT TAP. I REPLACED HOT TAP AND RESTORED POWER TO CUSTOMER AT 14:50//COD 2// VER/DBM IDC XXXX
14074 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-08-16 10:04 | 2012-08-16 11:30 | 4 | 86 | 4943081 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED FUSE. FUSE LINK WAS BROKE. ONLY 1 CUSTOMER OUT VER/KEP IDC XXXX
14075 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2022-01-02 11:18 | 2022-01-02 14:10 | 2 | 172 | 4260681 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Opened transformer on pole 329-41 to make repairs. Closed back in at 14:10.
14076 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-05-19 08:20 | 2013-05-19 09:46 | 4 | 86 | 4132841 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK 6T NO CREW REQUIRED ///VER/CRB L/3 CRB IDC XXXX
14077 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-06-10 18:17 | 2015-06-10 19:43 | 4 | 86 | 4551311 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR FUSE BLOWN/// FOUND BAD ARRESTOR ON XFMR, TOOK ARRESTOR OFF LINE, REFUSED XFMR POWER RESTORED.// SEND TO DOUG CHRISTIAN TO MAKE JOB TO REPLACE./ENTERED AED/ADH// VER/ ADH
14078 | Hazard | 3303902 | LESLIE | WOOTON | 2009-12-13 17:14 | 2009-12-13 18:40 | 4 | 86 | 52998-1 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9 CUTOUT VER/KEP L3/KEP
14079 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2021-04-06 07:53 | 2021-04-06 10:45 | 2 | 172 | 4422001 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25kva transformer bad on pole 38820965D00025 Released by crew 079S03; CREW ON SITE. CHANGED X-FMR, ALSO INSTALLED NEW CUTOUT AND FIBERGLASS BKT. ON AT 10:45
14080 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2013-02-16 12:38 | 2013-02-16 15:30 | 2 | 172 | 4823791 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 738-70.CHG CUTOUT VER/KEP IDC XXXX
14081 | Cannonsburg | 3001401 | LOUISA | CITY | 2009-10-12 11:49 | 2009-10-12 13:15 | 4 | 86 | 58424-1 | 344 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | STS WR# 32161639 //FUSE BROKE//COD 4// VER/DBM// L3/BOP IDC XXXX
14082 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-07-13 12:41 | 2012-07-13 18:25 | 1 | 344 | 4711981 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT, IT WAS BROKEN. APR CLOSE TICKET COD-1 ISO 38830623000028
14083 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-04-10 19:34 | 2022-04-10 21:00 | 4 | 86 | 4745711 | 344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKEN ON 851-345. CHANGING. BACK ON AT 21:00
14084 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-01-07 20:48 | 2009-01-07 23:40 | 2 | 172 | 53091-1 | 344 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP TRANSFOMER SECONDARY SIDE TWO CUSTOMER SAME PROBLEM. WILL HAVE TO CUT TREES TO CLIMB POLE,ONE CUSTOMER COMPLAIN ABOUT SATELLITE RECEIVER IDCC CNT1 XXXX
14085 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-07-22 17:16 | 2022-07-22 18:05 | 7 | 49 | 4548401 | 343 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer is leaking on pole 332-D-152.. will need line vrew to change out 50 kva 7200, cutout complete Released by crew 077S11 Off @ 1716 On @ 1805
14086 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-07-31 07:47 | 2009-07-31 13:30 | 1 | 343 | 61399-1 | 343 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF, WILL NEED POLE TOP FIBERGLASS EXTENSION, CUTOUT AND ARRESTOR, BIG BUCKET, ONLY 1 CUST OUT AT THIS TIME RELEASED BY CREW 077S02 OPENED OCR ON P # 249 / 346 TO CHANGE BAD CUTOUT ON P # 249 / 79 LINE CUTOUT OPENED AT 1215 AND RESTORED AT 1224 , LINE FUSE ON P #249 / 79 LEFT OPENED TO REPAIR P # 249 / 278 REPAIRS MADE AND POWER RESTORED AT 1330 RESTORING POWER TO ALL CUSTOMERS JKC IDC SEE ALSO 66524-1 XXXX
14087 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-12-11 09:48 | 2009-12-11 15:31 | 1 | 343 | 63309-1 | 343 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NET. BROKE AT XFMR// VER/DBM
14088 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2022-06-10 18:02 | 2022-06-10 23:45 | 1 | 343 | 4055631 | 343 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug crew req-ds061022 Released by crew 078S01/ UG fixed/ xfmr on 213-9001 restored @ 2345/ please close ticket/ MLH/ Transformer that was out is on pole 38830213009001 and it had 1 underground customer
14089 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-12-30 10:13 | 2019-12-30 15:56 | 1 | 343 | 4194931 | 343 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | One leg of customers ug burned up in the meter base, Crew required. Need power temp. Bad leg already isolated on pole Released by crew 078H04/arived RM repairs made back on at 15:56 please close tic RM
14090 | Whitesburg | 3401301 | FLEMING | NEON | 2011-04-12 09:32 | 2011-04-12 15:15 | 1 | 343 | 55673-1 | 343 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR 39534782 // BAD UNDERGROUND SERVICE NEED CREW TO CHANGE OUT RELEASED BY CREW 077S12 RELEASED BY CREW 075H01STS WR 39534782 // BAD UNDERGROUND SERVICE NEED CREW TO CHANGE OUT RELEASED BY CREW 077S12 SERVICE. REPLACED BAD URD. SERVICE WITH TEMP. OVERHEAD SERVICE. WILL CREATE JOB TO SEND TO TECH. DUPLICATING FOR TR OUTAGE SEE H1150465-1 VER/HFP L3/HFP IDC DCMT XXXX
14091 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-04-28 04:36 | 2008-04-28 06:30 | 3 | 114 | 54758-1 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000701// FUSE LINK ROTTEN AND BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOCATION//VER/CRB IDC XXXX
14092 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-09-22 19:18 | 2014-09-23 01:00 | 1 | 342 | 4520721 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 BAD 10 KVA XFMR IN BANK,LOOKS AS IF ANOTHER XFMR NEEDS CHG..HAS BEEN PUMPING OIL.CHG OUT TWO 10 KVA XFMRS.REPLACED WITH A 25KVA AND A 15 KVA.. VER/DKG L3/DKG
14093 | Hazard | 3309302 | VICCO | JEFF | 2020-08-20 18:33 | 2020-08-21 00:15 | 1 | 342 | 4352151 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout bad on pole 347-28. opened rec on pole 347-304 from 23:51 to 00:15 to saftely replace cutout.
14094 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2013-10-08 08:06 | 2013-10-08 10:00 | 3 | 114 | 4920631 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT SERV TO CHANGE,REPAIRS MADE ALL CUST RESTORED @1000 PLEASE CLOSE TICKET THANKS.BT VER/CRB L/3 CRB IDC XXXX
14095 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-05-22 07:03 | 2014-05-22 09:54 | 2 | 171 | 4737011 | 342 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | WILL CHECK FOR PROBLEMS// C/L FUSE BAD// REPAIRS MADE /// POWER RESTORED @ 09:54 // 5-22-14//COD 2// VER/DBM
14096 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-02-13 17:18 | 2017-02-13 23:00 | 1 | 342 | 4394731 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 079H03 TRANS CUTOUT BAD ON 12-26 REPLACED CUTOUT ARRESTO AND BRACKET RESTORED POWER AT 23:00/ ISO 37830312000026/ COD 1/ VER/BOW L3/HFP XXXHFP
14097 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2016-09-30 08:18 | 2016-09-30 14:00 | 1 | 342 | 4947021 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | ***SEE 4947021*** 480V METER BLOWN OUT OF METERBASE POLE 39830878D34679 (1 CUST ORIGINALLY) SERVICE OUTAGE, NEED TO GET METER ELECTRICAN TO LOOK AT THIS AND SEE WHAT WE NEED TO DO/ ISO 39830878D34703/ COD 2/ OPENED LINE FUSE 39830878D34703 (1 ADD CUST) @1120 HAVE ALL REPAIRS MADED AND HAVE CHECK EVERYTHING OUT, ALL IS GOOD AT THIS LOC BY AMG, 39830878D34703 TIME ON WAS 1400/ DUPLICATE IN HOIS/ VER/VBOW
14098 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-02-02 05:51 | 2019-02-02 07:45 | 3 | 114 | 4748131 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | tried to call customer--no answer..broken xfmr fuse.chging L3/HFP
14099 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-01-16 09:27 | 2008-01-16 11:21 | 3 | 114 | 57091-1 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411802//SEC LEAD BURNED OUT OF XFR,WILL OPEN BANK AND REPAIRMADE NECESSARY REPAIRS TO BURNED-OFF LEAD,RESTORED,ALL OK AFTERWARDS// COD 3 ISO/FLT - 38821132000029// VER/TOM IDC XXXX
14100 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2017-08-08 10:38 | 2017-08-08 16:20 | 1 | 342 | 4239481 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG OUT GETS 107 VOLTS UTILL LOAD IS PUT ON IT THEN GOES TO ZERO NEEDS AUTO-XFM FOR TONIGHT RELEASED BY CREW 078H01/ 1620/ INSTAL POWER TEMP 1 CUST PLEASE CLOSE TICKET THANKS.BT/ ISO 39831147C24638/ COD 1/ VER/BOW
14101 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2020-12-31 16:21 | 2020-12-31 17:18 | 6 | 57 | 4839431 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link pulled apart inside cutout door causing outage. I refused and restored @17:18
14102 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-02-07 05:02 | 2020-02-07 07:53 | 2 | 171 | 4373901 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401002/gaj/0502/all out tried calling cust no answer disp 3670 S Tackett,Customer has a broke cutout will have to climb pole to make repairs,Got the cutout changed and restored service at 07:53.
14103 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-07-27 21:42 | 2008-07-28 00:33 | 2 | 171 | 60926-1 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3202202// TRANSF BAD VER/JHM IDCC CNT1 XXXX
14104 | Paintsville | 3401101 | FALCON | FALC-OILS | 2020-10-05 12:49 | 2020-10-05 15:40 | 2 | 171 | 4527741 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 15:40. sh
14105 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-09-12 10:51 | 2020-09-12 12:45 | 3 | 114 | 4454311 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans out on 818-A2-66 due to failed fuse.restored at 12:45.
14106 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2019-07-22 09:00 | 2019-07-22 11:51 | 2 | 171 | 4756421 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830808B40234 SHOWING A SWITCH ON MAP BUT IT IS A LINE FUSELine fuse blown on 808-B4-234 due to bad xfmr cutout on pole 808-179.We will be making repairs///Line fuse blown on 808-B4-234 due to bad xfmr cutout on pole 808-179.We will be making repairs///Replaced cutout and restored power @ 11:51
14107 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2010-11-26 00:46 | 2010-11-26 03:37 | 2 | 171 | 59694-1 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD- CUT-OUT GATE IS LOCKED TRYING TO FIND SOM-ONE WITH KEY CALL BOB FOR REYNOLDS TO HELP//COD 2//WHEN ATTEMPTING TO RESTORE, LINE FUSE UPSTREAM WENT OUT (NEW ORDER CREATED) // VER/DBM IDC XXXX
14108 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2017-12-11 04:36 | 2017-12-11 06:30 | 3 | 114 | 4638161 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
14109 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-02-21 19:14 | 2013-02-21 22:05 | 2 | 171 | 4838581 | 342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3 PHASE TRANSFORMER Y DELTA 120/240 BANK, SUSPECT B PHASE TRANSFORMER BAD BECAUSE A & B PHASE TRANSFORMERS HAD BEEN ISOLATED FROM BANK, C PHASE ACTIVE TRANSFORMER FAILED , TRIMMED TREES AND REWIRED A PHASE TRANSFORMER AND MOVED LOAD TO A PHASE . ALL WORK COMPLETE / GXJ//COD 2// VER/DBM IDC XXXX
14110 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2013-10-17 17:19 | 2013-10-17 23:00 | 1 | 341 | 4944311 | 341 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHG CUTOUT.. VER/SEF
14111 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-07-20 09:40 | 2015-07-20 15:21 | 1 | 341 | 4915401 | 341 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | C/L FUSE BAD // REPAIRES MADE // POWER RESTORED @ 15:21 VER/CRB
14112 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-06-12 10:17 | 2008-06-12 15:57 | 1 | 340 | 63032-1 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3110902// FOUND A BAD 5 KVA TRANSFORMER, NEED CREW TO CHANGE, CAN GET TRUCKS TO IT, ALSO, NEED TO INSTALL NEW RISER, SINGLE BUSHING 7200 VOLT, 120/240 STS WR# 24754885/CREW ON SITE/FETR1700/XFMR CHANGED POWER RESTORED/1557/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP IDC XXXX
14113 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-10-30 03:05 | 2022-10-30 08:45 | 1 | 340 | 4078031 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Dispatched in accordance with KYPCo Late Night Callout Guidelines./no crew bad hot tap
14114 | Hazard | 3308001 | JACKSON | S.JACKSON | 2022-01-14 09:45 | 2022-01-14 15:25 | 1 | 340 | 4345751 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | got bad 25 kva 7200 two bushing primary transformer Released by crew 077S05 replaced xfmr restored power at 15:25..
14115 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2011-03-19 00:45 | 2011-03-19 02:10 | 4 | 85 | 55737-1 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE GOINGTO CHANGE CUTOUT BROKE GOINGTO CHANGE HAVE CUTOUT CHANGED COD-4 ISO TF 38830762000028 VER/HFP L3/HFP IDC XXXX
14116 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-08-26 11:15 | 2013-08-26 14:05 | 2 | 170 | 4707791 | 340 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | REPLACED B PHASE CUTOUT VER/CRB L/3 CRB IDC XXXX
14117 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-05-31 08:00 | 2017-05-31 13:40 | 1 | 340 | 4884651 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 CU PRIMARY BROKE 3 FT FROM DEADEND ON FUSE POLE 38830925000035. I OPENED LINE FUSE - NO GROUNDS PLACED. NEED BUCKET AND FLAGGERS. LCS NOTIFIED AND IS ENROUTE WITH CREW.// CREW ON SITE REPAIRING// REPAIRS COMPLETE, RESTORED AT 13:40
14118 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-06-20 20:40 | 2016-06-20 23:30 | 2 | 170 | 4393191 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT, MANUAL, NEED 1 MAN TO ASSIST.... OPENED LOOP ON 248-A-3 @ 22:40, ALL POWER RESTORED @ 23:30 DUPLICATE 37830248A00003 VER/AWD
14119 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-05-02 15:08 | 2018-05-02 17:58 | 2 | 170 | 4298851 | 340 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | Broke B phase cutout on xfmr/ might as well change all three cutouts while its out/ ISO 38830139A00352/ COD 2repairs made all cust restored please close ticket thanks.bt
14120 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-12-17 18:20 | 2011-12-17 19:28 | 5 | 68 | 4185781 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPAIRED BROKEN HOT TAP LEAD//COD 5// VER/DBM IDC XXXX
14121 | South Williamson | 3200302 | BELFRY | TOLER | 2013-03-14 07:20 | 2013-03-14 08:45 | 4 | 85 | 4905021 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED TRANSFORMER FUSE THAT BROKE. COD-4 MISMAPPED CUSTOMER MD FILED VER/KEP IDC XXXX
14122 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-11-27 11:17 | 2014-11-27 12:25 | 5 | 68 | 4811251 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 BAD 7200 CUT OUT DOOR IN BANK, REPLACED RESTORERD. ISO POLE 39831124A20615 COD 5// VER/ ADH
14123 | Whitesburg | 3314401 | MAYKING | ERMINE | 2009-05-29 17:15 | 2009-05-29 18:40 | 4 | 85 | 50586-1 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP FOUND BROKEN CUTOUT ON POLE 473-60 L3/HFP IDC XXXX
14124 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-02-04 16:10 | 2011-02-04 19:00 | 2 | 170 | 54084-1 | 340 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFMR LEAD BURNT INTO... REPLACED LEAD RESTORED POWER AT 1900 COD-2 ISO TF 37830355B00171 VER/HFP L3/HFP IDC XXXX
14125 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2020-05-04 23:10 | 2020-05-05 02:00 | 2 | 170 | 4799391 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse out on pole 516-2. Fuse holder burned up..Power restored at 2:00
14126 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-02-23 08:55 | 2015-02-23 14:35 | 1 | 340 | 4074321 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | METERING CABLE SHORTED OUT AND BLEW XFMR FUSE ON 480 BANK. METER ELECTRICIAN ENROUTE TO REPLACE. XFMR IS ALSO BAD. METER DEPT WORKING - LINE CREW ENROUTE TO REPLACE BAD XFMR. RESTORED @ 14:35. SH VER/CRB L3/HFP XXX
14127 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-23 22:11 | 2016-01-24 03:51 | 1 | 340 | 4646311 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074S04
14128 | South Williamson | 3200301 | BELFRY | BELFRY | 2016-04-28 13:11 | 2016-04-28 16:01 | 2 | 170 | 4137951 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF THE SERVICE DROP AT THE TRANSFORMER.
14129 | Pikeville | 3407101 | TOPMOST | DEMA | 2012-06-22 12:02 | 2012-06-22 17:42 | 1 | 340 | 4945611 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 KVA TRANSFORMER BAD, /// HAVE RICK RAY CALL TIM MCCOY10 KVA TRANSFORMER BAD, REPLACED WITH 15 KVA, ALL WORK COMPLETE / GXJ COD-1 ISO TF 37830186000043 VER/HFP L3/HFP
14130 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-07-14 10:15 | 2014-07-14 11:40 | 4 | 85 | 4239291 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY ONE CUSTOMER AFFECTED XFMR CUTOUT FAILED ON XFMR BANK POLE. REPLACED CUTOUT AND RESTORED @ 11:40. SH RELEASED BY CREW 076S02//COD 4// VER/DBM
14131 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-02-21 15:00 | 2015-02-21 17:50 | 2 | 170 | 4064641 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT, NO TRUCK. RELEASED BY CREW 079S02. REPLACED BAD CUTOUT.//COD 2// VER/DBM
14132 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-04-13 08:42 | 2011-04-13 09:50 | 5 | 68 | 56224-1 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | "C" PHASE FUSE BLOWN COD 5 DUE TO BAD TRANS ON ORDER 56181-1 VER/KEP
14133 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-01-24 09:30 | 2010-01-24 12:20 | 2 | 170 | 58666-1 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT BROKE DOWN. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT.//COD 2// VER/DBM IDC XXXX
14134 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-07-05 08:08 | 2016-07-05 10:58 | 2 | 170 | 4534731 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD WIRE IN TREE @ SEC. POLE
14135 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-05-22 17:55 | 2011-05-22 23:35 | 1 | 340 | 4123941 | 340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE IS OUT, GATE ACROSS ROAD IS LOCKED. RE-FUSED AND XFMR IS BAD, 15 KVA, 19.9 KV RELEASED BY CREW 077S02 VER/KEP IDC XXXX
14136 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-06-28 17:51 | 2013-06-28 23:30 | 1 | 339 | 4424391 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOT A 25 KVA TRANSFORMER BAD ON POLE 38830960000017. CAN TRUCK RIGHT BESIDE ROAD.. NEED 25 KVA TRANSFORMER AND A BIG BUCKET.. OPENED OE POLE TAP OFF OF THIS POLE TO CHANGE TRANSFORMER SAFELY AT 23:55.. RESTORED ALL CUSTOMERS AT 00:20.. COMPLETE RN
14137 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-08-01 18:37 | 2011-08-01 20:30 | 3 | 113 | 4652991 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE GATE BURNT UP ON POLE 181-28//// REPLACED C/O GATE POWER RESTORED.//COD 3// VER/DBM IDC XXXX
14138 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2020-11-24 09:37 | 2020-11-24 11:30 | 3 | 113 | 4720101 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKE FUSE
14139 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-11-22 14:55 | 2019-11-22 16:48 | 3 | 113 | 4057301 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out due to bad cutout on pole #55-37, isolated xfmr and closed line fuse at 16:48,need19.9 cutout only, closed xfmr at 18:45// NO CUSTOMERS ON TRANS
14140 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-02-02 07:11 | 2019-02-02 12:50 | 1 | 339 | 4748171 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | lid blew off of transformer,250 kva,19.9 kv,277/480 transformer,line crew truck accessible, Released by crew 077S04
14141 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-10-11 12:25 | 2020-10-11 14:18 | 3 | 113 | 4544971 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINEF 10-38 IS OUT,WILL PTRL////////BROKEN(CRACKED)CUTOUT ON IA XFR 10-59,WILL TAKE THIS CUTOUT OFFLINE,THEN WILL RE-FUSE LINE@10-38 TO RESTORE LAST XFR////CLOSED@14:18
14142 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-03-07 11:37 | 2014-03-07 13:30 | 3 | 113 | 4459171 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT VER/CRB
14143 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-05 13:31 | 2019-06-05 14:58 | 4 | 87 | 4431591 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON TRANSFORMER 38830768D00027 AND TOOK L/F OUT
14144 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-02-22 10:01 | 2009-02-22 15:40 | 1 | 339 | 50276-1 | 339 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE,MANUAL JOB,SENT FETR//3303903//VER/CRB IDC XXXX
14145 | Paintsville | 3409302 | KENWOOD | AUXIER | 2019-01-27 07:47 | 2019-01-27 09:40 | 3 | 113 | 4725591 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout failed. Replaced cutout and restored @ 9:40. sh L3/HFP
14146 | Hazard | 3310502 | HADDIX | CANOE | 2013-09-21 12:47 | 2013-09-21 14:40 | 3 | 113 | 4873771 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD 19.9 CUTOUT BAD ON STEPDOWN TRANSFORMER, VER/CRB L/3 CRB
14147 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-01-30 07:24 | 2008-01-30 09:17 | 3 | 113 | 61803-1 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THIS WAS NOT 79 CUSTOMER, JUST 3 CUST, HAD A RISER FALL OUT OF LUGS IN TRANSFORMER, HAVE REPAIRS MADE AND POWER IS RESTORED HERE VER/KEP IDC XXXX
14148 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-12-11 11:17 | 2018-12-11 13:10 | 3 | 113 | 4552311 | 339 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | customer and neighbor were having part power.replaced bad secondary connection on trans pole 4-98 correcting problem.restored power at 13;10.plz send copy to Peggy Wysong.customers did not mention any damages. L3/HFP
14149 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2019-12-11 10:06 | 2019-12-11 11:48 | 4 | 102 | 4144161 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfmr is bad @ this location 10kva only putting out 120 volts. I have contacted Tommy Goble and he will be bringing big bucket and xfmr to replace. Opened xfmr @ 10:06 LIFTED CLAMP ON POLE 38830856000014 @ 1115 POWER RESTORED @ 1148
14150 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-12-04 08:36 | 2012-12-04 14:15 | 1 | 339 | 4440701 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR.NEED 15 KVA.TRUCK ACCESSIBLE RELEASED BY CREW 076S01// CREW ON SITE REPLACING NOW TCM// VER/KEP IDC XXXX
14151 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2013-07-05 20:47 | 2013-07-05 22:40 | 3 | 113 | 4472731 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT SECONDARY CONDUCTOR DOWN. REPAIRING. REPLACED ABOUT 100 FEET OF #2 ACSR DUE TO DAMAGE. RESAGGED CONDUCTOR AND RESTORED XFMR @ 22:40. SH VER/KEP IDCC CDC89 XXXX
14152 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-11-27 11:33 | 2016-11-27 17:12 | 1 | 339 | 4131331 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR . NEED 3 MAN LINE CREW , 25KVA 19.9 XFMR , 19.9 CUTOUT & TBRACKET . MANUEL . RED&WHITE DOUBLE WIDE ACROSS FROM WILEY BR. ON HWY 28 RELEASED BY CREW 075H04 37830173C00138 VER/AWD
14153 | Pikeville | 3409502 | BURDINE | LEVISA | 2008-05-06 15:26 | 2008-05-06 21:05 | 1 | 339 | 57518-1 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA TRANSFORMER. 2 BUSHING. NEED A 25 KVA TRANSFORMER TO REPLACE THIS ONE. CAN GET TO POLE....DAH//3409502 RELEASED BY CREW 074S08/VER/CRB IDC XXXX
14154 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2021-08-22 16:31 | 2021-08-22 18:24 | 3 | 113 | 4136011 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout power on
14155 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2017-04-03 12:30 | 2017-04-03 14:23 | 3 | 113 | 4609061 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 138 C2 498 BAD 19.9 C/O. SEND TO R. VIRGIN RELEASED BY CREW 078S07--CREW ON SITE---CHANGED 19.9KV CUTOUT---PWR RESTORED AT 14:23---TBL TKT COMP.RMV/ ISO 38830138A00007/ COD 3/ VER/BOW L3/HFP XXXHFP
14156 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-08-06 10:31 | 2010-08-06 16:10 | 1 | 339 | 50266-1 | 339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN NEED BIG BUCKET TO MAKE REPAIRS RELEASED BY CREW 078S09 VER/HFP L3/HFP
14157 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2022-05-21 20:49 | 2022-05-21 21:15 | 13 | 26 | 4923591 | 338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored 21:15//BROKE FUSE
14158 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2021-05-17 14:22 | 2021-05-17 20:00 | 1 | 338 | 4593231 | 338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug service. power temp installed. no voltage now. lost good leg one customer out Released by crew 078S07.found and repaired the faults, removed the power temp transformer // repaired @2000
14159 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-06-09 21:16 | 2008-06-10 00:05 | 2 | 169 | 61022-1 | 338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3401002// TREES IN TRANSFORMER, CURRENT FUSE BAD // VER/TOM IDCC CNT1 XXXX
14160 | Hazard | 3310502 | HADDIX | CANOE | 2008-12-06 15:12 | 2008-12-06 20:50 | 1 | 338 | 54957-1 | 338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077H01// HAD TO LEAVE DUE TO STATION OUTAGE.// WILL BE BACK CUTOUT GATE BURNT UP// VER/TOM L3/TOM IDC XXXX
14161 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-12-13 10:46 | 2019-12-13 13:35 | 2 | 169 | 4150421 | 338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Transformer back in at 13:35
14162 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2012-12-21 12:10 | 2012-12-21 14:59 | 2 | 169 | 4500451 | 338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE HAD BROKE. REPLACED FUSE POWER BACK ON. ////VER/CRB L/3 CRB
14163 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-06-27 20:12 | 2019-06-28 01:50 | 1 | 338 | 4609831 | 338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kva 19.9. Need flaggers, NE and one man. Released by crew 079S02crew on site//restored at 01;50am
14164 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-06-15 14:58 | 2011-06-15 17:47 | 2 | 169 | 4322681 | 338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED LINE CUTOUT , ALL WORK COMPLETE / GXJ //COD 2// VER/DBM
14165 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-12-21 16:41 | 2022-12-21 19:30 | 2 | 169 | 4284911 | 338 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 19.9 XFM, paul layne coming to change out // restored @1930
14166 | South Williamson | 3411401 | DEWEY | INEZ | 2021-09-08 13:38 | 2021-09-08 19:15 | 1 | 337 | 4221841 | 337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Secondary pole 648-564 that is not shown on map has rotted off at ground and fell. This also caused customers serv. pole to break. I cut sec. loops at xfmr 648-A1-710 to de-energized and make safe at 16:30 this only affects the 1 customer. I have contacted line crew and they will be bringing pole to replace. 811 confirmation# 2109082104 /// Replaced sec. pole but customer at meter 190408691 is still out to make repairs. Customer pole was rotted not sure which fell first.
14167 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-01-22 16:38 | 2022-01-22 22:15 | 1 | 337 | 4396921 | 337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | fuse has melted out twice, need 25 kva 19.9 ransformer, can get bucket to pole and i put cutout door on pole ground at foot of pole Released by crew 077S05
14168 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-02-10 08:53 | 2011-02-10 14:30 | 1 | 337 | 55847-1 | 337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG SERVICE--GIVE TO B REYNOLDS RELEASED BY CREW 078S07//WR# 38764993// FOUND THE FAULT, DUG IT UP, MADE REPAIRS, POWER ON AT 14:30, BLR//COD 1 IDC XXXX
14169 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-12-21 17:53 | 2013-12-21 23:30 | 1 | 337 | 4182571 | 337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 43-137 BAD CUTOUT NO TRUCKS TO POLE MIT HAVE TO OPEN LINE 44- 267-65T TO WORK POLE TREES BAD THERE TO SEND NOTE TO TREE PEOPLE LINE NEEDS CUT BAD RELEASED BY CREW 078S08,,CREW ON SITE,, REPAIRS MADE, ALL POWER RESTORED VER/HFP L3/HFP
14170 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-11-15 10:12 | 2018-11-15 15:48 | 1 | 336 | 4413641 | 336 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad hot leg in URD direct burial secondery coming off pole 1-212, talked with P.R., he is going to get a crew to help with repairs. Released by crew 074S05 repairs made on at 15:48 L3/HFP
14171 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-12-13 22:38 | 2016-12-14 00:30 | 3 | 112 | 4192571 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFM. CUTOUT ON POLE 190-118.REPAIRED // VER/TOM L3/TOM
14172 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-10-01 12:57 | 2011-10-01 14:49 | 3 | 112 | 4937851 | 336 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE CKING TROUBLE/// CONNECTOR ON XFMR BAD REPLACED, POWER RESTORED. VER/HFP L3/HFP IDC XXXX
14173 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2020-03-26 12:04 | 2020-03-26 13:00 | 6 | 56 | 4512361 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned up, I changed it out
14174 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2021-01-21 08:51 | 2021-01-21 10:15 | 4 | 84 | 4882051 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfr fuse complete
14175 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-05-05 23:20 | 2010-05-06 02:08 | 2 | 168 | 56256-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19,9 25KVA TRANSFORMER-CALLED CREW RELEASED BY CREW 078S07 VER/ARN IDC XXXX
14176 | Pikeville | 3421001 | BREAKS | CITY | 2019-02-16 08:18 | 2019-02-16 11:06 | 2 | 168 | 4799131 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot tap lead burnt open will make repairs// Replaced hot tap and lead to cutout //restored @ 11:06
14177 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-01-24 18:54 | 2013-01-24 21:42 | 2 | 168 | 4738491 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNED UP. ///VER/CRB L/3 CRB IDC XXXX
14178 | Hazard | 3302704 | HAZARD | KENMONT | 2018-06-12 20:01 | 2018-06-12 21:53 | 3 | 112 | 4594231 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke
14179 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-11-21 12:25 | 2010-11-21 18:01 | 1 | 336 | 58487-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | PER DUTY SUPERVISOR & CUSTOMER THIS CAN WAIT UNTIL 11/22 FOR METER DEPARTMENT TO REPORGRAM TOU METER. // REPAIRED METER VER/HFP L3/HFP IDC XXXX
14180 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-03-13 11:59 | 2022-03-13 12:55 | 6 | 56 | 4619631 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse melted out and burnt up cutout door. Replaced door and restored @ 12:55. sh
14181 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2017-12-23 00:14 | 2017-12-23 05:50 | 1 | 336 | 4665111 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6t transformer fuse out due to bad transformer. talked to dennis transformer will be headed my way when they clear up with terry. changed xfmr out everything ok.
14182 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2011-01-28 09:33 | 2011-01-28 11:25 | 3 | 112 | 50670-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT, CREW ENROUTE--- POWER RESTORED.//VER/CRB IDC XXXX
14183 | Whitesburg | 3312901 | JENKINS | KONA | 2015-01-08 08:37 | 2015-01-08 09:33 | 6 | 56 | 4918691 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNING/I CHANGED CUTOUT GATE AND REFUSED XFMR//COD 6//ON 9:33// VER/ ADH L3/HFP HFPC FP0
14184 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2011-03-15 18:34 | 2011-03-15 19:30 | 6 | 56 | 54597-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39178437 // WITH BACK TO SOURCE RT HAND RECL OUT // PER FRANK THIS SHOULD HAVE BEEN A PHASE OUT /// CCC - COD-6 ISO RECL 37820197000098 VER/HFP L3/HFP IDC XXXX
14185 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-02-09 18:42 | 2019-02-09 21:30 | 2 | 168 | 4774141 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT
14186 | Hazard | 3310502 | HADDIX | CANOE | 2014-04-02 11:48 | 2014-04-02 12:30 | 8 | 42 | H4554581 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT. OPEN LINE FUSE ON POLE #37830074000010 AT 1148 AND CLOSED AT 1230 VER/CRB IDC XXXX
14187 | Hazard | 3302703 | HAZARD | HAZARD | 2010-01-25 16:35 | 2010-01-25 17:23 | 7 | 48 | 59672-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | "B" PHASE DOWNB PHASE DOWN OPENED OTHER PHASES AT 1635 RESSAGGED CONDUCTOR AND RESTORED POWER AT 1723 CREW 077H01 VER/KEP L3/KEP IDC XXXX
14188 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-12-22 20:49 | 2012-12-23 02:25 | 1 | 336 | 4509811 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SERVICER WILL WORK THIS JOB NEXT. XFMR FUSE BROKE AND MELTED OUT. VER/PDP
14189 | Whitesburg | 3314401 | MAYKING | ERMINE | 2022-09-29 16:59 | 2022-09-29 22:35 | 1 | 336 | 4939161 | 336 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad transformer/crew requiredBad 7200 100KVA xfrm on pole 449D-96 feeding mcdonalds. Need linecrew. 2Bad 7200 100KVA xfrm on pole 449D-96 feeding mcdonalds. Need linecrew. 2 Released by crew 077H15/ power restored 2235
14190 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-04-04 19:33 | 2009-04-04 20:15 | 8 | 42 | 65215-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3002107// STS WR# 29236986// SEND NOTE TO RAYBURN POLE 45-2092 LA BAD T-BRACKET BENT DOWN NEEDS REPLACED//COD 8//EMAILED TO L RAYBURN// VER/DBM IDC XXXX
14191 | Hazard | 3309302 | VICCO | JEFF | 2013-01-05 18:47 | 2013-01-05 21:35 | 2 | 168 | 4572261 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERV NEUT BURN INTO FROM BAD SPLICE GOT HOT === REM 2/3 INSTALLED 1/0 SERV === POWER OK VER/KEP IDC XXXX
14192 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-11-01 21:34 | 2020-11-02 03:10 | 1 | 336 | 4625511 | 336 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Lug on xfmr was loose and 1 hot leg on secondary side had came out . I put wire back in lug and tightened voltage now good//cod 1
14193 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-12-08 10:46 | 2010-12-08 11:42 | 6 | 56 | 64358-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR# 38034371 //NO CREW REQUIRED RESAGGING PRIMARY/40T//COD 6// VER/DBM IDC XXXX
14194 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-05-01 10:51 | 2011-05-01 11:39 | 7 | 48 | 53158-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN ... REPLACED FUSE , ALL WORK COMPLETE / GXJ//COD 7// VER/DBM IDC XXXX
14195 | Paintsville | 3409302 | KENWOOD | AUXIER | 2013-10-23 17:26 | 2013-10-23 18:50 | 4 | 84 | 4957751 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKE. REPLACED FUSE AND RESTORED @ 18:50. SH VER/CRB L/3 CRB
14196 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-08-08 15:53 | 2008-08-08 17:45 | 3 | 112 | 50345-1 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400303//TRANSFORMER FUSE BROKE RELEASED BY CREW 074S05 VER/TOM IDC XXXX
14197 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-11-12 13:45 | 2018-11-12 16:33 | 2 | 168 | 4392111 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on transformer , repairs made and power restored at 1633
14198 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2020-07-29 09:05 | 2020-07-29 09:33 | 12 | 28 | 4249391 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENING TO SAFLEY RAISE PRIMARY NEUTRAL UP ON POLE 38830161000015 // ISO 38830185000146 // COD 12 // OFF@ ON@ times off was 9:05 in at 9:33 please close ticket LRM
14199 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-01-26 12:12 | 2013-01-26 13:00 | 7 | 48 | 4742621 | 336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED TRANS TO SAFELY MAKE REPAIRS ON SERVICE TROUBLE REPORTED IN ORDER 4742421 // OPENED @ 1212 CLOSED @ 1300 COD-8 ISO TF 37830249C00030 VER/KEP IDC XXXX
14200 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-08-18 16:58 | 2013-08-18 18:05 | 5 | 67 | 4677061 | 335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S08--LIFTED HOTTAP ON POLE 38830117D00142 AT16:58//ISO//COD 5/// VER/DBM IDC XXXX
14201 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-05-22 08:03 | 2020-05-22 09:10 | 5 | 67 | 4885041 | 335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | primary jumper came out of the bottom of the cutout. repairs made, power restored at 0910
14202 | South Williamson | 3200302 | BELFRY | TOLER | 2018-01-03 15:08 | 2018-01-03 16:15 | 5 | 67 | 4703531 | 335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 38821015D00178trans fuse blown on 1015D178 trans fuse on 1015D178 melted out replaced fuse restored power at 16:15
14203 | Pikeville | 3421001 | BREAKS | CITY | 2015-01-08 08:13 | 2015-01-08 09:20 | 5 | 67 | 4918521 | 335 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER./COD 5// VER/ ADH
14204 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-10-08 10:05 | 2015-10-08 15:40 | 1 | 335 | 4327961 | 335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | UNDER GROUND TROUBLE FUSED BAD AT TRANSFORMER RELEASED BY CREW 078S09.. CREW ON SITE WAITING ON UG TRANSFORMER FUSE FROM PORTSMOUTH TO SEE IF TRANSFORMER WILL HOLD ETR 16:00.. 3 100T FUSES OUT AT 15:30 AND BACK ON AT 15:40 XFMR IS HOLDING.. PLEASE CLOSE TICKET CAY VER/HFP L3/HFP
14205 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-06-24 18:23 | 2010-06-24 19:30 | 5 | 67 | 56975-1 | 335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | IDC XXXX
14206 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-05-05 08:38 | 2012-05-05 14:13 | 1 | 335 | 4748791 | 335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED SERVICE///VER/CRB L/3 CRB IDC XXXX
14207 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-06-08 12:15 | 2019-06-08 17:50 | 1 | 335 | 4458251 | 335 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | xfmr to secondary lead pulled apart. I replaced it
14208 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-02-01 17:53 | 2013-02-01 23:28 | 1 | 335 | 4783591 | 335 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE CUSTOMER HAD PART POWER. BAD CONNECTION AT TRANSFORMER.// VER/DBM IDC XXXX
14209 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-02-24 08:58 | 2014-02-24 14:33 | 1 | 335 | 4429881 | 335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN ON POLE 165-93. I AM GOING TO REFUSE TRANS. 15 KVA TRANSFORMER IS BAD ON POLE 165-93. I AM CALLING FOR HELP. RELEASED BY CREW 074S01TRANS. FUSE IS BLOWN ON POLE 165-93. I AM GOING TO REFUSE TRANS. 15 KVA TRANSFORMER IS BAD ON POLE 165-93. I AM CALLING FOR HELP. WE CHANGED TRANS. VER/HFP L3/HFP
14210 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-04-06 17:03 | 2017-04-06 19:50 | 2 | 167 | 4623931 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPEN WIRE SECONDARY AND NEUTRAL DOWN. CAN TRUCK AND ELIMINATE ONE SPAN OF SEC BUT NEUTRAL WILL NEED TO BE REPAIRED. CREW ENROUTE TO ASSIST. COMPLETED REPAIRS AND CLOSED XFMR @ 19:50. SH VER/CRB L3/HFP XXXHFP
14211 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2012-09-19 11:50 | 2012-09-19 14:37 | 2 | 167 | 4068641 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD//// REPLACED BAD C/O, POWER RESTORED. VER/KEP IDC XXXX
14212 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-12-29 09:43 | 2015-12-29 12:30 | 2 | 167 | 4572551 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT // WILL RERPLACE // POWER RESTORED @ 12:30 COD-2 ISO TF 37820073D00464 VER/HFP L3/HFP
14213 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-07-20 21:06 | 2012-07-21 02:40 | 1 | 334 | 4788511 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQ, BAD 10KVA 7200 CSP, NEED TO REPLACE WITH AT LEAST 15KVA, CUTOUT, AND BRACKET, BEST WAY IN IS DOWN ROW AT 1045 WALNUT, MAY NEED TRACK BUCKET, RELEASED BY CREW 078S05 (ALL POWER RESTORED AT 02:40) VER/ARN
14214 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-05-21 11:16 | 2009-05-21 14:03 | 2 | 167 | 55802-1 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP REPAIRED CONNECTIONS L3/HFP
14215 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2009-09-14 07:14 | 2009-09-14 12:48 | 1 | 334 | 53767-1 | 334 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CUSTOMERS 911 ADDRESS IS 9086 MEATHOUSE CONN BAD ON TRANSF POLE L3/HFP IDC XXXX
14216 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2011-12-22 17:37 | 2011-12-22 23:11 | 1 | 334 | 4195781 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-8373 BAD 25KVA TRUCK TO POLE SEND TO VERNON M. RELEASED BY CREW 078S08/CREW ON SITE FETR 2351/VEM/REPAIRS MADE AND POWER RESTORED 2311/PLEASE CLOSE TICKET/THANKS/VEM ////VER/CRB IDC XXXX
14217 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-03-04 18:43 | 2022-03-04 21:30 | 2 | 167 | 4567881 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRIPLEX SEC CABLE SHORTED OUT,WILL MAKE REPAIRS/////RESTORED 21:30
14218 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2017-08-02 10:26 | 2017-08-02 13:13 | 2 | 167 | 4216471 | 334 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | SEE H4216471*** POLE 20 C4 5667 BAD 12KV C/O (2 CUST PRT OUT). CHANGE OTHER 2 W/ OUTAGE. 100T LF ON 20-350 WILL OUTAGE TAP. RELEASED BY CREW 078S07/CREW ON SITE/FETR 1345/VEM/OPENED FUSE 38830020C30350 AT 1255 (1 ADDITI CUST)/REPAIRS MADE AND ALL CUST RESTORED 1313/PLEASE CLOSE TICKET/THANKS/VEM/ VER/BOW
14219 | South Williamson | 3411401 | DEWEY | INEZ | 2017-05-09 20:08 | 2017-05-09 22:55 | 2 | 167 | 4773871 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF ON 647-518 DUE TO BAD CUTOUT///LINE FUSE BLOWN ON POLE 647-8///I CAN FRAME PRIMARY DOWN ENOUGH TO GET ON TONIGHT//REPAIRS MADE///CREW WILL NEED TO COME TOMOROW AND LOWER XFMR AND NEUTRAL AND SERVICE DROP//I WILL CALL THEM IN THE MORNING//RESTORED AT 22:55//COMPLETE//EM/ ISO 38830647D00008/ CDO 2/ VER/BOW
14220 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2013-08-11 09:46 | 2013-08-11 12:33 | 2 | 167 | 4649401 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE MELTED OUT, RESTORED POWER AT 12:33 VER/CRB L/3 CRB
14221 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-12-21 18:58 | 2014-12-21 21:45 | 2 | 167 | 4873611 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR ON POLE 24-829, NEED 25KVA, CUT OUT, BRACKET, ARR. 7200 RELEASED BY CREW 074H07// CHANGED TRANSFORMER AND RESTORED POWER. 21:45 TIM MCCOY RELEASED BY CREW 074H10 VER/KEP
14222 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-01-29 00:13 | 2016-01-29 03:00 | 2 | 167 | 4657561 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | METER DISPLAY BLANK PER CUSTOMER// XFMR FUSE OUT ON POLE 147-187 . ( FUSE WAS BROKE)//COD 2// VER/DBM
14223 | Hazard | 3303902 | LESLIE | WOOTON | 2021-03-04 04:06 | 2021-03-04 09:40 | 1 | 334 | 4300631 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at weatherhead, opened xfmr at 09:20 closed at 09:40
14224 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-05-18 18:58 | 2016-05-18 21:45 | 2 | 167 | 4232271 | 334 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | (2 CUST PART POWER ORGINALLY) TRANSFORMER CONNECTION FROM SECONDARY LEAD TO 1/0 LASH CABLE BURNT UP ON834-A-37 REPLACED CONNECTION OPENED TRANS (2 CUST) AT 21:30 AND RESTORED POWER AT 21:45/ ISO 38830834A00037/ COD 4/ DUPLICATE IN HOIS/ VER/BOW
14225 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2013-03-05 12:39 | 2013-03-05 15:26 | 2 | 167 | 4871661 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === NEED 1 MAN AND BIG BUCKET ===CHANGED CUTOUTS === REFUSED POWER OK ///VER/CRB L/3 CRB IDC XXXX
14226 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-01-07 11:43 | 2009-01-07 14:30 | 2 | 167 | 52546-1 | 334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3310501/FAILLED TRANSFORMER ADDED 1 FROM MISMAPPED CUSTOMER VER/KEP L3/KEP IDC XXXX
14227 | South Williamson | 3411401 | DEWEY | INEZ | 2010-12-30 18:04 | 2010-12-30 19:55 | 3 | 111 | 57162-1 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RESTORED @ 19:55. SH VER/KEP L3/KEP IDC XXXX
14228 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-11-16 17:55 | 2010-11-16 23:28 | 1 | 333 | 56523-1 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37786731 //....OPEN FUSE ON POLE 230-23...POLE FIRE NEED HELP TO LOWER EVERYTHING..P.HICKS..OPENED FUSE @17:55 HRS /// TIM SMITH, W. MELTON & J LAWSON COMING OUT TO MAKE REPAIRS//STS WR # 37786731 //....OPEN FUSE ON POLE 230-23...POLE FIRE NEED HELP TO LOWER EVERYTHING..P.HICKS..OPENED FUSE @17:55 HRS...MANUAL POLE, BUT FIRE DEPT HAS PUT FIRE OUT..NEED 19.9 C/O , ARR., AND T-BRKT, CAN LOWER EVERYTHING. RELEASED BY CREW 077H01 IDC XXXX
14229 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2022-01-23 22:49 | 2022-01-24 00:40 | 3 | 111 | 4399191 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | repalced bad cutout
14230 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-10-02 08:32 | 2014-10-02 14:05 | 1 | 333 | 4543851 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ALL 3 FUSES ARE BLOWN ON XFMR BANK // WILL CHECK // BAD 25 KVA // 240/480 // 7200 RELEASED BY CREW 074S05BAD 25KVA TRANSFORMER 240/480 BANK ON POLE 48-1134 DID NOT HAVE 25KVA TRANS IN STOCK. REPLACED WITH A 50KVA RE-ENERGIZED BANK CHECKED VOLTAGE /GOOD AT 14:05 RELEASED BY CREW 074H15 COD-1 ISO TF 37830048A21134 VER/HFP L3/HFP
14231 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-07-28 00:32 | 2015-07-28 01:09 | 9 | 37 | 4950031 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ASSOCIATED WITH POWERON ORDER 4949951// LINE FUSE @ 44-A-154 OPENED @ 2330 AND CLOSED IN AT 2345// HOT TAP LIFTED @ 44-A-382...
14232 | Cannonsburg | 3001401 | LOUISA | CITY | 2019-12-23 20:39 | 2019-12-23 22:30 | 3 | 111 | 4179091 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broke cutout, apr at 2230 close ticket. dwest//cod 3//
14233 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2017-08-21 19:05 | 2017-08-21 20:56 | 3 | 111 | 4283951 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER NEIGHBOR OUT OF POWER ALSO///FUSE ON XFMER POLE 214-118 BROKE///REFUSED AT 20:56///COMPLETE BR/ ISO 38830214000118/ COD 3/ VER/BOW
14234 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2020-02-26 22:36 | 2020-02-27 00:27 | 3 | 111 | 4435031 | 333 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | Pri jumper burnt off on pole 45b2056 on one phase. opened transformer then opened other two phases repairs made. jumper replaced. pls close. tre/ replaced hot taps then closed transfromer 38830045B12275/ ISO 38830045B12056/ COD 3 ¦¦¦ NOTE THIS TOOK NO ADDITIONAL CUSTOMERS OUT - L3/HFP
14235 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-03-23 19:33 | 2022-03-23 21:24 | 3 | 111 | 4665071 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout on pole 497-32. Need line crew.Broke cutout on pole 497-32. Talked to rick maggard he will be coming to make repairs. Released by crew 077H15.. restored power at 21:24
14236 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-02-02 17:09 | 2019-02-02 19:00 | 3 | 111 | 4749331 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing
14237 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-07-08 07:57 | 2013-07-08 13:30 | 1 | 333 | 4485171 | 333 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TRENSFORMER LUG BAD. TIGHTENED AS MUCH AS POSSIBLE, TRANSFORMER NEEDS TO BE REPLACED ASAP, CUST ON OXYGEN AND NEEDS AIR COND., POWER OK FOR NOW.======== MANUAL TRANSFORMER 15 KVA. 19.9 KV COD-1 ISO SO VER/HFP L3/HFP IDC XXXX
14238 | Hazard | 3310502 | HADDIX | CANOE | 2021-12-24 17:49 | 2021-12-24 23:22 | 1 | 333 | 4224361 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke 19,9 cutout on 55ft pole.. Will need two men in a big bucket. Released by crew 077H07. all power restored @ 23:22 p.hicks
14239 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-04-17 05:53 | 2016-04-17 11:26 | 1 | 333 | 4097171 | 333 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG NO VOLTAGE ON 1 LEG NEED LINE CREW TO REPAIR RELEASED BY CREW 078S05.REPLACED THE UNDERGROUND SERVICE,,,COMPLETE AT 11:26/ ISO 38830182B43694/ COD 1/ VER/BOW
14240 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-01-15 08:50 | 2019-01-15 14:23 | 1 | 333 | 4674201 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD riser burndt out of the bottom of the cutout on pole 72-C-468, will have to open all 3 L/Fs @72-C-412 to make repairs, Dave Sammons getting crew together to help with repairs, all work is manual. Didnt have to open L/F @412, got cutout replaced on 72-C-468 @1423. L3/HFP
14241 | Pikeville | 3402003 | KEYSER | MULLINS | 2016-01-14 14:15 | 2016-01-14 16:06 | 3 | 111 | 4620331 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR WILL NEED 50 KVA 7200-120/208 2 BUSHING 2 MEN & MATERIAL HANDLER VER/CRB
14242 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-02-17 15:09 | 2009-02-17 17:00 | 3 | 111 | 63354-1 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CREW HAD TO OPEN THE TRANSFORMER TO SAFELY MAKE REPAIRS. RELATED TO ORDER 63190-1 L3/HFP
14243 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-06-05 10:37 | 2014-06-05 16:10 | 1 | 333 | 4985231 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, NEED 15 KVA 7200V. CUT OUT , T BRKT AND ARR..MANUAL, NEED TRANSFORMER BUGGY, AND LINE TRUCK, 3 MAN CREW. RELEASED BY CREW 077H09.. ONLY 1 CUST OUT..POWER RESTORED. VER/CRB
14244 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-04-03 20:19 | 2014-04-03 22:10 | 3 | 111 | 4569401 | 333 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-3 ISO LF 38820771A49001 VER/HFP L3/HFP
14245 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-11-26 16:51 | 2009-11-26 19:37 | 2 | 166 | 66045-1 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PRIMARY WIRE DOWN BETWEEN POLE 188B150 AND 188B283. WIRE DOWN DUE TO BAD SLEEVE I HAVE WIRE UP EVERYTHING OK. ROW NEEDS CUT BAD FROM POLE 188B238 ALL THE WAY TO POLE 188B165. SEND COPY TO JASON BRADSHAW PIKEVILLE.//COD 6//ISO 37830188B00150 IDCC PN165. FP "NONE" XXXX
14246 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-05-31 06:48 | 2011-05-31 12:20 | 1 | 332 | 4212081 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#40169628 BAD 15 KVA 7200 120/240 TRUCK OK SINGLE CUST GARAGE CAN WAIT TALK WITH CUST POLE NO MIS MAP 45-A-664 POLE NO IN ALLEY RELEASED BY CREW 078S09 CREW ON SITE FETR 13:30 RLM JOB COMPLETE AT 12:20 PLEASE CLOSE TICKET RM//VER/CRB IDCC PN568 XXXX
14247 | South Williamson | 3411401 | DEWEY | INEZ | 2021-09-01 08:14 | 2021-09-01 11:00 | 2 | 166 | 4192031 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//replaced cutout//restored at 11:00//complete//em
14248 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-02-26 14:45 | 2008-02-26 20:17 | 1 | 332 | 50581-1 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000303//LIFTED HOT TAP ON POLE 67-49- AN TAGGED/ CALLED FIRE DEPT/NEED LINE CREW// POLE BURNT INTO// CORRECT TRANSFORMER POLE FOR CUSTOMER IS 67-516// NEED 40 CLASS 5 POLE AN NEW CUTOUT-EVERYTHING ELSE SHOULD GO BACK// TRUCKS TO POLE RELEASED BY CREW 078S07//CREW REQUIRED// POWER RESTORED AT 20:17 IDCC PN50, TOF1358 XXXX
14249 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-07-04 20:40 | 2018-07-05 02:12 | 1 | 332 | 4725531 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | fuse blown on transformer bank for water pump. found bad arrestor on transformer tank, replaced arrestor. all power restored @ 02:12 hrs.p.hicks
14250 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2010-01-12 21:24 | 2010-01-12 22:47 | 4 | 83 | 53344-1 | 332 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION BURNED INTO AT XFMR POLE 449-66...OPENED XFMR AT 22:36 MADE REPAIRS RESTORED POWER AT22:47//COD 4// VER/DBM IDC CHANGED TOF FROM 2236 XXXX
14251 | Paintsville | 3409302 | KENWOOD | AUXIER | 2009-11-15 09:07 | 2009-11-15 10:30 | 4 | 83 | 58004-1 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING NOW HOT TAP BURNED OFF.ON POLE 882-360 STIRRUP BURNT OFF FIXED EVERY THING BACK TO NORMAL - TREE WAS SEPEARATE ISSUE /// VER/TOM L3/TOM IDCC PN574, CNT2, CDC98 XXXX
14252 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2010-01-13 08:52 | 2010-01-13 10:15 | 4 | 83 | 53433-1 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 235-95. CUTOUT REPLACED EVERYTHING OK 37830235000095 COD-4 VER/KEP L3/KEP IDC XXXX
14253 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2018-02-09 07:08 | 2018-02-09 12:40 | 1 | 332 | 4819611 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tran c/o broke--replaced --in at 12:40--allgood-ds020918
14254 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2009-08-03 09:19 | 2009-08-03 12:05 | 2 | 166 | 64450-1 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUTOUT//COD 2// VER/DBM IDC XXXX
14255 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-04-18 15:28 | 2013-04-18 21:00 | 1 | 332 | 4023061 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | MARTY ADAMS 3268 REPORTS HIGH VOLTAGE 140V GATE CODE 10221 HIGH VOLTAGE READING 140 VOLTS PHASE-GROUND 280 VOLTS PHASE-PHASE CHECKED ALL CONN. LOOK OK , CHECKED VOLTAGE @ POLE 126-223 VOLTAGE WAS OK 249 PHASE-PHASE 124 PHASE-GROUND. 15 KVA XFMR CREW. ETR 21:00 ///VER / CRB L/3 CRB IDC XXXX
14256 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-01-25 10:54 | 2017-01-25 13:40 | 2 | 166 | 4329561 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , PHONE CO. HAS CLIMBED POLE , CUTOUT FELL OPEN . REPLACED CUTOUT VER/CRB L3/HFP XXXHFP
14257 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-07-01 15:14 | 2021-07-01 18:00 | 2 | 166 | 4837991 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke xfm cutout on 37830071000267// Replaced and restored @ 18:00
14258 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-08-13 16:45 | 2009-08-13 18:08 | 4 | 83 | H55702-1 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | FOUND BAD UG SPLICE. WILL HAVE TO DIG IT OUT TO REPAIR. CREW ONSITE AND ADDITIONAL CREW ENROUTE TO ASSIST. WILL HAVE XFMR 809-561 OPEN FOR APPROX 1 HOUR TO MAKE REPAIRS WHEN CREW ARRIVES. ONLY THREE CUST WITH PART OUT. OPENED XFMR 809-561 AT 16:45 INTERRUPTING REMAINING CUST UNTIL REPAIRS COMPLETE. 12 CUSTOMERS TOTAL. REPAIRS COMPLETE. RESTORED ALL CUSTOMERS AT 18:08. SH IDCC DUP TO OPEN TRANSFORMER XXXX
14259 | Pikeville | 3410602 | E.PRESTON | LANCER | 2010-08-28 15:28 | 2010-08-28 21:00 | 1 | 332 | 61524-1 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMER FUSE OPEN CHECKING NOW. BAD XFMER CALLING CREW.CREW IN ROUTE RELEASED BY CREW 076H06// COULD NOT WORK POLE. CHANGED XFMR ON POLE 956-5 TO A 25 KVA AND MOVED SECONDARY OVER TO THIS POLE.// ON AT 21:00 //VER/GAH L3/WDH IDC XXXX
14260 | Pikeville | 3402003 | KEYSER | MULLINS | 2016-04-11 17:20 | 2016-04-11 20:06 | 2 | 166 | 4081681 | 332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND CONNECTION ON XFM POLE ALMOST MELTED INTO///OPENED XFM UP ON POLE 30-06 @ 19:40 TO MAKE REPAIRS AND CLOSED BACK IN @ 20:06... VER/CRB
14261 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-05-05 09:44 | 2018-05-05 15:15 | 1 | 331 | 4309821 | 331 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 KVA transformer. Crew enroute to replace. Replaced and restored @ 15:15. sh
14262 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-07-28 19:44 | 2016-07-29 01:15 | 1 | 331 | 4703151 | 331 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON POLE 120-79, THIS IS UP ON THE MOUNTAIN, I WILL HAVE TO CUT A PATH, BAD R.O.W., TO MAKE REPAIRS. MADE REPAIRS, CLOSED CUT-OUT BACK IN @ 0115. VER/CRB
14263 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-05-11 14:34 | 2008-05-11 20:05 | 1 | 331 | 61242-1 | 331 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL BROKEN, TREE FELL ON TELEPHONE LINES PULLING OUR POLE AND NEUTRAL SPLICE ON #4 ALU. SERV. PULLED LOOSE, CUST. CAME HOME SMELLING SMOKE. MAY CALL ABOUT DAMAGES. RESPLICED POWER OKAY. MAY SEND COPIE OF THIS TICKET TO BRUCE, FOR FUTURE REFERENCE?//3308401//VER/CRB IDC XXXX
14264 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-03-27 19:09 | 2017-03-28 00:40 | 1 | 331 | 4589671 | 331 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED FOR EXTRA HAND RELEASED BY CREW 078S03CALLED FOR EXTRA HAND REPAIRED SERVICE NO CREW/// VER/DKM
14265 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2022-03-08 05:24 | 2022-03-08 10:55 | 1 | 331 | 4587241 | 331 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held for daylight per KPCO late night callout guidelines. Transformer cutout failed. Replaced cutout and restored @ 10:55. sh
14266 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2018-06-27 17:40 | 2018-06-27 20:25 | 2 | 165 | 4681481 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xform fuse out bad cutout replace ,bad connections on sec. ,repaired power restored
14267 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-09-13 22:15 | 2010-09-13 22:25 | 33 | 10 | 66234-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WR# 36865248 // ISO 38830044B00267 // COD 33 //WR# 36865248 // BAD HOT TAP OPENED LINE FUSE 10;15 0N 10;25// VER/DBM IDC XXXX
14268 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2018-10-08 19:40 | 2018-10-08 21:30 | 3 | 110 | 4208811 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 271-117 rotten phone company pole crew requird/35/5 pole size/need yard dog to set pole manual tree crew also/send to bobby tackett Released by crew 078S03,open xfmr @ 1940 pole replaced all cust restored @ 2130 please close ticket thanks.bt L3/HFP
14269 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2008-10-27 00:31 | 2008-10-27 02:21 | 3 | 110 | 59317-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3000802 TR FUSE OUT RESAGGING OPEN WIRE ** PULL OUT OF SLEEVE. CC 3 VER/PDP IDC XXXX
14270 | South Williamson | 3411401 | DEWEY | INEZ | 2018-12-22 15:35 | 2018-12-22 21:05 | 1 | 330 | 4592891 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 19.9 xfmr//truck approach//crew en route also found line fuse cutout broke on pole 744-162//top was hanging down and still making connection on bottom side of cutout//isolated line fuse at 20:10//restored at 21:05//complete//em--fuse cust count same as transformer count L3/HFP
14271 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-05-12 03:23 | 2015-05-12 03:53 | 11 | 30 | 4417471 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | OPENING RECLOSER SO VERNON CAN REMOVE GROUNDS AND RETURN FEED TO NORMAL VER/SEF L3/DKGXXX
14272 | Hazard | 3303901 | LESLIE | HYDEN | 2020-05-28 20:30 | 2020-05-29 02:00 | 1 | 330 | 4923521 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout. Power restored @ 02:00
14273 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2020-02-16 06:10 | 2020-02-16 11:40 | 1 | 330 | 4409451 | 330 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3409003/gaj/0615/part out possible fuse open on riser pole disp 3526 S Hall Riser fuse blown on 785-1091. One customer affected. Replacing all three cutouts & arresters. Restored service at 11:40. sh L3/HFP
14274 | Hazard | 3301101 | CHAVIES | CHAVIES | 2009-07-18 15:07 | 2009-07-18 16:57 | 3 | 110 | 58540-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DDC ATTEMPTED PHONE CONTACT. NO ANSWER. OR VOICE MAIL AVAILABLE.. AT 0116 , CUSTOMER CONTACTED . OK TO WAIT UNTIL THE A.M. TO CHECK . ADVISED TO CALL BACK IF POWER QUALITY ISSUES ARISE.// WE HAVE PRIMARY THAT CAME OFF POLE 37840288000085 AND WILL NEED TO BE PUT BACK. LINE STILL HOT. CAN GET 4-WHEELER TO POLE. WILL HAVE TO OPEN FUSE ON POLE 286-76 TO DE-ENERGIZE LINE. CREW REQUIRED. PIN INSULATOR AND TIE WIRE ALU. WIRE. VER/KEP L3/KEP IDCC TOF0039 XXXX
14275 | Hazard | 3308002 | JACKSON | PANBOWL | 2018-06-13 14:15 | 2018-06-13 15:10 | 6 | 55 | 4597511 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke into
14276 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2011-10-08 06:00 | 2011-10-08 11:30 | 1 | 330 | 4957151 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7200, NO TRUCKS RELEASED BY CREW 078S11 ///VER/CRB IDC XXXX
14277 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-08-22 12:45 | 2011-08-22 13:15 | 11 | 30 | 4741651 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED, NEED TO CHANGE 3CUTOUTS ON ARM ---7.2 KV RELEASED BY CREW 077S04OPENED AT 12.45 ON AT 13.15 //VER/CRB IDC XXXX
14278 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2009-04-29 19:30 | 2009-04-29 22:15 | 2 | 165 | 59261-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HARVEY OPENED FUSE TO ISOLATE BURNING POLE ON ORDER 59147-1 VER/KEP L3/KEP IDC XXXX
14279 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-04-17 22:21 | 2018-04-17 22:51 | 11 | 30 | 4248441 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 25min eta. Screw on stirrup arcing on pole 72-A-278, had to open l/f on this pole to make repairs, opened @2221, moved tap from B to C phase on a good stirrup and closed back in @2251. No outage until I opened l/f./ ISO 37830072A00278/ COD 11 L3/HFP
14280 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2013-02-11 17:01 | 2013-02-11 17:56 | 6 | 55 | 4811021 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 38830231000044 ROTTED AT GROUND , WIRE HOLDING POLE UP, WINDSTREAM IN ROUTE TO SET POLE, TREE CREW IN ROUTE, R VIRGIN IN ROUTE, TECH HAS BEEN HERE TO WRITE WORK ORDER RELEASED BY CREW 078S05 ///VER/CRB L/3 CRBROTTEN POLE OWNED BY WINDSTREAM//PHONE CO SET NEW POLE///TRANS. AEP COND///OPENED 30T L.F.PL. 38830231000036 @ 17:01 BACK ON 17:56 ///VER/CRB L/3 CRB IDC XXXX
14281 | Hazard | 3308001 | JACKSON | S.JACKSON | 2016-05-31 14:50 | 2016-05-31 20:20 | 1 | 330 | 4276351 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 15 KVA 7200 TRANSFORMER, BIG BUCKET MIGHT REACH IT, SEC BUSHING LOOSE ON INSIDE TRANSFORMER RELEASED BY CREW 077S05 CREATED OUTAGE 4277041 TO SHOW ADDITIONAL CUSTOMER OUTAGE.NEED 15 KVA 7200 TRANSFORMER, BIG BUCKET MIGHT REACH IT, SEC BUSHING LOOSE ON INSIDE TRANSFORMER RELEASED BY CREW 077S05 REPAIRS MADE AND POWER RESTORED AT 20:20 VER/AWD
14282 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-08-12 19:46 | 2021-08-13 01:16 | 1 | 330 | 4048861 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required need a 25kva to replace a 10 with new risers and cutout/trucks ok materialhandler big Released by crew 078S03//arrived RM/repaiirs made voltage good please close tic RM
14283 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-05-30 19:20 | 2011-05-30 22:05 | 2 | 165 | 4211291 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25KVA XFMR BAD IN 120/208 BANK. RESTURANT IS CLOSING SO WE CAN OPEN OTHER TWO XFMRS AND MAKE REPAIRS. CREW ENROUTE WITH NEW XFMR. CHANGED XFMR AND RESTORED @ 22:05. SH //VER/GAH IDC XXXX
14284 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-12-30 07:07 | 2013-12-30 08:57 | 3 | 110 | 4211551 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED BAD LIGHTENING ARRESTER, POWER IS BACK ON. THIS IS FOR THE HOUSE NOT TRL MADE CHANGE VER/CRB
14285 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-08-21 14:37 | 2008-08-21 15:10 | 10 | 33 | 53801-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3402801//WR#25887970//3402801// OPENED TRANSFORMER LONG ENOUGH TO REPLACE ALL NEUTRAL CONNECTIONS BELOW JCT BOX AND REPLACED BOX TCMILLER//VER/CRB IDC XXXX
14286 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-05-25 13:15 | 2012-05-25 15:05 | 3 | 110 | 4830751 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT--LINE FUSE ///VER/CRB L/3 CRB IDC XXXX
14287 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-11-08 11:00 | 2014-11-08 11:30 | 11 | 30 | 4713411 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 11:00-11:30 TO MAKE REPAIRS TO TRANSFORMER RISER// CUSTOMER HAD TROUBLE AND WILL CALL FOR RECONNECT AS WELL// ISO 38830069C24507// COD 11/ VER/BOW L3/HFP
14288 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-07-14 15:10 | 2020-07-14 17:00 | 3 | 110 | 4164231 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service wire burnt down. replaced and restored power at 17:00
14289 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-05-22 13:10 | 2011-05-22 15:00 | 3 | 110 | H4121151 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WE HAVE AN UNDERGROUND FEEDING PUMPHOUSE ONLY BAD. CUSTOMER SAID WE COULD WAIT UNTIL SUNDAY MORNING TO CHECK IT OUT. RELEASED BY CREW 074S01 ALL REPAIRS MADE POWER BACK ON..TOOK XFMR OFF AT 13:10 BACK ON AT 15:00//COD 4// VER/DBM IDCC DUP TO OPEN TRANFORMER XXXX
14290 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-12-15 19:16 | 2008-12-15 19:38 | 15 | 22 | 58747-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312202//RELATED TO 58691-1//CUTOUT BREAKING DOWN, HAD TO RE-OPEN LINE TO MAKE REPAIRS//COD 15// VER/DBM L3/KEP IDC XXXX
14291 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-01-22 01:03 | 2008-01-22 01:18 | 22 | 15 | 58797-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409302// GOBLE ENROUTE TO CHANGE CUTOUT// MAY END UP OPENING BREAKER TO SAFELY CHANGE/// @ 0006 ISSUED STEVE HALL >> NRO ON KENWOOOD/AUXIER 12KV CKT. @ 0023- OPENED FUSES AT POLE 858-153 CC 22 *** @ 0030 STEVE REPORTS FUSES WOULD NOT OPEN.. NOT OUTAGE AT THIS TIME FEEDER MAY NEED TO BE OPENED. *** FEEDER OPENED AT 0103 CLOSED AT 0104 *** 22 CUST OUT AT 0103 RESTORED AT 0118 AT POLE 858-153 SEE ORDER 58824-1 FOR FEEDER OUTAGE. 3409302// **** 22 CC OUT FROM 0103 REST AT 0118 VER/PDP IDC XXXX
14292 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2014-10-25 17:00 | 2014-10-25 22:30 | 1 | 330 | 4661731 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | ELBOW POPPED OFF AGAIN ON B PHASE RELEASED BY CREW 076S01.ON SITE CHECKING NOW())).PADMOUNT 785-1692 IS FEED FROM POLE 785-1264) NOT 785-959.OPENED @20:45 OPENED FUSES TO XFMER REPAIRES MADE CLOSED BACK IN @22:30 VER/KEP
14293 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2016-04-07 06:45 | 2016-04-07 06:55 | 33 | 10 | H4061781 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 454-6509, POLE454-6531 BURNT OFF, TRUCK OK/// CUT LOOP AT FUSE FUSE FED BOTH DIRECTIONS TIME ON 0514/// T&G TO BRENT T AT 454-6509 RELEASED BY CREW 078S11,,CREW ON SITE,,REPAIRS MADE,,OPENED FUSE 454-6509 TO REPLACE JUMPER @0645,,,FINAL RESTORATION AT 0655 DUP OF 4061781 FOR OUTAGE TO MAKE UP LOOP VER/HFP L3/HFP AJB
14294 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2022-03-07 15:24 | 2022-03-07 15:30 | 55 | 6 | 4580991 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary burnt down// repaired. power restored 15:30
14295 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2020-06-21 16:45 | 2020-06-21 17:15 | 11 | 30 | 4054531 | 330 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced connections one side secondary. xfmer open 16:45, closed 17:15
14296 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-04-30 09:00 | 2010-04-30 11:45 | 2 | 165 | 53002-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER CUTTING ROW THEN REPLACING CREW ON SCENE. POWER WAS RESTORED AT 11:45 D SAMMONS VER/KEP L3/KEP IDC XXXX
14297 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-06-11 09:03 | 2014-06-11 14:33 | 1 | 330 | 4041061 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAS ONLY 1 PH HOT WILL RUNNING OUT LINE,,,C PH BROKEN XFMER RIZER ON POLE 38830206A31073 CUSTOMER HAS ONLY 2PH HOT.TRUCK TO POLE.PSTAMPER RELEASED BY CREW ,078E04REPAIRS MADE ALL CUST RESTOREDPLEASE CLOSE TICKET THANKS.BT VER/HFP L3/HFP
14298 | Paintsville | 3401102 | FALCON | SALYERSVI | 2009-01-10 10:00 | 2009-01-10 12:45 | 2 | 165 | 53903-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401102// BAD BUSHING ON XFMR... OPENED XFMR @ 1000 TO MAKE REPAIRS//CREW ENROUTE//COD 2// REPLACED XFMR. RESTORED AT 12:45 P.M. PLEASE SEND TO P. WYSONG (CUSTOMER SAID TV BURNT UP). SH// EMAILED TO P WYSONG DBM// VER/DBM L3/KEP IDC XXXX
14299 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-01-29 09:11 | 2014-01-29 11:56 | 2 | 165 | 4322991 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY 2 CUSTOMSER PER SERVICER /// COD-2 ISO 37820032A00035 VER/HFP L3/HFP
14300 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2008-11-15 16:20 | 2008-11-15 18:10 | 3 | 110 | 65438-1 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007906/ S. HAMMONDS OPENED FUSE TO SAFELY ISOLATE A BURNING POLE SEE OUTAGE 65407-1 VER/LDA IDCC TOF1519 XXXX
14301 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-06-08 07:50 | 2017-06-08 08:45 | 6 | 55 | 4922281 | 330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 15T ON 38830234000076. MD NEEDED38830234000076 15T LINE FUSE C/O DOOR BURNT UP--REPLACED --IN AT 08:45--ALLGOOD-DS060817 MD ENTERED. VER/AWD
14302 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2017-09-12 20:40 | 2017-09-13 02:09 | 1 | 329 | 4356281 | 329 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED CONNECTION/// VER/DKM L3/HFP XXXHFP
14303 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-12-12 10:17 | 2017-12-12 15:46 | 1 | 329 | 4641231 | 329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3 phase lat pole 38830141D00438 2- 40ts blown--1 c/o broke 19,9--crew req--ds121217 Released by crew 078S013 phase lat pole 38830141D00438 2- 40ts blown--1 c/o broke 19,9--crew req--ds121217/crew on site/FETR 1445/vem3 phase lat pole 38830141D00438 2- 40ts blown--1 c/o broke 19,9--crew req--ds121217/crew on site/FETR 1445/vem/chg 3 c/o on 141-D-438/power restored at 1546/chg 2 c/o 141-D-376/opened at 1456/restored all cust 1523/please close ticket/thanks/vem/ ISO 38830141D00438/ COD 1
14304 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-04-11 16:24 | 2015-04-11 21:53 | 1 | 329 | 4308461 | 329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQ, 6 MEN, 15 KVA, SINGLE BUSHING 7200 120/240, NO TRUCK, BRING TWO WHEEL DOLLEY, CROSS CREEK ON HILLSIDE, CUST HAS METER, I HAVE BLANK OUT, WAS READING 230 PHASE TO GROUND WITH A LOAD ON IT, ALL CONNECTION ARE GOOD ON TRANSFORMER, SO I GUESS TRANSFORMER IS BAD RELEASED BY CREW 078S06//CREW ON SITE///CHANGED XFMR AND DROP///VOLT 124/124/249///TBL TKT COMP///ON @ 21:53 VER/KEP
14305 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-08-03 04:51 | 2010-08-03 10:20 | 1 | 329 | 60659-1 | 329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR IN TWO//COD 1// VER/DBM IDC SERVICER NEEDED CREW WITH BIG BUCKET XXXX
14306 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-05-17 09:58 | 2018-05-17 10:45 | 7 | 47 | 4364281 | 329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Crew opening XFMR and Hot Tap on pole 37830069000105 to tie in wire/ ISO 37830069000105/ COD 7/ 0958-1045
14307 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-03-18 08:51 | 2009-03-18 14:20 | 1 | 329 | 59671-1 | 329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411901// TRANSFORMER CUTOUT IS BROKEN. I AM GOING TO CHANGE CUTOUT. I CAN NOT REACH CUTOUT AND IT IS TOO CLOSE TO WORK OFF POLE. DENNIS IS SENDING A BIG BUCKET LATER ON TO CHANGE CUTOUT. POLE 97-60. RELEASED BY CREW 074S01 - HAD TO COVER LINE BE ON AT APROX.-15:00 R RAY // NO CUSTOMERS ON TRANSFORMER // VER/TOM L3/TOM IDCC PN137 XXXX
14308 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2018-07-05 12:24 | 2018-07-05 13:11 | 7 | 47 | 4728731 | 329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REPLACING POLE
14309 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-12-31 09:01 | 2018-12-31 14:30 | 1 | 329 | 4615051 | 329 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP TO REPAIR////////1 HOT LEG INTO MIDSPAN,MADE NECESSARY REPAIRS.ALL OK AFTERWARDS
14310 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-08-04 12:31 | 2012-08-04 18:00 | 1 | 329 | 4896101 | 329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKE DOWN SET POLE ON FIRE, WILL NEED CREW , WILL HAVE TO LOWER ON POLE. ISOLATED LINE ON POLE 289-6 TOOK CLAMP OFF. LOWER PRIMARY AND GUY AND NEUTRAL, REPLACED CUTOUT AND ARRESTOR AND BRKT., POWER RESTORED.//COD 1//ISO// VER/DBM IDCC PN20 XXXX
14311 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-05-08 06:41 | 2012-05-08 12:10 | 1 | 329 | 4758341 | 329 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD BARRELL CONNECTION AT WEATHERHEAD BURNT NEUTRAL AND POSSIBLY ENERGIZED NEUTRAL GOING INTO HOUSE, REPLACED SERVICE DROP, ALL POWER RESTORED VER/KEP IDC XXXX
14312 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2022-08-13 19:31 | 2022-08-14 01:00 | 1 | 329 | 4737111 | 329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva xfmr, need flaggers and crew. back on at 1am
14313 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-12-21 08:58 | 2012-12-21 14:27 | 1 | 329 | 4498491 | 329 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S08/SERVICER ON SITE/POSSIBLE BAD CONNECTION/VEM/ONE CUST HAS PART POWER/FETR FOR FULL POWER 1500/VEM/RE SQUEEZED SERVICE/CUST HAS FULL POWER 1427/PLEASE CLOSE TICKET/THANKS/ ////VER/CRB L/3 CRB
14314 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-11-07 17:14 | 2008-11-07 17:55 | 8 | 41 | 63114-1 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3116702// 8T ME FUSE LINK BROKE//COD 8// VER/DBM IDC XXXX
14315 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-04-03 12:32 | 2009-04-03 18:00 | 1 | 328 | 64675-1 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409401// ANOTHER FAILED CUTOUT.//COD 1 VER/KEP L3/KEP IDC XXXX
14316 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-10-31 11:57 | 2012-10-31 17:25 | 1 | 328 | 4292281 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 37830226000081, BAD ARRESTOR ON POLE 37830226000128, REPLACED ARRESTOR, POWER RESTORED AT.17:25 -- CAN CLOSE TICKET MWL COD-1 ISO LF 37830226000081 VER/HFP L3/HFP IDC XXXX
14317 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2011-11-03 11:25 | 2011-11-03 12:47 | 4 | 82 | H4046721 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPLACE SERVICE DROP AND REWORK CONNECTION AT TRANSFORMER, OPEN AT 11:25 AND CLOSE AT12:47 VER/KEP IDC XXXX
14318 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2013-01-23 10:02 | 2013-01-23 15:30 | 1 | 328 | 4732461 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER. WILL NEED CREW 15KVA TRANSFORMER CUTOUT AND CUTOUT BRACKET. THIS WILL BE HAND JOB NO TRUCK. THIS ORDER WILL NEED TO BE SENT TO ROW PIKEVILLE WHEN COMPLTED TREES NEED CUT. FROM FUSE POLE 67-73 TO END OF LINE. RELEASED BY CREW 074S11 XFMR REPLACED ON AT 15:30 D SAMMONS// VER/DBM IDC XXXX
14319 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-09-01 09:39 | 2015-09-01 10:20 | 8 | 41 | 4187421 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE APPEARS TO HAVE BROKEN ON 50 KVA XFMR ON POLE38830954D20097. REPLACING CUTOUT. REPLACED CUTOUT AND RESTORED @ 10:20. CUTOUT HAD FAILED. SH VER/CRB L3/DKG
14320 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2010-10-02 11:50 | 2010-10-02 14:34 | 2 | 164 | 56250-1 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUES LINK WAS BROKEN NOT BLOWN. REPLACED 6T FUSE VER/ARN IDC XXXX
14321 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-05-26 01:20 | 2010-05-26 04:04 | 2 | 164 | H50880-1 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AT 0140 , SERVICER OPENED LINE FUSE ON POLE 164-B-171 TO ISOLATE FAULT POLEBAD 19.9 CUTOUT.BAD 19.9 CUTOUT. NO TRUCKS TO POLE.BAD 19.9 CUTOUT. NO TRUCKS TO POLE. RELEASED BY CREW 078S01 IDCC DUP TO OPEN FUSE XXXX
14322 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2016-03-27 07:26 | 2016-03-27 12:54 | 1 | 328 | 4884911 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA === NEED LINE CREW 15 KVA 7200 TRANSF CUTOUT AND T BRACKET === THIS MANUAL === CHANGED TRANSF POWER OK/ ISO 37830394C00235/ COD 1/ VER/BOW
14323 | South Williamson | 3411401 | DEWEY | INEZ | 2012-03-20 11:16 | 2012-03-20 14:00 | 2 | 164 | 4597541 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD PULLED APART ON THIS POLE///I CHANGED CUTOUT TO NEW TYPE WHILE IT WAS OUT///RESTORED AT 14:00//COMPLETE//EM ///VER/CRB IDC XXXX
14324 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-08-23 18:22 | 2021-08-23 23:50 | 1 | 328 | 4141261 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | got bad 15 kva 7200 need transformer and 7200 cutout about four men Released by crew 077S05..all power restored @ 23:50..p.hicks/ ISO 37830128000196/ COD 1
14325 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2021-02-25 08:16 | 2021-02-25 09:38 | 4 | 82 | 4247981 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @220-60, checking. Fuse had melted out, refused @0938.
14326 | Whitesburg | 3401301 | FLEMING | NEON | 2010-12-10 11:22 | 2010-12-10 16:50 | 1 | 328 | 65065-1 | 328 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S11... BAD CONNECTION IN SERVICE ONLY HAD PART POWER, MADE REPAIRS RESTORED POWER AT 16:50//VER/CRB IDC XXXX
14327 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-01-07 11:37 | 2018-01-07 12:59 | 4 | 82 | 4717341 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no answer Cutout door had burnt up, replaced cutout, apr at 1259 close ticket/ ISO 38830478A31064/ COD 4
14328 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2013-01-23 08:32 | 2013-01-23 14:00 | 1 | 328 | 4732051 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NOBODY LIVES HERE, TALKED TO JOEY REED, HE WILL CHANGE CUTOUT AFTER LUNCH. RELEASED BY CREW 079H06. REPLACED CUTOUT//COD 1// VER/DBM IDC XXXX
14329 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-01-08 01:33 | 2017-01-08 02:55 | 4 | 82 | 4276771 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT, FUSE BROKE, POWER RESTORED VER/KEP L3/HFP XXXHFP
14330 | South Williamson | 3200302 | BELFRY | TOLER | 2018-03-28 11:27 | 2018-03-28 12:49 | 4 | 82 | 4137621 | 328 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | One leg of the secondary underground going to the car wash is bad. This is 350 aluminum. Customer said its ok to wait till tomarrow the 29th to make repairs. Released by crew 079S02 Tim Smith created OPS order. 1249
14331 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-06-01 05:26 | 2017-06-01 08:10 | 2 | 164 | 4893091 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR COMPLETE COD-2 ISO TF 38830206C02359 VER/HFP L3/HFP
14332 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-02-20 17:13 | 2015-02-20 18:35 | 4 | 82 | 4058251 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA REPLACING WITH 37.5 TRANSFORMER REPLACEDE ON AT 16:35 D SAMMONS VER/HFP L3/HFP
14333 | Paintsville | 3409302 | KENWOOD | AUXIER | 2019-11-15 01:58 | 2019-11-15 03:20 | 4 | 82 | 4036341 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR cutout is broke will change/// Replaced cutout and restored power @ 03:20
14334 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-01-30 16:58 | 2011-01-30 18:20 | 4 | 82 | 52325-1 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7.2KV CUTOUT//VER/CRB IDC XXXX
14335 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-02-14 21:58 | 2020-02-15 03:26 | 1 | 328 | 4407241 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310503/gaj/2203/all out disp 3144 A Strong..broke cutout on pole 79-2. manual, need 19.9 cutout, line crew and row to cut path to pole..power restored 3:26
14336 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-06-08 17:58 | 2009-06-08 19:20 | 4 | 82 | 57685-1 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACING OLD/BAD #6 OPEN WIRE SECONDARY//VER/CRB IDC XXXX
14337 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2016-04-09 21:06 | 2016-04-09 23:50 | 2 | 164 | 4076701 | 328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BURNT INTO. AT SEC POLE . LOOKS LIKE WIRE HEATED UP IN ONE OF THE HOT CONNECTIONS MELTED THE INSULATION AND GOT INTO THE NEUTRAL BURNING IT INTO. MADE REPAIRS EVERYTHING OK. SEND COPY TO PEGGY IN DAMAGE CLAIMS CUST SAID HE CHECKED EVERYTHING AND HIS REFRIGERATOR IS NOT WORKING NOW. THIS IS 200AMP 2/3 WIRE. SEND COPY TO ENG ALSO THIS CUST IS AROUND 267 FOOT FROM THE TRANSFORMER 1/0 FROM THERE TO SEC POLE 212-251 MAY NEED TO ADD 1/0 TO THE NEXT SEC POLE 212-219 VER/KEP
14338 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-09-08 13:51 | 2014-09-08 15:40 | 3 | 109 | 4480161 | 327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 078S01 30T FOR C PHASE @ 38830118D26534 RESTORED. VER/CRB
14339 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2015-05-06 07:53 | 2015-05-06 13:20 | 1 | 327 | 4394411 | 327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 277/480 SINGLE BUSHING 7200 XFORMER. NEED LINE CREW, TRUCKS TO POLE . THIS IS B PHASE XFORMER. OPENED ALL XFORMERS ON TRANSFER BANK AT 09:25. 100 KVA RELEASED BY CREW 078S01CREW SETTING UP TO CHANGE TRANSFORMERCREW SETTING UP TO CHANGE TRANSFORMER NEW TRANSFORMER SERIAL NUMBERS HI-2020612411 OLD SERIAL NUMBERS GE-PO49405-YNAHI-2020612411 OLD SERIAL NUMBERS GE-PO49405-YNA TIME ON 1320 VER/CRB L3/DKGXXX
14340 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2017-11-19 09:48 | 2017-11-19 15:15 | 1 | 327 | 4582711 | 327 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE-IN PULLED OUT ON ONE HOT LEG AT HOUSE 70, POLE 67-18. Released by crew 074E02 . replaced all connections at entrance , ALL WORK COMPLETE / GXJ
14341 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-04-25 11:41 | 2012-04-25 13:30 | 3 | 109 | 4706551 | 327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN.. VER/KEP IDC XXXX
14342 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-06-01 15:03 | 2020-06-01 19:15 | 2 | 252 | 4940791 | 327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary broke at dead end @95-17 going to 95-199, 1 span of primary down, this will take a 3 man line crew and a manual tree crew to put back up, pole on hillside, also will need some #2acsr. Rick Ray crew coming to make repairs. Only 1 customer out at this time. Released by crew 074S05 // Opened line fuse on 37830095000017 to make repairs @ 1800 // COD 1 //
14343 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-03-22 15:21 | 2022-03-22 17:10 | 3 | 109 | 4658601 | 327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans fuse open at 260-16,Will be trying to get it back In..Trans fuse open at 260-16,Broke Trans Cutout,Made Repairs and restored at 17:10.
14344 | Pikeville | 3413402 | GARRETT | LACKEY | 2009-03-07 15:46 | 2009-03-07 17:35 | 3 | 109 | 56064-1 | 327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT . REPLACED CUTOUT AND ARRESTER.//3413402//VER/CRB IDC XXXX
14345 | Hazard | 3309003 | JEFF | VIPER | 2019-07-28 13:53 | 2019-07-28 19:20 | 1 | 327 | 4800561 | 327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 KVA transformer need this is a CSP NEED TRANSFORMER cutout and t brackret 7200 lf offf @ 1735 on @ 1920 ¦¦ CHANGED THE TOF TO ORIGINAL TIME SINCE ORIGINALLY THE CUSTOMER REPORTED NO POWER @ 1353 - L3/HFP
14346 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-09-05 17:18 | 2016-09-05 22:45 | 1 | 327 | 4869731 | 327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 7200 120/240 RELEASED BY CREW 077S01 REPLACED TRANSFORMER.077H18/// VER/DKM
14347 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-11-22 07:07 | 2019-11-22 09:50 | 2 | 163 | 4055081 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout
14348 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-06-22 10:49 | 2022-06-22 16:15 | 1 | 326 | 4274671 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken C/O // Making repairs // Restored @ 16:15
14349 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-01-07 18:14 | 2017-01-07 23:40 | 1 | 326 | 4275991 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT ON 39831047000145.XFMR OPEN ON P47-145 BAD15 XFMR BRING 25 AND NEW RISERS CO&T BRACKETXFMR OPEN ON P47-145 BAD15 XFMR BRING 25 AND NEW RISERS CO&T BRACKET RELEASED BY CREW 078H06 VER/KEP L3/HFP XXXHFP
14350 | Hazard | 3303902 | LESLIE | WOOTON | 2010-07-01 14:49 | 2010-07-01 20:15 | 1 | 326 | 61331-1 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSF == GAS CO HAS TROUBLE ON THERE LINE BURNED TRANSF UP == REPLACED TRANSF POWER OK//COD 1// VER/DBM IDC XXXX
14351 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-20 17:04 | 2009-06-20 22:30 | 1 | 326 | 66488-1 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR. WILL CALL DUTY SUP. FOR CREW //VER/GAH
14352 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-03-16 03:42 | 2022-03-16 09:08 | 1 | 326 | 4629731 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines Bad cutout will replace
14353 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-10-26 08:31 | 2012-10-26 13:57 | 1 | 326 | 4173211 | 326 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CHECKED ADJACENT METERS AND THIS APPEARS TO BE THE ONLY ONE AFFECTED. BAD UG SERVICE. CREW ENROUTE TO INSTALL AUTO-XFMR UNTIL FAULT CAN BE LOCATED. RELEASED BY CREW 076S02// CREW ON SITE TCM// AUTO TRANSFORMER INSTALLED , PLEASE SEND COPY TO BILL JOHNSON TO LOCATE FAULTED CABLE,TCM//EMAILED TO B JOHNSON// VER/DBM IDCC CNT4, MCCDL XXXX
14354 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2017-05-02 20:39 | 2017-05-03 02:05 | 1 | 326 | 4737751 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD NEUTRAL IN UNDERGROUND SERVICE, CREW REQUIRED TO INSTALL POWERTEMP. METER LOCATED ON COVERED BACK PORCH. RELEASED BY CREW 078H11,PLACED POWERTEMP CUST RESTORED @ 0205 PLEASE CLOSE TICKET THANKS.BT// VER/DBM
14355 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2011-05-13 16:17 | 2011-05-13 19:00 | 2 | 163 | 4085781 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT BAD CUTOUT ON POLE 188-A-1. I HAVE CUTOUT CHANGED FUSED UP EVERYTHING OK.//COD 2// VER/DBM
14356 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-12-19 16:07 | 2008-12-19 18:50 | 2 | 163 | 60604-1 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT ON POLE 379-205, LIFTED HOT TAP ON 379-13. ONE CUST OUT. NEED LINE CREW TO LOWER EQUIPMENT. RELEASED BY CREW 078S01 COD-2 L3/HFP IDCC TOF1507, CUSTOMER CALLED UNTIL 1530 BUT STILL NOT REPORTING OUTAGE, ESTIMATING TIME OFF XXXX
14357 | Pikeville | 3409502 | BURDINE | LEVISA | 2014-06-29 07:16 | 2014-06-29 12:42 | 1 | 326 | 4166851 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT DOOR IS BURNED UP. I AM GOING TO GO INTO PIKEVILLE AND PICK UP NEW CUTOUT AND FIX PROBLEM. RELEASED BY CREW 074S01TRANS. CUTOUT DOOR IS BURNED UP. I AM GOING TO GO INTO PIKEVILLE AND PICK UP NEW CUTOUT AND FIX PROBLEM. I CHANGED DOOR.//COD 1// VER/DBM
14358 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2018-11-11 11:37 | 2018-11-11 14:20 | 2 | 163 | 4389411 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CUTOUT AND 15 KVA 7200 XFMR L3/HFP
14359 | Pikeville | 3413402 | GARRETT | LACKEY | 2014-01-28 13:04 | 2014-01-28 18:30 | 1 | 326 | 4319741 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6T FUSE OUT DUE TO BAD 5KVA TRANSFORMER. CALLED TIM HALL CREW ON THE WAY TRANSFORMER CHANGED OUT EVERYTHING OK CHANGED TO 10KVA VER/SEF IDC XXXX
14360 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-12-29 09:29 | 2008-12-29 14:55 | 1 | 326 | 64864-1 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WILL CHECK COMPLAINT OUTSTS WR # 27821269 //1 LEG OF 4/0 UG SERV IS BAD,CONTACTED PVILLE ABT MATERIALS,HELP,ETC. RELEASED BY CREW 074S06///DEH - FOUND LOOSE CONNECTION AT TRANSF (CSP). WE ARE GOING TO REPLACE TRANS WITH 25KVA CONVENTIONAL. ETR - 15:00.STS RELEASED BY CREW 074S06///DEH - FOUND LOOSE CONNECTION AT TRANSF (CSP). WE ARE GOING TO REPLACE TRANS WITH 25KVA CONVENTIONAL. ETR - 15:00. RESTORED AT 14:55. MISSED ARRIVED BUTTON, ARRIVED AT JOBSITE AT 14:10 L3/KEP IDC XXXX
14361 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-06-18 23:12 | 2015-06-19 01:55 | 2 | 163 | H460231 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ** SEE 460231** POLE 38831077D00667 IS BROKE. MAP SHOWES IT TO BE 38831077D00655 WILL NEED 35 CLASS 5 LINE CREW LINE TRUCK & MATERIAL HANDLER. 1 MANUAL TREE CREW RELEASED BY CREW 074S04/ 1 CUSTOMER OUT ORIGINALLY/ OPENED TRANSFORMER 38831077D00164 @ 23:12 (2 CUSTOMERS) CLOSED @ 01:55 (3 CUSTOMERS)/ ISO 38831077D00164/ COD 3/ DUPLICATE IN HOIS/ VER/BOW
14362 | Hazard | 3301101 | CHAVIES | CHAVIES | 2014-11-16 13:45 | 2014-11-16 16:28 | 2 | 163 | 4731981 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT , CHANGED CUTOUT , CLOSED XFMR FUSE BACK @ 16:28 VER/CRB
14363 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-05-21 19:19 | 2018-05-21 22:02 | 2 | 163 | 4389661 | 326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse was broke/ ISO 38830211000232/ COD 2
14364 | Whitesburg | 3401301 | FLEMING | NEON | 2022-10-09 16:20 | 2022-10-09 21:45 | 1 | 325 | 4009351 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 307-93. will need 25 kva 7200 and big bucket in order to change. P. Hicks and crew are coming to change transformer out
14365 | Pikeville | 3407101 | TOPMOST | DEMA | 2012-07-09 12:10 | 2012-07-09 17:35 | 1 | 325 | 4642891 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED ARRESTER AND REFUSED TRANSFORMER CUTOUT, ALL WORK COMPLETE / GXJ IDC XXXX
14366 | Pikeville | 3413402 | GARRETT | LACKEY | 2016-06-26 04:20 | 2016-06-26 09:45 | 1 | 325 | 4476951 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | WILL WORK AFTER DAYLIGHT.. GUY WIRE CAME LOSE FROM WRAP AND LAID AGAINST PRIMARY RISER AT TOP OF TRANSFORMER.. REPAIRED GUY AND CLOSED TRANSFORMER BACK IN AT 9:45 VER/CRB
14367 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2018-08-12 09:50 | 2018-08-12 15:15 | 1 | 325 | 4942611 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad tran .15kva, 7200-crew req-ds081218 Released by crew 078S01,repairs made all cust restored @ 1515 please close ticket thanks.bt
14368 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-04-03 07:44 | 2015-04-03 13:09 | 1 | 325 | 4262531 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 079S02 BAD TRANSFORMER CUTOUT. NO TRUCK ACCESS. RELEASED BY CREW 079S02/// 1248-1309RELEASED BY CREW 079S02 BAD TRANSFORMER CUTOUT. NO TRUCK ACCESS. I OPENED THE TAP AT 12:48, ALL IS BACK ON AT 13:09./ ISO 38821138C00132/ COD 1 L3/DKGXXX SEE 4264461 FOR OPENING OF LINE FUSE
14369 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2016-03-28 06:35 | 2016-03-28 12:00 | 1 | 325 | 4886251 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 162-32 BAD CUTOUT ALSO POLE 162-4004 SEC. NU BROKE OPENED TRANS. BANK 07:50 AM NEED LINE CREW AND TREE CREW RELEASED BY CREW 078S08,,,CREWS ON SITE,,WILL REPLACE CUTOUT AND WAIT FOR TREE CREW TO COMPLETE THEIR WORK BEFORE ENERGIZING,,ALL REPAIRS MADE,,ALL POWER RESTORED VER/CRB
14370 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2018-07-23 20:45 | 2018-07-23 21:10 | 13 | 25 | 4843351 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Released by crew 078H08transformer off at 20:45 to resqueeze connection. Back on at 21:10
14371 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-05-23 09:25 | 2012-05-23 10:30 | 5 | 65 | 4822101 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER ON POLE 52-114 , NOT 52-114 IS OUT THAT SERV ONE CUST. BAD CUTOUT POLE # WAS52-114 NOT 53-114 VER/KEP IDC XXXX
14372 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-08-22 03:08 | 2018-08-22 08:33 | 1 | 325 | 4986231 | 325 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TRIED TO CALL CUSTOMER NO ANSWER : Dispatched in accordance with KYPCo Late Night Callout Guidelines .TRIED TO CALL CUSTOMER NO ANSWER : Dispatched in accordance with KYPCo Late Night Callout Guidelines. bad connection at xfmr , restored power at 08:33 L3/HFP
14373 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-06-07 15:42 | 2012-06-07 21:07 | 1 | 325 | 4891661 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER OUT WILL BE TRYING NEED 15 KA TRANSFORMER 134 FEET 2/3 2MEN RIGHT OF WAY CREW 7200 POWER ON 21:07 VER/ARN IDC XXXX
14374 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-02-27 10:45 | 2009-02-27 11:10 | 13 | 25 | 52129-1 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-13 // CREW HAD TO OPEN LINE FUSE TO SAFELY REPLACE CUT OUT ...RELATED TO ORDER 52130-1 L3/HFP IDC XXXX
14375 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-01-19 22:45 | 2022-01-19 23:50 | 5 | 65 | 4388331 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout at pole 190-C-171,Got my Trans IsolatedBroke cutout at pole 190-C-171,Will be making repairs..
14376 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-11-26 03:05 | 2017-11-26 08:30 | 1 | 325 | 4602161 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 LEG OF 34UG SERV BURNED OFF AT A DISC SWITCH RIGHT AT A POTHEAD CONNECTION.WILL NEED TO REPLACE/REPAIR.WILL NEED FLAGGERS,CREW,ETC.
14377 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-02-10 05:05 | 2016-02-10 10:30 | 1 | 325 | 4686421 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRUCK OK HAVE ALREADY TALKED WITH BOB R ABOUT LOCATION, CREW REQUIRED//// RELEASED BY CREW 078S11 ISO 38830212000114 COD 1 VER/AWD
14378 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-06-04 06:21 | 2016-06-04 11:46 | 1 | 325 | 4294901 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE VER/CRB
14379 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-11-13 13:13 | 2021-11-13 14:18 | 5 | 65 | 4088931 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced cutout On @ 1418
14380 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2016-06-16 10:05 | 2016-06-16 15:30 | 1 | 325 | 4362191 | 325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD TRANSFORMER TRUCK OK RELEASED PLEASE DON`T FOR GET THE FETRCREW REQUIRED BAD TRANSFORMER TRUCK OK COD-1 ISO TF 38830213000125 VER/HFP L3/HFP
14381 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2022-05-11 08:46 | 2022-05-11 14:10 | 1 | 324 | 4876381 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 100kva 19.9. truck acc Released by crew 077S10 replaced transformer power restord at 14:10
14382 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-12-13 19:17 | 2013-12-13 21:05 | 3 | 108 | 4160471 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD BURNED OUT OF A HOT TAP CLAMP AT POLE 214-191. BILL CAMBELL IS COMING TO HELP FLAG TRAFFIC.//COD 3//ISO 37830214A00191// VER/HFP L3/HFP
14383 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-04-02 08:36 | 2012-04-02 14:00 | 1 | 324 | 4639071 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS FUSE BLOWN ON BANK -- 10 KVA 480 VOLT-- SEND TO TIM SMITH RELEASED BY CREW 077S10 RELEASED BY CREW 077H02 VER/HFP L3/HFP IDC XXXX
14384 | Pikeville | 3421001 | BREAKS | CITY | 2015-09-26 13:06 | 2015-09-26 15:48 | 2 | 162 | 4274831 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED UP,WILL REPLACE//////////////REPLACED CUTOUT AND RESTORED COD-2 ISO TF 37820220D00308 VER/HFP L3/HFP
14385 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-08-27 13:33 | 2008-08-27 16:15 | 2 | 162 | 56291-1 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401302//BAD CUT OUT IM GOING TO REPLACE THE CUTOUT//COD 2// VER/DBM IDC XXXX
14386 | Hazard | 3301101 | CHAVIES | CHAVIES | 2009-08-13 20:31 | 2009-08-13 22:19 | 3 | 108 | 57186-1 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NETURAL WIRE BROKE AND ALSO CUTOUT BROKE VER/KEP L3/KEP IDC XXXX
14387 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2015-01-16 09:53 | 2015-01-16 10:02 | 36 | 9 | 4938601 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL L/F OPENED//LINE FUSE CUTOUT ARCING. OPENED LINE FUSE 38830954B30487 @ 9:53, REPLACED CUTOUT AND CLOSED @ 10:02. SH RELEASED BY CREW 076S02 VER/CRB L3/HFP XXX AJB
14388 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-12-13 14:40 | 2017-12-13 16:28 | 3 | 108 | 4646691 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change broke cutout
14389 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2014-07-01 10:23 | 2014-07-01 15:47 | 1 | 324 | 4178581 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 25T FUSE OUT DUE TO INSULATOR PULLED OFF OF PIN. DUE TO DIFICULT LOCATION CUST IS OK WITH MAKING REPAIRS IN THE MORNING. I MADE AN OPS ORDER SO WE CAN CLOSE THIS ORDER OUT. OPS # 036242611 WR# 54179596 RELEASED BY CREW 074S11 COD-1 ISO LF 37830066D00015 VER/HFP L3/HFP
14390 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-12-13 12:25 | 2020-12-13 14:13 | 3 | 108 | 4764691 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Lead burnt almost into @ xfm ///Opened xfm @ 13:42 replaced secondary riser and bad connections ///Restored service @ 14:13/// Customer may have damages LR- The 1st CC call came in at 12:25 as part out
14391 | Hazard | 3309903 | SLEMP | BEECH FORK | 2014-02-13 08:59 | 2014-02-13 10:47 | 3 | 108 | 4379711 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FEEDER WILL NEED TO BE OPENED TO ISOLATE PRIMARY METERING FAULT . FEEDER WAS LOCKED OUT FROM 0859- RESTORED AT 1047 VER/HFP L3/HFP
14392 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-12-17 17:39 | 2010-12-17 19:00 | 4 | 81 | 53728-1 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP TO XFMR CUTOUT HAS BROKEN...WILL REPLACE....//...REPLACED HOT LINE CLAMP....CLOSED XFMR...POWER ON.....JRV...12/17/10 VER/TOM IDC XXXX
14393 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-06-01 14:11 | 2013-06-01 15:05 | 6 | 54 | 4205671 | 324 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG ON XFMR BURNED INTO , ONLY ONE CUST. WITH PART POWER. COD-6 ISO SO 38831083D30025 VER/HFP L3/HFP IDCC CCO XXXX
14394 | South Williamson | 3411401 | DEWEY | INEZ | 2013-12-14 20:57 | 2013-12-14 22:45 | 3 | 108 | 4162351 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LATERAL FUSE BLOWN AND XFMR FUSE AT END OF TAP ALSO BLOWN//DONT SEE ANYTHING //GOING TO REFUSE//ARCING AROUND CUTOUT AND ARRESTOR ON POLE 197//I REPLACED BOTH///RESTORED AT 22:45//COMPLETE//EM VER/HFP L3/HFP
14395 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-06-09 07:02 | 2009-06-09 08:50 | 3 | 108 | 58841-1 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT FUSE REPLACEDBAD CURRENT FUSE ON TRANS. BUSHING VER/KEP L3/KEP IDC XXXX
14396 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-08-03 11:22 | 2011-08-03 13:10 | 3 | 108 | 4658981 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INS. BROKE @ 24-569// OPENED LINE FUSE ON 24-68 @ 12:15// CREW IN ROUTE TO REPAIR// REPAIRS MADE// POWER IS RESTORED// VINES NEEDS CUT ALL AROUND 24-569 OR THIS WILL HAPPEN AGAIN SOON// SEND TO C. FARMER VER/KEP IDCC CNT16 XXXX
14397 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-11-04 11:06 | 2014-11-04 16:30 | 1 | 324 | 4698621 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RELEASED BY CREW 078H06,,CREW ON SITE,,SPLICE CAME APART ON OPEN WIRE SECONDARY,,ALL REPAIRS MADE,,ALL POWER RESTORED COD-1 ISO SO @ 38830356000016 VER/HFP L3/HFP
14398 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-11-23 18:28 | 2015-11-23 21:10 | 2 | 162 | 4481521 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//NO ANSWER// CREW REQ, BROKE C/O, HANGING CLOSE TO NEUTRAL, WILL NEED TWO MAN BUCKET TO CHANGE SAFETLY, HOUSE NUM ON MAIL BOX, TWO STORY BRICK HOUSE, NO SURE WHERE SEPTIC TANK IS RELEASED BY CREW 078S06.CREW ON SITECUTOUT REPLACED.ALL POWER RESTORED// VER/ ADH
14399 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-12-27 14:22 | 2011-12-27 16:10 | 3 | 108 | 4205931 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. FOUND SECONDARY CONNECTION HEATING UP THAT IM GOING TO REPAIR WHILE IM HERE. REPAIRED CONNECTION AND REPLACED CUTOUT. RESTORED @ 16:10. SH ////VER/CRB IDC XXXX
14400 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-12-02 20:19 | 2018-12-02 23:01 | 2 | 162 | 4501611 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | windstream pole 1148 - 163, 35-5 sec pole rotten, danger of falling. to r.virgen Released by crew 078S07--crew on site--replaced 30cl6 WS Pole w/35cl5--trans. 4/0Sec and 2-2/3 serv.D/D Lt..---all pwr restored at 23:01---tbl tkt comp ---rmv// /// PER VOICE RECORDER REPAIR CREW WAS PULLING CUSTOMERS METERS - 2 CUSTOMERS - NO TIMES STATED SHOWING 2 CUST OFF 5 MINUTES AFTER CREW ARRIVED (PER VOICE RECORDER CREW ARRIVED 2014) L3/HFP
14401 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-07-07 13:48 | 2012-07-07 16:30 | 2 | 162 | 4575561 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LEAKING TRANSFORMER FOUND- REPLACING WITH A 100KVA ------- REPLACED LEAKING TRANSFORMER, OPENED AT 15:45, CLOSED AT 1630 -- CAN CLOSE TICKET MWL
14402 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-04-09 20:34 | 2013-04-09 22:22 | 3 | 108 | 4992881 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRING NEUTRAL CONNECTION VER/KEP IDC XXXX
14403 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-01-21 18:02 | 2011-01-21 19:50 | 3 | 108 | 63470-1 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1ST SERVICERS TRUCK BROKE DOWN STS FUSE BROKE IN TWO. POWER RESTORED FUSE ACTUALLY BROKEN AT TOP BETWEEN WELD AND FUSE TAIL SERVICER SAID HE HAD SEVERAL LIKE THIS RECENTLY VER/KEP L3/KEP IDC XXXX
14404 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-11-11 13:09 | 2018-11-11 15:51 | 2 | 162 | 4389671 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED BAD 25XFR WITH A 37.5//////////RESTORED,ALL OK L3/HFP
14405 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-03-06 20:51 | 2021-03-07 02:15 | 1 | 324 | 4310941 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | cable booster out per cable co rep, sees fuse hanging down// Replaced broken cutout, also have a bad 12kv----10kva txmf, crew required. truck ok. Be best to bring small squirt boom to change. Pole # 477-59 Released by crew 078S11//replaced xfmr
14406 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-03-05 15:08 | 2011-03-05 17:50 | 2 | 162 | 50106-1 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39051517 // ONLY A PHASE OUT 2 CUSTOMERS, BROKEN CUTOUT, NO TRUCK, C. YOUNGMAN IN ROUTE FOR ASSISTANCE. CUTOUT REPLACED, APO COD-2 ISO LF 38830206B02094 VER/HFP L3/HFP IDC XXXX
14407 | Pikeville | 3409502 | BURDINE | LEVISA | 2014-05-10 15:03 | 2014-05-10 17:45 | 2 | 162 | 4682891 | 324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT HAS BROKEN DOWN ON POLE 37830334A40120. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. VER/CRB
14408 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-02-18 11:52 | 2011-02-18 17:15 | 1 | 323 | 58866-1 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 15KVA TRUCKS OK/SEND TO JOE HEMLEPP RELEASED BY CREW 078S03/ CREW ON SITE/// XFMER REPLACED & POWER RESTORED @ 17:15 J. HEMLEPP 078H05//VER/CRB IDC XXXX
14409 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2013-01-11 09:48 | 2013-01-11 15:11 | 1 | 323 | 4595451 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 220-142. CREW ENROUTE RELEASED BY CREW 074S02 ///VER/CRB L/3 CRB IDC XXXX
14410 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-04-22 16:02 | 2016-04-22 21:25 | 1 | 323 | 4116611 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA 7.2 KV / 120/240, SMALL MATERIAL HANDLER . REPLLACED TRANSFORMER , ALL WORK COMPLETE / GXJ VER/AWD
14411 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-04-15 17:12 | 2011-04-15 22:35 | 1 | 323 | 57170-1 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39594170 //, POLE IS BURNT OFF, WIRE CROSSES ROAD, LINE FUSE BLOWN ON POLE 177-10, POLE BURNT OFF IS 98, LINE FUSE CUTOUT WAS ALSO BAD ON POLE 10//VER/CRB IDC XXXX
14412 | Whitesburg | 3308402 | BECKHAM | CARR CREEK | 2009-03-26 18:22 | 2009-03-26 23:45 | 1 | 323 | 61897-1 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF, ONLY 1 CUST LEFT OUT//3308402. POLE # 327-177 IS BURNT OFF, ISOLATED AT 327-147. CREW NEEDED. BAD CUTOUT VER/PDP IDCC PN177 XXXX
14413 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-06-02 19:12 | 2009-06-03 00:35 | 1 | 323 | 61454-1 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA CREW REQUIRED/TRACK BUCKET REQUIRED RELEASED BY CREW 078S03//VER/CRB
14414 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-02-07 18:52 | 2015-02-08 00:15 | 1 | 323 | 4999421 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA XFMR BAD.HAND JOB NEED 3 MAN CREW. VER/CRB L3/HFP XXX
14415 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2019-09-04 08:55 | 2019-09-04 14:18 | 1 | 323 | 4978091 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10 kva xfmr.truck access,,, ryan newsome to change.. Released by crew 076S01.. changed transformer and stored power at 14:18.. complete rn
14416 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-11-13 08:10 | 2008-11-13 13:33 | 1 | 323 | 64373-1 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303903// CUTOUT WENT BAD BURNING POLE INTO, CALLED FOR CREW TO CHANGE OUT RELEASED BY CREW 077S01// HAD TO OPEN RELOSER TO SAFELY TRANSFER CONDUCTORS TO NEW POLE// MAFC ADDED OUTAGE FOR RECLOSER SEE TT H64373-1
14417 | Pikeville | 3311401 | REEDY STATION | DEANE | 2016-01-18 20:25 | 2016-01-19 01:48 | 1 | 323 | 4629811 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PATROLLING//LOOPED BURNT OPEN @ POLE 283-116//LOOP SLEEVE BURNDT INTO ON POLE 283-116, WILL REQUIRE 3 FT. 556 WIRE, 2 LOOP SLEEVES, BIG BUCKET, AND ANOTHER A LINEMAN.//166 COD FROM BEGINNING OF OUTAGE//ISO 37830283000116//COD 166//OPENED FEEDER BREAKER @ 0120 01/19/16 TO MAKE REPAIRS (SEE ORDER 4630571)//SEE DOL CASE 632712 FOR SWITCHING// RELEASED BY CREW 075H02
14418 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2016-01-18 20:25 | 2016-01-19 01:48 | 1 | 323 | 4629811 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PATROLLING//LOOPED BURNT OPEN @ POLE 283-116//LOOP SLEEVE BURNDT INTO ON POLE 283-116, WILL REQUIRE 3 FT. 556 WIRE, 2 LOOP SLEEVES, BIG BUCKET, AND ANOTHER A LINEMAN.//166 COD FROM BEGINNING OF OUTAGE//ISO 37830283000116//COD 166//OPENED FEEDER BREAKER @ 0120 01/19/16 TO MAKE REPAIRS (SEE ORDER 4630571)//SEE DOL CASE 632712 FOR SWITCHING// RELEASED BY CREW 075H02//
14419 | Hazard | 3303902 | LESLIE | WOOTON | 2012-11-20 16:52 | 2012-11-20 22:15 | 1 | 323 | 4411821 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRM FUSE BLOWN,..BAD 25KVA, 19.9 XFRM..120/240 V. CALL SOMEONE OUT TO BRING ME A XFMR PLEASE..P.HICKS.REPLACED BAD XFMR..ALL POWER RESTORED..P.HICKS ///VER/CRB L/3 CRB IDC XXXX
14420 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-03-04 05:37 | 2015-03-04 11:00 | 1 | 323 | 4096291 | 323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT START TIME// BAD CO 38830115C00263WILL WORK AT START TIME// BAD 19.9 CO POLE 115C263. LINE FUSE POLE 38830115D00329 OPEN RELEASED BY CREW 078S07.. CREW ON SITE REPAIRING ETR 12:00 VER/CRB L3/DKGXXXX
14421 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-05-11 18:49 | 2009-05-11 21:30 | 2 | 161 | 62580-1 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT IS BROKE ON POLE # 179-74, CALLING FOR CREW. COMPLTED KN
14422 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-01-05 14:20 | 2011-01-05 14:43 | 14 | 23 | 58976-1 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TR @ 1420 CONNECTIONS BAD ON SERVICE...P.HICKS COD-14 ISO TF 37830272A40505 VER/HFP L3/HFP IDC XXXX
14423 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2022-12-25 18:13 | 2022-12-25 23:35 | 1 | 322 | 4357631 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 120/240 send to levi grayson Released by crew 078S09
14424 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-09-27 05:37 | 2018-09-27 10:59 | 1 | 322 | 4164061 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans. fuse open @1150-106, checking. Bad 10 kva trans. 7200, no truck access. Released by crew 074S05// Arived and waiting on crew/// replaced bad 10kva with a 15kva restored power at 10:59 Tim McCoy
14425 | South Williamson | 3200302 | BELFRY | TOLER | 2011-02-08 13:36 | 2011-02-08 16:17 | 2 | 161 | 55334-1 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38738450 // XFMR FUSE OUT ......CUTOUT DOOR DETERIORATED.....WILL REPLACE DOOR & RE-FUSE....//......REPLACED DOOR....RE-FUSED....POWER STAYED ON ABOUT 3 MINUTES...THEN FUSE BLEW AGAIN....NEED CREW....& 15 KVA 7.2 KV.....TRUCK ACCESS....PLS SEND TO JOEY REED RELEASED BY CREW 080S01 VER/HFP L3/HFP IDC XXXX
14426 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-10-01 06:38 | 2009-10-01 12:00 | 1 | 322 | 60660-1 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WILL DISPATCH AT REG WORK TIME.BAD URD BILL LYNCH WILL INSTALL POWERTEMP RELEASED BY CREW 078S05---CREW WILL INSTALL POWER TEMP---POWER ON AT1200--POWER TRMP INSTALLED---ONLY ONE CUST OUT--- VER/KEP L3/KEP IDC XXXX
14427 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-12-08 14:09 | 2009-12-08 16:50 | 2 | 161 | 56521-1 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT, ALL WORK COMPLETE / GXJ//COD 2// VER/DBM IDC XXXX
14428 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-04-01 13:29 | 2022-04-01 16:10 | 2 | 161 | 4713011 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25KVA 7200, truck access. Released by crew 077S04 power restored at 16:10
14429 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-19 10:14 | 2008-06-19 11:00 | 7 | 46 | 50705-1 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT/ VER-IN PO - HFP VER/HFP
14430 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-12-26 14:34 | 2015-12-26 17:15 | 2 | 161 | 4562451 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV C/O RELEASED BY CREW 078S07.. CREW ON SITE ETR 17:30.. CUTOUT CHANGED AND CUSTOMERS RESTORED AT 17:15 TICKET COMPLETE CY// VER/ ADH
14431 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-08-03 16:58 | 2011-08-03 22:20 | 1 | 322 | 4661021 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830181D00101, BAD LOCATION, NEED 6 WHEELER AND TREES CUT, CREW IN ROUTE, GOING TO OPEN FUSE AND GROUND AT POLE 181-2, ALL POWER RESTORED, 30T FUSE ON POLE 181-2, XFMR ON THIS POLE IS NOT ON THIS FUSE, PLEASE ADD TO MAP. ALSO SEND TICKET TO TECH TO RELOCATE POLE 181-101. POLE IS WASHED OUT AND LEANING BAD.//COD 1// VER/DBM STC, CDC92, LCD38830181000002, PER PHONE CONF
14432 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2009-06-20 03:08 | 2009-06-20 08:30 | 1 | 322 | 60766-1 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000601//CREW REQUIRED BAD TRANSFORMER 25 KVA NO TRUCKS BRING BAG TO PUT TRANSFORMER IN SPIT OIL BUT NONE ON GROUND/2ND HOUSE ON LEFT UP CORY FROM GRAHN RELEASED BY CREW 078S03---POLE ON ROCK CLIFT, WILL NEED TO BE TROLLEYED,CAR IN THE WAY--- VER/ARN
14433 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-07-21 20:23 | 2019-07-22 01:45 | 1 | 322 | 4753081 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200-120/240 25kva.pole 1123-572. trk to pole, chage arrestor gone after shot of lightning Released by crew 078S07
14434 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2017-05-23 12:30 | 2017-05-23 17:52 | 1 | 322 | 4842611 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR.RYAN NEWSOME BRINGING ONE VER/CRB
14435 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-04-09 16:49 | 2019-04-09 19:30 | 2 | 161 | 4075461 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | B phase trans fuse blown.bad arrestor.replaced arrestor.restored power at 19:30
14436 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-02-01 14:44 | 2008-02-01 17:25 | 2 | 161 | 64101-1 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410502// FAILED CUTOUT CAUSE POLE FIRE//CHANGED POLE//RESTORED @ 1725//COD 1// VER/DBM IDCC CNT1 ASSUMED TIME OFF AND CHANGED FROM 1143 XXXX
14437 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-08-07 13:39 | 2015-08-07 16:20 | 2 | 161 | 4109851 | 322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR C/O BAD ON POLE 244-152, WILL CHANGE./// C/O REPLACED, POWER RESTORED./ ISO 37830244000152/ COD 2/ VER/BOW
14438 | Hazard | 3303901 | LESLIE | HYDEN | 2019-02-15 19:44 | 2019-02-16 01:05 | 1 | 321 | 4798591 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 19.9 NEED LINE CREW ITS MANUEL // iso 37830267000132 cod 1
14439 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-02-04 07:39 | 2013-02-04 13:00 | 1 | 321 | 4789091 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE AND TRANS. FUSE IS BLOWN ON POLE 215-182. I AM GOING TO REFUSE THEM BOTH. 10 KVA TRANS. IS BAD. WE NEED TO CHANGE TO A 25 KVA. I WILL CALL FOR HELP. RELEASED BY CREW 074S01//ISO 37830215B00182//COD 1//MD FILED// VER/DBM IDC XXXX
14440 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-07-02 11:33 | 2008-07-02 16:54 | 1 | 321 | 61325-1 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3007903//,,,TRANSFORMER FUSE BLOWN,, THIS IS THE 3RD TIME THIS TRANSFORMER HAS BEEN OUT , I SUGGEST A NEW 25KVA 7200V TRANSFORMER BE HUNG IN ITS PLACE,,, RAYBURN HAS BEEN NOTIFIED AND IS INFORMING A CREW //COD 1//ROB COMPHER 3370 OF DHE TO WORK THIS// VER/DBM IDC XXXX
14441 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-05-19 17:09 | 2008-05-19 22:30 | 1 | 321 | 66070-1 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3000201//POLE 382-89POLE TOP PIN IS BUSTED OFF PRI IS FLOATING INTO NEU CAUSING OUTAGE I;VE CALLED BILL FARLEY GETTING CREW NO TRUCKS TO POLE FUSE POLE IS 382-69 30-T ONE CUST, POLE 382-91 RELEASED BY CREW 078S09//ISO 38830382B00069//COD 1// VER/DBM IDC XXXX
14442 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-07-24 11:18 | 2012-07-24 13:05 | 3 | 107 | 4805211 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND A BAD CUTOUT ON THE 3 PHASE BANK POLE THAT FEED THE HEALTH DEPT, WELL NEED A CREW TO CHANGE THIS ONE, CREW REQ, CAN USE TRUCK ON THIS RELEASED BY CREW 078S06 VER/KEP
14443 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2021-03-12 17:40 | 2021-03-12 19:27 | 3 | 107 | 4332701 | 321 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neut broke/repairs made. pls close. tre
14444 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-02-28 03:33 | 2016-02-28 05:20 | 3 | 107 | 4783081 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CUSTOMERS REPORT NEIGHBORS ARE ALSO WITHOUT POWER//HAD CUSTOMER CHECK THEIR BREAKERS AND STILL NO POWER// XFMR OUT WILL REFUSE. FUSE LINK WAS BROKE , NOT BLOWN//COD 3
14445 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2015-11-05 09:23 | 2015-11-05 11:10 | 3 | 107 | 4411131 | 321 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 SERVICE DROP BURNT INTO , REPLACED DROP WITH #2 RESTORED POWER AT 11:10 VER/KEP
14446 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-08-29 22:00 | 2008-08-29 23:47 | 3 | 107 | 57581-1 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I LIFTED HOT LINE CLAMP TO CUTOUT. TR CUTOUT BAD. POLE 1148-17. ROW NEEDS CUT AROUND POLE 1148-17 SEND COPY TO ROW PIKEVILLE. REPLACED BAD CUTOUT EVERYTHANG OK. VER/PDP IDC XXXX
14447 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-03-07 10:50 | 2011-03-07 12:37 | 3 | 107 | 51295-1 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 402-125 WILL NEED BIG BUCKET TO MAKE REPAIRS.. REPLACED CUTOUT RESTORED POWER AT 12:37//VER/CRB IDC XXXX
14448 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-12-28 17:47 | 2019-12-28 19:34 | 3 | 107 | 4187761 | 321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout // made repairs and restored @ 1934
14449 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-01-16 15:50 | 2015-01-16 18:30 | 2 | 160 | 4939731 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 19.9 CUTOUT THIS IS THE FUSE ON 38830501000342 LINECREW REQUIRED NO TRUCKS TO POLE RELEASED BY CREW 078S11 POLE 38830501000342 VER/CRB L3/HFP XXX
14450 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-07-11 15:16 | 2014-07-11 16:20 | 5 | 64 | 4230211 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP HAS CAME LOOSE FROM STIRRUP ON TAKE OFF POLE 230-58, POWER RESTORED VER/CRB
14451 | Whitesburg | 3309302 | VICCO | JEFF | 2017-10-16 09:25 | 2017-10-16 14:45 | 1 | 320 | 4461301 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 5 KVA TRANSF BAD === NEED LINE CREW AND 10 KVA 7200 TRANSF THIS WILL TAKE 4WDRIVE TO GET TO THIS MANUAL ==== CHANGED TRANSF OUT POWER OK/ ISO 37830396A20112/ COD 1/ VER/BOW L3/HFP XXXHFP
14452 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-12-16 17:39 | 2008-12-16 22:59 | 1 | 320 | 59143-1 | 320 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3000902//ONE PHASE OUT PATROLING NOW A-PHASE FOUND AN LOOSE CONNECTIONS IN CT CABINET COMP KWB // VER/TOM L3/TOM IDC XXXX
14453 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2019-02-17 14:06 | 2019-02-17 15:10 | 5 | 64 | 4801351 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link appears to have broken. Restored @ 15:10. sh
14454 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2019-07-16 06:20 | 2019-07-16 11:40 | 1 | 320 | 4714991 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held in accordance with KPCO late night callout guidelines.,,CREW REQUIRED,,broke xfr cutout,,big bucket 278-272 Released by crew 078S05 crw on site all pwr restored @ 11:40 please close ticket LRM
14455 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-09-29 11:05 | 2008-09-29 16:25 | 1 | 320 | 51827-1 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201// BROKEN CUTOUT AND NEEDS BASKETT ON PRIMARY.NEEDS LINE CREW. NO TRUCKS TO POLE. RELEASED BY CREW 078S01,COMPLETE//VER/CRB IDC XXXX
14456 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-01-18 22:11 | 2016-01-18 23:15 | 5 | 64 | 4630221 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN, REFUSED TRANSFORMER CUTIUT, ALL WORK COMPLETE / GXJ VER/CRB
14457 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-03-20 12:35 | 2009-03-20 13:55 | 4 | 80 | 60376-1 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3408101// 6T TRANSFORMER FUSE BROKE.//COD 4// VER/DBM FP NONE XXXX
14458 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-11-15 12:31 | 2009-11-15 15:11 | 2 | 160 | 58261-1 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK REQ 32682312 BAD 50KVA 19.9 TRANS. 1-CUSTSEND TO LLOYD MC. RELEASED BY CREW 078S08 /// VER/TOM L3/TOM IDC XXXX
14459 | Paintsville | 3401802 | INDEX | HOSPITAL | 2021-04-24 18:52 | 2021-04-24 21:32 | 2 | 160 | 4477011 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link looked to have pulled apart inside cutout door. Refused and checked voltage to be good customers restored @21:32
14460 | Pikeville | 3409502 | BURDINE | LEVISA | 2014-08-04 14:45 | 2014-08-04 17:25 | 2 | 160 | 4330361 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SOURCE LEAD ON A SOLID BLADE DISC. AT POLE 37830358D00290 HAS BURRNED OUT OF HOT TAP CAUSING SINGLE PHASING. I AM GOING TO OPEN ALL 3 SOLID BLADE CUTOUTS AND REPAIR PRI. LEAD. I CHANGED LEAD IN SOLID BLADE.// ISO 37830358D00290/// COD 2 VER/DKG L3/DKG
14461 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2016-11-19 19:35 | 2016-11-19 20:55 | 4 | 80 | 4116291 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WRONG TRANS. ON ORDER POLE 1123-4586 6T BAD CUTOUT AND LA 4-CUST COD-4 VER/KEP
14462 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-01-07 10:47 | 2018-01-07 11:27 | 8 | 40 | 4717081 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | *SEE 4715181* Opened B & C Phase Recloser (8 customers) on pole 38831101C40087/ A Phase Was already out on stepdown pole 38831101C40563/ ISO 38831101C40087/ COD 8/ Opened C and B phase rec. @1047, made repaired1127
14463 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2013-05-31 06:55 | 2013-05-31 09:35 | 2 | 160 | 4200761 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE CHECKING FOR CAUSE BROKEN FUSE POWER RESTORED KWB ON POLE 39831122C00165 COD-2 ISO TF 39831122C00165 VER/HFP L3/HFP IDC XXXX
14464 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-12-30 23:43 | 2013-12-31 05:03 | 1 | 320 | 4213921 | 320 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CREW REQUIRED BAD UG CABLE ADDAPHASE REQUIRED/4/0 URD CABLE METER UNDER PORCH RIGHT SIDE OF HOUSE RELEASED BY CREW 078S03/CREW ON SITE/FETR0615/VEM/INSTALLED TEMP XFMR/FULL POWER RESTORED 0503/PLEASE COPY TICKET TO HEMLEPP AND REYNOLDS/THANKS/VEM VER/KEP
14465 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-08-04 12:05 | 2016-08-04 12:15 | 32 | 10 | 4733931 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ***SEE 4730601*** OPENING RECLOSER TO CLOSE SWITCH IN ORDER #4730601/ ISO 37830174A00220/ COD 32/ 1205-1215/ VER/BOW AJB
14466 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-10-08 17:05 | 2021-10-08 18:25 | 4 | 80 | 4330831 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Transformer on pole 328D-08 is leaking pretty bad will need to be changed out. 7200 25KVA transformer needed and cutout complete. Manual up behind a house. No power out as of now. Released by crew 077H15 Opened stepdown on 328D-280 at 17:05 closed back in at 18:25.
14467 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-08-19 11:30 | 2009-08-19 11:50 | 16 | 20 | 50425-1 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP RELATED TO ORDER 50005-1 CREW OPENED RECLOSER TO ALLOW THEM TO SAFELY REPLACE CUTOUT THAT FAILED //// COD-16 ISO OCR 37830426C00641 L3/HFP IDC XXXX
14468 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-10-05 18:50 | 2011-10-05 20:10 | 4 | 80 | 4950611 | 320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN/// FUSE LINK BROKE// REFUSED // POWER IS RESTORED // COD 4// VER/DBM IDC XXXX
14469 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-01-19 15:04 | 2015-01-19 15:15 | 29 | 11 | 4944901 | 319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SERVICER OPENED FUSE IN ORDER TO SAFELY REMOVE ROTTED CROSSARM & TRANSFER CONDUCTORS FROM POLE 38830118D26522 //COD 29//OPEND @ 15:04//CLOSED @ 15:15 // VER TIMES VIA VOICE REC // VER/HFP L3/HFP AJB
14470 | Hazard | 3303902 | LESLIE | WOOTON | 2018-06-28 10:01 | 2018-06-28 15:20 | 1 | 319 | 4684111 | 319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD PRIMARY METERING WILL GET HELP TO BYPASS ITBAD LIGHTNING ARRESTER ON CUST SIDE
14471 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-03-08 22:06 | 2013-03-09 03:25 | 1 | 319 | 4891971 | 319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE TO CLIMB TO CHG CUTOUT. NEED 1 MAN IN A PICK UP //BILL CAMPBELL TO ASSIST // BAD 15KVA 7200/120-240 TR //STEVE RAY & RICK RAY TO ASSIST // //VER/GAH IDC XXXX
14472 | South Williamson | 3411401 | DEWEY | INEZ | 2022-03-13 10:46 | 2022-03-13 16:05 | 1 | 319 | 4619221 | 319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on riser pole 743-c-203// no truck//crew enroute to assist//repairs made//restored at 16:05//complete//em
14473 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-07-01 10:56 | 2013-07-01 16:15 | 1 | 319 | 4436331 | 319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 100, CUTOUT IS BROKE ON TAKE-OFF POLE, CALLING FOR HELP. ONLY FEEDS LIGHTS FOR THE MEADOW SUBDIVISION, CAN BE CHANGED ANYTIME TODAY RELEASED BY CREW 077S02 VER/KEP IDC XXXX
14474 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-01-06 22:11 | 2014-01-07 03:30 | 1 | 319 | 4242201 | 319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR IS OUT, CANNOT GET XFMR BACK ON, WILL NEED 15 KVA, 7200 VOLTS, CUTOUT AND ARM BRACKET, TRUCK ACCESSIBLE WITH FLAGGERS, CAN HOLD UNTILL MORNING RELEASED BY CREW 077S02CSP XFMR IS OUT, CANNOT GET XFMR BACK ON, WILL NEED 15 KVA, 7200 VOLTS, CUTOUT AND ARM BRACKET, TRUCK ACCESSIBLE WITH FLAGGERS. COMPLTED VER/SEF
14475 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-11-21 04:47 | 2016-11-21 10:06 | 1 | 319 | 4120751 | 319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /BROKEN CUTOUT UP ON HILL SIDE === NEED LINE CREWBROKEN CUTOUT UP ON HILL SIDE === NEED LINE CREW RELEASED BY CREW 077S03// VER/ ADH
14476 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-01-03 11:21 | 2013-01-03 14:00 | 2 | 159 | 4566231 | 318 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEAD CONNECTION BURNT UP AT TRANSFORMER//REWORKED CONNECTIONS AT XFMR///RESTORED TO NORMAL AT 1400//COMPLETE//EM //ISO //COD 2// VER/DBM IDC XXXX
14477 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-10-13 19:19 | 2014-10-13 21:05 | 3 | 106 | 4614481 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 207D-80 , LINE FUSE OUT ON POLE 207D-53 . CLOSED LINE FUSE ON POLE 207D-53 @ 21:05 VER/CRB
14478 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2021-03-13 13:22 | 2021-03-13 14:15 | 6 | 53 | 4333471 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 280-29 HAS POLE BURNT HALF INTO, WILL HAVE TO OPEN SWITCH ON POLE 280-62 WHEN CREW ARRIVES TO MAKE REPAIRS..RESTORED POWER AT 14:15 // opened switch @1322 Released by crew 077H03
14479 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-04-30 19:34 | 2013-04-30 22:13 | 2 | 159 | 4060891 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN, CUT OUT BROKEN. NEED BIG BUCKET.//// REPLACED BROKEN C/O POWER RESTORED COD-2 ISO TF 37830229000155 VER/HFP L3/HFP IDC XXXX
14480 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2013-12-06 12:21 | 2013-12-06 15:00 | 2 | 159 | 4107091 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER OUT OF CUTOUT HAS COME OUT ,OPEN FUSE ON POLE 376-18 AT 14:18 CLOSED AT 15:00 POWER RESTORED SEPERATE OUTAGE FOR POLE 376-18, THIS OUTAGE ONLY AFFECTED 2 CUSTOMER, CUSTOMER WAS MISSMAPPED DID MD SEE 4108021 FOR OUTAGE FROM 1418 - 1500 FOR C PHASE 5 CUST (CENTER PHASE) VER/SEF L3/HFP
14481 | Whitesburg | 3312902 | JENKINS | JENKINS | 2015-06-23 08:12 | 2015-06-23 13:30 | 1 | 318 | 4642941 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR 37830382B00239/ ISO 37830382B00239/ COD 1/ REPLACED BAD XFM POWER RESTORED/ VER/BOW
14482 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-08-19 21:04 | 2019-08-19 22:50 | 3 | 106 | 4909511 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced and restored @ 22:50. sh // cod 3
14483 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2018-12-31 19:31 | 2018-12-31 22:10 | 2 | 159 | 4616811 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will replace/// Replaced bad cutout and restored service @ 22:10
14484 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2019-03-05 07:50 | 2019-03-05 09:36 | 3 | 106 | 4952301 | 318 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Transformer secondary leads were burned up. I opened the transformer at 08:58, and closed back in at 09:36. Power restored, send to Bill Johnson. Three customers here, one has four heat pumps and another has a four ton heat pump and is to far from the transformer.//SENT TO TECH//PART POWER FROM BEGINNING FOR ALL 3 CUSTS L3/HFP
14485 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-05-23 14:06 | 2008-05-23 19:24 | 1 | 318 | 50792-1 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3311101// CUSTOMER HAS PART POWER ..... SERVE IN AT XFMR WAS BAD.. MADE REPAIRS POWER RESTORED// VER/DBM IDCC PN30 XXXX
14486 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-03-03 15:49 | 2010-03-03 17:35 | 3 | 106 | 62571-1 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 8T FUSE BROKE. ....DAH//COD 3// VER/DBM IDC XXXX
14487 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-11-16 11:43 | 2009-11-16 12:36 | 6 | 53 | 60321-1 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CREW OPENED TRANS TO MAKE REPAIRS ON UG LINE VER/KEP L3/KEP IDC XXXX
14488 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-05-27 17:57 | 2016-05-27 23:15 | 1 | 318 | 4265841 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP TRANSFORMER NEED MATERIAL HANDLER AND 2 MEN AND A25 KVA 7200/120/240 ALSO WILL NEED TO INSTALL A CUTOUT AND T BRACKET. CREW REQUIRED RELEASED BY CREW 074S02// REPAIRS MADE VER/CRB
14489 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-03-29 07:14 | 2013-03-29 09:00 | 3 | 106 | 4965881 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AT POLE 107-125 6T TRANSFORMER FUSE BROKE REPLACED FUSE AND POWER RESTORED AT 9:00 AM PLEASE CLOSE TICKET VER/PDP IDC XXXX
14490 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2008-01-03 07:41 | 2008-01-03 10:20 | 2 | 159 | 53119-1 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 50 AMP CUTOUT == REPLACED == POWER ON//3309902//VER/CRB IDC XXXX
14491 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-11-10 07:24 | 2011-11-10 09:10 | 3 | 106 | 4063811 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// FUSE LINK HAD BROKE// REFUSED // POWER IS RESTORED VER/KEP IDC XXXX
14492 | Paintsville | 3409302 | KENWOOD | AUXIER | 2011-07-23 04:37 | 2011-07-23 09:55 | 1 | 318 | 4594691 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT-LINE-CLAMP OFF ON XFMR CUTOUT. REPLACED AND CLOSED XFMR @ 9:55. SH
14493 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2018-09-01 20:36 | 2018-09-01 23:15 | 2 | 159 | 4032861 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer is defectivebad xfmr, we changed it out L3/HFP
14494 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-12-22 16:51 | 2020-12-22 19:30 | 2 | 159 | 4795791 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse Released by crew 077S07
14495 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-12-24 14:42 | 2011-12-24 20:00 | 1 | 318 | 4200291 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 25KVA 7.2 KV TR, CUTOUT ARRESTOR & T-BRACKETNEUT WIRE IN THE SECONDARY SIDE OF TRANSF WAS LOOSE == ALSO CHANGE TRANSF WAS 5 KVA INST 25 KVA ALSO HAD BAD CUTOUT CHANGE IT TOO == POWER OK COD-1 ISO TF 37830417000073 VER/HFP L3/HFP IDC XXXX
14496 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-04-10 11:42 | 2013-04-10 17:00 | 1 | 318 | 4994561 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SEND TO BOB R. RELEASED BY CREW 078S08//BAD SEC. ///VER/CRB L/3 CRB IDC XXXX
14497 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2015-09-09 22:04 | 2015-09-10 01:57 | 2 | 233 | 4220411 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 1099-3612 2-UNDERGROUND FUSES OUT CALL DARRELL FETTERS 606 465-2974 THAT WANT TO NO ABOUT SCHOOL FOR THURDAY/CREW IN ENROUTE /WILL TEST CABLE/VEM VER/ARN
14498 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2019-05-01 18:51 | 2019-05-01 21:30 | 2 | 159 | 4196311 | 318 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on trans lead restored at 21:30//THIS AFFECTED 2 CUSTS//PER SERVI L3/HFP
14499 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2012-01-29 08:50 | 2012-01-29 11:29 | 2 | 159 | 4301891 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FUSE MELTED OUT AND HAD CONECTION ON SECONDARY POLE GOING BAD == REPAIRED AND REFUSED TRANSF == POWER OK VER/PDP IDC XXXX
14500 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2014-07-19 13:26 | 2014-07-19 15:12 | 3 | 106 | 4263691 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT.//COD 3// VER/DBM
14501 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2012-05-11 06:51 | 2012-05-11 09:30 | 2 | 159 | 4780731 | 318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED LEAD CAME OUT OF PRIMARY BUSHING//COD 2// VER/DBM IDC XXXX
14502 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-05-04 16:28 | 2008-05-04 21:45 | 1 | 317 | 56979-1 | 317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3311101//BAD 15KVA CSP 7200 120/240 37830530000013 COD-1 VER/KEP IDC XXXX DEB OK
14503 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2020-10-13 17:58 | 2020-10-13 23:15 | 1 | 317 | 4553101 | 317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA xfm ///will need 25 KVA ,cutout and bracket/// 7200 no truck Released by crew 074S02///REPAIRS MADE @ 23:15
14504 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-05-08 15:13 | 2019-05-08 20:30 | 1 | 317 | 4241131 | 317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad trans on 866-B-25.need one man and mat handler.25 kva 7200,7200 cutout and bracket trk app restored @ 2030
14505 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2015-06-20 15:16 | 2015-06-20 20:33 | 1 | 317 | 4618921 | 317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 TRUCKS OK RELEASED BY CREW 078S03 VER/HFP L3/HFP
14506 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2014-06-25 14:18 | 2014-06-25 19:35 | 1 | 317 | 4155411 | 317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER NO CUSTOMERS OUTAGED. THIS PROVIDES AC VOLTAGE FOR A RECLOSER. VER/CRB
14507 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-02-10 08:43 | 2010-02-10 14:00 | 1 | 317 | 54941-1 | 317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER BURNED OUT OF HOT TAP..REPLACED RISNER HOT TAP...BB//VER/CRB IDC XXXX
14508 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-06-28 20:43 | 2008-06-29 02:00 | 1 | 317 | 58271-1 | 317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O VER/HFP IDC XXXX
14509 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2019-06-11 09:58 | 2019-06-11 15:15 | 1 | 317 | 4481581 | 317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr on pole 422-124, manual pole.. Released by crew 077S11 REPLACED TRANSFORMER AN CUTOUT
14510 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2010-12-28 23:16 | 2010-12-29 00:35 | 4 | 79 | 56631-1 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR 38231561 //.....XFRMR FUSE OUT....POLE 964-B-97.....LOOKS OK....WILL RE-FUSE.....//....CUTOUT DOOR HAS DETERIORATED AND CAUSED USE TO BREAK.....REPLACED DOOR, & RE-FUSED.....POWER ON.....JRV....12/29/10 IDCC FEC49 XXXX
14511 | Hazard | 3310502 | HADDIX | CANOE | 2021-01-25 21:43 | 2021-01-26 00:21 | 2 | 158 | 4892261 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got broke cutout on transformer, got tim smith crew comming to help
14512 | Whitesburg | 3312901 | JENKINS | KONA | 2011-10-14 13:21 | 2011-10-14 14:40 | 4 | 79 | 4979731 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , I NEED HELP TO CHANGE IT. CHANGED CUTOUT AND REFUSED XFMR//COD 4// VER/DBM IDCC PN41 XXXX
14513 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-01-14 11:57 | 2020-01-14 14:35 | 2 | 158 | 4304121 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | hot tap lead out of top of c/o is broken, no trucks, and to close for me to try alone, send crew to make rep no trucks, just one cust off Released by crew 078S06. replaced hot tap restored1435
14514 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-02-07 11:30 | 2012-02-07 12:49 | 4 | 79 | 4325981 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/KEP IDC XXXX
14515 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-01-03 15:14 | 2014-01-03 20:30 | 1 | 316 | 4225261 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 10 KVA TRANS. ON POLE 166-152 IS BAD. I WILL NEED 1 MAN AND A MATERIAL HANDLER AND A 25 KVA/ 19.9 TRANS. RELEASED BY CREW 074S01TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 10 KVA TRANS. ON POLE 166-152 IS BAD. I WILL NEED 1 MAN AND A MATERIAL HANDLER AND A 25 KVA/ 19.9 TRANS. WE CHANGED TRANS.//COD 1// VER/DBM
14516 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-10-15 11:52 | 2009-10-15 14:30 | 2 | 158 | 65240-1 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK REQUEST 32222171POLE 118-181 BAD 25K KVA NEED 7.2 CUTOUT TRUCK TO POLEPOLE 118-181 BAD 25K KVA NEED 7.2 CUTOUT TRUCK TO POLE WR/ 32222171POLE 118-181 BAD 25K KVA NEED 7.2 CUTOUT TRUCK TO POLE WR/ 32222171 RELEASED BY CREW 078S08 COMPLETE..... IDC XXXX
14517 | Hazard | 3308001 | JACKSON | S.JACKSON | 2012-01-05 05:39 | 2012-01-05 06:58 | 4 | 79 | 4234351 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT FUSE PULL INTO ///VER/CRB L3/GDK IDC XXXX
14518 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2018-08-05 15:37 | 2018-08-05 18:15 | 2 | 158 | 4911181 | 316 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | off 18;00 on 18;15 lash cable bad in span 2 places repaired power restored//PART POWER TILL TRANS OPENED
14519 | Pikeville | 3407103 | TOPMOST | KITE | 2011-01-29 12:42 | 2011-01-29 15:20 | 2 | 158 | 51963-1 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND NO PROBLEMS WITH HARDWARE. CUSTOMER STATED THERE WAS A VERY POWERFUL WIND GUST WHEN POWER WENT OUT. LIMB MAY HAVE BLOWN INTO PRIMARY. WILL TRY FUSE. ARRESTER BAD ON 209-76. ISOLATED ARRESTER AND RE-FUSED AT 15:20. SH//VER/CRB IDC XXXX
14520 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-06-05 10:02 | 2009-06-05 15:18 | 1 | 316 | 63969-1 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WORK REQ # 30156670 // BAD 15 KVA 19.9 TRANSFORMER--MATERIAL HANDLER OK-CALLING CREW RELEASED BY CREW 078S07 L3/HFP IDC XXXX
14521 | Whitesburg | 3312901 | JENKINS | KONA | 2012-02-24 10:37 | 2012-02-24 15:53 | 1 | 316 | 4492811 | 316 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG BURNDT INTO ON THIS TRANS. POLE, WILL HAVE TO OPEN THIS TRANSFORMER TO MAKE REPAIRS. WILL KEEP TRACK OF TIMES.OPENED AT 15:44 CLOSED BACK IN AT 15:53. ////VER/CRB IDCC TOF1544 XXXX
14522 | South Williamson | 3411401 | DEWEY | INEZ | 2014-11-23 19:14 | 2014-11-24 00:30 | 1 | 316 | 4756851 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND LAYING ON BRACKET ARCING / OPENED RECLOSER 767-110 @ 2013 TO CLEAR IT/CLOSED @ 2026 --262 CUST/CUTOUT BROKE ON POLE 767-11/// NEED ONE MAN TO ASSIST//REPAIRS MADE//RESTORED AT 00:30 RELEASED BY CREW 079S01 VER/KEP
14523 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-04-11 20:36 | 2020-04-11 21:55 | 4 | 79 | 4622071 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 38820697C00112cutout door burned out on pole 697-24//replaced door//restored at 21:55//complete//em
14524 | Pikeville | 3421001 | BREAKS | CITY | 2014-09-11 12:32 | 2014-09-11 15:10 | 2 | 158 | 4489401 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37820220B00153 BAD TRANSFORMER CUTOUTCUTOUT FAILED/// ISO 37820220B00153// COD 2// VER/BOW
14525 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-12-11 11:42 | 2009-12-11 14:20 | 2 | 158 | 65747-1 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT.... REPLACED CUTOUT AND RESTORED POWER 14:20 12-11-09
14526 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-01-30 13:07 | 2010-01-30 15:45 | 2 | 158 | 61462-1 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 33666451 //......TRANSFORMER LEED BURNT INTO ON POLE. REPLACED CONNECTIONS ON XFMR, POWER RESTORED VER/HFP L3/HFP IDC XXXX
14527 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-05-18 08:55 | 2013-05-18 11:33 | 2 | 158 | 4130031 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TREE FELL THRU RELEASED BY CREW 074H03TREE FELL THRU LINE BREAKING LINE, WHEN REPAIRED CSP TRANSFORMER WOULD NOT PICK UP. WILL HAVE TO CHANGE XFMR. ///VER/CRB L/3 CRB//MADE MDC IDC XXXX
14528 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2018-01-09 16:27 | 2018-01-09 21:43 | 1 | 316 | 4725061 | 316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #2 primary dn from pole 49-77 and 49-346. Need barrel crew with big bucket truck. The wire pulled out of the dead end shoe. fuse not blown. Released by crew 074S07 37820049000077 Crews opened transformer cutout on 37820049000077 to safely repair downed conductor. Order 4725061. 2056-2143"
14529 | Whitesburg | 3312902 | JENKINS | JENKINS | 2010-07-04 14:30 | 2010-07-04 19:45 | 1 | 315 | 62107-1 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 NEED 1 MAN AN BIG BUCKET REPLACED TRANSFORMER//VER/CRB IDC XXXX
14530 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-01-07 18:42 | 2017-01-07 19:45 | 5 | 63 | 4276041 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GATE 37830179D00050 FAULTVER/AWD L3/HFP XXXHFP
14531 | Hazard | 3309904 | SLEMP | ROYAL DIAMOND | 2012-07-03 19:50 | 2012-07-03 21:35 | 3 | 105 | 4290781 | 315 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | REPLACE #2 BUS REGULATOR AT STATION //VER/GAH IDC XXXX
14532 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-02-21 11:15 | 2015-02-21 16:30 | 1 | 315 | 4058841 | 315 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, UG | 11:15 TIME OFF ON AT 16:30//COD 1//????????????????????
14533 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-11-24 16:35 | 2014-11-24 17:10 | 9 | 35 | 4763751 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 562-23 ROTTED AND LAYED OVER ABOUT 45 DEG. TREES HOLDING POLE UP BY PRI AND NUE, WIRE NOT BROKEN, STILL ENERGIZED.NEED 40/4 POLE, PTP, 7.2KV INSULATOR, CLEVIS AND SPOOL, STRAIGHT LINE POLE, CAN WORK WITH BUCKET. R/W OK. NEED 3 MAN LINE CREW. NEAR HEAD OF STONEY FORK RELEASED BY CREW 077H09/ OPENED STEPDOWN 37830538000072 @ 16:35 TO 17:10/ ISO 37830538000072/ COD 9 VER/CRB
14534 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2022-12-23 12:17 | 2022-12-23 13:20 | 5 | 63 | 4319711 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @47-C-221, checking. Fuse had melted out, refused @1320.
14535 | Hazard | 3309903 | SLEMP | BEECH FORK | 2012-07-03 19:50 | 2012-07-03 21:35 | 3 | 105 | 4290811 | 315 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | REPLACE #2 BUS REGULATOR AT STATION //VER/GAH IDC XXXX
14536 | Hazard | 3309904 | SLEMP | ROYAL DIAMOND | 2015-05-15 16:46 | 2015-05-15 18:31 | 3 | 105 | 4433451 | 315 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | REPLACING FAILED REGULATORS.
14537 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-09-08 07:35 | 2020-09-08 12:50 | 1 | 315 | 4440201 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 37830247C00235 transformer is bad, need 25kva 7200 transformer Released by crew 077S05 power restored at 12:50
14538 | Hazard | 3309903 | SLEMP | BEECH FORK | 2015-05-15 16:45 | 2015-05-15 18:30 | 3 | 105 | 4433441 | 315 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | REPLACING FAILED REGULATORS.
14539 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2012-02-27 11:45 | 2012-02-27 17:00 | 1 | 315 | 4510771 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S04//BURNT DEAD-END XFMR POLE 40CL4 DUE TO BAD CUTOUT///NEED CREW TO REPLACE/// NEED NEW 15KVA AND ALL NEW MATERIAL FOR DEAD-END PRIM. POLE ///1 CUST////OPENED L.F. CUTOUT 38830235000092 HOT TAP STILL ON!!!!///TRUCKS TO POLE RELEASED BY CREW 078H02////VER/CRB IDC XXXX
14540 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-01-13 01:00 | 2008-01-13 02:45 | 3 | 105 | 56335-1 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402204/ COD-3 / REPLACED CUTOUT ...ALL WORK COMPLETE / 01-13-08 GXJ VER/LDA IDC XXXX
14541 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-01-14 10:42 | 2020-01-14 10:51 | 35 | 9 | 4303671 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830857000062//COD 35//OFF @ 1042 ON @ 1051
14542 | South Williamson | 3411401 | DEWEY | INEZ | 2020-11-15 14:45 | 2020-11-15 20:00 | 1 | 315 | 4686571 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link was broke inside cutout door. Installed new fuse and restored @ 20:00
14543 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-10-30 11:50 | 2015-10-30 13:35 | 3 | 105 | 4396961 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULL INTO/ ISO 37830220000146/ COD 3/ VER/BOW
14544 | Hazard | 3303902 | LESLIE | WOOTON | 2017-04-07 06:45 | 2017-04-07 08:30 | 3 | 105 | 4626351 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | FUSE ROTTEN REPLACED IT/ ISO 37830462000010/ COD 3/ VER/BOW L3/HFP XXXHFP
14545 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-09-13 16:55 | 2010-09-13 17:40 | 7 | 45 | 66159-1 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN..RE FUSED XFMR..BB.//COD 7// VER/DBM IDC XXXX
14546 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-04-24 10:07 | 2014-04-24 15:22 | 1 | 315 | 4629521 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOT TAP ON POLE 38830237000015//BAD CUTOUT ON 237-55////LIFT H.T. ON PL# 237-15 TO MAKE REPAIRS///TAGGED TO R VIRGINBAD CUTOUT ON 237-55////LIFT H.T. ON PL# 237-15 TO MAKE REPAIRS///TAGGED TO R VIRGIN///REPLACED CUTOUT AND ARRESTOR ON PL # 237-55///RESTORED PWR ON PL 237-15 @ 15:22///PWR CK OK///TBL TKT COMPLETED
14547 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-10-07 21:20 | 2010-10-07 21:55 | 9 | 35 | 57926-1 | 315 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG OF U.G. OUT; REPLACING CABLE OFF AT 21:20 ON AT 21:55 ///VER/CRB IDC XXXX
14548 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-07-16 03:03 | 2009-07-16 08:18 | 1 | 315 | 64006-1 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | VER/HFP WORK REQ # 30762637 // BAD CURRENT LIMIT FUSEBAD CURRENT LIMIT FUSE--CALLED K BROWN TO ASSISTBAD CURRENT LIMIT FUSE--CALLED K BROWN TO ASSIST-REPLACED CUTOUT-CURENT LIMIT FUSE AN REPAIRED PRIMARY BUSHING ON TRANSFORMER-- L3/HFP IDC XXXX
14549 | Hazard | 3310502 | HADDIX | CANOE | 2010-08-17 15:55 | 2010-08-17 17:40 | 3 | 105 | 57006-1 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN///// FUSE BROKE, REFUSED, POWER RESTORED//VER/CRB IDC XXXX
14550 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-10-08 11:47 | 2009-10-08 12:50 | 5 | 63 | 63787-1 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LINE FUSE OPEN AT 303-170,SPLICE FAILEDA AT 303-38 RESAGGED WIRE//VER/CRB IDC XXXX
14551 | Hazard | 3302703 | HAZARD | HAZARD | 2013-03-14 12:20 | 2013-03-14 13:05 | 7 | 45 | 4905671 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BLOWN. --- FUSE BROKE FOR NO APPARENT REASON, POWER RESTORED. VER/KEP IDC XXXX
14552 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-09-08 17:15 | 2017-09-08 18:00 | 7 | 45 | 4341961 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER: NO ANSWER POLE 68-515 BAD ME 8T FUSE BROKE 38830068B00515 VER/AWD L3/HFP XXXHFP
14553 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-05-08 20:40 | 2016-05-08 21:15 | 9 | 35 | 4187741 | 315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE OFF THE PIN AND BUSTED OUT THE CROSSARM SEND CREW 20/3028 RELEASED BY CREW 078S08 RELEASED BY CREW 078H03 OPEN 2040 CLOSED 2115 VER/KEP
14554 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-05-19 18:23 | 2021-05-19 21:00 | 2 | 157 | 4601381 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on 37830117000086// Replaced andvrestored @ 21:00
14555 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-12-22 01:56 | 2008-12-22 07:10 | 1 | 314 | 62126-1 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN GOINGTO REPLACE SERVICE DROP SINGLE TRANS 37830377B00041 COD-1 VER/KEP L3/KEP IDC XXXX
14556 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2020-08-27 10:16 | 2020-08-27 15:30 | 1 | 314 | 4388401 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10 kva, 7200,120-240 feeds barn. truck access around fence into pasture Released by crew 078S07. crew on site fetr 15:30 ALL PWR RESTORED 15:30 PLEASE CLOSE TICKET lrm
14557 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-06-17 12:41 | 2016-06-17 17:55 | 1 | 314 | 4378731 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 19.9 XFMR//NEED 3 MEN//NO TRUCK///CREW ENROUTE//REPAIRS MADE//RESTORED AT 17:55//COMPLETE//EM/ ISO 38820794B00347/ COD 1/ VER/BOW
14558 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2020-05-15 10:28 | 2020-05-15 15:42 | 1 | 314 | 4838301 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Found a loose connection in a secondary splice,Will make repairs and restore,Restored service at 15:42.
14559 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2019-11-11 10:31 | 2019-11-11 15:45 | 1 | 314 | 4019651 | 314 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | a and c phase bank cutouts bad got them changed and power restored at 16:45 // xfer on pole 39831124A20634 customer mismapped and only customer on this xfer // MD made
14560 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2018-10-03 16:51 | 2018-10-03 22:05 | 1 | 314 | 4194311 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad hot leg on ug, Need power temp. //installed power temp///cust has full power now// complete br/ ISO 38830138C00205 / COD 1 L3/HFP
14561 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2020-07-06 15:56 | 2020-07-06 18:33 | 2 | 157 | 4118441 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse failedon 1015-C-97.restored power at 18:33
14562 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-12-06 10:28 | 2016-12-06 13:05 | 2 | 157 | 4169641 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 270D-151 . NEED 1 MAN BIG BUCKET . VER/CRB L3/HFP XXXHFP
14563 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-06-15 08:22 | 2015-06-15 10:59 | 2 | 157 | 4572151 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA SINGLE BUSHING, 7200 120/240, CAN USE TRUCK, BESIDE MOUNTAIN ENTER. TRANSFORMER FOR RAIL ROAD CROSSING, CREW REQ RELEASED BY CREW 078S06/CREW ON SITE/FETR1030/VEM/LINE FUSE ON 1097-26 HOTTAP IN TROUBLE/NEW FETR1115/VEM/65T@1097-28 NOT ON MAP/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1059/PLEASE CLOSE TICKET/THANKS/VEM VER/SEF
14564 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-06-04 11:01 | 2018-06-04 16:15 | 1 | 314 | 4553811 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse blown..bad 15KVA 19.9 xfmr will need crew to replace. Contacted Tim Hall and he is getting crew to replace.. Flagging required Released by crew 074H06
14565 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-12-25 15:56 | 2022-12-25 21:10 | 1 | 314 | 4356561 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMER Restored at 21:10
14566 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-05-20 19:10 | 2015-05-20 21:47 | 2 | 157 | 4450681 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TRANS CHGED NEED 50KVA LEAKING OIL TRUCK TO POLE RELEASED BY CREW 078S08///CHANGED OUT XFMR///PWR RESTORED @ 21:47///TBL TKT COMP///RMV// VER/ ADH
14567 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-07-22 18:02 | 2018-07-22 20:39 | 2 | 157 | 4836211 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad dearbute cutout. crew t change, trk to pole Released by crew 078S07//arrived RM repairs made please close tic RM L3/HFP
14568 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-11-09 18:26 | 2009-11-09 23:40 | 1 | 314 | 53941-1 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFMR, NO TRUCK, NEED ROW CREW AND LINE CREW, BILL FRALEY HAS BEEN NOTIFIED, ONLY 1 CUSTOMER ON THIS XFMR. RELEASED BY CREW 078S05//COD 1 PER SERVICER// VER/DBM IDC XXXX
14569 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2012-10-29 05:48 | 2012-10-29 11:02 | 1 | 314 | 4180461 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / "WILL CHECK AT REGULAR TIME" SDB / WILL CHECK AT REGULAR TIME FAILED CUTOUT. WILL NEED OUTAGE. CREW ENROUTE.SDB / WILL CHECK AT REGULAR TIME FAILED CUTOUT. WILL NEED OUTAGE ON POLE 37820148000049. CREW ENROUTE.// OPENED FUSE @ 1008 (38 CUST) // COD-39 ISO TF @ 37820148000049 DUPLICATING FOR 38 CUST IN H4180461 VER/HFP L3/HFP IDC XXXX
14570 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-11-05 11:59 | 2019-11-05 15:07 | 3 | 188 | 4293971 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate burndt into @25-A-222, will have to open L/F @25-A-43 to make repairs. Will keep track of times.//COD 1 FROM THE BEGINNING OF OUTAGE//Cutout gate burndt into @25-A-222, will have to open L/F @25-A-43 to make repairs. Will keep track of times. Opened @1404 made repairs and closed back in @1507.Cutout gate burndt into @25-A-222, will have to open L/F @25-A-43 to make repairs. Will keep track of times. Opened @1404 made repairs and closed back in @1507. Released by crew 074S05
14571 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-10-28 23:27 | 2017-10-29 02:04 | 2 | 157 | 4507331 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER-NO ANSWER// LINE FUSE BLOWN ON POLE#193-200 WILL PATROLL// CUTOUT BROKE ON POLE#193-410 WILL CHANGE/// CHANGED BROKEN CUTOUT AND RESTORED SERVICE @ 02:04/// VER/DKM L3/HFP XXXHFP
14572 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-02-23 16:23 | 2020-02-23 19:00 | 2 | 157 | 4426381 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad hot tap..changing. L3/HFP
14573 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2021-07-14 22:40 | 2021-07-15 01:17 | 2 | 157 | 4914101 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad clamp on pole 519-276. replace clamp, power restored
14574 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-09-08 12:46 | 2021-09-08 18:00 | 1 | 314 | 4221491 | 314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 19.9, 2 primery bushings by truck Released by crew 078S12//arrived RM xfm replaced volatge good please close tic RM
14575 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-01-06 15:47 | 2018-01-06 21:00 | 1 | 313 | 4713261 | 313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no answer bad cutout on pole 1109-24 help coming Released by crew 077H14
14576 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2020-07-18 16:02 | 2020-07-18 21:15 | 1 | 313 | 4180551 | 313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr , leaking oil bad , need 2 man crew and flaggers to change xfmr 15 kva7200 also need cutout and bracket per line servicer 1 CC on the TR
14577 | Hazard | 3311103 | STINNETT | WENDOVER | 2019-02-05 17:17 | 2019-02-05 22:30 | 1 | 313 | 4756721 | 313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 120/240
14578 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-03-26 17:23 | 2009-03-26 22:36 | 1 | 313 | 61878-1 | 313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3300601//POLE BURNED IN TWO,1 POLE TAP ISOLATED AT POLE 249-89,NEED 3 MAN CREW,45 CL 4 POLE,12 KV CUTOUT&BRKT,12 KV DEADEND ASSEMBLY,GUY MUCK,FETR SENT,NEW FETR SENT,// VER/CRB IDCC PN303 XXXX
14579 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-10-01 15:38 | 2019-10-01 20:51 | 1 | 313 | 4081151 | 313 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | C PHASE at recloser pole37830174A44375 pull out of a sleve, Released by crew 077S04/ repairs made power restored at 2051/ ISO 37830174A44375/ COD 1
14580 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2016-10-21 11:02 | 2016-10-21 16:15 | 1 | 313 | 4038091 | 313 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY RISER FELL OUT OF SECONDARY LUG OF TRANSFORMER./ ISO 37820171D00099/ COD 1/ VER/BOW
14581 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-05-30 22:27 | 2010-05-31 01:03 | 2 | 156 | 53795-1 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR FUSE IS OUT,WILL RE-FUSE IF POSSIBLE,MAY BE LEAKING OIL////BAD XFR,NEED TO REPLACE IT.HAVE CONTACTED DENNIS,HE IS GETTING HELP VER/LDA IDC XXXX
14582 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-07-03 16:28 | 2018-07-03 19:04 | 2 | 156 | 4718781 | 312 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | resqueezed service connections
14583 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-12-13 18:24 | 2013-12-13 19:03 | 8 | 39 | 4160111 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED 1 MAN,BUCKET,100 FT 1/0 TRIPLEX,GOING TO HAVE TO CHANGE SERV DROP OUT,IS DAMAGED FRM 1 END TO THE OTHER/////REPLACED BAD SERV,XFR OFF 18:24,ON AT 19:03//COD 8 VER/HFP L3/HFP
14584 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2021-05-09 11:20 | 2021-05-09 13:04 | 3 | 104 | 4552911 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Fuse blown @ 37830188C00029 due to guy wire making wrapped around top of pole @ 37830188C00430//Cleared up guy wire and restored @ 13:04
14585 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2022-02-20 01:27 | 2022-02-20 02:45 | 4 | 78 | 4519511 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Cutout door burnt up will replace///Replaced burnt up door///Restored @ 02:45
14586 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-04-27 11:30 | 2015-04-27 12:22 | 6 | 52 | 4369701 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED L/F 37830248B11636 TO SAFELY REPLACE TRANSFORMER ON TICKET 4368451 VER/CRB L3/HFP XXX
14587 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-01-22 14:49 | 2016-01-22 16:07 | 4 | 78 | 4641721 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE ON POLE 376-34 IS OUT FEEDS BOTH DIRECTION,BAD CUTOUT ON POLE 376-447 , REPLACED CUTOUT RESTORED POWER AT 16:07/MDE MADE/ADH// VER/ ADH
14588 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-08-04 11:34 | 2009-08-04 14:10 | 2 | 156 | 54787-1 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO REPLACE CUTOUT, ALSO LINE FUSE WAS OUT VER/KEP L3/KEP IDC XXXX
14589 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2017-02-07 10:36 | 2017-02-07 15:48 | 1 | 312 | 4363711 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RELEASED BY CREW 079S02.CREW REQUIRED,NTA. BAD CONNECTION IN ONE OF THE MANY INSULINKS IN THE SERVICE DROP.124.3VOLTS ON ONE LEG.RUDY RELEASED BY CREW 079M01 /// WILL REPAIR TOMORROW 02/08/17 ON OPS ORDER # 038738272 VER/HFP L3/HFP
14590 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2017-03-07 13:16 | 2017-03-07 18:28 | 1 | 312 | 4530281 | 312 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAD 2 BAD SPLICES IN A SERVICE DROP, CHANGED OUT 1818. ONLY 1 CUSTOMER WAS AFFECTED.37830048C10300 1 VER/AWD
14591 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2013-07-02 07:24 | 2013-07-02 10:00 | 2 | 156 | 4443771 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1148-647 BAD CUTOUT DOOR REPLACED VER/CRB L/3 CRB
14592 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-12-25 15:52 | 2012-12-25 17:36 | 3 | 104 | 4516111 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN WIRE SECONDARY BURNED DOWN. TRANSFORMER FUSE BLOWN ON POLE 35-A-512. PUT OPEN WIRE SECONDARY BACK UP AND REWORKED CONNECTIONS ON MID SPAN TAP THAT FAILED. ///VER/CRB L/3 CRB
14593 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-05-10 09:39 | 2013-05-10 12:15 | 2 | 156 | 4092691 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XMF FUSE OUT COD-2 ISO TF 38830453000263XMF FUSE OUT. REPLACED CURRENT LIMMITING FUSE AND REMOVED VINES FROM POLE. PLEASE SEND THIS TO JASON B TO BE SPRAYED. APR AT 1215 CLOSE TICKET COD-2 ISO TF 38830453000263 VER/HFP L3/HFP IDC XXXX
14594 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-02-21 02:56 | 2008-02-21 03:04 | 39 | 8 | 65883-1 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3402001/ LINK TO ORDER 65875-1 CREATED ORDER TO ALLOW SHOW RECL OPEN AT POLE 1127-821 DUE TO FAULTED RECL AT POLE 1103-117 ** SERVICER PATROLLING CKT VER/PDP 3402001/ . * 0256 SERVICER REPORTS FAULTED RECL AT POLE 1103-117 IN PROCESS OF CLOSING BYPASS. * @ 0256. SERV REPORTS RECL UPSTREAM L.O POLE 1127-821 . A PHASE RECL AT POLE 1127-821 OUT AT 0256 AND REST AT 0304 CC 31 IDCC CNT209 XXXX
14595 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-01-11 20:40 | 2022-01-11 22:24 | 3 | 104 | 4337321 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 875-104, cutout broken..changing.
14596 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-07-17 15:54 | 2015-07-17 18:30 | 2 | 156 | 4902801 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, WE CHANGED OUT AND CHECKED VOLTAGE// CAN CLOSE RESTORED AT 1830 MWL
14597 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-09-15 17:48 | 2021-09-15 23:00 | 1 | 312 | 4245521 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad line cutout on 483C/184 65 foot pole can not reach calling help power on
14598 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-12-11 03:53 | 2010-12-11 05:37 | 3 | 104 | 65230-1 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE ON POLE 38830620000094 OPENED FUSE ON POLE 38830620000249 AT 0353 ONLY ONE CUSTOMER BILL F ON HIS WAY WITH CURRENT LIMITING FUSE 1 CUSTOMER ON FUSE/TRANSFORMER VER/TOM IDC TOF221 XXXX
14599 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2021-07-08 12:40 | 2021-07-08 13:58 | 4 | 78 | 4871401 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 38830045D16159 rotten & leaning/needs replaced today, windstream pole 40 class 5/crew reqd. truck ok/send to Bobby Tackett Released by crew 078S04// opening tranformer and removing line clmappole 38830045D16159 rotten & leaning/needs replaced today, windstream pole 40 class 5/crew reqd. truck ok/send to Bobby Tackett Released by crew 078S04,cut loop @ 45-d1-6158 @ 1240 restored @1358
14600 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-05-06 05:54 | 2014-05-06 08:30 | 2 | 156 | 4666551 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH AT START OF REGULAR SHIFT// BAD CUTOUT.. CHG. CUTOUT VER/CRB
14601 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-04-24 19:18 | 2010-04-24 21:54 | 2 | 156 | 50274-1 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT I WILL BE CHANGING OUT. COD-2 ISO LF 38831003D00057.. WE NEED TO SHOW 3 25T FUSES ON THAT POLE. SEND COPY TO RON RYE ENG PIKEVILLE. ON POLE 1003D70. TRANSFORMER RISER WIRE ON SEC SIDE IS IN BAD SHAPE NEEDS TO BE CHANGED. LUGS ON TRANSFORMER ARE NOT IN GOOD SHAPE I TRYED TO TIGHTEN SOME. OTHER TWO CUTOUTS NEED CHANGED MAY HAVE TO CHANGE TRANFORMER DUE TO SHAPE OF LUGS VER/HFP L3/HFP IDCC CNT3, TOF1736 XXXX
14602 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-10-26 13:21 | 2019-10-26 15:05 | 3 | 104 | 4198911 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout serving xfmr is broke into, I changed it out
14603 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-11-28 13:42 | 2016-11-28 15:00 | 4 | 78 | 4134091 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED BAD SECONDARY CONNECTIONS AT THE TRANSFORMER. THE CUSTOMER ALSO HAS A PROBLEM WITH HER RANGE THAT KEEPS TRIPPING HER BREAKER./ ISO 37820009C00050/ COD 4
14604 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-01-25 08:11 | 2011-01-25 09:29 | 4 | 78 | 64048-1 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BLOWN ON PHASE B ON POLE 892-A-282....PATROLLING.....LINE LOOKS OK....IF NO HZRDS, WILL RE-FUSE....//...RE-FUSED CUTOUT....POWER ON.....LOOKS LIKE OLD FUSE JUST BROKE....JRV....01/25/11 //VER/CRB IDC XXXX
14605 | Hazard | 3303902 | LESLIE | WOOTON | 2014-10-07 15:36 | 2014-10-07 17:20 | 3 | 104 | 4566101 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON XFMR , OPENED LINE FUSE ON POLE 438-3 @ 17:05 , CLOSED LINE FUSE BACK @ 17:20 , CLOSED XFMR FUSE @ 17:20 . ONLY 2 CUST. ON XFMR . DUP IN HOIS FOR 1 CUST SEE H4566101 VER/HFP L3/HFP
14606 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-06-15 09:48 | 2012-06-15 15:00 | 1 | 312 | 4917831 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED. BAD TRANSFORMER ON POLE 168-29. METER# 533604615. WE NEED TO BRING A 25KVA---19.9 TO REPLACE A 15 KVA. LOCATED 1ST POLE BEFORE STEPDOWN IN RIGHT FK. OF GREASY CRK. TRUCK ACCESSIBLE. TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. IS BAD. RELEASED BY CREW 074S01//CRB MADE MDC//COD 1// VER/DBM IDCC PN28 XXXX
14607 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-10-26 08:16 | 2019-10-26 10:00 | 3 | 104 | 4197781 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke Will replace. replaced cutout & restored power.
14608 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-02-07 12:55 | 2008-02-07 13:47 | 6 | 52 | 52394-1 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000902// KEVIN REPORTED 50KVA NON-PCB LEAKING OIL - WILL NEED TO BE CHANGED OUT AND POSSIBLY AN OIL CREW WILL BE NEEDED// CREW ARRIVED// WILL CHANGE TRANSFORMER//OPENED XFMR1255/FETR 1515/COMPANY CREW TO CLEAN OIL/VEM/XFMR CHANGED AND POWER RESTORED 1347// VER/TOM IDC XXXX
14609 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-07-20 23:50 | 2011-07-20 23:56 | 52 | 6 | 4570631 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | OPENED FUSE TO MAKE UP CONNECTIONS INSIDE SWITCHING CABINET OPENED 2350 AND CLOSED 2356 VER/DKG L3/DKG
14610 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2012-02-26 08:31 | 2012-02-26 10:15 | 3 | 104 | 4507301 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD == REPLACED CUTOUT == POWER OK COD-3 ISO TF 37830343A00034 VER/HFP L3/HFP IDC XXXX
14611 | Hazard | 3302703 | HAZARD | HAZARD | 2015-07-21 17:53 | 2015-07-21 18:45 | 6 | 52 | 4928341 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPEN TRANSFORMER 37830296C30573 AT 18;37 AND CLODE AT 18;45,BAD CONNECTION ON POLE 37830296C30839 /// COD-6 ISO TF @ 37830296C30573 VER/HFP L3/HFP
14612 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2019-12-08 15:29 | 2019-12-08 16:21 | 6 | 52 | 4135691 | 312 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up. repairs made. pls close. tre
14613 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-03-18 17:36 | 2014-03-18 19:20 | 3 | 104 | 4506641 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN CALLING 1 MAN TO HELP CHANGE AND CREW TO FLAG NEED 1 MAN AND BIG BUCKET ,BAD CUTOUT ON POLE 246B-130 POWER IS BACK ON BUT CUTOUT IS BROKE // 2033 DONNIE SPENCER ON SITE//CUTOUT BROKEN CALLING 1 MAN TO HELP CHANGE AND CREW TO FLAG NEED 1 MAN AND BIG BUCKET ,BAD CUTOUT ON POLE 246B-130 POWER IS BACK ON BUT CUTOUT IS BROKE. OPENED LINE FUSE ON POLE 246B-83 @ 21:10 CLOSED BACK IN @ 21:20 5 CUST SEE H4506641 FOR 2ND OUTAGE VER/HFP L3/HFP
14614 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2011-05-30 17:43 | 2011-05-30 18:35 | 6 | 52 | 4210911 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WR#40162148 POLE 1099-191 12T TRANS FUSE BROKE //VER/GAH IDC XXXX
14615 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-05-03 15:15 | 2015-05-03 16:33 | 4 | 78 | 4386041 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR F IS OUT,WILL RE-FUSE/////////////FUSE HAD ROTTED INTO,REPLACED AND RESTORED VER/CRB
14616 | South Williamson | 3200302 | BELFRY | TOLER | 2011-11-23 10:27 | 2011-11-23 11:45 | 4 | 78 | 4107781 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT.CAN REPLACE..//...REPLACED BAD CUTOUT..POLE OK...POWER ON.JRV...11/23/11 ///VER/CRB IDC XXXX
14617 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-06-17 10:24 | 2021-06-17 13:00 | 2 | 156 | 4762961 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 122-122///will have to open fuses on pole 122-194 to change cutout safelycutout broke on pole 122-122///will have to open fuses on pole 122-194 to change cutout Opened line fuses @ 13:00/////Changed bad cutouts and closed line fuses in @ 13:00 and restored service
14618 | South Williamson | 3200302 | BELFRY | TOLER | 2021-12-08 13:33 | 2021-12-08 17:45 | 2 | 252 | 4162301 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | had transformer on pole 989D-12 open from 16:45 to 17:45.had to replace cust service drop.had some bad spots in it.only 2 cust on transformer.cust was mis-mapped
14619 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-08-15 20:58 | 2015-08-15 21:50 | 6 | 52 | 4139311 | 312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 91-6009 BAD LA POLE 91-463 25T LINE FUSE VER/SEF L3/HFP XXXHFP
14620 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-06-10 08:26 | 2011-06-10 13:37 | 1 | 311 | 4282731 | 311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV XFORMER//COD 1// VER/DBM IDCC PN516 XXXX
14621 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2012-07-02 11:39 | 2012-07-02 16:50 | 1 | 311 | 4229691 | 311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | REPLACED CUTOUT ,ON AT 16:50 , ALL WORK COMPLETE / GXJ
14622 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-03-06 12:31 | 2018-03-06 17:42 | 1 | 311 | 4971651 | 311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | arrived RM power on at meter customer breaker is off please close tic RM/ ISO 38830642000001/ COD 1
14623 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-01-13 08:49 | 2018-01-13 14:00 | 1 | 311 | 4742831 | 311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called cust//ckd breakers and meter//truck ok from behind /15kva Released by crew 078S03//ARCOSED LINE CREW OUT//,repairs made all cust restored @ 1400 please close ticket thanks.bt
14624 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-03-01 12:39 | 2016-03-01 17:50 | 1 | 311 | 4791941 | 311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA XFMR , NEEDS NEW CUTOUT & TBRACKET . 19.9V . RELEASED BY CREW 075H04 REPLACED TRANSFORMER ;; POWER RESTORED AT 17:50/ ISO 37830174D00334/ COD 1/ VER/BOW
14625 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2017-03-16 08:10 | 2017-03-16 13:21 | 1 | 311 | 4561431 | 311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA 7200 BTRK--NEED FIBERGLASS T BRACKET AND C/O--1 LANE RD BUT HAVE HAD NO TRAFFIC ISSUES???--CREW REQ--DS031617 RELEASED BY CREW 078S01 /ON SITE RM POWER BACK ON @13:21 PLEASE CLOSE TIC RM38830377000084 VER/AWD
14626 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-09-29 07:45 | 2011-09-29 12:56 | 1 | 311 | 4931091 | 311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PREVIOUS ORDER(4930421) CLOSED PREMATURELY,NOT A REPEAT OUTAGE, THIS IS THE SAME OUTAGE//FUSE LINK APPEARS TO HAVE BROKEN.BAD 50KVA 19.9 XFMR ON 818-197.BAD 50KVA 19.9 XFMR ON 818-197. RELEASED BY CREW 076S02//COD 1// REPLACED TRANSFORMER TCM// VER/DBM IDC CHANGED START TIME FROM 1003 TO MATCH PREVIOUS ORDER XXXX
14627 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-09-21 20:41 | 2014-09-22 01:52 | 1 | 311 | 4517161 | 311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | B PHASE UNDERGOUND CABLE HAS BURNED INTO AT THE TERMINATOR ON THE FUSE POLE. YOU MIGHT BE ABLE TO REPAIR CABLE WITHOUT REPLACING THE CONDUTOR. ALL THREE ARE NOT IN THE BEST SHAPE BEEN PATCHED UP BEFORE. VER/ARN
14628 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2011-06-02 17:51 | 2011-06-02 20:26 | 2 | 155 | 4225451 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 40223959 // BAD 7200V 25 KVA TRANSFORMER--TRUCK OK--NEED CREW RELEASED BY CREW 078S07//PRT ON SITE// REPLACED TRANSFORMER AND ARRESTOR VER/KEP IDC XXXX
14629 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-07-09 17:55 | 2016-07-09 20:30 | 2 | 155 | 4600621 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR CHING./ ISO 38830811000259/ COD 2/ VER/BOW
14630 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-07-25 19:35 | 2021-07-26 00:45 | 1 | 310 | 4954531 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva on pole 284-100 trucks ok.//cod 1
14631 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2021-04-30 08:57 | 2021-04-30 11:32 | 2 | 155 | 4500521 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke transformer cutout
14632 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2015-06-25 19:05 | 2015-06-25 21:40 | 2 | 155 | 4656861 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLOSED TRANS FUSE ON POLE991-D-138 CUTOUT BROKE BLOWING FUSE ON POLE 991-D-267 REFUSED DOOR ON267 RESTORED POWER TO HOLLOW AT20:20 WAITIN ON CREW TO REPLACE CUROUT ON 138 RELEASED BY CREW 079H03CLOSED TRANS FUSE ON POLE991-D-138 CUTOUT BROKE BLOWING FUSE ON POLE 991-D-267 REFUSED DOOR ON267 RESTORED POWER TO HOLLOW AT20:20 WAITIN ON CREW TO REPLACE CUROUT ON 138 REPLACED CUTOUT RESTORED POWER @21:40//SEE L/F OUTAGE ON OTHER TIX VER/CRB
14633 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-07-20 06:20 | 2015-07-20 11:30 | 1 | 310 | 4914431 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE ON KVA REFUSED AT 11:30 ALL POWER RESTORED PLEASE CLOSE TICKET THANKS DWW VER/CRB
14634 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-04-11 10:50 | 2016-04-11 16:00 | 1 | 310 | 4079191 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKE SEC POLE 207A-238 WINDSTREEM POLE NEED LINE CREW TO REPAIR TRUCK OK,OPEN XFMR @ 207A-237 1050 RELEASED BY CREW 078S05.. CREW ON SITE WAITING FOR WINDSTREAM TO SET POLE ETR 1730.. POLE REPLACED AND POWER RESTORED AT 1600.. PLEASE CLOSE TICKET CY VER/AWD
14635 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-12-08 11:46 | 2022-12-08 12:17 | 10 | 31 | 4242581 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LIFTED A CLAMP ON POLE 37830386000039 (COD 10) TO TIE WIRE BACK IN @ POLE 37830386000046//OFF @ 1146 ON @ 1217
14636 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-10-31 11:52 | 2019-10-31 14:27 | 2 | 155 | 4223911 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | arm pin insulator breaking down on pole37830294B40305, Released by crew 077S04//NO OUTAGE TILL STEP DOWN OPENED @ 1152 ON POLE 37830318A00286//COD 2//1152-1427
14637 | South Williamson | 3200302 | BELFRY | TOLER | 2022-09-09 08:50 | 2022-09-09 14:00 | 1 | 310 | 4858251 | 310 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug cable Released by crew 079S02restored @14:00 Released by crew 074H07
14638 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-07-16 13:06 | 2020-07-16 15:41 | 2 | 155 | 4171041 | 310 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kv 19.9 xfm.will need big bucket to replace..truck approach.restored
14639 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-11-03 11:38 | 2013-11-03 14:13 | 2 | 155 | 4006121 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT REPLACE VER/CRB L3/HFP
14640 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-03-04 11:00 | 2013-03-04 13:35 | 2 | 155 | 4869131 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BROKEN CUTOUT TRUCK OK COD-2 ISO PO 38830246C30318 VER/HFP L3/HFP IDC XXXX
14641 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-05-01 12:35 | 2010-05-01 17:45 | 1 | 310 | 53377-1 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOK LIKE NEUTRAL WIRE IN 4/3 DROP IS BURNT INTO CUST HAS 200AMP METER BASE. I WILL BE CHANGING THIS OUT TO 2/3 DROP. NEUTRAL BURNT INTO ABOUT 3 FOOT FROM POLE HOT CONDUCTORS WERE ABOUT MELTED TOGEATHER. NOTHING AROUND TO DAMAGE DROP. MAY HAVE BURNT DOWN DUE TO LOAD. SEND COPY OF THIS TO PEGGY IN DAMAGE CLAIMS AT THE TIME CUST SAID EVERYTHING WAS OK. BUT MAY END UP CALLING IN NEVER KNOW. VER/KEP L3/KEP IDC XXXX
14642 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-12-13 14:28 | 2012-12-13 15:30 | 5 | 62 | 4467621 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SECONDARY POLE WASHED OUT, SERVICE PULLED MASTS OFF BUILDING, WILL CUT LOOSE AT TRANSFORMER POLE, CUSTOMERS WILL HAVE TO REPLACE MASTS, THEN WE WILL HAVE TO FIGURE OUT HOW TO GIVE THEM SERVICE, TCM// CUSTOMER TO REPLACE MASTS FRIDAY WE WILL BE RUNNING NEW SECONDARY FRIDAY MORNING, IS THE PLAN, TCM//COD 5// VER/DBM
14643 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-03-14 10:32 | 2014-03-14 13:07 | 2 | 155 | 4491871 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON SECONDARY EXT AT THE TRANSFORMER POLE. ONLY TWO CUSTOMERS WERE OFF.//COD 2// VER/DBM
14644 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-09-15 10:43 | 2010-09-15 13:18 | 2 | 155 | 50011-1 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36891450 /// 7.2 LINE CUTOUT BAD AT POLE 37830177D00053 CALLING FOR CREW RELEASED BY CREW 077S04 OPENED XFMR AT1240 RESTORED ALL POWER AT 1318 CHANGED CUTOUT 077H01 COD-2 VER/HFP L3/HFP IDCC TON1316 XXXX
14645 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2015-03-04 14:57 | 2015-03-04 20:07 | 1 | 310 | 4099971 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE CUTOUT IS BROKEN, IN THE CLEAR, ON POLE 901-7069, LINE FUSE WAS NOT OUT ON POLE 901-4616, CREW REQ, NEED CUTOUT AND BIG BUCKET TO MAKE REPAIRS RELEASED BY CREW 078S06/ OPENED LINE FUSE 39830901D34616 CHANGING ALL THREE CUTOUTS ON ALL PHASES ON POLE 39830901D37069/ ISO 39830901D37069/ COD 1
14646 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-10-29 14:20 | 2022-10-29 16:55 | 2 | 155 | 4077171 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew bad fuse door
14647 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2018-06-16 09:41 | 2018-06-16 14:51 | 1 | 310 | 4607361 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfmr fuse blown on pole 188-C-187 this only affects 1 customer.bad 15kva xfmr will need 1 man and big bucket to change can use truck.Replaced xfmr and restored power @ 14:51
14648 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-06-17 13:10 | 2011-06-17 15:45 | 2 | 155 | 4334241 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 074S05///FUSE BLOWN//BAD CLF // REFUSED & BACK TO NORMAL COD-2 ISO TF 37820026000036 VER/HFP L3/HFP
14649 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-12-12 21:59 | 2012-12-12 23:01 | 5 | 62 | 4465591 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE ///VER/CRB L/3 CRB
14650 | Hazard | 3303902 | LESLIE | WOOTON | 2015-12-04 19:20 | 2015-12-04 21:55 | 2 | 155 | 4511101 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD SEC. CONNECTION ,MADE REPAIRES/ OPENED TRANSFORMER AND BACK ON @ 21:55/ ISO 37830366D00039/ COD 2/ VER/BOW
14651 | South Williamson | 3411401 | DEWEY | INEZ | 2013-05-22 07:30 | 2013-05-22 12:40 | 1 | 310 | 4156241 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON 673-163 DUE TO BAD ARRESTOR ON POLE 673-184//CUTOUT ALSO HAD CRACKS// I CHANGED CUT OUT AND ARRESROR//RESTORED AT 12:40//COMPLETE//EM
14652 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-12-09 16:55 | 2011-12-09 19:30 | 2 | 155 | 4165901 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN TRANSFORMER AT 17:18 CLOSE AT 17:25. 1/0 SECONDARY BURNT DOWN THEIR WILL BE TWO CUSTOMER OUT OF SERVICE UNTIL I CAN MAKE REPAIRS. OFF AT 18:54 ON AT 19:30//COD 4 IDCC CNT4 NEED TWO ADDITIONAL OUTAGES XXXX
14653 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-07-23 04:20 | 2020-07-23 09:30 | 1 | 310 | 4212441 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines had a broke cutout got repaired and power restored at 09:30
14654 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2010-01-18 07:35 | 2010-01-18 12:45 | 1 | 310 | 55730-1 | 310 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 12RELEASED BY CREW 077S04//WILL NEED SERVICE REPLACED WITH 2/3 BURNED IN TWO IN MIDSPAN WILL REQUIRE 2 MEN AND BIG BUCKET//STS WR# 33475824 // VER/DBM IDC XXXX
14655 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-02-16 13:35 | 2018-02-16 16:10 | 2 | 155 | 4851341 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 19.9 cutout /no crew required/ ISO 38830501000070/ COD 2
14656 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-10-09 05:55 | 2017-10-09 11:05 | 1 | 310 | 4430561 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FEEDING THIS CUSTOMER WAS OUT LAST NIGHT//CALLED CUST AND SHE SAYS EVERYONE ELSE CAME ON BUT HERS // REPAIRED BROKEN CUTOUT COD-1 ISO TF VER/HFP L3/HFP
14657 | Hazard | 3302704 | HAZARD | KENMONT | 2019-04-16 14:55 | 2019-04-16 17:30 | 2 | 155 | 4122691 | 310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 transformer Released by crew 077H03.. changedout xfmr, all power restored @ 17:30 hrs.p.hicks
14658 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2009-02-24 10:28 | 2009-02-24 12:11 | 3 | 103 | 51024-1 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403002// CUTOUT BROKE//VER/CRB IDC XXXX
14659 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2019-03-07 06:12 | 2019-03-07 07:55 | 3 | 103 | 4958221 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 448-54, replaced cutout restored power at 07:55..
14660 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2011-02-13 16:29 | 2011-02-13 21:38 | 1 | 309 | 56595-1 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED TO REPLACE 5KVA TRANSFORMER ... REPLACED TRANSFORMER WITH 10KVA, ALL WORK COMPLETE / GXJ //VER/GAH IDC XXXX
14661 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-07-31 19:37 | 2018-07-31 21:20 | 3 | 103 | 4884141 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout, replaced cutout restored power at 21: 20../ ISO 37830448A00245/ COD 3
14662 | Pikeville | 3403001 | PIKEVILLE | CITY | 2021-06-07 11:28 | 2021-06-07 13:11 | 3 | 103 | 4679551 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. fuse ope @1-171, checking. Bad cutout on trans, got it replaced and power restored @1311.
14663 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-04-19 15:47 | 2013-04-19 17:30 | 3 | 103 | 4027311 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PAT THOVSON WILL WRITE THIS ORDER//38830137000118 BAD CUT-OUT WIRE MADE SAFE FOR NOW CAN WAIT FOR MON, TECH ON SITE POWER RESTORED @ 1730 KWB COD-3 ISO LF 38830137000032 VER/HFP L3/HFP IDC XXXX
14664 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-02-24 08:36 | 2015-02-24 13:45 | 1 | 309 | 4077691 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 15 KVA 7200 XFORMER, NEED LINE . CUST SAID YOU CAN CROSS BOTTOM HE WILL SHOW CREW. RELEASED BY CREW 078S01.. CREW ON SITE FETR 14:00.. REPLACED XFMR CHECKED VOLTAGE GOOD.. COMPLETE//COD 1// VER/DBM
14665 | Paintsville | 3401101 | FALCON | FALC-OILS | 2016-05-28 11:27 | 2016-05-28 13:10 | 3 | 103 | 4267931 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OOTHREE CUSTOMERS OUTOO CORRECT TRANSFORMER POLE IS 828-173. XFMR CUTOUT BROKE - REPLACING. REPLACED CUTOUT AND RESTORED @ 13:10. SH/ ISO 38830828000173/ COD 3 CCC*** PER SERVICER/ VER/BOW
14666 | Hazard | 3302704 | HAZARD | KENMONT | 2015-02-21 08:07 | 2015-02-21 09:50 | 3 | 103 | 4060951 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER PHASE (A) ONLY//COD 3//37830296C20097 B PHASE OPEN === BAD CUTOUT ON POLE 37830296C20958 === NEED BIG BUCKET AND CUTOUT ===37830296C20097 B PHASE OPEN === BAD CUTOUT ON POLE 37830296C20958 === NEED BIG BUCKET AND CUTOUT === RELEASED BY CREW 077S03//COD 3// VER/DBM
14667 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-12-31 11:57 | 2018-12-31 13:40 | 3 | 103 | 4615531 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on pole 170-112.repairs made.restored.
14668 | Pikeville | 3407101 | TOPMOST | DEMA | 2013-05-27 07:31 | 2013-05-27 09:14 | 3 | 103 | 4187391 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. CAN GET TRUCK TO. I HAVE CUTOUT REPLACED FUSED UP EVERYTHING OK COD-3 ISO TF 37830161D00164 VER/HFP L3/HFP IDC XXXX
14669 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-02-14 19:45 | 2017-02-14 21:28 | 3 | 103 | 4397961 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT ON POLE 269B-280 , FUSE WAS BROKE . CLOSED XFMR BACK @21:28 . 3 CUST. OUT ./ ISO 37830269B00280/ COD 3 CCOD***** MD DONE/ VER/BOW L3/HFP XXXHFP
14670 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2020-09-03 18:46 | 2020-09-03 23:55 | 1 | 309 | 4428241 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required cutout broke on pole behind water tank trucks maybe Released by crew 078S03,repairs made all cust restored @ 2355 please close ticket thanks.bt
14671 | Hazard | 3307301 | BULAN | ARY-HEINE | 2013-11-09 14:36 | 2013-11-09 19:45 | 1 | 309 | 4024531 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE. ONLY 1 CUST. OUT.//ISO//COD 1//MD FILED// VER/DBM
14672 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-06-15 17:01 | 2017-06-15 22:10 | 1 | 309 | 4974751 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA, SINGLE BUSHING 7200 120/240, CK VOLTAGE AT HOUSE, 162 V PHASE TO GRD ON BOTH LEGS, 332 PH TO PH, CAN USE TRUCK POND IN FRONT OF HOUSE, DRIVE BESIDE POND, WATCH LOW HANGING PHONE LINE, CREW REQ RELEASED BY CREW 078S06,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED 39830902C00557 VER/AWD
14673 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-07-07 13:54 | 2015-07-07 19:03 | 1 | 309 | 4738041 | 309 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | CONNECTION ON SECONDARY SIDE OF TRANSF === REPAIRED CONNEDCTION ==== POWER OK/ ISO 37830279000104/ COD 1/ VER/BOW
14674 | South Williamson | 3411401 | DEWEY | INEZ | 2010-05-17 10:51 | 2010-05-17 16:00 | 1 | 309 | 63783-1 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 35147626 // CREW HAD TROUBLE ON UG SECONDARY OVER WEEKEND AND HAD TO TEMP SEC IN CONDUIT ON TOP OF GROUND. FEED THRU CONNECTION WAS NOT MADE UP IN PEDESTAL. REPAIRING.CREW HAD TROUBLE ON UG SECONDARY OVER WEEKEND AND HAD TO TEMP SEC IN CONDUIT ON TOP OF GROUND. FEED THRU CONNECTION WAS NOT MADE UP IN PEDESTAL. REPAIRING. COULD NOT REPAIR. RELEASED BY CREW 076S02 VER/HFP L3/HFP IDC XXXX
14675 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2020-03-20 13:12 | 2020-03-20 14:55 | 3 | 103 | 4495871 | 309 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr lead , put new leads & connections , restored power at 14:55..
14676 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-10-05 08:16 | 2011-10-05 13:25 | 1 | 309 | 4948071 | 309 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO FUSES OUT.2 HOLE CONNECTOR PADS FOR 350 MCM COPPER LEADS, BURNT OFF OF SECONDARY GROUND BUSHING ON MIDDLE XFMR OF 167KVA XFMR BANK.NOTIFIED TIM HALL.THIS HAS HAPPENED B4 BECAUSE OF CUST TROUBLE (THEY WILL NOT USE THEIR CAPACITOR BANK).//.DE-ENERGIZED XFMRS.TIM HALL OR SHAWN SUMNERS WILL CONTACT DDC ABOUT REPAIRS..MAY LEAVE OFF.JRV..//REPLACED 350 CU NEUTRAL WITH 500/CUSTOMER SAID THEY REPAIRED THEIR CAP BANK/ CLOSED IN AT 1325 VER/KEP IDC XXXX
14677 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-04-29 18:32 | 2017-04-29 20:15 | 3 | 103 | 4695911 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFM. CUTOUT ON POLE 285-29...REPAIRS MADE../ ISO 37830285000029/ COD 3/ VER/BOW L3/HFP XXXHFP
14678 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-08-12 08:43 | 2016-08-12 13:52 | 1 | 309 | 4766051 | 309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100 KVA 19.9, ON A BANK OF TRANSFORMERS, WILL REQUIRE A CREW WITH MATERIAL HANDLER BUCKET. REPLACED TRANSFORMER.. VER/AWD
14679 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2018-06-29 22:22 | 2018-06-30 03:30 | 1 | 308 | 4690861 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 10 kva 120/240/7200 Can use truck. Need 2 men, a material handler, and a 15 or 25 kva transformer Released by crew 074S07 COMPLETED 03:30
14680 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-04-04 13:38 | 2014-04-04 16:12 | 2 | 154 | 4574061 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT ON POLE 37820009C00026. THIS CUTOUT IS ON THE PRIMARY TAP AND IT IS OUT ALSO. HOMER & RICHARD ARE ON THE WAY HERE TO FLAG TRAFFIC SO I CAN REPLACE THE CUTOUT. POWER IS RESTORED.//COD 2// VER/DBM
14681 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-04-27 10:34 | 2010-04-27 15:42 | 1 | 308 | 51942-1 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT VER/KEP L3/KEP IDC XXXX
14682 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-02-17 14:16 | 2022-02-17 16:50 | 2 | 154 | 4492861 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva 7200 120/240 transformer on pole 140-248, trucks to pole Released by crew 078S02 XFMR replaced, closed at 16:50
14683 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-06-09 13:46 | 2021-06-09 16:10 | 3 | 144 | 4697271 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad XFMR on pole 177-A-71, 25KVA, 7200. Truck access. Released by crew 077S04 opened line fuse on pole 71 at 15:50 replaced transformer and restored all power at 16:10
14684 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2012-02-10 10:32 | 2012-02-10 15:40 | 1 | 308 | 4332161 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA///VER/CRB IDC XXXX
14685 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-07-05 17:26 | 2022-07-05 20:00 | 2 | 154 | 4388241 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout
14686 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-06-17 23:22 | 2012-06-18 01:56 | 2 | 154 | 4924811 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER OUT ON POLE 39831123C24524 BROKEN FUSE LINK BURNT UP CUTOUT DOOR // 2 COD// VER/TOM L3/TOM IDC XXXX
14687 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-04-14 09:37 | 2014-04-14 14:45 | 1 | 308 | 4601871 | 308 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE TRANS. FUSE IS BLOWN ON NEW BANK OF TRANSFORMERS AT POLE 190-5. I AM GOING TO REFUSE TRANS. TRANS. IS BAD. STEVE RAY IS SENDING HELP. RELEASED BY CREW 074S01-WILL RE-PLACE C-PH.X-FMR R RAY VER/CRB
14688 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-10-16 15:16 | 2010-10-16 17:50 | 2 | 154 | 60294-1 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER IS BAD I WILL NEED TRANSFORMER CUTOUT AND BRACKETT BIG BUCKETT AND ONE MAN REPLACED TRANSFORMER//VER/CRB IDCC FP0 XXXX
14689 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2011-10-28 08:38 | 2011-10-28 09:55 | 4 | 77 | 4029261 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3675 BOBBY TACKETT ON SITE CUTOUT FAILED OPENED FUSE ON 171-197 TO ISOLATE VER/KEP IDCC TOF0831, ESTIMATED TIME OFF XXXX
14690 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-08-22 19:02 | 2011-08-23 00:10 | 1 | 308 | 4745811 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE DOOR BURNT-UP BUT FUSE WAS ALSO BLOWN WITH NO CAUSE FOUND. WILL HAVE TO CHANGE CUTOUT TO CHECK XFMR. CHANGED CUTOUT - 25KVA XFMR BAD. CREW ENROUTE TO CHANGE. RELEASED BY CREW 076S02FUSE DOOR BURNT-UP BUT FUSE WAS ALSO BLOWN WITH NO CAUSE FOUND. WILL HAVE TO CHANGE CUTOUT TO CHECK XFMR. CHANGED CUTOUT - 25KVA XFMR BAD. CREW ENROUTE TO CHANGE. REPLACED XFMR, CUTOUT AND ARRESTER. RESTORED @ 00:10. SH //VER/GAH IDC XXXX
14691 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-02-25 07:16 | 2019-02-25 12:24 | 1 | 308 | 4906051 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | \\ crew required at p#142-6026 bad 12kv cutout and one 500 kva stepdown. crew required oil spill bring 3 12kv cutout and 3 34kv cutouts open A and B stepdown@1105 s.d. and cut outs replaced back in service 1213 Released by crew 078Q09 ¦¦ ONLY 1 CUSTOMER SERVED BY THIS STEPDOWN
14692 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-07-05 16:06 | 2008-07-05 16:50 | 7 | 44 | 62935-1 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED XFMR. SH COD - 7 VER/HFP IDC XXXX
14693 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-07-06 09:52 | 2015-07-06 15:00 | 1 | 308 | 4730051 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE IS BAD,WILL REM AND RE-FUSE/////////REMD CL FUSE,RESTORED POWER// VER/ ADH
14694 | Pikeville | 3413402 | GARRETT | LACKEY | 2012-07-13 20:41 | 2012-07-13 23:15 | 2 | 154 | 4719061 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN, REPLACED CUTOUT AND REFUSED LINE, ALL WORK COMPLETE / GXJ COD-2 ISO TF 37830159000559 )(&)(*_)(*_)(*_)(*_)*_)*_)*
14695 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-02-28 11:45 | 2022-02-28 13:02 | 4 | 77 | 4552471 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WORKING ON UG OFF TRANS 37830223B00207 opened transformer at11:45 to make repairs to connections closed back at13:02
14696 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2010-06-09 16:52 | 2010-06-09 22:00 | 1 | 308 | 59407-1 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 35498742 // POWER BACK ON COD-1 VER/HFP L3/HFP IDC XXXX
14697 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-12-02 18:02 | 2012-12-02 18:46 | 7 | 44 | 4437061 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE ///VER/CRB L/3 CRB IDC XXXX
14698 | Paintsville | 3401101 | FALCON | FALC-OILS | 2013-06-14 13:32 | 2013-06-14 18:40 | 1 | 308 | 4333481 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA XFMR. NEED THREE MEN AND LINE TRUCK TO CHANGE TO 25KVA APPROX 75 FEET UP BANK OFF A GRAVEL DRIVE. CREW ENROUTE. REPLACEMENT COMPLETE. RESTORED @ 18:40. SH COD 1 ISO TF 828-315 VER/SEF IDC XXXX
14699 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2014-11-06 08:12 | 2014-11-06 13:20 | 1 | 308 | 4704061 | 308 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SQUEEZON ON TRANSFORMER RISER, RESQUEEZED AND EVERYTHING IS FINE AT THIS LOC// COD 1// VER/ ADH
14700 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-02-17 08:57 | 2009-02-17 14:05 | 1 | 308 | 63040-1 | 308 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP WR # 28550499 SERV-IN PULLED LOOSE ON NET SERVICE L3/HFP
14701 | South Williamson | 3411401 | DEWEY | INEZ | 2019-10-16 04:37 | 2019-10-16 09:45 | 1 | 308 | 4143671 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout//servicer attempting to repair //xfmr cutout broke//crew bringing big bucket//xfmr cutout broke//crew bringing big bucket//repairs made//restored at 9:45/complete L3/HFP
14702 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-07-19 06:31 | 2021-07-19 09:05 | 2 | 154 | 4933191 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A phase only, 2 customersOn pole 144-A-62,A Phase Line fuse is open,(ASSESSING CONDITION)On pole 144-A-62,A Phase Line fuse is open,(ASSESSING CONDITION)Found a bad Arrester on pole 144-A-421 cut in in clear.Restored service at 09:05.
14703 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-06-08 06:16 | 2010-06-08 08:50 | 2 | 154 | 58570-1 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE DISPATCHED IN THE A.M. XFMR CUTOUT DOOR BURNT-UP. WILL HAVE TO REPLACE CUTOUT. REPLACED CUTOUT AND BLOWN ARRESTER. RESTORED @ 08:50. SQUIRREL HAD TAKEN OUT FUSE CAUSING DOOR TO EXPLODE. SH//COD 2// VER/DBM
14704 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-07-30 18:22 | 2012-07-30 23:30 | 1 | 308 | 4867511 | 308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOT A BAD 25KVA 7200 XFMR.PRIMARY ALSO OFF INSULATOR ON THIS POLE. WILL PROBABLY HAVE TO OPEN FUSE ON POLE 279-50 WHEN THEY CHANGE XFMR. CAN BE WORKED WITH BUCKET. // B CLEMONS & J BAKER // SEE 4868501 FOR RECLOSER OUTAGE TO MAKE REPAIRS //GOT A BAD 25KVA 7200 XFMR.PRIMARY ALSO OFF INSULATOR ON THIS POLE. WILL PROBABLY HAVE TO OPEN FUSE ON POLE279-50 WHEN THEY CHANGE XFMR. CAN BE WORKED WITH BUCKET.//// OPENED REC ON POLE 279-250 AT 22:54 CLOSED REC. 23:30. COMPLTED VER/TOM L3/TOM
14705 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-07-03 17:58 | 2011-07-03 23:05 | 1 | 307 | 4451331 | 307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7.2 KV TRANSFORMER. NEED 1 MAN, MATERIAL HANDLER AND FLAGMEN VER/TOM IDC XXXX
14706 | Hazard | 3303901 | LESLIE | HYDEN | 2022-05-08 20:43 | 2022-05-09 01:50 | 1 | 307 | 4866941 | 307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 xfm. truck acc / 7200 cutout & bracket needed Released by crew 077S10. Power restored.
14707 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-02-26 07:53 | 2022-02-26 13:00 | 1 | 307 | 4547761 | 307 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfm has low voltage on one leg///will need 25KVA xfm 19.9////Crew enroute///Changed xfm ,replaced #4 service with 50of #2 ///Replaced cutout///Restored @ 13:00///125/125/250
14708 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2018-12-13 19:29 | 2018-12-14 00:36 | 1 | 307 | 4563301 | 307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required.bad CSP trans on 82-A-170.possible trk app but doubtful. need 7200 15 kva trans and cutout & standoff bracket.crew arrived.restored power at 00:36. L3/HFP
14709 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-07-27 08:54 | 2009-07-27 14:01 | 1 | 307 | 59783-1 | 307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501// BROKE CUTOUT ON LINE FUSE IDC XXXX
14710 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-04-05 09:38 | 2010-04-05 14:45 | 1 | 307 | 58695-1 | 307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TO REPLACE THREE CUTOUT ON POLER //VER/CRB IDC XXXX
14711 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2022-09-20 08:53 | 2022-09-20 14:00 | 1 | 307 | 4899711 | 307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fuses out per customer (cust callback 606-794-5640) //. cutouts bad on pole 333-D2-276. changed cutouts and burnt brace.. power restored
14712 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-02-29 17:58 | 2012-02-29 23:05 | 1 | 307 | 4522081 | 307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | PRIMARY BUSHING BROKE OFF OF ONE METERING CAN.BYPASSED 1 PHASE TO RESTORE POWER AND ISOLATED BAD METERING.SEND TO DWAYNE THACKER, CLIFF FREEMAN, AND BOB SHURTLEFF//SENT EMAILS // VER/DBM IDC XXXX
14713 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-06-01 14:01 | 2011-06-01 19:08 | 1 | 307 | 4219361 | 307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 40199638 // ROADSIDE 25 KVA XFMR BAD IN 120-240 WYE DELTA BANK. DUTY SUPERVISOR NOTIFIED AND WILL SEND CREW TO CHANGE AS SOON AS ONE CAN BREAK AWAY FROM WORK IN PROGRESS. CHANGED TRANSFORMER AND VERIFIED VOLTAGE AT 19:08 VER/KEP IDC XXXX
14714 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2020-06-04 20:23 | 2020-06-05 01:30 | 1 | 307 | 4957921 | 307 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | METER ELECTRCIAN AND LINE ARE GOING TO CHANGE OUT PT, EVERYTHING PICKED UP OK //
14715 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-07-21 09:53 | 2012-07-21 11:35 | 3 | 102 | 4790491 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | X-FMR FUSE IS OPEN ON POLE 354-43. CHECKING OUT THE SITUATION. X-FMR CHECKED GOOD. GOING TO REFUSE CUT-OUT. FUSE HAD PULLED OUT IN CUT-OUT GATE CAUSING OUTAGE. REFUSED CUT-OUT THUS RE-ENERGIZING POWER TO CUSTOMERS AT 11:35 07/21/2012. J.S.B. COD-3 ISO TF 37830354000043 VER/HFP L3/HFP
14716 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-07-07 14:14 | 2010-07-07 14:48 | 9 | 34 | 62976-1 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED NEW LEADS INSTALLED IN EXISTING 50 KVA SEND TO LINE CREW RELEASED BY CREW 077S04 OPENED TR AT 1414- CLOSED AT 1448.//VER/CRB IDC XXXX
14717 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-07-30 16:06 | 2017-07-30 21:12 | 1 | 306 | 4207941 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR.NOT TRUCK ACCESSIBLE.NEED 3 MEN..CAN GET SQUIRT BOOM TO POLE. RELEASED BY CREW 076S01// STARTING REPAIRSREPAIRS COMPLETE, RESTORED AT 21:12 VER/CRB
14718 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-11-02 05:46 | 2015-11-02 10:52 | 1 | 306 | 4401901 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STEP-DOWN IS BAD ON POLE 37820098A00537 167KVA CREW ENROUTE VER/CRB
14719 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-03-10 19:44 | 2021-03-11 00:50 | 1 | 306 | 4324491 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Correct xfmr pole for this account is 900-49. Bad 25 KVA transformer. Can truck. Replaced xfmr and restored @ 00:50. sh // cod 1
14720 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-23 11:59 | 2011-05-23 17:05 | 1 | 306 | 4142641 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S01 7200 25KVA TRANSFORMER LEAKING OIL--NEEDS CHANGED--MATERIAL HANDLER CAN GET OFF RD AND WORK POLE CREW REQUIRED RELEASED BY CREW 078S07 OFF 1701 ON 1708 COD-1 VER/HFP L3/HFP
14721 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-10-06 09:31 | 2014-10-06 09:49 | 17 | 18 | 4556621 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICER FOUND BAD WIRE ON POLE 166-A-100, OPENING RECLOSER 142-B2-6040 TO REPLACE WIRE//WILL HAVE OPEN FOR ABOUT 45 MINUTES// WIRE MID SPAN IS BROKEN OPEN RECLOSER AT 9:31 CLOSE RECLOSER AT 09:49/// COD 17// VER/ ADH VER/DKG L3/DKGXXXX
14722 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-04-24 12:54 | 2008-04-24 14:36 | 3 | 102 | 53842-1 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL RE-FUSE XFRRE-FUSED XFR,ALL OK AFTERWARDS//3411802//VER/CRB IDC XXXX
14723 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-05-04 18:28 | 2017-05-04 20:10 | 3 | 102 | 4747261 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE. REWORKED ALL XFMR CONNECTIONS AND RESTORED @ 20:10. THREE CUSTOMERS AFFECTED. SH 38830850000143 VER/AWD
14724 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-10-07 10:54 | 2014-10-07 16:00 | 1 | 306 | 4564531 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER NO METER DISPLAY DUE TO BAD SERV END MADE REPAIR EVERYTHING OK VER/HFP L3/HFP
14725 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-10-08 11:55 | 2008-10-08 14:28 | 2 | 153 | 54286-1 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP RELATED TO ORDER 54181-1 CREW OPENED LINE FUSE TO ALLOW THEM TO REPLACE POLE THAT HAS TOP BURNT OFF//BA00D CUTOUT ON POLE 450-287 OPEN FUSE ON POLE 450 -24 3 CUSTOMERS OFF WILL CALL CREW FOR HELP COD-2 IDCC TOF1027, FEC57 XXXX
14726 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-06-22 19:37 | 2010-06-22 22:10 | 2 | 153 | 55023-1 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA BRINGING ONE FROM HAZ. //VER/GAH IDC XXXX
14727 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-01-17 19:21 | 2009-01-17 19:39 | 17 | 18 | 57817-1 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | VER/HFP CREW OPENED LINE FUSE LONG ENOUGH TO REPLACE A FUSE IN A PAD MOUNT TRANSFORMER COD-17 L3/HFP
14728 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-03-04 10:13 | 2019-03-04 13:03 | 5 | 170 | 4949631 | 306 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke in service on 71-15, will have to open trans to replace, will keep track of times. Opened trans @1229, made repairs and closed back in @1303, only 1 customer had part power until I opened trans.
14729 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-05-27 08:37 | 2014-05-27 11:10 | 2 | 153 | 4932171 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN ON POLE 794-250//CLOSED IN AND CUTOUT WAS ARCING///I REPLACED CUTOUT//RESTORED AT 11:10//COMPLETE VER/CRB
14730 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2013-12-16 08:48 | 2013-12-16 10:30 | 3 | 102 | 4164781 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK NO CREW REQUIRED//COD 3// VER/DBM L3/HFP
14731 | Hazard | 3303902 | LESLIE | WOOTON | 2020-03-12 21:49 | 2020-03-13 02:55 | 1 | 306 | 4473191 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout//lifted tap at pole 37830438000056 @ 0155 to isolate, no addtl customers interrupted //Power restored @ 2:55 // cod 1 //
14732 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-04-01 06:24 | 2022-04-01 10:55 | 6 | 271 | 4710351 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on arm. Crew required may be able to get service truck to pole. Released by crew 078S11 // XFMR ON 38830380000024 (1 COD) IS WHAT IS OUT // OPEN LF (5 COD) ON POLE AS WELL TO CHANGE CUTOUT OFF@ 1048 RESTORED ALL @1055///TR 38830380000024 was never out--mismapped customer
14733 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2012-01-26 17:54 | 2012-01-26 23:00 | 1 | 306 | 4295681 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 21-529 CUTOUT BAD B PHASE OPENED 3-65T LINE FUSES ON 21-28 TRUCK TO POLE SEND TO JOE H. RELEASED BY CREW 078S08/COS REPAIRS UNDERWAY// POWER REST. @ 23:00 J. HEMLEPP COD-1 VER/KEP IDC XXXX
14734 | South Williamson | 3411401 | DEWEY | INEZ | 2015-05-01 15:30 | 2015-05-01 17:12 | 3 | 102 | 4382251 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BROKEN ON POLE 38830768B00067 FEEDING TRANSFORMER FEEDING 3 CUSTOMERS REPLACED CLAMP VER/CRB
14735 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-01-06 15:47 | 2011-01-06 18:20 | 2 | 153 | 59330-1 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39349105 //CREW REQUIRED BAD 25 CSP NO TRUCKS NEEDS CUTOUT AND BRACKET/RED TRUCK AND WHITE VAN IN DRIVEWAY ON RIGHT RELEASED BY CREW 078S03//COD 2// VER/DBM IDC XXXX
14736 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-10-23 08:09 | 2010-10-23 13:15 | 1 | 306 | 62300-1 | 306 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | RELEASED BY CREW 074S02 REPLACED UNDERGROUND SEVICE.// VER/DBM IDC XXXX
14737 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-02-21 14:26 | 2020-02-21 16:08 | 3 | 102 | 4423191 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cut Out is broke on pole 237-A-213 Will replace and restore service,I can make repairs with truck. Restored service at 16:08. L3/HFP
14738 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-04-11 07:38 | 2009-04-11 09:20 | 3 | 102 | 51356-1 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT TRYING TO REFUSE///50 KVA 7200 120/240 XFMR BAD WILL REQUIRE TWO MEN AND A MATERIAL BUCKET//REPLACED 50 KVA RESTORED COMPLETE AT 09:20//VER/CRB IDC XXXX
14739 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-10-27 14:03 | 2014-10-27 14:37 | 9 | 34 | 4664751 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE NECESSARY TO ALLOW CREW TO SAFELY REPLACE CUTOUT = NO TRUCK ACCESS // COD-9 ISO LF 37830024B10029//VER/ ADH L3/HFP AJB CCO FEC57
14740 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-09-15 10:43 | 2010-09-15 13:16 | 2 | 153 | 50011-1 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36891450 /// 7.2 LINE CUTOUT BAD AT POLE 37830177D00053 CALLING FOR CREW RELEASED BY CREW 077S04 OPENED XFMR AT1240 RESTORED ALL POWER AT 1318 CHANGED CUTOUT 077H01 COD-2 VER/HFP L3/HFP IDC XXXX
14741 | Hazard | 3301401 | COMBS | COMBS | 2011-09-04 19:27 | 2011-09-04 22:00 | 2 | 153 | 4810891 | 306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 37830271C00107, NEED 1 MAN AND BUCKET TRUCK, 7200 CUTOUT AND TEE BRACKET.--- POWER RESTORED.//COD 2// VER/DBM IDC XXXX
14742 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-11-19 02:45 | 2008-11-19 07:50 | 1 | 305 | 66425-1 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR 27354511 DAMGED SERVICE DROP--CUSTOMER OPENED BREAKER--WILL RETIRN LATER TO REPAIR-RESEND RELEASED BY CREW 078S07 --OPENED TRANSFORMER POLE 45-3015 AT 07:1 0 TO MAKE REPAIRS APX 30 MINUTES // BACK ON AT 07:50 VER/KEP IDC XXXX
14743 | Paintsville | 3401101 | FALCON | FALC-OILS | 2011-06-16 11:05 | 2011-06-16 16:10 | 1 | 305 | 4326981 | 305 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN CONN FAILED // REPAIRS COMPLTED TO RESTORE 240V BUT APPEARS CUSTOMER HAS JUMPER INSIDE, NO CONTACT FOR CUSTOMER, DISCONNECTED AT METER UNTIL CUSTOMER CAN BE ON SITE // ALL WORK COMPLETE / GXJ// VER/DBM
14744 | Cannonsburg | 3001401 | LOUISA | CITY | 2014-01-24 16:59 | 2014-01-24 18:00 | 5 | 61 | 4310201 | 305 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | OLD FUSE HAD BROKEN, REFUSED XMF APR AT 1800 CLOSE TICKET. DWE COD-5 ISO TF 38830454A41763 VER/HFP L3/HFP IDC XXXX
14745 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-04-25 13:26 | 2010-04-25 18:31 | 1 | 305 | 50831-1 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34819030 // BAD 15KVA SEND TO LLOYD MC. NO TRUCKS TO POLE ONE CUST OUT RELEASED BY CREW 078S08 VER/HFP L3/HFP IDC XXXX
14746 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-02-01 10:51 | 2013-02-01 15:56 | 1 | 305 | 4781471 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEC. LUG BURNT OFF AT TRANSFORMER, J. COMBS BRINGING TRANSFORMER. ONLY 1 CUST. ON THIS TRANSFORMER. ///VER/CRB L/3 CRB IDC XXXX
14747 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-07-12 21:19 | 2013-07-12 22:20 | 5 | 61 | 4516681 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD C/O & 6T MP RELEASED BY CREW 078H12 VER/CRB L/3 CRB IDC XXXX
14748 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-04-19 08:40 | 2015-04-19 13:45 | 1 | 305 | 4333761 | 305 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR LEAD.OPENED XFMR AT 13:15 CLOSED IN AT 13:45/COD 1+1 DUPLICATE IN HOIS// VER/ ADH
14749 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2013-03-20 12:59 | 2013-03-20 14:00 | 5 | 61 | 4927051 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE/ FETR 14:30 JEH/ REPAIRS COMP. POWER REST. @ 14:00 // JEH// ( 4 METERED ACCOUNTS ON THIS TRANSFORMER) VER/KEP IDC XXXX
14750 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-06-21 15:29 | 2018-06-21 16:30 | 5 | 61 | 4635871 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o door, restored
14751 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-12-01 15:55 | 2015-12-01 21:00 | 1 | 305 | 4500001 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1064-76 .TALKED TO CREW WORKING SAID THEY WOULD CHANGE CUTOUT . CAN WORK WITH BIG BUCKET .ADDRESS 1501 HWY 542 , GRAY GARAGE ON RT. 19.9 CUTOUT . SEND TO RONNIE RICE ./ ISO 38831064000076/ COD 1/ VER/BOW
14752 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-12-27 07:43 | 2016-12-27 12:48 | 1 | 305 | 4240821 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON XFMR POLE, MANUEL POLE ACROSS CREEK, MIGHT NEED TO STRAIGTEN POLE BEFORE CLIMBING RELEASED BY CREW 077S02 REPAIRS MADE AND POWER RESTORED AT 1248 VER/CRB
14753 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-09-20 11:28 | 2018-09-20 16:33 | 1 | 305 | 4134621 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr, please send ticket to G. Shouse Released by crew 077S02
14754 | Whitesburg | 3314401 | MAYKING | ERMINE | 2022-03-02 06:14 | 2022-03-02 07:15 | 5 | 61 | 4558341 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutotut gate burnt up on pole 449-C1-1463.. replaced bad gate. power restored
14755 | Cannonsburg | 3110901 | WURTLAND | WURTLAND | 2008-02-13 00:04 | 2008-02-13 05:09 | 1 | 305 | 61944-1 | 305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3110901/// FOUND A AND C PHASE CUTOUTS OPEN ON PRIMARY METERING POLE, FOUND ARM TO BE SMOKING, AND PIECEING LAYING ON THE GROUND, CALL FOR CREW TO COME AND HELP. WELL NEED CROSSARM, ARRESTORS, ARM PINS, AND DEAD END INS. RELEASED BY CREW 078S06/CREW ON SITE/FETR0600/VEM/REPAIRS MADE AND POWER RESTORED 0509/CREW IS WORKING ON GETTING TRUCK OUT/VEM VER/ARN IDCC PN0002 XXXX
14756 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-06-26 15:51 | 2014-06-26 20:56 | 1 | 305 | 4160001 | 305 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION SERVICE DROP POPWER RESTORED VER/HFP L3/HFP
14757 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2016-04-18 09:51 | 2016-04-18 14:55 | 1 | 304 | 4099101 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1.6 T FUSE OUT DUE TO BAD TRANSFORMER.. NEED CREW 19.9 120/240 2BUS TRANSFORMER. CAN USE TRUCK RELEASED BY CREW 074S111.6 T FUSE OUT DUE TO BAD TRANSFORMER.. NEED CREW 19.9 120/240 2BUS TRANSFORMER. CAN USE TRUCK . TRANSFORMER CHANGED OUT EVERYTHING OK VER/CRB
14758 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-03-13 14:31 | 2015-03-13 19:35 | 1 | 304 | 4190761 | 304 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 69-588 HOT TAP BROKE OFF B PHASE NEED CREW SOCCER FIELD BY ASHLAND HIGH SCHOOL ON FLOYD ST. RELEASED BY CREW 078S08/COD 1//ISO 38830069A20588 // VER/DBM
14759 | Pikeville | 3402002 | KEYSER | STONECOAL | 2021-04-23 07:55 | 2021-04-23 10:27 | 2 | 152 | 4473071 | 304 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burned up .will make repairs. pulled off @ 10:15 on @10:27 power is restored. (no outage till transformer was opened) LR- The call came in as part out at 07:55 on 4-23-21.
14760 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2015-07-20 07:13 | 2015-07-20 09:45 | 2 | 152 | 4914591 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL NEED BIG BUCKET & 1 MAN TO MAKE REPAIRS. HAVE ALREADY CONTACTED PIKEVILLE VER/CRB
14761 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2019-03-09 22:58 | 2019-03-10 01:30 | 2 | 152 | 4965681 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout and restored @ 1:30.sh//cod 2
14762 | Pikeville | 3408401 | KIMPER | LONGFORK | 2009-08-24 14:40 | 2009-08-24 17:12 | 2 | 152 | 63621-1 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WILL DETERMINE NATURE OF PROBLEMTHIS IS THE XFR THAT IS BURNED UP,COULDNT GET TO IT TO REPLACE IT.THIS WAS ABT 2 WEEKS OR SO AGO.STILL CANT GET TO IT /// NOTED CUSTOMERS ACCOUNT & SERVICER TALKED TO CUSTOMER ABOUT NEEDING ACCESS TO POLE. L3/HFP IDC XXXX
14763 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-05-27 13:01 | 2009-05-27 18:05 | 1 | 304 | 56362-1 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3310501// STS THIS IS CSP TRANSFORMER, GOING TO TRY RESET HANDLE , BAD TRANSFORMER, CALL GLEN AND HE SAID HE WOULD GET CREW TO CHANGE TRANSFORMER RELEASED BY CREW 077S05 // WORK REQUEST 30000257// COD-1 ISO 38830992000063 L3/HFP IDC XXXX
14764 | Hazard | 3302703 | HAZARD | HAZARD | 2010-08-11 20:53 | 2010-08-11 23:25 | 2 | 152 | 53113-1 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR FAILED ON SECONDARY RISER OPENED XFMR AT 22:55 RESTORED COMPLETE AT 23:25//VER/CRB IDCC TOF2255, CNT21 XXXX
14765 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2021-04-19 07:58 | 2021-04-19 10:30 | 2 | 152 | 4460171 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout had failed. Made repairs and restored at 10:30
14766 | Hazard | 3309003 | JEFF | VIPER | 2022-08-29 19:58 | 2022-08-29 22:30 | 2 | 152 | 4810281 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | guy wire hitting xfmr
14767 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2017-10-08 14:04 | 2017-10-08 15:20 | 4 | 76 | 4422041 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER NUMEROUS TIMES BUSY SIGNAL TRANSFORMER CUTOUT FAILED. REPLACED AND RESTORED @ 15:20. SH/ ISO 38830786A00121/ COD4/ VER/BOW VER/HFP L3/HFP
14768 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-12-18 19:02 | 2011-12-19 00:06 | 1 | 304 | 4187021 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 19.9 XFMR // SHOULD POBABLY GO BACK WITH A 25KVA // COD 1//CREW REQUIRED RESTORED POWER AT 0006 //VER/GAH IDC XXXX
14769 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-04-06 14:27 | 2011-04-06 15:05 | 8 | 38 | 50732-1 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WR# POLE 1147-4059 10T ME FUSE LINK BROKE//VER/CRB
14770 | Hazard | 3303902 | LESLIE | WOOTON | 2011-08-22 14:07 | 2011-08-22 16:39 | 2 | 152 | 4739751 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NOT ARCING BUT SAW DAMAGE TO L/A WILL REPAIR IN THE MORNING RELEASED BY CREW 077S01BAD CUTOUT WILL NEED CREW WITH BIG BUCKET MANUEL , REPLACED CUTOUT AND ARRESTOR ---RESTORED POWER AT 1639 . JKC //VER/CRB IDC XXXX
14771 | Pikeville | 3421002 | BREAKS | GRASSY | 2019-11-14 14:05 | 2019-11-14 14:13 | 38 | 8 | 4034561 | 304 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | Short outage to safely bypass Regulator at Breaks Station/ DOL 971003 & 970950 off @ 1405 on @ 1413
14772 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-11-10 08:55 | 2015-11-10 10:11 | 4 | 76 | H4423221 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED: LINE CUTOUT BROKEN, NO TRUCK ACCESS, POLE 564, WILL NEED TO OPEN AT POLE 1125-63 FOR REPAIRS (NO HOT TAP ON LINE CUTOUT AT POLE 564 ) 19.9 KV RELEASED BY CREW 074S03 OPENED FUSE ON POLE 63 AT 8:55 CLOSED AT 10:11 D SAMMONS DUP OF 4423221 VER/HFP L3/HFP AJB
14773 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-11-28 09:17 | 2011-11-28 14:21 | 1 | 304 | 4118921 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN// BAD CUTOUT//7,200// RELEASED BY CREW 074H14 VER/KEP IDC XXXX
14774 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-04-22 08:08 | 2012-04-22 10:40 | 2 | 152 | 4693711 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7.2 KV CUTOUT //COD 2//ISO//MD FILED FOR MISSMAPPED CUST// VER/DBM IDC XXXX
14775 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-09-07 15:40 | 2018-09-07 18:12 | 2 | 152 | 4054631 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse/ ISO 37830100000061/ COD 2
14776 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-02-22 08:18 | 2020-02-22 10:50 | 2 | 152 | 4423871 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke into, I replaced it L3/HFP
14777 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2018-03-15 19:38 | 2018-03-15 20:54 | 4 | 76 | 4018561 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot tap on txmf riser was broke, replaced hottap, apr at 2054. close ticket
14778 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-05-16 11:00 | 2012-05-16 16:04 | 1 | 304 | 4800231 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE NO, 1123-C-4052 BROKE OFF AT GROUND LINE 30-6 SET IN 1959 2/3 WIRE AND NEW POLE CREW NEEDED SINGLE OUTAGE TO TRL. OFF AT 11;00 AM WILL NEED TO CLEAR TRANSFORMER TO MAKE REPAIRS RELEASE TO ROB DEH CREW RELEASED BY CREW 078S09//COD 4// VER/DBM IDC CHANGED CUSTOMER COUNT FROM 4 XXXX
14779 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-01-17 02:38 | 2015-01-17 05:10 | 2 | 152 | 4940291 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT DOOR ON LINE FUSE POLE 185-19 NEED LINE CREW. RELEASED BY CREW 078S01 RESTOREDE 0510 MD FILED FOR FUSE VER/KEP L3/HFP XXX
14780 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-10-21 15:50 | 2020-10-21 18:22 | 2 | 152 | 4574281 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Trans fuse is Blown going to be Looking it over.Had a bad Lightning Arrester,Cut it in clear and restored at 18:22..
14781 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2021-08-07 08:13 | 2021-08-07 13:17 | 1 | 304 | 4014041 | 304 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | crew required bad 4/0 ug one leg isolated on both ends/need add a phase Released by crew 078S03/arrived RM trouble shooting found bad hot leg fixed problem volatge good please close tic RM
14782 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-11-04 10:55 | 2008-11-04 13:27 | 2 | 152 | 62054-1 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27120650 // TRANSFORMER FUSE OUT BAD CUTOUT3308002// TRANSFORMER FUSE OUT BAD CUTOUT IDC XXXX
14783 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-05-14 10:00 | 2008-05-14 11:16 | 4 | 76 | 63895-1 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3409002// CREW OPENING U/G DIP FUSE TO REPAIR FAULTED U/G CABLE.OPENED AT 1000 CLOSED AT 1116 VER/KEP IDC PN395 XXXX
14784 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-03-01 19:29 | 2010-03-01 20:45 | 4 | 76 | 62028-1 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD BURNT OFF ON XFMR//// RECONNECTED LEAD, POWER RESTORED//VER/CRB IDC XXXX
14785 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-11-10 07:11 | 2014-11-10 12:15 | 1 | 304 | 4715751 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST HAS PART POWER // WILL CHECK BACK ON HILL // BAD 25KVA XFMR // CREW ENROUTE/ SEND TO S. RAY RELEASED BY CREW 074S05 VER/CRB L3/HFP
14786 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-08-30 11:23 | 2022-08-30 13:55 | 2 | 152 | 4815261 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke and took line fuse out as well. Power restored @ 13:55
14787 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-05-07 12:40 | 2013-05-07 15:12 | 2 | 152 | 4082291 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD FELL OUT OF XFMR//// REPLACED XFMR LEAD, POWER RESTORED COD-2 ISO TF 37830196D00217 VER/HFP L3/HFP IDC XXXX
14788 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-04-01 08:41 | 2015-04-01 13:45 | 1 | 304 | 4254131 | 304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA 7200 XFORMER NEED 15 KVA 7200. NEED LINE CREW TRUCKS TO POLE. RELEASED BY CREW 078S01 CLOSED 1345// VER/ ADH L3/DKGXXXX
14789 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-02-14 17:04 | 2016-02-14 18:45 | 3 | 101 | 4696091 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. REPLACED AND RESTORED @ 18:45. SH/ ISO 38830784C00015/ COD 3/ VER/BOW
14790 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-11-26 10:46 | 2008-11-26 12:27 | 3 | 101 | 52448-1 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP XFR FUSE IS OUT,WILL RE-FUSE IF NO PROBLEM IS EVIDENT.LITE ARRESTOR IS BLOWED UP,NEARLY ONTO T BRACKET.WILL TRY TO CLEAR UP WITHOUT CAUSING FURTHER PROBLEM ///SENT EMAIL TO RON RYE IDC XXXX
14791 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-06-28 21:19 | 2011-06-28 23:00 | 3 | 101 | 4433741 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ 37830048C30017// WILL CHANGECHANGED CUTOUT BACK TO NORMAL VER/KEP IDC XXXX
14792 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2022-07-18 13:22 | 2022-07-18 15:03 | 3 | 101 | 4513781 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. fuse open @72-A-272, checking. Trans. cutout busted here and pole covered in vines. Got cutout replaced and vines removed, restored @1503.
14793 | Hazard | 3309302 | VICCO | JEFF | 2019-01-22 11:27 | 2019-01-22 16:30 | 1 | 303 | 4704111 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 37830346A00494 U/G TERMINATION BURNT OFF
14794 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-03-02 12:27 | 2015-03-02 17:30 | 1 | 303 | 4091521 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 195-12/COD 1/BAD CUTOUT ON POLE 195-12 . POWER BACKON @ 17:30/ COD 1// VER/ ADH L3/HFP XXX
14795 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-12-26 07:44 | 2009-12-26 09:25 | 3 | 101 | 63386-1 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRYING TO REPLACED BASKET/ BROKE OFF/NO CREW REQUIRED
14796 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-09-26 15:41 | 2017-09-26 20:44 | 1 | 303 | 4391271 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 079H03///CUTOUT DOOR BROKEN ON 265B161 REPLACED DOOR RESTORED POWER AT 20;44/// VER/DKM ACBC FEC49
14797 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2015-07-28 10:47 | 2015-07-28 15:50 | 1 | 303 | 4951341 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PAUL PRATT RECIEVED CALL FROM CUSTOMER THAT POWER IS OUT/..BAD CUTOUT ON POLE 494-132 WIL NEED CREW , MANUEL POLE,, POWER RESTORED AT 15:50// VER/ ADH
14798 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2012-11-27 10:40 | 2012-11-27 12:21 | 3 | 101 | H4424091 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND BURNED OFF 8 FOOT CROSSARM. NEED CROSSARM, AND CUTOUT FOR 7200. I THINK YOU CAN USE BUCKET IF YOU BACK IN AT DRIVEWAY THAT SAYS STEPHANIES LN..APCO OPENED FUSE ON POLE 821B125 AT 10:40.//NO CUST ON APCO SIDE// ///VER/CRB L/3 CRB IDC LOOKS LIKE FROM COMMENTS THE INITIAL TRANSFORMER WOULD HAVE BEEN OUT BEFORE OPENING LINE XXXX
14799 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-12-27 08:01 | 2010-12-27 09:42 | 3 | 101 | 56060-1 | 303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN,WILL REPLACE IT///////REPLACED BROKEN 19.9 CUTOUT AND RESTORED.ALL OK AFTERWARDS CCC COD-3 ISO TF 38821130000155 VER/HFP L3/HFP IDC XXXX
14800 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2020-02-10 23:49 | 2020-02-11 02:20 | 2 | 151 | 4390581 | 302 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3000304/gaj/0001/McDonalds Corp part out disp 3319 M Phelps. bad 12kv c/o 20-5570. a phase -- opened other 2 phases to replace cutout no additional cust affected (2 CC) Released by crew 078S07 - back in at 0220
14801 | Hazard | 3420001 | SOFT SHELL | VEST | 2019-11-28 18:14 | 2019-11-28 20:45 | 2 | 151 | 4101121 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cuout broke on pole 37830108000032. power restored at 20:45
14802 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-08-17 08:44 | 2016-08-17 11:15 | 2 | 151 | 4799861 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER (0850) I CHANGED BAD CUTOUT AND REFUSED XFMR VER/AWD
14803 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-10-15 17:28 | 2012-10-15 22:30 | 1 | 302 | 4144031 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR C/O, NEED R/W CREW AND ONE A-MAN/// REPLACED C/O, POWER RESTORED.//COD 1// VER/DBM IDCC PN739 XXXX
14804 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2010-01-07 08:29 | 2010-01-07 11:00 | 2 | 151 | 64862-1 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA XFMR. CREW ENROUTE TO CHANGE. RELEASED BY CREW 076S02 // THIS TRANSFORMER FEEDS STATE HYW LIGHTS ONLY 240/480 VOLT NO RES CUSTOMERS OFF THIS TRANSFORMER TCM// ISO 38830784C00468 // COD 2// VER/DBM IDC XXXX
14805 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-09-11 12:58 | 2009-09-11 18:00 | 1 | 302 | 50641-1 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | VER/HFP CURRENT LIMITING FUSE WAS BAD L3/HFP IDC XXXX
14806 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2018-01-15 07:29 | 2018-01-15 10:00 | 2 | 151 | 4747931 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED ,184-60, replace xfr cutout,,no trucks Released by crew 078S05,replaced cutout all cust restored @ 1000 please close ticket thanks.bt // COD-2 ISO TF 38830184B00060
14807 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2018-05-18 17:23 | 2018-05-18 19:54 | 2 | 151 | 4372921 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 38831003D00057.trans cutout failed on 38831003D00070.i can make repairs.replaced cutout on 38831003D00070.restored power at 19:54
14808 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2022-01-07 05:08 | 2022-01-07 10:10 | 1 | 302 | 4318461 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connector failed at secondary pole. Repaired and restored @ 10:10. sh
14809 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-11-30 17:13 | 2016-11-30 22:15 | 1 | 302 | 4151981 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT---CLIMB JOB VER/CRB L3/HFP XXXHFP
14810 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2012-12-21 07:43 | 2012-12-21 12:45 | 1 | 302 | 4497741 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON PRIMARY METERING GOING TO OPEN PRIMARY METERING ON POLE 54-273. REPLACED BAD CUT -OUT RESTORED SERVICE. OPENED METRING UP@ 12:30 CLOSED BACK IN @12: 45 ////VER/CRB L/3 CRB IDC CHANGED TIME OFF FROM 1230 TO MATCH ALL OUT TICKET XXXX
14811 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-05-31 09:40 | 2012-05-31 14:42 | 1 | 302 | 4852751 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SECONDARY POLE 1124-109 TOP WAS BROKE OFF, CUSTOMER WORK ON ROAD AROUND HILL. LITTLE MUD . POLE IS SETTING ON ROCK CLIFF, WE MAY BE ABLE TO POLE IN BOTTOM. WILL BE DRILLING IN ROCK. SEND THIS TO TIM HALL, OPEN ON TP.1124-11, SP 1124-109 RELEASED BY CREW 074S05 ///VER/CRB L/3 CRB IDC XXXX
14812 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-02-24 16:13 | 2022-02-24 19:36 | 10 | 203 | 4541191 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke.//COD 1 FROM BEGINNING//Transformer cutout broke. Opened line fuse 878-38 @ 19:25 to safely make repairs.
14813 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-12-15 09:52 | 2014-12-15 12:23 | 2 | 151 | 4861221 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORKED ORIGINAL ORDER FROM OPS ORDER, FOUND BAD CUTOUT UPON ARRIVAL REPLACED CUTOUT CLOSE TIKET. COD-2 ISO TF 38830473000104 VER/HFP L3/HFP
14814 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2022-05-06 13:14 | 2022-05-06 15:45 | 2 | 151 | 4845681 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout broke on pole 351-C-54. cuout replaced, power restored
14815 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-06-11 09:58 | 2010-06-11 15:00 | 1 | 302 | 60021-1 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REQUIRES 15 KVA XFMR, 19.9 PRI 120/240 SEC. TIM H ALL WILL CALL CREW & LET YOU KNOW WHO TO SEND THIS TO. RELEASED BY CREW 074S04/// TIM MCCOYAND CREW HAS ARRIVED AT THE JOB SITE./// CHANGED XFMR OUT RESTORED POWER. AT 15:00 TIM MCCOY//COD 1// VER/DBM IDC XXXX
14816 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-08-15 08:53 | 2020-08-15 13:55 | 1 | 302 | 4329161 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM has Blown,Will be looking it over, We have a bad XFM on pole 170-49,Will need line crew and flaggers to change,19-9 15 KVA and cut-out.. Released by crew 074S01,comp 13:55
14817 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-01-12 09:54 | 2017-01-12 12:25 | 2 | 151 | 4290401 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE XFM. CUTOUT ON POLE 285-97.WILL MAKE REPAIRS..RESTORED @ 12:25. 37830285000097 VER/AWD L3/HFP HFP
14818 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-08-01 11:58 | 2015-08-01 17:00 | 1 | 302 | 4965971 | 302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A 1/0 TENSION SPLICE HAS FAILED AND PULLED LOOSE ON THE NEUTRAL ON 1/0 LASH, NEED TO DROP AND SPLICE OR REPLACE WITH 1/0 TRIPLEX. CREW REQUIRED, FORMAN AND A AND BC OR D. 150FT SPAN. RELEASED BY CREW 077S08.REPAIRES MADE POWER RESTORED @ 17:00HRS P.HICKS// VER/ ADH
14819 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-07-09 09:59 | 2014-07-09 15:00 | 1 | 301 | 4218401 | 301 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY BUSHING BAD ON XFMR . NEED XFMR & BIG BUCKET . 25 KVA XFMR RELEASED BY CREW 075H04 REPLACED TRANSFORMER POWER RESTORED AT 15;00//COD 1// VER/DBM
14820 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2008-08-09 03:19 | 2008-08-09 08:20 | 1 | 301 | 50428-1 | 301 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3403801// REPLACED TWO 300A SOLID BLADE CUTOUTS VER/KEP IDC XXXX
14821 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-06-25 11:44 | 2008-06-25 16:45 | 1 | 301 | 53848-1 | 301 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE HOT LEG OF THE UNDERGROUND SERVICE FAILED AT A SPLICE. VER/HFP IDC XXXX
14822 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-04-25 19:27 | 2015-04-25 20:10 | 7 | 43 | 4365521 | 301 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-81 BAD CUTOUT DOOR REPLACED DOOR/ ISO 38830069A10081/ COD 7/ VER/BOW L3/HFP XXX
14823 | South Williamson | 3411401 | DEWEY | INEZ | 2011-10-13 16:54 | 2011-10-13 21:55 | 1 | 301 | 4975561 | 301 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ACTUAL ISOLATION POLE IS 672-11//THERE IS ONLY ONE CUSTOMER OUT// XFMR CUTOUT BROKE/NO TRUCK//MILLER GETTING SOME HELP ON THE WAY// RELEASED BY CREW 079S01ACTUAL ISOLATION POLE IS 672-11//THERE IS ONLY ONE CUSTOMER OUT// XFMR CUTOUT BROKE/NO TRUCK//MILLER GETTING SOME HELP ON THE WAY// REPAIRS MADE//RESTORED AT 2155//COMPLETE/EM COD-1 ISO TF 38830672C00011 VER/HFP L3/HFP IDC XXXX
14824 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2022-06-27 18:15 | 2022-06-27 19:05 | 6 | 50 | 4331551 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patrolling. fuse or fuses blown on other side of river on kentucky side.968d8 missing b and c phase according to meter. can see middle fuse hanging down. everything seems clear on wv side. phases couldve blown together or into trees. //referred to KY disp 1430hrs//COD 2 FROM BEGINNING OF OUTAGE//CONTACTED JOSH(RDDC) THEY WILL STAY IN THE CLEAR TILL THIS OUTAGE IS CLEARED UP 1705//
14825 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2012-10-25 15:58 | 2012-10-25 17:38 | 3 | 100 | 4172311 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING. TENSION SLEEVE PULLED LOOSE FROM CUST. PIPE MAST, WILL HAVE TO OPEN TRANS. AT POLE 496-217 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES.OPENED AT 17:17, CLOSED BACK IN AT 17:38 VER/KEP IDCC TOF1717 XXXX
14826 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-02-22 14:25 | 2013-02-22 16:05 | 3 | 100 | 4840521 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR BAD, NEED 25KVA 7200, TRUCK OK, SEND TICKET TO JOE HEMLEPP RELEASED BY CREW 078S05////3347///ON SITE/ FETR 16:30//JEH// REPAIRS COMPLETE POWER RESTORED @ 16:05 //// JEH ///VER/CRB L/3 CRB IDC XXXX
14827 | Hazard | 3309002 | JEFF | JEFF | 2011-02-17 13:05 | 2011-02-17 14:45 | 3 | 100 | H58363-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSF == NEED LINE CREW AND ROW CREW == CALLED GLEN FOR LINE CREW RELEASED BY CREW 077S03 OPENED TAP @ 37830345C00177 TO ALLOW THEM TO SAFELY REPLACE TR @ 13??BAD 25 KVA TRANSF == NEED LINE CREW AND ROW CREW == CALLED GLEN FOR LINE CREW RELEASED BY CREW 077S03 OPENED LINE FUSE AT 13.05 CLOSED AT 14.45 DUPLICATE FROM 58363-1 VER/HFP L3/HFP IDC XXXX
14828 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-02-08 13:00 | 2011-02-08 13:20 | 15 | 20 | 55225-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38734838 //BAD CONNECTION AT TRANSFORMER RISER--NEED 4/0 RISER WIRE--CAN REACH WITH LARGE BUCKET-NEED TO CHANGE CUTOUT AT THIS TIME RELEASED BY CREW 078S07----- TIME OFF 13:00 -- TIME ON 13:20 VER/KEP IDC XXXX
14829 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2020-12-29 19:29 | 2020-12-29 21:09 | 3 | 100 | 4834381 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pulled into
14830 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-09-06 02:49 | 2012-09-06 03:49 | 5 | 60 | H4021751 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | A & B OUT (14 CC) GOT TWO LEADS BURNED OFF ON LINE SIDE OF RECLOSER OPEN C PHASE (5 CC) AT 0249 AND CLOSED AT 0340 //VER/GAH IDC XXXX
14831 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-10-13 16:45 | 2008-10-13 17:45 | 5 | 60 | 55500-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | VER/HFP OPENED FUSE @ 1645 CLOSED @ 1745 COD-5 STS WR # 26752946 /// POLE 37830095000062 LEANING OVER AND NEEDS STRAITENEDPOLE #95-62 ROTTEN AT GROUND LINE AND FELL OVER INTO TREE. POLE BELONGS TO AT&T JOE HUBBARD WILL CALL 10 14 08 AND SEE IT THEY WANT TO SET POLE OR HAVE US DO IT IDCC PN189 XXXX
14832 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-03-26 09:55 | 2008-03-26 11:35 | 3 | 100 | 60798-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409301// CREW OPENED LINE FUSE TO REPLACE CUTOUT//@ 0955 CREW REPORTED THEY FOUND A BAD PLACE IN THE CONDUCTOR ALSO AND WILL BE REPAIRING IT AS WELL/ VER/HFP IDCC PN56 XXXX
14833 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2008-07-14 14:00 | 2008-07-14 15:40 | 3 | 100 | 52482-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3309001 - POLE ROTTED OFF AT GROUND 417- 142 == REPLACED POLE == IDCC CNT1, TOF1233, ESTIMATED TIME OFF XXXX
14834 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-03-07 09:45 | 2012-03-07 11:00 | 4 | 75 | 4558001 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | // TM - THIS ORDER USED TO BE 4556871, BUT WAS CLOSED BY MISTAKE. CREATED NEW TICKET. NO OUTAGE, JUST LOW VOLTAGE. WE ARE GOING TO CHANGE TRANSFORMER ON POLE 96-21. WE OPENED TRANS. AT -9:45 , CHANGED TRANS. AND CLOSED TRANS. AT 11:00 VER/HFP L3/HFP IDC XXXX
14835 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-06-17 13:20 | 2019-06-17 14:20 | 5 | 60 | 4524531 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired service drop that had burnt down. pened txmf at 1320 closed at 1420 apr close ticket. please send copy to forestry trees are laying on primary cond at this location. not arking at this time.
14836 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2017-11-09 12:10 | 2017-11-09 13:50 | 3 | 100 | 4544711 | 300 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg fell out of one side of transformer, made repairs @1350./. ISO 37820053000205/ COD 3
14837 | Hazard | 3309301 | VICCO | REDFOX | 2009-07-22 15:33 | 2009-07-22 16:23 | 6 | 50 | H59168-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 077S02, SERVICE HAS 1 CONDUCTOR BAD, WILL NEED TO REPLACE. TOOK POWER OFF AT 1533 AND RESTORED AT 1623 VER/KEP L3/KEP IDC XXXX
14838 | Hazard | 3309003 | JEFF | VIPER | 2017-04-24 12:30 | 2017-04-24 17:30 | 1 | 300 | 4676791 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === REPLACED CUTOUT === POWER OK VER/CRB L3/HFP XXXHFP
14839 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-02-11 06:45 | 2019-02-11 11:45 | 1 | 300 | 4776611 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,APPEARS TOO HAZARDOUS TO FOOL WITH WITH LINE ENERGIZED .CREW ENROUTE TO HELP .MIGHT HAVE TO OPEN LINE LONG ENOUGH TO ISOLATE.WILL LET DDC KNOW IF NECESSARY TO OPEN .OPENED RECLR,OPENED 11:05 ,CLOSED 11:45 AFTER REPAIRS WERE COMPLETED//OTHER OUTAGE MADE FOR OCR OUTAGE
14840 | Hazard | 3309301 | VICCO | REDFOX | 2012-07-15 09:50 | 2012-07-15 14:50 | 1 | 300 | 4730401 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | FUSE OUT ON PRIMARY UNDERGROUND POLE # 324-172, JEFF COMBS CREW TO REPAIR UNDERGROUND RISER RELEASED BY CREW 077S02//COD 1
14841 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-10-07 13:30 | 2016-10-07 18:30 | 1 | 300 | 4967351 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE OPEN @137-D-650, CHECKING. BAD 25 KVA 19.9 @POLE 1137-D-650, WILL NEED A MATERIAL HANDLER AND 2 MEN TO CHANGE. RELEASED BY CREW 074S05,,POWER RESTORED AT 18:30 VER/AWD L3/HFP XXXHFP
14842 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2017-11-29 18:15 | 2017-11-29 23:15 | 1 | 300 | 4610491 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer meter blank,CREW REQUIRED,,280-136 bad 10 kva xfr,,need 25kva ,,,no bucket to pole, should get pickup to pole Released by crew 078S05---crew on site--replaced bad csp with 25kva conv. xfmr---volt ck good--tbl tkt comp.rmv
14843 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-04-27 04:36 | 2014-04-27 09:36 | 1 | 300 | 4638441 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE DISPATCHED AT REG START TIME 0730 TODAY.WILL BE DISPATCHED AT REG START TIME 0730 BAD CUT DOORWILL BE DISPATCHED AT REG START TIME 0730 BAD CUT DOOR CHG OUT CUT OUT POWER THERE IS ONLY ONE CUST ON THIS TRANS, OTHER 3 ON PL,286-215//MD FILED ON MISMAPPED PREMISES//COD 1// VER/DBM
14844 | South Williamson | 3411401 | DEWEY | INEZ | 2012-09-01 16:10 | 2012-09-01 17:50 | 3 | 100 | 4992161 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK APPEARS TO HAVE BROKEN. RE-FUSED @ 17:50. SH COD-3 ISO TF 38830671D00021 VER/HFP L3/HFP IDC XXXX
14845 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-02-21 07:30 | 2008-02-21 12:30 | 1 | 300 | 65911-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000701// BAD 25 KVA TRANSFORMER, NEEDS NEW CUT-OUT ROAD IS ICEY COME IN ON THE BIG ROCKY SIDEON POLE927-61 RELEASED BY CREW 078S09//COD 1// RELEASED BY CREW 078H03 VER/HFP IDC XXXX
14846 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-06-14 12:40 | 2010-06-14 17:40 | 1 | 300 | 63587-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TREE FELL AND TORE S/D DOWN ALSO DAMAGED XFMR CUST. WILL MAKE REPAIRS VER/KEP L3/KEP
14847 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-09-20 09:45 | 2012-09-20 10:45 | 5 | 60 | 4071491 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW OPENED RECLOSER TO SAFELY ISOLATE TROUBLE ON 4070791 AND MAKE REPAIRS COD-5 THIS WAS JUST A COUPLE OF SPANS FROM REC TO FAULT VER/KEP IDC XXXX
14848 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-03-15 01:57 | 2010-03-15 04:27 | 2 | 150 | 50057-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUTON 448-135 .. OPENED LINE FUSE ON POLE 448-130 AT 03:43 TO ISOLATE BAD CUTOUT CLOSED LINE FUSE AT 03:55... REPLACED CUTOUT RESTORED POWER AT 04:27 IDC XXXX
14849 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2014-12-02 02:05 | 2014-12-02 02:25 | 15 | 20 | 4824211 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RESTORING TICKET 4824141 VER/ARN L3/HFP HFPC FP114-217
14850 | Hazard | 3302704 | HAZARD | KENMONT | 2017-06-05 12:45 | 2017-06-05 15:15 | 2 | 150 | 4909221 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | REPAIRED COND
14851 | Hazard | 3309301 | VICCO | REDFOX | 2020-04-24 10:25 | 2020-04-24 15:25 | 1 | 300 | 4745101 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop burnt into on pole 300-79, made repairs
14852 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-10-05 19:00 | 2013-10-05 20:00 | 5 | 60 | 4913471 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE , WASNT BLOWN. VER/SEF L3/HFP IDC XXXX
14853 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-11-04 12:00 | 2013-11-04 12:50 | 6 | 50 | 4007941 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED CUT OUT POWER OFF 12:00 ON AT 12:50//COD 6// VER/DBM L3/HFP
14854 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-01-17 15:45 | 2012-01-17 16:45 | 5 | 60 | 4269941 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT//COD 5// VER/DBM IDC XXXX
14855 | Hazard | 3310502 | HADDIX | CANOE | 2010-01-14 15:20 | 2010-01-14 20:20 | 1 | 300 | 54243-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER 2 MEN BIG BUCKET//COD 1// VER/DBM IDC XXXX
14856 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-03-30 17:55 | 2019-03-30 20:25 | 2 | 150 | 4039081 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 256-139 . replaced broken cutout . closed back @ 20:25
14857 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-01-27 08:19 | 2014-01-27 10:49 | 2 | 150 | 4316061 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | CENTER PHASE FUSE//COD 2CONDUCTOR AND PIN FLOATING OUTSIDE PHASE..PIN CAME OUT OF ARM..850-49 SLAPPING OUSIDE PHASE INTO MIDDLE PHASE.STEVE HALL ON THE WAY..WILL PUT PIN BACK IN CROSSARM AND RE FUSE LINE.CONDUCTOR AND PIN FLOATING OUTSIDE PHASE..PIN CAME OUT OF ARM..850-49 SLAPPING OUSIDE PHASE INTO MIDDLE PHASE.STEVE HALL ON THE WAY..WILL PUT PIN BACK IN CROSSARM AND RE FUSE LINE.2 OTHER FUSES OFF AT..10.20.BACK ON AT 10.31(SEE ORDER 4316701) IDCC CCO, CNT1 XXXX
14858 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-05-30 09:22 | 2014-05-30 10:37 | 4 | 75 | 4953331 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BAD CUTOUT DOOR/4 CUSTOMERS OUT NOT 3 ON SAME TRANSFORMER//MADE MDC VER/CRB
14859 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-12-05 13:30 | 2010-12-05 13:45 | 20 | 15 | 63335-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER HAD TO OPEN FUSE BACK UP IN ORDER TO MAKE REPAIRS RELATED TO ORDER 63190-1//COD 20// VER/DBM IDC XXXX
14860 | Pikeville | 3410602 | E.PRESTON | LANCER | 2013-09-18 14:25 | 2013-09-18 16:55 | 2 | 150 | 4864581 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BIRNED UP ON 38830955D00113// WILL REPLACE// REPLACED// POWER IS RESTORED VER/SEF
14861 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-04-26 09:50 | 2012-04-26 10:20 | 10 | 30 | H4709631 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE ON POLE # 179-187, OPENED OTHER 2 FUSES AT 09:50 AND CLOSED ALL 3 BACK IN AT 10:20 VER/KEP
14862 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2021-05-24 10:15 | 2021-05-24 15:15 | 1 | 300 | 4614991 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva wye/delta 120/240 xfmer B-phase/truck ok, crew reqd. Released by crew 078S04 fetr 15:45all pwr restored15-15 LRM
14863 | Hazard | 3310502 | HADDIX | CANOE | 2018-12-16 12:01 | 2018-12-16 17:01 | 1 | 300 | 4571821 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on transformer L3/HFP
14864 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2015-04-24 08:12 | 2015-04-24 10:42 | 2 | 150 | 4361601 | 300 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED OFF ON TRANSF === CONNECTIONBURNED OFF ON SECONDARY SIDE REPAIRED POWER OK/ ISO 37830419B00092/ COD 2/ VER/BOW
14865 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-09-14 16:20 | 2008-09-14 16:40 | 15 | 20 | 62522-1 | 300 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3000901//TRANSFORMER RISER CONNECTION BAD-OPENED TRANSFORMER AT 16:20 TO MAKE REPAIRS// MADE TEMPOARY REPAIRS-E-MAIL TO VERNON MULLINS//VER/CRB MLR OK
14866 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-02-17 12:55 | 2010-02-17 13:45 | 6 | 50 | 58686-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NEED CREW SEND TO BILL LYNCH NEEDS RDD2 4/0 UNDER GROUND RELEASED BY CREW 078S08 WR#33906733 VER/KEP L3/KEP IDC XXXX
14867 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2010-04-05 10:45 | 2010-04-05 11:45 | 5 | 60 | 58754-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WR#34521730 POLE 45-7654 HOT BROKE ON PRI. BAD LA ALSO POLE 69-5142 CUTOUT DOOR ON FIRE REPLACED DOOR 6T TRANS. FUSE REMOVED BAD LA. REPAIRED HOT TAP//VER/CRB IDCC PN5142 XXXX
14868 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2011-04-08 21:00 | 2011-04-08 22:15 | 4 | 75 | 52261-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39503448 // CUTOUT GATE BURNED UP === REPLACE GATE == POWER OK COD-4 ISO TF 37830491000038 //VER/GAH IDC XXXX
14869 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-06-11 14:22 | 2016-06-11 19:22 | 1 | 300 | 4335451 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA TRANS. AT POLE 447-166, WILL GO GET BIG BUCKET AND CHANGE OUT. CHANGED OUT TRANS. AND CLOSED BACK IN AT 1922. COD-1 IOS TF 37830447000166 VER/HFP L3/HFP
14870 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2013-04-03 22:25 | 2013-04-03 23:15 | 6 | 50 | 4977531 | 300 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | BAD CONN APR AT 2315. OPENED XMF AT 2300 CLOSED AT 2315 CLOSE TICKET//COD 6// VER/DBM IDC XXXX
14871 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-10-05 12:30 | 2010-10-05 17:30 | 1 | 300 | 57026-1 | 300 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | PARTIAL POWER ONE HOT LEG IS OUT ON UNDERGROUND TO HOUSE...WILL HAVE TO BE DUG OUT..CALLED TIM MILLER... RELEASED BY CREW 076S01 RELEASED BY CREW 076H02PARTIAL POWER ONE HOT LEG IS OUT ON UNDERGROUND TO HOUSE...WILL HAVE TO BE DUG OUT..CALLED TIM MILLER... RELEASED BY CREW 076S01 // INSTALLED AUTO-TRANSFORMER TO RESTORE SERVICE TILL REPAIRS OR REPLACEMENT CAN BE MADE. RDM. ONLY ONE CUSTOMER HAD A PROBLEM.// ON AT 17:30 //VER/CRB IDC XXXX
14872 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-02-05 19:48 | 2012-02-05 22:18 | 2 | 150 | 4321731 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN ON XFMR POLE AFFECTING TWO CUSTOMERS. THIS WAS ONE OF THE HOT CONNECTIONS. RE-SQUEEZED AND RESTORED SERVICE @ 22:18. SH VER/SDB IDC XXXX
14873 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2016-06-05 14:30 | 2016-06-05 17:00 | 2 | 150 | 4308931 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED DOOR VER/CRB
14874 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-03-01 16:20 | 2018-03-01 18:50 | 2 | 150 | 4894341 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke replaced--allgood-ds030118
14875 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-29 21:45 | 2011-01-30 02:45 | 1 | 300 | 52141-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED 10 KVA WITH 15 KVA. VER/ARN IDC XXXX
14876 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2011-04-20 14:15 | 2011-04-20 15:05 | 6 | 50 | H61182-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED--BAD CUTOUT--NO TRUCK TOO WET RELEASED BY CREW 078S07//CREW ON SITE DIFFICULT LOCATION /// CREW OPENED TAP AT POLE 39831123C14076 AT 1415 TO REPLACE CUTOUTCREW REQUIRED--BAD CUTOUT--NO TRUCK TOO WET RELEASED BY CREW 078S07//CREW ON SITE DIFFICULT LOCATION/OPENED JUMPER PL# 1123-4076 @ 14:15 REPAIRS COMPLETE POWER RESTORED @ 15:05 J. HEMLEPP FROM 61182-1 VER/HFP L3/HFP IDC XXXX
14877 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2012-02-21 22:20 | 2012-02-21 22:30 | 30 | 10 | 4474631 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO 4418351 // OPENED RECLOSER IN ORDER TO PUT STIRRUP BACK ON AT SWITCH POLE // COD 30 // VER/DBM AJB
14878 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-11-18 03:45 | 2021-11-18 08:45 | 1 | 300 | 4103141 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines/no crew required replace fuse
14879 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2010-04-15 10:00 | 2010-04-15 12:30 | 2 | 150 | 63380-1 | 300 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SERVICE DROP HAS SHORTED OUT AT SPLICE AND BURNED 1 HOT LEG INTO. TIM HALL IS SENDING ME A PIECE OF WIRE TO FIX PROBLEM. I SPLICED SERVICE DROP.//VER/CRB IDC XXXX
14880 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-07-06 20:00 | 2013-07-06 22:30 | 2 | 150 | 4476321 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT A CUT OUT DOOR BURN UP ON POLE 38820793D00030.. GOING TO CHANGE AND GIVE IT A TRY.. CHANGED CUTOUT AND GOT TRANSFORMER BACK ON AT 22:30 //VER/GAH
14881 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2013-02-01 23:55 | 2013-02-02 00:25 | 10 | 30 | 4784501 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. VER/KEP IDCC PN391 XXXX
14882 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-06-17 14:49 | 2021-06-17 16:29 | 3 | 100 | 4764171 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | L/F open on 905-42/// Fuse had pulled apart inside cutout door causing outage. I refused and restored @16:29
14883 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-08-11 19:30 | 2014-08-11 20:00 | 10 | 30 | 4354941 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LOOKS LIKE BAD UNDERGROUND CONN. TWO HOMES NEED CREW RELEASED BY CREW 078S08//BAD SECONDARY HOT LEG///ATTEMPTING TO LOCATE, WAITING ON LOCATING EQUIP///LOCATING FAULTED CABLE//NO LUCK WITH LOCATING FAULTED SEC CABLE//IN ROUTE TO PICK UP 2 ADD-A-PHASES TO INSTALL ON HOUSES WITH FAULTED CABLE--ADD A PHS INSTALLED PWR RESTORED @ 10:42///PWR CK GOOD ON BOTH HOUSES//REYNOLDS TO FOLLOW UP ON REPAIRS TO UG// XFMR OUTAGE TIMES NOT PROVIDED BY REPAIR CREW // AJB CNT10 SEE H4354941 FOR INLT OUTAGE.
14884 | Hazard | 3302703 | HAZARD | HAZARD | 2009-02-12 07:25 | 2009-02-12 12:25 | 1 | 300 | 66293-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNED INTO AT POLE 37830296A30715 ON MIDDLE PHASE NEEDS A BIG BUCKET TO SKIN SPACER CABLE AND RE STIRRUP NEEDS CREW// RESTORED COMPLETE
14885 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-12-06 10:08 | 2009-12-06 12:38 | 2 | 150 | 61845-1 | 300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD XFMR ON POLE 447-136... REPLACED XFMR RESTORED POWER AT 12:38 COD-2 L3/HFP IDC XXXX
14886 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-06-30 16:41 | 2011-06-30 21:40 | 1 | 299 | H4442951-1 | 299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | POLE AND LINE IS ON HILL. HAVE TO PATROL ON FOOT. POLE 473-39 IS SPLIT OUT AND PRIMARY IS SAGGING VERY LOW. NEED TO DE-ENERGIZE TAP ON POLE 473-37 TO MAKE SAFE. OPENED CUT-OUT ON 473-37 AT 16:41. POWER RESTORED AT 21:40. J.S.B. RELEASED BY CREW 075H01 VER/KEP IDC XXXX
14887 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-03-13 10:01 | 2010-03-13 15:00 | 1 | 299 | 66330-1 | 299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077H12//VER/CRB IDC XXXX
14888 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-07-03 15:14 | 2021-07-03 20:13 | 1 | 299 | 4854221 | 299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200, 25kva xfmer. back yard carry in. no trk. Released by crew 078S07 Closed at 20:13. Ticket complete.
14889 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-06-17 11:16 | 2015-06-17 16:15 | 1 | 299 | 4586141 | 299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 076H04///XFMER CUTOUT BROKE ON POLE 830-143///REPLACED CUTOUT///XFMER FUSE BACK ON @ 16:15///COMPLETE BR VER/CRB
14890 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2022-12-24 12:56 | 2022-12-24 17:55 | 1 | 299 | 4346611 | 299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral and hot leg burndt into on customers service, will be making repairs. Please send a copy of this to damage claims, customer had some equipment burndt up on their home. Got repairs made and power restored @1755.
14891 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-05-06 20:01 | 2018-05-06 23:00 | 3 | 179 | 4317821 | 299 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad leg on underground. Send to bob reynolds Released by crew 078H04///unit 3345 opened transformer at 2200 and closed back at 2300
14892 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2011-04-24 07:36 | 2011-04-24 12:35 | 1 | 299 | 63397-1 | 299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMER CUTOUT/REPLACED CUTOUT-RESTORED POWER AT 12:35PM-PLEASE CLOSE TICKET/PRB IDC XXXX
14893 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-06-20 07:46 | 2011-06-20 12:45 | 1 | 299 | 4349051 | 299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD // WILL NEED TO CHANGE//CHANGED BAD CUTOUT & REFUSED//VER/CRB IDC XXXX
14894 | Pikeville | 3413402 | GARRETT | LACKEY | 2021-08-25 10:37 | 2021-08-25 15:35 | 1 | 298 | 4148371 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout on pole 37830064000218 broke//Crew required//Cutout replaced and restored @ 15:35
14895 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-08-09 23:37 | 2013-08-10 02:06 | 2 | 149 | 4642271 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT, NEED 1 MAN CUTOUT AND BIG BUCKET.------ POWER RESTORED, ONLY 2 CUST. OUT.//COD 2// VER/DBM
14896 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-06-03 08:13 | 2013-06-03 10:42 | 2 | 149 | 4213081 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830092D00960 BAD CUT-OUT ON THIS POLE CALLED FOR BACK UP PRI. ZONE POWER RESTORED KWB ///VER/CRB L/3 CRB
14897 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-03-21 22:46 | 2014-03-22 01:15 | 2 | 149 | 4517211 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT.CHGING CUTOUT. //VER/GAH
14898 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-13 08:01 | 2018-02-13 10:30 | 2 | 149 | 4836431 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//repairs made//restored at 10:30//complete//em/ ISO 38820721B00002/ cOD 2
14899 | Pikeville | 3408103 | SALISBURY | MARTIN | 2019-03-18 08:53 | 2019-03-18 11:22 | 2 | 149 | 4996111 | 298 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | One fuse blown on XFMR bank will check and refuse..Fuse link pulled apart inside cutout door.I replaced fuse and restored to full power @ 11:22 voltage and equpment checked good
14900 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-02-28 11:31 | 2022-02-28 14:00 | 2 | 149 | 4552441 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANS ON POLE 37820193A00065//Rick Ray enroute///Changed bad xfm and cutout//restored @ 14:00
14901 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2008-12-11 07:37 | 2008-12-11 12:35 | 1 | 298 | 56544-1 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3402202//BAD 25 KVA X FMR. HAVE CALLED FOR CREW RELEASED BY CREW 074S04// SENT TO WILLIE/REPLACED TRANSFORMER WR. VER/TOM L3/TOM IDC XXXX
14902 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-06-15 20:21 | 2011-06-15 22:50 | 2 | 149 | 4324681 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BURNED UP. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT DOOR.//VER/CRB
14903 | Whitesburg | 3312901 | JENKINS | KONA | 2014-06-26 22:33 | 2014-06-27 01:02 | 2 | 149 | 4160891 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNT INTO , REPLACED GATE RESTORED POWER AT 01:02 VER/ARN
14904 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-12-23 11:56 | 2018-12-23 16:54 | 1 | 298 | 4594631 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | crew required need role 1/0 wire and grips need same service grips/bring small truck to acess septic by meterbase /send to morgan Released by crew 078S03 arrived RM power on at 16:54 volatge 124,124 248 phaze to phaze volatge good on our side ,note customer has lost some applinces ,please close tic RM//SENT TO CLAIMS L3/HFP
14905 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2021-04-13 16:37 | 2021-04-13 17:50 | 10 | 73 | 4449051 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at weatherhead. repairs made.. open @ 17:25 closed 17:50
14906 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-03-10 14:35 | 2011-03-10 17:04 | 2 | 149 | 52961-1 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN AND HAS DEAD-END POLE BURNT THREE-FOURTHS OF THE WAY IN TWO. CREW ENROUTE TO ASSIST - DIFFICULT LOCATION. INSTALLED DOUBLE ARMS AND REPLACED CUTOUT. RESTORED @ 17:04. SH TAKE OFF POLE 857-249 TAP AND CUST ACCT. NOT MAPPED 2 SPAN TAP COD-2, TECH NEEDS TO GO TO FIELD AND FILE MD VER/KEP IDC XXXX
14907 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-03-27 16:33 | 2016-03-27 19:02 | 2 | 149 | 4885371 | 298 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN. AT WEATHER HEAD , REPLACED CONN. ONLY 1 CUST. AFFECTED ./ ISO 38831065000015/ COD 1/ VER/BOW
14908 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-01-25 04:23 | 2015-01-25 09:21 | 1 | 298 | 4962071 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE ON FIRE PER 911 DISPATCH//CALLBACK NUMBER 606-435-6069//FD ENROUTE /STS/4 / 0 SERVICE BURNED INTO WERE SPLICE WAS, NEED 75 FEET SERVICE AND CREW OPEN TRANSFORMER 0809 AND CLOSED AT 0921//STEVE SAID ORIGINAL 1 OUT UNTIL HE OPENED//FIX IT IN HOIS// VER/ ADH
14909 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-02-17 12:02 | 2009-02-17 17:00 | 1 | 298 | 63190-1 | 298 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP HAVE NOT FOUND IT YET, HAVE A VERY BAD LEANING SECONDARY POLE, BEHIND HOUSE TO BAD TO CLIMB, CALL FOR KEVIN BROWN TO COME AND HELP ME, TRANSFORMER OUTAGE IN ORDER 63354-1HAVE NOT FOUND IT YET, HAVE A VERY BAD LEANING SECONDARY POLE, BEHIND HOUSE TO BAD TO CLIMB, CALL FOR KEVIN BROWN TO COME AND HELP ME, FOUND BAD SERVE END, HAVE REPLACED, EVERTHING IS FINE HERE, NOW, NEED TO SEND A COPY OF THIS TO STEVE MARTIN, SECONDARY I L3/HFP
14910 | Hazard | 3309003 | JEFF | VIPER | 2021-01-19 12:06 | 2021-01-19 14:35 | 2 | 149 | 4877371 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | wire pulled out of sleeve will open up line to make repairs at 416;110 will lift clamps at pole 37830417000163//OFF @ 1345 rentregized at 14:35
14911 | South Williamson | 3411401 | DEWEY | INEZ | 2011-06-05 15:46 | 2011-06-05 18:15 | 2 | 149 | 4237181 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FAULT IN SERVICE DROP CAUSED XFMER FUSE @ 744-277 TO BLOW///MAKING REPAIRS///BR///REPAIRS MADE///RESTORED POWER @ 18:15///COMPLETE///BR//VER/CRB IDC XXXX
14912 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-02-27 12:44 | 2011-02-27 15:13 | 2 | 149 | 63457-1 | 298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLING CREW-BAD 25KVA TRANSFORMER--NEED NEW CUTOUT--MATERIAL HANDLER OK-SEND TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE/FETR1545/VEM/POWER RESTORED ALL CUST 1513/PLEASE CLOSE TICKET/THANKS/VEM VER/TOM IDC XXXX
14913 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-11-05 12:46 | 2014-11-05 14:25 | 3 | 99 | 4701891 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 162-251 40T MELTED OUT SEND NOTE TO ENG, TO CK. LOAD FUSE MIT BE TO SMALL//COD 3//EMAILED STEVE MARTIN/ADH// VER/ ADH
14914 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2018-10-21 14:25 | 2018-10-21 19:22 | 1 | 297 | 4302881 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot line clamp to line cutout at Iso pole 377-28 looks like it has been lifted off of the stirrup, or it was not fastened down good. Possibility hot line clamp failed and needs replaced. Inspected circiut and found no problems. Need a line servicer to connect hot line clamp to stirrup to energize line. It is not truck accessible.--replaced-in at 19:22-allgood-dsdm102118/ ISO 38830377000028/ COD 1 L3/HFP
14915 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-08-22 17:06 | 2009-08-22 18:45 | 3 | 99 | 60810-1 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-3 BROKEN CUTOUT REPLACED MOVED 1 CUST THAT WAS MISMAPPED VER/KEP L3/KEP IDC XXXX
14916 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2017-01-04 09:23 | 2017-01-04 14:20 | 1 | 297 | 4267801 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON P 901-5032 SPOKE WITH BLR GOING TO CHANGE WHEN DONE ON BUCK HOLLOW 15 KVA RELEASED BY CREW 078H06 VER/CRB L3/HFP XXXHFP
14917 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-05-26 13:21 | 2016-05-26 15:00 | 3 | 99 | 4261931 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED A BAD SPLICE ON ONE LEG OF THE SERVICE DROP. THE CUSTOMER HAD FULL POWER UNTIL I PULLED THE KWH METER AT 15:00. VER/AWD
14918 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-05-11 15:09 | 2015-05-11 16:48 | 3 | 99 | 4411791 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV C/O TRK OK, LINE CREW RELEASED BY CREW 078S07 VER/CRB
14919 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-06-26 17:43 | 2016-06-26 22:40 | 1 | 297 | 4479941 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 19.9 KV NO TRUCK ACCESS. NEED 4 MEN AND TRANSFORMER
14920 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2009-08-09 13:06 | 2009-08-09 13:39 | 9 | 33 | 66045-1 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLEW UP ON XFMR POLE 738-228. CUTOUT IS ALSO SMOKING. LIFTED HOT LINE CLAMP ON POLE 38830738A00078 TO ISOLATE AT 13:06.// CHANGED CUTOUT AND ARRESTER. RESTORED AT 13:30. SH//ISO //COD 9// VER/DBM IDC XXXX
14921 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2021-09-08 19:48 | 2021-09-09 00:45 | 1 | 297 | 4223371 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva Released by crew 078S07 crew on site FETR 01:00 LRM all pwr restored 00:45
14922 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-03-03 09:46 | 2022-03-03 11:25 | 3 | 99 | 4562591 | 297 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at pole power restored 11:25
14923 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-07-11 09:51 | 2016-07-11 11:30 | 3 | 99 | 4608331 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN.CHANGING..CUTOUT BAD ALSO../ ISO 38830930B00047/ COD 3/ VER/BOW
14924 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2021-04-20 15:17 | 2021-04-20 15:50 | 9 | 33 | 4464351 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Found connection on transformer pole that had been hot, T-bracket on pole 449A-234 bent to pole when tried to open, Opened line fuse on pole 449A-33 to make repairs. Line fuse open at 15:17 (no outage till line fuse was opened) 9 COD -- closed at 15:50
14925 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-05-14 20:19 | 2022-05-15 01:16 | 1 | 297 | 4891461 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans fuse open on pole 335-D-99,Have a Bad Trans will need Line crew and 7200 25 KVA Trans to make repairs,(MANUAL)..Restored at 01:16.
14926 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2022-11-29 04:57 | 2022-11-29 09:54 | 1 | 297 | 4199801 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o crew req-ds1129222 Released by crew 078S01 Repairs made, closed xfmr on 214-15 at 09:54. Ticket complete.
14927 | Hazard | 3302703 | HAZARD | HAZARD | 2013-10-29 09:58 | 2013-10-29 10:25 | 11 | 27 | 4971911 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO OUTAGE UNTIL SERVICER OPENED XFRMR TO REWORK CONNECTIONS AT 0958SERVICE BURNT DOWN AT POLE 37830296A30771, REMADE CONNECTIONS AT POLE . OPENED TRANSFORMER ON POLE 37830296A30772 AT 10:00, CLOSED AT 10:25. POWER RESTORED. VER/CRB L/3 CRB IDC XXXX
14928 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2011-01-22 07:19 | 2011-01-22 08:58 | 3 | 99 | 63539-1 | 297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN ,REPLACED CUTOUT RESTORED POWER AT 09:58 , ONLY THREE CUSTOMERS AFFECTED /// COD-3 ISO TF 37830449A40642 CHANGED THIS TO REFLECT FAILED EQUIPMENT- WAS CODED AS OVERLOAD BUT REPLACE CUTOUT SO I SAY EQUIPMENT FAILURE VER/HFP L3/HFP IDC XXXX
14929 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-11-03 06:12 | 2020-11-03 08:40 | 2 | 148 | 4637641 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @72-A-102, checking. Trans. fuse melted out, refused @0840.
14930 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-01-23 06:04 | 2018-01-23 11:00 | 1 | 296 | 4764891 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | serve ends connection heated up burning neutral into on service drop.#2-3 triplex.waiting for cust to come to un lock gate..30 min walk cannot carry tools and equip across swinging bridge.waiting for owner to come with the key./ opened transformer @ 100 closed @ 11/ 38830679000041/ cOD 1
14931 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-09-13 11:05 | 2018-09-13 13:33 | 2 | 148 | 4091451 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Splice broke in neutral secondery going from trans. pole 1126-A-166 to pole 1126-403, will need manual tree crew and line crew to put back up, I opened trans. @1105. Released by crew 074S05.crew made repairs and restored power @13:33
14932 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-11-11 10:26 | 2022-11-11 11:40 | 4 | 74 | 4125601 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o open on 1105-128 // broken 19.9 c/o // repaired & RESTORED @ 11:40
14933 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2016-04-20 08:46 | 2016-04-20 13:42 | 1 | 296 | 4106741 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE BAD REPLACED WITH 80 FT. 2/3/ ISO 38830069A31146/ COD 1/ 1342/ VER/BOW
14934 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-12-01 10:34 | 2021-12-01 15:30 | 1 | 296 | 4137501 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Trans fuse open on 480 Bank at pole 74-119,Pole is up Hill going to Try and refuse and restore service.Got fuse in but found Hot leg into in secondary going to pole74-C3-250,Will have to let secondary down to splice,Will have to open Bank back up..Open @ 13:51 and restored at 15:30..
14935 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-06-04 07:44 | 2010-06-04 12:40 | 1 | 296 | 56355-1 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 35417500 //FOUND BAD LOOP INSULATORON POLE 37820098B00725 COD-1 VER/HFP L3/HFP IDC XXXX
14936 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-05-01 10:19 | 2011-05-01 15:15 | 1 | 296 | 53148-1 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN -- BAD 10 KVA 19.9 TRANSFORMER. MANUAL. RELEASED BY CREW 077S04// WR# 39772086 //...VINES ON POLE BLEW FUSE... ALL POWER RESTORED @ 15:15//COD 1// VER/DBM IDC XXXX
14937 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-07-31 18:51 | 2015-07-31 20:05 | 4 | 74 | 4964831 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER CUTOUT ON POLE 878-39 IS BROKE///MAKING REPAIRS///CHANGED CUTOUT AND CLOSED XFMER IN AT 20:05///COMPLETE BR/ ISO 38830878000039/ COD 4/ VER/BOW
14938 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-06-13 15:49 | 2013-06-13 20:45 | 1 | 296 | 4300301 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 184A/142 SQUARE BOTTOM CUTOUT NO TRUCKS TO POLE, HOT TAP IS LIFTED. RELEASED BY CREW 078M03 VER/CRB L/3 CRB IDC XXXX
14939 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-11-27 10:05 | 2010-11-27 15:01 | 1 | 296 | 60071-1 | 296 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST HAD PART POWER/BAD SERVICE CONNECTIONS AT XFMR/REPAIRS MADE/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
14940 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-11-16 09:17 | 2015-11-16 11:45 | 2 | 148 | 4450741 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT/ ISO 37840576000046/ COD 2/ VER/BOW
14941 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2017-06-08 17:19 | 2017-06-08 19:47 | 2 | 148 | 4924691 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S07---BAD 7200 25KVA TRAN--CREW REQ--DS060817 RELEASED BY CREW 078S01/CREW ON SITE/FETR 2015/VEM/REPAIRS MADE AND ALL CUST RESTORED 1947/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
14942 | Pikeville | 3402002 | KEYSER | STONECOAL | 2018-06-22 10:20 | 2018-06-22 11:34 | 4 | 74 | 4643251 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-4 ISO TF 38821129B00094
14943 | Pikeville | 3421001 | BREAKS | CITY | 2012-03-09 17:34 | 2012-03-09 22:30 | 1 | 296 | 4567841 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER ENROUTE COD-1 ISO TF 37820220B00199 VER/HFP L3/HFP IDC XXXX
14944 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-01-17 16:02 | 2022-01-17 18:30 | 2 | 148 | 4375381 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on service pole//also burnt up lug in meterbase//i had parts//meterbase repaired and connection repaired//restored at 18:30//complete//em
14945 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-04-26 19:30 | 2015-04-26 20:07 | 8 | 37 | H4367791 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP XFMR. CAN TRUCK - NEED 25 KVA XFMR, CUTOUT AND FIBERGLASS BRACKET. CREW ENROUTE TO REPLACE./ ISO 38830882D00086/ COD 4/ SIDE TAPS 1930 TO 2007/ ORIGINAL TRANSFORMER 2014 / DUP OF 4367791 FOR SIDE TAPS TO ALLOW CREW TO REPLACE XFMR VER/HFP L3/HFP
14946 | South Williamson | 3411401 | DEWEY | INEZ | 2022-03-30 22:17 | 2022-03-31 00:45 | 2 | 148 | 4694981 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//replaced cutout//restored at 00:45//complete//em
14947 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-03-22 09:59 | 2008-03-22 14:55 | 1 | 296 | 59873-1 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT AND LIGHTNING ARRESTER WILL NEED TO BE REPLACED / T. GOBLE ENROUTE TO ASSIST / GXJ......ALL WORK COMPLETE / GXJ VER/HPF IDC XXXX
14948 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-12-18 14:11 | 2010-12-18 16:39 | 2 | 148 | 54073-1 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT AND BRKT . POLE CHARRED A LITTLE BUT OK , RESTORED POWER AT 1639 JKC &PEH//VER/CRB IDC XXXX
14949 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-01-29 12:31 | 2015-01-29 13:45 | 4 | 74 | 4972991 | 296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKE. OPERATED XFMR CUTOUT EARLIER TO REPLACE CONNECTION AND IT MAY HAVE WEAKEND FUSE. CHECKED ALL SECONDARY AND RESTORED @ 13:45. SH// COD 4// VER/ ADH L3/HFP
14950 | Whitesburg | 3312901 | JENKINS | KONA | 2022-11-27 12:10 | 2022-11-27 17:05 | 1 | 295 | 4185131 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout - need 12 kv cutout and t-brkt, big bucket Released by crew 077E10. Repairs made. Restored at 17:05.
14951 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-06-21 16:32 | 2018-06-21 21:27 | 1 | 295 | 4636631 | 295 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o on 21-2050, please replace other 2, trk to pole Released by crew 078S07 // cod 1//iso 38830021B12050//MD FILED
14952 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-05-30 12:55 | 2010-05-30 17:50 | 1 | 295 | 53597-1 | 295 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV WIRE BURNED INTO ONE HOT LEG AND NUT VER/KEP L3/KEP IDC XXXX
14953 | Whitesburg | 3401301 | FLEMING | NEON | 2011-12-26 21:01 | 2011-12-26 22:00 | 5 | 59 | 4203311 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE VER/PDP IDC XXXX
14954 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-01-20 05:05 | 2018-01-20 10:00 | 1 | 295 | 4758271 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse out, broke cutout , power restored
14955 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2017-09-28 10:42 | 2017-09-28 15:37 | 1 | 295 | 4396581 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CALLED CUSTOMER NO ANSWER--2 FEEDS OF 4/0 UG--ONE 120/120 THE OTHER 120/45--CON AT TRAN LOOK GOOD--NEED AUTOTRANS INSTALLED TILL UG CAN BE REPAIRED .KARENS PLACE JUST BEFORE THE LAKE--CREW REQ-DS092817 RELEASED BY CREW 078S01.. CREW ON SITE. COMPLTED AT 1537 PLEASE CLOSE THANKS TRE/ ISO 38830452000138/ COD 1/ VER/BOW
14956 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-08-02 08:32 | 2014-08-02 13:27 | 1 | 295 | 4319011 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 KV CUTOUT . REPLACED CUTOUT DOOR, ALL WORK COMPLETE / GXJ VER/CRB
14957 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-01-31 13:25 | 2008-01-31 18:20 | 1 | 295 | 62784-1 | 295 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT INTO//3310501//NEUTRAL//VER/CRB IDC XXXX
14958 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-03-13 21:01 | 2018-03-13 22:00 | 5 | 59 | 4013161 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE MELTED OUT REFUSED XFMR
14959 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-07 14:41 | 2008-03-07 15:40 | 5 | 59 | 54661-1 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308401// BAD CONNECTIONS ON XFMR POLE, SECONDARY LEAD BURNT OFF VER/HFP IDC XXXX
14960 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2014-01-07 22:16 | 2014-01-07 23:15 | 5 | 59 | 4256501 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE COD-5 ISO TF 38821064B00235 VER/HFP L3/HFP IDC XXXX
14961 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-03-19 21:13 | 2021-03-20 02:08 | 1 | 295 | 4356721 | 295 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | a phase fuse out on bank pole 3883-1074-C0-0718, will refuse, refused XFM and fuse stayed in still no voltage// bad 25kva 7200, 277/480// meter display is not working and will need to be replaced by meter electrician, meter # 436009518
14962 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-06-02 19:51 | 2008-06-02 20:50 | 5 | 59 | 54703-1 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED BAD ARRESTOR//3000102//VER/CRB IDC XXXX
14963 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-01-26 10:35 | 2015-01-26 15:30 | 1 | 295 | 4964771 | 295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT OFF POLE @ 326-53 NO TRUCK NEED LINE CREW TO REPLACE,OPEN SWITCH @ 326-11 @ 1120 CLOSED SWITCH @ 11:56/ ISOLATED GROUNDED AND TAGGED TO DDC AT POLE 38830326000120/ RELEASED BY CREW .. CREW ON SIGHT MAKING REPAIRS FETR 15:30 078S05.. OPENED XFMR ON 326-120 AT 15:20 BACK ON AT 15:30.. SOLID BLADE ON POLE 326-120 RESTORED AT 15:30 // SEE DUP H4964771 & HA4964771FOR ADD OUTAGE - PER SERVICER ONLY 1 CUST INITALLY OFF //VER/HFP L3/HFP AJB TOF1030 PER CUST CALLS.
14964 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-09-01 18:07 | 2011-09-01 19:45 | 3 | 98 | 4782401 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE CKING TROUBLE///TRANSFORMER FUSE BROKE , VER/KEP IDC XXXX
14965 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-10-15 12:33 | 2020-10-15 15:00 | 2 | 147 | 4558531 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | secondary connection on xfm pole burnt into. opened xfm from14:45 to 15:00 to make repaires. The 1st call came in at 12:33 for Part outage then the xfm was opened at 14:45
14966 | Hazard | 3309302 | VICCO | JEFF | 2016-12-26 15:37 | 2016-12-26 18:04 | 2 | 147 | 4238691 | 294 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE IN BROKE PER SERVICER VER/CRB
14967 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-06-11 11:12 | 2020-06-11 16:06 | 1 | 294 | 4004391 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. open @1138-D-43, checking. Fuse had melted out , refused @1606.
14968 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-09-08 21:08 | 2019-09-08 23:35 | 2 | 147 | 4993891 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout @37820001000052, checking. Bad cutout on side of the hill, will be cutting path and changing out. Got cutout replaced and closed back in @2335.
14969 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-01-24 07:43 | 2014-01-24 12:37 | 1 | 294 | 4306581 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ON SITE NO VOLTAGE AT METER BASE CHECKING UNDER-GROUND FOR VOLTAGE BAD UNDERGROUND CREW REQ,1/0UNDER GROUND NO,2 NEU WATER AND SEWER IN SAME DITCH CALL CUST, BEFORE WORKING RELEASED BY CREW 078S09/CREW TO INSTALL TEMP OVERHEAD/PLEASE COPY TICKET TO B REYNOLDS AND L RAYBURN FOR U/G REPAIR OR REPLACE/FETR1300/VEM/ONLY ONE CUST AFFECTED/POWER RESTORED 1237/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP L3/HFP
14970 | Whitesburg | 3314401 | MAYKING | ERMINE | 2014-01-03 11:37 | 2014-01-03 11:43 | 49 | 6 | 4224241 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CREW FOUND CONDUCTOR OFF INSULATOR OPENED RECLOSER AT 1137 CLOSED IT AT 1143 VER/CRB IDCC CCSCO XXXX
14971 | Pikeville | 3402002 | KEYSER | STONECOAL | 2020-10-29 09:52 | 2020-10-29 11:30 | 3 | 98 | 4595501 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @1128-44, checking. Bad trans. cutout @1128-97, will be changing out. Got cutout changed out,closed L/F back in @1130.
14972 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-02-20 17:22 | 2021-02-20 19:00 | 3 | 98 | 4197681 | 294 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | red to red froze out// will open xfmr to repair hot lead// piwer restored
14973 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2019-05-28 19:40 | 2019-05-28 21:18 | 3 | 98 | 4357211 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout busted on pole 24-C-1649, will be making repairs. Got cutout replaced and closed back in @2118.
14974 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-12-11 09:43 | 2013-12-11 11:21 | 3 | 98 | 4151521 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ALL THREE FUSES BLOWN ON BANK, NO THREE PHASE CUST ON BANK. GOING TO GET BANK TO SINGLE PHASE AND SHOOT TRANSFORMER, IF TRANDFORMER IS GOOD GOING TO LEAVE SINGLE TRANSFORMER AND GET CUST ON VER/SEF L3/HFP
14975 | South Williamson | 3411401 | DEWEY | INEZ | 2013-08-11 07:52 | 2013-08-11 09:30 | 3 | 98 | 4649021 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 744-214//GOING TO CLIMB AND CHANGE//REPAIRS MADE//RESTORED AT 9:30//COMPLETE//EM CC 3. VER/SDB
14976 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-02-26 13:41 | 2008-02-26 15:19 | 3 | 98 | 50571-1 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3116703//FOUND BAD L/A ON POLE 1123-6514 CLEARED UP OPEN WIRE SEC BEING UP BY TREES CLEARED UP,// VER/TOM IDC XXXX
14977 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2018-07-21 15:56 | 2018-07-21 20:50 | 1 | 294 | 4828771 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 38830247000096 no trucks/ making repairs/cutout replaced & xfmer on 274-96 restored @ 2050/ please close ticket/ MLH/ ISO 38830247000096/ COD 1
14978 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-06-16 20:51 | 2021-06-16 23:18 | 2 | 147 | 4761181 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 12 kv cutout no truck crew required Released by crew 078S11,repairs made all cust restored @ 2318 please close ticket thanks.bt
14979 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-03-10 16:09 | 2011-03-10 21:03 | 1 | 294 | 53075-1 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL HAVE TO REPLACE 10 KVA CSP TRANSFORMER 7200. LIFT HOT TAP ON POLE 1150-171 AND OPEN SERVICE 1150-301/302 AT 20:06 (SEE H53075-1)//COD 1// VER/DBM IDC CALLED OUT CREW XXXX
14980 | Hazard | 3309301 | VICCO | REDFOX | 2009-05-14 20:00 | 2009-05-14 20:42 | 7 | 42 | 55864-1 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, SAVING POLE, POWER RESTORED VER/TOM L3/TOM IDCC TOF1931, ESTIMATING TIME OFF XXXX
14981 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2020-05-22 14:56 | 2020-05-22 16:34 | 3 | 98 | 4888051 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATER ON POLE 37830343C00007 BLEW L/F ON POLE 37830343C00006//COD 3//Released by crew 077S03
14982 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-10-08 16:24 | 2014-10-08 18:51 | 2 | 147 | 4575661 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ POLE 272-174 BURNT TOP OF POLE OFF NEED LINE CREW TO REPLACE// ISOLATED TAGGED TO DDC AT 272-104// ONLY ONE FUSE ON POLE 38830272000104 FEEDING BOTH WAYS BROKE CUTOUT @ POLE 272-174 BURNT TOP OF POLE OFF NEED LINE CREW TO REPLACE,ISO TAG TO DDC & GROUNDED @ POLE 272-104,LINE FUSE IN @ 1851 ALL CUST RESTORED RELEASED BY CREW 078S05.REPLACED POLE 40 CLASS 5,,,NO INTERRUPTION RELEASED BY CREW 078H03 VER/ARN
14983 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2021-05-03 16:56 | 2021-05-03 17:45 | 6 | 49 | 4518091 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Riser burnt out of HT, repaired, and 65T restored @ 17:45
14984 | Pikeville | 3308404 | BECKHAM | PIPPA PASSES | 2022-07-21 11:33 | 2022-07-21 14:00 | 2 | 147 | 4542201 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke xfm cutout..//Replaced 7200 cutout and bracket.//Restored @ 14:00
14985 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2017-08-09 20:30 | 2017-08-09 21:12 | 7 | 42 | 4245031 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN TRANSFORMER UP AT 20:30 DUE TO BAD CUTOUT. REPLACED CUTOUT CLOSED TRANSFORMER BACK IN AT 21:12/ NO OUTAGE TILL XFORMER OPEN VER/KEP
14986 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-06-18 07:29 | 2009-06-18 12:23 | 1 | 294 | 53383-1 | 294 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL CONDUCTOR BROKE ON SERVICE DROP// VER/DBM IDC XXXX
14987 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-03-31 15:18 | 2015-03-31 20:12 | 1 | 294 | 4249051 | 294 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE HOT WIRE OF THE OPEN WIRE SECONDARY HAS BROKEN AND IS ON GROUND BETWEEN POLES 825-09 AND 825-44///I OPENED XFMER ON POLE 825-09 @ 16:15 TO MAKE SAFE///WIRE IS CROSSING RT460///WILL NEED AWP FLAGGERS AND BIG BUCKET WITH A COUPLE MEN TO PUT UP RELEASED BY CREW 076H07// CREW ON SITE TCM/ COD-1 VER/HFP L3/HFP
14988 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2022-11-14 06:00 | 2022-11-14 08:27 | 2 | 147 | 4139491 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @72-A-194, checking. Trans. fuse melted out, refused @0827.
14989 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-08-14 02:22 | 2015-08-14 04:00 | 3 | 98 | 4133641 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK REPAIRED POWER RESTORED KWB ***CHANGE ISO POLE *** VER/SEF
14990 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-08-03 14:22 | 2018-08-03 16:00 | 3 | 98 | 4904171 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | pedestal bad changing now. repairs made back to normal/ ISO 38830811B10183/ COD 3*** map showsn no customers per crew feeds at least 3
14991 | Pikeville | 3451201 | BEEFHIDE | BEEFHIDE | 2011-05-26 10:43 | 2011-05-26 13:10 | 2 | 147 | 4172511 | 294 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | BEEFHIDE STATION TRIPPED OUT // PH 3 12KV SA FAILED // CUT SAME IN CLEAR //VER/GAH
14992 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-12-01 13:37 | 2022-12-01 15:15 | 3 | 98 | 4217931 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout changed out power restored at 15:15
14993 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2011-02-28 20:38 | 2011-02-28 23:05 | 2 | 147 | 65181-1 | 294 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER ON POLE 37830222C00091 --- POWER RESTORED. //VER/GAH IDC XXXX
14994 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-11-30 14:48 | 2019-11-30 17:15 | 2 | 147 | 4106391 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changed cutout and restored @ 1715
14995 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-02-11 07:22 | 2011-02-11 09:00 | 3 | 98 | 56086-1 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE FUSE LINK BROKE. I AM GOING TO REFUSE TRANS. I REFUSED TRANS. AND IT STAYED IN. VER/KEP IDC XXXX
14996 | Pikeville | 3413401 | GARRETT | GARRETT | 2012-03-01 20:36 | 2012-03-02 01:30 | 1 | 294 | 4528911 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3413401...SERVICE DROP HAD BURNT DOWN.GOING TO REPLACE.THIS ONLY AFFECTED ONE CUSTOMER.REPAIRS COMPLETE @ 01:30 IDC XXXX
14997 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-09-17 12:56 | 2012-09-17 17:50 | 1 | 294 | 4053661 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND CONDUCTOR FAULTED BURNING UP METER BASE; WORKING WITH ELECTRICAN TO REPLACE METER BASE (POWER RESTORED AT 17:50) ///VER/CRB L/3 CRB IDC XXXX
14998 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-09-17 17:05 | 2016-09-17 18:43 | 3 | 98 | 4901501 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED THE TRANSFORMER FUSE THAT HAD BROKE. VER/CRB
14999 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-01-17 21:03 | 2016-01-17 23:30 | 2 | 147 | 4627401 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR. VER/KEP
15000 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-04-19 19:01 | 2010-04-19 23:55 | 1 | 294 | 65287-1 | 294 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG SEND TO BOB REYNOLDS RELEASED BY CREW 078S07 //VER/GAH IDCC CCU XXXX
15001 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-05-24 13:57 | 2012-05-24 16:24 | 2 | 147 | 4827941 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE ROTTED OUT VER/KEP IDCC FP NULL XXXX
15002 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-11-22 15:15 | 2008-11-22 16:53 | 3 | 98 | 50998-1 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP STS WR# 27405654 // 10 KVA TRANS. ON POLE 165-7 IS BAD { OVERLOADED }. WE NEED TO CHANGE IT TO A 25 KVA. I WILL CALL WILLIE FOE HELP. RELEASED BY CREW 074S01STS WR# 27405654 // 10 KVA TRANS. ON POLE 165-7 IS BAD { OVERLOADED }. WE NEED TO CHANGE IT TO A 25 KVA. I WILL CALL WILLIE FOE HELP. WE CHANGED TRANSFORMER TO A 25 KVA. IDC XXXX
15003 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2014-06-13 18:11 | 2014-06-13 19:49 | 3 | 98 | 4088391 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT. CAN USE BUCKET, BUT HAVE TO FLAG TRAFFIC. POWER IS BACK ON VER/CRB
15004 | Hazard | 3309302 | VICCO | JEFF | 2019-05-13 21:15 | 2019-05-13 21:57 | 7 | 42 | 4265731 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | servicer had to open xfmr to repair service//#4 secondary got hot and burnt neutral into. replaced secondary with #2. opened xfm on pole 323-128 from 21:15 to 21:57//cod 7 L3/HFP
15005 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-05-26 16:53 | 2010-05-26 19:20 | 2 | 147 | 51150-1 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE WIRE BURNT INTO... REPAIRED WIRE RESTORED POWER AT 19:20 RELEASED BY CREW 077S11//VER/CRB IDC XXXX
15006 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-09-08 07:00 | 2010-09-08 08:38 | 3 | 98 | 64451-1 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | E MAIL TO RAYBURN--BAD ARRESTOR NEEDS REPLACED--TRUCK OK WHEN DRY VER/KEP L3/KEP IDC XXXX
15007 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-03-09 16:23 | 2011-03-09 21:17 | 1 | 294 | 52395-1 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR LEADS// VER/DBM IDC XXXX
15008 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-05-06 11:38 | 2019-05-06 14:05 | 2 | 147 | 4231411 | 294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONDUCTOR PULLED OUT OF SLEEVE @ POLE 38830901000061//
15009 | South Williamson | 3200301 | BELFRY | BELFRY | 2011-01-13 16:40 | 2011-01-13 21:33 | 1 | 293 | 61124-1 | 293 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 38434691 // UG SERVICE BAD....VERY WEAK VOLTAGE ON ONE HOT LEG.....OTHER HOT LEG & NUETRAL OK....CALLED CREW....STANDING BY FOR DECISION.....//.....DALE HAMILTON BRINGING AUTO-XFMR TO INSTALL TO GIVE CUST 120/240 POWER UNTIL ARRANGEMENTS CAN BE MADE TO REPAIR/REPLACE UG SERVICE....JRV....01/13/11 VER/HFP L3/HFP IDC XXXX
15010 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-06-13 13:52 | 2011-06-13 18:45 | 1 | 293 | 4312261 | 293 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER --- 19.9 KV ---- 120/208//VER/CRB L3/WDH IDC XXXX
15011 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-03-26 13:41 | 2011-03-26 18:34 | 1 | 293 | 59480-1 | 293 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39318502 //....XFMR FUSE OUT....DONT SEE ANY CAUSE....WILL RE-FUSE...//...BAD XFMR...NEED CREW...PLEASE SEND TO JOEY REED...// RELEASED BY CREW 080S01 COD-1 ISO TF 38820794A00251 VER/HFP L3/HFP IDC XXXX
15012 | Hazard | 3307301 | BULAN | ARY-HEINE | 2015-03-03 17:04 | 2015-03-03 21:57 | 1 | 293 | 4094961 | 293 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA . NEED 1 MAN & BIG BUCKET , 25 KVA 7200 XFMR . RELEASED BY CREW 075H04 REPLACED TRANSFORMER AND RESTORED POWER AT 2157/ ISO 37830177B00089/ COD 1/ VER/BOW L3/HFP XXX
15013 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-04-27 21:16 | 2021-04-28 02:09 | 1 | 293 | 4486911 | 293 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | spoke with customer, meter is not lit and they can see cutout door hanging down //--bad 10kva 7200 tran and needs c/o replaced also--crew req-ds042721 Released by crew 078S01 Crew on site // cod 1
15014 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-01-12 22:07 | 2015-01-12 23:20 | 4 | 73 | 4931581 | 292 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | POLE 162-32 6T FUSE BROKE//COD 4// VER/DBM L3/HFP XXX
15015 | Pikeville | 3414901 | FISHTRAP | DISTRIBUTION | 2014-12-26 09:38 | 2014-12-26 14:30 | 1 | 292 | 4885471 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE F IS OUT,WILL RE-FUSE/////ACTUALLY A SOLID BLADE CUTOUT ON 37820078000221(UN-MAPPED)BROKEN.NEED 1 MAN TO HELP,ABT 200FT BACK ON HILL.OPENED ALL 3 BLADES ON 78-221 AND ALSO CUSTS CUTOUTS AT 78-31.//////////MADE NECESSARY REPAIRS AND RESTORED//MADE MDC// VER/CRB
15016 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-12-31 16:15 | 2009-12-31 21:07 | 1 | 292 | 53553-1 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED FOR CREW TO CHG SECONDARY/BRINGING ADD A PHASE FOR TEMP FIX TILL NEXT WEEK VER/KEP L3/KEP IDCC TOF1522 BRIGHT DIM CALL, CHANGED COUNT FROM 4 XXXX
15017 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-01-31 04:43 | 2009-01-31 09:35 | 1 | 292 | 53145-1 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3401002/// ANOTHER CURRENT LIMITING FUSE FAILED, BURNING COMPLETELY UP. THERE WAS NO OTHER TROUBLE. THE CURRENT LIMITING FUSE CAUSED THE TROUBLE. THIS IS THE FIFTH ONE THAT I HAVE DEALT WITH IN THE LAST TWO WEEKS.
15018 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-02-14 04:33 | 2018-02-14 09:25 | 1 | 292 | 4839011 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-1 ISO TF 38820866B00077dispatched in accordance with late night call out guidelines///cutou broke on pole 866-77//repairs made//restored at 9:25//complete//em
15019 | Pikeville | 3401001 | ELWOOD | DORTON | 2012-01-24 08:49 | 2012-01-24 11:15 | 2 | 146 | 4288561 | 292 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WATER IS OVER TOP OF CONNECTIONS IN JUNCTION BOX AND A HOT CONNECTION CORRODED INTO. I AM GOING TO OPEN TRANS. ON POLE 262-193 AND BAIL OUT THE WATER AND TRY TO SPLICE CONNECTION. I OPENED TRANS AT 10:50 AND CLOSED IT AT 11:15.//COD 1 + 1 // IDC XXXX
15020 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-12-27 10:23 | 2016-12-27 11:36 | 4 | 73 | 4238901 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 35/5 SECONDARY POLE 38821137D00438 IS ROTTEN AT THE GROUND LINE. GUY WIRE AND SECONDARY IS ALL THAT IS HOLDING THE POLE UP. SEND TO TIM HALL TO HAVE THE POLE REPLACED IN THE MORNING. RELEASED BY CREW 079S02 OPENED XFMR AT 1023 CIOSED AT 1136 VER/CRB
15021 | Pikeville | 3407101 | TOPMOST | DEMA | 2008-11-18 21:42 | 2008-11-19 02:34 | 1 | 292 | 66382-1 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3407101// 300 SPAN #6CW PRIMARY DOWN.... REPAIRED, ALL WORK COMPLETE / GXJ PRIMARY OPEN ON POLE 138-12 - CREW 1 CC VER/PDP IDC XXXX
15022 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-01-31 07:13 | 2012-01-31 12:05 | 1 | 292 | 4307221 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSF == CALLED FOR 1 MAN BIG BUCKET AND A 25 KVA TRANSF === RELEASED BY CREW 077S03BAD TRANSF == CALLED FOR 1 MAN BIG BUCKET AND A 25 KVA TRANSF === CHANGED TRANSF == POWER OK VER/KEP IDC XXXX
15023 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-10-17 15:03 | 2008-10-17 17:29 | 2 | 146 | 56620-1 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3116703//BAD 15KVA SEND TO V. MULLINSBAD 15KVA SEND TO V. MULLINS RELEASED BY CREW 078S08/CREW ON SITE/VEM/XFMR REPLACED AND POWER RESTORED 1729/PLEASE CLOSE TICKET/THANKS/VEM//COD 2 PER DANNY T//VER/CRB IDC XXXX
15024 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-10-05 15:05 | 2021-10-05 19:57 | 1 | 292 | 4320341 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 15 trucksok Released by crew 078S03---changed xfmr--volt ck good---tbl tkt comp---rmv
15025 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-07-12 11:24 | 2012-07-12 13:50 | 2 | 146 | 4696261 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAD A BAD 15 KVA SINGLE BUSHING TRANSFORMER AT THIS LOC, CREW REQ, CAN USE TRUCK IF YOU GET HERE BEFORE IT STARTS TO RAIN RELEASED BY CREW 078S06
15026 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2011-05-06 20:08 | 2011-05-06 22:34 | 2 | 146 | 4015831 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHECKING TROUBLE TOOK BAD LIGHTING ARR OFF LINE ON POLE 420-130 LINE FUSE MUST BE OUT ON POLE 420-121 WILL NEED ONE MAN AND GOOD LIGHTS TO WALK TO FUSE POWER ON 22:34//VER/CRB IDC XXXX
15027 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-08-31 21:52 | 2022-08-31 23:05 | 4 | 73 | 4824331 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp broke at 38830380000136. repairs made//iso 38830380000136 // cod 4
15028 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-05-17 05:28 | 2008-05-17 10:20 | 1 | 292 | 64997-1 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308401///BAD XFMR VER/HFP IDC XXXX
15029 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2009-06-18 08:47 | 2009-06-18 10:00 | 4 | 73 | 54000-1 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 91-85. 6T FUSE OUT. I HAVE CUTOUT CHANGED EVERYTHING OK.//COD 4//ISO 37830091D00085//MD FILED ON INCORRECT PREMISE LOCATION// VER/DBM IDC XXXX
15030 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-07-07 16:22 | 2014-07-07 21:14 | 1 | 292 | 4201311 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XMF FUSE, BAD 15 NEEDS UPGRADED TO 25KVA 7200 TRUCK OK LINECREW REQUIRED, ALSO NEED NEW 400W FLOODLIGHT REPLACED ON POLE. RELEASED BY CREW 078S11///UPGRADED BAD XFMR 15KVA TO 25KVA///REPLACED CUTOUT AND 400W FLOOD LIGHT//COD 1// VER/DBM
15031 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-11-18 19:16 | 2020-11-19 10:34 | 4 | 146 | 4706991 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Power on send to G.Combs to change 15 KVA to 25 KVA in am transformer fuse is melted out due to load // cod 2 //..open xfmr @ 10:15 hrs and close back in @ 10:34.p.hicks all power restored . On 11/19/20 opened Xfer to replace @ 1015 closed @ 1034
15032 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-03-28 06:23 | 2017-03-28 11:15 | 1 | 292 | 4590541 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.. CHANGING VER/CRB L3/HFP XXXHFP
15033 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-05-29 12:19 | 2015-05-29 14:45 | 2 | 146 | 4480041 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE. REPLACED AND RESTORED @ 14:45. SH// VER/ ADH
15034 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-02-21 16:27 | 2018-02-21 17:40 | 4 | 73 | 4869811 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout/ ISO 38830069D37124/ COD 4
15035 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-12-26 11:47 | 2009-12-26 14:13 | 2 | 146 | 66014-1 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFRMER REPLACED BAD XFRM & RESTORED POWER TO 3 CUSTOMERS AT 13:15 ON12-26-09 RELEASED BY CREW 074M02
15036 | Cannonsburg | 3001401 | LOUISA | CITY | 2018-07-07 10:04 | 2018-07-07 14:56 | 1 | 292 | 4747471 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Door willnot hold a fuse, cutout&arrester, will need replaced, may reach with big bucket not sure/// linecrew required Released by crew 078S11 // restored @ 1456
15037 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-07-27 12:57 | 2020-07-27 14:10 | 4 | 73 | 4238511 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 269-107. had xfm off from 14:00 to 14:10 to replace
15038 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-10-26 22:32 | 2014-10-26 23:45 | 4 | 73 | 4662921 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RESTORED @ 23:45. SH VER/ARN VER/DKG L3/DKGXXXX
15039 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-06-12 16:54 | 2021-06-12 19:20 | 2 | 146 | 4725741 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | dead end insolater broke on pole 38830234000059 and there are broke strans in span over road none of it is by truck. no tree crew, will need flaggers. owner says you can drive through field to fuse pole Released by crew 078H03 REPAIRS MADE T LEWIS
15040 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-06-09 13:27 | 2015-06-09 14:40 | 4 | 73 | 4544951 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 8T RESTORED 38830139C00207 VER/CRB
15041 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-09-12 10:38 | 2014-09-12 15:30 | 1 | 292 | 4493431 | 292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR & ARRESTER ON POLE 398-2363, WILL NEED LINE CREW & 15 KVA 19.9 XFMR & ARRESTER CAN USE TRUCK. RELEASED BY CREW 077S11 REPLACED 15 KVA TRANS VER/CRB
15042 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-02 17:07 | 2008-03-02 18:44 | 3 | 97 | 51983-1 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// BAD CUTOUT ON 227-73, LINE FUSE // ISO-FLT - 37830227D00073 COD 3// VER/TOM IDC XXXX
15043 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-05-27 08:58 | 2014-05-27 10:35 | 3 | 97 | 4932301 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS, CUTOUT IS BROKEN INTO. I AM GOING TO CHANGE CUTOUT. I CHANGED TRANS. CUTOUT. I ALSO LIFTED A HOT TAP FOR SAFTEY REASONS THAT SERVED 1 OTHER TRANS. I OPENED AT 10:08 AND CLOSED IT BACK IN AT 10:32. VER/CRB
15044 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-07-19 13:01 | 2018-07-19 14:38 | 3 | 97 | 4798931 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, replaced, power restored L3/HFP
15045 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-05-16 22:08 | 2011-05-16 23:45 | 3 | 97 | 4102921 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39991305 //....BURNT UP XFMR CUTOUT DOOR ON POLE 1013B206...OLDER CUTOUT...WILL HAVE TO REPLACE..//...REPLACED CUTOUT....POWER ON....JRV....05/16/11. ENTERED MD...HFP VER/HFP L3/HFP
15046 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-01-28 14:03 | 2018-01-28 15:40 | 3 | 97 | 4779381 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed on 833-170. Opened latteral to 833-13 @ 15:00 to put fire out and replace. Replaced cutout and restored @ 15:40. sh/ ISO 38830833D00170/ COD 3
15047 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-03-14 14:20 | 2009-03-14 19:11 | 1 | 291 | 58510-1 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 COD // BAD CUTOUT // VER/TOM L3/TOM IDC XXXX
15048 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-04-20 13:04 | 2020-04-20 17:55 | 1 | 291 | 4723391 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cut-out on pole 37830531A00003 has fuse open on pole 37830531A00106. Need line crew and flagging crew to make repairs. Replace all cut-outs if possible plz. Released by crew 077S06
15049 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-06-29 15:12 | 2009-06-29 20:03 | 1 | 291 | 52429-1 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD TRANS DUE TO TROUBLE LAST NIGHT CALLING DUTY SUPV RELEASED BY CREW 074H11 COD-1 ISO 38830983000066 L3/HFP IDC XXXX
15050 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-12-24 12:38 | 2012-12-24 14:15 | 3 | 97 | 4514191 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 140-71 40T CHGED 19.9 CUTOUT REMOVED INACTIVE LINE 140-351---TO 140-394//COD 3// VER/DBM
15051 | Whitesburg | 3401301 | FLEMING | NEON | 2014-12-06 23:38 | 2014-12-07 01:15 | 3 | 97 | 4843881 | 291 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE ON XFMR LEAD VER/SEF
15052 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-12-01 09:10 | 2019-12-01 10:47 | 3 | 97 | 4110701 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout//repaired and restored @ 1047//cod 3
15053 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-11-27 02:26 | 2017-11-27 04:03 | 3 | 97 | 4603291 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout, apr at 0403 close ticket
15054 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-05-29 19:01 | 2022-05-29 23:52 | 1 | 291 | 4980781 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR fuse was open on pole 230-D-70 and this XFMR exploded and the lid came off when I re-fused it. This needs a line crew with a 10KVA 19.9, truck access. // cod 1
15055 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-10-16 14:24 | 2022-10-16 19:15 | 1 | 291 | 4033131 | 291 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a Broke Neutral in service drop off pole 121-273,Going to pull Meter and make repairs..Restored at 19:15..
15056 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-03-10 15:54 | 2017-03-10 20:45 | 1 | 291 | 4546681 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830430B00004 TO 38830430B09003 NEU AND HOT LEG OF OPEN WIRE SEC DOWN (1 CUST ORIG)--OPEN TRAN 83-430B/4 AT 18:25 OPEN TRAN (3 CUST) ---TEMPREPAIRS MADE--TRAN IN AT 20:45 (4 CUST)--ALLGOOD--DS031017--WILL NEED TEC TO REPLACE OPEN WIRE W/TWIST/ ISO 38830430B00004/ COD 4/ DUPLICAT IN HOIS/ VER/BOW
15057 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-11-11 12:09 | 2020-11-11 17:00 | 1 | 291 | 4661971 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew requ,,,bad 7200 line fuse cutout @ 326-20,no trucks Released by crew 078S05
15058 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-04-19 11:13 | 2015-04-19 12:50 | 3 | 97 | 4333961 | 291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR F AND LINE F ARE OUT ON POLE 4-36,WILL PTRL///////APPEARS XFR CUTOUT FAILURE ALSO TOOK LINE F OUT,WILL REPLACE//////////REPLACED,CLOSED AND RESTORED ALL,ALL OK AFTERWARDS2+1// VER/ ADH
15059 | Pikeville | 3421002 | BREAKS | GRASSY | 2008-01-10 15:04 | 2008-01-10 16:02 | 5 | 58 | 55558-1 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3400902//CC 5//LATERAL FUSE BLOWN POLE 37820222B00016 FETR 16:30 HAVE TO WADE CREEK TO GET TO FUSE POLE// ***THIS AFFECTED VA CUSTOMERS ONLY, NO KY CUSTOMERS WERE INTERRUPTED*** VER/CKG IDC XXXX
15060 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-12-15 05:05 | 2010-12-15 07:30 | 2 | 145 | 50399-1 | 290 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSF POLE === REPAIRED CONNECTION == POWER OK COD-2 ISO TF 37830393C00100 VER/HFP L3/HFP IDCC FEC57 XXXX
15061 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-10-21 00:40 | 2018-10-21 01:09 | 10 | 29 | 4278521 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | neut leg out of sleeve on secondary, hanging low over road; opened xfmr at 0040hrs and blocking rd till servicer arrives; xfmr feeds up Beech st; servicer repaired conductor; energized xfmr at 1309hrs; ebpneut leg out of sleeve on secondary, hanging low over road; opened xfmr at 0040hrs and blocking rd till servicer arrives; xfmr feeds up Beech st; servicer repaired conductor; energized xfmr at 0109hrs; ebp Released by crew 078E02 L3/HFP
15062 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2019-03-27 13:09 | 2019-03-27 13:38 | 10 | 29 | 4030361 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER TO REPLACE BAD CONNECTIONS ON SECONDARY OFF 1309 ON 1338
15063 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-01-23 16:55 | 2017-01-23 21:45 | 1 | 290 | 4323751 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT/ ISO 37830205A00269/ COD 1/ BROKEN CUTOUT ON XFMR, OPENED LINE FUSE TO SAFELY REPLACE/ VER/BOW /// SEE 4324561 FOR FUSE OUTAGE = L3/HFP XXXHFP
15064 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-12-27 14:52 | 2015-12-27 15:50 | 5 | 58 | 4564791 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1147-4124 REPAIRED #2 AL. HOT LEG OPEN WIRE SEC. RESTORED XFMER OFF @ 15:25, ON @ 15:50/COD 10// VER/ ADH
15065 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-02-06 04:37 | 2015-02-06 07:02 | 2 | 145 | 4995191 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN WIRE SECONDARY DOWN. OPENED XFMR38830834A00576 @ 6:00 TO MAKE REPAIRS. PUT UP WIRE AND CLOSED XFMR @ 7:02. SH VER/CRB /// PER SERVICER 2 CUST ORIGINALLY OUT L3/HFP HFPC CNT1
15066 | Hazard | 3302704 | HAZARD | KENMONT | 2014-02-15 12:25 | 2014-02-15 17:15 | 1 | 290 | 4390161 | 290 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE, REPLACED CONNECTIONS VER/HFP L3/HFP
15067 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2018-08-12 18:11 | 2018-08-12 18:40 | 10 | 29 | 4944331 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | No outage until xfer fuse 38830045C14005 was open @ 1811 // 4/0 copper to copper squeezed with aluminum squeezons. Repairs made, and power restored at 18:40 L3/HFP
15068 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-06-12 17:59 | 2008-06-12 20:24 | 2 | 145 | 63375-1 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP....D LEWIS 061208 RELEASED BY CREW 074H08 VER/HFP IDC XXXX
15069 | Whitesburg | 3314401 | MAYKING | ERMINE | 2021-03-07 20:48 | 2021-03-07 21:46 | 5 | 58 | 4312381 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | failed cutout gate. changed gate out.. power restored @ 21:46 // cod 5
15070 | Hazard | 3303902 | LESLIE | WOOTON | 2010-11-09 18:13 | 2010-11-09 20:38 | 2 | 145 | 54427-1 | 290 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE WILL OPEN UP XFMR ON POLE 195. REPLACED CONNECTORS ON HOT LEADS. POWER RESTORED. COD-2 VER/HFP L3/HFP IDC XXXX
15071 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-06-07 21:10 | 2011-06-07 23:35 | 2 | 145 | 4263821 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA, 19.9 TRANSFORMER, NEED TRANSFORMER BAG COD-2 ISO TF 37830247D00924 VER/HFP L3/HFP IDC XXXX
15072 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-07-07 11:10 | 2008-07-07 13:35 | 2 | 145 | 63668-1 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3110903//BAD 15 KVA 7.200 SINGLE BUSHING 3RD TIME IN 10 DAYS IT HAS WENT OUT NEED LINE CREW TO RE-PLACE GIVE TO BILL FRALEY//COD 2//-----TAP OFF FROM 13:10 TO 13:35//ADDITIONAL 2 CUSTOMERS OUT// VER/DBM IDC XXXX
15073 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-08-23 20:00 | 2010-08-23 20:58 | 5 | 58 | 59671-1 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WIRE BROKE INTO AT TREE DROP HAS BEEN REPAIRED, STILL HAVING BAD VOLTAGE CHECK OTHER TRANSFORMERS ON SAME ST VOLTAGE NORMAL,. NEED CREW AND 50 KVA, SINGLE BUSHING 7200 120/240 VOLT TRANS FORMER RELEASED BY CREW 078S09 ALL POWER RESTORED AT 20:58//COD 5// VER/DBM IDCC TOF1518 XXXX
15074 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2016-11-17 06:20 | 2016-11-17 08:45 | 2 | 145 | 4106911 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE HAD BROKE. ONLY TWO CUSTOMERS ARE ON THIS TRANSFORMER THAT WAS OUT./ ISO 38820916B00163/ COD 2 CCC****** PER SERVICER COMMENTS/ VER/BOW
15075 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2020-12-28 08:15 | 2020-12-28 13:05 | 1 | 290 | 4829391 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 kva B phase wye delta 120/240 2 bushing can. truck ok. Released by crew 078S04/ Bphase xfmr changed out/ power restored @ 1305/ MLH
15076 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2011-06-21 15:15 | 2011-06-21 17:40 | 2 | 145 | 4364151 | 290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. REFUSE TRANSFORMER //VER/GAH IDC XXXX
15077 | South Williamson | 3411401 | DEWEY | INEZ | 2020-02-07 06:11 | 2020-02-07 11:00 | 1 | 289 | 4374221 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411401/gaj/0614/all out disp 3575 E McCoy//bad 10kva 19.9 xfmr//truck approach//crew will be heading thisway//repairs made//restored at 11:00//complete//em
15078 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2017-02-10 07:21 | 2017-02-10 12:10 | 1 | 289 | 4382431 | 289 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD HOT LEG ON URD SERVICE GOING TO 182 WALNUT DR., TIM HALL IS GETTING SOME HELP TO LOCATE THE PROBLEM.//COD 1//BAD HOT LEG ON URD SERVICE GOING TO 182 WALNUT DR., TIM HALL IS GETTING SOME HELP TO LOCATE THE PROBLEM. MADE REPAIRS AND RESTORED POWER @1210. VER/CRB L3/HFP XXXHFP
15079 | South Williamson | 3202201 | LOVELY | LOVELY | 2019-06-25 19:56 | 2019-06-26 00:45 | 1 | 289 | 4596521 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | customer mismapped///fault pole is 746-A-299///cutout broke on pole 746-a-299//need big bucket to replace cutout// Released by crew 079S01/crew on site//iso//cod 1//
15080 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-10-08 09:31 | 2008-10-08 14:20 | 1 | 289 | 54142-1 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUST TRANSFORMER POLE IS 21-2579-LINE FUSE OUT RELEASED BY CREW 078S07 ISO POLE 38830021B22610 COD-1 ENTERED MD FOR THIS CUSTOMER--HFPCUST TRANSFORMER POLE IS 21-2579-LINE FUSE OUT/ CALLING TREE CREW IDC XXXX
15081 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-03-22 10:58 | 2009-03-22 15:47 | 1 | 289 | 60669-1 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3404302//, ON SITE, XFORMER FUSE BLOWN, REFUSING IT RELEASED BY CREW 080S01 *** UPDATE 1310 , CREW COMING OUT OF PIKEVILLE TO REPLACE TR. REPLACED BAD TRANFORMER 03 22 09 TOM MCCOWN ONE OUTAGE. IDC XXXX
15082 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2020-01-17 05:26 | 2020-01-17 10:15 | 1 | 289 | 4314741 | 289 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Dispatched in accordance with KYPCo Late Night Callout Guidelines. bad serve end connection , replacing
15083 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-05-04 12:33 | 2020-05-04 17:22 | 1 | 289 | 4796921 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 30t at pole350-27 line fuse open ,,,350-101 pole burnt off ,,need 1 36 small pole topper,,,2 spans primary down 350-27 to 350-102,,,no trucks field is soft,,,could use 4 wheeler ,,,,,
15084 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-05-18 09:11 | 2009-05-18 14:00 | 1 | 289 | 61906-1 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 29866084 /// BAD TRANSF == NEED A 15 KVA TRANSF , CUTOUT , T-BRACKET == GET TRUCK TO TRANSF == RELEASED BY CREW 077S03RESTORED ALL POWER 14:00 COD-1 ISO POLE 37830369A00277 L3/HFP IDC XXXX
15085 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-03-31 14:28 | 2014-03-31 19:17 | 1 | 289 | 4548441 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED CREW NEED BIG BUCKET RELEASED BY CREW 078S08BUCKET TRUCK EN ROUTE/FETR2000/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1917/PLEASE CLOSE TICKET/THANKS/VEM COD-1 ISO PO @ 39831123C45528 VER/HFP L3/HFP
15086 | Hazard | 3420001 | SOFT SHELL | VEST | 2021-12-27 17:16 | 2021-12-27 22:05 | 1 | 289 | 4230691 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on 156A/320 send to P.Hicks Released by crew 077S03
15087 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2017-07-26 17:52 | 2017-07-26 22:41 | 1 | 289 | 4183041 | 289 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 39831147B00306 BAD UG LEG. NEED CREW AND POWER TEMP. RELEASED BY CREW 078S08--INSTALLED ADD-A-PHASE,,VOLT CK GOOD 118-118-232---TBL TKT COMP---RMV AED ENTERED. VER/AWD L3/HFP XXXHFP
15088 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-07-09 12:41 | 2022-07-09 17:30 | 1 | 289 | 4443401 | 289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout. Made repairs. Power restored at 17:30
15089 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2009-04-09 17:06 | 2009-04-09 19:30 | 2 | 144 | 50857-1 | 288 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 FUSE OUT IN BANK--BROKEN FUSE LINK COD-2 VER/KEP L3/KEP IDC XXXX
15090 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2014-01-13 14:20 | 2014-01-13 14:38 | 16 | 18 | 4278361 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REPLACING POLE HAD TO OPEN LINE FUSE UP DUE TO PRIMARY CONDUCTOR THAT WAS BROKEN // ( ONLY HAD ONE STRAND HOLDING WIRE UP) COD-16 ISO LF 37830067A00094 VER/HFP L3/HFP IDC XXXX
15091 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2013-07-09 15:08 | 2013-07-09 16:20 | 4 | 72 | 4492871 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY RISER BURNT INTO,REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT COD-4 ISO PO @ 38830206A31088 VER/HFP L3/HFP IDC XXXX
15092 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-01-09 08:12 | 2008-01-09 09:00 | 6 | 48 | 55088-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD L/A IM CUTING IN CLEAR DROP FELL ON OPEN WIRE FIRST//3116703//FOUND BAD L/A IM CUTING IN CLEAR DROP FELL ON OPEN WIRE FIRST RELEASED BY CREW 078S09)//VER/CRB IDC XXXX
15093 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-01-17 08:12 | 2009-01-17 09:00 | 6 | 48 | 57032-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3409303BAD CSP XFMR. CREW ENROUTE TO CHANGE. CLOSED XFMR AT 09:00 TO GIVE CUSTOMERS POWER TIL CREW ARRIVES. VER/KEP L3/KEP
15094 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-07-20 10:54 | 2012-07-20 15:42 | 1 | 288 | 4784221 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR BAD ON 841-42//TRUCK ACCESSIBLE IF USE MATS TO BACK TO POLE///15 KVA 19.9///CREW ENROUTE RELEASED BY CREW 079S01 COD-1 ISO TF 38820841A00042 VER/HFP L3/HFP
15095 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-04-05 12:25 | 2010-04-05 13:37 | 4 | 72 | 58816-1 | 288 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION AT XFMR COD-4 VER/HFP L3/HFP IDC XXXX
15096 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-06-03 15:42 | 2008-06-03 18:06 | 2 | 144 | 55095-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3010602/// SERVICER FOUND A BROKEN CUTOUT ON POLE 1148-6526 // ONE OF THREE OUTB-PH LINE FUSE IS BROKEN INTO ON POLE 1148-6526 GIVE TO VERNON MULLINS RELEASED BY CREW 078S09/CREW WAITING ON WEATHER TO MOVE THRU/MAY HAVE TO OPEN A AND C PHASE TO MAKE REPAIRS/VEM/FETR1845/VEM/CUTOUT REPLACED AND POWER RESTORED TO B PHASE 1806 /PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB
15097 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-12-06 09:54 | 2014-12-06 10:42 | 6 | 48 | 4839791 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 0954 / OPENED PHASE B RECLOSER AT POLE 1038-A2-444 TO REMOVE LOAD SO CREW CAB REPLACE CUT OUT AT POLE 38821038A20443. 6 CC INTERRUPTED. CLOSED B PHASE RECLOSER BACK IN AT 10:42. VER/CRB L3/HFP
15098 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2012-02-12 16:34 | 2012-02-12 18:10 | 3 | 96 | 4343051 | 288 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION///VER/CRB IDC XXXX
15099 | Pikeville | 3410602 | E.PRESTON | LANCER | 2013-03-03 06:48 | 2013-03-03 08:00 | 4 | 72 | 4867591 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT.RUSE LINK BROKE,HAVE REPLACED FUSE //VER/GAH IDC XXXX
15100 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-01-17 21:30 | 2009-01-17 22:06 | 8 | 36 | 57877-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | CREW HAD TO PULL ELBOW OFF OF PAD MOUNT TR 37830201A30423 TO REPLACE DEFECTIVE TR AT 37830201A30424 RELATED TO 57744-1 / COD-8 / VER/LDA L3/KEP
15101 | South Williamson | 3411401 | DEWEY | INEZ | 2010-08-03 17:34 | 2010-08-03 19:10 | 3 | 96 | 60930-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMER FUSE OPEN CHECKING NOW.FUSE BROKE CCC COD-3 ENTERED MD...HFP VER/HFP L3/HFP IDCC CCU XXXX
15102 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-04-06 21:06 | 2008-04-06 22:42 | 3 | 96 | 64731-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3401103...PARTIAL POWER...MAY NEED TO UPGRADE SEC...1/0 TRIPLEX 3 SERVICES OFF THIS SEC ALL ELECTRIC HEAT AND COOL..SQEEZE ON BURNED INTO..NOT A SERVE END...BB ATTEN: RON RYE. LOAD CHECK FOR POSS UPGRADE. VER/PDP IDC MCCNI, CNT1 XXXX
15103 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-06-10 10:12 | 2013-06-10 15:00 | 1 | 288 | 4250261 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR IS BAD WE NEED A 10 KVA 19.9 , CECIL SEXTONS CREW IS COMMING TO CHANGE OUT XFMR RELEASED BY CREW 077S12//COD 1// VER/DBM IDC XXXX
15104 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-03-14 19:20 | 2016-03-14 19:52 | 9 | 32 | H1242454-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | C PHASE HOT TAP RISER OPEN AT POLE 1074-15 AND LAYING ACROSS B PHASE, OPENED C PHASE LINE CUTOUT AT POLE 14 AT 17:10 (25 ORIGINAL CUST) . REPAIRS ON POLE 15 COMPLETE, ALL CUSTOMERS RESTORED @ 1952/ OPENED THE OTHER 2 LINE FUSES ON POLE 38831074D00014 @ 1920 (9 CUST) AND RESTORED THE LINE FUSES 38831074D00014 @ 1952/ ISO 38831074D00014/ COD 34/ DUPLICATE IN HOIS/ VER/BOW
15105 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2018-10-09 12:04 | 2018-10-09 12:10 | 48 | 6 | 4211621 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED OCR 38830019A00067 @ TO REPLACE BAD CUTOUT ON POLE 38830019A00079 //OPENED 1204//CLOSED 1210---tbl tkt comp RMV L3/HFP
15106 | Hazard | 3303902 | LESLIE | WOOTON | 2022-01-24 07:16 | 2022-01-24 09:40 | 2 | 144 | 4399411 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
15107 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-10-24 17:06 | 2011-10-24 19:30 | 2 | 144 | 4016711 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 1033-34. DID NOT HAVE A REPLACEMENT, BYPASSED CUTOUT. CURRENT LIMITING FUSE IS INTACT//TRANSFORMER ON A ONE POLE TAP PROTECTED BY A FUSE ALSO//EMAILED TO DENNIS MASSEY//COD 1//ISO //MD FILED ON MISSMAPPED CUST// VER/DBM IDC XXXX
15108 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2011-04-10 19:06 | 2011-04-10 21:30 | 2 | 144 | 54454-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR# 39507656 // NEED TO COME ON ON THE DYSARD HILL SIDE PER FIRE DEPT. // RELEASED BY CREW 078S08WR# 39507656 // NEED TO COME ON ON THE DYSARD HILL SIDE PER FIRE DEPT. // 4/3 SERVICE BURNT DOWN REPLACED 100FT. 4/3 WITH 100FT. 2/3 IDC XXXX
15109 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-08-30 19:09 | 2008-08-30 20:45 | 3 | 96 | 57886-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 26039850 //BAD CUTOUT. IDCC CNT1 XXXX
15110 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-07-30 14:09 | 2009-07-30 15:45 | 3 | 96 | 55547-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN LINE FUSE ON POLE 188-11 TR NO OUT ON POLE 188-A-12B REPLACED BAD LINE CUTOUT. VER/KEP L3/KEP IDC XXXX
15111 | Whitesburg | 3314401 | MAYKING | ERMINE | 2017-03-20 08:36 | 2017-03-20 11:00 | 2 | 144 | 4571371 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY BUSHINGS IN XFMR ARE BAD, CREW IS COMMING TO CHANGE. RELEASED BY CREW 077S12 REPLACED 25 KVA WITH 25 KVA POWER RESTORED AT 11:00 VER/HFP L3/HFP
15112 | Hazard | 3301401 | COMBS | COMBS | 2014-10-17 14:06 | 2014-10-17 15:18 | 4 | 72 | 4640661 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPEN1406 CLOSED AT 1518// 4 COD - MAP DISC ENTERED TO REFLECT//TOM VER/TOM L3/TOM
15113 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-09-25 14:58 | 2012-09-25 16:34 | 3 | 96 | 4086261 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE BAD 240--480V XMF IN A TWO CAN BANK, NO XMF INSTOCK WILL UPGRADE BANK 9/ 26/ 2012//CUST AGREED ///VER/CRB L/3 CRB IDC XXXX
15114 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-02-07 16:42 | 2019-02-07 21:30 | 1 | 288 | 4765021 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 19.9 xfmr//customer says we can use truck but will probably need mats or use pickup and climb pole//repairs made//restored at 21:30//complete/em
15115 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-07-19 14:47 | 2012-07-19 16:00 | 6 | 73 | 4769541 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 078S08 C PHASE ONLYPOLE 1147-456 BAD CUT/ LA CHGED 10T TRANS FUSE RECLOSER OUT 1147-4057 BACK ON 15;30 TRANS ON 16;00 VER/KEP
15116 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2012-04-18 12:42 | 2012-04-18 17:30 | 1 | 288 | 4684301 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR..ONE CUST.NEED 15KVA 7.2 KV XFMR & CUTOUT..CAN USE TRUCK.NEED CREW..// RELEASED BY CREW 080S01////VER/CRB IDC XXXX
15117 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-11-20 07:14 | 2021-11-20 08:50 | 3 | 96 | 4110311 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse melted out.. replacing 6t fuse
15118 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2020-05-04 09:40 | 2020-05-04 10:16 | 8 | 36 | 4795211 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 37830305000032 HAD TO OPEN RECL @ POLE 37830329000278 ¦¦ OPENED @ 0940 CLOSED @ 1016
15119 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-11-24 11:34 | 2020-11-24 12:10 | 8 | 36 | 4720421 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer restored FUSE BROKE
15120 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-04-06 13:21 | 2011-04-06 14:57 | 3 | 96 | 65484-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | L.A. BROKEN ON XFMR SETTING @ POLE 37830116000007. RELEASED BY CREW 280E02/// WILL HAVE TO OPEN LINE TAP UP AND TRANSFORMER TO REPLACE CUT OUT AND ARRESTOR. TOOK CUSTOMER OFF AT 13:21 BACK ON AT 14:57. TIM MCCOY RELEASED BY CREW 074H10 IDC XXXX
15121 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2008-10-03 07:54 | 2008-10-03 09:30 | 3 | 96 | 53088-1 | 288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3403002//THREE CUSTOMER HAVE SERVICE OFF THIS TRANSFORMER, FUSE BROKE//VER/CRB IDC XXXX
15122 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-03-29 10:32 | 2017-03-29 15:19 | 1 | 287 | 4594251 | 287 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | LOW VOLTAGE FROM XFMR TO METER . GOT HELP COMING TO GIVE ME A HAND . INSTALLED TEMP. XFMR . CREW GOING TO REPAIR TOMORROW . SEND TO DOUG FOR TECH. TO MAKE JOB FOR CREW . ONLY 1 CUST. VER/HFP L3/HFP
15123 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-07-22 11:32 | 2016-07-22 16:19 | 1 | 287 | 4666971 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SURGE PROTECTOR IS BAD . WILL NEED HELP POLE HAS BLDG BUILT AROUND IT. DENNIS MASSEY IS ON HIS WAY VER/AWD
15124 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-07-10 22:29 | 2008-07-11 02:00 | 2 | 211 | 51033-1 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER BAD POLE 48-1017 @ 2320 UNABLE TO REACH D/S CALLED BACKUP .. . CREW ON SITE REPLACING TRCSP TRANSFORMER BAD POLE 48-1017, LINE FUSE IN AT 23:45 ONE CUSTOMER AND STORAGE BUILDING IDCC CNT1 STP, CDC92 XXXX
15125 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-03-05 08:46 | 2010-03-05 13:33 | 1 | 287 | 63056-1 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 15 KVA TRANS. { 34.5} ON POLE 167-497 IS BAD. WILLIE IS SENDING A CREW TO CHANGE TRANS. RELEASED BY CREW 074S01 VER/KEP L3/KEP IDC XXXX
15126 | Pikeville | 3407103 | TOPMOST | KITE | 2020-03-19 16:10 | 2020-03-19 20:48 | 2 | 278 | 4493011 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6t fuse out due to bad 10kva transformer pole. crew on the way..Est time on order should be ok. i opened 40t fuse on pole 185-33 @ 18:25 closed back in @ 18;34 just had 1 cust off on pole 185-1826t fuse out due to bad 10kva transformer on pole 185-184 crew on the way..Est time on order should be ok. i opened 40t fuse on pole 185-33 @ 18:25 closed back in @ 18:34 just had 1 cust off on pole 185-182 . the way i have it fixed now i have a hot line clamp off line @ pole 185-33going to pole 185-18
15127 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-03-13 11:43 | 2008-03-13 16:30 | 1 | 287 | 56845-1 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411902// TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 10 KVA TRANS. IS BAD. TIM HALL IS GOING TO SEND A CREW TO CHANGE IT. THE CREW WILL CALL YOU WHEN THEY START THIS WAY. RELEASED BY CREW 074S01. COMPLTED RICK RAY 3-13-08//COD 1// VER/DBM IDC XXXX
15128 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2017-03-05 13:36 | 2017-03-05 18:23 | 1 | 287 | 4523531 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200, POLE 118A235, C/O & ARRESTOR. NO TRK. 6 WHEELER. RELEASED BY CREW 078S07//MADE MD TO SHOW MIS-MAPPED CUST PREM//CREW ON SITE--CHANGED XFMR AND CUTOUT--PWR RESTORED AT 18:23--TBL TKT COMP VER/CRB
15129 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2011-12-23 13:20 | 2011-12-23 18:07 | 1 | 287 | 4198961 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CUST HAS BAD UNDERGROUND, HAS 125 VOLT PHASE TO GROUND ON ONE LEG AND 75 ON THE OTHER, ALSO HAS 200 VOLTS PHASE TO PHASE, NEED CREW TO INSTALL POWER TEMP, TILL AFTER HOLIDAYS, THIS IS CEDAR SIDING HOUSE ON WILSON LANE, OFF CAROLINE RD, BEFORE YOU START OVER HILL TO CHINNS BRS, HAVE TRANSFORMER OPEN ON POLE 1122-66, JUST FEEDS THIS ONE CUST RELEASED BY CREW 078S06CUST HAS BAD UNDERGROUND, HAS 125 VOLT PHASE TO GROUND ON ONE LEG AND 75 ON THE OTHER, ALSO HAS 200 VOLTS PHS VER/HFP L3/HFP IDC XXXX
15130 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-11-06 04:28 | 2018-11-06 09:15 | 1 | 287 | 4368051 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broken on the arm on pole 24-B3-746, please send to Paul Layne to make repairs. Released by crew 074S05;;all repairs made L3/HFP
15131 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-05-15 11:58 | 2010-05-15 16:45 | 1 | 287 | 62692-1 | 287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077H01 BAD CUTOUT//COD 1// VER/DBM IDC XXXX
15132 | Pikeville | 3407101 | TOPMOST | DEMA | 2018-03-22 12:20 | 2018-03-22 14:43 | 2 | 143 | 4042511 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | refused xfmr, ALL WORK COMPLETE / GXJ
15133 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2015-09-10 08:59 | 2015-09-10 13:45 | 1 | 286 | 4222531 | 286 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VERY POOR CONNECTIONS AT MAST,WILL RE-WORK/////////REPLACED BAD CONNECTIONS AT MAST,ALL OK AFTERWARDS,ONLY 1 CUST AFFECTED NOT 2 VER/CRB
15134 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-02-01 17:28 | 2014-02-01 20:54 | 2 | 206 | 4335471 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE F OUT @ 26-9,FUSED IT AND RESTORED XFR THERE.THE XFR ACROSS ROAD ON 26-103 IS BAD.NEED MAT HANDLER,25 KVA XR,1 MAN.THE BAD XFR ON 103 MUST HAVE TAKEN FUSE OUT INITIALLY.//////REPLACED XFR AND RESTORED @ 20:54 1 CC 1848 -#2 CC 2054 VER/PDP
15135 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2016-06-26 14:41 | 2016-06-26 19:27 | 1 | 286 | 4479201 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200. NEED FOREMAN AND ONE MAN. CAN USE BIG BUCKET TO CHANGE OUT THE TRANSFORMER. POWER RESTORED AT 19:27. VER/CRB
15136 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-02-05 13:18 | 2017-02-05 15:41 | 2 | 143 | 4359661 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE DOOR HAD BURNT UP ON 38830525000165, REPLACED DOOR APR AT 1541 CLOSE TICKET . DEW VER/TOM L3/TOM
15137 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-07-22 07:07 | 2013-07-22 09:30 | 2 | 143 | 4573771 | 286 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRE 4/0 SERVICE LOOP, OPENED XFORMER ON POLE 380-195 AT 09:00 TO 09:30. IDC XXXX
15138 | Paintsville | 3401802 | INDEX | HOSPITAL | 2012-09-19 10:27 | 2012-09-19 12:50 | 2 | 143 | 4068091 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SECONDARY BURNED DOWN 654-169 TO 654-342.DUE TO BAD SERVE END.HEATED UP BURNING DOWN 2-3 TRIPLEX SECONDARY.CHGING OUT SECONDARY .. VER/KEP IDC XXXX
15139 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-01-25 21:34 | 2019-01-26 02:20 | 1 | 286 | 4723271 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required need 15 kva new riseer and cutout chg also trucks ok/need transformer bag also Released by crew 078S03//cod 1
15140 | Pikeville | 3120102 | STANVILLE | TRAM | 2021-09-08 11:47 | 2021-09-08 14:10 | 2 | 143 | 4221111 | 286 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | trees have rubbed service drop in 2, will have to open XFM on 1077-D-598 to make repairs, will keep up with times// opened XFM @ 13:46 closed @ 14:10// ROW needs cut from pole 1077-D-598 to pole 1077-D-599// email sent to corey farmer
15141 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-07-30 21:08 | 2008-07-31 01:54 | 1 | 286 | 62452-1 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK FOR PROBLEMSBAD XFR,NEED MATERIAL HANDLER AND CREW//3411801 / COD-1 VER/LDA IDC XXXX
15142 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-05-25 12:37 | 2022-05-25 15:00 | 2 | 143 | 4947421 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout (7200) broke on pole38830983000077 ..repaired.restored.
15143 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2015-03-13 11:42 | 2015-03-13 14:05 | 2 | 143 | 4190071 | 286 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLIT BOLT CLAMP BAD.REPLACED WITH SQUEEZON./ ISO 38831047000092/ COD 2
15144 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-12-25 06:29 | 2017-12-25 10:25 | 2 | 236 | 4675711 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | UG riser fuse cutout on 906-98 failed. Open line fuse 905-106 @ 8:15 to isolate. Closed line fuse @ 9:05 but original outaged cust still has no power. Checking padmount xfmr fuse. Padmount fuse melted out. Restored xfmr 906-99 @ 10:25. sh Released by crew 076S02
15145 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-01-24 08:27 | 2014-01-24 10:50 | 2 | 143 | 4306981 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER,, CREW ON SITE, REPLACED OVERLOADED 15KVA WITH A 25KVA,, ALL POWER RESTORED COD-2 ISO TF 39831047000090 VER/HFP L3/HFP
15146 | Cannonsburg | 3001401 | LOUISA | CITY | 2020-06-22 12:43 | 2020-06-22 15:06 | 2 | 143 | 4059521 | 286 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | made rpairs to service neutral, power restored
15147 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-09-26 10:21 | 2009-09-26 12:44 | 2 | 143 | 63665-1 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND TREE LAYING ON OPEN WIRE SECONDARY, I HAVE IT REMOVED, AND ALSO HAD A BAD CUTOUT ON POLE 1098-B2-0216, I HAVE IT CHANGED AND POWER IS RESTORED AT THIS LOC VER/KEP L3/KEP IDC XXXX
15148 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-07-04 06:57 | 2008-07-04 23:33 | 2 | 996 | 61990-1 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003701//POLE FIRE ON 38830186000090, ISOLATED AT 186-88, NEED CREW, 40-4 POLE 7200 CUTOUT, TRUCK OK, DRIVEWAY AT 2426 RT 1654, LINE FUSE RESTORED AT 09:20 RELEASED BY CREW 078S05 UPDATED FETR DUE TO OTHER TROUBLE IN AREA VER/ARN IDC XXXX
15149 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-02-15 04:59 | 2008-02-15 09:45 | 1 | 286 | 63390-1 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000301// 4/3 SERVICE BURNT DOWN VER/HFP IDCC PN4557 XXXX
15150 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-08-17 09:42 | 2017-08-17 14:28 | 1 | 286 | 4270841 | 286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BROKEN ON POLE 38830184C20428 COD-1 ISO PO @ 38830184C20428 VER/HFP L3/HFP SJGC PN (ADDED)
15151 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-08-19 17:23 | 2018-08-19 19:28 | 6 | 125 | 4974291 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 service drop burnt down opened xfmr at 18:56 closed back at 19:28 L3/HFP
15152 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-01-16 08:09 | 2012-01-16 09:44 | 3 | 95 | 4263731 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HOT TAP LEAD BUNRT INTO, REPLACE HOT TAP ///VER/CRB IDC XXXX
15153 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-09-01 12:52 | 2009-09-01 17:37 | 1 | 285 | 59221-1 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED XFMR ON AT 17:37 D SAMMONS//COD 1// VER/DBM IDC XXXX
15154 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2019-10-23 14:55 | 2019-10-23 15:52 | 5 | 57 | 4188571 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50kva 7200 trans. on pole 24-B2-655, secondary bushing has broke on it, will need line crew to make repairs. Changed out 50kva, power restored @1552, opened it up @1455.
15155 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-05-17 17:00 | 2012-05-17 18:35 | 3 | 95 | 4803981 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER OFF 17:00 ON18:35 ///VER/CRB L/3 CRB IDC XXXX
15156 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2020-05-22 08:55 | 2020-05-22 10:20 | 9 | 85 | 4885341 | 285 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | made repairs to secondery connections. power restored at 1020//opened trans 0955
15157 | Hazard | 3309002 | JEFF | JEFF | 2014-11-21 09:45 | 2014-11-21 14:30 | 1 | 285 | 4751101 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT & ARRESTER ON POLE 298-88, WILL NEED CREW MANUEL POLE ON HILLSIDE. RELEASED BY CREW 077S11 REPLACED CUTOUT BKT. AND ARR. POWER RESTOREDAT 14 30// COD 1//VER/ ADH
15158 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-03-29 16:20 | 2010-03-29 17:55 | 3 | 95 | 55707-1 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OPEN ON POLE 727-30 (NOT ON MAP)//TOP OF POLE 727-78 BURNT OFF // FAILED CUTOUT// SERVICER DOWN FRAMING POLE HIMSELF //COD 3//ISO 38830727000030 // MD FILED DBM // VER/DBM AJB
15159 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-11-24 15:23 | 2014-11-24 20:08 | 1 | 285 | 4776191 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SER. DROP BURN UP REPLACED 75FT WITH 2/3 SER POWER RESTORED 20:08// ISO 38830377000084/ COD 1/ VER/BOW
15160 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-11-10 18:53 | 2016-11-10 20:28 | 3 | 95 | 4091831 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE ON 191-C-27 FAILED REFUSED CUTOUT RESTORED POWER AT 20:28 VER/CRB
15161 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-02 14:20 | 2008-07-02 19:05 | 1 | 285 | 61402-1 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008701//BAD 10KVA 7200//TRUCKS TO POLE//BUCKET TREE CREW NEEDED// - COD 1 // VER/TOM IDC XXXX
15162 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-10-05 07:34 | 2014-10-05 12:19 | 1 | 285 | 4554661 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SERVICER ENROUTE// FUSE BROKE . VER/CRB
15163 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-07-27 21:00 | 2018-07-27 21:57 | 5 | 57 | 4864711 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REALLY POOR CONNECTIONS@XFR ON 3 SERVICES,REPLACED ALL.XFR OFF@21:00,ON@21:57
15164 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-04-02 12:45 | 2021-04-02 17:30 | 1 | 285 | 4414361 | 285 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | crew reqd/bad ug. tre Released by crew 078S04 will be replacing whole service DT in rout back on at 1730
15165 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-04-10 17:40 | 2008-04-10 19:15 | 3 | 95 | 65876-1 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3002107// POLE 4543 40T LINE FUSE 6T TRANS FUSE SEND NOTE BAD LA TRUCK OK NEED FLAGMEN//C PHASE 6 COD//VER/CRB IDC XXXX
15166 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-09-10 14:35 | 2017-09-10 16:10 | 3 | 95 | 4344651 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THEY WAS LINE FUSE ON POLE 292-40 HAD LEAD PULL OUT TOP OF LINE FUSE, THIS HAS 15 T FUSE 37830292000040 VER/AWD L3/HFP XXXHFP
15167 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2009-10-07 08:30 | 2009-10-07 13:15 | 1 | 285 | 57865-1 | 285 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | PUMP STATION AT SOCCER FIELD NEED CREW TO REPLACE CUTOUT ON 3 PHASE POLE RELEASED BY CREW 078S11 CROSSARM BURNT INTO WILL HAVE TOO REPLACE//VER/CRB IDC XXXX
15168 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-10-09 12:18 | 2011-10-09 17:03 | 1 | 285 | 4959361 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 1 MAN,15 KVA 7200 XFR,MAT HANDLER.NEED TO REPLACE XFR//////////XFR HAD FAULTED,REPLACED IT AND RESTORED,ALL OK AFTERWARDS.//VER/CRB IDC XXXX
15169 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-09-28 21:15 | 2016-09-28 22:50 | 3 | 95 | 4939721 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION FROM XFMR RISER TO #4 CU OPEN WIRE SECONDARY. RE-WORKED ALL CONNECTIONS AND MOVED ONE SET FROM SECONDARY TO RISERS TO REDUCE LOAD ON NEW CONNECTIONS. SH COD-3 ISO SO @ 38830760D00153 VER/HFP L3/HFP
15170 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2018-11-10 21:48 | 2018-11-11 02:33 | 1 | 285 | 4387921 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | crew required need new anchor at 272-3 truck ok line fuse blown tag to tackett 271-157 Released by crew 078S03,replace anchor all cust restored @ 0233 please close ticket thanks.bt L3/HFP
15171 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-07-25 14:40 | 2011-07-25 14:55 | 19 | 15 | 4618971 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | PRIMARY OFF OF POLE TOP PIN SLAPPING SIDE OF POLE,WILL HAVE TO KILL POWER AND CHANGE P.T.P. AND INS. WILL NEED HELP. I WILL ISOLATE AT POLE NO.331-147. OPENED AT 14:40 , CLOSED AT 14:55 VER/KEP IDC XXXX
15172 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2008-09-13 14:45 | 2008-09-13 16:20 | 3 | 95 | 62192-1 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308601//SERVICE DROP PULLED FROM HOUSE BROKE CONNECTION ON THE NEUTRAL// COD 3 // VER/TOM IDC XXXX
15173 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-04-02 17:35 | 2020-04-02 18:32 | 5 | 57 | 4556271 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | busted crossarm on p#1097-121 going to open fuses on p 1262 tag to lmccoy and ground at work site FETR 19:00 LRM opened @ 17:35 in at 18:32
15174 | Pikeville | 3421001 | BREAKS | CITY | 2008-11-10 09:12 | 2008-11-10 13:57 | 1 | 285 | 63585-1 | 285 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3400901//REPLACE CUTOUT//COD 1//OPENED RECLOSER UPLINE IN ORDER TO REPAIR CUTOUT LEAD//RECLOSER OUTAGE IN ANOTHER TRBL ORDER// VER/DBM IDC XXXX
15175 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-08-08 17:05 | 2011-08-08 21:50 | 1 | 285 | 4682321 | 285 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | GOING TO CHECK CONNECTION ON TRANSFORMER BAD CONNECTION IN METER BASE CLEAN CONNECTION OPENED TRANSFORMER AT 2100 CLOSED AT 2150 VER/HFP L3/HFP IDC XXXX
15176 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2014-09-03 11:37 | 2014-09-03 16:22 | 1 | 285 | 4457721 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA NO TRUCK.. CAN USE YARD DOG STAY AT BASE OF HILL TILL BAMBOO THEN TURN UP TREE LINE.. PLEASE CALL MR. MORELLA 606 571-1747 TO LET HIM KNOW UPON SHOW UP PLEASE.. GRAVE NEAR POLE FLOWERS AND SHRUBS TO WATCH OUT FOR.. FETR 17:00 RELEASED BY CREW 078H06---REPLACED BAD 25KVA W/50KVA--VOLT CK GOOD---TBL TKT COMP// COD 1// VER/ ADH
15177 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-02-12 17:30 | 2014-02-12 19:05 | 3 | 95 | 4376121 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HAVE CREW ON THE WAY TO REPLACE POLE.NO OUTAGE AT THIS TIME. PULLED XFMR OFF @ 017:30 ON @19:05// VER/DBM
15178 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-06-05 00:23 | 2016-06-05 01:20 | 5 | 57 | 4304141 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK 10- REFUSE CUT-OUT POWER RESTORED KWB// VER/ ADH
15179 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2022-08-03 14:33 | 2022-08-03 15:30 | 5 | 57 | 4669821 | 285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burnt in two, opened transformer @ 15:00 to make safe, Back on and repaired @ 15:30.
15180 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-10-16 09:01 | 2019-10-16 13:45 | 1 | 284 | 4145261 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 167kv transformer,voltage 277,34.5kv,truck acessible//OFF @ 0708//MADE THIS OUTAGE TO SHOW CORRECT POLE # 37830198D00216 L3/HFP
15181 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-04-10 10:31 | 2019-04-10 15:15 | 1 | 284 | 4077371 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR TO RE-FUSE UNLESS IT IS BROKEN,DOEST APPEAR TO BE BROKE THOUGH/////////CUTOUT IS BROKEN,WILL REPLACE IT.WILL TAKE A WHILE/////////REPLACED CUTOUT&RESTORED
15182 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-09-13 21:15 | 2019-09-13 22:26 | 4 | 71 | 4015341 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | top of pole 167-78 burnt off due to bad dead-end insulator..will frame down and make repairs.restored.. opened line fuse @ 2115 closed @ 2226
15183 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2018-01-08 16:52 | 2018-01-08 21:36 | 1 | 284 | 4722131 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva trans trk app need 1 A lineman and material handler trk replaced trans restored power at 21:36
15184 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-01-21 23:49 | 2008-01-22 01:00 | 4 | 71 | 58816-1 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 25 KVA FEEDING FOUR 200A SERVICES. LINK BROKE VER/PDP IDC XXXX
15185 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-12-08 20:43 | 2020-12-08 23:05 | 2 | 142 | 4754931 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse door in Trans Cutout has Melted going to get it down and replace with new door.Restored service at 23:05.
15186 | Hazard | 3302703 | HAZARD | HAZARD | 2011-06-21 17:04 | 2011-06-21 18:15 | 4 | 71 | 4365771 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER ---- POWER RESTORED. IDC XXXX
15187 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-02-17 14:53 | 2016-02-17 17:15 | 2 | 142 | 4728981 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | HAD WIRE BURNED OFF ON UNDERGROUND PESTAL// VER/ ADH
15188 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-03-10 21:08 | 2015-03-10 23:30 | 2 | 142 | 4180661 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830094A10214 BAD CUTOUT REPLACED//POLE 38830094A10214 BAD CUTOUT REPLACED VER/CRB
15189 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2020-09-06 14:01 | 2020-09-06 18:45 | 1 | 284 | 4437601 | 284 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Bad connection on txmf, txmf in bad location. manual treecrew and linecrew required. Released by crew 078S11 crew on site FEtr 18:45 all pwr restored 18:45
15190 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-06-05 12:38 | 2022-06-05 17:22 | 1 | 284 | 4021001 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFM fuse blown will refuse///Bad current limting fuse will be making repairs///Repairs made changed cutout restored @ 17:22
15191 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2021-05-02 16:46 | 2021-05-02 21:30 | 1 | 284 | 4513091 | 284 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CREW ENROUTE//Cust. only has 110V service has problem can only get pick up under bridge need 2 men to help let service down and repair it 23:00 EST.
15192 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-05-07 11:46 | 2012-05-07 16:30 | 1 | 284 | 4754981 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN POLE 875-401..TRANSFORMER BUSTED OIL ON THE GROUND.MILLER ON SITE.. RELEASED BY CREW 076S01// CREW ON SITE STARTING REPAIRS TCM// RELEASED BY CREW 076H01 // COMPLTED AT 16:30 BY RDM//COD 1//ISO 38830875A00102// VER/DBM IDC HAD TO COME TO SERVICE BUILDING TO GET MATERIAL XXXX
15193 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2018-07-15 13:42 | 2018-07-15 14:53 | 4 | 71 | 4774881 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pull into
15194 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2010-08-23 11:58 | 2010-08-23 14:20 | 2 | 142 | 59571-1 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT CONNECTOR ON POLE 900-122 VER/HFP L3/HFP IDC XXXX
15195 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-01-20 13:17 | 2015-01-20 15:39 | 2 | 142 | 4947201 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE FUSED TRANSFORMER UP EVERYTHING OK//COD 2// VER/ ADH
15196 | Paintsville | 3409302 | KENWOOD | AUXIER | 2019-01-27 23:19 | 2019-01-28 00:30 | 4 | 71 | 4726801 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called cust//meter is blank//temperatures below freezing// Transformer fuse broke. Restored @ 00:30. sh L3/HFP
15197 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-05-11 09:22 | 2016-05-11 11:44 | 2 | 142 | 4199001 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BAD ON POLE 375-73..MADE REPAIRS RESTORED POWER AT 11:44.. COD-2 ISO LF 37830375C00073 *_)(*_)(*_)(*_)*(_)*
15198 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2022-12-19 13:28 | 2022-12-19 15:28 | 5 | 120 | 4276771 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Customers hot leg is burndt into @ secondary pole 1150-300, will have to open trans. @1150-59 to make repairs, will keep track of times. Opened @1447, closed back in @1528.
15199 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-12-16 10:46 | 2019-12-16 15:30 | 1 | 284 | 4157851 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV BURNED INTO@XFR,WILL HAVE TO LET IT DOWN TO REPAIR,THEN PUT IT BACK UP///////MADE REPAIRS AND RESTORED,ALL OK PER CUST.SERVE-IN HEATED UP&NEUTRAL SHORTED INTO.
15200 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-02-09 05:13 | 2020-02-09 09:07 | 3 | 234 | 4385281 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr bad will need 1 a lineman material handler & 25 kva 19.9 /120-240///opened line fuse at 93-33 to safely rep[lace TR - off at XXXX - on at XXXX///xfmr bad will need 1 a lineman material handler & 25 kva 19.9 /120-240.opened tap on pole 93-33 @ 08:42 closed @ 0907
15201 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-08-28 11:01 | 2021-08-28 15:45 | 1 | 284 | 4165421 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 25kva may get truck to it Released by crew 078S03 crew on site FETR 16:00
15202 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-01-06 09:16 | 2021-01-06 14:00 | 1 | 284 | 4851401 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connections on pole
15203 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-10-28 10:36 | 2021-10-28 15:20 | 1 | 284 | 4028571 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | one leg of a 4/0 underground l000ks to be going bad. put the beast on it and the left leg drops about 10 volts. checked 2 bolt paddles at xfmr and they are tight Released by crew 078S12///repairs made///complete BR
15204 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-07-03 16:02 | 2018-07-03 18:24 | 2 | 142 | 4718491 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad cutout
15205 | Hazard | 3302703 | HAZARD | HAZARD | 2017-11-28 16:39 | 2017-11-28 17:50 | 4 | 71 | 4607821 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse 37830296C11541
15206 | Whitesburg | 3312901 | JENKINS | KONA | 2012-12-20 16:06 | 2012-12-20 20:50 | 1 | 284 | 4489581 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD AND CAUGHT THE POLE ON FIRE. I WILL HAVE TO REPAIR THE POLE, RICK IS BRINGING ME A NINE FOOT CROSSARM AND A NEW CUTOUT//COD 1// VER/DBM
15207 | South Williamson | 3411401 | DEWEY | INEZ | 2022-12-02 11:48 | 2022-12-02 14:10 | 2 | 142 | 4220681 | 284 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | secondary bushing loose on xfmr and had lead almoast burnt into//repaired connection and tightened down bushing//restored at 14:10//complete/em
15208 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-12-08 10:58 | 2014-12-08 13:20 | 2 | 142 | 4846961 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED AT WEATHERHEAD AND BURNED NEUTRAL IN TWO. REPLACED SERVICE AND RESTORED @ 13:20. SH// COD 2// VER/ ADH
15209 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-01-17 13:21 | 2010-01-17 18:05 | 1 | 284 | 55457-1 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830184B00009 WE HAVE ONE FUSE BLOWN ON THREE PHASE, CHECKING LINE, GOT POWER BACK ON AT 15:54 BUT WILL HAVE TO OPEN THREE PHASE FUSES TO COMPLETE JOB. TIM SMITH BRING BUCKET TO US TO HELP//// OPENED ONE PHASE BACK UP AT 18:00 CLOSED BACK AT 18:05 POWER ON. LEAD TO C/O LAYING ON ARM. MOVED RISER OFF ARM. IDC XXXX
15210 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-08-08 18:08 | 2015-08-08 20:30 | 2 | 142 | 4112691 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 272-1280 HAD POLE SPLIT OUT , POLE TOP PIN HANGING DOWN WITH PRIMARY, NEED POLE EXT. AND ONE MAN. TALKED TO MIKE EBERTON HE SAID HE WAS AT COMPANY AND WOULD COME. I WILL LIFT CLAMP ON POLE 272-559 AND GROUND./// INSTALLED POLE EXTENSION AND REMOVED GROUNDS POWER RESTORED. OPENED LINE AT 19:12 CLOSED AT 20:30 RELEASED BY CREW 077S08
15211 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-06-02 08:38 | 2020-06-02 11:00 | 2 | 142 | 4942761 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o door. replaced
15212 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-03-17 16:07 | 2016-03-17 18:29 | 2 | 142 | 4859831 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKENTRANS CUTOUT ON 1125-C-245 TRK ACCESSIBLE CAN CHANGE IT MYSELF REPLACED CUTOUT RESTORED POWER AT 18:18 ISO 38831125C30245 COD 2 VER/AWD
15213 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2019-05-03 14:05 | 2019-05-03 16:27 | 2 | 142 | 4209341 | 284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on pole 241-24..cut loop out on line fuse pole 241-258.xfm. on pole 241-24 does not feed anything..place in abnormal on pole 24.opened line fuse @ 15:48 and closed back in @ 16:27..please send copy to PR.//made aed//COD 2 FROM BEGINNING
15214 | Hazard | 3308002 | JACKSON | PANBOWL | 2021-11-09 08:58 | 2021-11-09 10:09 | 4 | 71 | 4069141 | 284 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | old cutout gate burned into on transformer fuse, cust said it burned up one computer. when voltage was surging,
15215 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2010-01-26 06:18 | 2010-01-26 11:01 | 1 | 283 | 59889-1 | 283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33597418 // RELEASED BY CREW 078S04//BAD B PHASE TRANSFORMER//VER/CRB IDC XXXX
15216 | Hazard | 3303901 | LESLIE | HYDEN | 2011-01-23 14:47 | 2011-01-23 19:30 | 1 | 283 | 63727-1 | 283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38538232 // BAD 25KVA 19.9 120/240 NEED 4 MEN TO CHANGE RELEASED BY CREW 077S01 WILL CHANGE MONDAY ON OPS. #0348190876 W>R>#38538520 RELEASED BY CREW 077H02 COD-1 ISO TF 37830412C00108 VER/HFP L3/HFP IDC XXXX
15217 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-08-02 08:36 | 2018-08-02 13:19 | 1 | 283 | 4894421 | 283 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed mid-span in service.
15218 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-02-06 17:02 | 2008-02-06 21:45 | 1 | 283 | 51783-1 | 283 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3401702//REPAIRED BAD CONNECTION ON HOT LEG OF SERVICE DROP AT THE TRANSFORMER. VER/HFP IDC XXXX
15219 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-09-18 10:12 | 2014-09-18 14:55 | 1 | 283 | 4508471 | 283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25VA TRANSFORMER 7200// BRING RISERS TORE OUT OF TRANSFORMER/// CAN PROBABLY GET TO WITH TALL MATERIAL HANDLER OUT OF DRIVEWAY// BAD 25KVA XFORMER , NEED LINE CREW. TRUCKS OK// NEW TRANSFORMER CP 1455092354 REPLACED SERVICE DROP AND LIGHT OLD TRANSFORMER 2773429-5 MCGRAW/// ISO 38830350000080//// COD 1// VER/BOW
15220 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-06-30 10:03 | 2018-06-30 14:46 | 1 | 283 | 4692161 | 283 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FAILED CONNECTION ON TRANS //PLEASE SEND TO D CHRISTIAN HAV E EVERYTHING RE-WORKED FROM TRANSFORMER DOWN//1 CUST AFFECTED//SENT TO TECH
15221 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-04-08 10:17 | 2013-04-08 15:00 | 1 | 283 | 4987371 | 283 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPAN OF SEC. BAD // WILL NEED TO CHANGE // CALLED T. HALL FOR CREW RELEASED BY CREW 074S05//CREW MADE REPAIRS//COD 1// VER/DBM IDC XXXX
15222 | Hazard | 3309302 | VICCO | JEFF | 2009-12-05 17:52 | 2009-12-05 22:35 | 1 | 283 | 58860-1 | 283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 CUTOUT FAILED AND POLE 37830275000218 IS BURNED INTO CALLING FOR EXTENSION AND ASSISTANCE FORM CREW IDCC PN218 XXXX
15223 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-12-03 21:42 | 2020-12-04 02:25 | 1 | 283 | 4743431 | 283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bring 7200/129/240 25 kva Released by crew 078S07 // waiting on tree crew to cut out secondary while changing out xfmr crew onsite FETR 03:15 asplundh will need time to cut out secondary LRM all pwr restored @ 2:25 found nothing wrong in the trees.//cod 1
15224 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2017-03-27 14:11 | 2017-03-27 18:54 | 1 | 283 | 4588931 | 283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 296A-458 NEED 2 MEN & BIG BUCKET ,& FLAGGERS . 25KVA 7200 . RELEASED BY CREW 075H04. COMP. POWER RESTORED VER/CRB L3/HFP XXXHFP
15225 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-09-19 12:57 | 2020-09-19 17:40 | 1 | 283 | 4478581 | 283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva think squirrel shorted out but signs of oil on ground very little truck ok Released by crew 078S03 crewon site FETR 17:30 all pwr restored 17:40 pleaseclose ticket LRM
15226 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-05-23 10:22 | 2022-05-23 15:05 | 1 | 283 | 4932511 | 283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | primary metering bypass broke. need big bucket and 7200 cutout Released by crew 077S10. replaced bypass cutouts, all power restored @ 15:05.. p.hicks
15227 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-03-21 08:02 | 2010-03-21 12:45 | 1 | 283 | 52128-1 | 283 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND SERVICE HAS A SHORT IN IT. I CALLED DENNIS AND HE IS SENDING HELP. WE SPLICED UNDERGROUND SERVICE AND STRAIGHTENED POLE. VER/LDA IDCC CDC89 XXXX
15228 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-05-04 08:56 | 2011-05-04 10:30 | 3 | 94 | 4006551 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT, REPLACED CUTOUT//COD 3// VER/DBM IDC XXXX
15229 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-02-04 11:16 | 2021-02-04 12:50 | 3 | 94 | 4936941 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke XCO on pole 22-8// will be making repairs// customer is restored
15230 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-03-27 05:11 | 2009-03-27 06:45 | 3 | 94 | 61996-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP COD-3 LIGHTNING ARRESTOR HAS BLOWN UP CAUSING XFMR FUSE TO BLOW L3/HFP IDC XXXX
15231 | Pikeville | 3413402 | GARRETT | LACKEY | 2018-05-20 09:46 | 2018-05-20 11:20 | 3 | 94 | 4381861 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | looks like 6t fuse broke fused up everything ok
15232 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-07-12 22:33 | 2020-07-13 03:15 | 1 | 282 | 4156651 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva transformer, crew required. changed transformer and restored at 03:15
15233 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2016-06-29 11:54 | 2016-06-29 14:15 | 2 | 141 | 4501311 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHGING VER/CRB
15234 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-05-26 13:47 | 2010-05-26 15:21 | 3 | 94 | 51063-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN WILL TRY XFMR---FOUND A BAD CUTOUT WILL CHANGE//COD 3// VER/DBM IDC XXXX
15235 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2008-03-16 00:59 | 2008-03-16 03:20 | 2 | 141 | 57610-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308601/// 2/3 SECONDARY BURNT DOWN VER/JHM IDCC CCO XXXX
15236 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-05-27 21:53 | 2019-05-28 02:35 | 1 | 282 | 4351531 | 282 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Called Customer: Customer states 90% of house is out of power/ 220 appliances arent working/ did try to reset breaker bad neutral was about 5 splices got all changed and power is 100% again/ ISO 38830186000043/ COD 1
15237 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-11-04 09:19 | 2011-11-04 11:40 | 2 | 141 | 4050111 | 282 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, UG | BAD CONNECTION IN THE UNDERGROUND JUNCTION BOX. TIM HALL IS BRINGING THE MATERIALS TO MAKE REPAIRS.// VER/DBM IDC XXXX
15238 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2021-03-08 13:36 | 2021-03-08 15:10 | 3 | 94 | 4315471 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout door burnt into// Possibly from a structure fire that melted service down the night before. Replaced door and restored @ 15:10
15239 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-06-01 17:44 | 2012-06-01 19:18 | 3 | 94 | 4868391 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED COD-3 ISO TF 38830327C00094 VER/HFP L3/HFP IDC XXXX
15240 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-08-07 20:38 | 2012-08-08 01:20 | 1 | 282 | 4909491 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200. THIS IS AT THE GOLF COURSE ON RIGHT JUST AS YOU TURN ON TO WOODMAN SUMMER ROAD. CAN USE TRUCK. //VER/GAH IDC XXXX
15241 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-01-17 15:55 | 2017-01-17 20:37 | 1 | 282 | 4306421 | 282 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 38830142D00423 HAS THE CNTR C/O OF A 3 CAN BANK BROKE, SADDLE BAGGED C/OS----38830142A00053 25T FUSE BLOWN B PHASE--BY TRK, OUT SIDE OF TWIT CARD AREA--CREW REQ--DS011717 RELEASED BY CREW 078S01/CREW ON SITE/FETR 2100/VEM/REPAIRS MADE B PHASE FUSE RESTORED 2037/PLEASE CLOSE TICKET/THANKS/VEM 38830142A00053 VER/AWD L3/HFP HFPC MCCDL CNT4
15242 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2014-02-02 10:02 | 2014-02-02 12:23 | 2 | 141 | 4336501 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | METER # 435942362 & 435941794 POLE #1123-6620 OPEN XFMAT 11:15 CLOSED BACK IN AT 11;30 ALL POWER RESTROLED HAD BAD SQUEESON CONN PLEASE CLOSE TIC RM//ISO//UNMETERED ACCOUNTS????//COD 1 + 1????
15243 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-10-16 07:32 | 2011-10-16 09:53 | 2 | 141 | 4987051 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CREW ON SITE/FETR1030/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST AT 0953/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN IDC XXXX
15244 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-07-10 23:35 | 2017-07-11 01:09 | 3 | 94 | 4103981 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE PULL INTO ON POLE 157=335 VER/ARN
15245 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-03-19 08:01 | 2011-03-19 12:43 | 1 | 282 | 55775-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 39227192 POLE 67-2001 BAD 50 KVA TRUCK TO POLE NEEDS CHGED TODAY RELEASED BY CREW 078S08 RELEASED BY CREW 078H02///CHANGED OUT BAD XFMR//COD 1// VER/DBM IDC XXXX
15246 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-01-23 15:27 | 2018-01-23 17:01 | 3 | 94 | 4768111 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | replaced arr. .line fuse 269-203 back in @ 17 :01 complete
15247 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-05-26 10:38 | 2015-05-26 11:25 | 6 | 47 | 4464681 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 246-111/NO CREW REQUIRED BROKE FUSE LINK/COD 6// VER/ ADH L3/DKGXXX
15248 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-02-13 07:06 | 2018-02-13 09:27 | 2 | 141 | 4836271 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 502-28. repaired and back in at 0927/ ISO 38830502000028/ COD 2
15249 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-09-02 21:18 | 2008-09-02 22:52 | 3 | 94 | 58719-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801//15T LINE FUSE CUTOUT DOOR BURNT UP/NO CREW REQUIRED VER/TOM IDCC PN95 XXXX
15250 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-03-12 22:14 | 2020-03-13 00:35 | 2 | 141 | 4473261 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva no truck,repairs made all cust restored @ 0035 please close ticket thanks.bt // cod 2
15251 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-11-15 19:39 | 2015-11-15 22:00 | 2 | 141 | 4450091 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE//NETURAL AND HOT LEG BURN INTO.MADE REPAIRES VER/ARN
15252 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-03-29 22:48 | 2014-03-30 01:09 | 2 | 141 | 4537091 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1062-425 BURNED ALMOST INTO,NEED FOREMAN,1 MAN,BIG BUCKET,X ARMS.WILL TRY TO MAKE TEMPORARY REPAIR @ 2243 FUSE OPENED AT POLE 312 NO POLE 1062-425 BURNED ALMOST INTO,NEED FOREMAN,1 MAN,BIG BUCKET,X ARMS.WILL TRY TO MAKE TEMPORARY REPAIR/////OPENED TO MAKE REPAIR AT 10:48 VER/PDP
15253 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-01-21 06:13 | 2012-01-21 10:55 | 1 | 282 | 4279461 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA TRANSFORMER BAD AT CELL TOWER SITE. CREW ENROUTE TO CHANGE. (MLLER,THOMAS & NEWSOM TO ASSIST)25 KVA TRANSFORMER BAD AT CELL TOWER SITE. CREW ENROUTE TO CHANGE. REPLACED XFMR AND RESTORED @ 10:55. SH //VER/GAH IDCC PN905 XXXX
15254 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2016-12-22 07:09 | 2016-12-22 11:51 | 1 | 282 | 4228291 | 282 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CHECKING, GETTING LOW VOLTAGE ON ONE SIDE OF URD WIRE. HAD A BAD LEG OF URD, REPLACED @1151. VER/CRB
15255 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-06-13 13:40 | 2012-06-13 18:22 | 1 | 282 | 4911791 | 282 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CREW REQUIRED BAD UNDERGROUND NEED ADD A PHASE/ISOLATED BAD PHASE ON BOTH ENDS RELEASED BY CREW 078S03 VER/HFP L3/HFP IDC XXXX
15256 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-02-06 10:51 | 2011-02-06 13:12 | 2 | 141 | 54826-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER, GOING TO OPEN TRANSFORMER AND MAKE REPAIRS//ISO 38831059B00309//COD 1+1// OPEN TRANSFORMER AT 1255 AND CLOSED AT 1312//COD 2 IDCC PN171 XXXX
15257 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2020-12-01 07:39 | 2020-12-01 10:00 | 2 | 141 | 4734281 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found bad c/o, will need crew to change this c/o is really close to pri, can use truck, Released by crew 078S06,repairs made all cust restored @ 1000 please close ticket thanks.bt
15258 | South Williamson | 3411401 | DEWEY | INEZ | 2012-07-12 09:43 | 2012-07-12 14:25 | 1 | 282 | 4694641 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT ON746-319//BAD 15 KVA 19.9 XFMR//CREW COMING TO CHANGE OUT//NO BIG TRUCK//HAVE REPAOIRS MADE//RESTORED AT 1425//COMPLETE//EM
15259 | Hazard | 3301101 | CHAVIES | CHAVIES | 2020-08-08 15:41 | 2020-08-08 17:15 | 3 | 94 | 4302001 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout. replaced and restored power at 17:15
15260 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-12-22 09:54 | 2013-12-22 12:15 | 2 | 141 | 4189621 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LF BLOWN ON 37820073D00139 // BROKE CUTOUT ON 73-78/// WILL CHANGE// REPLACED BAD CUTOUT//POWER IS RESTORED VER/SEF L3/HFP
15261 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-08-01 13:53 | 2019-08-01 18:35 | 1 | 282 | 4822801 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Repaired service drop @ 1835
15262 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-08-03 16:09 | 2010-08-03 18:30 | 2 | 141 | 60907-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830247C00661 WE HAVE GATE BURNT UP, WAITING FOR BANK TO CLOSE FOR CARS TO MOVE TO GET MY BUCKET IN THERE. XFMR WE HAVE OFF IS ON POLE 37830247C00957./////// CHANGED OUT C/O, POWER RESTORED. COD-2 VER/HFP L3/HFP IDC XXXX
15263 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-10-23 08:29 | 2018-10-23 10:50 | 2 | 141 | 4313461 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//NO POWER TO MTR//BROKE FUSE L3/HFP
15264 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-08-27 16:49 | 2010-08-27 19:10 | 2 | 141 | 61305-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CHECKING NOW.RISER INTHE BOTTOM OF CUT OUT CAME OUT PUT BACK IN RETIGHTIN THE NUT//COD 2// VER/DBM IDCC CNT1 XXXX
15265 | Hazard | 3303902 | LESLIE | WOOTON | 2015-08-06 10:34 | 2015-08-06 12:55 | 2 | 141 | 4103761 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT// VER/ ADH
15266 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-04-20 23:03 | 2009-04-21 03:45 | 1 | 282 | 62200-1 | 282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLING CREW RELEASED BY CREW 078S07///CREW ON SITE TO REPLACE 25KVA WITH A 25KVA AND #2 RISERS AND NEW 100AMP CUT-OUT PR TOLLIVER//REPAIRS MADE POWER RESTORED AT 03:45 VER/KEP L3/KEP IDC XXXX
15267 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-12-01 10:04 | 2009-12-01 14:45 | 1 | 281 | 53102-1 | 281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3309001// BAD TRANSF == CALLED FOR CREW & TRANSF == CHANGED TRANSF REM 15 KVA INST 25 KVA IDC XXXX
15268 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-06-27 10:44 | 2010-06-27 15:25 | 1 | 281 | 58040-1 | 281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XFORMER ON POLE 402-93 TO MAKE REPAIRS TO SERVICE DROP. BACK ON AT 15:25. VER/KEP L3/KEP IDC XXXX
15269 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-10-17 15:47 | 2019-10-17 20:28 | 1 | 281 | 4163701 | 281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout bad on pole 336-06.will need A or B lineman and NE with 7200 cutout and bracket to make repairs..restored..//cod 1
15270 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-01-03 09:44 | 2012-01-03 14:25 | 1 | 281 | 4228161 | 281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND SERVICE RELEASED BY CREW 077S04BAD UNDERGROUND SERVICE ---OPENED TRANSFORMER AT 11:12 CLOSED AT 12:00 (SEE H4228161)-- OPENED AT 14:10, CLOSED AT 14:25 (SEE H4228162) SPLICED WIRE, POWER RESTORED.//COD 1 + 2// VER/DBM IDC XXXX
15271 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-07-01 19:02 | 2014-07-01 23:43 | 1 | 281 | 4181021 | 281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LEAKING 5 KVA TRUCKS OK SMALL CLEANUP/CREW REQUIRED RELEASED BY CREW 078S03//// 23:10 UNTIL 23:31
15272 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-02-27 21:16 | 2008-02-28 01:57 | 1 | 281 | 51099-1 | 281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000102//SERVICER ETA 2145// B PHASE ON SPACER CABLE BURNT DOWN/ B FRALEYS CREW TO REPAIR// CALLED DRT TO HELP SWITCH RELEASED BY CREW 078S07//SWITCHING ORDER # 51110-1 CREATED TO SWAP LOAD OVER TO 47TH-39TH CIRCUIT// COD-1 VER/LDA IDC XXXX
15273 | Cannonsburg | 3001401 | LOUISA | CITY | 2016-05-03 20:49 | 2016-05-04 01:30 | 1 | 281 | 4171791 | 281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED TO CHANGE CUT OUT DOOR ON CUT OUT WAS DAMAGED MAY GET SERVICE BUCKET TO POLE // B TACKETT, R MORGAN, C SIMMONS & K GRIFFITH //,,,CREW ON SITE,,REPLACED CUTOUT DOOR VER/TOM L3/TOM
15274 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-05-27 11:00 | 2019-05-27 15:40 | 1 | 280 | 4349211 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed on 851-370. Difficult location - ROW crew enroute to assist. Cut trees and vines, replaced cutout, arrester and restored @ 15:40. sh//cod 1//iso//
15275 | Hazard | 3302703 | HAZARD | HAZARD | 2021-01-29 14:32 | 2021-01-29 15:42 | 4 | 70 | 4917031 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad 4/0 secondary connection at customers weather head, XFMR off at 14:32 back on at 15:42.
15276 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-02-18 13:10 | 2009-02-18 15:30 | 2 | 140 | 64260-1 | 280 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | FOUND HOT TAP BURNTED OFF B PHASE, HAVE CONTRACTOR COMING TO FIX THIS PROBLEM, I HAVE 3 PHASE BANK OPEN UP AT THE PRESENT TIME HAVE HOT TAP REPAIRED AND POWER IS RESTORED//COD 2// VER/DBM IDC XXXX
15277 | Paintsville | 3409302 | KENWOOD | AUXIER | 2009-02-18 20:11 | 2009-02-19 00:51 | 1 | 280 | 64750-1 | 280 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | SERVICE WAS DAMAGED DURING STORM AND SOMEONE SPLICED SERVICE DROP CLOSE TO POLE. SPLICE FAILED. WILL HAVE TO CLIMB POLE IN DIFFICULT LOCATION TO REPLACE #4 SERVICE WITH #2. (200 AMP SERVICE) COMPLETE. SH IDC XXXX
15278 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-06-21 12:18 | 2022-06-21 16:58 | 1 | 280 | 4269311 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 38830473000006 bad 3kva 7200 by squirtboom. did notice that one strandof wire apears to be broke in the 6a promery so be careful Released by crew 078S12. crew on site to make repairs. repairs made xfmr in @ 16:58 complete
15279 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-04-09 18:35 | 2021-04-09 23:15 | 1 | 280 | 4436351 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required. bad 10 kva transformer. need flaggers Released by crew 078S06
15280 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-03-12 07:25 | 2014-03-12 09:45 | 2 | 140 | 4469741 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR LIGHTNING ARRESTER BLEW UP AND BLEW XFMR FUSE. REPLACED ARRESTER AND CUTOUT DOOR. RESTORED @ 9:45. SH COD-2 ISO TF 38830809C30417 VER/HFP L3/HFP
15281 | South Williamson | 3411401 | DEWEY | INEZ | 2018-05-05 11:04 | 2018-05-05 13:24 | 2 | 140 | 4310091 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD XFMR CUTOUT.power restored @ 13:24
15282 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2014-04-07 23:35 | 2014-04-08 04:15 | 1 | 280 | 4584371 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT CAN REACH IT WITH TRK WILL REPAIR IT MYSELF VER/TOM L3/TOM IDCC CNT6, PN29 XXXX
15283 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-11-01 14:25 | 2012-11-01 16:45 | 2 | 140 | 4321831 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 078S08 POLE 70-2252 6T TRANS FUSE BROKE REPAIRED COD-2 ISO TF 38830070B12252 VER/HFP L3/HFP IDC XXXX
15284 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-12-19 23:14 | 2014-12-20 00:10 | 5 | 56 | 4871611 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 117-94 BAD CUTOUT CHGED VER/KEP
15285 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2019-04-14 17:33 | 2019-04-14 19:53 | 2 | 140 | 4099341 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse on 271-68 open/bad cutout 271-A3-4022/servicer to change/vem/repairs made and all cust restored 1953/ please show 15T on pole#271-68/please close ticket/thanks/vem
15286 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-11-14 19:40 | 2021-11-14 20:50 | 4 | 70 | 4091371 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Hot line clamp on pole 351C-270 was off stirrup. Unknown cause. Power restored at 20:50.//ISO 37830351C00270//cod 4
15287 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2014-07-07 14:00 | 2014-07-07 15:10 | 4 | 70 | 4200171 | 280 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I REMADE CONNECTIONS ON XFMR POLE VER/CRB
15288 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2018-09-24 14:36 | 2018-09-24 15:46 | 4 | 70 | 4151091 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced hot line clamp and customers restored @ 15:46 complete L3/HFP
15289 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-05-05 15:42 | 2009-05-05 18:02 | 2 | 140 | 56622-1 | 280 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | TRANSFORMER POLE SEC BUCKET 1147-4613 TRANFORMER SEC PED 1147-4713 RELEASED BY CREW 078S09 INSTALLED TEMPORARY POWER TEMP IKE WILL FIX TOMORROW TRAILOR NEXT DOOR PART POWER ALSO BUT VACANT VER/KEP L3/KEP
15290 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-03-27 15:00 | 2015-03-27 17:20 | 2 | 140 | 4235361 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 CUST SERVED OFF OF TRANSFORMER I FOUND LOOSE CONNECTION ON THE NEUTRAL BUSHING ON SECONDARY SIDE OF TRANSFORMER. THIS RESULTED IN AN OPEN NEUTRAL AND HIGH VOLTAGE AT THE METER BASE 250V PHASE TO GROUND ON 1 SIDE. I MADE REPAIRS EVERYTHING OK. CUST SAID THEY HAD DAMAGE. 1 CUST NOT AT HOME. SEND COPY TO PEGGY IN DAMAGE CLAIMS WILL PROBABLY GET A CALL ON THIS/COD 2/EMAILED PEGGY/ADH// VER/ ADH
15291 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2021-12-09 06:48 | 2021-12-09 07:58 | 4 | 70 | 4163611 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout went bad on pole 357-C-96. replaced damaged equipment, power restored///door was stuck closed but power was out upon arrival
15292 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-11-23 22:20 | 2015-11-23 23:30 | 4 | 70 | 4481811 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 220-9 . WILL MAKE JOB TO REPLACE ARRESTER ./AED MADE/ADH// VER/ ADH
15293 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2010-11-07 08:49 | 2010-11-07 09:24 | 8 | 35 | 53652-1 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSELINK VER/TOM IDC XXXX
15294 | Pikeville | 3403001 | PIKEVILLE | CITY | 2022-04-19 17:04 | 2022-04-19 19:24 | 2 | 140 | 4780691 | 280 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection failed in splice, will have to open bank, will keep up with times// opened XFM @ 19:24
15295 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-12-03 23:02 | 2011-12-03 23:30 | 10 | 28 | H4139091 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PRC CREW REQUIRED-- NO TRUCKS -37 1/2 CSP TRANSFORMER--HOT TAP LEAD BURNT OFF AT PRIMARY BUSHING-HANGING HOT WAS NOT ABLE TO CLEAR--BUSHING BURNT BAD ON TANSFORMER, NOT SURE IF REPAIRABLE, MIGHT NEED TO CHANGE TRANSFORMER RELEASED BY CREW 078S07 2302 - OPENED LINE FUSE AT POLE 20-1069 FOR SAFETY CLEARANCE - 2330 - RESTORED TO SERVICE //VER/GAH IDC XXXX
15296 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2022-07-17 13:28 | 2022-07-17 18:08 | 1 | 280 | 4502791 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva on pole 1147-856 trucks to pole. waiting on L. Mccoy and crew to change. Released by crew 078H33 crew on site 19:00 LRM
15297 | Hazard | 3302703 | HAZARD | HAZARD | 2012-03-08 16:05 | 2012-03-08 17:15 | 4 | 70 | 4564411 | 280 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | COD-4 ISO 37830296A30715 VER/HFP L3/HFP IDC XXXX
15298 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-08-16 09:28 | 2010-08-16 11:48 | 2 | 140 | 56295-1 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE LEG ON TRANSFORMER MELTED//COD 2// VER/DBM IDC XXXX
15299 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-04-24 17:00 | 2015-04-24 21:40 | 1 | 280 | 4363461 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER NUETRAL LUG AND TANK GRD LOOSE BAD CONNECTION IN SERVICE DROP VER/CRB
15300 | South Williamson | 3411401 | DEWEY | INEZ | 2017-02-16 08:25 | 2017-02-16 10:45 | 2 | 140 | 4401351 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE SWITCH OPEN ON POLE 38830767A00028 @ 2 CUST OUT E //CLAMP BURNT OFF ONC PHASE OF 38830767A00028//MAP SHOWS CUST ON B PHASE BUT SERVICER CONFIRMS IT IS C PHASE//MADE MDCENTER PHASE OUT///THIS IS ONLY CUSTOMER ON THIS PHASE ALONG WITH EQT COMPRESSOR STATION NEXT DOOR WHO IS HAVING PROBLEMS TOO///WENT BACK TO POLE 767-28 AND HOT TAP BURNT OFF CENTER PHASE///GOING TO REPAIR//REPAIRS MADE//RESTORED AT 10:45/// VER/CRB
15301 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-10-30 10:00 | 2015-10-30 12:20 | 2 | 140 | 4394571 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE//POLE 37830362000072 80% AT THE CUT OUT, SHOULD HOLD TILL FRIDAY//WILL NEEED 45C4 POLE CUTOUT AND 25KVA TRANSFORMER 2 CLEVIS,TRUCK ACC. ON SITE WORKING POLE REPLACED AND POWER RESTORED/ 10-1220/ ISO 37830362000072/ COD 2/ VER/BOW
15302 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2021-01-29 09:50 | 2021-01-29 11:00 | 4 | 70 | 4916681 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service neutral burned in two mid span--opening TR (no outage till TR was opened) to fix problemService wire burnt down. Replaced service. Transformer off from 9:50 - 11:00. Power resored
15303 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-05-05 12:50 | 2018-05-05 13:10 | 14 | 20 | 4307961 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad three phase 350 underground, direct baried. Bobby Reynolds is planning on doing outage and underground Saturday, 5/5 to run new underground. Released by crew 078H04 20 min 1310
15304 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-06-27 09:20 | 2011-06-27 14:00 | 1 | 280 | 4418971 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY TERMINATION HAS WENT BAD ON RISER POLE. // COD 1 // VER/DBM IDC XXXX
15305 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-02-21 10:35 | 2016-02-21 11:31 | 5 | 56 | 4742061 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 CU OPEN WIRE SEC. DOWN POLE 1146-114 TO 115 TRK TO 115 CREW REQD. RELEASED BY CREW 078S07/CREW ON SITE/VEM/NO OUTAGE AT THIS TIME /WILL NEED TO OPEN XFMR 1146-72 FOR REPAIRS /APROX ONE HOUR OUTAGE/VEM/OPENED XFMR AT 1035/REPAIRS MADE AND ALL CUST RESTORED 1131/PLEASE CLOSE TICKET/THANKS/VEM//COD 5// VER/DBM
15306 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-04-23 17:15 | 2012-04-23 18:25 | 4 | 70 | 4699761 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKEN DOWN ON POLE 146-28.GOING TO OPEN LINE FUSE ON POLE 146-19 TO ISOLATE TROUBLE AND MAKE REPAIRS /// LINE FUSE OPEN @ 17:15 RESTORED @ 18:25 /// TALKED TO TIM HALL AND HE IS GOING TO SEND CREW TO CHANGE POLE 37820146000028 TOMORROW /// 45/4, 19.9KV SINGLE PHASE DE WITH 25 KVA, 2 #2 SECONDARIES, AND A #2 SERVICE /// WILL ALSO NEED TREE CREW WITH BIG BUCKET TO CUT OVERHANGS WHILE POWER IS OUT /// PLEASE SEND THIS TO TIM HALL ///VER/CRB
15307 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-12-17 10:52 | 2012-12-17 13:12 | 2 | 140 | 4474601 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. IS CLOSED ON POLE 38831109A40151///// XFMR CUTOUT BROKEN ON POLE 38831110000019//COD 2//MADE MDC ///VER/CRB L/3 CRB
15308 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-08-09 23:30 | 2014-08-10 04:10 | 1 | 280 | 4349141 | 280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 356-385, WILL HAVE TO OPEN L/F ON POLE 356-355 TO CHANGE, OPENED AT 0300, CLOSED BACK AT 0410 ALL POWER RESTORED.
15309 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-09-04 19:30 | 2011-09-04 21:03 | 3 | 93 | 4810921 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT APR AT 2103 CLOSE TICKET//COD 1 IDC XXXX
15310 | Hazard | 3303902 | LESLIE | WOOTON | 2011-11-15 09:21 | 2011-11-15 14:00 | 1 | 279 | 4078221 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S01REPLACED CUTOUT 19..9 KV//MADE MDC ///VER/CRB IDC XXXX
15311 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2016-07-29 21:11 | 2016-07-30 01:50 | 1 | 279 | 4710931 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 304-24, MANUEL POLE WILL NEED ONE LINEMAN ,RESTORED POWER AT 01:50.. VER/KEP
15312 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-04-11 17:21 | 2008-04-11 22:00 | 1 | 279 | 66408-1 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | == PULLED SPLICE OUT OF SERV 4/3 ON NEUT == REPAIRED == CUST COULD HAVE DAMAGES//3312202//VER/CRB IDCC CCCE XXXX
15313 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-09-13 08:46 | 2017-09-13 10:19 | 3 | 93 | 4357221 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN NETURAAL ON SECONDARY AT POLE #37820001000242 VOLTAGE WHEN I ARRIVED WITH BEAST ON WAS 39 /202 PHASE TO GROUND . MADE REPAIRS & IS NOW 122/122-- 240.COUSTOMERS BREAKERS WERE OFF WHEN I ARRIVED. & SHE IS COMPLAINING OF DAMAGES. /// SENT EMIAL TO P WYSONG..HFP VER/HFP L3/HFP
15314 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-03-11 21:57 | 2015-03-11 23:30 | 3 | 93 | 4185051 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED 911 WITH AN ETA OF 2220//CUTOUT DOOR BURNED UP WILL CHANGE// REPAIRS MADE VER/CRB
15315 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-05-21 03:27 | 2008-05-21 05:00 | 3 | 93 | 50017-1 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801// BAD CUTOUT DOOR COD-3 VER/KEP IDC XXXX
15316 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2018-06-18 09:06 | 2018-06-18 13:45 | 1 | 279 | 4615251 | 279 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | BAD CT ON PRIM MTRNG,TIM HALL WILL GET CREW TO COME BY AND REPAIR OR POSSIBLY JUMPER IT OUT Released by crew 074S06/ ISO 37820007B00081/ COD 1
15317 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2014-12-01 12:12 | 2014-12-01 13:45 | 3 | 93 | 4815381 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NO OUTAGE & NO IMMEDIATE DANGER SECONDARY POLE 38821089A00228 IS ROTTEN AT THE GROUND LINE AND IS LEANING DOWN HILL. THIS IS AN AT&T POLE AND NEEDS REPLACED MONDAY. PHONE CABLE IS ALL THAT IS HOLDING THE POLE UP. CREW CAN MOVE THE POLE DOWN THE CREEK SOME SO THAT IT CAN BE TRUCK APPROACH. RELEASED BY CREW 079S02. REPLACED POLE 1089-228. WE HAD 3 CUSTOMERS OFF FROM 12;12 UNTIL 13:45. VER/CRB
15318 | South Williamson | 3411401 | DEWEY | INEZ | 2020-03-28 12:56 | 2020-03-28 17:35 | 1 | 279 | 4519111 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | on 1735
15319 | Whitesburg | 3312902 | JENKINS | JENKINS | 2021-09-24 09:17 | 2021-09-24 10:50 | 3 | 93 | 4286941 | 279 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | customer had neutral and one hot leg burn out in service. made repairs, power restored.. open @10:15 closed @ 10:50
15320 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-09-08 21:31 | 2022-09-08 23:04 | 3 | 93 | 4857491 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | attempted to contact customer/no answer at either number/no crew required replaced door
15321 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-06-01 20:31 | 2015-06-01 22:04 | 3 | 93 | 4497421 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL CHG SURGE PROTECTOR MADE REPAIRS & REFUSED XFMR.RESTORED @ 22;04 RELEASED BY CREW 074S04 VER/CRB
15322 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-11-14 15:12 | 2013-11-14 16:45 | 3 | 93 | 4039301 | 279 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SEC. RISER OPEN..REPLACED COD-3 VER/HFP L3/HFP
15323 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2012-04-10 07:04 | 2012-04-10 11:43 | 1 | 279 | H4659651 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPENED RECLOSURE ON POLE#38831053B10277 @ 11:38 CLOSED @ 11:43 PRIMARY METERING BACK ON @12:34///VER/CRB IDCC DUP FOR ORIGINAL PART POWER OUTAGE XXXX
15324 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-08-05 12:39 | 2008-08-05 13:10 | 9 | 31 | 65417-1 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000301// 6T CHANCE FUSE INSTALLED SAT BROKE//COD 9// VER/DBM IDC XXXX
15325 | South Williamson | 3411401 | DEWEY | INEZ | 2016-02-05 11:01 | 2016-02-05 15:40 | 1 | 279 | 4677681 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIDDLE CUTOUT BROKE ON PRIMARY METERING POLE//NEED BIG BUCKET CREW ENROUTE// RELEASED BY CREW 079S01 CLOSED @ 1540//TOM VER/TOM L3/TOM
15326 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-06-03 10:32 | 2021-06-03 12:05 | 3 | 93 | 4662681 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUT-OUT ON POLE #191-C-72, WILL REPLACE WITH NEW C/O, ARR. AND BKT. ON AT 12:05
15327 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-09-02 20:07 | 2020-09-02 21:40 | 3 | 93 | 4422061 | 279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will replace////Replaced bad cutout and restored service @ 21:40///Send copy to Ryan Thornberry pole is burnt may need to write job to change pole
15328 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-07-24 17:42 | 2012-07-24 22:20 | 1 | 278 | 4816491 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIGHTNING STRUCK POLE. BLEW CUTOUT TO PIECES. WILL BE MANUAL REPAIR. NEED NEW CUTOUT AND FUSE. HOPE IT DIDNT DESTROY XFMR. UNSURE. LAM RELEASED BY CREW 077E05//COD 1
15329 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2019-10-19 15:54 | 2019-10-19 17:56 | 13 | 122 | 4169521 | 278 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | opened xfmr @ 17:43 closed @17:56 L3/HFP
15330 | South Williamson | 3411401 | DEWEY | INEZ | 2014-07-02 14:43 | 2014-07-02 19:21 | 1 | 278 | 4184011 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 XFMER///NEED 1 MAN AND BIG BUCKET///REPLACED BAD XFMER///CUST BACK ON @ 19:21///COMPLETE BR//COD 1// VER/DBM
15331 | Hazard | 3311103 | STINNETT | WENDOVER | 2021-02-27 16:30 | 2021-02-27 21:08 | 1 | 278 | 4263371 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 2 man crew with a big bucket and 25 KVA 19.9 Transformer. Transformer changed power restored at 21:08.
15332 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-05-28 20:05 | 2017-05-29 00:43 | 1 | 278 | 4877461 | 278 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED BAD CUTOUT/WITH ARMS/DETAILS IN ACESSMENTS RELEASED BY CREW 078S03--C PHASE OPEN UPON ARRIVAL--OPENED A & B PHASE APPX 22:51--MADE REPAIRS TO X ARMS---CLOSED ON 206-1100 AT 00:43---TBL TKT COMP--RMV///ORIGINAL OUTAGE RECORD/// VER/DKM
15333 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2018-01-30 20:07 | 2018-01-31 00:45 | 1 | 278 | 4785331 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 281-180 cutout broke, crew required. trucks ok Released by crew 078H04/on site RM power on @ 12:45 please close tic R MORGAN
15334 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-11-30 10:32 | 2018-11-30 14:45 | 2 | 253 | 4493541 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 40t fuse out due to bad dead end insulator on pole 1125-590 crew on the way opened other fuse @ 142040t fuse out due to bad dead end insulator on pole 1125-590 crew on the way. opened B phase up at 14:20. and after repairs closed C and B phase back in at 14:45 // C phase 1 customer B phase one customer
15335 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-10-26 16:30 | 2009-10-26 18:49 | 2 | 139 | 55883-1 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK REQUEST 32388598//141-200 BAD 10KVA NEED 15KVA TRUCK TO POLE RELEASED BY CREW 078S08/CREW ON SITE/FETR1930/VEM/REPAIRS MADE AND POWER RESTORED 1849/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
15336 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-02-11 18:20 | 2022-02-11 22:58 | 1 | 278 | 4475111 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I replaced a broken cutout on pole 55-A2-1017.
15337 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-12-12 12:21 | 2013-12-12 14:40 | 2 | 139 | 4156571 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD XFMR, CALLING FOR HELP VER/SEF L3/HFP
15338 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-11-15 06:17 | 2016-11-15 10:55 | 1 | 278 | 4101421 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LATTERAL FUSE CUTOUT FAILED. REPLACED CUTOUT AND RESTORED @ 10:55. SH VER/CRB L3/HFP XXXHFP
15339 | Hazard | 3303902 | LESLIE | WOOTON | 2015-07-05 16:23 | 2015-07-05 18:42 | 2 | 139 | 4723971 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR OUT ON POLE 415-123 , BAD CUTOUT . REPLACED . CLOSED XFMR FUSE @ 18:42 . VER/CRB
15340 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-07-31 08:41 | 2009-07-31 11:00 | 2 | 139 | 62184-1 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STIRRUP HAS BURNT OFF SPACER CABLE, CALLING FOR HELP IDC XXXX
15341 | Hazard | 3310502 | HADDIX | CANOE | 2021-11-05 10:22 | 2021-11-05 15:00 | 1 | 278 | 4059801 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | got bad 10kva 19.9 transformer, need 15 kva to replaced it manual up on side of hill about 40 yds Released by crew 077S05, REPLACED XFMR & CUTOUT
15342 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-12-20 15:07 | 2019-12-20 19:45 | 1 | 278 | 4173301 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA TRANSFORMER//repairs made and power restored at 1945
15343 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-05-08 12:52 | 2015-05-08 17:30 | 1 | 278 | 4403701 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED AND BURNT #2 SERVICE NEUTRAL IN TWO. RELEASED BY CREW 076S02INSULINK CONNECTION FAILED AND BURNT #2 SERVICE NEUTRAL IN TWO. REPLACING SERVICE.INSULINK CONNECTION FAILED AND BURNT #2 SERVICE NEUTRAL IN TWO. REPLACING SERVICE. ONLY ONE CUSTOMER AFFECTED REPLACED SERVICE AND RESTORED @ 17:30. SH// VER/ ADH
15344 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-12-26 13:46 | 2015-12-26 16:05 | 2 | 139 | 4562341 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP ON OLD STYLE CUTOUT. REPLACED DOOR AND RESTORED @ 16:05. SH// VER/ ADH
15345 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-12-19 13:16 | 2008-12-19 15:35 | 2 | 139 | 60361-1 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401101// OPENED PRIMARY TAP THAT FEEDS XFMRS 903-39, 903-38 AND FAULT POLE 44 AT 14:36 TO ISOLATE BROKEN CUTOUT. REPLACED CUTOUT AND RESTORED AT 15:35. SH VER/KEP L3/KEP IDCC CNT1 XXXX
15346 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-06-12 08:56 | 2010-06-12 11:15 | 2 | 139 | 60600-1 | 278 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER BAD CONNECTION AT XFMR . OPENED XFMR AT 10:55 TO MAKE REPAIRS ,RESTORED POWER AT 11:15//COD 2// VER/DBM
15347 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-04-27 10:06 | 2010-04-27 12:25 | 2 | 139 | 51925-1 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..NEED TO SEND RON RYE A COPY...XFMR HAS BEEN PUMPING OIL AND CROSSARM NEEDS TO BE REPLACED NEARLY BURNED INTO...BB//COD 2//EMAILED TO TECH// VER/DBM IDC XXXX
15348 | Pikeville | 3407101 | TOPMOST | DEMA | 2012-03-15 10:51 | 2012-03-15 13:10 | 2 | 139 | 4581881 | 278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT. LOOKS LIKE FUSE WAS BROKEN. PUT NEW FUSE IN CLOSED IN EVERYTHING OK.//COD 2// VER/DBM IDC XXXX
15349 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2021-11-13 09:58 | 2021-11-13 14:35 | 1 | 277 | 4087981 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Customer is mis-mapped. Correct transformer pole for this meter is 38820966A32769. Please correct. Fuse link on riser pole 38820966A30642 appears to have broke. ooONE CUSTOMER AFFECTEDoo Restored @ 14:35. sh/mdr complete
15350 | Paintsville | 3401101 | FALCON | FALC-OILS | 2021-11-11 17:38 | 2021-11-11 22:15 | 1 | 277 | 4080121 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed on 806-204. Replaced cutout and restored @ 22:15. sh
15351 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-12-20 09:03 | 2020-12-20 13:10 | 3 | 247 | 4788031 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required 279-88 cutout broke ,no truck access up on hill Released by crew 078S05,,,opened line fuse38830279000029 @ 12:55 to safely make repairs.. Released by crew 078H07
15352 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2015-05-28 13:20 | 2015-05-28 17:57 | 1 | 277 | 4476601 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA PER JOE MORELAND//TRUCK TO POLE//COD 1//CREW REQUIRED//CREW ON SITE/FETR1830/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1757/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
15353 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2011-08-06 20:43 | 2011-08-07 01:20 | 1 | 277 | 4673301 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7.2 K.V. TRANSFORMER IDC XXXX
15354 | Pikeville | 3409502 | BURDINE | LEVISA | 2021-08-24 15:03 | 2021-08-24 19:40 | 1 | 277 | 4145021 | 277 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 358-338//will need crew to assist Released by crew 074S02. CREW ON SITE, WILL CHANGE ALL 3 CUTOUTS WHILE IT IS OUT
15355 | Pikeville | 3407103 | TOPMOST | KITE | 2015-04-09 14:23 | 2015-04-09 19:00 | 1 | 277 | 4296911 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED : CUSTOMER CONTACTED AND CAN WAIT TILL 04-10-15 A.M., 15 KVA , 7.2 KV / 120/240 TRUCK ACESS RELEASED BY CREW 074S03//SERVICER CREATED OPS ORDER # 030741763 // COD 1// VER/DBM
15356 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2022-04-18 14:08 | 2022-04-18 18:45 | 1 | 277 | 4775901 | 277 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt up/repairs made. tre
15357 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-09-09 11:23 | 2011-09-09 16:00 | 1 | 277 | 4851331 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE THREE CUTOUT COD-1 ISO LF 37830023000168 VER/HFP L3/HFP IDC XXXX
15358 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-11-20 11:38 | 2017-11-20 16:15 | 1 | 277 | 4589091 | 277 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connections burnt into @ sec. pole 190-346 feeding customer service..neutral and conductor.repairs made../ per servicer only one customer affected/ ISO 37830190D10397/ CDO 1
15359 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-06-11 09:14 | 2018-06-11 13:51 | 1 | 277 | 4581761 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o @ 118a 97, big bkt by road Released by crew 078S07/arrived RM fuse in @13:51 please close tic RM
15360 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-09-07 18:50 | 2015-09-07 23:27 | 1 | 277 | 4211821 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED BROKEN CUTOUT ON 621-43 NO TRUCKS TO POLE LINECREW REQUIRED RELEASED BY CREW 078S11---CREW ON SITE---REPAIRED CUTOUT---TBL TKT COMP VER/ARN
15361 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-01-02 19:43 | 2010-01-03 00:20 | 1 | 277 | 57854-1 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3 MEN ,,POWER TEMP,,,, CUT IN CLEAR AT POLE RELEASED BY CREW 078H08... POWER TEMP HOOKED UP.. CHECKED VOLTAGE 122/245.. POWER RESTORED 12:20 RELEASED BY CREW 078H22 VER/LDA IDC XXXX
15362 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-06-14 17:32 | 2021-06-14 20:45 | 5 | 193 | 4749991 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 37820009C00163.i opened the line fuse up on pole 9C-32 @20:24.climbed up and changed cutout on pole 9C-163 threw that door in.then went back to line fuse on pole 9C-32 and got that door back in @20:45
15363 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-09-12 10:23 | 2008-09-12 15:00 | 1 | 277 | 61823-1 | 277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402802// XFORMER FUSE BLOWN NEED NEW DOOR .. 1 METER OUT FEEDS OLD HOUSE NOT OCCUPIED EXCEPT FOR COWS// REPLACED DOOR // COMPLETE. // VER/TOM IDC XXXX
15364 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2011-02-25 08:38 | 2011-02-25 13:15 | 1 | 277 | 61347-1 | 277 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER, POWER RESTORED.// VER/DBM IDC XXXX
15365 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-11-04 16:42 | 2020-11-04 17:51 | 4 | 69 | 4642381 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfmr is leaking to bad to leave. Non truck access have called for line crew to replace. No outge at this time but will be opening xfmr when crew arrives to replace. OFF@ 1642 ON@ 1751
15366 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-06-15 16:14 | 2008-06-15 18:32 | 2 | 138 | 65258-1 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE. HAVE TO CUT BRUSH TO GET TO POLE. T. GOBLE EN-ROUTE TO ASSIST. REPAIRS COMPLETE. SH//3410602//VER/CRB
15367 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-07-13 12:14 | 2012-07-13 13:46 | 3 | 92 | 4711351 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD BAD CUTOUT ON TRANSFORMER//COD 2
15368 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-04-24 22:08 | 2012-04-24 23:40 | 3 | 92 | 4705121 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | APPEARS FUSE BROKE /// GOING TO REFUSE /// POWER RESTORED @ 23:40 /// TREES ARE ALL OVER XFMR POLE PLEASE SEND COPY TO R/W IDC XXXX
15369 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-02-22 06:49 | 2014-02-22 11:25 | 1 | 276 | 4425331 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL BE DISPATCHED TO 1000 DAYSHIFT SERVICER. A PHASE CUTOUT GATE BURNDT INTO AT POLE 399-165, FOUND NO TROUBLE ON LINE, WILL TRY TO REFUSE. CHANGED GATE CLOSED BACK IN AT 11:25. VER/KEP
15370 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-10-13 12:35 | 2022-10-13 14:07 | 3 | 92 | 4023461 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR OPEN BAD LIGHTNING ARRESTER, servicer is enroute, power restored
15371 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-12-31 10:41 | 2014-12-31 12:59 | 2 | 138 | 4894631 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK IN SEC. SPLICE HEATED UP AND BURNED THE NEUT. IN TWO // BOTH CUST.S OFF SEC. POLE 49-74 ( MR. HUFFMAN & MS. GRANT ) STATED THAT THEY HAVE DAMAGES// REWORKED SEC. & SERVICES // 2/3 SEC. NEEDS UPGRADED TO 1/0 ALSO POLE 49-74 IS VERY ROTTEN AT THE TOP NEEDS REPLACED SOON // SEND TO PEGGY W AND CLIFF FREEMAN//ONLY 2 CUST OUT VER/CRB
15372 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-01-07 01:57 | 2018-01-07 04:15 | 2 | 138 | 4714281 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t transformer fuse out. looks like fuse melted looked sec and everything over fused up everything ok
15373 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-05-11 08:42 | 2009-05-11 11:00 | 2 | 138 | 59026-1 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNT UP, MAY HAVE TO REPLACE CUTOUT, POWER RESTORED KN//3308401//VER/CRB
15374 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2016-04-24 16:02 | 2016-04-24 18:20 | 2 | 138 | 4121671 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN WIRE SECONDARY BREAKER HAS PULLED APART AND BURNED DOWN ONE LEG IN THREE SPANS. I CAN CLEAR THIS UP AND GET THE POWER BACK. POWER RESTORED AT 18;20. VER/CRB
15375 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-10-18 10:49 | 2013-10-18 15:25 | 1 | 276 | 4946051 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BUSHING BROKE ON XFMR AND LEAKING OIL///NEUTRAL BROKE IN SERVICE DROP///NEED 10KVA 19.9 XFMR AND SERVICE DROP PUT BACK UP///NO TRUCK ACCESS//CAN ONLY GET PICKUP UP IN HOLLER// RELEASED BY CREW 079S01//OPS ORDER 034812710 CREATED TO COME BACK OUT ON THIS //CUSTOMER IS OK WITH WAITING UNTIL MONDAY PER ERIC MCCOY//COD 1// VER/DBM
15376 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-03-04 02:04 | 2022-03-04 06:40 | 1 | 276 | 4565301 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no reading on meter no crew required
15377 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-05-21 00:57 | 2009-05-21 03:15 | 2 | 138 | 54240-1 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER FAILED IDC XXXX
15378 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-02-26 16:11 | 2013-02-26 20:47 | 1 | 276 | 4854371 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ON SITE/FETR2130/VEM/POWER RESTORED 2047/PLEASE CLOSE TICKET/THANKS/VEM COD-1 ISO LF 39831124A48045 VER/HFP L3/HFP IDC XXXX
15379 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-11-24 22:54 | 2008-11-25 03:30 | 1 | 276 | 51909-1 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409003// CENTER PHASE CUTOUT BROKE ON PRIMARY RISER POLE. CHANGING ALL THREE. ALSO CHANGING OLD ARRESTERS. FUSES ARE 25T. PLEASE ADD SIZE TO MAP. REPAIRS COMPLETE. SH VER/JHM IDCC CDC83 XXXX
15380 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-06-01 20:41 | 2021-06-01 21:50 | 4 | 69 | 4656821 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed, will be making repairs// restored/ ISO 38831125D00072/ COD 4
15381 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2010-05-22 11:48 | 2010-05-22 16:24 | 1 | 276 | 66303-1 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35236066 // BAD 15KVA TRANSFORMER--NO TRUCK-SEND TO B FRALEY RELEASED BY CREW 078S07 COD-1 VER/HFP L3/HFP IDC XXXX
15382 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-11-19 08:53 | 2011-11-19 10:25 | 3 | 92 | 4092491 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK IDC XXXX
15383 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-07-16 17:09 | 2019-07-16 21:45 | 1 | 276 | 4717841 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | power restored at 21:45
15384 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-07-18 06:54 | 2011-07-18 11:30 | 1 | 276 | 4556791 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEC. RESER HAS BURNED OFF XFMR// WILL NEED 20 500 COPPER //4 , 2 HOLE PADS // BOLTS // 3 GROUNDING STRAPS RELEASED BY CREW 074H14//COD 1//ISO//FEEDER 3411801// VER/DBM
15385 | Cannonsburg | 3113601 | WORTHINGTON | CSX WELD SHOP | 2015-02-23 08:33 | 2015-02-23 13:09 | 1 | 276 | 4074231 | 276 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | TRANSMISSION 69KV STRUCTURE BR 42 BURNT DOWN. DE-ENERGIZING WORTHINGTON STATION. VER/SEF L3/HFP XXX
15386 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-12-02 19:26 | 2013-12-02 20:12 | 6 | 46 | 4094431 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE OUT//TRANSFORMER FUSE BLOWN... FUSE TAIL BROKE. POWER RESTORED. VER/CRB L3/HFP
15387 | Pikeville | 3451201 | BEEFHIDE | BEEFHIDE | 2013-01-28 18:40 | 2013-01-28 20:58 | 2 | 138 | 4749061 | 276 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | PH 3 34KV BUS POT TR AT BEEFHIDE STATION FAILED - SAME CUT IN CLEAR AND SECONDARY FEED TO PH 3 JUMPERED TO PH 2.EQUIP. IN STATION BAD. RELEASED BY CREW 074S01 //VER/GAH IDCC MCCDL CDC98 XXXX
15388 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-05-02 21:18 | 2020-05-03 01:54 | 1 | 276 | 4788721 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken 7.2 cutout manuel pole, need cutout only fiberglass t-bracket already there Released by crew 077S07..alll power restored @ 01:54 hrs..p.hicks/ ISO 38831107000031/ COD 1
15389 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-05-30 01:24 | 2008-05-30 06:00 | 1 | 276 | 52743-1 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400301//BAD 15 KVA XFMR ON POLE #38831100000130. WILL NEED A FORMAN & 2 LINEMAN . THIS IS A HAND JOB.COD-1 /DISCREPANCY FILED/ VER/KEP IDC XXXX
15390 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-01-14 22:08 | 2017-01-14 23:40 | 3 | 92 | 4299121 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-291 BAD CUTOUT 6T TRANS FUSE//COD 3 L3/HFP
15391 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2011-04-26 23:24 | 2011-04-27 04:00 | 1 | 276 | 65872-1 | 276 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON POLE, NEED FLAGMEN. VER/TOM L3/TOM IDC XXXX
15392 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2019-04-19 13:54 | 2019-04-19 18:30 | 1 | 276 | 4134701 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | i think we have a bad splice at pole 1145-c-225 or 1145-c-258//COD 1//
15393 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-06-18 23:42 | 2015-06-19 00:05 | 12 | 23 | 4606461 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | GOT A LOOP BURNT OPEN ON POLE 38830645000054 IN ORDER 4605081/ OPENING RECLOSER IN ORDER TO PUT LOOP BACK TOGETHER/ ISO 38830645000228/ COD 12/ VER/BOW AJB
15394 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-02-08 16:24 | 2021-02-08 21:00 | 1 | 276 | 4950131 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10KVA 7200 XFM// crew required// cust restored/ ISO 38820937000010/ COD 1
15395 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-06-24 13:42 | 2012-06-24 14:51 | 4 | 69 | 4957011 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD PULLED LOOSE REFUSED XMF APR CLOSE TICKET /// CCC TO 4 BASED ON CALLS ISO TF 38830454D47509 VER/HFP L3/HFP
15396 | Pikeville | 3407103 | TOPMOST | KITE | 2016-12-24 04:00 | 2016-12-24 08:36 | 1 | 276 | 4231881 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN .. REPLACED CUTOUT , ALL WORK COMPLETE / GXJ //COD 1//ISO 37830257009001//
15397 | Hazard | 3303902 | LESLIE | WOOTON | 2021-11-15 11:34 | 2021-11-15 16:10 | 1 | 276 | 4094951 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester--line fuse at 486-58 (1 COD)
15398 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-01-05 19:24 | 2020-01-05 20:56 | 3 | 92 | 4215751 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830211000222 broke c/o .. replaced-lat in at 20:56-allgood-ds010520
15399 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-04-09 07:47 | 2016-04-09 10:05 | 2 | 138 | 4073661 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE. REPLACED AND RESTORED @ 10:05. SH// VER/ ADH
15400 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-02-01 08:29 | 2019-02-01 09:38 | 4 | 69 | 4745921 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will make repairs/Changed broken cutout and restored service @ 09:38 L3/HFP
15401 | South Williamson | 3411401 | DEWEY | INEZ | 2013-04-12 09:57 | 2013-04-12 12:15 | 2 | 138 | 4003521 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNT OFF ON LINE FUSE CUTOUT. REPLACED STIRRUP AND HOT LINE CLAMP. RESTORED @ 12:15. SH//COD 2// VER/DBM IDC XXXX
15402 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-01-03 09:41 | 2015-01-03 10:50 | 4 | 69 | 4900111 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK1// COD 4// VER/ ADH VER/DKG L3/DKGXXXX
15403 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-04-21 07:54 | 2018-04-21 12:30 | 1 | 276 | 4260441 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Splice Burnt into on servicereplaced service/ ISO 37830124000036/ COD 1
15404 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-01-23 18:54 | 2021-01-23 23:30 | 1 | 276 | 4887461 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. cutout busted @9-D4-256, will be changing. Got cutout replaced and closed back in @2330.
15405 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2013-06-22 07:33 | 2013-06-22 09:05 | 3 | 92 | 4385011 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 66-126 BAD LA 10T FUSE /// COD-3 ISO TF 38830066000126 VER/HFP L3/HFP
15406 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-08-20 21:37 | 2016-08-20 23:55 | 2 | 138 | 4819511 | 276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE REPLACEING NOW .CUTOUT REPLACED BACK TO NORMAL VER/KEP
15407 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-02-05 19:00 | 2015-02-05 19:25 | 11 | 25 | H4994321 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING LINE FUSE TO REPAIR BROKEN 162-28 TO SAFELY REPAIR BROKEN CUT OUT/COD 13/OPENED LINE FUSE 162-28 19:00 CLOSED 19:25 CHGED TWO CUTOUTS LINE FUSE AND TRANS FUSE2+11/1844 ORIGINAL 2 CUS// VER/ADH L3/HFP XXX
15408 | Hazard | 3301101 | CHAVIES | CHAVIES | 2009-12-25 11:05 | 2009-12-25 12:00 | 5 | 55 | 50448-1 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FUSE BLOWN
15409 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-06-08 21:25 | 2022-06-09 02:00 | 1 | 275 | 4042471 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | rplaced broke 19.9 cutout
15410 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-07-24 06:39 | 2017-07-24 11:14 | 1 | 275 | 4170091 | 275 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAD BAD CONNECTION ON SERVICE NEURTAL VER/CRB L3/HFP XXXHFP
15411 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-06-01 18:35 | 2012-06-01 23:10 | 1 | 275 | 4869371 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA XMF 7200 RELEASED BY CREW 078S11/ENROUTE@20:15ARRIVED@21:50/FETR/23:30//JEH/POWER REST. @ 23:10/// 078H05 COD-1 ISO TF 38830454D26528 VER/HFP L3/HFP IDC XXXX
15412 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-04-01 10:25 | 2021-04-01 13:15 | 4 | 170 | 4410651 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke Trans cutout on pole 98-C-136,Going to get it changed and restore service..// opened line fuse and transformer @1240 ON@1315
15413 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-06-01 14:37 | 2008-06-01 19:12 | 1 | 275 | 53760-1 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402204// FUSE DOOR BURNT OUT ON POLE 1121-407. I WILL BE REFUSING. 80 T FUSE DOOR BURNT OUT THAT SERVES HYDROCARBON. PRIMARY METERING FUSE.//ISO// VER/DBM IDC XXXX
15414 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-07-04 07:55 | 2016-07-04 12:30 | 1 | 275 | 4520541 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED AND BURNT CROSSARM IN TWO ON DBL ARM DEADEND POLE. (DIFFICULT LOCATION) REPAIRED AND REPLACED CUTOUT. RESTORED @ 12:30. SH
15415 | South Williamson | 3411401 | DEWEY | INEZ | 2009-04-10 23:20 | 2009-04-11 00:15 | 5 | 55 | 51295-1 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ROGER MAYNARD OPENED FUSE TO SAFELY REPLACE CUT OUT ON ORDER 51251 VER/KEP L3/KEP
15416 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2020-12-18 18:45 | 2020-12-18 19:40 | 5 | 55 | 4785031 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burndt into @pole 48-A3-419, had to open trans. to resqueeze connections. Open @1845, closed back in @1940.
15417 | Hazard | 3303902 | LESLIE | WOOTON | 2011-05-05 09:55 | 2011-05-05 14:30 | 1 | 275 | 4011141 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA 120/240 RELEASED BY CREW 077S01//COD 1// VER/DBM IDC XXXX
15418 | Hazard | 3302704 | HAZARD | KENMONT | 2009-07-17 09:25 | 2009-07-17 14:00 | 1 | 275 | 52841-1 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEND TO CREW CALL JIM MULLINS FOR CREW INFO WILL NEED 30 OF 2/0 4 WIRE TWIST RELEASED BY CREW 077S04 VER/KEP L3/KEP IDC XXXX
15419 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-04-15 19:58 | 2020-04-15 20:53 | 5 | 55 | 4700501 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Opening xfmr to repair secondary/// Opened @ 19:58 and closed @ 20:53
15420 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2013-03-01 18:40 | 2013-03-01 23:15 | 1 | 275 | 4865831 | 275 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 SIDE OF UNDERGROUND SER. IS ONLY GETTING 105 VOLTS///CREW ENROUTE // MASSEY & LAYNE & RICK RAY1 SIDE OF UNDERGROUND SER. IS ONLY GETTING 105 VOLTS///CREW ENROUTE// SPLICE FAILED INSIDE CONDUIT// REPAIRED SPLICE// POWER IS RESTORED// NEEDS R2D2 SET AT FOOT OF POLE TO GET OLD SPLICES OUT OF CONDUIT UP POLE SEE H4865831 FOR 1 CUSTOMER VER/HFP L3/HFP IDC XXXX
15421 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-05-17 09:40 | 2022-05-17 14:15 | 1 | 275 | 4901351 | 275 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no rew required replaced connections
15422 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-04-05 13:30 | 2012-04-05 14:25 | 5 | 55 | 4650231 | 275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. REFUSED @ 14:25. SH // COD 5// VER/DBM IDC XXXX
15423 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2019-06-27 08:56 | 2019-06-27 13:30 | 1 | 274 | 4604841 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required
15424 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-12-25 20:41 | 2008-12-26 01:15 | 1 | 274 | 63950-1 | 274 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR# 27805470 // BAD LEG ON UNDERGROUND. RELEASED BY CREW 078S01 VER/LDA L3/KEP IDC XXXX
15425 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-05-30 04:46 | 2008-05-30 09:20 | 1 | 274 | 52747-1 | 274 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 3002001/ HAVE A BAD 50 KVA SINGLE BUSHING TRANSFORMER BAD IN A 3 PHASE BANK, ALSO LIGHTNING ARRESTING IS BAD TOO, THIS IS THE ONE ON THE SOUTH SHORE SIDE OF THE POLE, THE ONE WITH THE BAD ARRESTOR, NEED CREW TO CHANGE, THIS 120/208 BANK RELEASED BY CREW 078S06//COD 1// VER/DBM IDC XXXX
15426 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2018-05-23 13:43 | 2018-05-23 18:17 | 1 | 274 | 4402521 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE # 38830021D26644//NEED 35 FT OF 4 AUGHT SERVICE DROP WIRE//3 PHASE WIRE/crew on site/FETR1830/vem/one cust out/cust restored 1817/please close ticket/vem
15427 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-05-20 08:56 | 2019-05-20 13:30 | 1 | 274 | 4303761 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | crew on site making repairs FETR 13:00 LRM all pwr restored please close ticket
15428 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-07-28 15:26 | 2015-07-28 20:00 | 1 | 274 | 4952471 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 528-78 . NEED 1 MAN & BIG BUCKET . RELEASED BY CREW 075H04 REPLACED TRANSFORMER AND RESTORED POWER AT 20:00/ ISO 37840528000078/ COD 1/ VER/BOW
15429 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2009-09-24 21:53 | 2009-09-25 00:10 | 2 | 137 | 61786-1 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT-UP. TRYING TO GAIN ACCESS TO REPLACE (FENCE). NEED BIG BUCKET TRUCK TO REACH - DUTY SUPERVISOR NOTIFIED AND IS CALLING SOMEONE TO ASSIST. REPAIR UNDERWAY. REPAIRS COMPLETE. SH VER/ARN IDC XXXX
15430 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-09-14 14:41 | 2020-09-14 19:15 | 1 | 274 | 4462751 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM fuse is blown on pole 99-45,Will have to cut path to get to pole,We have a broke cutout on pole 99-45 going to have to climb to change..Restored service at 19:15.
15431 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2021-01-25 17:11 | 2021-01-25 19:28 | 2 | 137 | 4891441 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 104-91 will be making repairs/// Replaced bad cutout and restored service @ 19:28
15432 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2009-07-27 09:51 | 2009-07-27 14:25 | 1 | 274 | 60567-1 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA FEEDING LIGHT CIRCUIT/BY TRUCK-------- POWER ON @ 14:25 IDC XXXX
15433 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-12-23 12:56 | 2014-12-23 17:30 | 1 | 274 | H4877061 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 COD FROM BEGINNING//@ 1318 STEPDOWN OPENED COD 27// FUSE IS OPEN ON 524-168, POLE 524-221 BURNT OFF DUE TO BAD CUTOUT, LINECREW REQUIRED WILL NEED 4 MOEPADS TO REACH POLE WITH TRUCK RELEASED BY CREW 078S11 VER/CRB AJBC LCD38830524000168 SEE 4877061 FOR LF OUTAGE.
15434 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-12-07 14:48 | 2016-12-07 17:05 | 2 | 137 | 4175151 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WRAP PULLED OUT AND ALLOWED GUY TO LAY AGAINST HOT SEC COND AND NEUTRAL OPENING CSP XFMR. REATTACHED GUY TO ANCHOR, REPLACED 10 FT DAMAGED SECONDARY AND RESTORED XFMR TO SERVICE @ 17:05. SH VER/AWD L3/HFP XXXHFP
15435 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2017-05-04 13:10 | 2017-05-04 17:44 | 1 | 274 | 4745301 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SECONDARY POLE IS DOWN I CUT THE LOOPS TO DE-ENERGIZE THE SECONDARY. JOEY REED IS EN-ROUTE. UTILITY LOCATE TICKET #1075041001 RELEASED BY CREW 079S02. REPLACED POLE 38820963C00147 VER/AWD
15436 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2012-02-23 17:06 | 2012-02-23 21:40 | 1 | 274 | 4488731 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL BROKEN IN SERVICE DROP.GOING TO REPAIR SPLICE.NEUTRAL HAS PULLED OUT OF SLEEVE.CUSTOMER SAID SHE HAS DAMAGES.TREE LIMB WAS LAYING ON DROP.ONLY 1 CUSTOMER AFFECTED //VER/GAH AJB
15437 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-03-02 11:38 | 2014-03-02 16:12 | 1 | 274 | 4443551 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SINGLE ALL OUT RE-PLACED BROKEN FUSE LINK 6-T POWER RESTORED. VER/CRB IDC XXXX
15438 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-04-15 08:30 | 2019-04-15 10:44 | 6 | 134 | 4114211 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Porcelin arrester failed and burnt the riser to the xfmr cutout in two. Crew enroute to assist with big bucket truck. VERIFIED TIME PER VOICE RECORDER
15439 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-05-10 09:38 | 2016-05-10 14:12 | 1 | 274 | 4192121 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT POLE 1077-630 DUE TO BAD CUTOUT. POLE 1077-630 HAS 25KVA TRANSFORMER ON IT THAT SERVES THIS CUST//MDC MADE//COD 1 VER/CRB
15440 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-01-18 09:22 | 2022-01-18 13:56 | 1 | 274 | 4379821 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 202 buena vista dr bad hotleg underground service pole to house//crew required// Released by crew 078S09 Repairs made, restored at 13:56.
15441 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2010-06-28 20:08 | 2010-06-28 22:25 | 2 | 137 | 59934-1 | 274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OUT AND XFRM. FUSE OUT CLOSED LINE FUSE IN AT22:00 L/A BAD ON TRAN. REPLACING//COD 2// VER/DBM
15442 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-12-13 10:34 | 2021-12-13 12:05 | 3 | 91 | 4190991 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse melted out.changing
15443 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-08-15 22:01 | 2010-08-15 22:40 | 7 | 39 | 56180-1 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WR#36450128 POLE 20-6548 10T FUSE BROKE//VER/CRB
15444 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2018-11-13 13:47 | 2018-11-13 15:18 | 3 | 91 | 4395261 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR COD-3 ISO LF 38821016C00003 L3/HFP
15445 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-02-20 13:11 | 2022-02-20 17:44 | 1 | 273 | 4520411 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans open @ 237-C-205,Will be trying to get it back in.Trans open @ 237-C-205,Have a bad 34- 25 KVA Trans, will need someone to bring Trans..Trans open @ 237-C-205,Have a bad 34- 25 KVA Trans, will need someone to bring Trans..Made repairs and restored @ 17:44..
15446 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-08-05 01:03 | 2008-08-05 05:36 | 1 | 273 | 65185-1 | 273 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | 3308603//OFF DUE TO STATION TRANSFORMER FAILURE/WILL HAVE TO REMAIN OPEN UNTIL MOBILE IS INSTALLED VER/KEP IDC XXXX
15447 | Hazard | 3303901 | LESLIE | HYDEN | 2020-11-04 17:33 | 2020-11-04 19:04 | 3 | 91 | 4643791 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Open fuse @ 18:55 Closed @ 19:04
15448 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-01-23 14:55 | 2011-01-23 16:26 | 3 | 91 | 63729-1 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BAD POWER RESTORED AT 1626 CLOSE TICKET COD-3 ISO TF 38830620000060 VER/HFP L3/HFP IDC XXXX
15449 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-11-02 07:06 | 2015-11-02 11:39 | 1 | 273 | 4401971 | 273 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED A BAD NEUTRAL CONNECTION AT THE TRANSFORMER POLE. VER/CRB
15450 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-04-30 20:55 | 2015-04-30 22:26 | 3 | 91 | 4379901 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6 T FUSE BROKE.CHG FUSE./COD 3// VER/ ADH
15451 | Whitesburg | 3312902 | JENKINS | JENKINS | 2012-06-25 11:48 | 2012-06-25 13:19 | 3 | 91 | 4959951 | 273 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PUT NEW XFMR LEAD IN
15452 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-02-27 13:34 | 2012-02-27 14:13 | 7 | 39 | 4511451 | 273 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BROKEN HOT TAP LEAD. ////VER/CRB IDC XXXX
15453 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-07-31 09:29 | 2008-07-31 11:00 | 3 | 91 | 62707-1 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000901// RELEASED BY CREW 078S11//COD 3// VER/DBM IDC XXXX
15454 | Paintsville | 3409302 | KENWOOD | AUXIER | 2013-05-10 14:59 | 2013-05-10 16:30 | 3 | 91 | 4095571 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN LIGHTNING ARRESTER ON 882-410 TOOK OUT PHASE A LINE FUSE ON 882-253. REPLACED ARRESTER AND CLOSED LINE FUSE @ 16:30. SH COD-3 ISO LF 38830882A00253 VER/HFP L3/HFP IDC XXXX
15455 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-01-22 20:33 | 2009-01-22 20:54 | 13 | 21 | H59270-1 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3010601// HAD TO OPEN @ 39831148A00235 DUE TO TOP OF CUTOUT DOOR BURNING// THIS OUTAGED 77 CUSTOMERS// BAD CUTOUT// BACK ON @ 2054// ONLY 77 OUT ON THIS OUTAGE THE OTHER 13 WERE OUTAGED SEPERATELY/ VER/TOM L3/TOM
15456 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-08-18 14:39 | 2014-08-18 19:12 | 1 | 273 | 4380261 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 074H17.REFUSED XFMR. ALSO POLE#38831052B00086 DOES NOT HAVE A LINE FUSE ON IT// MADE MAP DESCREPANCY ADH// COD 1// VER/ ADH
15457 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2019-10-07 17:07 | 2019-10-07 18:38 | 3 | 91 | 4113511 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout , replaced cutot restored power at 18:38..
15458 | Whitesburg | 3409503 | BURDINE | JENKINS | 2015-02-05 10:55 | 2015-02-05 15:28 | 1 | 273 | 4992431 | 273 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IS BROKEN INTO IN SERVICE, I NEED BIG BUCKET TO REPAIR. THE CREW SAID THEY WOULD SEND THEIR BUCKET AS SOON AS THEY COULD. I PULLED THE CUSTOMERS METER UNTIL THE BUCKET GETS HERE RELEASED BY CREW 077S12/ BROKE WIRE RIGHT BESIDE TAPED SPLICENO REASON FOR WIRE TO HAVE BROKE OTHER THAN IT JUST FAILING/ ISO 37830358D00097/ COD 1/ VER/BOW L3/HFP XXX
15459 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-08-31 15:39 | 2021-08-31 20:12 | 1 | 273 | 4185981 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Vines has blown xfm fuse will re-fuse///Removed vines///Bad 25KVA 19.9 xfm Steve Ray is coming to change / restored @2012
15460 | Hazard | 3303901 | LESLIE | HYDEN | 2008-07-15 12:22 | 2008-07-15 16:55 | 1 | 273 | 52896-1 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3303901// RELEASED BY CREW 077S01 // VER/TOM IDC XXXX
15461 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2020-04-26 10:18 | 2020-04-26 14:51 | 1 | 273 | 4752261 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR IS BAD,NEED 25KVA///////////REPLACED XFR&RESTORED POWER,ALL OK AFTERWARDS
15462 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2013-08-01 11:09 | 2013-08-01 12:40 | 3 | 91 | 4612981 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE FUSE BLOWN ON 38831003D00060//WILL PATROL/BAD CUTOUT// CHANGED// POWER IS RESTORED// TIME ON 12:40 VER/KEP L3/HFP IDC XXXX
15463 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-07-19 16:02 | 2021-07-19 20:35 | 1 | 273 | 4935911 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke Trans Cutout,Going to Change it and restore service.Made repairs and restored at 20:35.//cod 1
15464 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-05-15 19:32 | 2020-05-16 00:05 | 1 | 273 | 4840151 | 273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 25 trucks ok Released by crew 078S03///replaced xfmr///closed in at 00:05///complete BR/ ISO 38830197000214/ COD 1
15465 | South Williamson | 3200302 | BELFRY | TOLER | 2015-03-30 18:18 | 2015-03-30 20:34 | 2 | 136 | 4244821 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT NO TRUCK APPROACH REPLACED BROKEN CUTOUT COD-2 ISO PO @ 38821063A00076 VER/HFP L3/HFP
15466 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-06-22 11:59 | 2022-06-22 14:15 | 2 | 136 | 4275331 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | repalcd broke cutout, pwer restored
15467 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-08-09 15:12 | 2010-08-09 16:20 | 4 | 68 | 51654-1 | 272 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RISER WIRE ON CENTER PHASE TRANSFORMER ON FIRE SECONDARY WIRE MELTED VER/HFP L3/HFP IDC XXXX
15468 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-07-09 20:08 | 2010-07-09 22:24 | 2 | 136 | 64439-1 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE IT WHEN RAIN SLACKS UP A LITTLE///////////////REPLACED CUTOUT,RE-FUSED AND RESTORED5 VER/HFP L3/HFP IDC XXXX
15469 | Hazard | 3301401 | COMBS | COMBS | 2016-05-23 08:19 | 2016-05-23 10:35 | 2 | 136 | 4250331 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830247D00609, REPLACING CUTOUT NOW., POWER RESTORED @ 10:35/ ISO 37830247D00609/ COD 2/ VER/BOW
15470 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-01-15 10:22 | 2022-01-15 11:30 | 4 | 68 | 4348191 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse broken, changing
15471 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2019-07-29 18:53 | 2019-07-29 23:25 | 1 | 272 | 4804971 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required 15 kva biggest material handler Released by crew 078S03
15472 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-05-13 21:34 | 2009-05-13 23:50 | 2 | 136 | 54222-1 | 272 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONN ON POLE IDC XXXX
15473 | Hazard | 3307301 | BULAN | ARY-HEINE | 2020-12-29 04:33 | 2020-12-29 09:05 | 1 | 272 | 4832321 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | / broke cutout/ manual pole/ servicer doesnt have material to replace/ will be crew required/ Broken 12KV cutout on pole 153-107, manual in a yard. Didnt have one on the truck to replace it with. Released by crew 077H20. restored 09:05
15474 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-07-23 21:35 | 2011-07-24 02:07 | 1 | 272 | 4605401 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFORMER 7200, TRUCKS TO POLE. RELEASED BY CREW 078S01/CREW ON SITE/FETR0300/VEM/POWER RESTORED 0207/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN
15475 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-06-16 18:44 | 2013-06-16 21:00 | 2 | 136 | 4350291 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9 CUTOUT AND ARRESTER APR AT 2100 CLOSE TICKET//COD 2// VER/DBM IDC XXXX
15476 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-09-30 11:12 | 2016-09-30 12:20 | 4 | 68 | 4948471 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED HOT TAP AT POLE 1032-105 FOR SAFETY ISSUES/. PUT FIRE OUT ,REPLACED CUTOUT & ARRESTOR. PULLED OFF AT11:12 ON AT 12:20/ ISO 38831032000105/ COD 4/ VER/BOW
15477 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2022-01-15 12:56 | 2022-01-15 17:28 | 1 | 272 | 4348541 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Linecrew required broken cutoout on arm. Released by crew 078S11 Crew on site. // xfmr on 38830454D17621 was one off has 1 customer on it // restored @1728
15478 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-06-06 09:09 | 2013-06-06 11:25 | 2 | 136 | 4227541 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE/ WILL REPLACEBAD CURRENT LIMIT FUSE POWER RESTORED KWB COD 2 ISO TF 115C-211 VER/SEF IDC XXXX
15479 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2022-08-14 14:21 | 2022-08-14 14:55 | 8 | 34 | 4738511 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Lugg burnt up on transformer. Put new lugg bolt in
15480 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-01-06 10:20 | 2014-01-06 14:52 | 1 | 272 | 4236151 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37820265B00364 BURNED OFF DUE TO CUTOUT FAILURE. CREW ENROUTE. CAN USE TRUCK RELEASED BY CREW 074S02 RELEASED BY CREW 074H08 LOWERED EQUIPT MADE REPAIRS R RAY//COD 1// VER/DBM
15481 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-07-28 12:16 | 2011-07-28 16:48 | 1 | 272 | 4633981 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CONNECTION BAD IN UG JUNCTION BOX. DUTY SUPERVISOR ENROUTE TO ASSIST. ONE CUSTOMER OUT BUT WILL NEED TO OPEN XFMR 38830979C00130 WHEN READY TO START. <<ONLY ONE CUSTOMER AFFECTED>> FOUND UG SERVICE CABLE BAD. OPENED XFMR @ 16:37, INSTALLED AUTO-XFMR AND CLOSED XFMR @ 16:48. SH RELEASED BY CREW 076S02//COD 1 + 8 IDCC TOF1637 XXXX
15482 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2018-05-03 17:29 | 2018-05-03 19:45 | 2 | 136 | 4303481 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xform cutout broke replace power restored 19:45/ ISO 39831147A00240/ COD 2
15483 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2018-02-17 15:12 | 2018-02-17 17:28 | 2 | 136 | 4855431 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | I cleared up the arrester but could not replace it. The pole is no truck and the arrester is close to the lower conductor on a vertical pole./ ISO 38821012D00013/ COD 2
15484 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2013-12-19 10:48 | 2013-12-19 15:20 | 1 | 272 | 4176141 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT RETORED CUST @ 1520 / // COD-1 ISO TF 37830535000025 VER/CRB L3/HFP
15485 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-03-11 17:28 | 2022-03-11 19:44 | 2 | 136 | 4601421 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed on 882-349. Replaced cutout and restored @ 19:44. sh
15486 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-11-27 14:37 | 2019-11-27 15:45 | 4 | 68 | 4087271 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will make repairs/// Replaced broken cutout and restored service @ 15:45
15487 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-12-01 16:43 | 2015-12-01 21:15 | 1 | 272 | 4500261 | 272 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NEED LINE CREW BAD UNDER GROUND NEED TEP./ CREW ON SITE TO INSTALL POWER TEMP ETR 22:00/ POWER TEMP INSTALLED AND CUST RESTORED AT 21:15.. NEED TO SEND NOTE TO TECH TO WRITE JOB TO REPAIR/REPLACE UNDERGROUND.. TICKET COMPLETE .. CAY/ ISO 38830117B00358/ COD 1/ VER/BOW
15488 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-04-18 17:23 | 2015-04-18 19:39 | 2 | 136 | 4332851 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED OUT,WILL REPLACE EITHER DOOR OR CUTOUT ITSELF////////HAD TO REPLACE CUTOUT//////CLOSED AND RESTORED,ALL OK AFTERWARDS// VER/ ADH
15489 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2018-09-04 11:56 | 2018-09-04 16:28 | 1 | 272 | 4041281 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout at 500-149///waiting on GF to evaluate dead tree inside work zone. rEPLACED BROKEN CUTOUT. APR AT 1628 CLOSE TICKET
15490 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-05-11 13:42 | 2016-05-11 14:50 | 4 | 68 | 4200691 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 374-16, REPLACED CUTOUT, RESTORED POWER AT 14:50. ISO 37830374C00016 COD 4 VER/AWD
15491 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-08-18 17:08 | 2010-08-18 21:40 | 1 | 272 | 57817-1 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED POLE 245-156 ISOLATED 1 CUSTOMER OUT FIRE ON 245-291/TRUCK OK LOWER HARDWARE ON POLE RELEASED BY CREW 078S03 VER/KEP L3/KEP IDC XXXX
15492 | Hazard | 3303902 | LESLIE | WOOTON | 2021-12-13 21:59 | 2021-12-14 00:15 | 2 | 136 | 4193441 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse pulled into. restored 00:15
15493 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-03-21 18:29 | 2022-03-21 20:45 | 2 | 136 | 4655551 | 272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced door
15494 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-01-14 22:47 | 2012-01-15 03:18 | 1 | 271 | 4261741 | 271 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG-- NEED PRC CREW -200 AMP SERVICE ALL ELECTRIC HOUSE--NEED POWER TEMP INSTALLED RELEASED BY CREW 078S07 T B & BABY NICK RESPONDINGBAD UG-- NEED PRC CREW -200 AMP SERVICE ALL ELECTRIC HOUSE--NEED POWER TEMP INSTALLED RELEASED BY CREW 078S07// INSTALLING POWER TEMPBAD UG-- NEED PRC CREW -200 AMP SERVICE ALL ELECTRIC HOUSE--NEED POWER TEMP INSTALLED RELEASED BY CREW 078S07// INSTALLING POWER TEMP// TOLD CUSTOMER WE WOULD BE BACK FIRST OF WEEK TO FIX UG VER/ARN IDCC CNT2 XXXX
15495 | Whitesburg | 3409503 | BURDINE | JENKINS | 2020-12-03 06:49 | 2020-12-03 09:20 | 7 | 151 | 4740711 | 271 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | customer experienced part power due to bad connection.. had to open transformer to make repairs // repaired connections and checked voltage to be good. open @ 9:00 closed @ 9:20
15496 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-12-09 12:25 | 2011-12-09 16:56 | 1 | 271 | 4164851 | 271 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED SERVICE DROP & CHECKED ALL CONNECTIONS .COUSTOMER STATES THEY ARE STILL SEEING A DROP IN VOLTAGE . CHECKED ALL CONNECTIONS & HAD 0 VOLTAGE DROP AT ALL CONNECTIONS. NEED TO HAVE RECORDING VOLT METER INSTALLED HERE. ///VER/CRB IDC XXXX
15497 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-06-20 13:45 | 2014-06-20 18:16 | 1 | 271 | 4122831 | 271 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 19.9KV LARRY LAWSON WILL WORK//COD 1 VER/CRB
15498 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-07-13 09:04 | 2016-07-13 13:35 | 1 | 271 | 4621951 | 271 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CREW COMMING TO MAKE REPAIRS, PLEASE SEND TO GEORGE WHITAKER RELEASED BY CREW 077S12 R EPLACED BAD ARRESTOR ON PL 423C-232 POWER RESTORED AT 13:35/ ISO 37830423C00077/ COD 1/ VER/BOW
15499 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2018-07-22 11:39 | 2018-07-22 16:10 | 1 | 271 | 4833891 | 271 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection @ entrance
15500 | Hazard | 3420001 | SOFT SHELL | VEST | 2015-03-09 22:34 | 2015-03-10 03:05 | 1 | 271 | 4174921 | 271 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE ON POLE # 37830108000023, CANNOT GET TO POLE, WILL NEED HELP//LINE FUSE CUTOUT BROKE ON POLE # 108-23, CANNOT GET TO POLE, WILL NEED HELP. OPENED RECLOSER AT 2;27, CLOSED AT 2;56
15501 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2017-07-15 10:00 | 2017-07-15 11:30 | 3 | 90 | 4127281 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PORCELIN LIGHTNING ARRESTOR FAILED///I GOT IT IN THE CLEAR WITH A STICK AND RESTORED POWER///COULDNT CHANGE BECAUSE PHASE WILL HAVE TO BE COVERED UP TO REPLACE//RESTORED AT 11:30//COMPLETE//EM 38821065D20198 VER/AWD
15502 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-07-27 21:30 | 2021-07-27 23:00 | 3 | 90 | 4969181 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Off at 2130 On at 2300 to make repairs to connection on secondary poleBad red to red at secondary pole
15503 | Hazard | 3303902 | LESLIE | WOOTON | 2016-06-28 11:55 | 2016-06-28 14:10 | 2 | 135 | 4494291 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT VER/AWD
15504 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-09-16 23:00 | 2008-09-17 00:30 | 3 | 90 | 64724-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE HAVE A 19.9 CUTOUT SERVING TRANSFORMER WITH 3 CUSTOMERS ON IT BREAKING DOWN. POWER IS STILL ON AT THIS TIME BUT I WILL HAVE TO OPEN IT LONG ENOUGH TO REPLACE CUTOUT VER/PDP IDC XXXX
15505 | Hazard | 3302703 | HAZARD | HAZARD | 2013-03-16 19:45 | 2013-03-16 20:00 | 18 | 15 | 4912321 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR WAS ARCKING. HAD LEAD LOOSE , NO POWER OUT OPENED XFMR @ 19:45 CLOSED BACK IN @ 20:00 ///VER/CRB L/3 CRB IDC XXXX
15506 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-03-05 12:32 | 2019-03-05 12:38 | 45 | 6 | 4953351 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPENED L/F 38830139D00091 TO ISOLATE ARRESTOR 38830140B00319//COD 45//TRANSFORMER 38830140B00319 WILL REMAIN OPEN UNTIL CUTOUT IS CHANGED//OFF @ 1232 ON @ 1238
15507 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-03-30 17:00 | 2009-03-30 18:30 | 3 | 90 | 63158-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | XFMR POLE ROTTEN. PUT TEMPORARY GUY ON IT UNTIL CREW CAN CHANGE OUT. OPENED XFMR 47 AT 17:00. CLOSED AT 18:30. SH//COD 3// VER/DBM IDC XXXX
15508 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-10-01 12:30 | 2015-10-01 17:00 | 1 | 270 | 4298931 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 19.9 D.E. INSULATOR ON POLE 37830318A00290, LINE FUSE OPEN ON POLE 37830318A00124, MANUAL POLE. RELEASED BY CREW 077S04 VER/CRB L3/HFP XXXHFP
15509 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-07-23 11:51 | 2017-07-23 13:21 | 3 | 90 | 4164221 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM. CUTOUT BROKEN ON POLE 121-337...REPAIRS MADE..RESTORED VER/CRB L3/HFP XXXHFP
15510 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-10-12 18:56 | 2014-10-12 19:50 | 5 | 54 | 4609631 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 162-160 6T FUSE BROKE SEND NOTE TREE AT THIS ADDRESS NEEDS CUST CUST COMP. COD-5 ISO TF 38830162C00160 VER/HFP L3/HFP
15511 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-01-23 21:15 | 2017-01-23 21:45 | 9 | 30 | 4324561 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING LINE FUSE TO REPAIR BROKEN CUOUT ON POLE 37830205A00269/ ISO 37830205A00225/ COD 9/ OPENED 2115/ CLOSED 2145/ VER/BOW // RELATED TO 4323751 = L3/HFP XXXHFP
15512 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-02-19 10:59 | 2015-02-19 11:53 | 5 | 54 | H4041871 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | AEP EQUIP FAILURE 600 AMP SWITCH FAILED ON POLE 45-4022 CREW REQ.//COD 19//CREW ON SITE/FETR1145/VEM/NEW SWITCH NOT COMPATIABLE SWITCH/NEW FETR1215/VEM/REPAIRS MADE AND POWER REST TO ALL 1153/PLEASE CLOSE TICKET/THANKS/VEM // A PHASE 17 CUST INITALLY OUT OPENED B & C 5 CUST (ON 17TH ST SIDE SEE H4041871) @ 1059 VER/HFP L3/HFP
15513 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2010-03-17 13:30 | 2010-03-17 14:15 | 6 | 45 | 51128-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND BAD TRANSFORMER DURING CONVERSION JOB CREW ENROUTE TO REPLACE VER/KEP L3/KEP IDC XXXX
15514 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-07-31 19:45 | 2014-07-31 20:00 | 18 | 15 | 4315271 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND A BAD CUTOUT, WHICH WAS THE LINE FUSE ON POLE 1146-206, TIME OFF WAS 1945, TIME ON WAS 2000, POWER IS RESTORED TO ALL CUST. CUSTOMER SAW ARC ON POLE 114-206, RELATED TO TICKET 4314951 COD 18//VER/ ADH
15515 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2010-03-22 07:26 | 2010-03-22 08:20 | 5 | 54 | 52549-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3312201/// STS34336584/// PRIMARY ROLLED OFF INSULATORWIRE OFF INS VER/JHM IDC XXXX
15516 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-11-06 06:18 | 2008-11-06 08:33 | 2 | 135 | 62558-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003// BAD CUTOUT/VER/CRB IDC XXXX
15517 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-02-14 18:15 | 2019-02-14 18:45 | 9 | 30 | 4795271 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew on site working/ open at 18:15 closed at 18:45
15518 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-06-04 12:08 | 2009-06-04 12:26 | 15 | 18 | 58385-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | //HAD TO OPEN LINE TO MAKE REPAIRS TO CONDUCTOR//SEE ORDER 57484-1//COD 7// VER/DBM
15519 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2018-09-13 20:15 | 2018-09-13 22:30 | 2 | 135 | 4094191 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 sec was burnted into, have rep maded, was not 11 cust just two at this loc all power restored at 2230 by amg
15520 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-12-10 06:20 | 2012-12-10 10:50 | 1 | 270 | 4455471 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED. CREW IS ENROUTE TO REPLACE ALL THREE CUTOUTS AS THEY ARE THE SAME TYPE. <<ONLY ONE CUSTOMER AFFECTED>> REPLACED CUTOUTS AND ARRESTERS AND CLOSED @ 10:50. SH COD-1 ISO TF 38830785B31218 VER/HFP L3/HFP
15521 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2021-02-02 20:45 | 2021-02-02 23:00 | 2 | 135 | 4931721 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke//cutout repaired power restored at 23:00//cod 2
15522 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-11-11 15:15 | 2016-11-11 17:30 | 2 | 135 | 4093651 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NEED LINE CREW TO SET NEW POLE ==== OLD POLE IS READY TO KICK OUT OF GROUND === NEED 45 POLE & TRANSF 10 OR 15 KVA CAN GET TRUCKS TO POLE === RELEASED BY CREW 077S03/ ISO 37830443000062/ COD 2 OPEN LINE FUSE ON POLE 443-62 AT 15:15 POWER RESTORED AT 17:30 REPLACED POLE/ VER/BOW
15523 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-10-06 19:00 | 2019-10-06 23:30 | 1 | 270 | 4103401 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kVA xfer.. crew inroute restored @ 2330
15524 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-04-27 20:00 | 2011-04-27 22:15 | 2 | 135 | 66636-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39733836 //CUST. STATED THAT POLE WAS BURNING WILL CHECKCUST. STATED THAT POLE WAS BURNING WILL CHECK// LINE FUSE CUTOUT BAD ALSO XFMR CUTOUT BAD// CHANGED BOTH CUTOUTS AND PUT POLE FIRE OUT COD-2 ISO LF 38831148000052 *(*&)(*&)(*&)(*&)(*&)(*& IDC DCMT XXXX
15525 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-10-14 10:00 | 2013-10-14 12:15 | 2 | 135 | 4934861 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT AND ARRESTER.//COD 2//ISO 38821090A00018// VER/DBM
15526 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-08-15 01:59 | 2010-08-15 02:17 | 15 | 18 | 55400-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OPENED BOTH FUSES ON POLE 45-61 AT 0159/MADE REPAIRS AND RESTORED BOTH FUSES AT 0217/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP L3/KEP IDCC TOF 8/14 XXXX
15527 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-06-14 08:45 | 2013-06-14 13:15 | 1 | 270 | 4326981 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD 15 KVA 19.9 120/208 ON C PHASE ON POLE 478-180. NEED LINE CREW TO REPLACE XFORMER TRUCKS TO POLE OK. XFORMER OK FOUND BAD CURRENT FUSE BAD , CHANGED IT OUT VOLTAGE GOOD.//COD 1// VER/DBM IDCC PN7086 XXXX
15528 | Hazard | 3309003 | JEFF | VIPER | 2021-11-22 17:00 | 2021-11-22 19:15 | 2 | 135 | 4116921 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Repaired neutral connection on weatherhead @ 19:15
15529 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-05-19 21:25 | 2019-05-20 01:55 | 1 | 270 | 4302091 | 270 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired service//found loose connection//
15530 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-02-22 18:15 | 2011-02-22 22:45 | 1 | 270 | 60287-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38903503 /// ETA 1850 WE WILL HAVE TO CHANGE XFMR ,TWO CUTOUTS, AND REWORK LOOPS ON THIS BUCK ARM POLE // SEE 60306-1 FOR BREAKER OUTAGE // COD-1 ISO TF 37830448C30114 VER/HFP L3/HFP IDC XXXX
15531 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-07-15 12:45 | 2008-07-15 17:15 | 1 | 270 | 53002-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303903//BAD 25KVA CSP RELEASED BY CREW 077S01 REPLACED XFMR P HICKMAN // VER/TOM IDC XXXX
15532 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-06-14 14:40 | 2018-06-14 19:10 | 1 | 270 | 4602311 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad manual 15 kva trans. on pole 24-B3-725, will need flaggers, 3 man line crew, and 7200 trans. and cutout. Rerouted line, reenergized service @1910.
15533 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-02-27 09:13 | 2008-02-27 10:43 | 3 | 90 | 50835-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308603//TOP OF POLE 400-263 IS BURNED OFF I ISOLATED TROUBLE ON POLE 400-217 CECIL SEXTON WILL FUSE LINE BEFORE COMING BACK ON MTN AND ALL CUST WILL BE BACK ON WE WILL REPAIR POLE REPAIRED POLE ALL CUSTOMERS BACK ON AT 1043 VER/HFP IDC XXXX
15534 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2017-01-23 21:06 | 2017-01-23 22:00 | 5 | 54 | 4324531 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 1123-4092 BAD LA 6T TRANS FUSE SEND NOTE TO RAYBURN NEED CUTOUT AND LA CHGED NO TRUCK TO POLE POWER BACK ON/ ISO 39831123C14092/ COD 5/ VER/BOW L3/HFP XXXHFP
15535 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-11-29 12:20 | 2008-11-29 13:50 | 3 | 90 | 52954-1 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 38830784C00121. XFMR FUSE ALSO BLOWN. BAD ARRESTER PROB CAUSE. CLEARED ARRESTER AND REFUSED XFMR AND 15T LINE FUSE ON POLE 784-121. PLEASE ADD FUSE TO MAP. SH//3409002//MADE A MDE//VER/CRB IDC XXXX
15536 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-07-11 08:40 | 2013-07-11 09:25 | 6 | 45 | H4505171 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE ,, STIRUP BURNED OFF A PHASE CHECKING LINE FOR POSSIBLE FAULT//COD 10 + 6// REPAIRED STIRUP AND RESTORED POWER AT 09:25// IDCC TOF623 CNT16 XXXX
15537 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-01-10 18:56 | 2017-01-10 21:11 | 2 | 135 | 4284581 | 270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO REQUIRED REPLACED CUTOUT CREW VER/CRB L3/HFP XXXHFP
15538 | Hazard | 3303901 | LESLIE | HYDEN | 2008-08-29 21:19 | 2008-08-30 01:48 | 1 | 269 | 57590-1 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER WILL GO GET ONE AND MATERIAL HANDLER TO REPLACE IT . REPLACED TRANSFORMER AND CHECKED VOLTAGE EVERYTHING OK VER/PDP IDC XXXX
15539 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-04-07 09:37 | 2009-04-07 14:06 | 1 | 269 | 50164-1 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT.//3404302/VER/CRB IDC XXXX
15540 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-07-29 16:58 | 2008-07-29 21:27 | 1 | 269 | 61905-1 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ,,,,,,25KVA,,,,7200V POLE IS NEW CONSTRUCTION SO SHOULD BE JUST A SWAP,,,IS TRUCK ASSISIBLE OFF OF MATTIE MAY HAVE TO BLOCK ROAD FOR A LITTLE BIT BUT IS LOW TRAFFIC. //WR#25492162/CREW ON SITE/FETR2115/VEM//VER/CRB IDC XXXX
15541 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-04-03 08:43 | 2017-04-03 13:12 | 1 | 269 | 4608321 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT.NEED BIG BUCKET..CALLED TIM MILLER.HE IS SENDING BIG BUCKET./ ISO 38830875C00472/ COD 1/ VER/BIW L3/HFP XXXHFP
15542 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-09-16 11:31 | 2008-09-16 16:00 | 1 | 269 | 64569-1 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400303// REPLACE 3 19.9 CUTOUT//COD 1//ISO 38831126A00190// VER/DBM IDC XXXX
15543 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-12-02 07:40 | 2013-12-02 12:09 | 1 | 269 | 4091821 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, NEED THREE NEW CUTOUTS AND ARRESTOR FOR 7200 RELEASED BY CREW 077S05 REPLACED CUTOUTS AND RESTORED POWER AT 1209 VER/SEF L3/HFP
15544 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2018-05-10 20:25 | 2018-05-11 00:54 | 1 | 269 | 4334751 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//VOICEMAIL//no crew required
15545 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-12-26 11:13 | 2016-12-26 15:42 | 1 | 269 | 4237871 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT,WILL CHECK AND RE-FUSE///////BAD 25KVA 7.2 XFR,NEED CREW.IS IN BACK YARD ON HILL,WILL NEED TO WINCH TO POLE////////REPLACED BAD XFR,ALL OK AFTERWARDS VER/CRB
15546 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-05-25 10:16 | 2020-05-25 14:45 | 1 | 269 | 4903031 | 269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed 19.9 cutout up on hill nta.need new cutout bracket as well.need 1 man,19.9 cutout and standoff bracket.replaced cutout restored power at 14:45/ ISO 37820009C00005/ COD 1
15547 | Hazard | 3310502 | HADDIX | CANOE | 2017-04-29 17:47 | 2017-04-29 22:15 | 1 | 268 | 4695711 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KV TRANSFORMER 19.9KV, NEED NEW TRANSFORMER 15KV AND NEW COTOUT AND BRACKET 19,9 KV ,2 MEN AND BIG BUCKET,WILL HAVE TO BLOCK SECONDARY ROAD, RELEASED BY CREW 077H07 CHANGED XFMROOO VOLTAGE GOODOOO077H18
15548 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2018-07-17 17:32 | 2018-07-17 22:00 | 1 | 268 | 4790261 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed and burnt pole top off. Crew enroute to assist. Made repairs - Restored @ 10:00. sh L3/HFP
15549 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-06-19 17:28 | 2008-06-19 18:35 | 4 | 67 | 50925-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001003// 6T FUSE APPEARED TO BE BROKEN//COD 4// VER/DBM
15550 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-11-24 09:17 | 2017-11-24 11:31 | 2 | 134 | 4599091 | 268 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired secondary connection complete/ ISO 38830206A31089/ COD 2
15551 | Pikeville | 3410602 | E.PRESTON | LANCER | 2013-03-23 15:26 | 2013-03-23 19:54 | 1 | 268 | 4950301 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 167 KVA 277/480 (SINGLE PRIMARY BUSHING/TWO SECONDARY BUSHINGS) XFMR IS BAD. CENTER XFMR IN THREE XFMR BANK. RELEASED BY CREW 076S02//COD 1// VER/DBM IDC XXXX
15552 | Pikeville | 3413402 | GARRETT | LACKEY | 2010-08-02 11:50 | 2010-08-02 14:04 | 2 | 134 | 60440-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN ... REFUSED TRANSFORMER, ALL WORK COMPLETE / GXJ//COD 2// VER/DBM IDC XXXX
15553 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2009-07-20 20:04 | 2009-07-21 00:32 | 1 | 268 | 50980-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3202202 ON SITE, XFORMER FUSE BLOWN, REFUSING IT, BAD 25 KVA XFORMER, CALLED R MARCUM FOR HELP, SEND TICKET TO JOEY REED RELEASED BY CREW 080S01 // WORK REQUEST - 30823164 IDC XXXX
15554 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-07-22 11:17 | 2019-07-22 15:45 | 1 | 268 | 4757931 | 268 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg connection was burned open @ xfmr.Made repairs and restored customer to full power
15555 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-02-21 10:06 | 2011-02-21 12:20 | 2 | 134 | 59666-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA // WR# 38878728 // POLE NO 91-D-294 BAD 10 KVA 7200 120 240 VOLT TRANSFORMER NEEDED,SINGLE BUSHING, READ VOLTAGE 136/PH TO GRD PH TO PH 270 NEEDS CHANGE RELEASED BY CREW 078S09//REPAIRS COMPLETE POWER RESTORED @ 12:20 J. HEMLEPP 078H05 (2 CUSTOMERS) //COD 2// ISO// VER/DBM IDCC PN480 XXXX
15556 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2020-08-22 15:58 | 2020-08-22 17:05 | 4 | 67 | 4357781 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer reconnected // need to have pole on 353-78 and 377-129 changed out soon, both in very bad shape// opened both xfers to change out secondary @ 1558 closed @ 1705
15557 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-07-06 14:33 | 2019-07-06 15:40 | 4 | 67 | 4666811 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED NO ANSWER/no crew required 6t fuse broken cutout
15558 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2019-12-24 22:54 | 2019-12-25 01:08 | 2 | 134 | 4180531 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | spoke with cust, meter is blank and neighbors are out // Tank mounted arrester failed blowing xfmr fuse. Removed blow arrester and restored @ 1:08. sh // cod 2
15559 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-01-29 15:57 | 2012-01-29 20:25 | 1 | 268 | 4302901 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA REPLACED XFMR//COD 1 VER/KEP IDC XXXX
15560 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2012-04-30 10:21 | 2012-04-30 12:35 | 2 | 134 | 4722761 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT ON POLE 393-8, BAD XFMR ON POLE 393-121, WILL ISOLATE XFMR CREW WILL REPLACE TOMORROW VER/KEP
15561 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-03-13 13:33 | 2021-03-13 15:47 | 2 | 134 | 4333981 | 268 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection on hot leg at secondary pole 858-B-258 had went bad. I made repairs and restored to full voltage @ 15:47
15562 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-06-04 21:56 | 2010-06-05 00:10 | 2 | 134 | 56989-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | AED CREATED REMOVE WHEN COMPLETED. VER/PDP IDC XXXX
15563 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2014-11-01 16:35 | 2014-11-01 17:42 | 4 | 67 | 4688311 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE OPEN ON POLE 353-168, FOUND NO TROUBLE, REFUSED AT 1742.// COD 4// VER/ ADH
15564 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-11-30 13:22 | 2010-11-30 15:36 | 2 | 134 | 61117-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO POWER OFF AT THIS TIME, WILL NEED TO REPLACE 2 CRACKED CUTOUTS WHEN CREW ARRIVES,//ISO 37830180000020//COD 3/ POLE # 180-20// VER/DBM IDC XXXX
15565 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-03-29 09:47 | 2020-03-29 14:15 | 1 | 268 | 4522691 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad neutral connection
15566 | Pikeville | 3407103 | TOPMOST | KITE | 2014-12-24 10:39 | 2014-12-24 15:07 | 1 | 268 | 4879191 | 268 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY SIDE OF CSP TRANSFORMER OPEN ON ONE LEG, TIM HALL TO SEND TRANSFORMER, CUTOUT AND ARRESTER, ONE MAN AND MATERIAL HANDLER / GXJ . ALL WORK COMPLETE / GXJ/ ISO 37830185000193/ COD 1/ VER/BOW VER/DKG L3/DKGXXXX
15567 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2009-07-31 18:32 | 2009-07-31 23:00 | 1 | 268 | 53828-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR# 31021498 BAD 200A UNDERGROUND METER BASE CHGED// VER/DBM IDC XXXX
15568 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2009-10-23 11:17 | 2009-10-23 15:45 | 1 | 268 | 66064-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP WR # 32347013 //..........CUSTOMER TO DROP LOAD AND WE ARE GOING TO DE-ENERGIZE PAD MOUNT XFMR AND CHECK BAYONET FUSES, WE HAVE ONE PHASE OUT ON THE SECONDARY SIDE........X3 BAYONET FUSE OUT, LOOKING FOR ONE IN THE OFFICE NOW....NO FUSES IN WHITESBURG, CHECKING HAZARD NOW, EXTENDING OUTAGE TIME. P.HICKS.......REPLACED BAYONET FUSE. ALL POWER RESTORED. 15:45HRS P.HICKS L3/HFP IDC XXXX
15569 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-03-13 08:52 | 2009-03-13 13:20 | 1 | 268 | 57928-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | PRIMARY METERING MAKING ARKING SOUND METER ELECTRICAN COMING TO TEST METERING BYPASS B PHASE VER/PDP IDCC FEC57 XXXX
15570 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-06-02 12:35 | 2013-06-02 17:03 | 1 | 268 | 4209211 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE BLOWN ON POLE 37830249A00021, BAD ARRESTOR ON POLE 37830249A00023, CUT ARRESTOR IN CLEAR ON CSP TRANSFORMER, POWER RESTORED AT 17:03 COD-1 ISO LF 37830249A00021 VER/HFP L3/HFP IDC XXXX
15571 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-07-27 21:36 | 2016-07-27 23:50 | 2 | 134 | 4694791 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING XFMR CUTOUT. RESTORED @ 23:50. SH VER/CRB
15572 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-01-19 08:18 | 2011-01-19 09:25 | 4 | 67 | 62573-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 38495460 // POLE 91-129 BAD CUTOUT DOOR 10T FUSE//COD 4// VER/DBM IDC XXXX
15573 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-10-09 16:26 | 2019-10-09 18:40 | 2 | 134 | 4125181 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 453-139 replaced and back on at 18:40
15574 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-04-01 13:59 | 2011-04-01 15:45 | 3 | 106 | 61145-1 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | //TOP OF XFMR POLE BURNT OFF DUE TO BAD XFMR CUTOUT. LIFTED HOTLINE CLAMP ON 38830810A00422 TO ISOLATE FAULT LEAVING XFMR ON THAT POLE ONLINE. CLOSED LINE FUSE ON 809-4 @ 15:20 RESTORING UP TO AND INCL 810-422. CREW WORKING TO MAKE REPAIRS. REPAIRS COMPLETE. RESTORED REMAINING CUSTOMERS AT 15:45. SH RELEASED BY CREW 076S02//VER/CRB IDC XXXX
15575 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-11-07 06:51 | 2013-11-07 09:05 | 2 | 134 | 4017641 | 268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE IS BAD. I AM GOING TO CHANGE IT. I FIXED TRANS. AND CLOSED IT IN AT 09:05 VER/CRB
15576 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-02-24 15:06 | 2018-02-24 16:35 | 3 | 89 | 4879121 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout broke on pole 818-27//repairs made//restored at 16:35//complete//em
15577 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-06-19 09:51 | 2010-06-19 11:20 | 3 | 89 | 51227-1 | 267 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FIXED SECONDARY LEAD ON TRANSFORMER; PWR RESTORED AT 1120 HRS; CLOSE TICKET COD-3 VER/HFP L3/HFP
15578 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2016-09-20 12:31 | 2016-09-20 14:00 | 3 | 89 | 4911981 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON TRANSFORMER BANK. VER/AWD
15579 | Whitesburg | 3314401 | MAYKING | ERMINE | 2020-04-02 15:01 | 2020-04-02 16:30 | 3 | 89 | 4555851 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout burnt upp.. will have to replace.. cutout replaced. power restored @16:30
15580 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-07-26 11:33 | 2009-07-26 16:00 | 1 | 267 | 66166-1 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3302701// BAD TR ON THIS POLE, CREW ENROUTE TO MAKE REPAIRS. IDC XXXX
15581 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2022-05-26 21:55 | 2022-05-26 23:24 | 3 | 89 | 4956091 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmer bad/no truck 25kva/send to B tackett. Released by crew 078S04,removed vines xfmr in @ 2324 please close ticket thanks.bt
15582 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-10-20 06:36 | 2011-10-20 08:05 | 3 | 89 | 4002221 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 8T FUSE BROKE. FUSED UP EVERYTHING OK. VER/KEP IDC XXXX
15583 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2011-08-21 11:53 | 2011-08-21 16:20 | 1 | 267 | 4735431 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT C PH, NEED CREW TO CHANGE OUT CUT-OUT ON POLE 21-3098 ONLY FEEDS OFFICE MAX, CALL MGR BEFORE WORKING RELEASED BY CREW 078S09//P TOLLIVER ON SITE WILL REPLACE ALL 3 CUT-OUTS//REPLACED 3 GALVANIZED CUT OUTS ALL 3 WERE BAD COMPLETE AT 16:20 P TOLLIVER// COD-1 ISO TF 38830021B33098 VER/HFP L3/HFP IDC XXXX
15584 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-02-08 15:51 | 2011-02-08 17:20 | 3 | 89 | 55379-1 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 845-246 HAS TOP BURNT OFF DUE TO BAD CUTOUT// CREW ENROUTE//REPAIRS MADE RESTORED AT 17:20//COMPLETE//EM//VER/CRB IDC XXXX
15585 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-08-14 17:46 | 2015-08-14 22:13 | 1 | 267 | 4135791 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200, 15KVA XMF TRUCK OK, LINECREW REQUIRED RELEASED BY CREW 078S11/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2213/PLEASE CLOSE TICKET/TANKS/VEM// VER/ ADH
15586 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-01-28 08:11 | 2017-01-28 09:40 | 3 | 89 | 4338251 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.DIFF LOCATION HOUSE BUILT AROUND POLE.CHANGING CUTOUT 38830874000042 VER/AWD L3/HFP XXXHFP
15587 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2014-03-13 14:13 | 2014-03-13 18:40 | 1 | 267 | 4489651 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST HAS PART POWER // LUG BURNT UP ON 25KVA 7.2 KV TR AND WILL REQUIRE MANUAL CREW // CREW ENROUTE @ 1635LUG BURNED UP ON TRANSFORMER CREW ENROUTE. COD-1 ISO TF 37820151000239 VER/HFP L3/HFP
15588 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2022-10-01 19:12 | 2022-10-01 20:41 | 3 | 89 | 4962641 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced door
15589 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2020-01-04 12:48 | 2020-01-04 17:15 | 1 | 267 | 4211161 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required 15kva trucks ok just around from mountain top church Released by crew 078S03 crew on site FETR 17:15 LRM pwr restored @ 17:15 please close Ticket LRM
15590 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-02-12 13:33 | 2016-02-12 18:00 | 1 | 267 | 4691421 | 267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED LINE CREW TO REPAIR RELEASED BY CREW 078S05 CREW ON SITE GOING TO CHANGE CUTOUT PWR RESTORED @ 18:00 ISO 38830329000129 COD 1 VER/AWD
15591 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-01-26 08:34 | 2013-01-26 13:00 | 1 | 266 | 4742421 | 266 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEE 4742621 FOR DETAIL OF THIS OUTAGE AND CORRECT POLE # VER/KEP IDC XXXX
15592 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-06-12 05:04 | 2018-06-12 09:30 | 1 | 266 | 4588361 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | spoke with customer, she was calling for her elderly father who is without power//several CB operations before this call came in//customer is unable to reset breakers or check meter//Dispatched in accordance with KYPCo Late Night Callout Guidelines.broken transformer cut out on pole 806-116.opened line on pole 806-204 to make repairs.open line at 8:20 // line fuse only served that one cust.
15593 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-07-04 18:28 | 2018-07-04 22:54 | 1 | 266 | 4723781 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer fuse out . will refuse xfmr.is bad will need 15 kva 19.9 120/240 1 man & material handler Released by crew 074S04
15594 | Pikeville | 3403001 | PIKEVILLE | CITY | 2010-07-15 21:11 | 2010-07-15 23:24 | 2 | 133 | 50734-1 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR TO RE-FUSE,,,,,ACTUALLY HAD TO REPLACE CUTOUT,DOOR WAS BURNED OUT,HAD NO REPLACEMENT DOOR.ALL OK AFTERWARDS VER/KEP L3/KEP IDC XXXX
15595 | Hazard | 3303902 | LESLIE | WOOTON | 2019-05-01 06:29 | 2019-05-01 08:42 | 2 | 133 | 4191381 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 7200 CUTOUT L3/HFP
15596 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2010-04-25 09:48 | 2010-04-25 12:01 | 2 | 133 | 50676-1 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 34818689 // XFORM. FUSE OLD BROKE RELEASED BY CREW 078H09 COD-2 VER/HFP L3/HFP IDC XXXX
15597 | Hazard | 3303902 | LESLIE | WOOTON | 2022-07-11 16:19 | 2022-07-11 20:45 | 1 | 266 | 4461841 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout
15598 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-04-21 13:31 | 2011-04-21 15:44 | 2 | 133 | 61748-1 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT COD-2 ISO TF 38830141A00170 VER/HFP L3/HFP IDC XXXX
15599 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-06-08 17:49 | 2019-06-08 22:15 | 1 | 266 | 4462701 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT TO REPLACE,BACK ON BANK&COVERED IN KUDZU.NEED BIG BUCKET,1 MAN.WILL REPLACE PORCELIN CUTOUT ALSO/////SNAKY AREA PER CUST////////CLEARED VINES,REPLACED CUTOUT&RESTORED POWER
15600 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-02-07 14:52 | 2016-02-07 17:05 | 2 | 133 | 4681791 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CORRECT XFMR POLE FOR THIS CUSTOMER IS 38830882B00006. FOUND SECONDARY RISER ON XFMR BURNT IN TWO DUE TO BAD CONNECTION. BOTH CUSTOMERS AFFECTED - REWORKED CONNECTIONS AND RESTORED @ 17:05. SH MD FILED VER/KEP
15601 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-02-11 13:19 | 2017-02-11 17:45 | 1 | 266 | 4386201 | 266 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD TRANSFORMER CONNECTION VER/CRB L3/HFP XXXHFP
15602 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-01-01 22:21 | 2014-01-01 22:59 | 7 | 38 | 4217621 | 266 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE SERVICE IS BURN,T AT SPLICE IN SERVICE, WILL NEED HELP CHANGING IT OUT ON HILLSIDE. WILL GET UP WITH KENNY TO GET HELP.OPENED XFMR C/O AT 22:21 POLE37830181B00012//// REPLACED SERVICE CLOSED XFMR AT 23:59 POWER RESTORED VER/KEP
15603 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-07-01 22:56 | 2016-07-02 03:22 | 1 | 266 | 4512831 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 420-131.REPLACED XFMR RESTORED POWER AT 03:22.. VER/KEP
15604 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2013-11-15 17:44 | 2013-11-15 22:10 | 1 | 266 | 4042431 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KV TRANSFORMER..NEED A LINEMAN AND BIG BUCKET....REPLACED ENERGIZED AT 22:10 VER/CRB
15605 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2011-06-21 08:34 | 2011-06-21 13:00 | 1 | 266 | 4360361 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA 19.9 XFMR. BUCKET TRUCK REPLACED XFMR R.RICE.//VER/CRB IDC XXXX
15606 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-05-29 07:59 | 2020-05-29 12:25 | 1 | 266 | 4926351 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Power restored @ 12:25
15607 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-01-30 07:32 | 2014-01-30 09:45 | 2 | 133 | 4327731 | 266 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER , SECONDARY LEAD BURNT OFF ON XFMR BANK ON POLE 448-360, MADE REPAIRS RESTORED POWER AT 09:45 VER/HFP L3/HFP IDC XXXX
15608 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-05-31 13:23 | 2009-05-31 15:36 | 2 | 133 | 54023-1 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOT TAP OFF 655-16 FEEDING 655-17..TOP OF POLE BURNING..BB//ISO 38830655A00016//COD 2// VER/DBM
15609 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-02-09 12:02 | 2019-02-09 14:15 | 2 | 133 | 4773621 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | eta 13:50 all pwr restored @ 14:15 please close ticket LRM broken fuse tail
15610 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2019-09-10 16:55 | 2019-09-10 19:08 | 2 | 133 | 4001271 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA. Can change with big bucket Released by crew 077H05bad 25 kva transformer ;changed transformer and restored power at 19: 08
15611 | Pikeville | 3409502 | BURDINE | LEVISA | 2014-04-27 13:47 | 2014-04-27 16:00 | 2 | 133 | 4639151 | 266 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE SECONDARY PHASE WIRES AT THE TRANSFORMER.//COD 2// VER/DBM
15612 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-02-11 00:14 | 2016-02-11 02:27 | 2 | 133 | 4688381 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE BURNT INTO AT CUTOUT ON POLE 398-113, OPENED LINE FUSE ON POLE 398-178 AT 01:29 TO ISOLATE ..MADE REPAIRS RESTORED POWER AT 02:25. - NO ADDITIONAL CUSTOMERS OUTAGED WHEN VER/TOM L3/TOM
15613 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2012-08-06 18:24 | 2012-08-06 22:50 | 1 | 266 | 4905181 | 266 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA 7200/ 277/480, 2.5 % IMP. ADD POLARITY, SINGLE BUSHING PRIMARY SIDE, ONE MAN AND MATERIAL HANDLER . REPLACED TRANSFORMER , ALL WORK COMPLETE / GXJ ///VER/CRB L/3 CRB IDC XXXX
15614 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-05-31 09:55 | 2008-05-31 10:14 | 14 | 19 | H53122-1 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3300602//PART OF 53122-1//A PHASE RECLOSER OPEN ON POLE #296-1477.... TWO SPANS PRIMARY BURNT DOWN//COD 46 ...WILL HAVE TO OPEN ALL 3 PHASES TO MAKE REPAIRS (WILL INTERRUPT 14 MORE CUST)//CHECKING FOR CAUSE//OPENED RECLOSERS AT 9:55 & CLOSED THEM AT 10;14...RESTORED POWER//FAILED QUICKSLEEVE WAS CAUSE// VER/DBM IDC XXXX
15615 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2011-10-12 13:07 | 2011-10-12 17:33 | 1 | 266 | 4970931 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20T LINE FUSE ON HILLSIDE/CREW REQUIRED BROKEN CUTOUT WILL HAVE TO OPEN 3 PHASE UP TO FIX MADE UP SOLID/NO TRUCKS/SEND TO FRALEY RELEASED BY CREW 078S03 ///VER/CRB IDCC FEC57 XXXX
15616 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-09-02 14:59 | 2013-09-02 19:25 | 1 | 266 | 4813601 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | #ABAD 15 KVA XFMR , NEED SOMEONE TO BRING XFMR,15KVA 7200//COD 1 VER/HFP L3/HFP XXXX
15617 | South Williamson | 3411401 | DEWEY | INEZ | 2014-11-02 07:34 | 2014-11-02 12:00 | 1 | 266 | 4691941 | 266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 19.9 XFMR ON POLE 838-142//NEED ONE MAN AND BIG BUCKET//XFMR REPLACED//RESTORED AT 12:00//COMPLETE//EM VER/SEF
15618 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-12-11 11:05 | 2008-12-11 15:30 | 1 | 265 | 56633-1 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401702// BAD TRANSFORMER CREW ENROUTE. RELEASED BY CREW 074S02 VERIFIED 1 CUSTOMER ON THE TRANSFORMER// VER/TOM L3/TOM IDC XXXX
15619 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-07-05 16:20 | 2015-07-05 20:45 | 1 | 265 | 4723961 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREES HAVE GROWN UP AROUND TRANS. AND TOOK OUT FUSE. I AM GOING TO REFUSE TRANS. CUTOUT IS BROKEN ALSO. I AM GETTING HELP TO CHANGE CUTOUT. WE CHANGED CUTOUT VER/CRB
15620 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-09-17 23:00 | 2018-09-18 03:25 | 1 | 265 | 4122681 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broke cutout/// apr at 0325 close ticket//cod 1
15621 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2019-06-28 15:10 | 2019-06-28 19:35 | 1 | 265 | 4613451 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | due to 2/3 sec burnt down at 91-c-363. repairs have been made closed transformer fuse back in at 19:35 everything ok. send copy to peggy in damage claims neutral and both hot conductors were burnt into cust could possibly call in damage. not sure what caused this connections looked to be good conductor may have had a bad place in it that made contact with the neutral burning wire down
15622 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-12-11 07:25 | 2008-12-11 11:50 | 1 | 265 | 56541-1 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3315051// REPLACED 7200 CUTOUT , ARR AND BRKT , POLE CHARRED BUT OK JEFF COMBS VER/TOM L3/TOM IDC XXXX
15623 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-09-29 15:05 | 2019-09-29 19:30 | 1 | 265 | 4071721 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRF IS OUT,WILL RE-FUSE//////CORRECTION,CUTOUT IS BROKEN,VERY CLOSE TO PRIM COND,NEED MATERIAL HANDLER,1 A LINEMAN,ALSO A 15KVA XFR JUST IN CASE XFR MIGHT BE BAD.
15624 | Hazard | 3303901 | LESLIE | HYDEN | 2018-02-13 21:30 | 2018-02-14 12:10 | 2 | 265 | 4838731 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 7200 cutout ///OPENED CUTOUT AT 2130 AND CLOSED AT 2155. WILL NEED 40FT POLE CHANGED OUT IN THE POLE, FIRE OUT BUT POLE BURNT HALF WAY THRU/crew required, hold till morning to change pole/ Released by crew 077Q02 /// ASK DENZIL ABOUT TIMES OFF & ON FOR 02/14
15625 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2019-12-23 12:10 | 2019-12-23 13:03 | 5 | 53 | 4177951 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot leg burndt up on pole 48-A4-385, will have to open trans. to make repairs, will keep track of times. Opened trans. @1210 made repairs and closed back in @1303.
15626 | Pikeville | 3409502 | BURDINE | LEVISA | 2010-03-09 14:22 | 2010-03-09 15:15 | 5 | 53 | 64324-1 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. FUSE LINK BROKE. I REFUSED TRANS. COD-5 VER/HFP L3/HFP IDC XXXX
15627 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2015-04-15 14:32 | 2015-04-15 18:57 | 1 | 265 | 4322721 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LF @ 46-176, BAD B PHASE CUTOUT @ 46-2318 RELEASED BY CREW 078S07/1 CUSTOMER AFFECTED/MAD MADE FOR CUSTOMER/ADH/CREW ON SITE/FETR2000/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1857/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830046B10176/ COD 1 CCC*** L3/DKGXXXC PN CLEARING DEVICE POLE WAS INCORRECT
15628 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-05-07 19:20 | 2014-05-07 23:45 | 1 | 265 | 4672491 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 XFMR ON POLE 770-150///NEED LINE CREW //CAN WORK WITH SQUIRT BOOM//XFMR CHANGED//RESTORED AT 23:45//COMPLETE//E//COD 1// VER/DBM
15629 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-01-11 08:14 | 2014-01-11 12:39 | 1 | 265 | 4271151 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 38831127A00305// REMOVED XFMR HOT TAP// REPAIRS MADE// POWER IS RESTORED//COD 3// VER/DBM L3/HFP HFPC PN165 CNT3
15630 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2018-12-19 16:32 | 2018-12-19 20:57 | 1 | 265 | 4580931 | 265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | FOUND BROKEN NEUTRAL IN A 200A 4/3 SERV DROP.MADE REPAIRS.WILL CREATE A JOB AND BRING SOME HELP&CHANGE SERV OUT TO 2/3.BROKE RIGHT AT A NEUTRAL SPLICE L3/HFP
15631 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-01-30 17:33 | 2019-01-30 21:58 | 1 | 265 | 4740381 | 265 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced bad connection in service drop.customer is not home ¦¦ L3/HFP
15632 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-05-08 12:47 | 2010-05-08 17:12 | 1 | 265 | 57869-1 | 265 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PARTIAL POWER AT MTR,WILL DETERMINE PROBLEM/////SERVE-IN CONNECTION BAD,REPLACED AND RESTORED TO NORMAL//VER/CRB IDC XXXX
15633 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-11-18 06:07 | 2011-11-18 07:35 | 3 | 88 | 4089181 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE ///VER/CRB IDC XXXX
15634 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-05-19 12:48 | 2017-05-19 15:00 | 2 | 132 | 4818951 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN ON 1057-25,WILL REPLACE IT/////////REPLACED CUTOUT&RESTORED/ ISO 38821057D00025/ COD 2 L3/HFP XXXHFP
15635 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-04-07 20:51 | 2015-04-08 01:15 | 1 | 264 | 4285951 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ POLE 181D-168 NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05 VER/TOM L3/TOM
15636 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-08-10 13:39 | 2018-08-10 14:45 | 4 | 66 | 4937881 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | New line fuse just installed this morning broke on 38830882D40998 (xfmr on 998 was not off). Outage affected 4 transformers. Restored @ 14:45. sh/ ISO 38830882D40998/ COD 4
15637 | Whitesburg | 3312901 | JENKINS | KONA | 2021-06-21 21:21 | 2021-06-22 01:45 | 1 | 264 | 4786681 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on primary metering, I need one man and a cutout to make repairs//cod 1
15638 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2008-12-29 08:13 | 2008-12-29 09:19 | 4 | 66 | 64834-1 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3417602//....JRV ON SITE @ 08:50......ONE HOT OPEN-WIRE SECONDARY BURNT DOWN....CAN REPAIR...XFRMER FUSE BLOWN ON POLE 38820965A00049....TOTAL OF 4 CUSTS OUT.....FETR OF 09:45...//....CONDUCTOR REPAIRED....RE-FUSED XFRMR......JRV...12/29/08 // VER/TOM L3/TOM IDC XXXX
15639 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-04-08 16:07 | 2010-04-08 16:40 | 8 | 33 | 61090-1 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR# 34589588 // 10T ME FUSE LINK BROKE//COD 8// VER/DBM IDC XXXX
15640 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-02-10 13:58 | 2014-02-10 16:10 | 2 | 132 | 4371121 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORM FUSE BROKE DOOR STILL IN REFUSE POWER RESTORED VER/CRB
15641 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-08-07 16:48 | 2010-08-07 19:00 | 2 | 132 | 51121-1 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SPLICE IN SECONDARY M.D.I. VER/PDP
15642 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-11-01 12:08 | 2020-11-01 14:20 | 2 | 132 | 4612971 | 264 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection at pole
15643 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-08-13 16:47 | 2021-08-13 18:15 | 3 | 88 | 4055861 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout all pwr restored 18:15
15644 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-05-14 18:21 | 2018-05-14 22:45 | 1 | 264 | 4349081 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 100 kva 19.9kv 120/240 two bushing can use truck . crew required Released by crew 074S07. Arrived at jobsite. Made repairs and closed back in at 10:45 Tim McCoy COD-1 ISO TF 38831125C40675
15645 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-12-30 18:01 | 2019-12-30 22:25 | 1 | 264 | 4197191 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA XFMR on 924-57. Crew enroute to pick one up in Paintsville. Replaced xfmr and restored @ 22:25. sh
15646 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-11-19 12:51 | 2015-11-19 17:15 | 1 | 264 | 4471641 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | XFM FUSE BLOWN ON POLE 265A-115 FEEDING ONE CUSTOMER..HAS OPEN WIRE SEC. THAT IS DECAYED GOING TO RE-PLACE SERVICE DROP..REPLACED SERVICE DROP.RESTORED @ 17:15 VER/CRB
15647 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-27 18:01 | 2019-06-27 22:25 | 1 | 264 | 4607751 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 19.9 xfmr on pole 768a-85//crew enroute//repairs made//restored at 22:25//complete//em
15648 | Hazard | 3420001 | SOFT SHELL | VEST | 2009-07-12 08:36 | 2009-07-12 13:00 | 1 | 264 | 62361-1 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP LINE FUSE OUT ON 108-40, 1 CUSTOMER, CUTOUT BROKE ON POLE # 108-40, CALLED P HICKMAN CREW TO COME TO ME COD-1 ISO LF 37830108000040 L3/HFP IDC XXXX
15649 | Hazard | 3303902 | LESLIE | WOOTON | 2020-04-02 15:55 | 2020-04-02 16:17 | 12 | 22 | 4555911 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened l/f ON POLE 37830389C00021 TO REPLACE CUTOUT ON POLE 37830389C00421//OFF @ 1555 ON @ 1617
15650 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2020-07-05 10:51 | 2020-07-05 15:15 | 1 | 264 | 4111681 | 264 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva, 120/208, 7200 by truck at the burnaugh baptist church Released by crew 078H03
15651 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-11-28 00:51 | 2010-11-28 05:15 | 1 | 264 | 60206-1 | 264 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411902 2/3 SERVICE DROP HAS MELTED FROM SECONDARY POLE BACK TO TRANS. POLE. I AM GOING TO CALL FOR HELP AND CHANGE SEC. AND SERVICE DROP TO 1/0. WE HAVE HAD TROUBLE HERE IN THE PAST WITH DAMAGES. WE CHANGED SECONDARY CONDUCTOR AND SERVICE DROP TO 1/0. VER/PDP IDC XXXX
15652 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2016-01-21 18:17 | 2016-01-21 19:45 | 3 | 88 | 4639421 | 264 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION FAILED ON 38830978A30446 CAUSING THREE CUSTOMERS TO LOOSE ONE LEG OF SERVICE. REWORKED CONNECTION AND RESTORED @ 19:45. SH VER/CRB
15653 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-06-21 16:05 | 2015-06-21 17:33 | 3 | 88 | 4630041 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE // POWER RESTORED// VER/ ADH
15654 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2012-04-08 22:21 | 2012-04-08 23:05 | 6 | 44 | 4655881 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | XFMR FUSE OPEN ON POLE 38830182B43509, FUSE DOOR HAD BEEN TRACKING OVER AND FINALY BURN UP. REPLACED DOOR, ALL POWER RESTORED, LINE FUSE WAS NOT OPEN. //VER/GAH IDCC FEC49 XXXX
15655 | Pikeville | 3410602 | E.PRESTON | LANCER | 2018-01-06 02:23 | 2018-01-06 04:35 | 2 | 132 | 4711151 | 264 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg on secondary burned into at xfmr pole//feeding toward 955-306//only 2 customers affected//repairs made//restored at 4;35//complete//em
15656 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-09-09 14:54 | 2009-09-09 15:16 | 12 | 22 | 57488-1 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RESEND -SEND TO V MULLINS--NEED 4/0 RISER WIRE-TRUCK OK RELEASED BY CREW 078S07//WR#31630634//CREW GATHERING MATERIAL AND SMALL BUCKET/FOREMAN CHECKING JOB/WILL TAKE OUTAGE TO MAKE REPAIRS/VEM RELEASED BY CREW 078H14078S07//WR#31630634//CREW GATHERING MATERIAL AND SMALL BUCKET/FOREMAN CHECKING JOB/WILL TAKE OUTAGE TO MAKE REPAIRS/VEM /XFMR OPEN AT1454 BACK IN AT 1516/REPLACED BAD CONNECTIONS ON POLE 45-2524/PLEASE CLOSE TI1// VER/TOM IDC XXXX
15657 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-06-12 22:45 | 2016-06-13 00:57 | 2 | 132 | 4340861 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANSFORMER// EMAILED PEGGY WYSONG VER/TOM L3/TOM
15658 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-08-15 15:16 | 2016-08-15 16:44 | 3 | 88 | 4780511 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 1057-C-98 REPLACED CUTOUT RESTORED POWER AT 16;44 VER/HFP L3/HFP
15659 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2018-03-14 09:16 | 2018-03-14 13:40 | 1 | 264 | 4013801 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 163-b-385. talked to cust they are running on generator will be ok to come back in the morning to replace transformer. i created an order iwa1 WR# 69025966 this will be worked on Released by crew 074S11/ ISO 37830163B20385/ COD 1
15660 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2015-02-17 22:42 | 2015-02-18 00:10 | 3 | 88 | 4037691 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE LOOKS LIKE IT BROKE. FUSED BACK UP EVERYTHING OK. VER/SEF L3/HFP XXX
15661 | Pikeville | 3407101 | TOPMOST | DEMA | 2018-11-07 18:21 | 2018-11-07 22:45 | 1 | 264 | 4377971 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | replace xfmr cutout and arrester pole 206 and refused line cutout pole 58, ALL WORK COMPLETE / GXJ L3/HFP
15662 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2021-06-09 10:14 | 2021-06-09 11:20 | 4 | 66 | 4695781 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO OUTAGE TILL TR WAS OPENED TO MAKE REPAIRS///Opened transformer on 69-d3-7058 @ 10:46, closed at 11:20. Connection burnt up on mast, and wire melted. No outage when i arrived
15663 | Hazard | 3309301 | VICCO | REDFOX | 2015-05-04 08:18 | 2015-05-04 10:30 | 2 | 132 | 4386901 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS ON XFMR, REPLACED ALL CONNECTIONS AND XFMR LEADS/COD 2// VER/ ADH
15664 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2017-09-01 18:33 | 2017-09-01 20:45 | 2 | 132 | 4319391 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT CHANGING..CHD BACK ON AT 20.45/ ISO 38830784D00275/ COD 2/ VER/BOW
15665 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2020-03-01 07:50 | 2020-03-01 08:56 | 4 | 66 | 4441711 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Lash cable needs replaced from 524-223 to 524-292. linecrew required. Released by crew 078S11///repairs made////complete BR -- 38830524000224 opened TR at 0750 to 0856 4 CC L3/HFP
15666 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-01-04 00:38 | 2022-01-04 03:26 | 3 | 168 | 4296601 | 264 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg burned in 2 at XFM, will have to open XFM to make repairs, will keep up with times// opened XFM @ 02:58 closed @ 03:26//cod 3
15667 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2018-01-25 20:09 | 2018-01-25 21:15 | 4 | 66 | 4774001 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
15668 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-06-24 03:34 | 2008-06-24 07:58 | 1 | 264 | 53323-1 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S11//3007903//VER/CRB IDC XXXX
15669 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-03-17 11:51 | 2010-03-17 16:15 | 1 | 264 | 51060-1 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 44-7027 2/3 SEC BURNT LOOSE ON POLE SEND TO LLOYD M. HAD CUST TURN MAIN OFF CK. WITH CUST AFTER REPAIRES MADE TO TURN MAIN BACK ON. RELEASED BY CREW 078S08 / W/R 34289173 COMPLETE @ 4:15 VER/KEP L3/KEP IDC XXXX
15670 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-10-03 09:38 | 2010-10-03 11:50 | 2 | 132 | 56379-1 | 264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT....POLE 34-C-1......WILL RE-FUSE....FETR 12:00....//....FUSE LINK HAD JUST BROKEN....NO FAULT....RE-FUSED....POWER ON....JRV....10/03/10//COD 2// VER/DBM IDC XXXX
15671 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-11-17 09:22 | 2012-11-17 13:45 | 1 | 263 | 4404581 | 263 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERV BURN INTO AT NEUT === CONNECTION HEATED UP AND MELTED INTO NEUT === REPLACED 4/3 SERV WITH 2/3 SERV === CUST HAS DAMAGES CUST TO CALL IN === POWER OK// VER/DBM IDCC PN141 XXXX
15672 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-12-06 13:17 | 2010-12-06 17:40 | 1 | 263 | 63617-1 | 263 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION VER/HFP L3/HFP IDC XXXX
15673 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-05-22 09:37 | 2018-05-22 14:00 | 1 | 263 | 4392251 | 263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required
15674 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-06-21 09:43 | 2009-06-21 14:06 | 1 | 263 | 53329-1 | 263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER OUT UP ON HILL IN TREES, TRANSFORMER BAD NEED TO CHANGE OUT, 3 MEN LINE CREW 25 KVA 7200 XMF SINGLE BUSHING. 3 MEN TREE CREW TO CUT BRUSH UP HILL. VER/ARN IDC XXXX
15675 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-12-06 18:37 | 2013-12-06 23:00 | 1 | 263 | 4109811 | 263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT,WILL REPLACE IT////////REPLACED CUTOUT AND RESTORED,ALL OK AFTERWARDS VER/CRB L3/HFP
15676 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-07-13 05:58 | 2020-07-13 10:21 | 1 | 263 | 4157421 | 263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.//// xfm. cutout broke on pole 147-261////will need flagging crew to make repairs..restored..
15677 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-02-11 12:37 | 2013-02-11 17:00 | 1 | 263 | 4809361 | 263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 7200V/25 KVA SINGLE PHASE XFORMER.3049 STRATTON FORK. 276.4V LEG TO LEG,134.5V LEG TO GROUND,TRUCK APPROACH. DOGS ON CHAINS RELEASED BY CREW 079M01 RELEASED BY CREW 079H06 ///VER/CRB L/3 CRB IDC XXXX
15678 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2009-07-26 13:52 | 2009-07-26 18:15 | 1 | 263 | 51480-1 | 263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, XFORMER FUSE BLOWN, REFUSING IT VER/KEP L3/KEP IDC XXXX
15679 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-07-18 16:47 | 2011-07-18 21:10 | 1 | 263 | 4559511 | 263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFORMER 7200, TRUCKS TO POLE. NEEDS LINE CREW. RELEASED BY CREW 078S01 COD-1 ISO TF 38830165D00251 VER/HFP L3/HFP
15680 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-02-15 10:08 | 2014-02-15 14:30 | 1 | 262 | 4389701 | 262 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN FROZE OUT, REPLACED CONNECTORS POWER RESTORED VER/HFP L3/HFP
15681 | Hazard | 3309301 | VICCO | REDFOX | 2019-08-04 14:44 | 2019-08-04 19:06 | 1 | 262 | 4839361 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TRANSFORMER ON POLE 37830350000006//COD 1//MADE MD//sent to claims//TRANSFORMER IS NOT SHOWING ON MAP
15682 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-02-07 05:54 | 2014-02-07 10:16 | 1 | 262 | 4365291 | 262 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS///////POOR SERVE-IN CONNECTIONS ON XFR POLE WAY BACK ON HILL,MADE NECESSARY REPAIRS,ALL OK AFTERWARDS COD 1. VER/SEF
15683 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-07-07 10:04 | 2022-07-07 12:15 | 2 | 131 | 4418091 | 262 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on XFM.//Will open xfm to repair.//Repairs made.//XFM off from 11:35 to 12:15
15684 | South Williamson | 3200302 | BELFRY | TOLER | 2012-08-15 11:04 | 2012-08-15 13:15 | 2 | 131 | 4939431 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE OUT ON C PHASE..POLE 990C1-483..ARRESTER BAD ON POLE 966D2-2708.//.REPLACED ARRESTER.RE-FUSED LINE..JRV..08/15/12 IDCC CNT1, PN2729 XXXX
15685 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-07-21 10:18 | 2021-07-21 14:40 | 1 | 262 | 4941651 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 20-55 will be getting help to make repairs
15686 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-07-07 16:10 | 2014-07-07 18:21 | 2 | 131 | 4201241 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VINES TO CLEAR,XFR TO RE-FUSE///////CUTOUT ON XARM BROKEN,NEED 1 MAN,BUCKET,CUTOUT,NOTE NEW FETR///////////REPLACED CUTOUT AND RESTORED POWER//COD 2// VER/DBM
15687 | South Williamson | 3411401 | DEWEY | INEZ | 2013-10-30 07:09 | 2013-10-30 09:20 | 2 | 131 | 4974331 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN ON POLE 743-100///GOING TO TRIMM SOME LIMBS AND REFUSE//FOUND CUTOUT WAS BROKE ONCE I GOT UP THERE//I REPLACED CUTOUT AND TRIMMED SOME LIMBS//RESTORED AT 9:20//THIS WHOLE TAP HAS TERRIBLE R/W//PLEASE SEND TO FORESTRY,NEEDS CUT//COMPLETE//EM. VER/SEF
15688 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-12-11 18:13 | 2013-12-11 20:24 | 2 | 131 | 4154601 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR FUSE IS OUT,WILL RE-FUSE///ACTUALLY,CUTOUT IS BROKEN,HANGING FRM HOT COND.NEED BIG BUCKET,1 A MAN////REPLACED BROKEN CUTOUT,ALL OK AFTERWARDS//COD 2// VER/DBM L3/HFP
15689 | Hazard | 3303901 | LESLIE | HYDEN | 2015-01-12 07:59 | 2015-01-12 12:21 | 1 | 262 | 4929431 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE RUSTTED OFF === ANCHER UNDER GROUND === INSTALLED NEW ACHOR === RELEASED BY CREW 077S03 REPLACED ANCHOE AND GUY ;;RESTORED POWER AT 12 21 VER/CRB L3/DKGXXXX PER VOICE RECORDER GUY BROKE AND FLIPPED ONTO TRANSFORMER RISER
15690 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-07-06 07:33 | 2009-07-06 11:55 | 1 | 262 | 51431-1 | 262 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WORK REQUEST # 30597525 //-1 FUSE OUT IN BANK--BAD 12KV --10KVA TRANSFORMER IN 120-208 WYW BANK-TRUCK OK-CALLING CREW--ALSO NEED 3 NEW CUTOUTS RELEASED BY CREW 078S07---CREW ON SITE, NEED TO REPLACE LA AND CO, ALSO REWORK HIGH SIDE RISERS COD-1 ISO 38830069A10111 L3/HFP IDC XXXX
15691 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-03-19 06:31 | 2018-03-19 08:42 | 2 | 131 | 4025401 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced all 3 cutouts 206-2491,,all power restored @ 08;42 Released by crew 078S05
15692 | Paintsville | 3410602 | E.PRESTON | LANCER | 2016-07-04 11:34 | 2016-07-04 13:45 | 2 | 131 | 4522031 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. REPLACED CUTOUT AND RESTORED @ 13:45. SH/ ISO 38830980000028/ COD 2/ VER/BOW
15693 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-03-06 14:09 | 2020-03-06 16:20 | 2 | 131 | 4456901 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutout broke will need help//Steve Ray is getting me 1 man/// Changed bad cutout and restored service @ 16:20
15694 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-09-15 21:00 | 2020-09-16 01:22 | 1 | 262 | 4467081 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad splice, burned service drop in two, will be making repairs. changed out service drop. customer is restored
15695 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-05-23 14:18 | 2011-05-23 18:40 | 1 | 262 | 4145571 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 40076637 // SEND BACK TO ME BAD 15KVA BRING 25 KVA RELEASED BY CREW 078S08 VER/KEP
15696 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-12-27 07:30 | 2011-12-27 11:52 | 1 | 262 | 4203941 | 262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED, BAD 25 KVA CSP 7200, COULD NOT RESET, ALREADY HAS CUTOUT, JUST NEED XFMR, TRUCK OK RELEASED BY CREW 078S05//POWER RESTORED AT 11:52 PTOLLIVER// ////VER/CRB IDC XXXX
15697 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-01-16 20:43 | 2009-01-17 01:04 | 1 | 261 | 56388-1 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308502//10 KVA XFMR BAD CALLING FOR 2 MAN CREW AND A 25 KVA 19.9 TRUCK ACCESIBLE RELEASED BY CREW 077S04...... REPLACED XFMR RESTORED POWER AT 01:04 / COD-1 / VER/LDA L3/KEP
15698 | Pikeville | 3408103 | SALISBURY | MARTIN | 2022-01-01 09:08 | 2022-01-01 10:35 | 3 | 87 | 4244361 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changed out broke cutout and got restored at 10:35
15699 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-01-30 09:44 | 2008-01-30 14:05 | 1 | 261 | 62086-1 | 261 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION ON HOT LEG OF SERVICE AT THE TRANSFORMER SINGLE COD ISO/FLT - 38821129B00182// IDC XXXX
15700 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-04-11 09:55 | 2013-04-11 11:22 | 3 | 87 | 4998361 | 261 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR , MADE REPAIRS RESTORED POWER AT 11:22 ///VER/CRB L/3 CRB IDC XXXX
15701 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-09-05 08:04 | 2012-09-05 12:25 | 1 | 261 | 4017041 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON POLE 43-28 CUTOUT CHG OUT REPLACED 6-T POWER RESTORED KWB COD-1 ISO TF 38830043000028 VER/HFP L3/HFP IDC XXXX
15702 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2009-05-30 20:03 | 2009-05-30 21:30 | 3 | 87 | 51980-1 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE 214-135. VER/PDP IDCC CNT3, PN134 XXXX
15703 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-05-25 21:54 | 2012-05-26 02:15 | 1 | 261 | 4832081 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SERVICE DROP BURNT DOWN TREES TRANS OFF 12;50 TO 2;15 AM //VER/GAH IDCC CNT1, TOF0050 XXXX
15704 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-06-30 17:21 | 2016-06-30 21:42 | 1 | 261 | 4507971 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRF IS OUT,WILL RE-FUSE//////////RE-FUSED&RESTORED,APPEARS FUSE ROTTED INTO COD-1 ISO TF 38821132000032 VER/HFP L3/HFP
15705 | Pikeville | 3408101 | SALISBURY | PRINTER | 2015-02-22 18:03 | 2015-02-22 19:30 | 3 | 87 | 4072821 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 6T FUSE BROKE FUSED UP EVERYTHING OK. SEND COPY TO ENG PIKEVILLE CHECK LOAD ON TRANSFORMER./ ISO 38831122000190/ COD 3/ VER/BOW
15706 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-09-09 10:54 | 2020-09-09 15:15 | 1 | 261 | 4444931 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink failed on weatherhead. Made repairs and restored @ 15:15. ooONLY 1 CUST AFFECTEDoo sh
15707 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-12-26 17:28 | 2022-12-26 18:55 | 3 | 87 | 4363441 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link broke. Correct line fuse pole # is 38830737000066 and its a 25T. Restored @ 18:55. sh
15708 | Pikeville | 3421001 | BREAKS | CITY | 2010-05-08 15:46 | 2010-05-08 15:55 | 29 | 9 | H57828-1 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIM COMING TO POLE 220-51 IS HOT BUT WHERE BRIDGE ST TAPS ON IS BURNED INTO IN THE CLEAR.DALE ENROUTE SHORTLY TO HELP.OPENED AT 220-61 TO REPAIR AT 15:46PM,CLOSED AND RESTORED TO ALL AT 15:55 IDCC DUP TO OPEN FUSE XXXX
15709 | Hazard | 3309302 | VICCO | JEFF | 2013-12-26 11:49 | 2013-12-26 16:10 | 1 | 261 | 4202271 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON PRIMARY METER POLE === CALLED FOR LINE CREW ==== RELEASED BY CREW 077S03CUTOUT BROKE ON PRIMARY METER POLE 37830299C00157 === CALLED FOR LINE CREW ==== CHANGED CUTOUTS ON PRIMARY METERING POLE === REFUSED LINE POWER OK//COD 1// VER/DBM L3/HFP IDC XXXX
15710 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-05-23 07:01 | 2011-05-23 11:22 | 1 | 261 | 4138161 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 40066582 /// CUTOUT BROKEN HANGING OFF POLE .3PH. BANK OF XFORMS. NEED LINE CREW AND BUCKET 3 NEW CUTOUTS. CUST STILL HAS PART POWER AT POST OFFICE NOTIFY THEM BEFORE OPEN OTHER 2 CUTOUTS RELEASED BY CREW 078S04//REPLACED 3 BROKEN CUTOUTS DATE ON CUTOUTS 04/98 POWER RESTORED P TOLLIVER// COD-1 ISO TF 38830118D16278 VER/HFP L3/HFP
15711 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-04-01 09:04 | 2010-04-01 10:31 | 3 | 87 | 56786-1 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED XFMR. SH COD-3 VER/HFP L3/HFP IDC XXXX
15712 | Hazard | 3310502 | HADDIX | CANOE | 2011-11-27 09:24 | 2011-11-27 13:45 | 1 | 261 | 4116871 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS BAD 15KVA 19.9 TRANSFORMER, NEED THREE MAN CREW .TRANSFORMER IS CROSS THE CREEK//COD 1// VER/DBM IDC XXXX
15713 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-01-18 13:06 | 2013-01-18 13:35 | 9 | 29 | 4672311 | 261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW FOUND CUTOUT ARCING HERE//OPENED FUSES IN ORDER TO REPAIR//COD 9// VER/DBM IDC XXXX
15714 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2022-08-08 18:49 | 2022-08-08 23:10 | 1 | 261 | 4706491 | 261 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 100kva 120/240 wye bank/truck ok Released by crew 078S04 Repairs made, closed at 23:10. Ticket complete.
15715 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-02-03 01:35 | 2011-02-03 03:45 | 2 | 130 | 53685-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CLF BAD---- REMOVED CLF REFUSED XFMR VER/ARN IDC XXXX
15716 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-10-21 18:50 | 2014-10-21 19:55 | 4 | 65 | 4650801 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT INTO @ POLE 183B-236CUTOUT DOOR BURNT INTO,REPAIRS MADE ALL CUST RESTORED @ 1955 PLEASE CLOSE TICKET THANKS.BT// COD 4/ VER/HFP L3/HFP
15717 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-02-14 16:34 | 2011-02-14 17:39 | 4 | 65 | 57423-1 | 260 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR CAME APART//VER/CRB IDCC MCCDL XXXX
15718 | Pikeville | 3311401 | REEDY STATION | DEANE | 2017-02-07 20:24 | 2017-02-07 22:34 | 2 | 130 | 4369731 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DKM/OPENED BREAKER AT 2024 DUE TO FAILED LOOP AT POLE 284-128 AND CLOSED BREAKER BACK AT 2234/// VER/DKM L3/HFP HFPC TOF2026
15719 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-03-25 17:00 | 2018-03-25 19:10 | 2 | 130 | 4104191 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burnt out on pole 38830880000059. changed door and closed fuse in at 19:10. to restore power..complete rn
15720 | Pikeville | 3413401 | GARRETT | GARRETT | 2017-09-01 09:50 | 2017-09-01 10:10 | 13 | 20 | H4315691 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT CRACKED ON POLE 17-12 OPENING LINE FUSES ON POLE 17-6 TO SAFELY MAKE REPAIRS.OPENED FUSES @ 9:50 AND CLOSED BACK IN @ 10:10 COD-15 ISO LF @ 37830017000006 VER/HFP L3/HFP
15721 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-06-25 18:00 | 2009-06-25 22:20 | 1 | 260 | 60478-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 15KVA, 25 WILL WORK,, TALK TO CUST ABOUT WHERE TO GO INTO POLE, MAT BUCKET OK, PULLED METER,CUST IS USING GENERATOR//WR# 30471550//COD 1// VER/DBM
15722 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-02-26 09:05 | 2011-02-26 11:15 | 2 | 130 | 63150-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR 38956202 // TRANSFORMER IS BAD ON POLE 1128-68. WE ARE GOING TO CHANGE TRANS. WE CHANGED A 15 TO A 25 KVA VER/TOM IDC XXXX
15723 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-10-02 10:58 | 2011-10-02 11:50 | 5 | 52 | 4940091 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE MELTED OUT. LINK MAY HAVE BROKEN. RE-FUSED @ 11:50. SH COD-5 ISO TF 38830833A00074 VER/HFP L3/HFP IDC XXXX
15724 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2021-03-23 19:43 | 2021-03-23 21:53 | 2 | 130 | 4367661 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connection
15725 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-12-19 09:53 | 2015-12-19 12:03 | 2 | 130 | 4544561 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER ON X-FMR CUT-OUT BLEW APART. WILL HAVE TO CLIMB AND REPLACE CUT-OUT AND ARRESTER. POWER RESTORED AT 12:03, 12/19/2015 VER/CRB
15726 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-03-31 08:05 | 2015-03-31 09:10 | 4 | 65 | 4245611 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULL INTO ON TRANSFORMER/ ISO 37830126D30253/ COD 4/ VER/BOW
15727 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-10-16 07:29 | 2010-10-16 11:49 | 1 | 260 | 60221-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER POLE 737-99. CALLED TIM MILLER. HE IS GOING TO SEND ONE MAN AND MATERIAL HANDLER TRUCK TO CHANGE TRASFORMER. RELEASED BY CREW 074S11// CREW ON SITE CHANGING POT TCM// TRANSFOMER WAS ON POLE 737-99 AND ONLY ONE CUSTOMER SERVED OFF THIS POLE TCM////VER/CRB IDC XXXX
15728 | Pikeville | 3421002 | BREAKS | GRASSY | 2017-11-03 15:52 | 2017-11-03 20:12 | 1 | 260 | 4527541 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad cutout on pole 37820221A40198/ ISO 37820221A40198/ COD 1
15729 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-05-04 05:15 | 2009-05-04 06:20 | 4 | 65 | 64966-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND TRANSFORMER FUSE AND ROTTENED AND BROKEN, HAVE IT REPLACED AND POWER IS RESTORED AT THIS LOC VER/KEP L3/KEP IDC XXXX
15730 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2018-01-02 17:15 | 2018-01-02 17:35 | 13 | 20 | 4699541 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired 2 hotleg connections, no outage until i pulled meter/ 1715-1735/ ISO 39831099D16021/ COD 13
15731 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-10-25 13:30 | 2008-10-25 17:50 | 1 | 260 | 58916-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP POLE BURNT ABOUT INTO. NEEDS CHANGED//// JEFF COMBS COMMING TO HELP CHANGE THIS OUT. REMOVED TAP OFF LINE AT 13:30 POLE 288-56. IDCC TOF1034 XXXX
15732 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-02-11 19:04 | 2022-02-11 23:24 | 1 | 260 | 4475341 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required; bad xfmr; rreplace with 25KVA, replace bracket and cutout (existing old box style cutout); truck ok; no flaggers Released by crew 078E02 .arrived RM xfm on @ 23:24 please close tic RM
15733 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2014-06-04 13:40 | 2014-06-04 14:45 | 4 | 65 | 4972741 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BADCUT OUT REPLACED BAD CUT-OUT POWER RESTORED KWB VER/CRB
15734 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-02-24 10:40 | 2013-02-24 15:00 | 1 | 260 | 4842941 | 260 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE WIRE BURNT INTO AT MASK .. MADE REPAIRS RESTORED POWER AT 15:00 ///VER/CRB L/3 CRB IDC XXXX
15735 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-12-28 11:04 | 2008-12-28 11:30 | 10 | 26 | 64559-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT TIME OFF 11.04 TIME ON 11;30// VER/ARN L3/KEP IDC XXXX
15736 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-09-26 18:50 | 2015-09-26 19:16 | 10 | 26 | 4275901 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BREAKING DOWN ON POLE 351-341. OPENED LINE FUSE @ 1850 (10 CUST - NO CUST OUT BEFORE) //CUT-OUT BREAKING DOWN ON POLE 351-341. CUT TOP OF POLE OFF AND REPLACED WITH A FIBERGLASS EXTENTION. REPLACED CUT-OUT. OPENED LINE FUSE ON POLE 351-175 AT 18:50 AND RESTORED POWER AT 19:16. 926/2015CUT-OUT BREAKING DOWN ON POLE 351-341. CUT TOP OF POLE OFF AND REPLACED WITH A FIBERGLASS EXTENTION. REPLACED CUT-OUT. COD-10 ISO LF 37830351C00175 VER/HFP L3/HFP
15737 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2014-01-01 23:30 | 2014-01-02 00:35 | 4 | 65 | 4217751 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | OLD FUSE BROKE, I REPLACED FUSE VER/KEP IDC XXXX
15738 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-09-19 08:02 | 2020-09-19 10:12 | 2 | 130 | 4477731 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad con. on xfmr pole
15739 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-11-17 08:35 | 2010-11-17 10:45 | 2 | 130 | 57360-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACING CONNECTION ON TRANSFORMER POLE//COD 2// VER/DBM IDC XXXX
15740 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-02-07 20:50 | 2019-02-07 23:00 | 2 | 130 | 4766011 | 260 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | nuetral broken in service drop.repaired nuetral restored power at 23:00
15741 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2022-11-28 07:25 | 2022-11-28 08:30 | 4 | 65 | 4194861 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED @ 0725service drop burned down.i opened transformer fuse on pole 1012A-31 at 07:25.il be making repairsservice drop burned down.i opened transformer fuse on pole 1012A-31 at 07:25.il be making repairs .i replace service wire and got transformer fuse on pole 1012A-31 back in at 08:30
15742 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2021-02-09 11:20 | 2021-02-09 13:30 | 2 | 130 | 4951561 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse
15743 | South Williamson | 3411401 | DEWEY | INEZ | 2021-06-09 14:38 | 2021-06-09 16:48 | 2 | 130 | 4697531 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr fuse out on 745-B-88/// Xfmr cutout was broke. I replaced and restored @ 16:48
15744 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-07-21 16:07 | 2015-07-21 20:27 | 1 | 260 | 4927731 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT IN PROCESS OF REPLACING CUTOUTS, REPLACED ONE CUTOUT AND TWO FUSES, OPENED XMF AT 2019 APR AT 2027 CLOSE TICKET COD-1 ISO TF 38830380000353 VER/HFP L3/HFP
15745 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-01-21 09:10 | 2020-01-21 13:30 | 1 | 260 | 4325011 | 260 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | appears that there is a loose connection inside xfmr. have called for crew & xfmr L3/HFP
15746 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-10-21 13:05 | 2017-10-21 15:15 | 2 | 130 | 4475481 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT AND REFUSED XFMR, ALL WORK COMPLETE / GXJ/ ISO 38830851C40760/ COD 2/ VER/BOW L3/HFP XXXHFP
15747 | Paintsville | 3410602 | E.PRESTON | LANCER | 2019-08-08 07:40 | 2019-08-08 12:00 | 1 | 260 | 4857301 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | MADE AED//Bad 4/0 UG svc - one leg open. Crew to install temp Auto Xfmr later today. Released by crew 076S02Bad 4/0 UG svc - one leg open. Crew to install temp Auto Xfmr later today. Released by crew 076S02..Palced auto xfmer on till repairs can be made
15748 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-11-29 09:20 | 2021-11-29 10:25 | 4 | 65 | 4131131 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 43-212/repairs made. pls close. tre /// also box truck hit line our neutral is in the phone line and low at pole 38830043000028 please sent to Pat to look at
15749 | Whitesburg | 3401301 | FLEMING | NEON | 2013-02-02 12:05 | 2013-02-02 14:15 | 2 | 130 | H4785731 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SLEEVE PULLED OUT AND BURNDT DOWN 2 SPANS OF OPEN WIRE SEC. BETWEEN POLES 332-45, 46, AND 48. WILL NEED 1 MAN AND SOME #4 COPPER TO PUT BACK UP. OPENED THIS TRANS. AT 12:05 AT POLE 46, WHILE MAKING REPAIRS.PUT SEC. BACK UP, CLOSED TRANS BACK IN AT 14:15 //VER/GAH IDCC DUP TO OPEN TRANSF XXXX
15750 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-01-13 10:15 | 2016-01-13 11:07 | 5 | 52 | H46155111 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE B PHASE OCR OPEN//110 CC// POLE 19-33 6A PRI. DOWN REC. OPEN 44-606 4:10 RELEASED BY CREW 078S08//LOOP BURNT OPEN 19-33/DIFFICULT LOCATION/FETR1230/VEM/CREW ON SITE/NEW FETR 1130/VEM//1002 GAVE V MULLINS PERMISSION TO REPLACE DDC HOLD TAG ON POLE 19-33 WITH HIS OWN//SEE DOL CASE 631660 FOR SWITCHING//SEE ALSO ORDERS 4615781 & 4616601// AJB
15751 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-01-17 12:55 | 2022-01-17 15:05 | 2 | 130 | 4372581 | 260 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4cu primary riser broken at xfmr bushing---replaced and repaired--voltage good---pwr restored @ 15:05---tbl tkt comp--rmv
15752 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-02-13 19:05 | 2011-02-13 21:15 | 2 | 130 | 56612-1 | 260 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS//////BAD CONNECTIONS ON XFR POLE(2 CUSTS),REWORKED ALL CONNECTIONS AND RESTORED,ALL OK AFTERWARDS //VER/GAH IDC CHANGED START TIME FROM 1905 DIM LIGHT WAS FIRST CALLXXXX
15753 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-12-17 11:45 | 2010-12-17 12:50 | 4 | 65 | H53189-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN WIRE SECONDARIES BURNT DOWN....ONE HOT LEG DOWN....BURNT DOWN UNDER A CONNECTION ON POLE 32-C-47...HAVE BURNT PHONE CABLE DOWN ALSO....WILL PULL XFMR OFF ON POLE 32-C-46....CAN PROB REPAIR WITH OUT CREW...//....PULLED OFF @ 11:45....REPAIRED CONDUCTORS...CLOSED XFMR @ 12:50....JRV...12/17/10//VER/CRB IDCC DUP TO OPEN TRANSFORMER XXXX
15754 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2009-01-23 06:30 | 2009-01-23 08:40 | 2 | 130 | 59287-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3116701// FUSE LINK IS BROKEN POWER SHOULD BE RESTORED BY 08;40AM COMP,KWB VER/KEP L3/KEP
15755 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-03-10 20:05 | 2015-03-10 22:15 | 2 | 130 | 4180361 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830172C00157 . CUTOUT IS FOR TAP.BAB CUTOUT ON POLE 172C-157 . CUTOUT IS FOR TAP.CLOSED LINE FUSE @ 22:15 POWER BACK ON . SEND TO DOUG C. POLE HAS 2 CROSS ARMS 1 IS BURNED INTO . WILL BE OK UNTILL CREW CAN GET TO JOB , BUT NEEDS CHANGED. VER/CRB
15756 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-06-28 10:05 | 2010-06-28 14:25 | 1 | 260 | 58870-1 | 260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200 15 KVA. XFORMER ON POLE 261-70, NEEDS LINE CREW TRUCKS TO POLE. CLOSE GATE , CATTLE. ADDRESS 21813 RELEASED BY CREW 078S01/ J. HEMLEPP & CREW ON SITE. REPAIRS COMPLTED, CUST RESTORED @ 14:25///// VOLTAGE AT METER 119/238 IDC XXXX
15757 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-11-29 15:39 | 2013-11-29 16:16 | 7 | 37 | 4087561 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SECONDARY HAS BURNED DOWN AGAIN BETWEEN POLE 38821014C20332 AND THE CHURCH BUILDING. WE ARE GOING TO REPLACE THE 1/0 CONDUCTOR WITH 4/0. TRANSFORMER FUSE DID NOT BLOW, BUT WE WILL OPEN IT TO REPLACE THE SECONDARY CONDUCTOR WHEN WE GET READY. OPENED TRANSFORMER UP AT 15:39, AND CLOSED BACK IN AT 16:16. VER/CRB IDC XXXX
15758 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-01-18 05:50 | 2012-01-18 10:09 | 1 | 259 | 4271861 | 259 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS//////BAD CONNECTION AT XFR POLE,RE-WORKED ALL.ALL OK AFTERWARDS VER/KEP IDC XXXX
15759 | Hazard | 3309003 | JEFF | VIPER | 2017-02-07 16:41 | 2017-02-07 21:00 | 1 | 259 | 4367831 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 368-38 , NEED 2 MEN , 1 A LINEMAN , 1 ASSIST . NEED 25KVA XFMR 19.9 , CAN WORK POLE WITH BUCKET . RELEASED BY CREW 075H04..CHANGED OUT XFMR. ALL POWER RESTORED @21:00..P.HICKS 37830368000038 COD 1 VER/AWD L3/HFP XXXHFP
15760 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-12-21 18:45 | 2022-12-21 23:04 | 1 | 259 | 4285031 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 7200 cutout not by truck. gat has aep lock on it Released by crew 078S12///repairs made///Complete BR
15761 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-06-23 14:58 | 2012-06-23 15:05 | 37 | 7 | 4954521 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED RECLOSER @ 1458 TO REPAIR LOOP // ON @ 1505 // COD-37 ISO OCR @ 38830117A00011 VER/HFP L3/HFP AJB INLT CUST CALL WAS FLICK LGHT ONLY.
15762 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-07-12 15:40 | 2022-07-12 19:59 | 1 | 259 | 4467721 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva 7200 truck accesbile crew on site FETR 20:30 LRMBad 25kva 7200 truck accesbile all pwr restored 19:59 please close ticket LRM
15763 | Hazard | 3310502 | HADDIX | CANOE | 2014-04-02 08:11 | 2014-04-02 12:30 | 1 | 259 | 4554581 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT. OPEN LINE FUSE ON POLE #37830074000010 AT 1148 AND CLOSED AT 1230 VER/CRB IDCC PN10, XXXX
15764 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-03-12 15:41 | 2015-03-12 20:00 | 1 | 259 | 4188011 | 259 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED SECONDARY ONLY ONE CUST AFFECTED.//COD 1// VER/DBM
15765 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-11-28 20:02 | 2010-11-29 00:21 | 1 | 259 | 60357-1 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#37894183 BAD 15 KVA BRING 25 KVA TRUCK TO POLE RELEASED BY CREW 078S08/CREW ON SITE/FETR0130/VEM/REPAIRS MADE AND POWER RESTORED 0021/PLEASE CLOSE TICKET/THANKS/VEM VER/PDP IDC XXXX
15766 | Hazard | 3303902 | LESLIE | WOOTON | 2011-04-06 16:51 | 2011-04-06 21:10 | 1 | 259 | 50909-1 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED BAD 10 KVA XFRM AND CUTOUT, WITH 15 KVA. COD-1 ISO TF 378304860000134 VER/HFP L3/HFP IDC XXXX
15767 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-09-10 20:54 | 2015-09-11 01:13 | 1 | 259 | 4226661 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 KVA XMF TRUCK OK LINECREW REQUIRED/ ISO 38830453000184/ COD 1BAD 19.9 KVA XMF TRUCK OK LINECREW REQUIRED RELEASED BY CREW 078S11/CREW ON SITE/FETR0200/VEMBAD 19.9 KVA XMF TRUCK OK LINECREW REQUIRED RELEASED BY CREW 078S11/CREW ON SITE/FETR0200/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0113/PLEASE CLOSE TICKET/TANKS/VEM VER/SEF
15768 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-02-04 17:47 | 2017-02-04 22:06 | 1 | 259 | 4358861 | 259 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP ABOUT TO BURN INTO MID SPAN PER AEP EMPLOYEE NEED 75 FT 4/0 TRIPLEX,4 GRIPS,4/0 T0 350 OR 500 SQUEEZES(3),PRESS,1 A LINEMAN,BUCKET TRUCK///////////MADE REPAIRS&RESTORED ////////LOOSE SPLITBOLT LET SERV DROP HEAT UP AND LOOSE ONE LEG,REPLACED 4/0 SERVICE/// VER/DKM L3/HFP XXXHFP
15769 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-03-20 09:05 | 2018-03-20 13:24 | 1 | 259 | 4029751 | 259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | top of pole burnt off, J. combs crew coming to repair Released by crew 077S02repairs made and restored at 1324
15770 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-06-05 02:34 | 2016-06-05 04:00 | 3 | 86 | 4304351 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL HAD JUST BROKE, REFUSED XMF APR AT 0400 CLOSE TICKET VER/KEP
15771 | Hazard | 3309002 | JEFF | JEFF | 2022-01-17 09:21 | 2022-01-17 13:39 | 1 | 258 | 4368621 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | very remote location, 4x4 only, manual pole, all power restored @ 13:39 p.hicks
15772 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2012-07-25 13:57 | 2012-07-25 18:15 | 1 | 258 | 4826061 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED SERVICE BUCKET CUTOUT DOOR BURNT INTO. TRUCK TO POLE .PSTAMPER RELEASED BY CREW 078E04,, REPLACED CUTOUT, ALL POWER RESTORED, BT//COD 1// VER/DBM
15773 | Hazard | 3308001 | JACKSON | S.JACKSON | 2018-01-21 22:42 | 2018-01-22 00:51 | 2 | 129 | 4761561 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out, power restored
15774 | Whitesburg | 3312902 | JENKINS | JENKINS | 2008-07-17 07:02 | 2008-07-17 11:20 | 1 | 258 | 53498-1 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMERBURNED UP WILL NEED A CREW TO REPLACE RELEASED BY CREW 074S07//3312902 VER/ARN IDC XXXX
15775 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-02-06 10:03 | 2008-02-06 12:12 | 2 | 129 | 51026-1 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | NEUT WIRE DOWN == 1SPAN OUT OF SAGE NEEDS TO RESAGE ==NEED LINE CREW == GUY WIRE BROKE == REPAIRED VER/ARN IDC XXXX
15776 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-04-06 18:34 | 2014-04-06 20:00 | 3 | 86 | 4580021 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SINGLE TRANSFORMER OUT WIRE TO HOT TAP BROKEN AND REPAIRED PWER RESTORED VER/KEP
15777 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-03-08 13:24 | 2020-03-08 14:50 | 3 | 86 | 4460951 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Replaced xfm arrester on pole 37830139C00126 actual restoration time was 15:50
15778 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-12-31 06:10 | 2013-12-31 10:28 | 1 | 258 | 4213981 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG , VOLTAGE 123.4 AND 79.9 PHASE TO GROUND. RELEASED BY CREW 078S01 VER/CRB
15779 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-09-07 15:27 | 2018-09-07 16:53 | 3 | 86 | 4054551 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse/ ISO 37830179B00021/ COD 3
15780 | Pikeville | 3407103 | TOPMOST | KITE | 2009-06-07 19:01 | 2009-06-07 21:10 | 2 | 129 | 53380-1 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP FUSE BROKEN ... REPLACED FUSE, ALL WORK COMPLETE / GXJ COD-2 ISO 37830234000021 L3/HFP IDC XXXX
15781 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-10-11 19:17 | 2015-10-11 21:26 | 2 | 129 | 4339341 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OPEN CHECKING NOW/PRIMARY OFF INSULATOR AT POLE 833-401RESTORED 2126 VER/KEP
15782 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2019-07-06 16:51 | 2019-07-06 18:17 | 3 | 86 | 4668271 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | lf out on p 903-85 all pwr restored @ 18:17 please close ticket LRM
15783 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-03-06 14:59 | 2008-03-06 16:25 | 3 | 86 | 54338-1 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411802///NEED TO REPLACE CUTOUT 3782005000040 VER/HFP IDC XXXX
15784 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-10-18 10:36 | 2016-10-18 12:45 | 2 | 129 | 4024781 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR./ ISO 37820032A00017/ COD 2/ MD DONE MISMAPPED CUSTOMERS/ VER/BOW L3/HFP XXXHFP
15785 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-07-19 17:58 | 2015-07-19 19:24 | 3 | 86 | 4912441 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR F IS OUT,WILL RE-FUSE///////////RE-FUSED AND RESTORED,ALL OK AFTERWARDS /////FUSE HAD ROTTED INTO/ ISO 38821130000023/ COD 3 CCC****/ VER/BOW
15786 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2012-01-28 19:12 | 2012-01-28 20:38 | 3 | 86 | 4301201 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONLY HAD 120 VOLTS COMING OUT OF CSP XFMR. RESET IT AND EVERYTHING PICKED UP. ADVISED CUSTOMER TO CALL BACK IF IT HAPPENS AGAIN AND WE WOULD GO AHEAD AND CHANGE IT. SH//COD 3// VER/DBM IDC XXXX
15787 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2018-12-20 07:54 | 2018-12-20 12:12 | 1 | 258 | 4581661 | 258 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | arrived ck voltage at mtr 93 volt ph to grnsfod, 118 ph to ph, ck voltage at transformer, had same on both open transformer, at 0900, will be crew req, 120/240 delta bank, dbl bushing, 10 kva, WELL BE CREW REQ, send to bobby reynolds can use trucks beside social sec office Released by crew 078S06 ON @ 1212 L3/HFP
15788 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-02-19 10:43 | 2014-02-19 12:09 | 3 | 86 | 4400601 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE 2 BAD CUTOUTS ON 3 PHASE BANK POLE, HAD TO OPEN RECLOSER ON POLE 1098-24, OPEN AT 1100 CLOSED BACK AT 1130, CREW REQ, SEND TO MR. ROB C. ALL POWER IS RESTORED BUT TO 3 CUST AT THE CHURCH RELEASED BY CREW 078S06 RELEASED BY CREW 078Q08 VER/SEF
15789 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-05-20 16:19 | 2009-05-20 17:45 | 3 | 86 | 53421-1 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN/// FUSE BROKE REFUSED POWER RESTORED//VER/CRB
15790 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2021-09-15 11:00 | 2021-09-15 12:26 | 3 | 86 | 4243291 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 206-1169 xfr cutout broke ,no truck in back yard Released by crew 078S05//arrived RM power on @ 12:26 please close tic RM
15791 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-11-09 20:13 | 2022-11-10 00:31 | 1 | 258 | 4119141 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required need 15kva trucks ok may need bag leaking oil Released by crew 078S03//arrived RM xfm replaced volatge good please close tic RM
15792 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-03-08 06:27 | 2014-03-08 10:45 | 1 | 258 | 4460751 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR..NEED 1 MAN ..TRUCK ACCESSIBLE. VER/CRB
15793 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2008-04-06 13:36 | 2008-04-06 17:54 | 1 | 258 | 64565-1 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001001//BAD 10KVA 7200 XFMR, POLE IS 12 STEPS FROM DRIVEWAY, CONTACTED BILL FRALEY AND HE IS GATHERING A CREW. RELEASED BY CREW 078S05//COD 1// VER/DBM IDC XXXX
15794 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-10-16 13:22 | 2013-10-16 17:40 | 1 | 258 | 4940361 | 258 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 074S01 RELEASED BY CREW 074S01 REPLACING SERVICE DROP ONLY ONE CUSTOMER AFFECTED. VER/CRB L/3 CRB
15795 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2020-12-01 08:04 | 2020-12-01 09:30 | 3 | 86 | 4734401 | 258 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | secondarry squeezon was melted off at transformer pole, all rep made all good at this loc
15796 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-03-19 13:51 | 2013-03-19 16:00 | 2 | 129 | 4920071 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR. COD-2 ISO TF 38830237000098 VER/HFP L3/HFP IDC XXXX
15797 | Hazard | 3301101 | CHAVIES | CHAVIES | 2021-04-13 18:19 | 2021-04-13 22:37 | 1 | 258 | 4449301 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25KVA 7200 XFMR on pole 195-125. I spoke with customer and they said it was ok to drive through their yard. Crew required. Released by crew 077S04, made repairs restored power at 22:37
15798 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-11-11 14:36 | 2020-11-11 16:45 | 2 | 129 | 4662941 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 1123-2077 bad 12kv c/o. no trk crew reqd Released by crew 078S07. Crew on site. Repairs made, Closed at 16:45. Ticket complete.
15799 | Paintsville | 3401802 | INDEX | HOSPITAL | 2014-05-04 14:34 | 2014-05-04 16:00 | 3 | 86 | 4661741 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2-3 TRIPLEX SEC BURNED DOWN.CHGING OUTEC AND 2-3 DROP.. VER/SEF
15800 | Pikeville | 3401001 | ELWOOD | DORTON | 2014-10-06 10:34 | 2014-10-06 12:00 | 3 | 86 | 4557101 | 258 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SQUEEZE-ON AT TRANS. HAS MELTED HOT LEAD. I AM GOING TO REWORK LEADS IN TRANS. I REWORKED LEADS ON TRANS. COD-3 ISO SO VER/HFP L3/HFP
15801 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-04-01 17:02 | 2019-04-01 21:20 | 1 | 258 | 4048831 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required with big bucket/broke cutout 38830171000040 on @ 2120
15802 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-09-11 19:51 | 2010-09-11 22:00 | 2 | 129 | 65638-1 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN ... REPLACED TRANSFORMER CUTOUT AND REFUSED LINE CUTOUT, ALL WORK COMPLETE / GXJ IDC XXXX
15803 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-10-16 22:52 | 2015-10-17 03:10 | 1 | 258 | 4355081 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA 120/240 / 7.2KV, TRUCK ACCESS . REPLACED 10 KVA XFMR WITH 15 KVA , ALL WORK COMPLETE / GXJ VER/ARN
15804 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-07-24 17:09 | 2012-07-24 19:18 | 2 | 129 | 4815631 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP TO0 LONG, NEED SEC POLE SET AND 1/0 SEC. TWO SEPERATE APARTMENTS OFF SAME METER, NEED TECH TO LOOK AT THIS POSSIBLY METERING APARTMENTS SERERATE. FIRE HAZARD. SEC CONN MELTED AT XMF. TIMEOFF 1905 TIME ON 1918 APR CLOSE TICKET.// IDC XXXX
15805 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-02-23 15:46 | 2012-02-23 17:12 | 3 | 86 | 4488231 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN NET. IN SEC. COND. REPAIRED COND G. SHOUSE COD=3 ISO TF 37830174D00001 VER/HFP L3/HFP AJB
15806 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-01-19 00:32 | 2011-01-19 04:50 | 1 | 258 | 62518-1 | 258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW TO CHANGE OUT AT STARTING TIME 01/19/11.15 KVA 19.9 120/240 CAN USE TRUCK////THREE MEN BUCKET JUST IN CASE TRUCK WILL NOT REACH VER/ARN IDC XXXX
15807 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-04-12 10:43 | 2011-04-12 15:00 | 1 | 257 | 55748-1 | 257 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART OUT//// BAD CONNECTIONS RECONNECTED ON SERVICE POLE, POWER OK. 15 REPLACED CONNECTORS ON SERVICE POLE. POWER OK. TIME 15:00 ; COD-3 IS TF 37830247C00413 VER/HFP L3/HFP IDC CHANGED COUNT FROM 3 PROBABLY SERVICE ONLY XXXX
15808 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-05-31 04:37 | 2012-05-31 08:54 | 1 | 257 | 4851861 | 257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT-UP///VER/CRB L/3 CRB IDC XXXX
15809 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-01-25 18:25 | 2009-01-25 22:42 | 1 | 257 | 59790-1 | 257 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3310501// 3PHASE SERV MELTED TOGETHER NEAR SERV ENTRANCE .UNKNOWN CAUSE AT THIS TIME.POSSIBLY OVERLOADED.WILL HAVE TO OPEN XFMR BANK TO REPAIR./ WILL OPEN TRANSFORMER UP TO MAKE REPAIRS - ABOUT 1 HOUR OUTAGE /3310501// 3PHASE SERV MELTED TOGETHER NEAR SERV ENTRANCE .UNKNOWN CAUSE AT THIS TIME.POSSIBLY OVERLOADED.WILL HAVE TO OPEN XFMR BANK TO REPAIR.FOUND BAD SPLITBOLT CONNECTION WHICH CAUSED PROBLEM.OPENED XFMR BANK AT 2145 CLOSED BACK IN AT 22:42 / COD-2 // VER/LDA L3/KEP
15810 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-08-21 14:53 | 2010-08-21 19:10 | 1 | 257 | 59022-1 | 257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#36541389 CALLED TREE CREW RELEASED BY CREW 078S08 REROUTING SEC ALL POWER RESTORED AT 1910//VER/CRB IDC XXXX
15811 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2019-03-06 12:17 | 2019-03-06 16:18 | 3 | 241 | 4956441 | 257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE POLE 1062-310trans cutout failed on 1062C310.opened trans at 16;10,replaced cutout,restored power at 16:18.
15812 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-10-21 08:37 | 2021-10-21 12:54 | 1 | 257 | 4371191 | 257 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug/crew reqd. tre Released by crew 078S04//arrived RM trouble shooting UG .found bad hot leg made repairs have good volatge now time on 12:54 please close tic RM
15813 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-02-05 07:07 | 2016-02-05 11:24 | 1 | 257 | 4676881 | 257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL SEE IF I CAN REPLACE IT SAFELY/////////REPLACED BROKEN 19.9 XFR CUTOUT AND RESTORED,ALL OK AFTERWARDS/ VER/AWD
15814 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2020-09-15 08:33 | 2020-09-15 12:50 | 1 | 257 | 4464551 | 257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | A phase xfmer bad. 25kva 120/240. truck ok. crew reqd. Released by crew 078S04 crew on site FETR 13:00all pwr restored 12:50
15815 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-07-03 18:48 | 2015-07-03 23:05 | 1 | 257 | 4716641 | 257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 139-239 BAD 15KVA TRUCK TO POLE IF YOU BRING PADS RELEASED BY CREW 078S08,REPLACE XFMR ALL CUST RESTORED @ 2305 PLEASE CLOSE TICKET THANKS.BT VER/KEP
15816 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-04-26 18:03 | 2016-04-26 22:20 | 1 | 257 | 4128391 | 257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XMF ON 549-23 AT 1803 TO MAKE SAFE, LINECREW REQUIRED. NEED 25KV 34.5 XMF RELEASED BY CREW 078S11--CREW ON SITE---CHANGED 25KVA-CUTOUT AND ARRESTOR--RESQUEEZED ALL CONNECTIONS AT RISER---VOLT CK GOOD---TBL TKT COMP/ ISO 38830549000023/ COD 1/ 2220/ VER/BOW
15817 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-01-31 12:13 | 2019-01-31 16:30 | 1 | 257 | 4743921 | 257 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK FOR PROBLEMS/////////BAD 10KVA CSP XFR.NEED TO REPLACE,CREW ENROUTE.ONE SIDE NOT PUTTING OUT CORRECT VOLTAGE//////////////REPLACED BAD XFR,ALL OK AFTERWARDS ¦¦ L3/HFP
15818 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2015-09-24 14:03 | 2015-09-24 18:20 | 1 | 257 | 4266351 | 257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-573 BAD 10/15 240VOLT TRANS. BK. TRUCK TO POLE MIT BRING 2-15 OR 2-25 KVA TRANS. 2-BUSHING 120/240 TRANS. IN 240 VOLT TRANS. BANK/ PER GREG BELL GO BACK WITH 2-25 AND CAOULD USE SINGLE BUSHING.. CREW ON SITE ETR 19:00.. XFMRS CHANGED AND CUSTOMERS RESTORED AT 18:20 TICKET COMPLETE CAY/ ISO 38830045A20573/ COD 1/ VER/BOW
15819 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-07-08 16:39 | 2014-07-08 20:56 | 1 | 257 | 4209781 | 257 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BROKE NEUTRAL IN SERVICE. ONLY 1 CUST. WITH PART POWER . SERVICE WAS GOING TO OUT BUILDING . VER/CRB
15820 | Hazard | 3309302 | VICCO | JEFF | 2020-01-27 10:14 | 2020-01-27 14:30 | 1 | 256 | 4341431 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, manuel pole
15821 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-04-22 12:33 | 2017-04-22 13:37 | 4 | 64 | 4667781 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILING ON 37830424000224. TOOK OFF CLAMP AT 37830424000074 TO ISOLATE AND REPLACE CUTOUT. REPLACED CUTOUT AND LOWERED PRIMARY DOWN ON OLD POLE. CUT OFF OLD BURNT SECTION OF POLE. POWER RESTORED TO 2 CUSTOMERS 1233-1337 VER/AWD // 4 CUST IS CORRECT PER POR = L3/HFP XXXHFP
15822 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-06-27 20:30 | 2009-06-28 00:46 | 1 | 256 | 65314-1 | 256 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | SPLICED BAD 1/0 URD CABLE, ONLY 1 CUST AFFECTED. VER/ARN
15823 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-10-26 23:41 | 2013-10-27 01:49 | 2 | 128 | 4966741 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT DOOR CHANGE OUT DOORS OFF AND ON AT 143
15824 | Pikeville | 3413402 | GARRETT | LACKEY | 2016-05-02 14:32 | 2016-05-02 16:40 | 2 | 128 | 4159851 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ACTUAL POLE # 37830064000109, C & A PHASE TRANSFORMER FUSES BLOWN .CLEARED ROW AROUND POLE AND REFUSED TRANSFORMERS, ALL WORK COMPLETE / GXJ/ ISO 37830064000109/ COD 2/ VER/BOW
15825 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-09-30 09:02 | 2021-09-30 11:10 | 2 | 128 | 4304311 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I repaired a bad secondary connection on pole 175-88.
15826 | Hazard | 3309302 | VICCO | JEFF | 2017-12-28 07:14 | 2017-12-28 11:30 | 1 | 256 | 4684191 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse is out, bad xfmr 37830322C00242, crew coming to replacexfmr fuse is out, bad xfmr, crew coming to replace. please send ticket to P. Hicks Released by crew 077S02 all power restored @11:30 hrs..p.hicks
15827 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2012-09-13 14:32 | 2012-09-13 16:40 | 2 | 128 | 4046331 | 256 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER.BAD CONNECTION ON SECONDARY RISER ON XFMR POLE..//..REPLACED BAD CONNECTION.VOLTAGE GOOD NOW.ONLY 1 CUST AFFECTED..JRV..09/13/12 COD-2 ISO SO @ 38821041A00079 VER/HFP L3/HFP IDC XXXX
15828 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-12-21 13:25 | 2010-12-21 13:33 | 32 | 8 | 54844-1 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREWS REPLACING BAD CUTOUT//ISO 39831147C14094 // COD 32 // MD FILED// VER/DBM IDC XXXX
15829 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-10-28 08:34 | 2009-10-28 12:50 | 1 | 256 | 60828-1 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD 15KVA 19.9 120/240 RELEASED BY CREW 077S01 COD-1 ISO TF 37830410B00036 L3/HFP IDC XXXX
15830 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-12-23 14:42 | 2022-12-23 16:50 | 2 | 128 | 4325101 | 256 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | transformer riser burnt in two. repaired
15831 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-07-06 11:37 | 2011-07-06 13:45 | 2 | 128 | 4474641 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR FUSE IS OUT,WILL RE-FUSE////////FUSE HAD ROTTED INTO,RE-FUSED AND RESTORED VER/KEP IDC XXXX
15832 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2018-04-18 14:31 | 2018-04-18 15:35 | 4 | 64 | 4250981 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on the arm, at pole 115-6057. Need line crew, truck to pole. Changed three cutouts on the arm. power restored at 15:35
15833 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-04-09 09:59 | 2016-04-09 14:15 | 1 | 256 | 4074141 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAIL ON WHEATHER HEAD ,NEED 1 MAN AND A STORES MAN, WILL MEET THEM IN HAZARD.OPEN AT 14:00 AND CLOSE AT 14:15,SPLIT BOLT CONNECTION FAIL.// VER/ ADH
15834 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-03-06 09:16 | 2022-03-06 10:20 | 4 | 64 | 4570751 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp replaced complete
15835 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-02-23 12:24 | 2008-02-23 16:40 | 1 | 256 | 66520-1 | 256 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDER GROUND RELEASED BY CREW 078S08//3116701//VER/CRB IDC XXXX
15836 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-01-24 10:33 | 2022-01-24 11:37 | 4 | 64 | 4400151 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke, repaired and restored @ 11:37
15837 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2017-10-09 08:29 | 2017-10-09 12:45 | 1 | 256 | 4433181 | 256 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKEN FEEDING PRI. METERING ON POLE 56-517////WILL MAKE REPAIRS...REPAIRS MADE.. VER/HFP L3/HFP
15838 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-03-02 07:44 | 2009-03-02 12:00 | 1 | 256 | 53634-1 | 256 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3410502//PART POWERPART POWER. WILL HAVE TO REPLACE SECONDARY AND SERVICE DROP//VER/CRB IDCC CDC92 XXXX
15839 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2022-11-16 11:52 | 2022-11-16 14:00 | 2 | 128 | 4149081 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad con--repaired-allgood-ds111622
15840 | Cannonsburg | 3000101 | ASHLAND | 25-25STREET | 2016-06-01 11:13 | 2016-06-01 11:45 | 8 | 32 | 4279061 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING BUSTED PRIMARY BUSHING/ ISO 38830045C45677/ COD 8---CREW ON SITE--TIME OFF AT 11:13--TIME ON 11:45---CHANGED OUT XFMR, CUTOUT AND ARRESTOR--HAD TO MAKE REPAIRS TO #6CU PRIMARY---TBL TKT COMP/ VER/BOW
15841 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-03-13 20:50 | 2015-03-14 01:06 | 1 | 256 | 4191661 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 469-51 .. REPLACED CUTOUT RESTORED POWER AT 01:06 VER/KEP
15842 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-04-03 13:44 | 2009-04-03 15:52 | 2 | 128 | 64751-1 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308001//SERVICER ETA 15:00// W.M. BAD CUTOUT//COD 2// VER/DBM IDC XXXX
15843 | Whitesburg | 3312902 | JENKINS | JENKINS | 2016-11-17 12:31 | 2016-11-17 13:35 | 4 | 64 | 4108151 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP, I REPLACED IT/ FUSE IS ACTUALLY ON POLE 37830382B00227 MD DONE/ ISO 37830382B00227/ COD 2/ VER/BOW L3/HFP HFPC CNT2
15844 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-03-15 21:27 | 2012-03-15 23:35 | 2 | 128 | 4586611 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIGHTNING BLOWED CUTOUT INTO REPLACED IT AND CLOSED LINE FUSE IN @ 2335 VER/KEP IDC XXXX
15845 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2021-11-22 10:40 | 2021-11-22 12:48 | 2 | 128 | 4115151 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cUTOUT CHANGED, RESTORED @ 12:48
15846 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-11-15 12:12 | 2011-11-15 14:20 | 2 | 128 | 4078971 | 256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED---B PHASE CUTOUT BAD ON TRANSFORMER BANK--TRUCK TO POLE RELEASED BY CREW 078S07//P TOLLIVER ON SITE//REPLACED 3 CUTOUTS POWER RESTORED AT 14:20 PTOLLIVER ///VER/CRB IDC XXXX
15847 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-03-05 14:28 | 2010-03-05 14:45 | 15 | 17 | 63195-1 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WORK REQUEST 34141911 // BURNT UP RISER ON TRANSFORMER // CREW ENROUTE TO ASSIST// IDC XXXX
15848 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2012-06-22 05:35 | 2012-06-22 09:50 | 1 | 255 | 4943901 | 255 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SDB / DAY SERVIICER TO CHECK, RISER WIRE ON SECONDARY LEAD FROM TRANSFORMER BURNT INTO ///VER/CRB L/3 CRB
15849 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-07-27 09:25 | 2017-07-27 13:40 | 1 | 255 | 4184801 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED CURRENT LIMITING FUSE. TIME RESTORED 1340/ ISO 38830164C43612/ COD 1/ VER/BOW SJGC FEC57
15850 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-10-07 04:30 | 2014-10-07 08:45 | 1 | 255 | 4562331 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE VER/HFP L3/HFP
15851 | Pikeville | 3407103 | TOPMOST | KITE | 2009-04-20 08:31 | 2009-04-20 12:46 | 1 | 255 | 59543-1 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3407103// ... TRASFORMER OPEN, ARRESTER BLOWN ... ALL WORK COMPLETE / GXJ//COD 1 VER/KEP L3/KEP IDCC PN14 XXXX
15852 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-04-15 16:15 | 2014-04-15 17:40 | 3 | 85 | 4608211 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REMOVED TAP ON POLE 472-112 TO MAKE REPAIRS//COD 3//ISO 37830472000113// VER/DBM
15853 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2022-09-20 08:16 | 2022-09-20 09:07 | 5 | 51 | 4899201 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Wire burnt in two @ Hot Tap, repaired
15854 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-11-15 09:10 | 2012-11-15 13:25 | 1 | 255 | 4399371 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND SERVICE, CALL BRUCE AND HE IS GETTING CREW TOGETHER TO SEE IF WE CAN REPAIR OR REPLACE SERVICE VER/KEP IDC XXXX
15855 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2012-09-08 10:25 | 2012-09-08 11:50 | 3 | 85 | 4029621 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN LINE FUSE..RE FUSED LINE FUSE..65 T ///VER/CRB L/3 CRB IDC XXXX
15856 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-07 18:15 | 2016-01-07 22:30 | 1 | 255 | 4593791 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SD BURNED APART AT POLE 38831003D00057, NEED 100 FT 1/0 / 3 AND 1 MAN WITH SERVICE BUCKET OR PICK-UP . REPLACED SD, ALL WORK COMPLETE / GXJ/ONLY 1 CUSTOMER AFFECTED PART OUT THE WHOLE TIME// VER/ ADH
15857 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-12-18 13:05 | 2012-12-18 14:30 | 3 | 85 | 4480231 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..CHG OUT CUTOUT ///VER/CRB L/3 CRB
15858 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-04-29 19:00 | 2014-04-29 20:25 | 3 | 85 | 4649161 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ALL OUT RELACED BROKEN 6-T FUSE LINK POWER RESTORED KWB VER/CRB IDC XXXX
15859 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2020-08-04 12:09 | 2020-08-04 13:00 | 5 | 51 | 4285151 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OPENING RECLOSER ON 38820916A00152 TO REPAIR BROKE CROSSARM OPENED AT 1209 CLOSED AT 1300
15860 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2012-05-26 00:50 | 2012-05-26 02:15 | 3 | 85 | H4832081 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SERVICE DROP BURNT DOWN TREES TRANS OFF 12;50 TO 2;15 AM //VER/GAH IDCC DUP TO OPEN TRANS XXXX
15861 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-05-20 18:45 | 2017-05-20 23:00 | 1 | 255 | 4829891 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 20 MIN ETA POLE 117-288 ROTTEN FELL OVER OPENED TRANS. ON POLE 117-271 18:45 NEED 35/5 BACK YARD TOOL POLE HAS UNDER GROUND ON POLE NO TRUCKS MADE SAFE. RESTORED. WILL CREATE WORK ORDER TOMORROW FOR FURTHER REPAIRS PER B REYNOLDS. AWD 38830117A00271 38830117A00288 VER/AWD
15862 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-03-29 16:05 | 2020-03-29 20:20 | 1 | 255 | 4533931 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva xfm //// Dennis Massey is going to bring xfm/// Changed bad xfm and restored service @ 20:20
15863 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-06-22 18:45 | 2013-06-22 23:00 | 1 | 255 | 4386851 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR IN DIFFICULT LOCATION. NEED THREE MEN AND LINE TRUCK. CREWS ONSITE. INSTALLED A SPAN OF SECONDARY FROM 737-160 TO 737-161 TO PICK UP SERVICE. RESTORED @ 23:00. WILL SEND A JOB TO ENGINEERING TO SEE ABOUT THIS XFMR. SH VER/ARN
15864 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-07 18:15 | 2016-01-07 22:30 | 1 | 255 | 4593791 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SD BURNED APART AT POLE 38831003D00057, NEED 100 FT 1/0 / 3 AND 1 MAN WITH SERVICE BUCKET OR PICK-UP . REPLACED SD, ALL WORK COMPLETE / GXJ/ONLY 1 CUSTOMER AFFECTED PART OUT THE WHOLE TIME// VER/ ADH
15865 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2009-06-17 13:39 | 2009-06-17 15:04 | 3 | 85 | 61301-1 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP FUSE BROKE COD-3 ISO 37830024B11594 L3/HFP IDC XXXX
15866 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-05-01 16:15 | 2016-05-01 20:30 | 1 | 255 | 4151551 | 255 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON B PHASE .POLE 148-100 . REPLACED CUTOUT . POWER BACK @ 20:30 .// VER/ ADH
15867 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2019-10-02 10:10 | 2019-10-02 12:05 | 8 | 115 | 4084561 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hotline clamp riser burnt off on phase C transformer in bank. Crew enroute to assist. Opened latteral off 954-379 @ 11:45 to safely make repairs. Advised all customers. Restored all outaged cust @ 12:05. sh Released by crew 076S02
15868 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2010-12-28 10:22 | 2010-12-28 11:13 | 5 | 51 | 56432-1 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SRTS WR # 38220254 // CUTOUT BROKE ON POLE 38830454B43632 REPLACING CUTOUT REPLACED BROKE CUTOUT ON POLE 38830454B43632 POWER RESTORED AT 1113 CLOSE TICKET COD-5 ISO TF 38830454B43632 VER/HFP L3/HFP IDCC PN3526 XXXX
15869 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2022-12-25 12:00 | 2022-12-25 13:25 | 3 | 85 | 4354901 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse failed. Restored at 13:25.
15870 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2017-02-06 08:01 | 2017-02-06 08:52 | 5 | 51 | 4360381 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE PULLED INTO, REFUSED @0852. VER/CRB L3/HFP XXXHFP
15871 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-05-14 22:27 | 2022-05-14 23:52 | 3 | 85 | 4891611 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | replaced arrester complete
15872 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2019-09-24 18:00 | 2019-09-24 22:15 | 1 | 255 | 4054751 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 253-25 bad 25 kva xfr ,,,trucks to pole ,,,tight driveway ,small truck would work best Released by crew 078S05 complete please close ticket LRM time 22:15
15873 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2008-05-22 15:50 | 2008-05-22 17:15 | 3 | 85 | 50533-1 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3309001// HOT LINE CLAMP ON XFMR COME OFF....REPLACED CLAMP//COD 3// VER/DBM IDC XXXX
15874 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-07-04 18:00 | 2018-07-04 22:15 | 1 | 255 | 4723161 | 255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED TRANS
15875 | Whitesburg | 3312901 | JENKINS | KONA | 2014-07-24 16:54 | 2014-07-24 21:08 | 1 | 254 | 4284231 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR BURNED UP , I NEED A 25 KVA 7200 V. XFMR, TWO MEN AND A MATERIAL HANDLER RELEASED BY CREW 077S12 VER/CRB
15876 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-07-01 15:53 | 2018-07-01 18:00 | 2 | 127 | 4695241 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout
15877 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-01-01 07:00 | 2011-01-01 09:07 | 2 | 127 | 57496-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK COMPLAINT/////NOTHING EVIDENT AT THIS TIME.MAN,BUCKET ENROUTE SOON,WILL REPLACE CUTOUT IF NECESSARY/REPLD BAD CUTOUT AND RESTORED COD-2 ISO TF 3782000200044 VER/HFP L3/HFP IDCC TOF0614, CALL WAS FULL POWER ALLOWED TIME FOR REPLACEMENT XXXX
15878 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-02-17 15:56 | 2008-02-17 20:10 | 1 | 254 | 64239-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308002 /// HOT TAP LOOSE VER/JHM IDCC PN NULL CUSTOMER TURNED OF BREAKER XXXX
15879 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2009-03-14 19:56 | 2009-03-14 22:03 | 2 | 127 | 58626-1 | 254 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 1 BAD CUTOUT IN 3 PHASE PLATFORM BANK// CALLED V MULLINS N CREW RELEASED BY CREW 078S07/BREAKER IN NR/OPENING XFMR BANK TO CHG CUTOUT/VEM/PLEASE CLOSE TICKET/THANKS/VEM VER/LDA IDCC PN4386 XXXX
15880 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-05-14 10:05 | 2022-05-14 12:12 | 2 | 127 | 4889101 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad trans. cutout on pole 93-225, got it replaced and power restored @1212.
15881 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-04-17 18:08 | 2011-04-17 20:15 | 2 | 127 | 59964-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | STS WR # 39600524 // BAD 25KVA 7200 XFMR AT POLE 183-407, TRUCK OK. SEND TO P TOLLIVER. CREW HAS BEEN NOTIFIED. COD-2 ISO TF 38830183D00407//PT ON SITE//ALL CUST. RESTORED AT 20:15 PR TOLLIVER//VER/PDP IDC XXXX
15882 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-04-17 21:38 | 2008-04-17 23:45 | 2 | 127 | 51973-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LUG BURNED OFF25KVA REPAIRED WILL TRY TO COME BACK TOMORROW TO DO COMPT REBUILD IDCC FEC57, CNT1 XXXX
15883 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-01-14 20:01 | 2019-01-15 00:15 | 1 | 254 | 4673541 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew req bad 15kv single bushing 120/240 7200, can use truck, turn at red light at rt 2, towards river, first pole on right after crossing railroad tracks Released by crew 078S06 L3/HFP
15884 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-05-04 11:08 | 2010-05-04 15:22 | 1 | 254 | 55574-1 | 254 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG--CREW REQUIRED-350 UG WIRE IN CONDUIT--320 AMP SERVICE TO OFFICES RELEASED BY CREW 078S07POWER TEMP INSTALLED 5/4/10 M.P. XFMR POLE 70 B4 3669 RELEASED BY CREW 078H12 VER/HFP L3/HFP IDCC PN3644 XXXX
15885 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-02-15 00:38 | 2015-02-15 02:45 | 2 | 127 | 4023701 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER FUSE OPEN POLE#37830143D00031 TRANS. FUSE IS OUT. I AM GOING TO REFUSE TRANS.TRANS. FUSE IS OUT. I AM GOING TO REFUSE TRANS. CUT OUT IS BROKEN. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. VER/KEP L3/HFP XXX
15886 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-05-11 20:08 | 2008-05-11 22:15 | 2 | 127 | 62035-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE TO REPLACE BAD CUTOUT CHANGED BAD CUTOUT. COD-2 VER/KEP IDC XXXX
15887 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-12-04 12:33 | 2010-12-04 14:40 | 2 | 127 | 62961-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED ON 67-55. REPLACED CUTOUT AND RESTORED @ 14:40. SH//COD 2// VER/DBM IDC XXXX
15888 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-09-24 17:21 | 2009-09-24 21:35 | 1 | 254 | 61665-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25KVA 19.9 120/240. CAN USE BUCKET....DAH RELEASED BY CREW 074S08.......XFMR CHANGED. POWER RESTORED @ 21:45.....B. CAMPBELL//VER/CRB IDC XXXX
15889 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-01-10 09:53 | 2016-01-10 12:00 | 2 | 127 | 4599551 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 875-181.POLE ON FIRE.PUTTING OUT POLE,, CHANGING CUTOUT.NEED TO SEND A COPY TO CLIFF FREEHMAN POLE 875-181 NEEDS CHANGED OUT.//SENT TO TECH VER/CRB
15890 | Whitesburg | 3312901 | JENKINS | KONA | 2010-01-25 11:53 | 2010-01-25 14:00 | 2 | 127 | 59448-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER IS BAD WILL NEED A 25 KVA AND CUTOUT AND T BRACKETT CECIL SEXTON IS GOING TO REPLACE THIS RELEASED BY CREW 074S07//VER/CRB IDC XXXX
15891 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2010-10-26 18:08 | 2010-10-26 20:15 | 2 | 127 | 64911-1 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | #4 SOLID COPPER RISER BROKEN OUT OF XFORMER HOT LEG. POWER BACK ON.//VER/CRB IDC XXXX
15892 | Pikeville | 3408103 | SALISBURY | MARTIN | 2019-02-13 08:43 | 2019-02-13 10:50 | 2 | 127 | 4788071 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PER P.R. TRANSFORMER FUSE OUT HERE. 6t fuse out due to bad cutout will be changing out changed out cutout everything ok
15893 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2011-06-23 09:46 | 2011-06-23 14:00 | 1 | 254 | 4398581 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT BIG BUCKETT TO POLE./CREW ON SITE MAKING REPAIRS//REPAIRS COMPLETE POWER REST. @ 14:00 J. HEMLEPP 078H05 ROANOKE DDC SHOULD HAVE AN OUTAGE FOR THIS FOR THE FEEDER. JOE WORKED WITH THEM TO ISOLATE THE BREAKER TO MAKE THESE REPAIRS... JEFF KENNEDY COD-1 ISO TF 38830190000062 VER/HFP L3/HFP IDC XXXX
15894 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-07-26 10:59 | 2016-07-26 15:13 | 1 | 254 | 4681461 | 254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9-25KVA XMF TRUCK OK LINECREW REQUIRED RELEASED BY CREW 078S11/ OVERVIEW DR---CREW ON SITE--CHANGED 50 KVA--VOLT CK GOOD---TBL TKT COMP---RMV/ ISO 38830525C10313/ COD 1 VER/CRB
15895 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2022-07-24 20:47 | 2022-07-25 01:00 | 1 | 253 | 4569981 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Tried to call cutomer, get a slow busy signal every time.bad cutout chging
15896 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2019-02-27 19:02 | 2019-02-27 23:15 | 1 | 253 | 4935131 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 30 VOLTS ONE LEG OF CSP Released by crew 077S01 changed transformer and restored power at 23 15
15897 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2018-08-27 19:07 | 2018-08-27 23:20 | 1 | 253 | 4005911 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | One customer only. THis service is in trouble, and comes across a creek up the hill through a thicket. The customer is ok with waiting until tomorrow, we will need a tree crew and 2 or 3 linemen this is #4 al service should be changed to #2. Can use truck on takeoff pole. Released by crew 074S07
15898 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2011-10-03 10:17 | 2011-10-03 14:30 | 1 | 253 | 4942371 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED//VER/CRB IDC CHANGED FROM FUSE CLEARING TO CUTOUT PER CALL XXXX
15899 | Hazard | 3303902 | LESLIE | WOOTON | 2013-07-30 09:08 | 2013-07-30 13:21 | 1 | 253 | 4606311 | 253 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND RELEASED BY CREW 077S01 REPLACED UG WIRE AND METER BASE , CHECKED POWER ---OK VER/HFP L3/HFP IDC XXXX
15900 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-06-22 10:49 | 2016-06-22 15:02 | 1 | 253 | 4405821 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT AND ARRESTER. VER/CRB
15901 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-05-24 19:17 | 2020-05-24 23:30 | 1 | 253 | 4899581 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | back in at 23:30
15902 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-06-22 13:35 | 2021-06-22 17:48 | 1 | 253 | 4792941 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout @165-60,no truck access, will be making repairs. Got cutout replaced and power restored @1748.
15903 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-08-11 06:27 | 2015-08-11 10:40 | 1 | 253 | 4121051 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S11//// REPLACING BAD CUTOUT & ARRESTER OPENED FUSE ON 501-277 AT 1012 TO SAFELY REPLACE CUTOUT&ARRESTER ON 501-403 APR AT 1040 CLOSE TICKET VER/CRB
15904 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-02-20 14:17 | 2013-02-20 18:30 | 1 | 253 | 4835051 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION VER/HFP L3/HFP IDC XXXX
15905 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-01-25 13:47 | 2017-01-25 18:00 | 1 | 253 | 4330261 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV TRANSFORMER 19.9KV TRUCK ACCESSIBLE RELEASED BY CREW 077H07 REPAIRS MADE AND POWER RESTORED AT 18:00 VER/CRB L3/HFP XXXHFP
15906 | Pikeville | 3402002 | KEYSER | STONECOAL | 2022-06-10 21:13 | 2022-06-11 00:44 | 3 | 211 | 4056111 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester broke and is laying close to metal bracket will have to lift hottap on 1105-D-143 to clear up arrester, will keep up with times// off @ 00:23, on @ 00:44
15907 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-11-03 13:07 | 2020-11-03 17:20 | 1 | 253 | 4639271 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 Kva 7200 transformer on pole 37830362000226. Truck accessible. Need crew to replace. Released by crew 077S06 1720
15908 | Pikeville | 3413401 | GARRETT | GARRETT | 2012-10-01 19:24 | 2012-10-01 23:37 | 1 | 253 | 4104221 | 253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAMILTON, DALE & MCKINNEY, ERIC T. & LAYNE, PAUL B. ELEMINATED 3 300A SWITCHED AT POLE 65-158 AND REPLACED 1 TRANSFORMER CUTOUT AT POLE 65-158, .OPENED OCRS AT POLE 37830065A00476 AT 22:40 AND CLOSED AT 23:23, ALL WORK COMPLETE RELEASED BY CREW 074S03 // COD-1 (0 PER POWERON) ISO TF 37830065D00158 SEE 4105611 FOR RECL OUTAGE VER/HFP L3/HFP IDCC CNT5 XXXX
15909 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2008-11-05 15:36 | 2008-11-05 17:00 | 3 | 84 | 62486-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT//3301701/VER/CRB IDC XXXX
15910 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-04-19 17:28 | 2013-04-19 18:52 | 3 | 84 | 4029161 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER..CONNECTIONS BURNING UP ON XFMR SECONDARY LEADS GOING TO LASH CABLE ON POLE 1038A4-329..CAN REPAIR.WILL HAVE TO OPEN XFMR.4 METERS ON THIS CAN..//..OPENED XFMR @ 18:30.MADE REPAIRS.CLOSED XFMER @ 18:52.ALL POWER OK..JRV.04/19/13 ///VER/CRB L/3 CRB IDCC TOF1830 CN3, PN419 XXXX
15911 | Hazard | 3420001 | SOFT SHELL | VEST | 2011-08-27 07:24 | 2011-08-27 11:36 | 1 | 252 | 4763821 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3420001//NEED 1 MAN , BIG BUCKETNEED 1 MAN , BIG BUCKET. REPAIRS MADE, POWER BACK ON//VER/CRB IDC XXXX
15912 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-10-04 15:37 | 2013-10-04 16:40 | 4 | 63 | 4911131 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | COD-4 ISO TF 37830174B00099 FUSE BROKE , WASNT BLOWN VER/HFP L3/HFP IDC XXXX
15913 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-08-04 09:28 | 2019-08-04 10:31 | 4 | 63 | 4838661 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door, failed. changed cutout & arrestor. all power restored @ 10:31. pls close. tre
15914 | Hazard | 3309302 | VICCO | JEFF | 2019-06-09 05:28 | 2019-06-09 06:10 | 6 | 42 | 4464091 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutouts on 37830348A00065/need 1 lower class/flaggers/2-19.9 cutoutsTransformer cutout is broke no power off yet calling for 1 man and flaggers cod 6Transformer cutout is broke no power off yet calling for 1 man and flaggers open at 05:28 closed at 06:10
15915 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-07-05 12:44 | 2014-07-05 13:20 | 7 | 36 | 4195121 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ISO POLE 38830020B33024 HOT TAP BURNT OFF REC. REPAIRED/// CCC COD-7 A PHASE LEAD BURNT OFF VER/HFP L3/HFP
15916 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-04-29 07:06 | 2014-04-29 08:30 | 3 | 84 | 4645211 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE///CHANGING NOW//REPAIRS MADE///RESTORED AT 8:30//COMPLETE//EM COD-3 ISO TF 38820818A00134 VER/HFP L3/HFP
15917 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-08-18 08:03 | 2019-08-18 09:27 | 3 | 84 | 4901801 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
15918 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-11-28 08:10 | 2008-11-28 09:34 | 3 | 84 | 52743-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR OPENED FOR THE SECOND TIME WILL NEED TO REPLACE NEXT WEEK IF IT HOLDS TILL THEN//3307301//VER/CRB IDC POSSIBLE BAD TRANSFORMER XXXX
15919 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-06-01 12:50 | 2013-06-01 14:14 | 3 | 84 | 4205351 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED CUTOUT AND ARRESTER ON 573-97, APR AT 1414 CLOSE TICKET COD-3 ISO LF 38830573000027 VER/HFP L3/HFP IDC XXXX
15920 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-06-13 21:22 | 2010-06-13 22:25 | 4 | 63 | 63172-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND LINE FUSE OUT, PATROLLED LINE DID NOT FIND ANYTHING WRONG, FUSE LOOKED IT HAD MELTED OUT OR JUST BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC
15921 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-03 09:24 | 2008-12-03 11:30 | 2 | 126 | 54134-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP XFMR FUSE OUT, VINES ON XFMR. BAD XFMR, CALLING FOR HELP RELEASED BY CREW 077S02//3308401 COD-2 IDC XXXX
15922 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-01-07 13:30 | 2010-01-07 14:54 | 3 | 84 | 65123-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED TRANSFORMER & LINE FUSE TO ALLOW THEM TO SAFELY REPLACE POLE THAT HAS TOP BURNT OFF DUE TO CUTOUT FAILING.// COD 3// VER/DBM IDC XXXX
15923 | Paintsville | 3401802 | INDEX | HOSPITAL | 2016-01-13 18:39 | 2016-01-13 20:45 | 2 | 126 | 4618391 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT.CHANGING.655-20./ ISO 38830655A00020/ COD 2/ VER/BOW
15924 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-05-31 17:47 | 2011-05-31 18:50 | 4 | 63 | 4215631 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 728-11...CHANGED COUT RE FUSED.. VER/KEP IDC XXXX
15925 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-03-28 22:11 | 2022-03-28 23:14 | 4 | 63 | 4685551 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link appears to have broke. Restored @ 23:14. sh
15926 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-07-21 17:38 | 2015-07-21 21:50 | 1 | 252 | 4928301 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CLOSED LINE FUSE ON POLE 858-148 AT 19:21 AND IT BLEW XFMER FUSE ON POLE 858-251///FEFUSED XFMER FUSE BUT IT CAME BACK OUT///BAD 25KVA ON POLE 858-251///NO TRUCK NEED 3 MEN AND 25KVA XFMER // R MAYNARD & T GOBLE & R NEWSOME///REPAIRS MADE///BACK ON AT 21:50///COMPLETE BR // COD-1 ISO 3883085800148 VER/HFP L3/HFP
15927 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-05-23 16:06 | 2011-05-23 17:30 | 3 | 84 | 4147061 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CUTOUT COD-3 ISO TF 37820099000067 VER/HFP L3/HFP
15928 | Hazard | 3303902 | LESLIE | WOOTON | 2017-05-30 16:15 | 2017-05-30 17:39 | 3 | 84 | 4881231 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | XFMR BUSHING ARCING WILL REPLACE RELEASED BY CREW 077S01 REPAIRS MADE , OPENED TRANSFORMER AT 1615 AND RESTORED POWER AT 1739 37830487000101 VER/AWD
15929 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-06-05 19:54 | 2015-06-05 22:00 | 2 | 126 | 4517011 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM FUSE BLOWN WILL RE-FUSE/// BAD 50 KVA 7200 NEED 1 MAN CAN USE TRUCK/// CHANGED BAD XFM AND RESTORED SERVICE @ 22:00 VER/CRB
15930 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-12-16 13:54 | 2019-12-16 16:00 | 2 | 126 | 4158581 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2-3 triplex burned down, blew xfmr fuse on38830853000057..replacing,,cust still has trees on his side,, disc will call back tomorrow for reconnect. got xfmr back on at 16.00
15931 | South Williamson | 3202201 | LOVELY | LOVELY | 2021-08-24 10:28 | 2021-08-24 14:40 | 1 | 252 | 4143481 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up at xfmr pole//i repaird connections//restored at 14:40//complete/em IT forced closed per Charles R Barker//IT Force Closed
15932 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2020-05-03 17:45 | 2020-05-03 17:57 | 21 | 12 | 4791201 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened line fuse at 45-B2-2589 at 1745 and closed at 1757opened line fuse @ 17:45 & back in @ 17:57
15933 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2016-12-13 10:41 | 2016-12-13 14:53 | 1 | 252 | 4191381 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SILVER TOP CUTOUT (12 KV) IS CRACKED AND CHIPPED.THERE HAS BEEN BURNING ON POLE AROUND ARRESTER/CUTOUT BRAKET (BRAKET TO POLE) AND GUY ATTACHMENT. TRUCK ACCESSIBLE. NO TREE CREW NEEDED. RELEASED BY CREW 078F01,REPLACED CUTOUT ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/AWD L3/HFP XXXHFP
15934 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2015-07-11 14:57 | 2015-07-11 16:00 | 4 | 63 | 4777921 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 901-5542, HAVE CHANGED AND POWER IS RESTORED AT THIS LOC AT 1600// VER/ ADH
15935 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-02-22 09:58 | 2015-02-22 11:22 | 3 | 84 | 4070871 | 252 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ALL THREE CUSTOMERS PART POWER ORIGNIALLY, ALL THRE CUSTOMERS TAKING OFF AT SAME TIME, ALL THREE CUSTOMERS RESTORED AT SAME TIME/ BAD CONNECTION AT XFMR BURNT LEAD INTO , MADE REPAIRS RESTORED POWER 11:22 OPENED TRANSFORMER 11:12/ ISO 37830353A00037/ COD 3/ VER/BOW
15936 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-09-08 18:39 | 2018-09-08 20:45 | 2 | 126 | 4059971 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broken on pole 166-4..will make repairs..repairs made..
15937 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-08-14 23:27 | 2012-08-14 23:45 | 14 | 18 | 4937981 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER BELW UP//SERVICER OPENED LINE FUSE INORDER TO CLEAR UP AND ISOLATE TRANSFORMER//COD 14// VER/DBM IDC XXXX
15938 | Hazard | 3303902 | LESLIE | WOOTON | 2019-04-02 16:41 | 2019-04-02 17:44 | 4 | 63 | 4051471 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | COGINELL INSULATOR BROKE NO POWER OUT AT THIS TIME. WILL HAVE TO OPEN WHEN REPAIRS ARE MADE Released by crew 077S01 clamp open at 16:41, power restored at 17:44 L3/HFP
15939 | Pikeville | 3413402 | GARRETT | LACKEY | 2012-05-07 18:56 | 2012-05-07 20:20 | 3 | 84 | 4757111 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT /// APPEARS FUSE BROKE /// POWER RESTORED @ 20:20 COD-3 ISO TF 37830135000026 VER/HFP L3/HFP IDC XXXX
15940 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-09-25 21:29 | 2011-09-25 23:35 | 2 | 126 | 4915741 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 496-180, REPLACED CUTOUT RESTORED POWER AT 23:35 IDCC CDC83 XXXX
15941 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-05-17 02:22 | 2010-05-17 03:25 | 4 | 63 | 63531-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR 35143752 POLE 1147-4181 BAD CUTOUT VER/ARN IDC XXXX
15942 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-04-27 12:50 | 2017-04-27 14:56 | 2 | 126 | 4687721 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWERBAD TRANS CUTOUT ON 113-88 I SPOKE TOO CUSTOMER KIM SCOTT VIA PHONE 606-794-1310 SHE GAVE ME PERMISSION TO ACCESS POLE REPLACED CUTOUT RESTORED POWER AT 14:56 38821130000088 VER/AWD L3/HFP XXXHFP
15943 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-10-27 09:13 | 2012-10-27 10:37 | 3 | 84 | 4175701 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN PATROLING LINE 245-209/ISOLATED ON 245-225 POLE IN INACTIVE SOMETHING WRONG ON 245-236/NO CREW REQUIRED REQUIRED AT THIS TIME NEED TO SEND TO TECH ABOUT HAVING INACTIVE LINE REMOVED OR BURNT OFF POLE FIXED//COD 3//MD FILED//EMAILED TO TECH// VER/DBM IDC XXXX
15944 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-11-29 11:23 | 2012-11-29 12:05 | 6 | 42 | 4430701 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BY-PASS CONNECTION HEATING ON MIDDLE AND RD PHASE REG. REG ON IN NEUTRAL - DISCS OPEN CTRLS OFF & TAGGED. PAUL MUNCEY CLEARED UP PROBLEM VIA STICKS. IDC XXXX
15945 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-03-28 11:54 | 2010-03-28 13:18 | 3 | 84 | 55187-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 6T FUSE OUT I WILL BE CHANGING OUT. CHANGED CUTOUT FUSED UP EVERYTHING OK. VER/HFP L3/HFP AJB
15946 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2021-04-28 12:17 | 2021-04-28 13:20 | 4 | 63 | 4488681 | 252 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Transformer off from 13:10 to 13:20. Burned out connection repaired LR-Part out call came in at 12:17 on 4/28.
15947 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2013-01-04 19:12 | 2013-01-04 20:15 | 4 | 63 | 4569621 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED INTO === REPLACED FUSE === POWER OK ///VER/CRB L/3 CRB IDC XXXX
15948 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-08-03 21:15 | 2011-08-04 01:27 | 1 | 252 | 4661771 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA/CREW TO CHG/FETR 0100/VEM/POWER RESTORED 0127/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
15949 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-01-04 08:22 | 2009-01-04 09:46 | 3 | 84 | 51203-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401103///...CUTOUT BROKEN...CHG CUTOUT..BB VER/TOM L3/TOM IDC XXXX
15950 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2008-06-28 10:43 | 2008-06-28 14:55 | 1 | 252 | 57358-1 | 252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE CALLED FOR BIG BUCKET & 1 MAN == FLAGERS == REPLACED CUTOUT ==COD -1 37830151000026 LINE FUSE POLE MD FILED VER/KEP IDC XXXX
15951 | Whitesburg | 3314401 | MAYKING | ERMINE | 2018-04-10 17:38 | 2018-04-10 21:50 | 1 | 252 | 4208111 | 252 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr burnt secondary bushing into power restored at 21:50/ ISO 37830449D10933/ COD 1
15952 | Pikeville | 3402003 | KEYSER | MULLINS | 2016-12-24 07:16 | 2016-12-24 11:27 | 1 | 251 | 4233811 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE PULLED INTO @ POLE 103-52, REFUSED @1127.//COD 1
15953 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2009-07-30 18:39 | 2009-07-30 22:50 | 1 | 251 | 57645-1 | 251 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3400101// CUST HAS ONE WIRE ON SER BURNED OPEN -----WIRE CONNECTOR BURNED INTO// VER/DBM IDC XXXX
15954 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2020-10-18 12:19 | 2020-10-18 16:30 | 1 | 251 | 4565631 | 251 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad conn. at 151/19 calling help
15955 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-11-30 18:04 | 2010-11-30 22:15 | 1 | 251 | 61418-1 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37934094 //....BAD CUTOUT ON 1139-B-40.....STILL ARCING.....WILL HAVE TO OPEN LINE TO SAFELY CLEAR BAD CUTOUT UP....CAN REPLACE....// SEE 61462-1 FOR OUTAGE TO ISOLATE TROUBLESTS WR # 37934094 //....BAD CUTOUT ON 1139-B-40.....STILL ARCING.....WILL HAVE TO OPEN LINE TO SAFELY CLEAR BAD CUTOUT UP....CAN REPLACE...OPENED RECLOSER ON 1138-C-235 @ 21:38.....CLOSED BACK AT 21:43.....REPLACED BAD XFMR CUTOUT....BACK ON @ 22:15.....JRV......11/30/10 COD-1 VER/HFP L3/HFP IDC XXXX
15956 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-11-30 21:25 | 2016-12-01 01:36 | 1 | 251 | 4154821 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 32-C-2 I CAN REPLACE CUTOUT REPLACED CUTOUT RESTORED POWER AT 01:36
15957 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-02-02 12:39 | 2014-02-02 16:50 | 1 | 251 | 4336841 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD TRANSFORMER 10KVA NO TRUCKS BRING YARD DOG/YELLOW CAUTION TAPE IN TREE AT ADDRESS BROWN VINYL SIDING RELEASED BY CREW 078S03//COD 1// VER/DBM
15958 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-01-05 11:31 | 2011-01-05 15:42 | 1 | 251 | 58912-1 | 251 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK COMPLAINT///////SERVE-IN CONNECTION(HOT LEG)HAD COME APART,REPAIRED AND RESTORED,ALL OK AFTERWARDS VER/HFP L3/HFP IDC XXXX
15959 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-06-27 18:31 | 2019-06-27 22:42 | 1 | 251 | 4608781 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva xfmr, replaced xfmr restored power at 22:42
15960 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-02-11 16:49 | 2012-02-11 21:00 | 1 | 251 | 4336511 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER.CREW NOTIFIED.HAND CHANGE ..NOT TRUCK ACCESSIBLE.///VER/CRB IDC XXXX
15961 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-03-01 10:19 | 2018-03-01 14:30 | 1 | 251 | 4892981 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | the cutout is broke into on the pole. please send to George Whitaker Released by crew 077S12 POWER RESTORED AT 14:30 COD-1 ISO TF 37830427B00259
15962 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-01-07 12:49 | 2018-01-07 17:00 | 1 | 251 | 4717661 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no reading on meter/no crew requirered/ ISO 38830245D00255/ COD 1
15963 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-08-06 11:39 | 2022-08-06 15:50 | 1 | 251 | 4691471 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced cutout and restored @ 15:50. sh
15964 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2010-11-28 18:08 | 2010-11-28 22:19 | 1 | 251 | 60342-1 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#37894068 BAD TRANS. NO TRUCKS RELEASED BY CREW 078S08/SCOUTING TRACK BUCKET ROUTE/FETR2357/VEM/REPAIRS MADE AND POWER RESTORED 2219/PLEASE CLOSE TICKET/THANKS/VEM VER/PDP IDC XXXX
15965 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-04-11 11:19 | 2020-04-11 15:30 | 1 | 251 | 4620961 | 251 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot lead in srevice brunt into repaired service power ok
15966 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-12-27 15:13 | 2016-12-27 19:24 | 1 | 251 | 4243461 | 251 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | S/D NEEDS REPAIRED 37830318A001122/3 SERVICE DAMAGED NEEDS REPLACED, LOOKS LIKE ITS BURNT IN TWO MIDSPAN AND BAD CONNECTION AT SEC. POLE. RELEASED BY CREW 077S04..CREW ON SITE P.HICKS..FOUND BAD CONNECTION, REPLACED SERVICE ANYWAY..ALL POWE RESTORED @ 19:24 P.HICKS..LEFT CUSTOMERS DISC TURNED OFF. CALLED CUSTOMER TO INFORM THEM OF DN SWITCH/AWD 37830318A00112 VER/AWD
15967 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-01-16 11:39 | 2009-01-16 15:50 | 1 | 251 | 56071-1 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD TRANSFORMER, CALLING FOR HELP RELEASED BY CREW 077S02 COD-1 L3/HFP
15968 | South Williamson | 3202201 | LOVELY | LOVELY | 2019-10-09 13:49 | 2019-10-09 18:00 | 1 | 251 | 4124511 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke and has burned pole halfway into//help coming with crossarm to band-aid pole and replace cutout//repairs made//restored at 18;00///complete/em
15969 | Hazard | 3303902 | LESLIE | WOOTON | 2014-01-07 09:34 | 2014-01-07 13:45 | 1 | 251 | 4248601 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA 19.9 120/240 RELEASED BY CREW 077S01//COD 1// VER/DBM
15970 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-12-06 06:30 | 2013-12-06 10:41 | 1 | 251 | 4104881 | 251 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CREW REQUIRED--BAD UG--320 AMP SERVICE--NEED POWER TEMP-- RELEASED BY CREW 078S07 VER/SEF L3/HFP
15971 | Whitesburg | 3401301 | FLEMING | NEON | 2012-10-15 12:49 | 2012-10-15 17:00 | 1 | 251 | 4143041 | 251 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I REPLACED SQUEEZE-ON CONNECTOR ON XFMR POLE ///VER/CRB L/3 CRB IDC XXXX
15972 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2020-07-12 08:19 | 2020-07-12 12:30 | 1 | 251 | 4154371 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulator on pole 305-140, I need a lineman and manual row. crew to cut around pole and path to pole
15973 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-07-11 08:18 | 2012-07-11 12:29 | 1 | 251 | 4680021 | 251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQ, BAD 10KVA 7200, TRUCK OK IN YARD, REPLACE WITH AT LEAST 15KVA, RELEASED BY CREW 078S05/CREW ON SITE/FETR1330/VEM/REPAIRS MADE AND POWER RESTORED 1229/PLEASE CLOSE TICKET/THANKS/VEM
15974 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-01-31 13:00 | 2015-01-31 13:50 | 5 | 50 | 4977461 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #2 SEC. NEUT. HAS BURNED IN TWO IN MID SPAN // NEED LINE CREW, FLAGGERS, 150 OF 1/0 TWIST TO REPLACE// SEC. SPLICE OVERHEATED BURNING NEUT. APART /OPENED XFMR AT 13:00//POWER RESTORED @ 13:50// CUST.S MAY HAVE DAMAGES SEND TO PEGGY WYSONG/ ISO 37820025D00124/ COD 5/ VER/BOW
15975 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-12-30 22:45 | 2014-12-30 23:35 | 5 | 50 | 4893851 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE BAD CONNECTION ON POLE, GOING TO RE-SQUEEZE CONNECTIONS,,,RE-SQUEEZED CONNECTIONS POWER BACK ON.///OPENED XFMR AT 10:45 CLOSED BACK AT 11:35/ ISO 38831125D00420/ COD 5/ VER/BOW
15976 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-05-12 23:12 | 2009-05-13 01:17 | 2 | 125 | 50184-1 | 250 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3411901// SERVICE DROP HAS TREES BRANCHES LAYING ON WIRE, ALSO CUSTOMER HAS EQUIPMENT DAMAGE IDC XXXX
15977 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-10-24 07:20 | 2009-10-24 09:25 | 2 | 125 | 50951-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP 3417602// TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. FUSE LINK HAD BROKEN. I REFUSED TRANS. COD-2 IS TF 38820941D00190 L3/HFP IDC XXXX
15978 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2009-05-03 22:07 | 2009-05-03 22:32 | 10 | 25 | 64657-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TRANSFORMER AT 22:07... REPLACED TRANSFORMER CUTOUT, ALL WORK COMPLETE / GXJ VER/ARN IDCC TOF2121 XXXX
15979 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-04-08 15:04 | 2010-04-08 19:14 | 1 | 250 | 61026-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34588493 // BAD CUTOUT, CALLED R MARCUM FOR HELP, SEND THIS TO RANDALL RELEASED BY CREW 080S01BAD CUTOUT, CALLED R MARCUM FOR HELP, SEND THIS TO RANDALL RELEASED BY CREW 080S01 RELEASED BY CREW 079H02//COD 1// VER/DBM IDC XXXX
15980 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-05-04 04:33 | 2015-05-04 08:43 | 1 | 250 | 4386681 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK DURING NORMAL WORK HOURS, XFMR FUSE BLOWN ON POLE 520-73, LOOKS LIKE IT JUST BROKE RESTORED POWER AT 08:43./COD 1// VER/ ADH
15981 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-08-30 12:48 | 2019-08-30 16:58 | 1 | 250 | 4965231 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | finally found problem, service neutral burnt into serving a barn, repaired
15982 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-09-21 14:00 | 2019-09-21 14:50 | 5 | 50 | 4043941 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Secondary bushing busted on a CSP 25 kva / 7200 trans. on pole 73-D-303, this will take a line crew with a big bucket, will need a 25kva and a cutout and bracket, power is on at this time but will have to open trans. to make repairs when crew arrives. This also needs a bust anchor reinstalled, its pulling customers mast over. Rick Ray coming to change out. Released by crew 074S05. CREW ONSITE//OFF @ 1400 ON @ 1450
15983 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-11-02 15:23 | 2019-11-02 19:33 | 1 | 250 | 4285021 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced: c/o--60 2/3 srv--con at tran and weatherhead ---and advised cust get with landlord and get mtr base replaced --ds110219
15984 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2009-11-11 09:40 | 2009-11-11 11:45 | 2 | 125 | 60062-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP RELATED TO ORDER 57882-1 THIS ORDER IS FOR THE TRANSFORMER OUTAGE TO ALLOW CREW TO MAKE REPAIRS IN THAT ORDER...REMOVED HOT TAP AT POLE 37830164000196 AT 08:40 , TRANSFORMER ON POLE 196 STILL IN SERVICE ... OPENED TRANSFORMER ON POLE 196 AT 09:40 ... ALL WORK COMPLET / GXJ /// CREATED ORDER 60041-1 & 60062-1 FOR OUTAGES IN THIS ORDER. L3/HFP IDC XXXX
15985 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-03-05 11:35 | 2009-03-05 15:45 | 1 | 250 | 55242-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3401702// ANOTHER CURRENT LIMITING FUSE FAILED. THE TRANSFORMER FUSE WAS NOT BLOWN. THE CURRENT LIMITING FUSE JUST BURNED UP. WE HAVE HAD SEVERAL OF THESE FAIL IN THE LAST FEW WEEKS.//COD 1// VER/DBM IDC XXXX
15986 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-05-14 21:30 | 2012-05-14 21:40 | 25 | 10 | H4793671 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FOUND FUSE BLOWN ON PRIMARY UNDERGROUND RISER POLE, TRIED ONCE WITH A 6T CAME OUT, THEN I ISOLATED RUN OF CABLE FRROM POLE 901-5650 TO PAD MOUNT TRANSFORMER 901-5701, TRIED AGAIN, FUSE CAME BACK OUT AGAIN, HAVE CALLED FOR CREW TO HELP ME WITH THIS. CABLE FROM POLE TO PAD IS OLD CABLE WITH NEUTRAL ON THE OUTSIDE. RELEASED BY CREW 078S06//OPENED AT 901-7021@ 21:30 TO CLOSE AT PAD MT 901-5700 POWER RESTORED AT 21:40 BAD CABLE BETWEEN 901-5650 TO 5701 TAGGED W/HOLD CARD //VER/CRB L/3 CRB IDCC CDC94 XXXX
15987 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-01-03 09:15 | 2016-01-03 13:25 | 1 | 250 | 4582191 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN THE SERVICE DROP HAS FAILED AND BURNED THE NEUTRAL INTO. NEED THIRTY FEET OF 1/0 TRIPLEX, AND THREE 500 MCM TO 1/0 CONECTORS, AND A PRESS TO MAKE THE CONNECTIONS. POWER IS RESTORED, ONLY ONE CUSTOMER WAS OFF./ ISO 38821137A00327/ COD 1/ VER/BOW
15988 | Hazard | 3310502 | HADDIX | CANOE | 2019-09-05 17:45 | 2019-09-05 19:50 | 2 | 125 | 4985241 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse broke. restored power at 19:50
15989 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-08-14 14:25 | 2008-08-14 16:30 | 2 | 125 | 52028-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001003// 2ND TIME CSP HAS TRIPPED THIS MONTH, RESET AGAIN, VOLTAGE OK, NEED NEW 37.5 KVA XFMR AND CUTOUT, TRUCK OK, NOT ON FUSE WILL TAKE OUT LINE IF IT GOES BAD.//COD 2// VER/DBM IDC XXXX
15990 | Hazard | 3309904 | SLEMP | ROYAL DIAMOND | 2009-09-26 10:29 | 2009-09-26 12:34 | 2 | 125 | 63704-1 | 250 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOST TRANSMISSION LINE CREWS WORKING TO RESTORE VER/KEP L3/KEP IDC XXXX
15991 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2008-03-27 07:38 | 2008-03-27 11:48 | 1 | 250 | 61195-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3000304// BAD PRI INS. POLE 21-529 RELEASED BY CREW 078S08/TWO FUSES OUT ON POLE 21-28/CREW OPENED REMAINING FUSE TO CHG INSULATORS/FETR1200/VEM/REPAIRS MADE FUSES BACK IN AT 1148/VEM VER/KEP IDC XXXX
15992 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2022-06-14 11:05 | 2022-06-14 11:30 | 10 | 25 | 4102311 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opened xfr on 809-445 at 11:05.. secondary burned into. repairing..
15993 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-05-26 11:05 | 2011-05-26 13:10 | 2 | 125 | 4172701 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT OPEN AT XFMR POLE. XFMR CUTOUT WILL ALSO NEED TO BE CHANGED AS IT IS TRACKING WITH THE FUSE BLOWN AND I DONT HAVE THAT TYPE OF DOOR TO REPLACE IT WITH. OPENED XFMR ON 881-142 @ 12:00. CLOSED XFMR AT 13:10 BUT HAD TO LEAVE ONE CUSTOMER OUT UNTIL THEY MAKE REPAIRS. SH//COD 2// ISO 38830881000142
15994 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2019-04-25 11:46 | 2019-04-25 15:56 | 1 | 250 | 4157841 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 38830190000107 bad 15kva 7200 2 bushing can.on left viewed from source.crew in route .open 3 cut outs . ground and tag to Mr McCoy at 83-190/27.lh,ds042519 Released by crew 078H08 crew on site FETR 16:00 all pwr restored @ 15:56 please close ticket LRM
15995 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-02-29 03:15 | 2008-02-29 05:20 | 2 | 125 | 51370-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PAD MOUNT TRANSFORMER FUSE BAD ( FAILED) ** SEVR RETURNING TO SHOP FOR NEW FUSE... CC/2 ** OFF 0315- REST 0520 IDC XXXX
15996 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2014-10-23 18:35 | 2014-10-23 22:45 | 1 | 250 | 4657331 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 074H17 NEUTRAL BURNT INTO IN MID SPAN BETWEEN TRANSFORMER POLE 1121-195 AND SEC POLE 1121-409. FIELD VIEW SHOWS THIS TO BE 1/0 SEC BUT WAS ACTUALLY 2/3 NOT SURE IF THIS SHOULD HAVE BEEN CHANGED TO 1/0 AT SOMETIME. WE INSTALLED 1/0 BACK. CUST SAID THEY DID HAVE DAMAGE. SEND THIS TO PEGGY IN DAMAGE CLAIMS WE WILL PROBABLY GET A CALL ON THIS. AND IT WAS DUE TO NEUTRAL BURNT OPEN IN MID SPAN.// EMAILED PEGGY/ COD 1// VER/ ADH
15997 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2012-01-21 22:45 | 2012-01-21 23:35 | 5 | 50 | 4281391 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED, OPENWIRE SECONDARY BURNT DOWN AT POLE 38830206A31066, ALL WIRE IN CLEAR, XFMR IS STILL ENERGIZED, #4 SOLID COPPER, SEVERAL FEET BURNT UP, TRUCK OK, COULD USE TREE TRIMMERS. RELEASED BY CREW 078S05/XFMER OPEN@22:45// POWER REST. @23:35 J. HEMLEPP // VER/TOM L3/TOM IDC XXXX
15998 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-05-12 21:25 | 2009-05-12 23:30 | 2 | 125 | 50080-1 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 228-145 WE HAVE LINE C/O BROKE // MD MADE // IDC XXXX
15999 | Hazard | 3302704 | HAZARD | KENMONT | 2012-04-20 18:40 | 2012-04-20 20:45 | 2 | 125 | 4691161 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT. OPENED TRANSFORMER ON POLE 37830296C20466 AT 18:40... THEN OPENED LINE FUSE ON SAME POLE AT 18:55. WAITING ON CREW.. RELEASED BY CREW 077H18 // PLEASE UPDATE THE FETR // SEE 4691331 FOR FUSE OUTAGE // COD-9 ISO TF 37830296C20466 VER/HFP L3/HFP IDCC CNT9, PN288, CDC83, TOF1748 XXXX
16000 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2017-05-26 11:02 | 2017-05-26 13:07 | 2 | 125 | 4866101 | 250 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SEC SPLICE FAILED VER/CRB
16001 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2014-06-26 13:35 | 2014-06-26 17:45 | 1 | 250 | 4159481 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1148-6513 BAD 15 KVA TRANS. B PHASE 120/240 TRUCK TO POLE RELEASED BY CREW 078S08 VER/CRB
16002 | Pikeville | 2974101 | BIG ROCK STATION | CONAWAY | 2014-11-26 16:59 | 2014-11-26 21:09 | 1 | 250 | H4804461 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 CUST OUT SINCE 1659//L/F ON POLE 37820175000005 OPENED @ 1821//COD 6//CUTOUT BROKE ON POLE # 151-203 NO TRUCK/// OPENED LINE FUSE ON POLE# 175-5 @ 18:21 TO ISOLATE TROUBLE/// NEED 1 MAN// REPAIRS MADE AND CLOSED IN LINE FUSE ON POLE # 175-5 @ 21:09 AND RESTORED SERVICE///// SEND TICKET TO CLIFF FREEMAN ABOUT POLE # 151-203 BEING BURNT VER/CRB
16003 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-02-22 18:20 | 2022-02-22 22:30 | 1 | 250 | 4531781 | 250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customers service had burnt out. resagged and re squeezed connections. power restored/ ISO 37830356B00003/ COD 1
16004 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-02-15 14:05 | 2009-02-15 18:15 | 1 | 250 | 62107-1 | 250 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | APPEARS TO BE A PROBLEM ON THE POLE AT THE XFR,WILL REPAIRAPPEARS TO BE A PROBLEM ON THE POLE AT THE XFR,NEED HELP,CREW ENROUTE1 SEC COND ROTTED INTO,ALSO PRIM N WAS GONE ,PUT NEUTRAL BACK IN,ALL OK AFTERWARDS//COD 1
16005 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-05-17 11:11 | 2016-05-17 15:20 | 1 | 249 | 4225621 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN 222-126 TO 198-83 TREE PERSONNELL ON SITECREW REQUIRED FROM 198 83 T0 84 #4 COPPER TRANSFORMER OPEN TRUCK TO 126 ONLY RELEASED BY CREW 078S03 HAD TO REPLACE ONE SPAN OF NEUTRAL POWER RESTORED AT 15:20 VER/AWD /// NEED MORE INFO WHAT WAS OUT? HFP
16006 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-03-26 14:22 | 2012-03-26 15:45 | 3 | 83 | 4618721 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S07//REPLACED SECONDARY CONNECTIONS//COD 3//ISO 69-A3-1089// VER/DBM IDC XXXX
16007 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-04-16 14:32 | 2015-04-16 15:55 | 3 | 83 | 4326611 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | //REPLACING FAILED TRANSFORMER CUTOUT. VER/CRB
16008 | Hazard | 3303902 | LESLIE | WOOTON | 2016-07-14 17:51 | 2016-07-14 22:00 | 1 | 249 | 4635221 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON POLE37830437A20328 15KV, NEED CREW AND BUCKET,1 15KV TRANSFORMER AND 72KV CUTOUT AND BRACKET,TRUCK ACCESSIBLE RELEASED BY CREW 077H07//COMPLETE 2200 ON 07-14 VER/CRB
16009 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2022-07-06 09:51 | 2022-07-06 14:00 | 1 | 249 | 4395751 | 249 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot lead has come out of bushing on bank pole 786-32 checking. opened @ 13:50 to make repairs. closed @ 14:00
16010 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-03-28 05:12 | 2009-03-28 06:35 | 3 | 83 | 62320-1 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/ARN IDCC CNT1 XXXX
16011 | Whitesburg | 3312901 | JENKINS | KONA | 2018-04-16 18:46 | 2018-04-16 21:45 | 3 | 179 | 4242211 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 37830404D00133 manual need one man will need to open line fuse on pl 37830404D00043 to safety change cutout 2 additional customers/ opened 37830404D00043 @ 2110 and closed @ 2145
16012 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2015-02-25 07:06 | 2015-02-25 11:15 | 1 | 249 | 4079541 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER. DUTY SUPERVISOR NOTIFIED AND HE WILL BE SENDING CREW ASAP. RESTORED @ 11:15. SH/ ISO 38830738A00078/ COD 1/ VER/BOW
16013 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-09-22 16:21 | 2017-09-22 20:30 | 1 | 249 | 4382951 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED 15KVA TRUCKS OK/ VER/KEP VER/ALB
16014 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-09-07 06:50 | 2012-09-07 10:59 | 1 | 249 | 4025811 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA NEED 15 OR 25 KVA TRUCK TO POLE NEED TO GO TO 2424 RT. 207 HAVE TALKED TO CUST THERE RELEASED BY CREW 078S08 (POWER RESTORED AT 10:59) VER/KEP IDC XXXX
16015 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2018-04-21 06:35 | 2018-04-21 10:44 | 1 | 249 | 4260341 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | wire fell out of hot line clamp going to csp xfmr. I put new hot line clamp on/ ISO 37830423C00136/ cOD 1
16016 | Pikeville | 3421001 | BREAKS | CITY | 2018-06-26 10:06 | 2018-06-26 12:45 | 4 | 159 | 4669111 | 249 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | A phase cutout going bad on on pole 37820220C20145, will have to open all 4 l/fs @220-C2-145 to make repairs, will keep track of times. Opened all 4 l/fs @1215, made repairs and closed back in @1245.
16017 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-05-16 13:23 | 2020-05-16 14:46 | 3 | 83 | 4842401 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp termination broke , I replaced it
16018 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-01-24 18:26 | 2012-01-24 22:35 | 1 | 249 | 4290771 | 249 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CUSTOMER IS ONLY GETTING 120V IN METER BASE.VOLTAGE ON POLE CHECKED GOOD, 4/0 UNDERGROUND SERVICE MUST HAVE A CONDUCTOR OPEN.WILL NEED A 3MAN CREW //DALE HAMILTON & PAUL LAYNE & TOM MCCOWN // OPENED XFMR @ 22:00 ON @ 22:35.TEMPORARY REPAIRS MADE (AUTO TRANSFORMER), WILL HAVE TO WORK IN THE MORNING COD-4 ISO TF 38831126A00461 SEE DUP H1164300-1 FOR 3 CUST OUTAGE.. VER/HFP L3/HFP IDC XXXX
16019 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-03-15 07:42 | 2009-03-15 09:05 | 3 | 83 | 58713-1 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3413401 - REPLACED CUTOUT, INSTALLED ANIMAL, GUARD, AND REPLACED INSULATOR ... ALL WORK COMPLETE / GXJ //VER/GAH IDCC CNT1 XXXX
16020 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-04-26 10:01 | 2015-04-26 14:10 | 1 | 249 | 4366951 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND BLEW LINE FUSE 38830783000122 THATS NOT ON MAP. PLEASE ADD THIS 10T LINE FUSE TO MAPS. REPLACING CUTOUT. REPLACED CUTOUT AND CLOSED LINE FUSE 783-122 @ 14:10. SH/ ISO 38830783000122/ COD 1/ VER/BOW
16021 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-11-11 20:37 | 2021-11-11 22:00 | 3 | 83 | 4081231 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Tommy morris reports issue whith transformer and line fuse. Burnt up dead end insulator on pole 352-289. Power restored at 22:00.
16022 | Hazard | 3310502 | HADDIX | CANOE | 2020-07-12 21:11 | 2020-07-13 01:20 | 1 | 249 | 4156181 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got broke 19.9 transformer cutout on pole 37830075000166 behind the house manel need a crew Released by crew 077S05 replaced cutout and restored power at 01:20
16023 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-04-23 08:52 | 2018-04-23 10:15 | 3 | 83 | 4264141 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Old cutout, fuse appears to be broke. Replaced cutout, arrester and bracket. Restored @ 10:15. sh L3/HFP
16024 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-01-08 10:30 | 2014-01-08 11:53 | 3 | 83 | 4258831 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND SERVICE DROP BURNT DOWN , DUE TO BAD CONNECTION AT WEATHER HEAD, TCM// OPENED TRANSFORMER AT 10:30 CLOSED BACK IN AT 11:53 TCM/ VER/CRB
16025 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-03-19 18:27 | 2012-03-19 19:50 | 3 | 83 | 4595761 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR BAD ON 38830979C00188 TOOK OUT XFMR FUSE HERE & LINE FUSE ON 38830979C00090//COD 3//AED CREATED//// VER/DBM IDC XXXX
16026 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-05-19 12:36 | 2009-05-19 16:45 | 1 | 249 | 65680-1 | 249 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3402801// BAD UG CABLE. CREW ON SITE SETTING TEMPORARY AUTO-TRANSFORMER TO GIVE CUSTOMER FULL POWER UNTIL THIS CAN BE LOCATED AND REPAIRED (LATER DATE). ONLY ONE CUSTOMER AFFECTED. RESTORED AT 16:45. SH// VER/DBM IDCC MCCDL XXXX
16027 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-10-19 10:16 | 2015-10-19 14:25 | 1 | 249 | 4360331 | 249 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT INTO IN SERVICE WILL REPAIR//// REPLACED BAD CONNECTION IN SERVICE DROP AND RESTORED SERVICE @ 14:25/// OLY 1 CUSTOMER AFFECTED VER/KEP L3/HFP XXXHFP
16028 | Hazard | 3310502 | HADDIX | CANOE | 2021-08-06 07:32 | 2021-08-06 08:55 | 3 | 83 | 4010831 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
16029 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-08-07 08:29 | 2017-08-07 12:38 | 1 | 249 | 4233011 | 249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON TRANSFORMER, HAVE TO CLIMB POLE TO CHANGE OPEN LINE FUSE AT 1207 AND BACK ON AT 1238 (NO ADDITIONAL CUSTOMERS AFFECTED) L3/HFP XXXHFP
16030 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-10-04 08:32 | 2009-10-04 12:40 | 1 | 248 | 50750-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308402//POWER RESTORED.//VER/CRB IDC XXXX
16031 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2013-06-26 09:32 | 2013-06-26 13:40 | 1 | 248 | 4400231 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND ARRESTER === NEED LINE CREW ==== CUTOUT UP BETWEEN PHASES ==== POWER ON NOW TOP OF CUTOUT IS BROKE OFF === NEEDS DONE TODAY === MANUAL POLE MAY HAVE TO HAVE OUTAGE TO CHANGE CUTOUT RELEASED BY CREW 077S03 ON SITE WORKING::: CHANGED CUTOUT POWER RESTORED AT 13:40 COD 1 ISO TF 466-44 VER/SEF IDC XXXX
16032 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2021-03-22 05:22 | 2021-03-22 09:30 | 1 | 248 | 4360811 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burned up. repairs made power restored at 0930
16033 | Pikeville | 3413402 | GARRETT | LACKEY | 2015-04-03 17:46 | 2015-04-03 19:50 | 2 | 124 | 4266471 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1-65T FUSE OUT ON POLE 64-9. I OPENED OTHER 2 FUSE UP DUE TO POLE 64-238 BEING BURT OFF. CREW REQUIRED TRUCKS CAN BE USED RELEASED BY CREW 074S11 VER/KEP
16034 | Hazard | 3303902 | LESLIE | WOOTON | 2021-03-19 18:36 | 2021-03-19 20:40 | 2 | 124 | 4356491 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt out. repaired
16035 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2017-01-31 16:10 | 2017-01-31 17:12 | 4 | 62 | 4348881 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY LEAD HAD WAS AGAINST THE CSP TRANSFORMER AND GROUNDED OUT CAUSING THE TRANSFORMER TO OPEN. VER/CRB L3/HFP XXXHFP
16036 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2015-12-07 10:58 | 2015-12-07 11:29 | 8 | 31 | 4515551 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 39831123D16042 FUSE OUT PATROLED LINE SPACER BROKE AND REPLACED POWER RESTORED KWB // SECONDARY SPACER BROKE ON OPEN WIRE // COD-8 ISO TF 39831123D16042 VER/HFP L3/HFP
16037 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-02-23 11:42 | 2014-02-23 15:50 | 1 | 248 | 4428021 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR ON 737-36. NO TRUCK - DIFFICULT LOCATION 150 FT UP STEEP MOUNTAIN. CREW HAS XFMR CHANGED. RESTORED @ 15:50. SH//COD 1// VER/DBM
16038 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-01-07 11:19 | 2009-01-07 11:50 | 8 | 31 | 52497-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BROKE OFF COD-8 VER/KEP L3/KEP IDC XXXX
16039 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-11-02 14:11 | 2010-11-02 16:15 | 2 | 124 | 51040-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT, BAD TRANSFORMER, NEED 10KVA 7200 AND BUCKET TRUCK. MADE OPPS ORDER# 031413302 FOR CREW TO CHANGE TRANSFORMER WED.//CUST WAS OK IF WE CHANGED THIS TOMORROW, CREATED OPS ORDER AND EMAILED TO BRUCE LINDON //COD 2 (SAME CUST ON BOTH ACCTS PER SERVICER)// VER/DBM IDC XXXX
16040 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-02-19 20:56 | 2010-02-20 01:04 | 1 | 248 | 59263-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 33949353 //, ON SITE, SECONDARIES DOWN, CALLED R MARCUM FOR HELP, XFORMER OFF AT 0020, BACK ON AT 0104 VER/JHM IDCC TOF0020 ONE CUSTOMER WAS OFF INITIALLY, PN134 XXXX
16041 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-01-19 09:27 | 2010-01-19 10:29 | 4 | 62 | 56353-1 | 248 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION ON SECONDARY//VER/CRB IDC XXXX
16042 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2019-10-09 10:42 | 2019-10-09 14:50 | 1 | 248 | 4123621 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad 336 to 4/0 connection, and wire damaged. Need two 336 to 336 aluminum connections, and two 336 to 336 connections, also about 8-10ft of 336 aluminum hot leg. Bad connection on Metal structure #38830045C14141. connection repaired
16043 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2019-12-23 16:42 | 2019-12-23 20:50 | 1 | 248 | 4178791 | 248 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | Lug burnt up inside meterbase. also melted meter will do change meter order. all repairs made close ticket. dwest//
16044 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-09-14 18:52 | 2017-09-14 23:00 | 1 | 248 | 4363531 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS 68-115 BAD 37.5 TRUCK TO POLE RELEASED BY CREW 078S08 VER/ARN VER/HFP L3/HFP
16045 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2010-06-01 09:52 | 2010-06-01 14:00 | 1 | 248 | 54715-1 | 248 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S09 RELEASED BY CREW 078M01//VER/CRB IDC XXXX
16046 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2022-01-02 10:12 | 2022-01-02 14:20 | 1 | 248 | 4260231 | 248 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Have secondary burned into off pole 967-A2-1012,Will be making repairs..A bad squeeze on caused 1 AWG secondary to burn into off pole 967-A2-1012,Will be making repairs..Restored at 14:20.
16047 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-01-15 13:06 | 2021-01-15 15:10 | 2 | 124 | 4871391 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke XCO on bank pole, changed XCO and restored service
16048 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-10-29 15:54 | 2012-10-29 20:02 | 1 | 248 | 4184811 | 248 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | HAVE BAD LEG IN 4/0 UNDERGROUND SERVICE, VOLTAGE WAS 123 ACROSS THE HOT LEGS AND 123 ON ONE LEG AND NOTHING ON THE OTHER TO GROUND, ///VER/CRB L/3 CRB IDC XXXX
16049 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-12-19 19:37 | 2008-12-19 23:45 | 1 | 248 | 61018-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003// POLE FIRE AT 38830230000279, ISOLATED AT 239-155, 6 CUST RESTORED AT 22:40, REMOVED INACTIVE PRIMARY AND NEUTRAL FROM POLE 38830230000278, NEED TO RETURN WHEN GROUND IS FROZEN TO REMOVE POLE 230-279 AND XFMR, PLEASE SEND COPY OF TICKET TO LLOYD RAYBURN, FINAL RESTORATION 23:45 VER/LDA L3/KEP IDC XXXX
16050 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-04-30 10:49 | 2008-04-30 11:20 | 8 | 31 | 55674-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//3116101//BROKEN FUSE, CHANGED CUTOUT AND FUSE BARREL/VER/CRB IDC XXXX
16051 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-06-08 06:29 | 2011-06-08 08:33 | 2 | 124 | 4265551 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT VER/KEP IDC XXXX
16052 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-04-19 13:07 | 2008-04-19 17:15 | 1 | 248 | 52341-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT //3308503//VER/CRB AJBC CDC88
16053 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-07-14 14:11 | 2011-07-14 16:15 | 2 | 124 | 4547201 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED UP,WILL REPLACE IT///////REPLACED BAD CUTOUT,CLOSED AND RESTORED,ALL OK AFTERWARDS COD-2 ISO TF 37830165000068 VER/HFP L3/HFP IDC XXXX
16054 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-08-15 14:41 | 2012-08-15 16:45 | 2 | 124 | 4940711 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FAILED//COD 2//REPLACED AND POWER ON @ 1645// VER/DBM IDC XXXX
16055 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-03-03 15:02 | 2022-03-03 16:04 | 4 | 62 | 4564311 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
16056 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2019-08-06 10:55 | 2019-08-06 15:03 | 1 | 248 | 4846421 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | need 25 kva trucks ok with 1/0 service wire Released by crew 078S03 on site FETR 15:40 LRM all pwr restored @ 15:03 please close ticket LRM
16057 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-07-28 12:50 | 2009-07-28 16:58 | 1 | 248 | 53867-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNT UP ON A PHASE... REPLACED GATE RESTORED POWER AT 16:50//NEW POLE IN BETWEEN -172 AND -165//NEW POLE # NOT KNOWN//HAS 20T FUSES ON IT//B PHASE WAS BLOWN//1 CUSTOMER AFFECTED PER SERVICER//MD FILED//ISO ?// VER/DBM IDCC FEC49 XXXX
16058 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-06-20 18:57 | 2014-06-20 19:59 | 4 | 62 | 4129931 | 248 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | POLE 162-32 6T XFMER FUSE REST @19:50MP VER/KEP
16059 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-02-15 17:11 | 2014-02-15 19:15 | 2 | 124 | 4391071 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END PULLED LOOSE..REPLACED 3 SERVE ENDS ON XFMR POLE. COD-2 ISO SO VER/HFP L3/HFP
16060 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2022-08-09 12:11 | 2022-08-09 14:15 | 2 | 124 | 4709441 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10kva/truck ok. tre Released by crew 078S04 transfromer changed and restored at 1415
16061 | Hazard | 3311103 | STINNETT | WENDOVER | 2012-09-12 19:37 | 2012-09-12 23:45 | 1 | 248 | 4043841 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, MANUAL..REPLACED C/O.ALL POWER RESTORED.P.HICKS COD-1 ISO TF 37830435000147 VER/HFP L3/HFP IDC XXXX
16062 | Paintsville | 3401802 | INDEX | HOSPITAL | 2016-01-26 14:11 | 2016-01-26 16:15 | 2 | 124 | 4651701 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHGING.CHG CONNECTIONS ON XFMR POLE AND SECONDARY POLE ALSO.. VER/CRB
16063 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-08-29 22:17 | 2018-08-30 02:25 | 1 | 248 | 4013231 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line crew bad 12 kv c/o, no trks Released by crew 078S07///replaced cutout///closed at 02:25///complete BR
16064 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-01-02 11:41 | 2020-01-02 13:45 | 2 | 124 | 4203911 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | primary pulled out of sleeve.grd tagged on 901-56.grd on 901-56..re sagging wire
16065 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-09-23 08:23 | 2008-09-23 09:25 | 4 | 62 | 66417-1 | 248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3007904//TRANSFORMER LEAD BURNT INTO,,,,,BACK ON VER/TOM IDCC CNT1 XXXX
16066 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-03-23 09:13 | 2020-03-23 13:20 | 1 | 247 | 4501881 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER J GILLEY TRANSFORMER CUTOUT BROKEN HERE. NEED CREW TO REPLACE. WILL CALL BACK ON WHO IS GOING TO REPLACE CUTOUT replaced cutout power restored at 13:20
16067 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-07-08 18:38 | 2008-07-08 22:45 | 1 | 247 | 65044-1 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3301101//BAD 15 KVA TRANSF == NEED 1 MAN BUCKET AND TRANSF , CUTOUT T BRACKET == IDC XXXX
16068 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-06-28 13:53 | 2020-06-28 18:00 | 1 | 247 | 4084541 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | primary wire is down between poles 204-135 and 204-9003, will need line crew and manuel r-o-w crew// RESTORED@ 1800
16069 | Pikeville | 3407103 | TOPMOST | KITE | 2013-01-09 11:58 | 2013-01-09 16:05 | 1 | 247 | 4581031 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 15 KVA TRANSFORMER ( 7.2 KV / 120/240 ), NO TRUCK ACCESS, CAN WINCH . REPLACED TRANSFORMER, ALL WORK COMPLETE / GXJ COD-1 ISO TF 37830233000022 VER/HFP L3/HFP IDC XXXX
16070 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2013-10-16 09:22 | 2013-10-16 13:29 | 1 | 247 | 4939531 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | /POLE 38830045B12128A ROTTED OFF AND FELL--MADE SAFE NEED NEED CREW--30 CL 6 POLE--A POLE NOT IN FIELD VIEW--NEED COMPLETE 100W DD LIGHT--2/3 TWIST TO SPLICE--TRUCKS TO POLE RELEASED BY CREW 078S07,,CREW ON SITE,,REPAIRS MADE, ONLY 1 CUSTOMER WAS OUT,ALL POWER RESTORED RELEASED BY CREW 078H03 VER/CRB L/3 CRB
16071 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2019-11-13 11:37 | 2019-11-13 15:44 | 1 | 247 | 4030621 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50 KVA transformer calling help Released by crew 077S03..CREW ON SITE TO CHANGE XFMR.15:44 ALL POWER RESTORED P.HICKS
16072 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2008-03-27 15:52 | 2008-03-27 19:59 | 1 | 247 | 61283-1 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3008002//2 CROSSARMS ROTTED AND FELL... KNOCKING PRIMARY INTO TRANSFORMER BANK 70-1530//COD 1//ISO 38830070A41530// 3 BAD ARMS WORKING OVER TOP OF PLATFORM BANK / RESAGING CONDUCTORS IN NEXT SPAN # 4// VER/DBM IDC XXXX
16073 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-12-07 19:43 | 2010-12-07 23:50 | 1 | 247 | 64210-1 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 10 KVA TRANS. ON POLE 192-8 IS BAD. I AM CALLING WILLIE FOR HELP.WE CHANGED TRANS. TO A 15KVA. //VER/GAH IDC XXXX
16074 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-04-14 10:33 | 2018-04-14 14:40 | 1 | 247 | 4223671 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer: no answer bad cutout manual one man to help pole 473-343 power restored at 14:40
16075 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-08-02 07:03 | 2013-08-02 11:10 | 1 | 247 | 4615831 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE WILL GO TO LOUSIA BUILDING TO FIND ONE COD-1 ISO TF 38830477000322 VER/HFP L3/HFP
16076 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-07-07 19:48 | 2019-07-07 23:55 | 1 | 247 | 4675261 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | S RAY CREW REQ// METER IS BLANKMETER IS BLANK/// Cutout broke on side of hill/// will need 2 men this is difficult location for 1 man by himself Released by crew 074S02
16077 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-05-26 09:54 | 2015-05-26 14:01 | 1 | 247 | 4464331 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BOBBY REYNOLDS WAS INFORMED WURTLAND RIVER PUMP STIATION HAS A FUSE OUT ON POLE 1098-4005///// BAD 7200///25 KVA XFR 2 BUSHING 240-480 CENTER CAN ON THE BANK.CUSTOMER HAS DROPPED THERE LOAD.CONTACT TONY THARP 606-922-2827 WHEN COMPLTED RELEASED BY CREW 078H19/CREW ON SITE/FETR 1500/VEM/REPAIRS MADE AND BANK RESTORED 1401/PLEASE CLOSE TICKET/THANKS/VEM// VER/ ADH
16078 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-03-12 07:53 | 2012-03-12 12:00 | 1 | 247 | 4570841 | 247 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SERVE END ON SERVICE DROP, HAVE REPAIRS MADE AND POWER IS BACK TO FULL POWER AT THIS LOC VER/HFP L3/HFP IDC XXXX
16079 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2014-01-08 13:23 | 2014-01-08 17:30 | 1 | 247 | 4260791 | 247 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEU. BROKE ON 1/0 LASH CABLE 38830046A20168 REPAIRED NEU. AN 2 HOT LEGS XFORM OFF 16;30 ON 17;30 SEND COPY TO ENG. CHECK SIZE OF SEC. COD-10 VER/HFP L3/HFP IDCC CNT10 CREATED DUP TO OPEN TRANSFORMER XXXX
16080 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-07-09 09:53 | 2019-07-09 10:12 | 13 | 19 | 4683241 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Replacing broke deadend bell.., opened @9:53 closed @10:12 L3/HFP
16081 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-01-30 01:23 | 2014-01-30 05:30 | 1 | 247 | 4326521 | 247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN// WILL REFUSE// BAD 10 KVA// CREW ON THEIR WAY TO REPLACE WITH A 25 KVA/// REPAIRS MADE//POWER IS RESTORED VER/KEP
16082 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-06-02 10:30 | 2022-06-02 14:36 | 1 | 246 | 4997711 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 12kv, truck ok. crew required Released by crew 078S11crewon site FETR 14:40 LRM all pwrrestored14:36please close ticket LRM
16083 | Hazard | 3303902 | LESLIE | WOOTON | 2012-11-19 08:49 | 2012-11-19 12:55 | 1 | 246 | 4407661 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | ELBOW ON UNDERGROUND CABLE PRIMARY BAD === NEED TO REPLACE ELBOW ==REPLACED ELBOW ON UNDERGROUND === REFUSED POWER OK MAP NOT CORRECT IN POWERON // COD-1 ISO DF 37830365000342 VER/HFP L3/HFP IDCC PN287 XXXX
16084 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2016-05-10 19:44 | 2016-05-10 23:50 | 1 | 246 | 4194601 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, HAVE BROKEN CUTOUT, NO TRUCKS, WILL NEED NEW C/O POLE NUM. 18-172 RELEASED BY CREW 078S06,,CREW ON SITE,,ALL REPAIRS MADE,,ALL POWER RESTORED// VER/ ADH
16085 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-09-06 16:47 | 2013-09-06 18:09 | 3 | 82 | 4826371 | 246 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 1 FUSE OUT AT POLE 1084A-300 ***CHANGE ISO POLE*** VER/SEF IDC XXXX
16086 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-07-12 05:59 | 2018-07-12 10:05 | 1 | 246 | 4765071 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm fuse blown will refuse/// Cutout broke this is a difficult location will get ahold of Steve Ray to try to get some help/// Changed bad cutout and restored service @ 10:05
16087 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-10-02 08:44 | 2018-10-02 10:47 | 2 | 123 | 4188531 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | riser out from top of cutout repairs being made. all power restored @ 10:47. pls close. tre L3/HFP
16088 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2011-04-27 16:15 | 2011-04-27 18:19 | 2 | 124 | 65956-1 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 077S03== TRANSF LEAKING == NEED LINE CREW RELEASED BY CREW 077S03
16089 | Hazard | 3309903 | SLEMP | BEECH FORK | 2009-09-26 10:29 | 2009-09-26 12:32 | 2 | 123 | 63703-1 | 246 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOST TRANSMISSION LINE CREWS WORKING TO RESTORE VER/KEP L3/KEP IDC XXXX
16090 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-05-08 07:22 | 2015-05-08 09:25 | 2 | 123 | 4402681 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD 19.9 CURRENT LIMIT FUSE/COD 2// VER/ ADH
16091 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-01-17 14:00 | 2018-01-17 15:22 | 3 | 82 | 4753501 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CUST @ POLE 38830904000017 CALLED IN FOR NEIGHBOR// Line fuse link appears to have broke. Replaced fuse and restored @ 15:22. sh
16092 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2016-10-13 10:44 | 2016-10-13 11:25 | 6 | 41 | 4990411 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WAS BAD I CHANGED IT OUT VER/CRB L3/HFP XXXHFP
16093 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-08-19 16:43 | 2017-08-19 18:05 | 3 | 82 | 4279061 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED SERVICE AND CONNECTIONS ON POLE OPENED XFMR AT 16:43 CLOSED AT 18:05 VER/KEP
16094 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-07-17 16:23 | 2020-07-17 17:45 | 3 | 82 | 4176011 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout,,,complete
16095 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-08-09 05:15 | 2017-08-09 09:21 | 1 | 246 | 4241991 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DISPATCHED IN ACCORDANCE WITH KYPCO LATE NIGHT CALLOUT GUIDELINES, BAD CURRENT LIMMITTING FUSE , REPLACED FUSE APR AT 0921 CLOSE TICKET VER/HFP L3/HFP
16096 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-02-02 12:09 | 2010-02-02 14:12 | 2 | 123 | 62338-1 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE/////XFR IS BAD,WILL BE REPLACING IT.STEVE RAY WILL BE DOING WORK,SEND TICKET TO STEVE RAY,THX TF RELEASED BY CREW 074S06 CHANGED TO 25 KVA FR. 15 KVA.//MADE A MD//VER/CRB IDC XXXX
16097 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-11-25 15:52 | 2008-11-25 19:58 | 1 | 246 | 52278-1 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 1 CUST NEED FLAGMAN POLE 45-2136 RELEASED BY CREW 078S08//3002107// VERY BAD PLACE LOTS OF TRAFFIC STS W/R 27443282//ISO//COD 1// VER/DBM IDC XXXX
16098 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2012-12-26 13:12 | 2012-12-26 15:15 | 2 | 123 | 4529711 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE BLOWED ON POLE# 104-54 WILL PATROL TAP. RE-FUSED LINE FUSE RESTORED SERVICE ///VER/CRB L/3 CRB
16099 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-01-14 13:10 | 2010-01-14 15:13 | 2 | 123 | 54148-1 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 519-168... REPLACED CUTOUT RESTORED POWER AT 15:13 VER/KEP L3/KEP IDCC CDC83 XXXX
16100 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-08-08 10:42 | 2017-08-08 12:45 | 2 | 123 | 4239531 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BAD, CHANGING/ ISO 38830876D00144/ COD 2/ VER/BOW
16101 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2019-07-16 19:32 | 2019-07-16 23:38 | 1 | 246 | 4718411 | 246 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired service drop,opened xfr 902-263 @ 23:14 closed @ 23:38,complete OPENED TFO ON 4709131
16102 | Hazard | 3303902 | LESLIE | WOOTON | 2012-02-24 21:53 | 2012-02-24 23:15 | 3 | 82 | 4501441 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD HOT LINE CLAMP ////VER/CRB IDC XXXX
16103 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-05-14 06:38 | 2018-05-14 10:44 | 1 | 246 | 4345591 | 246 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION @ TRANSFORMER
16104 | Paintsville | 3401101 | FALCON | FALC-OILS | 2021-11-07 10:46 | 2021-11-07 12:08 | 3 | 82 | 4064171 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout failed. Replaced and restored @ 12:08. sh
16105 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-06-20 15:20 | 2014-06-20 19:26 | 1 | 246 | 4124191 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ POLE 303-16 NEED CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05 OPEN 303-13 LINE FUSE FOR CUTOUT REPLACEMENT(IN SEPARATE ORDER?),, CLOSED 1926//COD 1//ISO// VER/DBM
16106 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-08-11 17:08 | 2010-08-11 18:30 | 3 | 82 | 52749-1 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT WE GOT BIG BUCKET COMING O US///REPLACE CUTOUT AND RESTORE POWER//OPEN LINE FUSE AT 18;18 AND RESTORE POWER AT 18;30.... VER/ARN IDCC TOF1818 XXXX
16107 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2020-12-03 13:24 | 2020-12-03 17:30 | 1 | 246 | 4742321 | 246 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad 1/0 ug srv-crew req-ds120320 Released by crew 078S01 all pwr restored 17:30 LRM
16108 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-07-22 21:53 | 2009-07-22 23:15 | 3 | 82 | 63080-1 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BURNT UP VER/TOM L3/TOM IDC XXXX
16109 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2012-01-29 22:27 | 2012-01-30 00:30 | 2 | 123 | 4304041 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | SEC. DEAD END SHOE BROKE AT POLE LETTING HOT LEGS CONTACT NEUTRAL, BURNING NEUTRAL INTO. //VER/GAH IDC XXXX
16110 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-12-06 22:13 | 2022-12-07 00:16 | 2 | 123 | 4236171 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans Cutout broke at 190-B-130,Will be making repairs.Restored 00:16..
16111 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-05-10 10:02 | 2015-05-10 12:05 | 2 | 123 | 4407811 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SPRING BROKE IN OLD TYPE CUTOUT AND BURNT FUSE DOOR UP. REPLACING CUTOUT. REPLACED CUTOUT, ARRESTER AND BRACKET. RESTORED @ 12:05. ONLY TWO METERS AFFECTED SH// VER/ ADH
16112 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2011-05-14 08:12 | 2011-05-14 10:15 | 2 | 123 | 4089531 | 246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT,, CHANGING OUT NOW,,, ALL REPAIRS MADE POWER BACK ON
16113 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2019-05-27 09:47 | 2019-05-27 13:52 | 1 | 245 | 4348791 | 245 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced sec connection at trans pole 113C37
16114 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-10-21 08:30 | 2020-10-21 09:05 | 7 | 35 | 4572301 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Transformer off from 08:30 to 09:05. Connection failed at mast pipe
16115 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-06-19 14:13 | 2019-06-19 18:18 | 1 | 245 | 4547681 | 245 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer service drop burnt up.will replace.restored.
16116 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2010-07-27 18:55 | 2010-07-27 19:30 | 7 | 35 | 58179-1 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ARCED AT CONTACT POINT AND DROPPED OPEN. FUSE NOT BLOWN. CHANGING CUTOUT. REPLACED CUTOUT AND RE-FUSED @ 19:30. SH//COD 7// VER/DBM IDC XXXX
16117 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-06-01 16:00 | 2012-06-01 20:05 | 1 | 245 | 4865711 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED C/O COD-1 ISO LF 37830056000032 VER/HFP L3/HFP IDC XXXX
16118 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-02-24 16:00 | 2011-02-24 20:05 | 1 | 245 | 60827-1 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38936259 //BAD CUTOUT ON POLE 37830249C00018 CREW AND FLAGGERS REQUIRED, DUTY SUPERVISOR NOTIFIED. // SEE 60887-1 FOR RECLOSER OUTAGE TO MAKE REPAIRS ///BAD CUTOUT ON POLE 37830249C00018 CREW AND FLAGGERS REQUIRED, DUTY SUPERVISOR NOTIFIED. OPENED RECLOSERS ON POLE 37830248A41086 AT 18:12, CLOSED AT 20:05 POWER RESTORED. COD-1 ISO LF 37830249C00018 VER/HFP L3/HFP IDC XXXX
16119 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-01-18 10:45 | 2010-01-18 14:50 | 1 | 245 | 55816-1 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | U.G. SERVICE CUT IN CLEAR IT IS ATTACHED TO OLD POLE THERE IS A NEW POLE SET ALL ATTACHMENTS TRANSFERRED WE NEED TO TRANSFER THE U.G. SERVICE TO NEW POLE AND PULL THE OLD ONE BOTH NEUTRAL AND HOT LEG IS NICKED AND HAS CONDUCTOR EXPOSED. THE POWER WAS ON WHEN I ARRIVED. IT WILL REQUIRE A LINE TRUCK AND BUCKET TRUCK AND A 2-OR-3 MAN CREW 4/0 WITH A 2/0 NEUTRAL. TIM MCCOY // VER/DBM IDC CHANGED CAUSE FROM EQUIPMENT, CHANED OFF FROM 0944 PER COMMENTS XXXX
16120 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-01-10 10:25 | 2010-01-10 14:30 | 1 | 245 | 51667-1 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, HELP COMING, POWER RESTORED AT 14:30 VER/KEP L3/KEP IDC XXXX
16121 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-05-09 12:11 | 2011-05-09 16:16 | 1 | 245 | 4022461 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA CSP TRANSFORMER CREW ENROUTE RELEASED BY CREW 074S02//WR#39882938//VER/CRB IDC XXXX
16122 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2018-02-17 13:30 | 2018-02-17 17:35 | 1 | 245 | 4854811 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | will re fuse xfmr. fuselink was broke. not blown, replaced fuse.back on @17:35/ ISO 38831101C10382/ COD 1
16123 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2022-06-29 18:25 | 2022-06-29 22:00 | 2 | 215 | 4348021 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 Secondary burnt down @ 38831121D00403.//Will open XFM 1121D-337 to remove vines and make repairs//XFM open from 21:30 to 22:00
16124 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2016-02-04 09:15 | 2016-02-04 13:20 | 1 | 245 | 4674431 | 245 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CHECK VOLTAGE AT METER, HAD 116 V, PH TO GR, BUT HAD NO VOLTAGE PH TO PH, SUSPECT BAD 4/0 UNDERGROUND, HAVE TRANSFORMER OPEN UP AT THIS LOC, OPEN AT 0915 RELEASED BY CREW 078S06,,SQUIRREL DAMAGE, MAKING REPAIRS, INSTALLING WEATHERHEAD,,,BLR VER/AWD
16125 | Hazard | 3309003 | JEFF | VIPER | 2017-02-15 14:18 | 2017-02-15 18:23 | 1 | 245 | 4400261 | 245 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE BAD IN SECONDARY NEED 2 MEN OR CREW === NEED DROPE SECONDARY DOWN TO WORK ONIT OVER ROAD WAY ===REPAIRED SECONDARY === POWER OK OPEN TRANSF AT 17:54 CLOSED 18:23/ ISO 37830394A00133/ COD 4/ VER/BOW L3/HFP HFPC DUP
16126 | Paintsville | 3401802 | INDEX | HOSPITAL | 2014-08-03 06:25 | 2014-08-03 10:30 | 1 | 245 | 4325961 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4/0 CONNECTIONS BURNED INTO..REPLACING 10 4/0 4 CONNECTIONS..BACK ON AT 10.30 VER/CRB
16127 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-11-11 05:12 | 2017-11-11 07:43 | 2 | 151 | 4548701 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP BURNED INTO,WILL REPAIR////////REPLACED 4/3 WITH 2/3 DROP//////POSSIBLE DAMAGES,SEND TO PEGGY WYSONG////APPEARS SERVE-IN HEATED UP AND CAUSED INSULATION FAILURE////////MAY NOT HEAR FROM CUST BUT IS POSSIBLE
16128 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2016-04-28 08:00 | 2016-04-28 12:05 | 1 | 245 | 4136261 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200,120/240 15KVA. LINE CREW TRK ACC. RELEASED BY CREW 078S07.. CREW ON SITE ETR 12:00.. NEW ETR 12:15 DIFFICULT LOCATION BESIDE OF HOUSE /// ON @ 1205 COD-1 ISO TF 39831123C24533
16129 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2018-12-31 16:30 | 2018-12-31 20:35 | 1 | 245 | 4616481 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 254-408 secondary pole rotted and fail,cut loops at 254-407,,,crew required,,35-5,,trucks to pole Released by crew 078S05 2035
16130 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-08-14 08:46 | 2020-08-14 12:51 | 1 | 245 | 4323991 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva 7200by truck on pole 38830404C40380. not the xfmr that feeds the log house. its the one that feeds the large green building Released by crew 078H03//arrived RM power on @12:51 please close tic RM
16131 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2018-04-07 10:07 | 2018-04-07 10:56 | 5 | 49 | 4198721 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse link
16132 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-09-11 20:55 | 2012-09-11 21:30 | 7 | 35 | 4041051 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 20-5528 8T TRANS FUSE BROKE WRONG FUSE INSTALLED REINSTALLED 10T TRANS FUSEPOLE 20-5528 8T TRANS FUSE BROKE INSTALLED 10T SEND NOTE TO RAYBURN TRANS NEEDS CHGED TO 50KVA TRUCK TO POLE COD-7 ISO TF 38830020C45528 VER/HFP L3/HFP IDC XXXX
16133 | Pikeville | 3403001 | PIKEVILLE | CITY | 2010-02-02 08:09 | 2010-02-02 08:44 | 7 | 35 | 62237-1 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE FOR XFMR IS BLOWN------FUSE APPEARED TO HAVE BROKEN//VER/CRB IDC XXXX
16134 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-04-04 15:05 | 2020-04-04 19:10 | 1 | 245 | 4560651 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR fuse blown // Bad 15kva xfmr cannot access with big truck due to bridge. I have contacted Rick Ray with the details and he will be getting a crew to come make repairs. Released by crew 076S03 RESTORED @ 1910
16135 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-11-14 08:30 | 2012-11-14 12:35 | 1 | 245 | 4396131 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 VER/KEP IDC XXXX
16136 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2015-03-28 11:06 | 2015-03-28 11:55 | 5 | 49 | 4238501 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN. RESTORED @ 11:55. SH/COD 5// VER/ ADH
16137 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-07-21 16:16 | 2017-07-21 20:21 | 1 | 245 | 4152411 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | HAD OUTAGE ON RECLOSER 37830108000116 (ORDER 4151671 - HFP) FEEDING 87 CUSTOMER OPENED @ 214 CLOSED @ 238/ CALLED CUSTOMER RSAID THEY CAME ON THEN WENT BACK OFF AND THEY RESET BREAKERS/ ATTEMPTED TO HAVE CUSTOMER CHECK METER BUT CUSTOMER COULDNT BECAUSE IT WAS SO HIGH OFF THE GROUND COULD SEE IT . FUSE BROKE . CLOSED BACK @ 20-21 . VER/CRB L3/HFP XXXHFP
16138 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-08-13 22:28 | 2016-08-14 02:33 | 1 | 245 | 4772611 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPACING 10KV TRANSFORMER METER # IS 533674354 FOR MAPS THR POLE # IS 905-11..REPAIRS MADE//COD 1//ISO 38830905000011//MD FILED// VER/DBM
16139 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2010-05-07 18:10 | 2010-05-07 22:15 | 1 | 245 | 57143-1 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | GROUND WIRE INTO ON XFMR... BAD CUTOUT WILL NEED BIG BUCKET... REPLACED XFMR & CUTOUT RESTORED POWER AT 2215//COD 1// VER/DBM IDC XXXX
16140 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-10-05 15:00 | 2019-10-05 15:35 | 7 | 35 | 4098601 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened line fuse pole 139-c-125 at 15:00 dut to bad cutout pole 139-c-347. changed cutout closed line fuse back in at 15:35 everything ok
16141 | Pikeville | 3409502 | BURDINE | LEVISA | 2016-11-25 17:07 | 2016-11-25 21:12 | 1 | 245 | 4129931 | 245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | FOUND BAD SPLICE IN SERVICE DROP.REPAIRED AND RESTORED.. VER/TOM L3/TOM AJBC MCCDIS
16142 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2014-07-07 09:38 | 2014-07-07 13:42 | 1 | 244 | 4198411 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT , KEITH CAMPBELL COMING TO HELP. --- REPLACED 3 CUTOUTS FEEDING PRIMARY UNDERGROUND. RELEASED BY CREW 077S04// CLOSED @ 1333 AJB
16143 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-11-04 09:33 | 2010-11-04 11:35 | 2 | 122 | 51660-1 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT TO REPLACE(BROKEN)////////REPLACED CUTOUT AND RESTORED //VER/GAH IDC XXXX
16144 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-03-23 14:19 | 2009-03-23 15:20 | 4 | 61 | 60906-1 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP COD-4 BROKEN FUSE LINK L3/HFP IDCC CCO, FEC57 XXXX
16145 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2009-12-17 06:38 | 2009-12-17 08:40 | 2 | 122 | 51300-1 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. TWO CUSTOMERS AFFECTED. RE-FUSED. SH COD-2 ISO TF 38830784D20484 VER/HFP L3/HFP
16146 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-06-13 14:16 | 2019-06-13 18:20 | 1 | 244 | 4496481 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | current limiting fuse went bad. back in at 18:20
16147 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2018-12-23 17:50 | 2018-12-23 19:52 | 2 | 122 | 4595281 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on take off pole will work 12/24/18 ops order# 030950537//CUSTOMER AGREED TO THIS L3/HFP
16148 | Hazard | 3307301 | BULAN | ARY-HEINE | 2015-09-30 09:51 | 2015-09-30 11:53 | 2 | 122 | H4291811 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 154-123 , BAD CUTOUT ON POLE 154-130 , REPLACED CUTOUT . POLE WILL NEED CHANGED OUT TOMORROW , PUT POLE FIRE OUT SHOULD BE OK FOR TONIGHT . WILL NEED 45 POLE, FIBERGLASS TBRACKET & ARRESTER . ..POLE IS DEAD END XFMR POLE . CAN WORK POLE WITH TRUCKS . CLOSED LINE FUSE BACK @ 21:40 ./ ISO.. 37830154000123/ COD 2..CREW ON SITE, OPEN 154-123 @ 09:51 HRS..CLOSED BACK IN @ 11:53 HRS..ALL POWER RESTORED AND POLE CHANGED OUT.P.HICKS RELEASED BY CREW 077H09 VER/CRB
16149 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2011-04-16 20:41 | 2011-04-17 00:45 | 1 | 244 | 59501-1 | 244 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEAD HAS FALLEN OUT OF XFR BUSHING,WILL TRY TO REPAIR////LUG BROKEN,REPLACED AND RESTORED,ALL OK AFTERWARDS VER/KEP IDC XXXX
16150 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2015-10-02 10:28 | 2015-10-02 12:30 | 2 | 122 | 4302141 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830443000069 === LINE FUSE OUT ON POLE 37830419D20382 === CHANGED CUTOUT === REFUSED LINE POWER OK/CLOSED 1230/FIX IT HOIS// VER/ ADH
16151 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-07-22 16:51 | 2019-07-22 20:55 | 1 | 244 | 4763501 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Reworked all connections on service. sh
16152 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-12-01 12:31 | 2019-12-01 14:33 | 2 | 122 | 4112211 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced bad connections//cod 2
16153 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-06-04 12:21 | 2014-06-04 16:25 | 1 | 244 | 4972171 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA 480 XFMR BAD.CUST OK TO CHG FRIDAY.NO TRUCK.WILL TAKE 4 WHEELER HAND JOB.OKD WITH TIM MILLER.//IO MADE WILL WORK FRIDAY OKD BY CUST VER/CRB
16154 | Paintsville | 3409302 | KENWOOD | AUXIER | 2019-11-14 05:46 | 2019-11-14 06:47 | 4 | 61 | 4032571 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR fuse blown will check and refuse// Fuse link had broke inside cutout door. I put in new fuse and restored power @ 06:47
16155 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2015-11-15 10:03 | 2015-11-15 14:07 | 1 | 244 | 4449321 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN DUE TO SIZE WILL REPLACE WITH 2/3 DROP 4/3 IS WHATS HERE RELEASED BY CREW 077H14SERVICE BURNT DOWN DUE TO SIZE WILL REPLACE WITH 2/3 DROP 4/3 IS WHATS HERE OPENED XFMR AT 13:41 CLOSED BACK AT 14:07 // SEE DUP H4449321 FOR 1 -- ISO TF 37830295D00149 VER/HFP L3/HFP
16156 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-01-27 17:38 | 2010-01-27 21:42 | 1 | 244 | 60501-1 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED A 19.9 DOOR TO CUTOUT. CUSTOMER WAITING AT SITE AND GARTE IS OPEN.......DAH RELEASED BY CREW 074S08RE-FUSED AND RESTOREDRE-FUSED AND RESTORED,HAD TO REPLACE CUTOUT DOOR VER/KEP L3/KEP IDC XXXX
16157 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2022-06-14 11:08 | 2022-06-14 13:10 | 2 | 122 | 4105231 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap burnrd out of the stirrup,,, replacing
16158 | South Williamson | 3411401 | DEWEY | INEZ | 2008-05-11 17:20 | 2008-05-11 21:24 | 1 | 244 | 61680-1 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONN BAD ON POLE 672-D-191 VER/KEP IDC XXXX
16159 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-06-20 18:45 | 2019-06-20 22:49 | 1 | 244 | 4558371 | 244 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | badd connections on pole in back yard customer restored to full power at 22:49
16160 | Pikeville | 3407101 | TOPMOST | DEMA | 2015-10-04 08:36 | 2015-10-04 12:40 | 1 | 244 | 4314691 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT ON POLE 161-182 FAILED, BURNING POLE AT APART AT GUY ATTACHMENT, CAN LOWER, NO EQUIPMENT OR HELP NEEDED . OPS ORDER # 038372504 SENT TO TECH TO CHECK POLE , ALL WORK COMPLETE / GXJ/EMAILED TECH/ADH/ MD MADE/ADH 2 CUSTOMERS REALLY OFF WITH LINE FUSE 161-1// VER/ ADH L3/HFP HFPC PN37830162000001
16161 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-06-14 10:49 | 2010-06-14 14:53 | 1 | 244 | 63436-1 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR 35552712 //CREW REQUIRED BAD 25 KVA TRUCKS OK LAST HOUSE UP GRAVEL ROAD STREET NAME RELEASED BY CREW 078S03/CREW ON SITE/FETR1545/VEM/REPAIRS MADE POWER RESTORED 1453/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB
16162 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-03-30 20:21 | 2015-03-31 00:25 | 1 | 244 | 4245071 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER, 7200 NEED 3 LINEMEN. VER/KEP
16163 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2018-09-30 19:33 | 2018-09-30 21:35 | 2 | 122 | 4183841 | 244 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole
16164 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-06-14 14:16 | 2010-06-14 16:18 | 2 | 122 | 63999-1 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON PRIMARY TAP MCCARTY ON HIS WAY CUTOUT IS 19.9 RELEASED BY CREW 078S02/ 50 T LINE FUSE COD-2 VER/HFP L3/HFP
16165 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-01-06 04:10 | 2017-01-06 08:14 | 1 | 244 | 4272691 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SCADA TRANSMISSION OPERATIONS SUGGEST EAST PRESTONSBURG STATION TRANSFORMER LOCKOUT//COD 609///DKM/0834/ARRESTOR BLEW ON STATION SERVICE PHASE 3/// VER/DKM // NOTE 1 PIKEVILLE CUST ON THIS CKT THIS IS NOT A DUPLICATE = L3/HFP L3/HFP TOF0415
16166 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-06-10 15:26 | 2009-06-10 19:30 | 1 | 244 | 51581-1 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT BROKE CUTOUT ON TRANSFORMER, CALL LASSO AND HE IS GETTING CREW TO COME CHANGE IT OUT RELEASED BY CREW 077S05//VER/CRB IDC XXXX
16167 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2015-03-17 23:13 | 2015-03-18 01:15 | 2 | 122 | 4205661 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT ON POLE 38820941B31653. ILL CHANGE IT OUT. POWER IS BACK ON. VER/SEF L3/DKGXXXX
16168 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-11-28 19:41 | 2015-11-28 23:45 | 1 | 244 | 4490201 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT. NEED ONE LMA AND A BIG BUCKET THAT WILL REACH THE FARTHEST OFF THE SIDE. POLE IS COVERED IN KUDZU AND IS ACROSS THE CREEK. POWER IS RESTORED. SEND TO COREY FARMER TO CUT THE KUDZU OFF THE POLE. VER/TOM L3/TOM
16169 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-12-16 21:13 | 2015-12-16 23:15 | 2 | 122 | 4538491 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3 PHASE SERVICE DROP BURNED DOWN..# 2-4 WIRE..NEED BIG BUCKET AND 100, OF #2 -4 WIRE TRIPLEX853-85. OPENED ALL 3 CUTOUTS ON BANK...WILL INSTALL NEW DROP IN THE AM../EMAILED ROGER/BOBBY/ADH// VER/ ADH
16170 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-09-29 15:28 | 2011-09-29 17:30 | 2 | 122 | 4932271 | 244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. AT XFMR. ON SIDE OF HILL.//COD 1 IDC XXXX
16171 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2021-07-04 22:00 | 2021-07-05 01:30 | 2 | 210 | 4856741 | 244 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY GETTING 120 VOLTS FROM OURSIDE, WILL BE CHECKING. FOUND CONNECTION BAD ON TRANSFORMER MADE REPAIRS. OPENED X-FMR ON 296 AT 00:56 BACK ON AT 01:30
16172 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-08-05 22:57 | 2021-08-06 03:00 | 1 | 243 | 4010421 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva 7200 trans--crew req Released by crew 078S01 crew on site FETR 3:30 LRM all pwr restored 03:00 please close ticket
16173 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-04-19 15:39 | 2008-04-19 17:00 | 3 | 81 | 52400-1 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT RELEASED BY CREW 078H04//3000701//VER/CRB IDC XXXX
16174 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-05-31 16:47 | 2018-05-31 20:50 | 1 | 243 | 4530581 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 809-340.open line fuse at pole 809-294 to make repairs.Repairs complted.left trans open do to customer damage,customer to call back when repairs are made.
16175 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-06-12 18:29 | 2009-06-12 19:50 | 3 | 81 | 58643-1 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 1104-4, WILL REPLACE AND REFUSE///////POWER RESTORED @ 19:50//VER/CRB
16176 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-06-23 08:27 | 2010-06-23 12:30 | 1 | 243 | 55509-1 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR# 35692356 // POLE 140-608 BAD 25KVA 19.9 TRANS NEED SMALL TRAC MACHINE RELEASED BY CREW 078S08/ J. HEMLEPP & CREW ON SITE/// XFMER CHANGED OUT.// CUST. RESTORED @ 12:30/// 6-23-2010 J. HEMLEPP IDC XXXX
16177 | Hazard | 3420001 | SOFT SHELL | VEST | 2020-02-11 10:32 | 2020-02-11 11:53 | 3 | 81 | 4392131 | 243 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | broken cutout on xfmr bank, going to replace all 3, power restored
16178 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-06-10 16:19 | 2017-06-10 17:40 | 3 | 81 | 4929491 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKE FUSE/ ISO 37830127B10151/ COD 3/ VER/BOW
16179 | Paintsville | 3409302 | KENWOOD | AUXIER | 2013-11-13 17:39 | 2013-11-13 19:00 | 3 | 81 | 4037021 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE ON XFMER FUSE @ POLE 882-323///GOING TO REFUSE////REFUSED AT 19:00 RESTORING ALL CUST.///COMPLETE BR VER/CRB
16180 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2017-10-28 17:24 | 2017-10-28 18:45 | 3 | 81 | 4506061 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 103-140 WILL CHANGE CUTOUT/// LIFTED HOT TAP ON POLE 103-34 TO ISOLATE TROUBLE//// CHANGED CUTOUT AND RE-ENERGIZED @ POLE 103-34 AND RESTORED SERVICE @ 18:45 VER/AWD L3/HFP HFPC LCD37820103B00034
16181 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-01-06 10:03 | 2022-01-06 11:24 | 3 | 81 | 4311191 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pulled in two on transformer
16182 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-05-02 09:07 | 2015-05-02 13:10 | 1 | 243 | 4383521 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED TRANSFORMER , ALL WORK COMPLETE / GXJ VER/CRB
16183 | Whitesburg | 3309302 | VICCO | JEFF | 2010-03-30 12:32 | 2010-03-30 16:35 | 1 | 243 | 56010-1 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY LUG BURN OFF ==CALLED FOR LINE CREW AND TRANSF == VER/KEP L3/KEP AJB
16184 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2022-12-19 22:34 | 2022-12-19 23:55 | 3 | 81 | 4278091 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse//cod 3
16185 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-11 08:07 | 2009-06-11 12:10 | 1 | 243 | 57932-1 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP REPLACED XFMR FUSE L3/HFP IDC XXXX
16186 | Pikeville | 3413401 | GARRETT | GARRETT | 2011-07-04 19:19 | 2011-07-04 20:40 | 3 | 81 | 4463201 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT, ALL WORK COMPLETE / GXJ COD-3 ISO TF 37830065D00198 VER/HFP L3/HFP IDC XXXX
16187 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-10-07 18:07 | 2022-10-07 22:10 | 1 | 243 | 4005461 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | loop burnt open on 38830984000019 // crew enroute // repairs made & COMPLETE @ 22:10
16188 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-03-09 11:27 | 2016-03-09 15:30 | 1 | 243 | 4830881 | 243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA, 7200 VOLT XFMR, BUCKET ACCESSIBLE, ALL POWER RESTORED/ ISO 37830155000109/ COD 1/ VER/BOW
16189 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-12-17 09:17 | 2015-12-17 13:19 | 1 | 242 | 4539261 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | @ 1004 CHECKING XFMRBAD 15 KVA LEAKING OIL CREW REQUIRED TRUCK OK MATERIAL HANDLERBAD 15 KVA LEAKING OIL CREW REQUIRED TRUCK OK MATERIAL HANDLER/SEND TO RON VIRGINBAD 15 KVA LEAKING OIL CREW /REQUIRED TRUCK OK MATERIAL HANDLER/SEND TO RON VIRGIN RELEASED BY CREW 078S03/ON SITE RMALL POWER RESTROLED AT 13:19 PLEASE CLOSE TIC RM COD=1 ISO TF 38830204000127 VER/HFP L3/HFP
16190 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-03-06 06:33 | 2012-03-06 10:35 | 1 | 242 | 4555291 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD SECONDARY CONNECTION//COD 1// VER/DBM IDC XXXX
16191 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-04-25 21:14 | 2020-04-25 23:15 | 2 | 121 | 4750401 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout. power restored at 2315
16192 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-06-12 00:59 | 2011-06-12 03:00 | 2 | 121 | 4299821 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUT OUT DOOR. COD-2 ISO LF 38830597000009 VER/HFP L3/HFP IDC XXXX
16193 | South Williamson | 3411401 | DEWEY | INEZ | 2012-10-10 11:53 | 2012-10-10 15:55 | 1 | 242 | 4128661 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON POLE 212//GOING TO ELIMIMINATE CURRENT LIMIT FUSE TO SEE IF IT WILL STAY//BAD 15KVA XFMR//CREW ENROUTE//CAN USE SQUIRT BOOM TO CHANGE//CHANGED OUT//RESTORED AT 1555//COMPLETE//EM VER/KEP IDC XXXX
16194 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-12-12 08:38 | 2019-12-12 12:40 | 1 | 242 | 4146921 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON POLE 39831097B00186//COD 1//WILL BE REPLACING//
16195 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-02-07 12:59 | 2009-02-07 15:00 | 2 | 121 | 56477-1 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE FUSE MAY HAVE BROKE. 6T FUSED UP ERYTHING OK.// VER/TOM L3/TOM IDCC CNT1 XXXX
16196 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2022-03-23 19:59 | 2022-03-23 22:00 | 2 | 121 | 4665181 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM cutout broke.// Will be making repairs.//Replaced 7200 cutout.// Restored @ 22:00
16197 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-09-09 19:29 | 2011-09-09 21:30 | 2 | 121 | 4853441 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT IS BROKEN INTO. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. IDC XXXX
16198 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-01-15 07:33 | 2018-01-15 10:40 | 2 | 187 | 4747951 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop bad @ house, will splice & repair. xfmer off @ 09:45, on @ 10:40
16199 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-05-17 20:19 | 2014-05-17 22:20 | 2 | 121 | 4719911 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE GOT OLD AND BROKE. POWER BACK ON @ 22:20
16200 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2018-06-22 22:26 | 2018-06-23 00:27 | 2 | 121 | 4650491 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required
16201 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-08-21 17:28 | 2016-08-21 19:29 | 2 | 121 | 4822611 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED/6T FUSE/ ISO 38830160000007/ COD 2/ VER/BOW
16202 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2010-06-15 06:28 | 2010-06-15 10:30 | 1 | 242 | 64793-1 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35570424 // FOUND A WESTINGHOUSE ENCLOSED CUTOUT THAT IS BROKEN ON POLE 1147-406, IN BEHIND THE HOUSE, CAN NOT GET TRUCK TO POLE, WELL NEED A LINE CREW TO MAKE REPAIRS, JUST ONE CUST IS OUT. WELL NEED NEW CUTOUT, THIS IS A CLIMBER RELEASED BY CREW 078S06//PRT ON SITE//REPAIRED GUY AND REPLACED CUTOUT POWER RESTORED AT 10:30 PR TOLLIVER // COD-1 VER/HFP L3/HFP
16203 | Hazard | 3309301 | VICCO | REDFOX | 2018-09-07 06:13 | 2018-09-07 10:15 | 1 | 242 | 4051971 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Dispatched in accordance with KYPCo Late Night Callout Guidelines. xfmr fuse out, bad lightning arrester, replaced arrester and closed fuse, still no power. line fuse must be out also. power restored COD-1 ISO LF 37830349000140
16204 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2017-09-22 20:01 | 2017-09-23 00:03 | 1 | 242 | 4383451 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 38821089C00303/ FUSE BROKEN/MD FILED/RESTORED 0003 9-23-17/COD-1/ VER/KEP VER/ALB
16205 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-12-09 03:44 | 2015-12-09 05:45 | 2 | 121 | 4519721 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN AT THE WEATHERHEAD CAUSED THE SERVICE TO BURN DOWN. VER/ARN
16206 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-05-11 21:24 | 2017-05-11 23:25 | 2 | 121 | 4783781 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKE--REPLACED--ALLGOOD--DS051117/ ISO 38830212000089/ COD 2/ VER/BOW
16207 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-08-22 21:47 | 2014-08-22 23:48 | 2 | 121 | 4408901 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR// COD 2// VER / ADH
16208 | Pikeville | 3402003 | KEYSER | MULLINS | 2013-04-19 13:14 | 2013-04-19 15:15 | 2 | 121 | 4026411 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON 38831103000006// WILL REFUSE// XFMR BAD// CREW ON THE WAY COD-2 ISO TF 38831103000006 VER/HFP L3/HFP IDC XXXX
16209 | South Williamson | 3411401 | DEWEY | INEZ | 2019-10-13 10:13 | 2019-10-13 12:14 | 2 | 121 | 4136211 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 12:14. sh
16210 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-12-14 14:59 | 2013-12-14 17:00 | 2 | 121 | 4161551 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR C/O BROKE DOWN SETTING POLE ON FIRE, WILL TRY TO PUT OUT. XFMR WILL BE OPEN ON POLE 158-29////// PUT FIRE OUT, CHANGED C/O, ARRESTOR AND BRKT. POWER RESTORED. VER/CRB L3/HFP
16211 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2021-11-12 08:13 | 2021-11-12 12:15 | 1 | 242 | 4083541 | 242 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | leg bad in UG service causing part power. will be installing ADD a phase to restoer to full power. crew will make permanent repairs a later date.//// installed machine and restored at 12:15///Created DAE 1000062183 and emailed copy to Tommy Goble for follow up
16212 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-04-13 18:33 | 2012-04-13 22:35 | 1 | 242 | 4671941 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON UG. 124 PHASE TO GROUND AND 68 PHASE TO GROUND.NEED CREW TO PUT ON POWER TEMP. RELEASED BY CREW 078S01//FETR22:30/JEH//POWER TEMP INSTALLED/POWER REST.@ 22:35 078H05//EMAILED TO LINE CREWS IDC XXXX
16213 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-01-24 18:58 | 2013-01-24 23:00 | 1 | 242 | 4738501 | 242 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | XFMR RISER AND CONNECTIONS ARE MELTED //REWIRED XFMR// POWER IS RESTORED/// OFF 22:15 ON 23:00 ///VER/CRB L/3 CRB IDCCTOF2215, MCCDL, CDC92, CNT4 XXXX
16214 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-03-31 16:54 | 2021-03-31 18:55 | 2 | 121 | 4408541 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//big bucket enroute to assist//repairs made/restored at 18:55//complete//em
16215 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-08-30 18:29 | 2022-08-30 20:30 | 2 | 121 | 4818891 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Secondary burnt into between xfm pole 169-91 and secondary pole 169-173 ////Repairs made and restored service @ 20:30
16216 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-05-26 10:13 | 2016-05-26 14:15 | 1 | 242 | 4261011 | 242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN, MAY BE ABLE TO REACH WITH LARGE BUCKET BY BACKING INTO DITCH. HORNETS NEST ON XMF LINECREW REQUIRED RELEASED BY CREW 078S11 VER/AWD
16217 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-04-03 06:49 | 2014-04-03 10:50 | 1 | 241 | 4558191 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 375-371, REMOVED CLAMP ON POLE 376-550 TO ISOLATE & PLACED TAG FO CECIL SEXTON. RELEASED BY CREW 077S11 VER/CRB
16218 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2009-04-13 07:35 | 2009-04-13 11:36 | 1 | 241 | 51719-1 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202203// CUTOUT BAD VER/TOM L3/TOM IDC XXXX
16219 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2011-02-20 21:39 | 2011-02-21 01:40 | 1 | 241 | 59543-1 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN. CUTOUT DOES NOT LOOK RIGHT - GOING UP TO CHECK IT. REPLACED BAD CUTOUT, TRIED XFMR FUSE AND DISCOVERED BAD XFMR. CREW ENROUTE TO CHANGE. CHANGED XFMR AND RESTORED @ 1:40. SH IDC XXXX
16220 | Pikeville | 3421001 | BREAKS | CITY | 2019-09-01 11:17 | 2019-09-01 15:18 | 1 | 241 | 4971011 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Two conductors and the neutral burndt into on sec. pole 220-C2-900, will have to have a piece of 4/0 quad to make repairs, Paul Layne coming to assist, opened the trans. bank @220-C2-505 @1333. Got repairs made @1518.
16221 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-05-28 19:29 | 2012-05-28 23:30 | 1 | 241 | 4838241 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR .WILL NEED 15 KVA 7200/120/240 & CUTOUT.1 A LINEMAN & MATERIAL HANDLER VER/ARN IDC XXXX
16222 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-07-23 09:29 | 2015-07-23 13:30 | 1 | 241 | 4934401 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED FUSE// VER/ ADH
16223 | Hazard | 3310502 | HADDIX | CANOE | 2008-01-26 15:30 | 2008-01-26 19:31 | 1 | 241 | 60166-1 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR//3310502/VER/CRB IDC XXXX
16224 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-06-21 13:29 | 2015-06-21 17:30 | 1 | 241 | 4628661 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP HAS BURNED OFF AT THE TRANSFORMER DEAD END POLE 38821037B00274. WILL NEED TWO MEN AND A EIGHT FOOT CROSS ARM, CUTOUT AND ARRESTER TO MAKE TEMPORARY REPAIRS. I HAVE GOT MY SERVICE BUCKET TO THE POLE TO USE. POWER IS RESTORED, SEND TO COREY FARMER TO HAVE THE APPLE TREE CUT FROM THIS POLE, PROPERTY OWNER SAID WE CAN CUT IT./EMAILED ROW/ADH// VER/ ADH
16225 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-04-09 07:42 | 2010-04-09 11:43 | 1 | 241 | 61446-1 | 241 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | WR#34598568 2- BAD CUTOUTS 3-LA RELEASED BY CREW 078S08/CREW ON SITE /CHG 3 CUTOUTS AND 6 LA/FETR1135/VEM/NEW FETR1150/VEM/REPAIRS MADE AND POWER RESTORED 1143/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
16226 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-11-20 08:46 | 2021-11-20 12:47 | 1 | 241 | 4110461 | 241 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | insulink burnt up/ repairs made. pls close. tre
16227 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-11-10 12:19 | 2012-11-10 16:20 | 1 | 241 | 4379551 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR LOOKS TO BE JUST HANGING DOWN, NOT BLOWN. I AM GOING TO CLOSE DOOR. CUTOUT BAD. WE CHANGED CUTOUT. ///VER/CRB L/3 CRB IDC XXXX
16228 | Hazard | 3310502 | HADDIX | CANOE | 2014-12-13 14:47 | 2014-12-13 18:48 | 1 | 241 | 4858891 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNT UP, WILL BE CHANGING IF I GOT ONE TO FIT IT/// ONE I FOUND WOULDNT WORK WILL HAVE TO CHANGE IT OUT//COD1// VER/ ADH
16229 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-07-29 10:29 | 2011-07-29 14:30 | 1 | 241 | 4637141 | 241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR. SERVES ONE HOUSE WHICH IS AN ACTIVE ACCOUNT BUT NO ONE LIVING THERE AT PRESENT. DUTY SUPERVISOR NOTIFIED AND WILL HAVE REPLACED THIS AFTERNOON. RELEASED BY CREW 076S02// ON AT 14:30 IDC XXXX
16230 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-03-31 15:51 | 2015-03-31 19:51 | 1 | 240 | 4249671 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BROKE @ BSKT. HENDRIX,CLOSE SPACEING RELEASED BY CREW 078S07////CHANGED CUTOUT AND ARRESTOR///TBL TKT COMP COD-1 VER/HFP L3/HFP
16231 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-05-01 09:14 | 2009-05-01 10:34 | 3 | 80 | 61902-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP BAD ARRESTER L3/HFP IDC XXXX
16232 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-08-11 13:25 | 2010-08-11 14:45 | 3 | 80 | 52485-1 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL AND 1 HOT LEG BURNT IN TWO AT POLE 38830206A10272, CUSTOMER COUNT WILL ONLY BE THOSE ON THIS POLE. APPROX. 3 //VER/GAH IDC XXXX
16233 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-02-15 16:00 | 2022-02-15 18:00 | 2 | 120 | 4483011 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Got a broke seconday leg and neutral. Pole445-59 is in bad shape and manual not safe to climb. Needs to be changed out before we can restore. You can get a yard dog to the pole to change. Talked to hazard line and they are getting a job wrote up to come change the pole out. Released by crew 077H15 lift clamp on 445-57 at 16:00 restored at 18:00
16234 | Pikeville | 3402002 | KEYSER | STONECOAL | 2015-08-06 16:14 | 2015-08-06 20:14 | 1 | 240 | 4105411 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074H17 BROKEN CUTOUT ON POLE38821105D00150 REPLACED CUTOUT REENERGIZED LINE AT 20:14 A PHASE VER/CRB
16235 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-06-15 18:10 | 2010-06-15 18:40 | 8 | 30 | 65289-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | JRV ON SITE @ 15:55.....TALKED TO CUST....THEY ARE BOTH OK...AND ARE NOT UPSET...JUST CONCERNED AND WANTED TO LET US KNOW THAT WE MAY HAVE A PROBLEM....MEASURED VOLTAGE ON GUY TO GROUND....READING AROUND 100 VOLTS....POLE 1086-269....(VERY OLD CONSTRUCTION)....OLD RUSTY DOWN GUY, VERY CLOSE TO XFRMER PRIMARY RISER...GUY BOND DETERIORATED..POLE TOP BURNT....OLD JD DEAD END INSULATORS CRACKED...WILL REPLACE..//.PULLED LINE OFF AT POLE 1086-C-7 @ 18:10....BACK ON @ 18:40... VER/KEP L3/KEP
16236 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-03-09 19:25 | 2022-03-09 23:25 | 1 | 240 | 4595301 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfm fuse blown ///Bad 25 KVA 7200/// Steve Ray is enroute///Changed bad xfm and replaced cutout///Restored @ 23:25
16237 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2014-03-29 18:10 | 2014-03-29 19:10 | 4 | 60 | 4535451 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUTBAD CUT OUT DOOR REPLACED DOOR 10T FUSE VER/CRB
16238 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-04-27 07:40 | 2010-04-27 09:00 | 3 | 80 | 51835-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT...CHANGING CUTOUT..BB//COD 3// VER/DBM IDC XXXX
16239 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2015-08-17 19:25 | 2015-08-17 20:25 | 4 | 60 | 4144201 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 343D-32 . REPLACED CUTOUT & CLOSED XFMR @ 20:25 . SEND TO DOUG C. FOR TECH TO MAKE JOB TO CHANGE XFMR OUT , XFMR WAS HOT TO TOUCH NEEDS CHANGED . CAN GET BUCKET TO XFMR .SENT EMAIL/ ISO 37830343D00032/ COD 4/ VER/BOW
16240 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-09-30 19:05 | 2008-09-30 20:25 | 3 | 80 | 52400-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3001101// NU. BURNT INTO WR// COD 3 // VER/TOM IDC XXXX
16241 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-02-23 15:10 | 2014-02-23 15:50 | 6 | 40 | 4428381 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREWS OPENED UP FUSE IN ORDER TO REPLACE TRANSFORMER IN ORDER 4428021 SAFELY//COD 6// VER/DBM
16242 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-05-26 17:20 | 2012-05-26 21:20 | 1 | 240 | 4833731 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NEED TO REPLACE U.G.SERVICE. SEND TO D. HAMILTON RELEASED BY CREW 074S05//BAD URD SVC, WILL TRY TO PULL SVC OUT OF CONDUIT AND REPLACE CABLE. OPENED XFMR 1151-782 TO MAKE REPAIRS AT 20:15, REPAIRS MADE, CLOSED AT 21:20. INTERRUPTION OUTAGED 1 MORE CUST. //VER/GAH IDCC CCO XXXX
16243 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-02-08 09:50 | 2022-02-08 10:30 | 6 | 40 | 4457181 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up at secondary pole
16244 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-07-09 18:11 | 2010-07-09 20:11 | 2 | 120 | 64346-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE BAD CUTOUT TOP OF POLE BURNING CKING TO SEE WHAT IT TO REPAIR///PUT OUT FIRE AND REPLACE CUTOUT..... COD-3 VER/HFP L3/HFP IDCC PN21, CNT3 XXXX
16245 | South Williamson | 3200302 | BELFRY | TOLER | 2020-11-17 14:14 | 2020-11-17 15:34 | 3 | 80 | 4701461 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replace cutout Off at1414 On at 1534_ 3 CC FETR 1600
16246 | Hazard | 3302703 | HAZARD | HAZARD | 2018-02-23 11:40 | 2018-02-23 12:10 | 8 | 30 | 4875261 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | opened to replace bad pole at 11:40 power restored at 12:10
16247 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2008-02-22 11:41 | 2008-02-22 12:41 | 4 | 60 | 66249-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT ON POLE 235-95 WILL BE CHECKING TRANSFORMER OUT. LOOKS LIKE TRANSFORMER FUSE BROKE.//VER/CRB IDC XXXX
16248 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-11-19 05:10 | 2012-11-19 07:10 | 2 | 120 | 4407301 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT IS BURNED UP. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. VER/HFP L3/HFP IDC ORIGINAL CALL WAS FLICKERING BUT I HAVE NOT INDICATION OF WHEN OUTAGE OCCURED LEFT OFF TIME AS IS XXXX
16249 | South Williamson | 3200302 | BELFRY | TOLER | 2015-11-18 23:26 | 2015-11-19 00:26 | 4 | 60 | 4467931 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON 1039-A-19 REPLACED WITH NEW ONE RESTORED POWER AT 00:26 ONLY 4 CUSTOMERS OUT/ MD DONE / ISO 38821039A00019/ COD 4/ VER/BOW
16250 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2014-08-25 15:37 | 2014-08-25 16:37 | 4 | 60 | 4422831 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE, REPLACED FUSE AND POWER IS BACK ON.// ISO 38821064D00015// COD 4// VER/BOW
16251 | Cannonsburg | 3001401 | LOUISA | CITY | 2018-02-17 14:35 | 2018-02-17 15:15 | 6 | 40 | 4854531 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Opening transformer to replace secondary connections that are firing up38830454A41556 open tran repair sec--open 14:35--repaired--closed 15:15/ ISO 38830454A41556/ COD 6
16252 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-06-02 11:45 | 2013-06-02 13:45 | 2 | 120 | 4208911 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP OFF LINE SERV TO PLACE BACK ON,ALL CUST RESTORED @1345 PLEASE CLOSE TICKET THANKS.BT COD-2 ISO PO @ 38830278000154 VER/HFP L3/HFP IDC XXXX
16253 | South Williamson | 3411401 | DEWEY | INEZ | 2022-07-18 12:45 | 2022-07-18 14:45 | 2 | 120 | 4513231 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke// Released by crew 079S01
16254 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2013-08-25 13:32 | 2013-08-25 14:12 | 6 | 40 | H4705381 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN WIRE SECONDARY DOWN--OPENED TRANSFORMER AT 13:32--CALLED L MCCOY TO ASSIST--BAD CONECTION AT TRANSFORMER #4 CU OPENWIRE DOWN VER/SEF IDCC DUP TOP OPEN TRANSFORMER XXXX
16255 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-02-28 10:20 | 2008-02-28 11:20 | 4 | 60 | 51179-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402002/ 4 CUSTOMERS OFF 1020 ON @ 1120 IDC XXXX
16256 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2020-05-18 09:59 | 2020-05-18 12:41 | 3 | 162 | 4848291 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | burnt off xarm @ 38830020C45612, 8 ft arm, braces Released by crew 078S07//COD 1 FROM BEGINNING//WILL HAVE TO OPEN L/F 38830020C30350//THIS WILL OUT ANOTHER 2 CUSTS @ 1202//RESTORED 1241
16257 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2017-10-15 21:06 | 2017-10-16 01:06 | 1 | 240 | 4460011 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1148-126 BAD 12 KV C/O. IS LF. TRK TO POLE RELEASED BY CREW 078S07/ON SITE RM POWER ON @01:06 PLEASE CLOSE TIC RM//VER/ADH L3/HFP XXXHFP
16258 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2019-07-09 16:24 | 2019-07-09 16:54 | 8 | 30 | 4685391 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 37.5 KVA TRANS//NO OUTAGE TILL LINE CREW ARRIVES//RON VIRGIN SHOT TROUBLE//COD 8/arived RM lifting hot tap on 44C14076 to de-energize one span tap to chane xfmopen16:24 closed @16:54 please close tic RM L3/HFP
16259 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2014-01-14 15:00 | 2014-01-14 17:00 | 2 | 120 | 4281731 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | CREW REPLACING PADMOUNT TR 38830045B43727 & RETURNING U/G SUBDIVISION TO NORMAL AFTERWARDS /// TRACKING# KY092613-0105-7727 FOR ABNORMAL // ENTERED MD // COD-2 ISO @ 38830045B43729 VER/HFP L3/HFP
16260 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-01-15 05:15 | 2009-01-15 07:15 | 2 | 120 | 55120-1 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000801 -NO CREW REQUIRED BROKEN NEUTRAL WIRE/COD-2 VER/KEP L3/KEP
16261 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-11-17 20:10 | 2010-11-17 21:10 | 4 | 60 | 57719-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BURNT UP/SLICED SERVICE DROP/ RESTORED AT 21:10//COMPLETE//EM.//VER/CRB IDC XXXX
16262 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-11-09 15:20 | 2012-11-09 17:20 | 2 | 120 | 4377771 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CUTOUT OPEN CHECKING NOW FUSE BROKE ///VER/CRB L/3 CRB IDCC CCU XXXX
16263 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2013-10-28 13:00 | 2013-10-28 13:40 | 6 | 40 | 4970041 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED TRANSFORMER ON POLE DUE TO BAD CUTOUT AND ARM BURNING AT 13:00 AND BACK ON AT 13:40 CHANGED CUTOUT EVERYTHING OK. VER/CRB L/3 CRB
16264 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-03-07 16:49 | 2008-03-07 17:29 | 6 | 40 | 54719-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3308602// TRANSFORMER FUSE HAS DETERRIORATED AND BROKE VER/HFP IDC XXXX
16265 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2008-11-17 20:30 | 2008-11-17 21:10 | 6 | 40 | 66103-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3309101//15T FUSE LINK IS BLOWN ON 100 KVA TRANSFORMER. NO VISIBLE CAUSE, I AM GOING TO REFUSE. FUSE LINK APPEARED TO JUST BE BROKEN // VER/TOM IDC XXXX
16266 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2011-10-27 15:15 | 2011-10-27 17:15 | 2 | 120 | 4027101 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT FUSE WAS BROKEN. FUSED UP TRANSFORMER EVERYTHING OK. COD-2 ISO TF 37830091B00198 VER/HFP L3/HFP IDC XXXX
16267 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-04-22 12:05 | 2008-04-22 14:45 | 5 | 160 | 53284-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3309104//SECONDARY POLE 377-24 HAS ROTTED OFF AND FALLEN. I HAVE ISOLATED SECONDARY AND HAVE ONLY ONE CUSTOMER OUT. FLAGMEN ON THE WAY TO SET OT SIGNS AND FLAG. I HAVE CONTACTED CREW AND THEY WILL BE ON THEIR WAY SHORTLY RELEASED BY CREW 077S07//COD 5// VER/DBM IDC CHANGED START TIME FROM 1142 XXXX
16268 | Hazard | 3307301 | BULAN | ARY-HEINE | 2018-09-06 15:39 | 2018-09-06 19:39 | 1 | 240 | 4050091 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | broke pole 37830128000097 vehicle caught neutral that was low because of broke pole/ ISO 37830129B00033/ COD 1/ All power restored
16269 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-09-05 14:30 | 2016-09-05 15:10 | 6 | 40 | 4869471 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ***SEE 4869101*** BAD STEPDOWN TRANSFORMER ON POLE 38830116D00709/ ISO 38830116D00115/ COD 6/ ,OPENED @1430,,CLOSED @1510/ VER/BOW L3/HFP XXXHFP AJB
16270 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-06-15 08:05 | 2022-06-15 10:05 | 2 | 120 | 4121771 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a Hot leg burned into Mid Span in secondary off pole 286-187,Will have to open Trans to replace service Conductor.Replaced Trans cutout on 286-187 and restored service at 10:05.
16271 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-12-02 11:24 | 2011-12-02 12:24 | 4 | 60 | 4136161 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE COD-4 ISO TF 38830045D26560 VER/HFP L3/HFP IDC XXXX
16272 | Paintsville | 3401102 | FALCON | SALYERSVI | 2021-04-10 10:09 | 2021-04-10 14:09 | 1 | 240 | 4437371 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Customers hot leg was burndt into @ their weatherhead, got repairs made and power restored @1409. // customer actually feed from transformer 38830850000114 one customer out
16273 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2013-10-14 12:00 | 2013-10-14 16:00 | 1 | 240 | 4935451 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, UG | BAD UG LINE CREW REQ NO TRUCK,XFMR OPEN @ POLE 250-98 RELEASED BY CREW 078S05,,CREW ON SITE..FOUND AND REPAIRED NAD SPLICE IN CONDUIT, ALL POWER RESTORED//COD 1// VER/DBM
16274 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-01-02 14:15 | 2022-01-02 16:15 | 2 | 120 | 4261571 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failed at pole 205-D3-597//changed it out and restored at 1615
16275 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2015-05-25 10:02 | 2015-05-25 14:02 | 1 | 240 | 4461941 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR IN BANK OF XFMR,S OPENED AT 13:06 CLOSED AT 14:02// VER/ ADH
16276 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2020-11-10 10:01 | 2020-11-10 11:21 | 3 | 80 | 4656711 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse melted// refused and restored
16277 | Hazard | 3303902 | LESLIE | WOOTON | 2021-02-06 08:45 | 2021-02-06 12:45 | 1 | 240 | 4941351 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout to xfmr broken, need big bucket and 19.9 cutout, help is on the way, p.hicks,repaires made all power restored @ 12:45 p.hicks
16278 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-08-20 13:49 | 2009-08-20 14:29 | 6 | 40 | 54750-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WORK REQUEST # 31328694 // CUTOUT BAD ,CUSTOMER STILL HAVE POWER WILL OPEN XFMR TO MAKE REPAIRS RELEASED BY CREW 077H15 COD-6 ISO TF 37830497000024 L3/HFP IDC XXXX
16279 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-07-12 08:30 | 2009-07-12 09:50 | 3 | 80 | 62188-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3413401// POLE FIRE DUE TO BAD CUTOUT. I WILL BE WORKING ON. I INSTALLED NEW CUTOUT AND BRACKET. FUSED UP EVERYTHING OK. POLE HAS A BAD BURNT PLACE BACK IN DOWN ABOUT 3 FOOT FROM TOP OF POLE. POLE IS SAFE. SEND COPY OF THIS TO RON RYE ENG. POLE WILL NEED TO BE CHANGED. SENT EMAIL TO RON RYE...HFP L3/HFP IDCC TOF0750 ESTIMATED TIME OFF XXXX
16280 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-11-19 07:10 | 2008-11-19 07:50 | 6 | 40 | H1112399-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR 27354511 DAMGED SERVICE DROP--CUSTOMER OPENED BREAKER--WILL RETIRN LATER TO REPAIR-RESEND RELEASED BY CREW 078S07WR --OPENED TRANSFORMER POLE 45-3015 AT 07:1 0 TO MAKE REPAIRS APX 30 MINUTESWR // BACK ON AT 07:50 VER/KEP IDC XXXX
16281 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-09-24 09:07 | 2011-09-24 13:07 | 1 | 240 | 4911441 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON U.G.. NEED POWER TEMP. CUT BAD LEG AT XFORMER, OUTHER LEG STILL HOT. RELEASED BY CREW 078S01/CREW TO REPAIR U/G SERV/OPEN XFMR AT 1227/FETR 1430/VEM/REPAIRS MADE AND XFMR RESTORED 1307/PLEASE CLOSE TICKET/THANKS/VEM IDCC CBT2 XXXX
16282 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2008-05-28 13:37 | 2008-05-28 14:57 | 3 | 80 | 52228-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE, XFORMER FUSE BLOWN, 3 CUST OUT, FUSE BROKE AT BOTTOM OF CUTOUT DOOR//2150502//VER/CRB IDC XXXX
16283 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2015-01-14 18:25 | 2015-01-14 22:25 | 1 | 240 | 4936061 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR IS BURNT UP ON 738-162. CREW ENROUTE TO REPLACE. REPLACED WITH 25 KVA AND RESTORED @ 22:25. SH//COD 1// VER/ ADH
16284 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-01-27 18:05 | 2011-01-27 22:05 | 1 | 240 | 66529-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR EST TIME 02:30 1-28-2011 RELEASED BY CREW 077H03TRANSFORMER CHANGED OUT AND POWER RESTORED AT 22:05//COD 1// VER/DBM IDC CHANGED START TIME FROM 1716, ESTIMATED TIME OFF XXXX
16285 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-01-02 22:30 | 2008-01-03 02:30 | 1 | 240 | 53019-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308503// BAD TRANSF 10 KVA 7200 KV == MAN TRANSF AND MATREASL HANDLE == CHANGED TRANSF INST 25 KVA VER/ARN IDC XXXX
16286 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2013-02-15 19:30 | 2013-02-15 23:30 | 1 | 240 | 4822941 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR..NEED 1 MAN AND MATERIAL HANDLER..TRUCK ACCESS..BACK ON 23.30 ///VER/CRB L/3 CRB IDC XXXX
16287 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-04-23 23:43 | 2014-04-24 03:43 | 1 | 240 | 4629031 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SEC. CROSSING RD BURN DOWN FEEDS 1 CUST NEEDS TO BE REPLACED SPLICED OUT MADE CUST HOT SEND COPY TO S. MARTIN VER/KEP
16288 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-11 13:10 | 2008-06-11 14:30 | 3 | 80 | 62661-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3008702// BROKEN HOT TAP ON LINE FUSE ON POLE 165-348 VER/HFP IDC XXXX
16289 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-05-15 18:30 | 2017-05-15 20:30 | 2 | 120 | 4802261 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT , REPLACED CUTOUT VER/CRB
16290 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-03-25 18:30 | 2018-03-25 19:30 | 4 | 60 | 4094741 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LINE FUSE OPEN AT 806-30, CREW REQ TOP OF POLE BROKE NEED TO REPLACE WITH 40-4, NEED GUY AND ANCHOR, 25KVA, NO TRUCK, MANUAL TREE CREW, 4 CU P&N AND #2 AL N. Released by crew 074E02/1830-1930
16291 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-08-31 10:10 | 2009-08-31 10:25 | 16 | 15 | 56909-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAVE BURNT UP STIRRUP AND HAVE TO OPEN FUSE ON POLE 1124-141 TO CHANGE OUT SAFELY. // OFF @ 1010 ON @ 1025 IDC XXXX
16292 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2010-04-07 15:30 | 2010-04-07 17:30 | 2 | 120 | 60320-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34567843 / BAD 25KVA TRANSFOMER---POLE 1124-1521 COD-1 VER/HFP L3/HFP IDCC PN1629, TOF1400 XXXX
16293 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-06-25 11:00 | 2010-06-25 15:00 | 1 | 240 | 57271-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 XFORMER ON POLE 261-17, ALSO REG. ON POLE 285-15 GOT WATER IN CONTROL BOX, VOLTAGE WAS 139.9 HAD TO LOEWER MAN. TO 125.5. CONTROL NEEDS REPLACED. NO TRUCKS TO POLE FOR XFORMER CHANGE. OPENED XFORMER AT 11:00. RELEASED BY CREW 078S01/CREW ON SITE DIFFICULT ACCESS EVEN WITH YARD DOG/ POSSIBLE MANUAL CARRY IN. J. HEMLEPP//REPLACED TRANSFORMER CHECKED VOLTAGE WITH LOAD ON CHECKED GOOD J HEMLEPP COMPLETE// VER/KEP L3/KEP IDC XXXX
16294 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-01-07 15:30 | 2022-01-07 16:50 | 3 | 80 | 4321501 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse broke. Restored @ 16:50. sh
16295 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-06 19:34 | 2011-01-06 20:34 | 4 | 60 | 59379-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE { SMALL TYPE } IS BURNED INTO AT POLE 216-13. I AM GOING TO REMOVE IT AND REFUSE TRANS. I REMOVED CURRENT FUSE AND REFUSED TRANSFORMER. SEND AN EMAIL TO BOB SHURTLEFF PLEASE.//COD 4// VER/DBM IDC XXXX
16296 | Paintsville | 3401802 | INDEX | HOSPITAL | 2017-03-21 10:20 | 2017-03-21 14:20 | 1 | 240 | 4574611 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED AT WEATHERHEAD. 4/0 TO 350 MCM CONNECTION REQUIRES BIG PRESS THAT ONLY LINE CREW HAS. CREW ENROUTE FROM PAINTSVILLE TO BRING ME THE PRESS AND CONNECTIONS. REPLACED TWO CONNECTIONS AND RESTORED @ 14:20. SH VER/HFP L3/HFP
16297 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2011-04-03 18:30 | 2011-04-03 18:45 | 16 | 15 | 61809-1 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN AND SET POLE ON FIRE. FULL POWER WHEN I ARRIVED. OPENED XFMR ON 954-40 @ 18:30, REPLACED BAD CUTOUT AND CLOSED XFMR @ 18:45. POLE APPEARS TO BE OUT - COULD NOT DETECT ANY FIRE, SMOKE OR HEAT. SH RELEASED BY CREW 076S02//VER/CRB L3/ JKW IDC XXXX
16298 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-03-09 16:35 | 2016-03-09 17:35 | 4 | 60 | 4832011 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-162 BAD CUTOUT DOOR 6T FUSE/ 38830044A00162/ COD 4/ VER/BOW
16299 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-06-16 14:05 | 2012-06-16 18:05 | 1 | 240 | 4920741 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA XFMR ON 876-52. THERE IS A NEW 25KVA XFMR ON 38830876C00183. INSTALLING 40FT SPAN OF 1/0 SECONDARY FROM 876-183 TO 876-52 TO PICK UP SECONDARY - WILL TAKE BAD XFMR OFFLINE AND CREATE A JOB FOR ENGINEERING TO UPGRADE XFMR ON 876-183 TO 50KVA TO ACCOMODATE 4 - 200 AMP SERVICES. WORK IS COMPLETE. CLOSED XFMR AT 18:05 RESTORING ALL CUSTOMERS. SH//COD 1// VER/DBM IDC XXXX
16300 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-01-10 08:43 | 2018-01-10 12:43 | 1 | 240 | 4725901 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | removing power temp and replacing bad undeground. only one customer out,repairs made all cust restored & temp off please close ticket thanks.bt/ ISO 38830188C00266/ COD 1
16301 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2019-07-19 16:57 | 2019-07-19 17:57 | 4 | 60 | 4735591 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout broke will replace/// replaced bad cutout @ 17:57 and restored service L3/HFP
16302 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-08-23 15:19 | 2022-08-23 17:19 | 2 | 120 | 4786001 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XCO broke on 1125-C1-516// will be making repairs
16303 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2013-02-05 19:24 | 2013-02-05 20:12 | 5 | 48 | 4794301 | 240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT GATE BURNDT INTO, CHANGED OUT CLOSED BACK IN AT 20:12. COD-5 ISO TF 37830352D00060 VER/HFP L3/HFP IDC CALL WAS FLICKERING BUT DONT KNOW WHEN IT OPENED LEFT AS IS XXXX
16304 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-08-03 18:48 | 2016-08-03 22:48 | 1 | 240 | 4730241 | 240 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR, REPLACED #4 SERVICE DROP WITH #2 SERVICE, RESTORED POWER AT 22:48.. VER/AWD
16305 | Hazard | 3303901 | LESLIE | HYDEN | 2019-08-20 15:31 | 2019-08-20 19:30 | 1 | 239 | 4913121 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 243-121. Need a 10kva 7200 transformer and a big bucket. Released by crew 077H20//cod 1
16306 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-06-16 15:21 | 2010-06-16 19:20 | 1 | 239 | 66363-1 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON URD SERVICE, CREW REQUIRED, NEED POWER TEMP, PLEASE SEND TO J LINKOUS, 1/0 WITH #2 NEUTRAL RELEASED BY CREW 078S05 INSTALLED POWER TEMP POWER RESTORED AT 19:20 VER/KEP L3/KEP
16307 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2017-07-12 21:36 | 2017-07-13 01:35 | 1 | 239 | 4112391 | 239 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUSTOMER FUSE IS BLOWN HANGING DOWN ON POLES BAD 37.5 KVA DBL BUSHING C PHASE CAN USE TRUCK, THIS IS EMS BUILDING BESIDE WHERE DAIRY CHEER USE TO BE, RIGHT DOWN FROM ADVANCE AUTO 120/240 V CREW REQ 39831073B43603/ ISO 39831073B43603/ COD 1/ OPENED OTHER 2 PHASES @2345,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED @0135,,,REPLACED CUTOUTS AND ARRESTERS,,ALL POWER RESTORED
16308 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-07-28 08:22 | 2020-07-28 12:21 | 1 | 239 | 4242611 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR fuse open on pole 270-A4-664 with a bad arrestor. Replaced the arrestor and power restored at 12:21.
16309 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2021-07-01 16:13 | 2021-07-01 20:12 | 1 | 239 | 4838851 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout. replaced time on 20:12
16310 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-04-28 22:31 | 2009-04-29 02:30 | 1 | 239 | 56620-1 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411902 TRANSFORMER IS BAD. I AM CALLING FOR HELP. WE CHANGED TRANSFORMER. IDC XXXX
16311 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2013-01-02 12:41 | 2013-01-02 16:40 | 1 | 239 | 4564081 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE HOT LEG IN SERVICE AT SECONDARY POLE IS BURNED INTO AT SERVE-END. POLE IS ROTTEN, UNSAFE TO CLIMB. TIM HALL IS TRYING TO GET ME A FLAGGING CREW SO I CAN USE SQUIRT BOOM. I CHANGED #4 SERVICE DROP TO A # 2 SERVICE DROP. ///VER/CRB L/3 CRB IDC XXXX
16312 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2021-12-29 15:13 | 2021-12-29 19:12 | 1 | 239 | 4236591 | 239 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Bad conn. on transformer
16313 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-01-28 16:16 | 2012-01-28 20:15 | 1 | 239 | 4300991 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON POLE 68-243.GOING TO REFUSE.BAD 15KVA XFMR.NEED TO BRING A 25KVA 19.9 TO REPLACE.ALSO 150 OF #2AA TO REPLACE A NEUTRAL (DAVE LEWIS TO ASSIST)XFMR FUSE BLOWN ON POLE 68-243.GOING TO REFUSE.BAD 15KVA XFMR.NEED TO BRING A 25KVA 19.9 TO REPLACE.ALSO 150 OF #2AA TO REPLACE A NEUTRAL.XFMR REPLACED AND POWER RESTORED @ 20:15//COD 1//ISO// VER/DBM IDC XXXX
16314 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-07-12 18:46 | 2017-07-12 22:45 | 1 | 239 | 4112041 | 239 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD 350 MCM URD, AT THIS LOC, CHECK VOLTAGE AT METER P TO P HAD 22.8 P TO GRD ON RIGHT SIDE 101, P TO GRD ON LEFT SIDE 121 CREW REQ, MAYBE ABLE TO USE POWER TEMP RELEASED BY CREW 078S06,,INSTALLED 25KVA POWER TEMP,,PLEASE PUT IN ABNORMAL AND SEND TICKET TO RAYBURN. ONLY 1 CUSTOMER/ ISO 39830902C00672/ COD 1/ VER/BOW
16315 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-07-31 10:22 | 2010-07-31 14:21 | 1 | 239 | 59796-1 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | --BELHAVEN-ARGILLITE- CIRCUIT--30 CL 7 WINDSTREAM POLE ROTTED OFF AND FELL-CALLING CREW-NEED POLE--NEED POLE GUY AND 100W HPS DD LIGHT AND ARM-OPEN WIRE AND SERVICE SHOULD GO BACK RELEASED BY CREW 078S07/CREW LOADING UP /FOREMAN ON SITE/VEM/REPAIRS MADE AND POWER RESTORED 1421/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
16316 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-08-25 10:41 | 2012-08-25 14:40 | 1 | 239 | 4971061 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN // WILL REFUSE// BAD 167 KVA// 277-480// BIG BUCKET // L/T// 4 MEN // RELEASED BY CREW 074S05 XFMR CHANGED ON AT 14:40 D SAMMONS//COD 1// VER/DBM IDC XXXX
16317 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-04-13 16:11 | 2014-04-13 20:10 | 1 | 239 | 4600151 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER IS BAD. POLE 214-159. I AM CALLING FOR HELP. /// S RAY & D LEWIS & T MCCOWN & B CAMPBELLTRANSFORMER IS BAD. POLE 214-159. I AM CALLING FOR HELP. RELEASED BY CREW 074S01 ENTERED MD COD-1 ISO TF 37830214D00159 VER/HFP L3/HFP
16318 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-07-13 13:16 | 2012-07-13 17:15 | 1 | 239 | 4712541 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRUCK TO POLE RELEASED BY CREW 078S08 COMPLETE 1715 COD-1 ISO TF 38830090000268
16319 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-12-07 07:22 | 2017-12-07 11:21 | 1 | 239 | 4627541 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug.need auto tran portable .or repair 200+ 4/0 w2/0 neu alum .120v-28v/0v--ds120717 Released by crew 078S01//COD 1,installed power temp cust restored @ 1121,need to replace ug please close ticket thanks.bt // SENT EMAIL AS REQUESTED & ENTERED AED Tracking# KY120717-1135-9166
16320 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-03-30 11:01 | 2016-03-30 15:00 | 1 | 239 | 4005291 | 239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200-10 KVA. SILVERTOP C/O & OLD ARRESTER ALSO NEED CHANGE. TRK OK RELEASED BY CREW 078S07. CHANGE BAD 10 KVA AND CUTOUT TIME RESTORED 1500 WDR ISO 38830141B00348 COD 1 VER/AWD
16321 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-09-02 22:06 | 2009-09-03 00:05 | 2 | 119 | 62661-1 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 4T FUSE MAY HAVE BROKE OR MELTED OUT. I FUSED BACK UP WITH A 6T FUSE EVERYTHING OK. SEND COPY TO RON RYE ENG PIKEVILLE. 25 KVA TRANSFORMER HAS 3 200AMP CUST. SEVERAL LIGHTS AND TV BOSTER ON IT. LOAD CHECK. //VER/GAH IDC XXXX
16322 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2016-01-16 23:53 | 2016-01-17 00:27 | 7 | 34 | H4626231 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE SEC. BURNT OPEN NEED CREW RELEASED BY CREW 078S08/OPENING XFMR ON 1148-590 FOR REPAIRS/LOOP BURNT OPEN 1148-589/APROX ONE HOUR OUTAGE/VEM/OPENED XFMR @1153/REPAIRS MADE AND ALL CUST RESTORED 0027/PLEASECLOSE TICKET/THANKS/VEM VER/KEP AJB FOR OP OF XFR.
16323 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-12-19 13:22 | 2019-12-19 17:20 | 1 | 238 | 4170501 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10kva xfmr, need xfmr cutout, 15 kva xfmr, 1 man material handler.back on 1720
16324 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-08-06 13:32 | 2015-08-06 17:30 | 1 | 238 | 4104671 | 238 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE DROP WILL REPAIR/// REPAIRED NEUTRAL AND RESTORED SERVICE @ 17:30 124/124/248/// ONLY 1 CUSTOMER AFFECTED VER/CRB
16325 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-10-25 12:35 | 2008-10-25 12:49 | 17 | 14 | 58966-1 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP RELATED TO ORDER 58951-1 /// CREW OPENED RECLOSER TO ALLOW THEM TO ISOLATE A POLE THAT IS ON FIRE DUE TO CUTOUT FAILING. COD-17 IDC XXXX
16326 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2013-04-16 07:11 | 2013-04-16 09:10 | 2 | 119 | 4012011 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED ONE OF THE TRANSFORMER SECONDARY RISER. COD-2 ISO TF 37820057A00022 VER/HFP L3/HFP IDC XXXX
16327 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-07-28 17:03 | 2020-07-28 19:02 | 2 | 119 | 4246751 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, at 37830247A01013 (2 CC)
16328 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-12-14 21:16 | 2010-12-14 23:15 | 2 | 119 | 50313-1 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..CHANGED OUT CUTOUT..BB//COD 2// VER/DBM IDC XXXX
16329 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-03-01 16:21 | 2013-03-01 18:20 | 2 | 119 | 4865591 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 174-42 ONLY ONE CUST. OUT /// ONLY 1 CUST ON TR PER SERVICER // CCC COD-1 ISO LF 37830174A00449 VER/HFP L3/HFP IDC CHANGED COUNT FROME1 XXXX
16330 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-05-06 07:27 | 2011-05-06 11:25 | 1 | 238 | 4013331 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | CUTOUT HAS BROKEN DOWN & HAS BURNED THRU THE CROSSARM I WILL CHANGE CUTOUT AND RELOCATE ON THE ARM/CHANGED CUTOUT/ PT BAD/ BYPASSED PT/ D. HALL HAS REWIRED MTRING SO IT SHALL MTR CORRECTLY/ POWER BACK ON COD-1 ISO TF 38830980000113 VER/HFP L3/HFP IDC XXXX
16331 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-06-26 14:10 | 2015-06-26 18:08 | 1 | 238 | 4663581 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25KVA 19.9 XFMR BAD, HAVE CALLED SPARKMAN TO GET ONE DOWN HERE. RELEASED BY CREW 077S08 RELEASED BY CREW 077H07 VER/CRB
16332 | Hazard | 3303901 | LESLIE | HYDEN | 2013-11-04 06:14 | 2013-11-04 10:12 | 1 | 238 | 4007011 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303901 - WILL CHECK AT REGULAR WORKTIME AS PER SET GUIDELINES // BAD CUTOUT ON TRANSFORMER., REPLACED BAD CUTOUT GATE. POWER RESTORED. VER/KEP
16333 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-12-05 19:24 | 2017-12-05 21:23 | 2 | 119 | 4624101 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire 38830092A00452/ opened line fuse 38830092A00009 @ 1924/ open lf pole 92-9 @ 19:254, fire @ 92 -452,repairs made all cust restored @ 2123 please close ticket thanks.bt /// 1ST CALL WAS FULL POWER @ 1828
16334 | South Williamson | 3411401 | DEWEY | INEZ | 2009-04-10 20:12 | 2009-04-11 00:10 | 1 | 238 | 51251-1 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE FUSE NOT MAPPED AT POLE 38830672A00038 MD FILED VER/KEP L3/KEP
16335 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2012-12-08 13:16 | 2012-12-08 17:14 | 1 | 238 | 4451951 | 238 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | POLE 46-3 TWO CROSS ARMS BURNT OFF NEED TWO ARMS 3- CUTOUTS OPENED OTHER TWO FUSES 14;15(SEE H4451951) CALL CITY WATER PLANT AFTER 4;00PM TO OPEN GATE 327-2064 RELEASED BY CREW 078S08//COD 1// VER/DBM IDC CPN5863, CNT1, LOOKS LIKE DUPLICATE WAS NOT NEEDED XXXX
16336 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-09-17 18:22 | 2020-09-17 22:20 | 1 | 238 | 4473321 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Customer has half power. Crew enroute to assist and will probably need to open xfmr 809-692 long enough to make repairs. Installed temp Auto xfmr to restore. sh 2220 1cust
16337 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-09-29 21:59 | 2010-09-29 23:58 | 2 | 119 | 55335-1 | 238 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON SERVICE VER/ARN IDC XXXX
16338 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2013-11-19 08:52 | 2013-11-19 10:51 | 2 | 119 | 4056241 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK 2 CUST OUT PER SERVICER VER/CRB
16339 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2012-01-19 12:04 | 2012-01-19 14:03 | 2 | 119 | 4275781 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING BAD XFR 50 KVA///VER/CRB IDCC MCCDIS XXXX
16340 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2014-05-07 22:52 | 2014-05-08 02:50 | 1 | 238 | 4672811 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE 4-3 SERVICE DROP BURNT DOWN DUE TO SOME INSULINK CONNECTION. 1 CUST OUT METER # 190226209 SEND COPY TO PEGGY DAMAGE CLAIMS. CUST COULD POSSIBLY CALL IN.CHANGE 4/2 DROP TO A 2/3 DROP, CUST IS 100AMP IDCC CNT6 XXXX
16341 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-09-21 12:55 | 2022-09-21 14:54 | 2 | 119 | 4905091 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | lightening arrester went bad on xmfr.got power restored @14:54.ticket complete.
16342 | Hazard | 3307301 | BULAN | ARY-HEINE | 2016-08-18 11:05 | 2016-08-18 13:04 | 2 | 119 | 4810291 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === REPLACED === REFUSED POWER OK VER/AWD
16343 | South Williamson | 3411401 | DEWEY | INEZ | 2008-11-19 10:32 | 2008-11-19 14:30 | 1 | 238 | 66605-1 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT BROKE. RELEASED BY CREW 079S01//CREW ON SITE STARTING REPAIRS TCM// VER/KEP IDC XXXX
16344 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-04-10 19:34 | 2012-04-10 21:33 | 2 | 119 | 4664161 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN C/O///// REPLACED XFMR C/O, POWER RESTORED.//COD 2// VER/DBM IDC XXXX
16345 | Hazard | 3310502 | HADDIX | CANOE | 2015-07-05 14:47 | 2015-07-05 18:45 | 1 | 238 | 4723461 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 240-87 , OPENED SOLID BLADE SWITCH ON POLE240-54 .POWER WAS OUT FROM POLE 240-87 WHEN ARRIVED .NEED LINE CREW , CAN WORK POLE WITH BUCKET , POLE CAN BE LOWERED . RELEASED BY CREW 075H04 MADE REPAIRS AND RESTORD POWERAT 1845 CREW 077H01 VER/CRB
16346 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-05-21 11:43 | 2018-05-21 13:42 | 2 | 119 | 4385251 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | replaced xfmr cutout, arrester, and current limiting fuse and refused xfmr / ALL WORK COMPLETE / GXJ
16347 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2011-06-05 23:52 | 2011-06-06 00:26 | 7 | 34 | H4238601 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED ON XFMR POLE. <<ONLY AFFECTS SIX CUSTOMERS>> WILL HAVE TO OPEN XFMR ON 785-452 FOR 15 MINUTES TO MAKE REPAIRS. OPENED XFMR @ 23:52. RE-WORKED CONNECTIONS AND CLOSED XFMR @ 00:26. SH VER/TOM L3/TOM IDCC DUP TO OPEN TRANSFORMER XXXX
16348 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-11-16 12:41 | 2008-11-16 14:40 | 2 | 119 | 65687-1 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3312202// == CUT ARRESTER IN TH CLEAR == REFUSED == COD-2 VER/KEP IDCC CDC83 XXXX
16349 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2013-10-06 10:09 | 2013-10-06 14:07 | 1 | 238 | 4914121 | 238 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CUST HAS PART POWER NOT ALL OUT, FOUND BAD UNDERGROUND, HAS 115V ACROSS HOT LEGS, GROUND TO RIGHT HOT LEG V IS 37V, GROUND TO LEFT HOT LEG IS 119, ADDRESS IS 910 CAROLINE RD, NOT 431, FIRST HOUSE ON LEFT AS YOU DROP OVER HILL TO CHINNS BRANCH, NEED CREW TO INSTALL POWER TEMP VER/SEF L3/HFP IDC XXXX
16350 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2014-10-26 10:42 | 2014-10-26 14:40 | 1 | 238 | 4662291 | 238 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTIONS AT THE WEATHER HEAD. ONLY ONE CUSTOMER HAD PART POWER. VER/CRB VER/DKG L3/DKGXXXC FP I ERASED FAULT POLE NUMBER SINCE FAULT WAS AT THE WEATHERHEAD
16351 | Hazard | 3307301 | BULAN | ARY-HEINE | 2016-03-16 09:11 | 2016-03-16 09:45 | 7 | 34 | 4853601 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED FUSE TO REPLACE CUTOUT OFF @ 0911 CLOSED @ 0945 VER/HFP L3/HFP
16352 | Hazard | 3309302 | VICCO | JEFF | 2008-04-17 08:10 | 2008-04-17 08:44 | 7 | 34 | 51732-1 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3309302// SECONDARY LEADS BURNT UP, REPLACED OPENED TR @ 0810 CLOSED @ 0844 COD&OT --HFP VER/HFP IDC XXXX
16353 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-12-25 11:02 | 2015-12-25 15:00 | 1 | 238 | 4558631 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFORMER 19.9 ON POLE 478-647, NEED LINE CREW TRUCK TO POLE RELEASED BY CREW 078S01.. TRANSFORMER REPLACED AND RESTORED AT 15:00 PLEASE CLOSE TICKET// VER/ ADH
16354 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-09-14 17:25 | 2020-09-14 21:23 | 1 | 238 | 4463321 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad URD, crew required..Bad UG secondary, crew required.. OPS order created OPS# 037215377 Released by crew 074S09
16355 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-06-18 09:49 | 2013-06-18 11:48 | 2 | 119 | 4363611 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN,WILL SEE IF I CAN REPLACE IT///////////REPLACED BROKEN CUTOUT,ALL OK AFTERWARDS // COD-2 ISO TF 37820050000171 VER/HFP L3/HFP
16356 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-06-27 07:51 | 2014-06-27 09:50 | 2 | 119 | 4161371 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 164-36 BAD 19.9 CUTOUT NO TRUCK POLE 164-37 OPENED LINE FUSE AT 08:45 ON 09:45 (SEE ORDER 4161541) //COD 2// VER/DBM
16357 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2016-02-21 14:05 | 2016-02-21 16:04 | 2 | 119 | 4744241 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE CUTOUT HAS FAILED. NO TRUCK ACCESS. I OPENED B & C PHASE AT 16:08. POWER RESTORED AT 16:04.//SEE OTHER OUTAGE 4744461 VER/CRB
16358 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-01-09 08:35 | 2015-01-09 12:33 | 1 | 238 | 4923051 | 238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD IN TOP OF CUOUT ON PRIMARY METER IS BURNED INTO, GOT GREG SHOUSE CREW COMMING TO HELP REPAIR/ ISO 37830172C00476/ COD 1/ VER/BOW AJBC MCCDIS
16359 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-04-16 10:43 | 2018-04-16 14:40 | 1 | 237 | 4238691 | 237 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | corroded connection on trans former. repairs made.. open transformer @ 14:15 closed back @ 14:40 cod 1 iso 37830353B00170 // cust had part power before opening xfer
16360 | Hazard | 3303902 | LESLIE | WOOTON | 2014-08-11 13:07 | 2014-08-11 17:04 | 1 | 237 | 4353951 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JOURNEY OPERATING CALLED PAUL PRAT - OIL WELL(S) OUTRELEASED BY CREW 077S03RELEASED BY CREW 077S03 === BAD CUTOUT ON LOAD SIDE OF STEP DOWN === REPLACED CUTOUT === REFUSED STEP DOWN POWER OK COD-1 ISO LF 37830486000207 VER/HFP L3/HFP
16361 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-10-25 22:56 | 2017-10-26 00:15 | 3 | 79 | 4498971 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER// SHE AND HER TWO NEIGHBORS ARE OUT//XFMR FUSE MELTED OUT , CHANGING.. // COD 3 // VER/DBM L3/HFP XXXHFP
16362 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-01-24 15:41 | 2009-01-24 17:00 | 3 | 79 | 59626-1 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409303// TRANSFORMER FUSE OUT CHECKING// TRANSFORMER FUSE BROKE REFUSED .. COMPLETE TT....//COD 3// VER/DBM L3/KEP
16363 | South Williamson | 3200302 | BELFRY | TOLER | 2021-06-13 11:56 | 2021-06-13 13:15 | 3 | 79 | 4728691 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cust had cutout door burned into and door didnt open on pole 990-C-354.one i found the prb i changed the door and restored power @13:15
16364 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-05-17 06:51 | 2015-05-17 10:48 | 1 | 237 | 4437571 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BROKE IN HALF ,NEED LINE CREW ON 3-PH LINE RELEASED BY CREW 078S09///CREW ON SITE///CUTOUT REPLACE//PWR RESTORED @ 10:48///TBL TKT COMP/ ISO 39831097A00074/ COD 1/ VER/BOW
16365 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2019-12-01 19:21 | 2019-12-01 20:40 | 3 | 79 | 4114171 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout changed, power restored at 20:40/ ISO 39831123C24580/ COD 3
16366 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-11-18 12:37 | 2013-11-18 16:34 | 1 | 237 | 4053361 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 310-187 ( 40/ 5 ) BURNT OFF AT TRANSFORMER, NEED WHEELER TO GET TO POLE,MAY NEED DOZER. NEED LINE CREW . LINE FUSE OPENED ON POLE 310-86 ( 40T ) RELEASED BY CREW 078S01 RELEASED BY CREW 078H14//OPS ORDER BEING MADE PER CUST OK VER/CRB L3/HFP HFPC PN38830310000187 & 187
16367 | Pikeville | 3413401 | GARRETT | GARRETT | 2019-05-28 15:18 | 2019-05-28 19:15 | 1 | 237 | 4355581 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6t fuse out due to bad transformer. crew on the way. transformer changed out everything ok
16368 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2020-11-15 09:46 | 2020-11-15 11:05 | 3 | 79 | 4678351 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t trans fuse out due to bad cutout replaced cutout. everything ok
16369 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-07-19 07:57 | 2017-07-19 11:54 | 1 | 237 | 4141281 | 237 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 XFRF OUT ON 3PHASE BANK,WILL RE-FUSE///////FUSE BLEW,XFR IS BAD///////NEED 100KVA19.9,277-480,CREW.CAN USE BUCKET RELEASED BY CREW 074S06...REPLACED XFMR AND RESTORED POWER @ 11:54 VER/CRB
16370 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2016-06-27 03:48 | 2016-06-27 07:45 | 1 | 237 | 4481081 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NOT 6 CUST JUST ONE, 4/3 SERVICE DROP NEUTRAL BROKEN AND HOT LEGS, MADE REPAIRS, ALL GOOD AT THIS LOC NOW, RESAGGED DROP, AT 0745 BY AMG VER/AWD
16371 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-04-26 19:35 | 2010-04-26 20:54 | 3 | 79 | 51665-1 | 237 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTOR ON XFMR POLE, POWER RESTORED//VER/CRB IDCC CNT1 XXXX
16372 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-03-18 15:24 | 2019-03-18 16:43 | 3 | 79 | 4997861 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | riser wire burnt into on bottom of line cutout on pole 468-68,made repairs restored power at 16:43..
16373 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-08-28 16:39 | 2014-08-28 17:58 | 3 | 79 | 4434191 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RISER BURNT INTO ON XFMR CUTOUT, REPLACED CUTOUT. RESTORED POWER AT 17:58, ONLY 3 CUSTOMERS AFFECTED.///// COD 3 CCC*********************/// ISO 37830375B00035// VER/BOW
16374 | Hazard | 3309301 | VICCO | REDFOX | 2011-01-24 15:16 | 2011-01-24 16:35 | 3 | 79 | 63954-1 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT //VER/CRB IDC XXXX
16375 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-05-20 05:10 | 2019-05-20 09:07 | 1 | 237 | 4302871 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | hot line riser from cutout burnt into, repairs made. changed cutout while here. pls close. tre
16376 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-07-10 09:22 | 2011-07-10 10:41 | 3 | 79 | 4498761 | 237 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING. NUETRAL LEG BURNDT INTO AT POLE 377-142, GONNA OPEN TRANS. AT POLE 377-26 TO MAKE REPAIRS,MANUAL POLE, WILL KEEP TRACK OF TIMES.OPENED TRANS. AT 09:22, CLOSED BACK AT 10:41 RESTORING ALL CUST. COD-3 ISO TF 37830377D00026 VER/HFP L3/HFP IDC CHANGED TIME OFF FROM 0746 XXXX
16377 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-01-29 16:48 | 2014-01-29 20:45 | 1 | 237 | 4325111 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE///////BAD 25 KV XFR,7200.NEED 1 MAN.ALSO A MATERIAL HANDLER BUCKET///////REPLACED XFR,ALL OK AFTERWARDS VER/KEP
16378 | Hazard | 3303902 | LESLIE | WOOTON | 2018-07-06 16:33 | 2018-07-06 20:30 | 1 | 237 | 4742141 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT CREW REQUIRED Released by crew 077S01 replaced cutout and restored power at 2030
16379 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-07-14 15:22 | 2010-07-14 19:19 | 1 | 237 | 50266-1 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER, TIM SMITH IS COMMING TO CHANGE OUT RELEASED BY CREW 077S05 VER/KEP L3/KEP IDC XXXX
16380 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-04-24 17:18 | 2009-04-24 21:15 | 1 | 237 | 58606-1 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 29519031 // MAT BUCKET OK, 15KVA NEW RISERS, SEC, 3 MEN RELEASED BY CREW 078H08//CREW ON SITE P R TOLLIVER//REPLACED TRANSFORMER ALL POWER RESTORED AT 21:15 P R TOLLIVER L3/HFP IDC XXXX
16381 | Pikeville | 3407103 | TOPMOST | KITE | 2015-11-30 07:53 | 2015-11-30 11:50 | 1 | 237 | 4493931 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 7.2 KV 120/240 15 KVA TRANSFORMER , TRUCK ACCESS, CREW ENROUTE . REPLACED TRANSFORMER, ARRESTER, AND CUTOUT, ALL WORK COMPLETE / GXJ COD-1 ISO TF 37830209000180 VER/HFP L3/HFP
16382 | Pikeville | 3409502 | BURDINE | LEVISA | 2008-02-18 00:23 | 2008-02-18 04:20 | 1 | 237 | 64562-1 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409502/// CUTOUT FAILED AND BURNED THE TOP OF THE POLE OFF IDC XXXX
16383 | South Williamson | 3200302 | BELFRY | TOLER | 2014-01-21 02:11 | 2014-01-21 03:30 | 3 | 79 | 4297651 | 237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TR CUTOUT.. SERVICER REPAIRING.CUTOUT DOOR BURNED UP, REPLACED DOOR AND POWER IS BACK ON. THIS CUTOUT NEEDS RELOCATED AROUND THE POLE. THE RISER TO THE TRANSFORMER GOES BETWEEN A THREE INCH GAP BETWEEN THE POLE AND THE GUY WIRE, VER/CRB
16384 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2017-08-17 10:40 | 2017-08-17 12:38 | 2 | 118 | 4269341 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | METERS 533728728/533728727/CALLED CUSTOMER-NO ANSWER // CREW REQUIRED: 3 MAN LINE CREW AND 2 MAN MANUAL ROW CREW, REPLACE 150FT SPAN 2/3 SECONDARY FROM POLE 66-15 TO POLE 66-220, VINES ON SECONDARY BROKE NEUTRAL, CUSTOMER OK TO WAIT TILL A.M., BROWN METAL GARAGE AT END OF LUCY HALL BR. 37830066C00063 1040 TO 1238 VER/KEP
16385 | Pikeville | 3413401 | GARRETT | GARRETT | 2011-03-12 18:20 | 2011-03-12 20:18 | 2 | 118 | 53894-1 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | COD 2//MADE MDCTRANSFORMER FUSE OPEN AND ARRESTER BLOWNTRANSFORMER FUSE OPEN AND ARRESTER BLOWN ... REPLACED CUTOUT AND ARRESTER , ALL WORK COMPLETE / GXJ//VER/CRB IDC DCMT XXXX
16386 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-09-18 19:19 | 2016-09-18 20:18 | 4 | 59 | 4905151 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON POLE 126-A-694, I LIFTED CLAMP ON POLE 126-A-292 @1919, CHANGED C/O AND PUT OUT POLE FIRE, PUT CLAMP BACK ON @2018, ALL POWER RESTORED. VER/CRB
16387 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-09-12 17:04 | 2020-09-12 21:00 | 1 | 236 | 4455041 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200, 25 kva. help on the way. restored 21:00
16388 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2022-01-03 18:32 | 2022-01-03 20:30 | 2 | 118 | 4294871 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 15 kva transformer on pole 357-C-187. transformer is manual out in horse lot. crew to come out in the morning and replace with 25 kva 19.9 Released by crew 077S11 OPS order created #035265882
16389 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-03-09 07:22 | 2012-03-09 09:20 | 2 | 118 | 4565841 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN FUSE 195-44/NO CREW REQUIRED VER/KEP IDC XXXX
16390 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-07-18 18:24 | 2014-07-18 22:20 | 1 | 236 | 4260681 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | POLE 69-8095 TRANS POLE BAD UNDERGROUND NEED TEP. CALL CUST. BRANDON 937-626-1463 SO HE CAN TURN HIS BRECKER BACK ON RELEASED BY CREW 078S08//COD 1//ISO 38830069B28095POLE 69-8095 TRANS POLE BAD UNDERGROUND NEED TEP. CALL CUST. BRANDON 937-626-1463 SO HE CAN TURN HIS BRECKER BACK ON RELEASED BY CREW 078S08, CREW ON SITE, POWER TEMP INSTALLED, ONLY 1 CUSTOMER AFFECTED// VER/DBM
16391 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-11-23 10:29 | 2011-11-23 14:25 | 1 | 236 | 4107791 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / CUT OUT AT POLE 270-B-40 FAILED-----269-71-----269-298--- BAD CUTOUTS///VER/CRB IDC XXXX
16392 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-12-21 14:49 | 2018-12-21 17:57 | 5 | 188 | 4587061 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg connection bad on sec. on pole 120-239.repairs made.opened up @ 17:45 and closed back in @ 17:57..also please send copy to Mike Hatfeild to right up job to replace pole.pole is rotted and needs replaced.//SENT TO TECH L3/HFP
16393 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-04-23 04:34 | 2021-04-23 08:30 | 1 | 236 | 4472851 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate burned in half. Replaced gate and restored power at 8:30
16394 | Hazard | 3309302 | VICCO | JEFF | 2020-04-20 10:12 | 2020-04-20 14:08 | 1 | 236 | 4722411 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Looked like conn. on hot lead brunt netural into replaced conns. power ok
16395 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2018-09-16 12:21 | 2018-09-16 13:20 | 4 | 59 | 4104611 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xformer fuse out. fuse link broke . replaced fuse.
16396 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-11-07 09:52 | 2015-11-07 11:50 | 2 | 118 | 4417321 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | X-FMR CUTOUT BAD ON POLE 402-459. CHANGED CUT-OUT AND PUT POLE FIRE OUT. RESTORED POWER AT 11:50 11/07/2016. VER/CRB
16397 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2011-08-01 09:19 | 2011-08-01 13:15 | 1 | 236 | 4650291 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | NEUT. WIRE HAS PULLED OUT OF SPLICE // WILL REPLACE SER.//REPLACED SER// POWER IS RESTORED//VER/CRB STC PER PHONE CONF
16398 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-01-20 15:32 | 2015-01-20 17:30 | 2 | 118 | 4947771 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON XFORMER POLE 185-111, BIG BUCKETT CAN WORK FROM RD. RELEASED BY CREW 078S01.. CREW ON SIGHT REPLACING CUTOUT ..FETR 19:00/ ISO 38830185000111/ COD 2/ VER/BOW
16399 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2018-06-09 09:29 | 2018-06-09 11:27 | 2 | 118 | 4571281 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | riser came out of hot line clamp pole 321-361
16400 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2016-02-26 12:09 | 2016-02-26 16:05 | 1 | 236 | 4780111 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END FROZE OPEN.CONTRACTORS CHANGED POLE OUT AND SPLICED SERVICE DROP INSTEAD OF REPLACING THE DROP..777-13// VER/ ADH
16401 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-04-22 16:04 | 2015-04-22 20:00 | 1 | 236 | 4355431 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON XFMR FOR TV BOOSTER . REPLACED CUTOUT . ONLY 1 CUST ON XFMR POLE . 37830482B00041 VER/CRB
16402 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-02-18 08:14 | 2011-02-18 09:13 | 4 | 59 | 58777-1 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFR LEAD HOT LEG HAS COME LOOSE FRM SEC COND,WILL REPAIR/////////RE-WORKED CONNECTIONS AND RESTORED,ALL OK AFTERWARDS//VER/CRB IDC XXXX
16403 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2020-11-16 21:01 | 2020-11-16 22:00 | 4 | 59 | 4697871 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fuse was broke inside of cutout gate. refused.. power restored
16404 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-06-20 07:41 | 2020-06-20 08:40 | 4 | 59 | 4049831 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o door. replaced
16405 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2017-11-24 21:04 | 2017-11-24 23:02 | 2 | 118 | 4600601 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT SEC ONTO XFR RISER,WILL REPAIR///////MADE NECESSARY REPAIRS&RESTORED,ALL OK AFTERWARDS
16406 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-08-28 08:21 | 2015-08-28 09:20 | 4 | 59 | 4178721 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1123-7031 6T FUSE BROKE 4-CUST ON TRANS/ ISO 39831123D37031/ COD 4/ VER/BOW
16407 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-06-12 14:19 | 2008-06-12 18:15 | 1 | 236 | 63160-1 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 24758884//BAD TRANSFORMER 25 KVA 19.9 RELEASED BY CREW 074S05 RELEASED BY CREW 074H08 VER/HFP IDC XXXX
16408 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2010-11-05 16:34 | 2010-11-05 20:30 | 1 | 236 | 53319-1 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD BURNING TOP OF POLE OFF == LOWER EVERYTHING DOWN == REFRUSED POWER OK == LINE POLE IS 37830491000018 ==//ISO //COD 1//MD FILED// VER/DBM IDC XXXX
16409 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2019-11-18 09:07 | 2019-11-18 11:05 | 2 | 118 | 4043441 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT IN CLEAR ON C PHASE RECLOSER 38831052A00339//COD 12 FROM THE BEGIINING OF OUTAGE//PICKED CUSTS BACK UP @ 1105/ C PHASE RECLOSER 38831052A00339//COD 12 FROM THE BEGIINING OF OUTAGE//. hot tap & sturrip have been replaced reclosure is back to normal Released by crew 074S04
16410 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2016-04-28 09:38 | 2016-04-28 13:34 | 1 | 236 | 4136771 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 TRIPLEX SEC CABLE DOWN,IN CURVE AND CROSSES ROAD AT TOP OF HILL.NEED HELP/////SAMMONS ENROUTE AFTER LUNCH./////////MADE REPAIRS AND RESTORED,LOOKED LIKE SEC CABLE SHORTED OUT&BURNED DOWN// VER/ ADH
16411 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-10-28 08:55 | 2019-10-28 12:51 | 1 | 236 | 4209021 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on 1/0 secondary,, chg out #2-3 triplex and 1/0 sec
16412 | South Williamson | 3411401 | DEWEY | INEZ | 2012-02-29 10:32 | 2012-02-29 12:30 | 2 | 118 | 4517291 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE TO METER ON HILL HAD NEUTRAL AND HOT LEG BURNT INTO// ONLY AFFECTED ONE METER OFF THIS XFMR WHICH ONLY FEEDS GAS WELL//I HVE REPAIRS MADE//COMPLETE//EM IDC XXXX
16413 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-03-03 10:16 | 2020-03-03 11:15 | 4 | 59 | 4447031 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse is out will refuse. fuse link was broke. refused & power is restored.
16414 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-03-06 13:29 | 2011-03-06 17:25 | 1 | 236 | 50666-1 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39052664 // TOP OF POLE BURNED OFF , WE WILL HAVE TO LOWER EVERYTHING COD-1 ISO PO @ 37830333A00088 VER/HFP L3/HFP IDC XXXX
16415 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2015-10-10 15:41 | 2015-10-10 16:40 | 4 | 59 | 4337101 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1147-4669 OLD CUTOUT DOOR FELL OPEN CLOSED BACK SEND NOTE TO RAYBURN CUTOUT AND LA NEEDS CHGED NO TRUCK/ ISO 39831147C24669/ COD 4 CCC**** MD DONE/ VER/BOW L3/HFP XXXHFP
16416 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2020-02-24 07:59 | 2020-02-24 11:55 | 1 | 236 | 4426921 | 236 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o ..pole 138-316 Released by crew 078S07 all pwr restored @ 11:55 please close ticket LRM L3/HFP
16417 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-08-29 14:16 | 2011-08-29 15:15 | 4 | 59 | 4772771 | 236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN// TREES HAD GOTTEN INTO CUTOUT BURNING UP THE CUTOUT DOOR// CHANGED DOOR//CUT TREE IN CLEAR// REFUSED// POWER IS RESTORED// TREES NEEDS CUT ASAP IN THIS SPAN//COD 4//SENT TO FORESTRY// VER/DBM IDC XXXX
16418 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-05-21 22:26 | 2014-05-22 02:21 | 1 | 235 | 4732211 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT INSTALLED CUT-OUT AND 6-T FUSE POWER RESTORED KWB VER/SEF
16419 | Hazard | 3309302 | VICCO | JEFF | 2009-05-03 14:29 | 2009-05-03 18:24 | 1 | 235 | 64251-1 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP BOTTOM OF LIGHT ARRESTER BLOW OFF HITTING PRIMARY LEAD == BLOWING TRANSF FUSE COD-1 ISO POLE 37830348A00282 L3/HFP IDC XXXX
16420 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2018-08-07 12:38 | 2018-08-07 16:33 | 1 | 235 | 4918231 | 235 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | bad 7200 25kva 2 pri. bush , 3 wire 240v delta, pole 45-385, center can/ primary riser burnt in the clear/FETR 1730/vem/repairs made and power restored to all cust 1633/please close ticket/thanks/vem/ ISO 38830045C14395/ COD 1
16421 | Hazard | 3311103 | STINNETT | WENDOVER | 2017-12-27 12:53 | 2017-12-27 13:40 | 5 | 47 | 4681811 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse broke on pole37830412B00344. power restored at 13:40
16422 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-04-04 10:38 | 2014-04-04 11:25 | 5 | 47 | 4572851 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED C/O//COD 5// VER/DBM
16423 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2008-03-15 19:43 | 2008-03-15 20:30 | 5 | 47 | 57562-1 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 2153502 RESTORED 81 CUST AT 20:30 //,,, OPENED RECLOSER POLE #820-C-309 AT 1943 CLOSED IN AT 2030 UP TO POLE #821-B-15, POLE #845-A-4 BURNED 1/2 INTO , CALLED FOR CREW TO REPAIR//VER/CEP // 5 CUST ON KY SIDE IDC XXXX
16424 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2008-03-11 06:20 | 2008-03-11 10:15 | 1 | 235 | 56120-1 | 235 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUTOUT GOING BAD == NEED BIG BUCKET & FLAGERS == TO CHANGE CUTOUTS AFTER TRAIN IS LOADED VER/HFP IDC XXXX
16425 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-11-24 07:23 | 2014-11-24 11:18 | 1 | 235 | 4759981 | 235 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED TO RED IS PULLED OUT ON POLE 400-1. OPENED X-FMR ON POLE 400-1 AT 11:05 TO MAKE REPAIRS AND CLOSED XFMR BACK IN AT 11:18 RESTORING POWER. 11/24/2014 // SEE DUP H4759981 FOR 2 CUST WHEN TR OPENED // VER/HFP L3/HFP
16426 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-06-30 10:35 | 2014-06-30 14:30 | 1 | 235 | 4174271 | 235 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOW VOLTAGE COMING INTO CUSTOMERS DISC. BOX. I AM CHECKING NOW. FRANK BLANKENSHIP IS BRINGING HIS BUCKET TRUCK TO HELP CHECK PROBLEM. SOMEONE HAD USED A SPLITBOLT ON HOT CONNECTION AND IT HAD LOOSENED UP. I RESQUEEZED CONNECTION. VER/HFP L3/HFP
16427 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-09-28 07:45 | 2020-09-28 11:40 | 1 | 235 | 4501591 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service connection burnt up. made repaires
16428 | Whitesburg | 3309302 | VICCO | JEFF | 2016-08-04 20:35 | 2016-08-05 00:30 | 1 | 235 | 4735991 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE OUT ON POLE. BAD 15 KVA 7200. 2 MEN REQUIRED TO REPAIR.FUSE OUT ON POLE. BAD 15 KVA XFMR..FUSE OUT ON POLE. BAD 15 KVA XFMR..MADE REPAIRS RESTORED POWER AT 00:30..ONLY ONE CUSTOMER.. VER/AWD
16429 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2022-12-27 11:08 | 2022-12-27 11:55 | 5 | 47 | 4366121 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 11:55. sh
16430 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-07-20 21:56 | 2013-07-21 01:51 | 1 | 235 | 4566421 | 235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED OUT,NO REPLACEMENT ON TRUCK IM USING.WENT TO PVILLE AND PICKED UP A REPLACEMENT DOOR.//////////REPLACED DOOR,RESTORED POWER. CC = 1 VER/SDB IDC XXXX
16431 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-07-03 17:35 | 2012-07-03 21:30 | 1 | 235 | 4285531 | 235 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SERV DROP.ALL WORK COMP
16432 | Pikeville | 3421001 | BREAKS | CITY | 2008-02-16 00:39 | 2008-02-16 01:05 | 9 | 26 | 63693-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3400901/// TRANSFORMER FUSE WAS BROKEN VER/JHM IDCC CCO XXXX
16433 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-01-10 21:16 | 2014-01-11 01:10 | 1 | 234 | 4270191 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 01:10 VER/KEP L3/HFP
16434 | Hazard | 3303902 | LESLIE | WOOTON | 2008-06-05 18:01 | 2008-06-05 21:55 | 1 | 234 | 58554-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TOP OF XFMR ON POLE # 389-390 BLOWN OFF RELEASED BY CREW 077H15//3303902/NO CUST OFF THIS TRANS//VER/CRB
16435 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2021-12-04 14:06 | 2021-12-04 18:00 | 1 | 234 | 4148311 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | temp fix with add a phase box
16436 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-01-25 12:35 | 2013-01-25 14:32 | 2 | 117 | 4740271 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT OPENED SIDE TAP AT 1420 CLOSED AT 1430 COD-2 ISO TF 37820126000041 DUP IN HOIS FOR 3 CUST ON TAP OFF POLE 37820126000041 SEE H4740271 FOR DUP FOR 3 CUST VER/HFP L3/HFP IDC XXXX
16437 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-05-20 08:33 | 2020-05-20 10:30 | 2 | 117 | 4866021 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Burnt transformer fuse, Back in @10:30
16438 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-02-25 06:27 | 2010-02-25 07:45 | 3 | 78 | 60763-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE BURNT UP. I WILL BE MAKING REPAIRS. REPAIRS MADE FUSE UP EVERYTHING OK. SEND COPY TO PERRY FARMER PIKVILLE. TWO OF THESE HAVE BURNT UP IN LAST 12 HOURS.//VER/CRB IDC XXXX
16439 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2016-01-19 07:22 | 2016-01-19 11:16 | 1 | 234 | 4631171 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE ON WEATHER WENT BAD == BURNED SERV INTO === REPAIRED SERV ==== POWER OK/ISO 37830181D00341 COD 1/ VER/ AWD
16440 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-01-18 16:15 | 2014-01-18 20:09 | 1 | 234 | 4292771 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND CABLE HIGH VOLTAGE ONE SIDE LOW ON THE OTHER CHECKED CONNECTION AT POLE AND MTR BASE .. CHECKED WITH BEAST.. NEED LINE CREW TO BRING POWER TEMP // MULLINS & MORGAN & HOWARD/CREW ON SITE/FETR2045/VEM/POWER TEMP INSTALLED AND FULL POWER RESTORED 2009/PLEASE COPY TICKET TO L RAYBURN AND B REYNOLDS/THANKS/VEM VER/HFP L3/HFP
16441 | Whitesburg | 3312901 | JENKINS | KONA | 2021-09-09 14:18 | 2021-09-09 16:15 | 2 | 117 | 4227181 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | nuetal sleeve pulled out. redid connections.. power restored
16442 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-10-19 20:39 | 2010-10-19 21:57 | 3 | 78 | 61110-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT ON POLE 448-476... REPLACED CUTOUT RESTORED POWER AT 21:57, ONLY 3 CUSTOMERS AFFECTED COD-2 ISO TF 37830448D00476 VER/HFP L3/HFP IDC XXXX
16443 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-03-22 15:43 | 2009-03-22 17:40 | 2 | 117 | 60709-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN INTO. I AM GOING TO REPLACE CUTOUT. I CHANGED CUTOUT.//COD 2// VER/DBM IDC XXXX
16444 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2022-01-06 11:35 | 2022-01-06 11:53 | 13 | 18 | 4311471 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opened xfmer @ 11:35 to make repairs/back in @ 11:53/pls close. tre
16445 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-10-04 10:10 | 2020-10-04 12:07 | 2 | 117 | 4524201 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at pole. repaired / restored
16446 | Cannonsburg | 3001401 | LOUISA | CITY | 2020-03-14 11:14 | 2020-03-14 12:32 | 3 | 78 | 4477981 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Two fuses blown on txmf bank, and one door burnt up. apr at 1232 close ticket
16447 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2018-12-07 13:31 | 2018-12-07 17:25 | 1 | 234 | 4515811 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | splice failed at trans pole 1139B40.replaced 100 ft of 2/3 service drop.restored power at 17:25 L3/HFP
16448 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-08-14 09:36 | 2010-08-14 13:30 | 1 | 234 | 54608-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFRMR CUTOUT ON POLE 72-D-37....UP ON HILL....CAN REACH FROM BIG BUCKET....CALLING CREW NOW..//....REPLACED BAD CUTOUT...POWER ON....JRV...08/14/10 VER/HFP L3/HFP
16449 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2020-02-26 09:54 | 2020-02-26 11:51 | 2 | 117 | 4433051 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL HAVE TO REPLACE IT///////REPLACED BROKEN CUTOUT&RESTORED POWER,ALL OK AFTERWARDS ////////WAS A PORCELIN TYPE,REPLACED WITH POLYMER TYPE L3/HFP
16450 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-06-10 15:01 | 2013-06-10 18:55 | 1 | 234 | 4253411 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED C/O ///VER/CRB L/3 CRB IDCC PN40 XXXX
16451 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2016-05-18 11:36 | 2016-05-18 12:15 | 6 | 39 | 4229831 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-506 6T TRANS FUSE CUTOUT DOOR BURNT UP
16452 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2015-06-11 10:36 | 2015-06-11 14:30 | 1 | 234 | 4554391 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT. I CANNOT REACH THE CUTOUT. IT IS ON THE TOP OF A 60 FOOT POLE. LINE CREW CAN REACH IT WITH THEIR BUCKET TO CHANGE IT, RELEASED BY CREW 079S02/ ISO 38820966A42704/ COD 1/ VER/BOW
16453 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-06-26 08:39 | 2020-06-26 11:03 | 6 | 144 | 4075981 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Arrestor on A phase xfmr cutout for bank on 876-B-115 has burnt up and blown fuse. I have line crew enroute to repair. We will be opening remaining 2 xfmr cutouts and L/F for side tap when ready to make repairs.opened @ 10:45 made repairs and restored @11:03
16454 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-02-06 10:57 | 2018-02-06 12:15 | 3 | 78 | 4808681 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop had a bad place in wire , opened xfmr at 10:57, cut tree & replaced service drop, restored power at 12:15..
16455 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-07-27 19:15 | 2016-07-27 23:09 | 1 | 234 | 4693981 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMERS SERVICE NEUTRAL WAS BROKE ON POLE 46-203, REPLACED CONNECTION 2309. VER/CRB
16456 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2010-06-09 17:29 | 2010-06-09 19:26 | 2 | 117 | 59428-1 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAD BAD CONNECTIONS ON XFMR POLE. COMPLTED COD-2 VER/HFP L3/HFP
16457 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-04-06 14:43 | 2016-04-06 16:40 | 2 | 117 | 4058821 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT ON POLE 117-61 BAD CUTOUT DOOR BURNT OUT REPLACED DOOR FUSED UP EVERYTHING OK/ ISO 37830117000061/ COD 2/ VER/BOW
16458 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-09-04 16:33 | 2010-09-04 18:30 | 2 | 117 | 63674-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WR# 36752188 // FUSE LINK BROKE//COD 2// VER/DBM IDC XXXX
16459 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-01-18 11:38 | 2016-01-18 13:35 | 2 | 117 | 4628341 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XFM ON POLE 73-396 @ 13:10 TO MAKE REPAIRS CLOSED BACK IN @ 13:35.FOUND CONNECTIONS MELTED ON SEC. POLE 73-495./ ISO37820073C00396/ COD 2/ VER/BOW
16460 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-06-13 11:01 | 2020-06-13 14:05 | 3 | 184 | 4013401 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | opened transformer on 141 at 13:40 closed back at 14:05 replaced bad connections at transformer
16461 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2019-05-07 11:27 | 2019-05-07 12:45 | 3 | 78 | 4235741 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad c/0 door. changed 2 hot connections at pole. xfmer off @ 12:30 on @ 12:45//PART POWER FROM THE BEGINNING OF OUTAGE//OUTAGE STARTED @ 1127
16462 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2019-01-19 19:17 | 2019-01-19 20:35 | 3 | 78 | 4688901 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required broke cutout 249-52 L3/HFP
16463 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2017-06-17 10:12 | 2017-06-17 11:30 | 3 | 78 | 4987281 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-270 BAD CUTOUT AND LA CHGED 20T LINE FUSE 1123-478 VER/CRB
16464 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-07-31 22:58 | 2008-08-01 02:52 | 1 | 234 | 63187-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNT INTO VER/ARN IDC XXXX
16465 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-10-09 23:18 | 2018-10-10 01:15 | 2 | 117 | 4213451 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o door burnt up--replaced--in at 01:15--allgood--ds101018 L3/HFP
16466 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-02-03 09:27 | 2021-02-03 10:45 | 3 | 78 | 4933201 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 375-C-82. customer is mismapped. cutout broke on pole 375-C-82. cutout replaced, power restored @ 10:45
16467 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2017-06-04 16:31 | 2017-06-04 20:25 | 1 | 234 | 4904541 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 449-551, REPLACED XFMR RESTORED POWER AT 20:25 37830449C20551 1
16468 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-04-25 13:45 | 2015-04-25 14:24 | 6 | 39 | H4364411 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 @ 37830247D01085 === NEED LINE CREW AND A 50 KVA 7200 === CHANGED TRANSF OUT === OPEN LINE FUSE @ 37830248B11636 AT 13:45 SO CREW COULD LIFT HOT TAP @ 37830247D01085// ALL POWER BACK ON @ 14:24 POWER OK/ ISO 37830247D01085/ COD 1/ IN HOIS FOR OFF TIME ON LINE FUSE 37830248B11636 6 CUSTOMERS VER/HFP L3/HFP
16469 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-10-25 12:50 | 2009-10-25 13:29 | 6 | 39 | 52995-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP MISMAPPED-CORRECT TRANSFORMER POLE FOR CUSTOMER IS 38830045A41708--E MAIL TO RAYBURN BAD ARRESTOR ON POLE 38830045A41708 NEEDS REPLACED ENERED MD & SENT EMAIL TO L. RAYBURN TO HAVE ARRESTOR REPLACED..HFP L3/HFP IDCC PN1638 XXXX
16470 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-01-06 22:40 | 2009-01-07 00:37 | 2 | 117 | 52189-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-2 OPENED CUTOUT ON POLE 49-198 TO ISOLATE AND ALLOW SERVICER TO REPLACE CUTOUT ON POLE 49-199 L3/HFP IDCC PN199 XXXX
16471 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-10-13 18:36 | 2014-10-13 22:30 | 1 | 234 | 4614341 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NEED LINE CREW TO REPAIR BAD UG NO TRUCK RELEASED BY CREW 078S05 VER/CRB
16472 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-02-14 07:43 | 2019-02-14 09:40 | 2 | 117 | 4792921 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 9:40. sh
16473 | Hazard | 3309301 | VICCO | REDFOX | 2010-07-16 13:18 | 2010-07-16 15:15 | 2 | 117 | 50932-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING SECONDARY CONNECTION NOW....FOUND BAD CONNECTION ON TRANSFORMER ,,, IN SUCH A BAD LOC. REDONE ALL CONNECTIONS... P.HICKS... ALL POWER RESTORED @15:15 HRS. COD-2 VER/HFP L3/HFP IDC XXXX
16474 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2020-09-14 15:27 | 2020-09-14 16:45 | 3 | 78 | 4463011 | 234 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop hot leg burnt in two. Repaired
16475 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-05-21 18:33 | 2014-05-21 19:12 | 6 | 39 | 4730891 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE VER/SEF
16476 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-10-23 21:32 | 2013-10-23 22:50 | 3 | 78 | 4958311 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK //VER/GAH L3/HFP
16477 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-10-07 15:33 | 2019-10-07 17:30 | 2 | 117 | 4112181 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN,WILL REPLACE IT/////////REPLACED CUTOUT&RESTORED POWER
16478 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-03-03 12:12 | 2013-03-03 13:30 | 3 | 78 | 4867831 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. CUTOUT IS BAD. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT.//COD 3// VER/DBM IDC XXXX
16479 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-02-11 08:38 | 2008-02-11 10:35 | 2 | 117 | 58831-1 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311401//OLD CUTOUT NEEDS REPLACED AND SECONDARY RISERS NEED REBUILT. POWER IS NOT OFF. ALSO SECONDARY CONNECTIONS ARE MELTING OFF DUE TO OVERLOAD ON 2/3 SECONDARY THAT SERVES 2 MOBILE HOMES RELEASED BY CREW 077S07 VER/HFP IDCC TOF0736 ESTIMATED TIME OFF XXXX
16480 | Pikeville | 3413401 | GARRETT | GARRETT | 2014-06-25 10:08 | 2014-06-25 12:05 | 2 | 117 | 4153621 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER IS MISMAPPED , THIS METER IS SERVED FROM 271 INSTEAD OF 270 . REPLACED CUTOUT, ALL WORK COMPLETE / GXJ
16481 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-09-17 17:36 | 2012-09-17 18:15 | 6 | 39 | 4054681 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 329-371, OPENED LINE FUSE AT POLE 329-49 AT 17:36 TO ISOLATE ,REPLACED CUTOUT. RESTORED POWER AT 18:15 COD-6 ISO LF 37830329000049 ///VER/CRB L/3 CRB IDC XXXX
16482 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-10-05 02:22 | 2014-10-05 03:40 | 3 | 78 | 4554531 | 234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN. POWER RESTORED. FETR 0400 VER/KEP
16483 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-03-28 15:50 | 2008-03-28 19:43 | 1 | 233 | 61654-1 | 233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3402801//CUST HAVING VOLTAGE PROBLEMS(WAS GETTING BACKFEED/OVERVOLTAGE)//30T FUSE BLOWN ON POLE 38830809000687 DUE TO LIGHTNING. LIGHTNING ARRESTORS NEED REPLACED ON POLE 38830809D41008 AND 38830809D41009. PLEASE SEND TO ENGINEERING. ALSO SEND TO PERRY FARMER BECAUSE THIS HAS BEEN OUT DUE TO LIGHTNING SEVERAL TIMES. SH//COD 1// VER/DBM IDCC PN1010 XXXX
16484 | Pikeville | 3413402 | GARRETT | LACKEY | 2018-03-28 10:38 | 2018-03-28 14:31 | 1 | 233 | 4137121 | 233 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10 kva xfmr,no truck access, this xfmr powers the elevator only and customer has agreed to wait till Thursday 03-29-18 for full power restoration, ops order # 031651264 created for repair, LCS T. McCoy informed / GXJ Released by crew 074S03
16485 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-12-18 02:30 | 2015-12-18 06:23 | 1 | 233 | 4541441 | 233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA // CREW ENROUTE// POWER RESTORED @ 6:23 VER/CRB
16486 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-11-13 00:13 | 2019-11-13 04:06 | 1 | 233 | 4027861 | 233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15KVA can get squirt boom to pole/// Myles Robinette and Shane Tackett coming to assist/// Changed bad xfm and cutout ///Restored @ 04:06/ ISO 37830190B00054/ COD 1
16487 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-03-19 11:22 | 2020-03-19 15:15 | 1 | 233 | 4491801 | 233 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | Bad 19.9 cutout. crew requiredA
16488 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-05-23 13:12 | 2012-05-23 17:05 | 1 | 233 | 4823321 | 233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | MYLES ROBINETTE IS COMING TO CHG. XFMR PLEASE SNND THIS TO HIM. RELEASED BY CREW 074S04//// XFMR REPLACED// POWER IS RESTORED// NEEDS SEC. POLE SET CUST. SER IS VERY LONG// R/W NEEDS CUT IN HOLLOW VER/KEP IDC XXXX
16489 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-06-23 06:47 | 2018-06-23 10:00 | 5 | 193 | 4651451 | 233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp loose at pole 38821081000075/ open xfmr 38821081000075 @ 0950 (4cc)/ Restored 1000
16490 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-11-13 09:27 | 2020-11-13 13:20 | 1 | 233 | 4672591 | 233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva transformer, 7200, 120/240, two bushing. Trucks to pole. Pole 1123-c2-4568. Crew required Released by crew 078S02/ ISO 39831123C24568/ COD 1
16491 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-02-10 05:04 | 2018-02-10 08:57 | 1 | 233 | 4822351 | 233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | contacted customer// customer reports meter is blank // customer states ok to wait until start time today //XFRF IS OUT,WILL RE-FUSE////////RE-FUSED&RESTORED,FUSE HAD ROTTED INTO
16492 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-11-11 11:58 | 2008-11-11 15:51 | 1 | 233 | 63930-1 | 233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401801//BAD 15 KVA XFMR....CALLED TIM MILLER..HE IS SENDING A CREW TO CHG XFMR...BB RELEASED BY CREW 076S01// ON SITE REPLACING BAD 15 KVA TCM//COD 1// VER/DBM IDCC PN80 XXXX
16493 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-05-02 10:31 | 2013-05-02 12:27 | 2 | 116 | 4065201 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONECUSTOMER STILL OFF WILL NEED TO REPLACE METER BASE WILL CALL WHEN WORK IS COMPLTED RELEASED BY CREW 078H18 ///VER/CRB L/3 CRB IDC XXXX
16494 | Hazard | 3309003 | JEFF | VIPER | 2022-02-17 17:44 | 2022-02-17 19:40 | 2 | 116 | 4495141 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced c/o
16495 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-02-24 06:44 | 2012-02-24 08:40 | 2 | 116 | 4491361 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP L3/HFP IDC XXXX
16496 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-06-26 22:11 | 2009-06-27 02:03 | 1 | 232 | 64035-1 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT VER/ARN
16497 | Hazard | 3309003 | JEFF | VIPER | 2018-01-01 12:13 | 2018-01-01 16:05 | 1 | 232 | 4692561 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Called Customer No Answer will need to replace service drop/ ISO 37830370000093/ COD 1
16498 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-08-12 17:53 | 2011-08-12 21:45 | 1 | 232 | 4700871 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TREE LIMB FELL THROUGHT SECONDARY POLE, &BLOWED XFMR FUSE. BAD XFMR. CHANGED XFMR RESTORED POWER AT 2145. COD-1 ISO TF 37830400B00214 VER/HFP L3/HFP IDC XXXX
16499 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2013-07-24 08:08 | 2013-07-24 10:04 | 2 | 116 | 4586141 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE XFMR CUTOUT. HAVE CONTACTED CREW TO HELP WITH THIS VER/CRB L/3 CRB IDC XXXX
16500 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2021-04-27 14:22 | 2021-04-27 15:20 | 4 | 58 | 4484391 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad c/o on 211-73// also repaired bad place in cust. s/d // opened xfmr @ 14:22 // closed @ 15:20
16501 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-03-02 22:33 | 2016-03-03 02:25 | 1 | 232 | 4804771 | 232 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NO VOLTAGE ON 1 LEG U.G. SERVICE. CREW, ADDAPHASE..2ND HOUSE ON RIGHT RELEASED BY CREW 078S07,,,CREW ON SITE,,,INSTALLED POWER TEMP,,ALL POWER RESTORED VER/KEP
16502 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-12-12 07:53 | 2013-12-12 08:51 | 4 | 58 | 4155531 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE VER/SEF L3/HFP
16503 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-06-25 21:01 | 2010-06-25 22:57 | 2 | 116 | 57623-1 | 232 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NEUT ON UNDERGROUND AT POLE BAD == REPAIRED == POWER OK IDC XXXX
16504 | Hazard | 3309301 | VICCO | REDFOX | 2014-12-25 19:29 | 2014-12-25 21:25 | 2 | 116 | 4884921 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, BAD CUTOUT ON POLE 301-335, REPLACED CUTOUT, POWER RESTORED
16505 | Hazard | 3303902 | LESLIE | WOOTON | 2022-05-05 13:39 | 2022-05-05 17:31 | 1 | 232 | 4840721 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kva tranformer. Manual Released by crew 077S06.replaced xfmr..
16506 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-07-29 14:24 | 2008-07-29 16:20 | 2 | 116 | 61847-1 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3001102// CALLED CWT TO ASSIST-E MAIL TO RAYBURN TO REPLACE ARRESTOR IDCC CNT1, PN55 XXXX
16507 | Whitesburg | 3401301 | FLEMING | NEON | 2010-07-31 16:12 | 2010-07-31 18:08 | 2 | 116 | 59882-1 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD AND I WILL NEED ONE MAN TO HELP THANKS//VER/CRB IDC XXXX
16508 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2017-01-15 19:14 | 2017-01-15 23:06 | 1 | 232 | 4300471 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1914 SCADA INDICATES FEEDER BREAKER LOCKOUT ON THE ALLEN-ALLEN 12KV CKT//BURNT OFF CROSSARM ON RECLOSER POLE 1027-C-590//CALLING CREW//CROSSARM BURNT OFF ON REC POLE DUE TO CUTOUT FAILURE. OPENED SW 1027-64 AND TAGGED TO DDC.//SEE DOL CASE 714714//COD 813//CLOSED CB @ 2059//CLOSED SWS 1027-64 @ 2306 // NOTE DUP DUE TO OMS AREA CROSSING VERIFIED TIMES PER DOL & SCADA L3/HFP
16509 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-03-28 20:11 | 2020-03-29 00:03 | 1 | 232 | 4520551 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad cutout on 513B/9 power ok
16510 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2014-12-31 06:03 | 2014-12-31 09:55 | 1 | 232 | 4894111 | 232 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKEN ON 4/3 SERVICE DROP HAVE REPAIRS MADED ALL IS GOOD AT THIS LOC VER/CRB
16511 | South Williamson | 3411401 | DEWEY | INEZ | 2022-01-12 11:18 | 2022-01-12 15:10 | 1 | 232 | 4339091 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 KVA xfmer @ pole 720-C-80 will be making repairs// repairs made restored @ 15:10 complete AP
16512 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-02-22 18:10 | 2008-02-22 22:02 | 1 | 232 | 66379-1 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003701//LINE FUSE OPENED AT 1810 TO ISOLATE// COD -1// VER/TOM IDC XXXX
16513 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-09-09 19:03 | 2018-09-09 22:55 | 1 | 232 | 4067601 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tran c/o broke-replaced-allgood-ds090918
16514 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-03-24 17:14 | 2010-03-24 19:10 | 2 | 116 | 54122-1 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP OPEN AT THE HOTTAP. THE WIRE HAD NEVER BEEN TIGHTEN ON THE HOTTAP....DAH COD-2 VER/KEP L3/KEP IDC XXXX
16515 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-02-27 06:53 | 2017-02-27 10:45 | 1 | 232 | 4424921 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DONNIE JACKSON FOUND HOT SEC DOWN//CREW REQ//WIRE APPEARS TO HAVE BURNED DOWN IN THE CLEAR, WILL GO BACK WITH 1/0 SECONDARY R RAY VER/CRB L3/HFP XXXHFP
16516 | South Williamson | 3411401 | DEWEY | INEZ | 2017-12-04 14:04 | 2017-12-04 16:00 | 2 | 116 | 4620211 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke on pole 744-277//repairs made//restored at 16:00//complete//em
16517 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-06-24 13:08 | 2015-06-24 17:00 | 1 | 232 | 4651281 | 232 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | CUT OUT DOOR BURNT UP//// REPLACED BAD DOOR AND RESTORED SERVICE//// THIS WAS @ PRIMARY METERING POLE# 358-D-430 ON C PHASE// VER/ ADH
16518 | Cannonsburg | 3001401 | LOUISA | CITY | 2013-03-19 16:48 | 2013-03-19 20:40 | 1 | 232 | 4922221 | 232 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | CUSTOMER COMPLAINING ABOUT LOW VOLTAGE. ONE FUSE WAS BROKE ON XMF BANK, REPLACED FUSE APR AT 2015 CLOSE TICKET COD-1 ISO TF 38830454A41655 VER/HFP L3/HFP IDC XXXX
16519 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-06-19 12:27 | 2015-06-19 14:23 | 2 | 116 | 4610761 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED NEUTRAL CONNECTION THAT HAD BURNED INTO AT THE TRANSFORMER.// VER/ ADH
16520 | Hazard | 3308002 | JACKSON | PANBOWL | 2014-07-11 21:53 | 2014-07-12 01:45 | 1 | 232 | 4231071 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1059D-177 . REPLACED CUTOUT , CLOSED XFMR BACK @ 01:45
16521 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-06-17 11:06 | 2010-06-17 14:58 | 1 | 232 | 50462-1 | 232 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO OUTAGE......FOUND BAD INSULINK CONNECTOR ON ONE HOT LEG OF 2/3 SERVICE DROP, WHERE IT HAD BEEN SPLICED.....REPLACED CONNECTION.....VOLTAGE GOOD NOW.....VOLTAGE GOOD NOW....JRV.....06/17/10
16522 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-01-09 13:53 | 2022-01-09 17:45 | 1 | 232 | 4328951 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LONG 1/0 SERV PULLED LOOSE@XFR.NEED 1 MAN,LONG REACHING BUCKET,PIECE OF 1/0 SERV DROP//////////MADE REPAIRS&RESTORED@17:45,ALL OK AFTERWARDS///////PULLED APART@TENSION SPLICE
16523 | Pikeville | 3421001 | BREAKS | CITY | 2020-08-13 08:04 | 2020-08-13 10:00 | 2 | 116 | 4318221 | 232 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke in secondary///will make repairs/// Repaired broken neutral and several bad secondary and service drop connections///Customer has damage to equipment Please send copy to Damage Claims///Restored service @ 10:00 this secondary only fed two customers per servicer
16524 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2015-06-26 20:37 | 2015-06-26 21:35 | 4 | 58 | 4666051 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 77-34 SOLID BLADE CUTOUT BROKEN, VER/ARN
16525 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-12-25 19:39 | 2018-12-25 21:35 | 2 | 116 | 4598111 | 232 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Called customer: customer saw flash on transformer and heard a pop lights went off ofr a second then came back on and stayed dim throughout house,,,resqueezed service connection complete L3/HFP
16526 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2017-01-02 16:54 | 2017-01-02 18:50 | 2 | 116 | 4262771 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | METER IS BLANK TRANSFORMER CUTOUT FAILED. REPLACED AND RESTORED @ 18:50. SH 38830810B00209 VER/AWD L3/HFP XXXHFP
16527 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-02 16:54 | 2008-12-02 18:50 | 2 | 116 | 54013-1 | 232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401//C/O GATE BURNED UP CALLED JEFF COMBS TO BRING ONE FROM STORES, CHANGED GATE POWER RESTORED//COD 2// VER/DBM L3/KEP IDC XXXX
16528 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2019-03-29 12:21 | 2019-03-29 14:00 | 4 | 99 | 4035261 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service burnt down on pole 351-C-30. need to open transformer long enough to make repairs. repairs made.. opened @ 13:16 closed @ 14:00
16529 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-06-03 13:43 | 2009-06-03 15:00 | 3 | 77 | 50440-1 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LARRY BROWN REPORTS OUTAGE HERE AT 2910 ROGERS DR// CHANGED BAD CUTOUT.//COD 3// VER/DBM IDCC XXXX
16530 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-07-25 17:29 | 2013-07-25 21:20 | 1 | 231 | 4593601 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA NEED LC AND YD\FETR 20:00 LRM RELEASED BY CREW 078H06/FETR 22:30 JEH/ REPAIRS COMP. POWER REST. @ 21:20// JEH VER/SEF IDC XXXX
16531 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-01-31 06:19 | 2019-01-31 10:10 | 1 | 231 | 4742321 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burned down will replace
16532 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-10-03 10:23 | 2016-10-03 14:14 | 1 | 231 | 4955961 | 231 | PARTIAL POWER | EQUIPMENT FAILURE | NONE | FOUND NEUTRAL BROKE @ CUSTOMER WEATHERHEAD..PULLED CUSTOMER METER AND REPAIRED... VER/CRB L3/HFP XXXHFP
16533 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-03-22 09:43 | 2014-03-22 11:00 | 3 | 77 | 4517661 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 10T FUSE OUT DUE TO BROKEN CUTOUT . WILL BE CHANGING. CUTOUT CHANGED OUT EVERYTHING OK. VER/SEF
16534 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2021-03-07 13:49 | 2021-03-07 17:40 | 1 | 231 | 4311801 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on xfmr pole burning neutral in two midspan. Replaced service and restored @ 17:40. sh
16535 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-09-08 08:11 | 2011-09-08 12:02 | 1 | 231 | 4847081 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE INTO ON POLE NO.377-246 RELEASED BY CREW 077S12 REPLACED CUTOUT VER/KEP IDC XXXX
16536 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-10-30 16:31 | 2019-10-30 17:48 | 3 | 77 | 4221511 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse Cutout broke on pole 193-226 will make repairs// Changed bad cutout and restored service @ 17:48
16537 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-06-05 14:13 | 2015-06-05 18:04 | 1 | 231 | 4515741 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT. CREW ENROUTE WITH BIG BUCKET TRUCK AND CUTOUT. 19.9KV. RELEASED BY CREW 074S02/// REPAIRS MADE 18:04 BACK TO NORMAL R RAY/ ISO 37820169000010/ COD 1/ VER/BOW
16538 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-09-02 07:17 | 2015-09-02 11:08 | 1 | 231 | 4189611 | 231 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, LOOKING FOR PROBLEM REPAIRS MADE NEW S.D & REPAIRED NEUT. N SEC. XFMER OFF @ 10:45, ON @ 11:08 (2 ADD. CUST) DUPLICATE IN HOIS/ ISO 38830069D37131/ COD 3/ VER/BOW
16539 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2021-01-10 13:39 | 2021-01-10 17:30 | 1 | 231 | 4859801 | 231 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | insulaink had failed and burned hot leg and neutral into on service drop///i repaired service drop//restored at 17:30//complete//em
16540 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-05-21 11:43 | 2019-05-21 13:00 | 3 | 77 | 4310951 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout
16541 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-05-19 17:25 | 2020-05-19 21:16 | 1 | 231 | 4859391 | 231 | PARTIAL POWER | EQUIPMENT FAILURE | INSULATOR | 1 OF 3 XFR FUSES IS OUT.THIS IS A DELTA BANK THAT I CANT REACH.KINDOF UNSAFE TO GET ON POLE WITH THIS TO OPEN/CLOSE FUSES.1 MAN&BUCKET ENROUTE. APPEARS BAD PIN TYPE INSULATOR CAUSED OUTAGE HERE,WE REPLACED IT
16542 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-07-15 23:19 | 2019-07-16 03:10 | 1 | 231 | 4714601 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Might be a broken line from pole/part power in house. Customers transformer pole is 38830850000153. Three xfmr delta bank - C phase xfmr bad. I isolated outside xfmrs, cut secondary leads out of bank, bonded H2 bushing to neutral and restored as a single 25 KVA xfmr. oo2 cust affectedoo I will send engineering a job to remove two outside xfmrs - 3 phase no longer used here. sh
16543 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-04-05 14:13 | 2020-04-05 15:30 | 3 | 77 | 4562211 | 231 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection @ xfm...repaired and restored...
16544 | Hazard | 3309302 | VICCO | JEFF | 2017-12-30 14:19 | 2017-12-30 15:36 | 3 | 77 | 4689071 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout fuse door replaced door
16545 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-04-04 07:07 | 2010-04-04 07:40 | 7 | 33 | 58363-1 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SECONDARY POLE 37830094000236 HAS BURNED DOWN NO COUST.SERVED FROM THIS SEC. NEED TO HAVE JOB WRITTEN TO RETIRE POLES 37830094000236 & 37830094A10282 POLES & SECONDARY.CHG COUST COUNT TO 5 VER/KEP L3/KEP IDC XXXX
16546 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2020-12-21 21:57 | 2020-12-22 01:48 | 1 | 231 | 4791921 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 by truck, bring a material handler squirt boom if possible. after you drive by the barn on saddle town its the gate on your left Released by crew 078H03
16547 | Hazard | 3309301 | VICCO | REDFOX | 2015-03-01 17:33 | 2015-03-01 21:24 | 1 | 231 | 4089091 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD XFMR, WILL NEED 19.9 KV, 25 KVA . MANUEL. POWER RESTORED VER/SEF L3/HFP XXX
16548 | South Williamson | 3411401 | DEWEY | INEZ | 2014-10-07 12:37 | 2014-10-07 13:10 | 7 | 33 | 4565041 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 769-40//REPAIRS MADE/RESTORED AT 13:10//COMPLETE//EM COD-7 ISO TF 38820769C00040 VER/HFP L3/HFP
16549 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2018-05-31 13:36 | 2018-05-31 17:27 | 1 | 231 | 4528471 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 1123-4617 bad 12kv c/o, trks ok, to v. mullins Released by crew 078S07/crew on site/FETR 1745/vem/repairs made and power restored to all cust 1727/please close ticket/thanks/vem
16550 | Hazard | 3303901 | LESLIE | HYDEN | 2021-09-10 22:58 | 2021-09-11 00:15 | 3 | 77 | 4231201 | 231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broke fuse
16551 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-05-02 11:35 | 2011-05-02 13:30 | 2 | 115 | 53513-1 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 15 T OUT ON 458-32--BAD 19.9 ARRESTOR ON 226-CUT IN CLEAR-SEND NOTE TO D CHRISTIAN--ON 1330--ALSO BLEW TR FUSE--CUSTOMER HAD LIGHTING DAMAGE--- FORGOT FCETR--WILL TRY HARDER- OL JIMBO COD-2 PER JIM ISO TF 37830458000226 VER/HFP L3/HFP IDC XXXX
16552 | Whitesburg | 3312902 | JENKINS | JENKINS | 2018-07-06 19:09 | 2018-07-06 21:04 | 2 | 115 | 4744241 | 230 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral in the service was broke into , I spliced it back. customer is still having trouble , I disconnected customer to get an electrician to find her problem. will call back to be reconnected
16553 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-02-08 15:09 | 2011-02-08 15:55 | 5 | 46 | 55370-1 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BROKEN HOT TAP COD-5 ISO PO 38830070A10059 VER/HFP L3/HFP IDC XXXX
16554 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-03-30 22:02 | 2011-03-30 23:57 | 2 | 115 | 60668-1 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTIONS ON TRANSFORMER SECONDARY RISERS ARE ABOUT BURNED INTO. I AM GOING TO OPEN TRANS. AND RESQUEEZE CONNECTIONS. I RESQUEEZED TRANS. CONNECTIONS. CUSTOMER SAID HE HAD A TV AND MICROWAVE DAMAGED. SEND TO PEGGY WYSONG. //VER/GAH IDC XXXX
16555 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-05-14 16:40 | 2009-05-14 20:30 | 1 | 230 | 55622-1 | 230 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | B PHASE OUT ON PRIMARY METERING POLE LOOKED LINE OVER I GOING TO REFUSE CUTOUT FUSE CAME BACK OUT GOING TO ISOLATE COAL CO. LINE AND TRY AGAINOPENED RV ON POLE 423-278 AT 1945 CLOSED IT AT 1959 CLOSED METERING IN AT2030
16556 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-08-13 15:08 | 2016-08-13 17:03 | 2 | 115 | 4770971 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830188B12011 FUSE BROKE, BROKE C/O--REPLACED BOTH--ALLGOOD--DS081316 VER/AWD
16557 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2020-10-26 09:21 | 2020-10-26 13:11 | 1 | 230 | 4584571 | 230 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | basket & hot clamp burnt up. repairs made. pls close. tre/ 38830115B00370
16558 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2017-10-31 10:47 | 2017-10-31 12:42 | 2 | 115 | 4519191 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTOMER HAS NEUTRAL AND ONE CONDUCTOR BURNT INTO ON SEC. WIRE.WILL CUT LOOPS AND MAKE REPAIRS////ONLY FOUND NEUTRAL BURNT INTO ON SEC. FEEDING THIS ONE CUSTOMER..SAYS THEY HAVE APPLIANCES BURNT UP///PLEASE SEND COPY TO PEGGY WYSONG..
16559 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-01-13 10:10 | 2020-01-13 14:00 | 1 | 230 | 4296991 | 230 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | restored b phase xfmer.
16560 | Hazard | 3309302 | VICCO | JEFF | 2010-10-03 12:40 | 2010-10-03 16:30 | 1 | 230 | 56429-1 | 230 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKEN MIDSPAN IN SECONDARY---NEED CREW TO HELP REPLACE SECONDARY -- CUST. HAS EQUIPMENT DAMAGE THROUGHOUT HOME. OPEN X-FMR AT 15:45 (INTERRUPTING 2 MORE CUSTOMERS, SEE H56429-1)) CLOSED AT 16:30 POWER RESTORED. // SENT TO D CHRISTIAN AND P WYSONG // VER/DBM IDC XXXX
16561 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-03-11 10:30 | 2017-03-11 14:20 | 1 | 230 | 4548221 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SURGE PROTECTOR APPEARS TO BE BAD .WILL REPAIR.XFMR IS ALSOO BAD WILL NEED 25KVA 19.9/120-240 2 LINEMAN & 4WHEEL DRIVE MATERIAL HANDLER. POWER IS RESTORED VER/AWD
16562 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-05-14 14:40 | 2018-05-14 17:10 | 2 | 150 | 4347951 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed and burnt neutral and one hot conductor open on sec pole 810-337. Opened xfmr 38830810A00250 @ 15:50 to make repairs.//COD 2//Connection failed and burnt neutral and one hot conductor open on sec pole 810-337. Opened xfmr 38830810A00250 @ 15:50 to make repairs. Made repairs and closed xfmr @ 17:10. sh
16563 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-07-31 12:15 | 2012-07-31 16:05 | 1 | 230 | 4870551 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. THERE IS A BANK OF XFMRS ON POLE 38830858A00206 THAT ARE NOT SHOWING ON MY FIELDVIEW. REPLACED CUTOUT AND RESTORED @ 16:05. THREE 25KVA XFMRS ON POLE 38830858A00206 SERVE METER 428783879. PLEASE ADD TO MAP. <<ONLY ONE CUSTOMER AFFECTED>> SH//ISO//COD 1//MD FILED// VER/DBM
16564 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2009-01-15 18:22 | 2009-01-15 18:45 | 10 | 23 | 55311-1 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008002//BAD 10T FUSE//COD 10T/ VER/KEP L3/KEP
16565 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-01-04 22:35 | 2021-01-05 00:30 | 2 | 115 | 4848221 | 230 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | spoke with customer, what they are describing sounds more to be a dim lights condition than a part power//advised to turn main breaker off to avoid damage // customer has broken neutral in service drop// will be making repairs// customer is restored
16566 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-05 04:05 | 2011-01-05 07:55 | 1 | 230 | 58769-1 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PRIMARY OPEN DUE TO BAD CURRENT LIMIT FUSE. I WILL BE MAKING REPAIR. I HAVE REPAIRS MADE FUSED UP EVERYTHING OK. SEND COPY OF THIS TO ENG PIKEVILLE TOM MAMING. I HAVE HAD 10 OR 12 OF THESE 23KV COMPANION 11 BACK UP CURRENT-LIMITING FUSE TO BURN UP. NOT SURE WHAT IS GOING ON. THESE HAVE ONLY BEEN ON LINE LESS THAN 2 YEARS I TALKED TO DONNIE JACKSON HE HAS HAD SEVERAL OF THESE TO BURN UP ON A NEW SECTION OF LINE. WE NEED TO DO SOMETHING ELSE UNTIL WE FIND SOMETHING OUT. VER/KEP L3/KEP IDC XXXX
16567 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-07-24 07:25 | 2008-07-24 09:20 | 2 | 115 | 59613-1 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400301// TRANSFORMER CUTOUT DOOR BURNED UP...REPLACED DOOR AND 1.6 T FUSE D LEWIS 07-24-08 RELEASED BY CREW 074H08 VER/TOM IDCC CNT1 XXXX
16568 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-04-19 19:45 | 2008-04-19 21:40 | 2 | 115 | 52516-1 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP. I HOPE CUTOUT DOOR IS OK. I AM GOING TO CHANGE DOOR AND SEE IF IT STAYS IN. I CHANGED DOOR. VER/ARN IDCC CNT1 XXXX
16569 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2015-11-21 13:05 | 2015-11-21 15:00 | 2 | 115 | 4476391 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE A BAD CUTOUT .WILL CHANGE .REPLACED BAD CUTOUT/ ISO 37830066C00012/ COD 2/ VER/BOW
16570 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-06-09 13:53 | 2022-06-09 15:48 | 2 | 115 | 4049141 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Loop burned open at pole 38830066000104 - not truck accessible crew on site fetr 15:50 LRM all pwr restored 15:48 pleaseclose ticket LRM///opened fuse on 66-98 to make repairs
16571 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-03-05 17:53 | 2018-03-05 21:43 | 1 | 230 | 4969241 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 KVA trans 881-1994 on need 25KVA 7200 trans mat handler and one A lineman trk appreplaced trans restored power at 21:42/ ISO 38830881000194/ COD 1** per servicer
16572 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-02-06 12:23 | 2014-02-06 14:18 | 2 | 115 | 4362871 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR TO RE-FUSE//////CHECK THAT,CUTOUT IS BROKEN,WILL REPLACE IT///////REPLACED CUTOUT AND RESTORED,ALL OK AFTERWARDS VER/HFP L3/HFP IDC XXXX
16573 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-12-11 10:44 | 2017-12-11 14:34 | 1 | 230 | 4638871 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Txmf fuse hanging dn, Bad 19.9kv Txmf, 25kva may reach with bucket crew required./ 38830165A00141 is actual transformer thats bad its not shown on map. Crew on site making repairs, Repairs made ticket complete/ ISO 38830165A00141/ COD 1/ actual fault/isolating pole not shown on map md done
16574 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2017-02-27 11:49 | 2017-02-27 13:44 | 2 | 115 | 4425791 | 230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKED LIKE FUSE JUST BROKE, APR AT 1344 CLOSE TICKET. DWEST VER/CRB L3/HFP XXXHFP
16575 | Hazard | 3303902 | LESLIE | WOOTON | 2019-10-03 09:24 | 2019-10-03 13:13 | 1 | 229 | 4089351 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole need new leads put in xfmr, Released by crew 077H14.re-made connections on xfmr pole, found open nue in meter base, made repairs, voltage ok..p.hicks
16576 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-08-29 08:21 | 2008-08-29 12:10 | 1 | 229 | 57205-1 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD 19.9 CUTOUT AND LA RELEASED BY CREW 078S08 RESTORED @12:10 8/29/08 M.PHELPS COD-1 IDC XXXX
16577 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-05-29 08:11 | 2014-05-29 12:00 | 1 | 229 | 4947621 | 229 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER , SERVICE WIRE BROKE IN MID SPAN, THIS IS # 4 SERVICE DROP WILL GET CREW TO REPLACE WITH 2/3 WIRE , 150 SPAN. RELEASED BY CREW 077S11 REPLACED SERVICE VER/KEP
16578 | Hazard | 3307301 | BULAN | ARY-HEINE | 2019-07-14 08:11 | 2019-07-14 12:00 | 1 | 229 | 4706721 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva transformer, 7200 kv,will replace 72 cutout also.
16579 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-05-20 22:26 | 2022-05-21 02:15 | 1 | 229 | 4919681 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr on 404-185 in @ 0215/ Please close ticket/MLH
16580 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2012-11-21 18:16 | 2012-11-21 22:05 | 1 | 229 | 4414181 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6T FUSE OUT DUE TO BAD TRANSFORMER. CREW ON THE WAY. WE HAVE TRANSFORMER CHANGED OUT EVERYTHING OK. ///VER/CRB L/3 CRB IDC XXXX
16581 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2019-06-20 11:02 | 2019-06-20 14:51 | 1 | 229 | 4554791 | 229 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad ground connection at xfmr, made repairs , replaced cutout, restored power at 14:51
16582 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-05-22 19:36 | 2012-05-22 23:25 | 1 | 229 | 4820041 | 229 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG OPEN IN URD SERVICE /// GOING TO CHECK CONNECTIONS ON POLE /// CONNECTIONS ON POLE CHECK GOOD /// WILL NEED TO GET ADD-A-PHASE TO FIX FOR TONIGHT /// WILL NEED 2 MEN /// CUSTOMER SAID THEY ARE INTERESTED IN GOING WITH AN OVERHEAD SERVICE /// PLEASE SEND TO CLIFF FREEMAN TO GET TECH OUT ASAP TO DISCUSS OPTIONS//COD 1//EMAILED TO TECH// VER/DBM IDC XXXX
16583 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-04-10 13:19 | 2015-04-10 17:08 | 1 | 229 | 4304681 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 55` POLE CALLING BRUCE FOR HELPBROKE 19.9 CUTOUT ON 55 FOOT POLE NEED BIG BUCKET AND CUTOUT . THIS SERV A LITTLE STORGE BUILDING. LARRY LAWSON WITH ELLIOTT IS COMMING TO CHANGEBROKE 19.9 CUTOUT ON 55 FOOT POLE NEED BIG BUCKET AND CUTOUT . THIS SERV A LITTLE STORGE BUILDING. LARRY LAWSON WITH ELLIOTT IS COMMING TO CHANGE RELEASED BY CREW 077S05/CLOSED 1708// VER/ ADH
16584 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-08-31 12:51 | 2020-08-31 16:40 | 1 | 229 | 4407541 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 19.9 XFM, crew required
16585 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-01-30 10:06 | 2017-01-30 13:55 | 1 | 229 | 4341811 | 229 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SERVICE DROP/ ISO 37820098D47010/ COD 1/ VER/BOW L3/HFP XXXHFP
16586 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-09-10 23:42 | 2016-09-11 03:31 | 1 | 229 | 4884341 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O HAVE REPLACED AND POWER IS RESTORED AT THIS LOC AT 0331 BY AMG//COD 1// VER/DBM
16587 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-12-17 14:26 | 2008-12-17 18:15 | 1 | 229 | 59615-1 | 229 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3116702//FOUND BAD UNDER CABLE GIVE TICKET TO BILL FRALEY WILL MAKE REPAIRS IN MORNING GIVE COPY OF TICKET TO DAN HUFF RELEASED BY CREW 078S09//EMAILED TO D HUFF// VER/KEP L3/KEP IDC XXXX
16588 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2021-09-02 10:11 | 2021-09-02 14:00 | 1 | 229 | 4201791 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/0 quadraplex 480 volt service burndt down off bank pole 47-C-327, looks like a connection failed and burndt the service down, 1 water pump meter out of power, will be making repairs.
16589 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-04-28 11:11 | 2014-04-28 15:00 | 1 | 229 | 4641011 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOT A BAD CSP TRANSFORMER, NEED 25 KVA TRANS AND CUTOUT AND ARRESTOR FOR 7200 RELEASED BY CREW 077S05 REPLACED TRANSFORMER COD-1 ISO TF 38831083C40423 VER/HFP L3/HFP
16590 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-09-01 16:41 | 2019-09-01 20:30 | 1 | 229 | 4971601 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr on pole 329-54, will need 15 kva 19.9 xfmr , repaced xfmr restored power at 20:30
16591 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-01-15 12:36 | 2014-01-15 16:25 | 1 | 229 | 4284091 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 15 KVA { 19.9 } TRANSFORMER IS BAD. I CALLED FOR HELP. WE CHANGED TRANS.//COD 1// VER/DBM L3/HFP
16592 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-06-12 09:51 | 2008-06-12 13:40 | 1 | 229 | 63022-1 | 229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008001// BAD CUTOUT DOOR VER/HFP IDC XXXX
16593 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-02-28 08:50 | 2016-02-28 12:39 | 1 | 229 | 4783191 | 229 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN. @ XFMR BAD , REPAIRED CONN. XFMR HAS BEEN LEAKING OIL SEND TO BRUCE & DOUG TO GET CHANGED OUT . 15KVA 19.9 & CUTOUT , TBRACKET , CAN WORK POLE WITH BUCKET EMAILED HAZARD/ADH// VER/ ADH
16594 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-01-05 10:39 | 2015-01-05 11:55 | 3 | 76 | 4907351 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE. REPLACED. RESTORED @ 11:55. SH/ ISO 38830763000006/ COD 3/ VER/BOW
16595 | Pikeville | 3421001 | BREAKS | CITY | 2017-05-16 17:54 | 2017-05-16 19:48 | 2 | 114 | 4805711 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE ON 243B15 FAILED DUE TO AGE REPLACED FUSE RESTORED POWER A 19;48 VER/CRB
16596 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-10-14 14:04 | 2010-10-14 15:20 | 3 | 76 | 59738-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | STS WR # 37329254 POLE 1124-4238 TRANS. RISER BURNT OFF COD-3 VER/HFP L3/HFP IDC XXXX
16597 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-12-09 08:50 | 2019-12-09 12:06 | 2 | 196 | 4136921 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | bad cutout manual pole Released by crew 077H14 // opened line fuse to change cutout Off @ 1134 On @ 1206
16598 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-01-10 11:26 | 2019-01-10 13:20 | 2 | 114 | 4656041 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Hot Line Clamp burnt off on secondary at pole 39831147C14007/ opening transformer 39831147C14173hot line clamp on pole 39831147C14007 burnt off on A phase feeding 3 phase tap. opening xfmers on pole 39831147C14173 @ 12:33. send to b. tackett Released by crew 078H17,repairs made all cust restored @ 1320 please close ticket thanks.bt
16599 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2015-07-27 19:27 | 2015-07-27 23:15 | 1 | 228 | 4949171 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIDDLE PHASE CUTOUT CRACKED SETTING POLE1089A507 ON FIRE BETWEEN ARM BRACES AND SPAN GUY ATTACHMENT POLE MOSTLY BURNT INTO BEST TO REPLACE IT NOW 45 4 POLE WILL SEND MATERIAL LIST TO FOREMAN// HAD TO OPEN @ 1089-A-3 @ 2240 TO MAKE SAFE (260 CUST)////TOMMIDDLE PHASE CUTOUT CRACKED SETTING POLE1089A507 ON FIRE BETWEEN ARM BRACES AND SPAN GUY ATTACHMENT POLE MOSTLY BURNT INTO BEST TO REPLACE IT NOW 45 4 POLE OPENED @ 2240 CLOSED @ 2315/ DUPLICATE IN HOIS/ VER/BOW
16600 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2017-01-28 01:16 | 2017-01-28 02:32 | 3 | 76 | 4338151 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED THE TRANSFORMER FUSE THAT HAD BROKE./// VER/DKM
16601 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2021-05-28 09:44 | 2021-05-28 11:00 | 3 | 76 | 4635331 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found broken c/o, have replaced power restored at 1100 at this loc
16602 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-06-18 09:12 | 2020-06-18 13:00 | 1 | 228 | 4040401 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfmr is bad and in difficult location. This only feeds caution lights for roadway. I have talked to Tommy Goble and he will be replacing this at later date. Will need row cut before can be done Released by crew 076S03//I NOTIFIED THE KDOT
16603 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2020-05-22 09:37 | 2020-05-22 13:25 | 1 | 228 | 4885811 | 228 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hot leg burnt up got it repaired and power back to full quality at 13:25
16604 | Cannonsburg | 3001401 | LOUISA | CITY | 2009-01-06 18:39 | 2009-01-06 19:17 | 6 | 38 | 52071-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27950070 // BROKE CUTOUT,,,,,IT WAS A LOOSE CONNECTION AT THE HOT TAP L3/HFP IDC XXXX
16605 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-12-21 05:30 | 2016-12-21 09:18 | 1 | 228 | 4225911 | 228 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BOTH CONN AT CUSTOMERS WEATHER HEAD ONE WAS BAD, FULL POWER CLOSE TICKET. DWEST VER/HFP L3/HFP
16606 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-08-26 19:12 | 2014-08-26 19:50 | 6 | 38 | H4426081 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART OF 4426081//LOOSE CONNECTION ON XFMR.TOOK XFMR OFF AT 19..12.BACK ON AT 19.50//COD 6// VER/DBM
16607 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-02-09 12:56 | 2014-02-09 14:12 | 3 | 76 | 4369181 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED XFMR FUSE VER/SEF
16608 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-02-15 11:25 | 2010-02-15 15:13 | 1 | 228 | 57868-1 | 228 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL INVESTIGATE COMPLAINT///////SERV DROP CONNECTIONS WERE POOR,1 WAS OPEN,ALSO,THE NEUTRAL WAS INTO.MADE REPAIRS AND RESTORED//EMAILED TO PEGGY WYSONG DBM// VER/DBM IDC XXXX
16609 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-12-03 13:12 | 2010-12-03 17:00 | 1 | 228 | 62768-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BURNT DOWN....WILL HAVE TO OPEN XFMR TO REPLACE...4/3 DROP WAS UNDERSIZED AND BURNT DOWN...CUSTOMER HAD A 200AMP METERBASE...SEND A COPY OF THIS TO PEGGY WAYSON...POWER RESTORED @ 17:00//COD 1 (+4 SEE H62768-1)// VER/DBM IDC XXXX
16610 | Pikeville | 3402003 | KEYSER | MULLINS | 2016-04-05 14:16 | 2016-04-05 16:10 | 2 | 114 | 4055301 | 228 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED CONNECTION AT XFMR SECONDARY BUSHING 38831127A00118 COD 2 VER/AWD
16611 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-02-24 13:12 | 2014-02-24 14:09 | 4 | 57 | 4431001 | 228 | PARTIAL POWER | EQUIPMENT FAILURE | NONE | ONLY PART POWER COMING IN, BAD CONNECTION ON XFMR POLE, MADE REPAIRS VER/HFP L3/HFP
16612 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-02-20 15:12 | 2011-02-20 19:00 | 1 | 228 | 59494-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE BLOWN--- FUSE CAME BACK OUT BAD XFMR I CALLED D SAMMONS FOR XFMR HELP --TRUCK APP.//VER/CRB IDC XXXX
16613 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2012-05-01 08:26 | 2012-05-01 10:20 | 2 | 114 | 4728271 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP ON POLE 188-343. I MAY HAVE TO CHANGE CUTOUT. I CHANGED CUTOUT DOOR. ///VER/CRB L/3 CRB IDC XXXX
16614 | Pikeville | 3402003 | KEYSER | MULLINS | 2013-08-02 15:18 | 2013-08-02 16:15 | 4 | 57 | 4617591 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR. FUSE BLOWN //WILL REFUSE// FUSE LINK APPEARED TO HAVE BROKE// POWER IS RESTORED VER/SEF L3/HFP
16615 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-08-19 09:08 | 2011-08-19 09:46 | 6 | 38 | 4729701 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, CHANGED CUTOUT ALL POWER RESTORED AT 0946 CLOSE TICKET COD- 6 ISO TF 38830454B33237 VER/HFP L3/HFP IDC XXXX
16616 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-04-15 09:37 | 2016-04-15 10:53 | 3 | 76 | 4093431 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WAILL REPLACE BAD CUTOUT. POWER IS RESTORED./ ISO 38831077A00483/ COD 3/ VER/BOW
16617 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-02-06 15:44 | 2008-02-06 17:00 | 3 | 76 | 51599-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | IDC TRANS FIRE FOUND A BAD TRANSFORMER CUTOUT ON POLE 901-5677, HAVE IT CHANGED AND POWER IS RESTORED TO THE CHRISTAIN CHRUCH AT THIS TIME VER/HFP IDC XXXX
16618 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2012-01-13 09:07 | 2012-01-13 12:55 | 1 | 228 | 4256801 | 228 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD INSULINK SPLICE ON 1 HOT LEG OF SERVICE NEAR XFMR POLE..REPLACED CONNECTION..GOOD VOLTAGE NOW..JRV..01/13/12 VER/KEP IDC XXXX
16619 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-03-03 13:00 | 2019-03-03 16:48 | 1 | 228 | 4946781 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 425-158 , made repairs restored power at 16:48..
16620 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-08-21 13:51 | 2012-08-21 15:45 | 2 | 114 | 4958801 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830224D00105 ----- CREW ENROUTE.==== POWER RESTORED. VER/KEP IDC XXXX
16621 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-07-05 13:09 | 2020-07-05 14:25 | 3 | 76 | 4111971 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pulled into on pole 37830250B00093 MADE MD TO SHOW MISMAPPED CUST//COD 3
16622 | South Williamson | 3200301 | BELFRY | BELFRY | 2016-09-26 15:57 | 2016-09-26 19:45 | 1 | 228 | 4927781 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 990-A-502 CANT REACH IT WITH SERVICE TRUCK NEED A LINEMAN AND BIG BUCKETREPLACED CUTOUT RESTORED POWER AT 19;45 COD-1 ISO TF 38820990A00502 VER/HFP L3/HFP
16623 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-09-25 15:44 | 2020-09-25 16:22 | 6 | 38 | 4496111 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link had broke inside cutout dor causing outage. I instaled new fuse and restored @ 16:22
16624 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-12-19 08:59 | 2008-12-19 10:15 | 3 | 76 | 60089-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS TRANSFORMER FUSE HANGING DOWN STS TRANSFORMER FUSE BROKE IN TWO VER/ARN L3/KEP IDC XXXX
16625 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-01-24 09:13 | 2018-01-24 10:10 | 4 | 57 | 4769871 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | secondary leads on trans. bad connection 077h04 // PER ORDER 4768341 HAD A BAD CONNECTION ON THE XFMR POLE AND NEEDED CREW TO COME BACK TO REPLACE XFMR RISERS - L3/HFP
16626 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-11-03 22:03 | 2011-11-03 23:57 | 2 | 114 | 4048961 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A CUTOUT SERVING PRI. METERING HAS BROKEN DOWN ON POLE 358-430. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. VER/ARN IDCC PN253 XXXX
16627 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-04-20 23:56 | 2009-04-21 01:12 | 3 | 76 | 62222-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CUST SAID LINE CREW DONE WORK ON POLE ABOUT TWO DAYS AGO. POLE HAS NE EQUIPMENT. LOOKS LIKE NEW 6T FUSE BROKE. FUSED BACK UP EVERYTHING OK. VER/KEP L3/KEP IDC XXXXW
16628 | Pikeville | 3408101 | SALISBURY | PRINTER | 2019-09-30 13:44 | 2019-09-30 15:00 | 3 | 76 | 4075331 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 38831147000068, made repairs and restored @ 1500
16629 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-07-22 18:13 | 2020-07-22 22:01 | 1 | 228 | 4206781 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout at 39831099D26898. repairs made. pls close. tre
16630 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2022-04-29 15:18 | 2022-04-29 16:15 | 4 | 57 | 4815591 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Made per Adam Kidd found burnt up cutoutBad cutout on pole 38831121C00043 burnt crossarm into and cutout hanging by riser.//Crew en route.//No customers outage at this timeBad cutout on pole 38831121C00043 burnt crossarm into and cutout hanging by riser.//Crew en route.//No customers outage at this time.//Opened xfm @ 15:18.//Replaced cutout and crossarm and restored @ 16:15
16631 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-04-08 09:19 | 2009-04-08 10:35 | 3 | 76 | 50416-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// CUTOUT IS BROKE, REPLACED CUTOUT. 7.2 KV//COD 3// VER/DBM IDC XXXX
16632 | Whitesburg | 3308402 | BECKHAM | CARR CREEK | 2008-01-05 10:20 | 2008-01-05 14:08 | 1 | 228 | 54000-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308402// LUG BURNT OFF XFMR WILL HAVE TO REPLACE XFMR REPLACED LUG ONLY -// VER/TOM IDC XXXX
16633 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-03-29 18:44 | 2009-03-29 20:00 | 3 | 76 | 62805-1 | 228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP COD-3 WR # 29128840TRANSFORMER FUSE BROKE. L3/HFP IDC XXXX
16634 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2010-03-12 22:50 | 2010-03-13 02:37 | 1 | 227 | 65948-1 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT, ALL WORK COMPLETE / GXJ 1 CC ON TR BANK ON POLE 139-A-382 FROM START OF OUTAGE TO REST TIME. VER/PDP IDCC PN71, TOF2150, CNT2 XXXX
16635 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-06-11 09:23 | 2018-06-11 13:10 | 1 | 227 | 4581801 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT
16636 | Hazard | 3309302 | VICCO | JEFF | 2019-06-12 13:23 | 2019-06-12 17:10 | 1 | 227 | 4488561 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout gate calling for help need cutout lighting arr. T bracket 7200V Released by crew 077S03 power restored at 17:10
16637 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-08-20 08:43 | 2012-08-20 12:30 | 1 | 227 | 4954091 | 227 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEND BACK RELEASED BY CREW 078S08POLE 164-297 SERVICE LOOP BURNT OPEN NEED CREW BIG BUCKET FIXED LOOP AND REPLACED CUT-OUT ON POLE POWER RESTORED AT 12:30 IDCC PN281 XXXX
16638 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2021-03-07 07:13 | 2021-03-07 11:00 | 1 | 227 | 4311161 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers service burnt at weatherhead.// Only customer out. Repairs made
16639 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-05-24 14:33 | 2017-05-24 18:20 | 1 | 227 | 4850171 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE BURNT OUT OF HOT LINE CLAMP GOING TO TRANSFORMER CUTOUT.. BIG BUCKET AND 1 MAN ON THE WAY TO MAKE REPAIRS. REPAIRS MADE EVERYTHING OK 38830955D00339 VER/AWD
16640 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-04-20 11:23 | 2017-04-20 15:10 | 1 | 227 | 4660171 | 227 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED INTO ON SEC. POLE/// REPAIRED CONNECTIONS//RSTORED AT 15:10//COMPLETE/EM VER/CRB L3/HFP XXXHFP
16641 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-06-12 07:58 | 2012-06-12 11:45 | 1 | 227 | 4904811 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ONLY ONE COUSTOMER IS OUT . I CUT SERVICE TO CLEAR UP ROAD.I HAVE CONTACTED T. MILLER HE IS BRINGING A POLE. I WILL NEED THIS OUTAGE TICKET BACK . THANKS G.R. RELEASED BY CREW 074S04// VER/DBM IDC XXXX
16642 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2012-10-02 08:43 | 2012-10-02 12:30 | 1 | 227 | 4106641 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.BACK ON MTN.CHGING. VER/KEP IDC XXXX
16643 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-04-07 23:01 | 2014-04-08 02:48 | 1 | 227 | 4584191 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REMOVED ARRESTOR FROMLINE ON POLE 697D106 VER/TOM L3/TOM IDCC FP NULL XXXX
16644 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-08-25 08:52 | 2009-08-25 12:39 | 1 | 227 | 64856-1 | 227 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | BANK CONNECTIONS BURNT NEUTRAL DOWN AND CONNECTIONS -HELP COMING-TIM SMITH---WILL HAVE TO OPEN BANK FOR 1 HOUR TO FIX/VER/CRB IDC XXXX
16645 | South Williamson | 3411401 | DEWEY | INEZ | 2012-04-15 10:43 | 2012-04-15 14:30 | 1 | 227 | 4673951 | 227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CHECKING NOW .INSULINK PULLED INTO RESQUEZED BACK TO NORMAL ///VER/CRB IDC XXXX
16646 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-02-21 14:04 | 2020-02-21 17:50 | 1 | 226 | 4423131 | 226 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part out, have bad connections on house veryhigh srv, can not reach with ladder, triedd with my truck, need a big bucket at this loc Released by crew 078S06 Released by crew 078H06 // repairs made @ 1750 L3/HFP
16647 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-07-31 00:22 | 2009-07-31 02:15 | 2 | 113 | 59364-1 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401103// FOUND BAD ARRESTER ON POLE 146. CLEARED ARRESTER AND RE-FUSED 40T LINE FUSE AT 02:15. SH//COD 2// VER/DBM IDC XXXX
16648 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-03-31 09:14 | 2022-03-31 13:00 | 1 | 226 | 4700211 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout. manual. help on the way. restored 13:00
16649 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2008-12-20 10:29 | 2008-12-20 14:15 | 1 | 226 | 61187-1 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD - 1 SORRY MYLES...THIS ONE CAME IN JUST AFTER WE SPOKE..THANK----CUT OUT BROKEN----CALLED DUTY SUP. FOR EXTRA HELP RELEASED BY CREW 074H14SORRY MYLES...THIS ONE CAME IN JUST AFTER WE SPOKE..THANK----CUT OUT BROKEN----CALLED DUTY SUP. FOR EXTRA HELP =====REPLACED CUTOUT BACK TO NORMAL L3/HFP IDC XXXX
16650 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-08-17 22:00 | 2014-08-17 23:53 | 2 | 113 | H4376531 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | GOOD LUCK RELEASED BY CREW 078S08/CREW ON SITE/FETR0030/VEM/LOOP BURNT OPEN @91-C-55/NO TRUCKS/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2353/PLEASE CLOSE TICKET/THANKS/VEM DUPLICATE OUTAGE ON OTHER 2 CUSTOMER FROM 2200 TILL 2353 VER/SEF IDCC CDC88 XXXX AJB
16651 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2009-12-11 15:39 | 2009-12-11 19:25 | 1 | 226 | 54071-1 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 2206403 WR # 33048797 // BAD 25 KVA POLE 214-213 SEND TO VEM RELEASED BY CREW 078H12//COD 1// VER/DBM
16652 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-11-11 09:14 | 2008-11-11 13:00 | 1 | 226 | 63850-1 | 226 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | U.G. LINE FUSE OUT//3411902//U.G. LINE FUSE OUT, NEED TO REPLACE BAD ARRESTOR//VER/CRB IDC XXXX
16653 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-01-28 17:30 | 2010-01-28 19:23 | 2 | 113 | 60732-1 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER GOING OUT; INTERMITTANT PWR DROPS; NEED 25KVA 7200 TRANSFORMER, CUTOUT AND BRACKET; CREW IN-ROUTE; EFFECTING 2 CUSTOMERS; TRUCK ACCESSABLE; RELEASE TO CREW RELEASED BY CREW 078S12 / CHANGING XFR AND REPLACING ALL LOOPS ON OPEN WIRE COD-2 VER/KEP L3/KEP IDCC TOF1309 BRIGHT DIM XXXX
16654 | Hazard | 3310502 | HADDIX | CANOE | 2021-03-19 16:52 | 2021-03-19 18:45 | 2 | 113 | 4356271 | 226 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | secondary connection burnt out. made repaires
16655 | Whitesburg | 3312902 | JENKINS | JENKINS | 2018-08-06 23:49 | 2018-08-07 01:42 | 2 | 113 | 4916151 | 226 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | called customer, experiencing problems with large appliances//lights going bright/dim//customer saw arcing on nearby outdoor light pole // bad splice between xfmr lead and service. I replaced it//cod 1
16656 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-05-13 20:57 | 2010-05-14 00:43 | 1 | 226 | 61771-1 | 226 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 35116036 // FOUND LEG BAD IN 4/0 UNDERGROUND, IT IS THE HOT LEG CLOSE TO THE DRIVE WAY IN THE METERBASE,HAVE CONTACTED MR. MULLINS, IS GOING TO BRING THE POWER TEMP TO RESTORE POWER TO THIS HOUSE, IT IS THE FIRST HOUSE UP WOOD DR, ON THE RIGHT, HAS 400W FLOOD SHINING IN BACK YARD, RELEASED BY CREW 078S06/CREW ON SITE/FETR0200/VEM/POWER TEMP INSTALLED/PLEASE E-MAIL TICKET TO L.RAYBURN TO SCHEDULE UG REPAIR/THANKS/VEM - SENT TO RAYBURN IDC XXXX
16657 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-07-17 08:49 | 2014-07-17 12:35 | 1 | 226 | 4256051 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 114-184 BAD CONN. ON SEC. POLE ON HILL SIDE NEED CREW.CUST HAS MAIN BRK OFF.TALK TO CUST WHEN CREW HAS COMPLTED THEIR WORKPOLE 114-184 BAD CONN. ON SEC. POLE ON HILL SIDE-- NEED CREW RELEASED BY CREW 078S08---OPENED 114-149@ 11:45 - CLOSED @ 12:35 REPLACED CUTOUT ON POLE 114-10 RELEASED BY CREW 078H01 VER/CRB AJB
16658 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-02-13 20:24 | 2011-02-14 00:10 | 1 | 226 | 56613-1 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR 19.9 // NOTIFIED BETTINAZZI FOR 1 MAN, BIG BUCKET & TR //BAD 15 KVA XFMR 19.9... REPLACED XFMR RESTORED POWER AT 00:10 //VER/GAH IDC XXXX
16659 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-02-18 15:22 | 2013-02-18 17:15 | 2 | 113 | 4827631 | 226 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE////// REMADE CONNECTIONS ON XFMR POLE POWER RESTORED.//COD 2// VER/DBM IDC XXXX
16660 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2013-04-11 08:27 | 2013-04-11 10:20 | 2 | 113 | 4998051 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD C/O, WILL CHANGEBAD CONNECTION AT XFMR, ALSO REPLACED BAD CUTOUT . OPENED XFMR AT 10:12 & RESTORED POWER AT 10:20. ///VER/CRB L/3 CRB IDCC TOF1012 XXXX
16661 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-05-09 05:49 | 2011-05-09 09:35 | 1 | 226 | 4020791 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR HAS BURNED INTO. I AM GOING TO REPLACE DOOR. I REPLACED DOOR. //VER/GAH IDC XXXX
16662 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-05-18 22:37 | 2022-05-19 02:23 | 1 | 226 | 4908811 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke Trans cutout at 142-137,Will be making repairs,Manual Pole..Lift Hot Tap 142-126 to isolate trouble Grounded and tagged to myself..Restored at 02:23..
16663 | Hazard | 3309302 | VICCO | JEFF | 2009-08-05 14:09 | 2009-08-05 17:55 | 1 | 226 | 63701-1 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | VER/KEP L3/KEP IDC XXXX
16664 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2017-06-27 08:19 | 2017-06-27 10:12 | 2 | 113 | 4049411 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REPLACING BAD TRANSFORMER 37830163A00066/ ISO 37830163A00066/ COD 2/ ON @ 1012/ SEND TO PEGGY WYSONG DAMAGE COMPLAINT/ VER/BOW
16665 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2022-04-04 19:44 | 2022-04-04 23:30 | 1 | 226 | 4722291 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER 37820033A00116//L/f out on pole 37820033A00054/bad 15kVa CSP on pole 37820033A00116/// Replaced xfmr and restored @23:30
16666 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-11-15 16:47 | 2015-11-15 20:33 | 1 | 226 | 4449951 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER BACK AND GOT VOICE MAIL // BROKEN 19.9 LINE FUSE ON POLE 502/191 NEED LINE CREW FLAGERS TO CHANGE OUT, THIS IS ON 2565 NOT US23 // MULLINS & MARTIN & SIMMONS &/CREW ON SITE/FETR2045/VEM VER/ARN
16667 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-01-04 08:10 | 2008-01-04 11:56 | 1 | 226 | 53591-1 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 TRANSFORMER FUSE IN BANK OF TRANSFORMERS IS BLOWN. I AM GOING TO REFUSE TRANS. TRANSFORMER IS BAD. I AM CALLING FOR SOME HELP. RELEASED BY CREW 074S01 VER/KEP IDC XXXX
16668 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-10-15 13:14 | 2017-10-15 17:00 | 1 | 226 | 4458171 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV C/O POLE 115C173 RELEASED BY CREW 078S07/ON SITE BR SERVICER REQUESTED 3 GUYS AND FLAGGERS ,POWER ON @ 17:00 PLEASE CLOSE TIC BR 38830115C00173 VER/AWD L3/HFP XXXHFP
16669 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-02-20 13:22 | 2014-02-20 15:15 | 2 | 113 | 4405651 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED PRIMARY DOWN ACROSS INTERSTATE POLE 199-94 CAN ISOLATE ON THAT POLE 2 CUSTOMERS OFF/SEND TECH TO REMOVE OR FIX RELEASED BY CREW 078S03 ROTTEN WIRE VER/SEF
16670 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2008-07-05 23:14 | 2008-07-06 03:00 | 1 | 226 | 63088-1 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000802//BAD 25KVA 7200 XFMR, TRUCK OK, BILL FRALEY IN ROUTE RELEASED BY CREW 078S05 COD-1 VER/HFP IDC XXXX
16671 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-04-09 09:47 | 2018-04-09 13:33 | 1 | 226 | 4202981 | 226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad connection on transformer
16672 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-01-16 11:23 | 2012-01-16 11:48 | 9 | 25 | 4264451 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 11:23 OPENED LINE////////ON 11:48, PRIMARY NEUTRAL BAD RESPLICED BAD CONNECTION, COMPLTED. ////VER/CRB IDC XXXX
16673 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-02-19 18:02 | 2017-02-19 21:47 | 1 | 225 | 4407991 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA 7200 XMF, PROB NEEDS TO BE UPGRADED TO A 25KVA, CREW REQUIRED TRUCK OK RELEASED BY CREW 078S11--CREW ON SITE--CHANGING XFMR/CO/ARR---VOLT CK GOOD---0N AT 21:47---TBL TLKT COMP/// VER/DKM L3/HFP XXXHFP
16674 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-11-21 14:18 | 2018-11-21 15:33 | 3 | 75 | 4467611 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link appears to have broke on xfmr 38830828000112. Restored @ 15:33. sh L3/HFP
16675 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-10-25 11:55 | 2017-10-25 12:20 | 9 | 25 | 4497341 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING LINE FUSE TO REPLACE BROKEN CUTOUT/OFFF @ 1155 ON 1220 ISO 37830156000209/ COD 9/ VER/BOW L3/HFP XXXHFP
16676 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-02-15 15:58 | 2016-02-15 19:43 | 1 | 225 | 4697761 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR @ POLE 351-115 NEED LINE CREW TO REPLACE TRUCK OK RELEASED BY CREW 078S05---CREW ON SITE---REPLACED 15KVA---AND REPAIRED BROKEN PRIMARY NEUTRAL---VOLT CK GOOD----XFMR ON AT 19:43--TBL TKT COMP---RMV// VER/ ADH L/3 CRB
16677 | Pikeville | 3408101 | SALISBURY | PRINTER | 2010-11-30 16:30 | 2010-11-30 17:15 | 5 | 45 | 61179-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUT TREE OFF OF 1/0 SEC. FOUND BAD CONNECTIONS AT TRANSFORMER POLE 1123A48. REPLACED CONNECTIONS EVERYTHING OK. HAD TRANSFORMER OFF AT 16:30 AND BACK ON AT 17:15 COD-5 VER/HFP L3/HFP IDC XXXX
16678 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-01-09 21:08 | 2010-01-09 23:41 | 2 | 153 | 51562-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 796-B-56. REMOVED HOT TAP ON TRANSF CUTOUT AND REFUSED LINE CUTOUT ON POLE 796-B-240 AT 22:20ON SITE.REPLACED CUTOUT.LAST CUSTOMER ON AT 23:41 //VER/GAH IDC XXXX
16679 | Pikeville | 3421001 | BREAKS | CITY | 2011-03-15 15:10 | 2011-03-15 15:35 | 9 | 25 | 54530-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED, BURNING POLE 2/3 THRU.//PUT FIRE OUT//TIM HALL SENT A REQUEST TO ENGINEERING FOR A WORK ORDER TO REPLACE THE POLE.//ISO 37820243D00030//COD 9// VER/DBM IDC CHANGED TIME OFF FROM 1449 XXXX
16680 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-08-18 15:09 | 2020-08-18 18:54 | 1 | 225 | 4343641 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout has to be worked manually, rental house no one is living here at the moment, customer agreed to wait until tomorrow for repairs ops order 033165656
16681 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-01-30 08:20 | 2008-01-30 12:05 | 1 | 225 | 61937-1 | 225 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3401002//SERVE-END BURNED INTO ON HOT CONDUCTOR. I AM GOING TO SPLICE WIRE. I RESQUEEZED CONNECTIONS. 1 CUSTOMER OUT/// VER/TOM IDC XXXX
16682 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-01-14 16:15 | 2016-01-14 17:00 | 5 | 45 | 4620491 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 SEC CABLE BETWEEN 1059-50&1059-77 HAS NEUTRAL BROKE IN IT.HOMER ENROUTE TO HELP.HAVE TO LET CABLE DOWN TO REPAIR,ALSO HAVE TO OPEN XFR//////MADE REPAIRS,XFR OFF-16:15,ON 17:00 VER/CRB
16683 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-07-28 12:10 | 2012-07-28 15:55 | 1 | 225 | 4856961 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 92-4035 6T TRANS AND BAD LA REPAIRED POLE 92-4036 6T TRANS FUSE LIGHTING//POWER RESTORED-PLEASE CLOSE-PRB VER/KEP
16684 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-07-07 10:36 | 2015-07-07 11:21 | 5 | 45 | 4736881 | 225 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVE-IN PULLED OUT ON XFMR POLE// VER/ ADH
16685 | South Williamson | 3411401 | DEWEY | INEZ | 2022-07-31 16:55 | 2022-07-31 20:40 | 1 | 225 | 4644471 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 19.9 xfmr on 744-487//crew enroute//repairs made//restored at 20:40//complete//em
16686 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-06-04 16:25 | 2010-06-04 20:10 | 1 | 225 | 56711-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD XFMR CUTOUT//COD 1// VER/DBM IDC XXXX
16687 | South Williamson | 3411401 | DEWEY | INEZ | 2015-04-22 18:55 | 2015-04-22 20:10 | 3 | 75 | 4356521 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE BROKEN REFUSED DOOR AND POWER BACK ON 38830672D30222 VER/CRB
16688 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-03-28 12:02 | 2013-03-28 13:17 | 3 | 75 | 4964431 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 6T TRANSFORMER FUSE BROKE. FUSED UP EVERYTHING OK.. SEND COPY TO ENG PIKEVILLE POLE DONT LOOK GOOD AT GROUND LINE AND SETTING RIGHT ON THE EDGE OF CREEK BANK.//EMAILED TO TECH//COD 3// VER/DBM IDC XXXX
16689 | Hazard | 3303902 | LESLIE | WOOTON | 2010-05-16 14:05 | 2010-05-16 17:50 | 1 | 225 | 63262-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9KV CUTOUT//COD 1// VER/DBM IDC XXXX
16690 | Paintsville | 3409302 | KENWOOD | AUXIER | 2011-10-12 13:45 | 2011-10-12 17:30 | 1 | 225 | 4971111 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOT TAP ON POLE 153 // POLE 929-222 BURNT OFF, REPAIRING NOW // REPAIRS COMPLTED AND SERVICE RESTORED AT 17:30 // ONLY ONE CUSTOMER OUT ///VER/CRB IDC XXXX
16691 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-12-06 22:45 | 2016-12-06 23:10 | 9 | 25 | 4172581 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING LINE FUSE ON 38830185000146 TO COMPLETE REPAIRS RELATED TO 4172291. 2245-2310 VER/AWD L3/HFP XXXHFP
16692 | Pikeville | 3407103 | TOPMOST | KITE | 2015-04-15 11:55 | 2015-04-15 15:40 | 1 | 225 | 4322111 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED : 15 KVA TRANSFORMER 7.2 KV / 120/240 , TRUCK ACCESS .., ALL WORK COMPLETE / GXJ/ COD 1// VER/ ADH
16693 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-02-10 15:25 | 2010-02-10 16:40 | 3 | 75 | 55506-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE CURRENT LIMITING FUSE FAILED IT BURNED COMPLETELY UP. THE TRANSFORMER FUSE WAS NOT BLOWN. THIS IS THE SECOND ONE IN A WEEK THAT I HAVE HAD. MAYBE WE SHOULD SUSPEND INSTALLING NEW ONES UNTIL WE HAVE IDENTIFIED AND CORRECTED THE DEFECT.//VER/CRB IDC XXXX
16694 | Hazard | 3303901 | LESLIE | HYDEN | 2012-01-29 12:20 | 2012-01-29 13:35 | 3 | 75 | 4302341 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSED ROTTED//COD 3// VER/DBM IDC XXXX
16695 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2014-06-06 06:21 | 2014-06-06 07:36 | 3 | 75 | 4988831 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED, REPLACED DOOR, ALL WORK COMPLETE / GXJ VER/KEP
16696 | Paintsville | 3410602 | E.PRESTON | LANCER | 2021-06-02 13:33 | 2021-06-02 17:18 | 1 | 225 | 4659451 | 225 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | one phase of service drop is open will replace service drop. have called for manual tree crew & material handler. cut trees & replaced service drop, & cutout on xfmr
16697 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2010-05-02 14:25 | 2010-05-02 15:40 | 3 | 75 | 54036-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WR#34926145 POLE 69-8165 BAD LA AND 10T TRANS FUSE//VER/CRB IDC XXXX
16698 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-01-08 11:25 | 2018-01-08 15:10 | 1 | 225 | 4720521 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CALLED CUST//WIRE DOWN//CORRECT POLE # 38831109000018//COD 1//OPEN WIRE SECONDARY DOWN//CUST CALLED IN WRONG ACCT FOR BARN// wire pull out of sleeves open sec down got phillip hicks crew comming Released by crew 077S05..ALL POWER RESTORED @15:10 P.HICKS
16699 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-06-30 14:05 | 2014-06-30 15:20 | 3 | 75 | 4175201 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-324 BAD CUT AND LA BAD HOT TAP REPAIRED/// CCC COD 3//// CHANGE ISOLATION POLE IN HOIS VER/HFP L3/HFP
16700 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-02-14 21:55 | 2011-02-14 22:40 | 5 | 45 | 57591-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. BURNT NEUTRAL IN TWO/ OPENED TRANS. AT 2155 CLOSED AT 2240 VER/KEP IDC XXXX
16701 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-12-04 13:20 | 2008-12-04 14:05 | 5 | 45 | 54484-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP CREW OPENED LINE FUSE (5 CUST) TO REPLACE DEFECTIVE CROSS ARM. IDC XXXX
16702 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-11-20 14:10 | 2013-11-20 17:55 | 1 | 225 | 4059841 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSF LEAKING === NEED A 50 KVA TRANSF 480 V / 277 V == NEED LINE CREW AND TRANSF == RELEASED BY CREW 077S03. VER/SEF
16703 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-08-14 10:54 | 2015-08-14 14:39 | 1 | 225 | 4134571 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFR. CREW REQUIRED.NO BIG TRUCKS///// 6 WHEELER OR 4 WHEEL DRIVE PICKUP RELEASED BY CREW 078S05/CREW ON SITE/FETR1445/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1439/PLEASE CLOSE TICKET/VEM VER/CRB
16704 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-05-15 13:35 | 2012-05-15 17:20 | 1 | 225 | 4797741 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10KVA XFMR IS BAD. CREW ENROUTE TO CHANGE. CHANGED XFMR AND RESTORED @ 17:20. SH ///VER/CRB L/3 CRB IDC XXXX
16705 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-03-18 09:51 | 2012-03-18 10:36 | 5 | 45 | 4591591 | 225 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 6T TRANS FUSE MELTED OUT INSTALLED 10T 50 KVA TRANS // COD-5 ISO TF 38830069C14112 VER/HFP L3/HFP IDC XXXX
16706 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-06-20 13:15 | 2018-06-20 17:00 | 1 | 225 | 4628631 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew requiredreplaced door
16707 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-10-30 11:34 | 2015-10-30 12:49 | 3 | 75 | 4396871 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR ON POLE 38821036D00061. I WILL REPLACE THE DOOR.ON 1249 / ISO 37830024B31286/ COD 3/ VER/BOW
16708 | Hazard | 3302703 | HAZARD | HAZARD | 2008-09-23 09:05 | 2008-09-23 09:30 | 9 | 25 | 66430-1 | 225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CREW OPENED TRANSFORMER TO REPAIR CONNECTION @ TRANSFORMER RELATED TO ORDER 66405-1 IDC XXXX
16709 | Pikeville | 3407103 | TOPMOST | KITE | 2009-08-31 14:46 | 2009-08-31 18:30 | 1 | 224 | 57982-1 | 224 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | B PHASE OPEN ON POLE 185-19, WIRE BURNED LOOSE FROM TOP OF CUTOUT, H. MARTIN ENROUTE TO ASSIST ....REPAIRED, ALL WORK COMPLETE / GXJ//COD 2// VER/DBM IDC XXXX
16710 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2014-12-21 11:47 | 2014-12-21 11:55 | 28 | 8 | 4873071 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | A PHASE/DUE TO BAD CABLE SWITCHING PRIMARY RISER 1142-B2-865 OUT/CIRCUITS DO NOT TIE/APPROX ONE HOUR OUTAGE/VEM/OPENED@1147/CLOSED IN AT 20-A1-445@1155 RESTORING ALL CUST/DDC TO CREATE ABNORMAL/VEM VER/ARN AJBC TOF0934
16711 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2008-02-01 17:04 | 2008-02-01 20:48 | 1 | 224 | 64729-1 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409001// CUTOUT BROKE DOWN AND BURNED TOP OF POLE OFF.//CREW ON SITE STARTING REPAIRS TCM//COD 1// VER/DBM IDC XXXX
16712 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2019-08-07 05:36 | 2019-08-07 09:20 | 1 | 224 | 4850731 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. fuse open @1125-C1-461, checking. Bad trans. cutout here, got changed out @0920.
16713 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2021-08-16 12:28 | 2021-08-16 16:12 | 1 | 224 | 4079381 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 167 kva transformer on pole 306-195. need big line truck from hazard and flagging crew.. voltage on transformer is 277/480//OPS# 038 455 057
16714 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2010-11-07 16:28 | 2010-11-07 17:00 | 7 | 32 | 53699-1 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CENTER XFMR IN A THREE XFMR BANK IS LEAKING OIL FROM BOTTOM ON TO SIDEWALK. OIL CONTAINED - DUTY SUPERVISOR NOTIFIED. WILL HAVE TO OPEN BANK ON 954-644 WHEN CREW ARRIVES. OPENED @ 16:28. RESTORED @ 17:00. SH RELEASED BY CREW 076S02/VER/CRB IDC XXXX
16715 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2015-06-05 11:01 | 2015-06-05 14:45 | 1 | 224 | 4514721 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 KVA TRANSFORMER BAD ON 737-236. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE TO REPLACE. RELEASED BY CREW 076S02// CREW ON SITE TCM/ ISO 38830737000236/ COD 1/ VER/BOW
16716 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-12-14 14:27 | 2015-12-14 14:43 | 14 | 16 | 4531481 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING FUSE TO INSTALL SOLID BLADE TO ISO BAD CUTOUT ON 69-D3-7179/APROX 30 MINUTE OUTAGE/VEM/FETR1515/VEM/30T ON 69-7050 OPEN@1427/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1443/PLEASE CLOSE TICKET/THANKS/VEM RELATED TO 4530481 COD-14 ISO LF 38830069D37050 VER/HFP L3/HFP
16717 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2021-04-28 12:49 | 2021-04-28 13:45 | 4 | 56 | 4488871 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out door had burned in too on pole 38821086A00134.the cutout its self was bad shape so i changed it out and got customer restored at 13:45
16718 | South Williamson | 3411401 | DEWEY | INEZ | 2016-12-28 22:50 | 2016-12-29 00:42 | 2 | 112 | 4247031 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: TRANSFORMER WAS ARCING. MAY HAVE CAUGHT FIRE. BROKEN CUTOUT ON POLE 768-206 I WILL MAKE REPAIRS.REPLACED CUTOUT & CLOSED XFMR IN @ 00:42/// VER/DKM
16719 | Pikeville | 3413401 | GARRETT | GARRETT | 2011-02-24 14:14 | 2011-02-24 17:58 | 1 | 224 | 60771-1 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE BURNED AT BASE, CREW ENROUTE TO TIE POLE AND MAKE REPAIRS / GXJ RELEASED BY CREW 074S03//CREW ON SITE TO TEMP GUY POLE AND RE- SQUEEZE CONNECTIONS.POLE BURNED AT BASE, CREW ENROUTE TO TIE POLE AND MAKE REPAIRS / GXJ RELEASED BY CREW 074S03//CREW ON SITE TO TEMP GUY POLE AND RE- SQUEEZE CONNECTIONS.////CUST COMPLAINED OF APPLIANCE DAMAGE, PLS SEND TO PEGGY WYSON. // SENT EMAIL AS REQUESTED HFP VER/HFP L3/HFP IDC DCMT XXXX
16720 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-08-26 07:31 | 2014-08-26 11:15 | 1 | 224 | 4423941 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR ON 904-14. DUTY SUPERVISOR NOTIFIED - FLAGGING CREW AND LINE CREW ENROUTE. REPLACED XFMR AND RESTORED @ 11:15. SH VER/SEF
16721 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-10-12 11:06 | 2020-10-12 14:50 | 1 | 224 | 4548061 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required ,,bad 10 kva xfr ,329-145,feeding barn,,truck to pole big bucket Released by crew 078S05,repairs made all cust restored @ 1450 please close ticket thanks.bt
16722 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2016-05-10 18:18 | 2016-05-10 20:10 | 2 | 112 | 4194171 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION BURNED #4 SERVICE DOWN. REPLACED ENTIRE SERVICE WITH #2. RESTORED TWO OUTAGED CUSTOMERS AT 20:10. SH// VER/ ADH
16723 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-09-08 20:31 | 2016-09-09 00:15 | 1 | 224 | 4878671 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 38830188D00054 BAD 15KVA 7200 TRAN--CREW REQ--BTRK--DS090816 RELEASED BY CREW 078S01,SMALL SQUIREL ON XFMR REMOVED ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT//COD 1// VER/DBM
16724 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2008-12-12 03:08 | 2008-12-12 05:00 | 2 | 112 | 57299-1 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORMER FUSE BLOWN, REFUSING IT, FUSE BROKE L3/KEP IDC XXXX
16725 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-06-03 22:25 | 2015-06-04 00:17 | 2 | 112 | 4508971 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED CUTOUT BACK YARD VER/CRB
16726 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-08-27 17:35 | 2021-08-27 19:27 | 2 | 112 | 4163111 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke Trans cutout at 263-B-293,Going to Make repairs..Replaced cutout and restored at 19:27.
16727 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-05-26 14:55 | 2021-05-26 16:47 | 2 | 112 | 4626611 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans fuse open @ 262-170,We have a broke cutout,going to get it changed and restore service.Restored @ 16:47.
16728 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-04-08 17:13 | 2020-04-08 19:05 | 2 | 112 | 4578801 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm cutout broke on pole 37830164000033. Changed and energized @19:05
16729 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-05-30 05:46 | 2014-05-30 09:30 | 1 | 224 | 4952671 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED/ REPLACED CUTOUT ALSO VER/CRB
16730 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-02-25 17:11 | 2008-02-25 20:55 | 1 | 224 | 50335-1 | 224 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3008001// CALLED DRT TO HELP// THE CORRECT TRANSFORMER FOR THIS CUSTOMER IS 69-5659// BAD MIDSPAN SERVICE SPLICE// REPAIRED SERVICE TO HOUSE NEXT DOOR//HAD TO OPEN XFRMR TO REPAIR... OUTAGE WAS 3 MINUTES.. MOMENTARY//ISO// VER/DBM IDC XXXX
16731 | Hazard | 3303902 | LESLIE | WOOTON | 2012-01-15 17:00 | 2012-01-15 17:32 | 7 | 32 | 4262681 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OUTAGE FROM 1654-1732 AT LINE FUSE POLE 366-D-111 TO REPLACE INSULATOR AT POLE 366-D-118. CC 7 IDCC TOF1654 XXXX
16732 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-01-24 21:58 | 2008-01-24 22:30 | 7 | 32 | 59547-1 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3008001//CSP BREAKER OUT// E MAIL TO RAYBURN CSP TRSNSFORMER LEAKING OIL AN SECONDARY NEEDS REPLACED WITH 1/0 TWIST// ISO/FLT - 38830069D37113// COD 7// SENT TO RAYBURN AND MARTIN///VER/TOM IDC XXXX
16733 | Hazard | 3310502 | HADDIX | CANOE | 2020-04-02 11:25 | 2020-04-02 15:09 | 1 | 224 | 4555031 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | transformer cross creek , got austin strong coming to help , i belived bad connection on transformer change connections on transfomer
16734 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2014-11-03 06:16 | 2014-11-03 10:00 | 1 | 224 | 4694731 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKE. RESTORED @ 10:00. SH/ ISO 38830930B30785/ COD 1// VER/BOW
16735 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-03-04 12:59 | 2020-03-04 14:51 | 2 | 112 | 4451931 | 224 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 fuse blown on xfmr bank 833-A-268 will check and refuse// Fuse had pulled apart inside C/O door. I refused and restored power @ 14:51
16736 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2010-04-09 14:15 | 2010-04-09 17:59 | 1 | 224 | 61634-1 | 224 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT IN TRANSFORMER BANK-NEED CREW-SEND TO V MULLINS RELEASED BY CREW 078S07/NEED TO CHG 3 CUTOUT AND 3 LAS/FETR1815/VEM/REPAIRS MADE AND POWER RESTORED 1759/PLEASE CLOSE TICKET/THANKS/VEM //VER/CRB IDCC PN5599, CNT6 XXXX
16737 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-12-12 14:21 | 2009-12-12 18:05 | 1 | 224 | 64052-1 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 37830466000035, BAD 15 KVA XFMR, 7200. CREW -MATERIAL HANDLER///// CHANGED XFMR, POWER RESTORED VER/KEP L3/KEP
16738 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-09-10 11:44 | 2012-09-10 13:36 | 2 | 112 | 4035561 | 224 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE HOT IS OUT OF TRANSFORMER BUSHING, LUG BURNED INTO ON SEC SIDE OF TRANSFORMER//COD 2// VER/DBM IDC XXXX
16739 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2020-05-01 10:34 | 2020-05-01 11:30 | 4 | 56 | 4784651 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | top burnt off of cut out. repairs made. restored
16740 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-11-20 18:36 | 2009-11-20 19:08 | 7 | 32 | 59920-1 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP WORK REQ # 32783352 // CALLED DRT TO HELP CALLED DRT TO HELP-OPENED TRANSFORMER AT 18:36 TO MAKE REPAIRSCALLED DRT TO HELP-OPENED TRANSFORMER AT 18:36 TO MAKE REPAIRS--BACK ON AT 19;08 L3/HFP IDC XXXX
16741 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2021-04-04 08:31 | 2021-04-04 10:23 | 2 | 112 | 4416821 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | open wire burnt down/repairs made/pls close. tre
16742 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-04-04 20:11 | 2017-04-04 23:55 | 1 | 224 | 4614581 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW ENROUTE//BAD SPAN OF 1/0 LASH//HAVE VOLTAGE AT XFMR,NO VOLTAGRE AT SECONDARY POLE//CANT FIND BAD PLACE IN SECONDARY//CREW ENROUTE TO HELP REPLACE SECONDARY//BAD SPAN OF 1/0 LASH//HAVE VOLTAGE AT XFMR,NO VOLTAGE AT SECONDARY POLE//CANT FIND BAD PLACE IN SECONDARY//CREW ENROUTE TO HELP REPLACE SECONDARY//FOUND BAD PLACE IN CABLE//MADE REPAIRS//RESTORED AT 23:55//COMPLETE//38820818A00197 VER/AWD L3/HFP XXXHFP
16743 | Hazard | 3303901 | LESLIE | HYDEN | 2017-12-06 18:46 | 2017-12-06 22:30 | 1 | 224 | 4627271 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | steep concrete driveway/ no meter reading cutout open.bad kmate fuse..restored power at 22:30/ ISO 37830412D00288/ COD 1
16744 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-08-13 09:06 | 2013-08-13 12:50 | 1 | 224 | 4659611 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN//COD 1// VER/DBM
16745 | Pikeville | 3421001 | BREAKS | CITY | 2016-01-26 11:18 | 2016-01-26 11:50 | 7 | 32 | 4651121 | 224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 220-127..WILL MAKE REPAIRS.COMPLTED.//NO OUTAGE TILL 1100/CLOSED 1150 VER/CRB
16746 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-04-04 09:26 | 2022-04-04 13:10 | 1 | 224 | 4719381 | 224 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | made repairs to secondery connections
16747 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-06-10 13:56 | 2021-06-10 17:39 | 1 | 223 | 4706861 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 40d377/may get truck to it but cust has septic in yard will have to talk to him about where its at. crew reqd. Released by crew 078S04
16748 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-01-20 04:42 | 2008-01-20 08:25 | 1 | 223 | 57854-1 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401302////BAD 25KVA// REPLACED TRANSFORMER VER/KEP IDC XXXX
16749 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-07-25 09:47 | 2013-07-25 13:30 | 1 | 223 | 4591511 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG BAD ON THE UNDERGROUND SECONDARY CABLE. TIM HALL WILL HAVE A CREW HERE SOMETIME TODAY. RELEASED BY CREW 079S02  ONLY 1 CUSTOMER AFFECTED  WIRE REPLACED AND POWER RESTORED @ 13:30  CONTACTED PHONE COMPANY VER/CRB L/3 CRB IDC XXXX
16750 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2017-02-05 20:23 | 2017-02-06 00:06 | 1 | 223 | 4360051 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR , WILL NEED 15 KVA XFMR 7200 & CUTOUT ..RESTORED POWER AT 00:06../// VER/DKM L3/HFP XXXHFP
16751 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-03-23 07:29 | 2017-03-23 11:12 | 1 | 223 | 4578901 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON MANUEL POLE, CALLED FOR ONE MAN, POWER RESTORED/ ISO 37830131C20142/ COD 1/ VER/BOW
16752 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-02-15 16:53 | 2020-02-15 20:36 | 1 | 223 | 4408981 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15kva 7200, 1 man and material handlerbad xfmr, need two men and a material handler Released by crew 077S12 repairs made and power restored at 2036
16753 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-02-28 22:52 | 2012-02-29 02:35 | 1 | 223 | 4515861 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S04----BAD CUTOUT --- POWER RESTORED. CC = 1 IDC XXXX
16754 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-05-23 17:14 | 2015-05-23 20:57 | 1 | 223 | 4459511 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE DOWN ON POLE 286-100. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. VER/SEF
16755 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2010-01-02 22:58 | 2010-01-03 02:41 | 1 | 223 | 57999-1 | 223 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | MIDDLE CUTOUT HOT TAP LEAD BROKEN AT CUTOUT--V MULLINS TO WORK RELEASED BY CREW 078S07//CREW ON SITE/FETR0330/VEM/REPAIRS MADE AND PUMP STATION RETURNED TO NORMAL 0241/PLEASE CLOSE TICKET/THANKS/VEM VER/LDA IDC XXXX
16756 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-07-12 12:17 | 2014-07-12 16:00 | 1 | 223 | 4232081 | 223 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS TO BE SERV DROP CONNECTION GONE BAD,WILL REPAIR///////MADE NECESSARY REPAIRS,ALL OK AFTERWARDS.HAD #2 SPLITBOLTS AS CONNECTORS(NOT GOOD) VER/CRB
16757 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-12-23 19:07 | 2017-12-23 22:50 | 1 | 223 | 4670721 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuse blown on pole 144-309///patrolled and found pole top insulator broken on pole 144-310////will need one man and bucket with 19.9 pole top insulator..restored
16758 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-09-07 10:56 | 2012-09-07 14:39 | 1 | 223 | 4026591 | 223 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | 3800 POND CREEK POLE#1086-289 PER CHRIS DESKINS (3605) PART OUT.//.BAD INSULINK CONNECTOR ON 1 HOT LEG OF SERVICE ENTRANCE..REPLACED BOTH CONNECTORS WITH BETTER CONNECTORS.ONLY ONE CUST AFFECTED..JRV.09/07/12 ///VER/CRB L/3 CRB IDC XXXX
16759 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-06-06 09:17 | 2008-06-06 13:00 | 1 | 223 | 58958-1 | 223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3408402//WILL CHECK SERV FOR PROBLEMSXFR IS BAD,LOW VOLTAGE ON 1 LEG.CREW WILL CHANGE IT OUT SHORTLY RELEASED BY CREW 074S06 S D RAY AND CREW ONSIGHT CHANGING OUT 25KVA.CHECKED VOLT. 122/244 VER/HFP
16760 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-04-25 11:36 | 2018-04-25 15:19 | 1 | 223 | 4277521 | 223 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | crew on site/cut out door burnt up/576-131/FETR 1515/vem/repairs made and full power restored 1519/please close ticket/thanks/vem/ ISO 38830576D00131/ COD1
16761 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-02-09 10:51 | 2021-02-09 14:33 | 1 | 222 | 4951481 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT.//////////REPLACED BROKEN CUTOUT&RESTORED.ALL OK AFTERWARDS
16762 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2019-05-29 20:54 | 2019-05-30 00:36 | 1 | 222 | 4381321 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke into , I changed it out
16763 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2017-08-23 12:58 | 2017-08-23 16:40 | 1 | 222 | 4293231 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER X-1 BUSHING CLAMP BROKE ON POLE37830225D00182 THAT ONLY SERVES SPECTRUM TV SERVICE ,MADE REPAIRES, ONLY 1 CUSTOMER/ ISO 37830225D00182/ COD 1/ VER/BOW
16764 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-03-06 21:56 | 2008-03-06 23:10 | 3 | 74 | 54438-1 | 222 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED OPEN ON LASH CABLE RE PAIRED COMP VER/LDA IDC XXXX
16765 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2019-03-06 13:02 | 2019-03-06 14:16 | 3 | 74 | 4956541 | 222 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | connection beyween the service and the service entrance cable was bad I replaced it L3/HFP
16766 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-02-01 08:21 | 2008-02-01 09:35 | 3 | 74 | 63368-1 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001102// CUTOUT FELL APART 66-160 RELEASED BY CREW 078S08 VER/ARN IDCC CNT1 XXXX
16767 | South Williamson | 3411401 | DEWEY | INEZ | 2021-10-12 08:01 | 2021-10-12 09:15 | 3 | 74 | 4341941 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//replaced cutout//restored at 9:15//complete//em
16768 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-05-22 07:01 | 2014-05-22 08:15 | 3 | 74 | 4736951 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DEAD TREE FELL AND HIT PRI. CONDUCTOR AND SHOOK HOT TAP OFF OF STIRUP.I AM GOING TO REPLACE HOT TAP. I REPLACED HOT TAP.//COD 3// VER/DBM
16769 | Whitesburg | 3309302 | VICCO | JEFF | 2022-10-02 14:59 | 2022-10-02 16:13 | 3 | 74 | 4966541 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Lf was opened. Didnt find anything power restored at 16:13.
16770 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-12-09 13:01 | 2012-12-09 14:15 | 3 | 74 | 4454081 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHANGING.HAD LINE FUSE OFF FRON 14.00 UNTIL 14.15 (SEEH4454081)//COD 3// VER/DBM IDC XXXX
16771 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-02-10 12:16 | 2011-02-10 13:30 | 3 | 74 | 55906-1 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I REPLACED A FAILED CUTOUT.//COD 3// VER/DBM IDC XXXX
16772 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-08-05 18:46 | 2015-08-05 20:00 | 3 | 74 | 4982691 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE37830170000103 , REPLACED CUTOUT , CLOSED XFMR FUSE @ 20:00 . VER/CRB
16773 | Hazard | 3311103 | STINNETT | WENDOVER | 2011-09-21 14:18 | 2011-09-21 18:00 | 1 | 222 | 4893491 | 222 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER CHECKING CONNECTIONS /// OPENED TR @ 1750 TO MAKE REPAIRSPART POWER CHECKING CONNECTIONS/// CHANGED CONNECTIONS, POWER RESTORED COD-4 ISO TF 37830412B00344 SEE DUP H4893491 VER/HFP L3/HFP IDC XXXX
16774 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-08-25 19:48 | 2016-08-25 23:30 | 1 | 222 | 4836601 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER 1955--C/O BROKE--REPLACED--ALLGOOD--DS082516--NOTE HOUSE BEING RENOVATED --VACANT???--ONLY CUST ON TRAN:-)O VER/KEP
16775 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-11-25 22:13 | 2013-11-26 01:55 | 1 | 222 | 4074001 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG LEG ON A 1/0 HOT NLEGS AND #2 COPPER NEUTRAL. ISOLATED BAD LEG IN UG PED. THE ONE ON THE LEFT SIDE OF METER BASE IS BAD. NEED POWER TEMP. AND LINE CREW. RELEASED BY CREW 078S01 VER/KEP IDC XXXX
16776 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-01-16 19:21 | 2014-01-16 23:03 | 1 | 222 | 4288021 | 222 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NEED PRC CREW TO INSTALL POWER TEMP-BAD UG RELEASED BY CREW 078S07///INSTALLED POWER TEMP///VOLTAGE CK GOOD////FORWARD TO B REYNOLDS TO HAVE REPAIRS MADE TO UG CABLE VER/CRB L3/HFP
16777 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-12-27 14:37 | 2022-12-27 18:19 | 1 | 222 | 4367611 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 25KVA TRANSFORMER ON POLE 410-A-55 /// NEED LINE CREW BIG BUCKET Released by crew 077H12.comp
16778 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-01-23 06:54 | 2022-01-23 08:45 | 2 | 111 | 4397661 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv door. relaced door restored power.1076 Sugar Camp Road, Greenup, KY, 41144/ Customer states power was out for 8 minutes then came back on and he said he heard buzzing and saw arcing coming from the lines
16779 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-09-01 17:13 | 2018-09-01 20:55 | 1 | 222 | 4031881 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We will need big bucket to change bad cutout
16780 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-07-23 09:49 | 2021-07-23 13:31 | 1 | 222 | 4948971 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp burnt out. replaced clamp, power restored
16781 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-09-05 12:31 | 2011-09-05 13:45 | 3 | 74 | 4818261 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, HAVE CHANGED AND POWER IS RESTORED AT THIS LOC COD-3 ISO TF 39830902C00402 VER/HFP L3/HFP IDC XXXX
16782 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-01-09 10:14 | 2017-01-09 11:28 | 3 | 74 | 4280301 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE, IN PROCESS OF REPLACING CUTOUT, REPLACED BAD CUTOUT APR AT 1128 CLOSE TICKET/ ISO 38830502000185/ COD 3 L3/HFP
16783 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2017-07-31 10:03 | 2017-07-31 11:54 | 2 | 111 | 4209801 | 222 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRSNSF SECONDARY SIDE === NREPAIRED POWER OK VER/AWD
16784 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2013-05-16 17:46 | 2013-05-16 19:00 | 3 | 74 | 4123311 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT PL#39831123C14024///CHANGING CUTOUT AND ARRESTOR///REPLACED CO&LA///VOLT OK///BACK ON 19:00HRS//COD 3// VER/DBM
16785 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-11-16 11:38 | 2011-11-16 15:20 | 1 | 222 | 4082151 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD GOING INTO TRANSFORMER ON A HOT LEG WAS JUST ABOUT BURNED INTO. I REPLACED LEAD WIRE. CUSTOMER SAID EVERYTHING IS OK NOW. SEND TO ENG. DEPT. WE HAVE TRANSFERED OUR EQUIP UP ON 2 NEW POLES. TV AND PHONE CO. HAVE ALSO TRANSFERED THERE WIRES. THE 2 STUB POLES ARE LEFT BESIDE NEW POLES AND CUSTOMER WANTS THEM REMOVED. POLES 286-98 AND 286-67. VER/HFP L3/HFP IDC XXXX
16786 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-02-12 13:55 | 2012-02-12 15:46 | 2 | 111 | 4342581 | 222 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | XFR FUSE OUT,WILL RE-FUSE//////SURGE ARRESTOR ON ONE XFR HAD FAILED,REMD IT FRM CIRCUIT,CLOSED XFR AND RESTORED TO NORMAL///VER/CRB IDC XXXX
16787 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-03-18 13:59 | 2013-03-18 15:50 | 2 | 111 | 4916251 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND 19900 CUTOUT BROKEN ON POLE 241-139..CONTACTED SUPERVISOR FOR SOMEONE TO BRING ME A CUTOUT..D LEWIS 16:09..REPAIRS MADE AND POWER RESTORED..17:48..D LEWIS COD-2 ISO TF 37820241C00139 VER/HFP L3/HFP IDC XXXX
16788 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2014-06-29 13:08 | 2014-06-29 16:50 | 1 | 222 | 4167741 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD REPLACED CUTOUT &ARR. SPLICED 4?3 SEC IN TREE POWER RESTORED 16:50//COD 1// VER/DBM
16789 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-05-09 10:18 | 2008-05-09 14:00 | 1 | 222 | 59047-1 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NEW CREW 25KVA NO TRUCKS TALK TO P TOLLIVER 19.9 RELEASED BY CREW 078H04//3008701///REPLACED CURRENT LIMITING FUSE VOLTAGE O;KAY 124\248 COMPLETE P R TOLLVIER//VER/CRB IDC XXXX
16790 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-07-14 14:43 | 2021-07-14 18:25 | 1 | 222 | 4912201 | 222 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on sec pole. Reworked all sec connections. Restored @ 18:25. One customer affected. sh
16791 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-07-15 13:08 | 2021-07-15 16:50 | 1 | 222 | 4916411 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | repair undergound service
16792 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2010-06-01 18:16 | 2010-06-01 20:07 | 2 | 111 | 55075-1 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEND TO RANDALL MARCUM,HE WILL CHECK THIS IN THE MORNING.POLE TOP IS BURNED OFF,TOOK LINE FUSE OUT THAT SERVES THIS POLE //SERVICER CONTACTED CUSTOMER AND THEY SAID THESE ACCOUNTS WERE NOT BEING USED, WOULD BE OK TO FIX THIS IN THE MORNING//SERVICER CREATED OPS ORDER 039520448 //COD 2// VER/DBM IDC XXXX
16793 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-07-21 20:29 | 2011-07-21 22:20 | 2 | 111 | 4576361 | 222 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON POLE 241-98 COD- 2 ISO SO 37820241C00098 VER/HFP L3/HFP
16794 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2018-04-24 12:07 | 2018-04-24 13:21 | 3 | 74 | 4270811 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | called cust--they are turning off main breaker and ok to disp in morn/crew required send to mullins/4/0 alum underground Released by crew 078S03/crew on site/vem/opened xfmr 1207/repairs made and power restored to all cust 1321/please close ticket/thanks/vem//NO OUTAGE TILL TRANSFORMER OPENED L3/HFP
16795 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-03-10 16:48 | 2016-03-10 20:30 | 1 | 222 | 4835411 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP XFORMER 7200. EED LINE CREW AND CUTOUT BRACKETT AND ARRESTER MAY GET TRUCKS TO POLE. RELEASED BY CREW 078S01.. CREW ON SITE ETR 2100..XFMR CHANGED BACK ON AT 2030.. COMPLETE CY VER/KEP
16796 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-11-08 21:08 | 2010-11-09 00:50 | 1 | 222 | 54137-1 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 37678802 //,,,BAD 37.5KVA 7200 XFMR, CREW REQUIRED, B FRALEY NOTIFIED. RELEASED BY CREW 078S05 // COD-1 //VER/GAH IDC XXXX
16797 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-01-14 17:45 | 2010-01-14 19:36 | 2 | 111 | 54265-1 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FIRE ON POLE, BAD 6 INCH DISK. NEED TO RELACE. CAN USE TRUCK. TOOK HOTTAP OFF LINE ON POLE 38830984000104. OPEN TWO TRANSFORMERS AT 17:45...DAH RELEASED BY CREW 074S08//ISO//COD 2// VER/DBM IDCC TOF1559 XXXX
16798 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-10-26 07:04 | 2012-10-26 10:46 | 1 | 222 | 4173091 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CONNECTION ON 500 MCM COPPER HAVE CONTACTED TIM MILLER & GAVE A LIST OF MATERIAL.HAVE INFORMED COUST. TO LEAVE LOAD OFF TILL REPAIRS ARE MADE. REPLACED XFMR RISERS & CONNECTIONS//COD 1// VER/DBM IDC XXXX
16799 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-02-22 20:39 | 2017-02-22 22:30 | 2 | 111 | 4415191 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN . REPLACED FUSE LINK, ALL WORK COMPLETE / GXJ VER/CRB L3/HFP XXXHFP
16800 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-05-30 21:16 | 2020-05-30 22:30 | 3 | 74 | 4935071 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse broken, replacing..//cod 3
16801 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2018-07-08 13:29 | 2018-07-08 15:20 | 2 | 111 | 4751171 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout , We changed it out
16802 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-07-07 09:24 | 2022-07-07 11:15 | 2 | 111 | 4417631 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing
16803 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-12-26 13:39 | 2018-12-26 15:30 | 2 | 111 | 4599531 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout changing L3/HFP
16804 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2017-10-08 06:09 | 2017-10-08 08:00 | 2 | 111 | 4419181 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER, THEIR METER IS NOT LIT UP// REPLACED XFMR CUTOUT, ALL WORK COMPLETE / GXJ VER/ARN L3/HFP XXXHFP
16805 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-10-15 10:21 | 2012-10-15 11:35 | 3 | 74 | 4142161 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-6102 BAD WESTINGHOUSE CUTOUT AND LA CHGED ////VER/CRB L/3 CRB IDC XXXX
16806 | Hazard | 3303902 | LESLIE | WOOTON | 2016-04-28 18:58 | 2016-04-28 20:12 | 3 | 74 | 4139791 | 222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4139661***/ BAD TRANSFORMER CUTOUT 37830462000109/ ISO 37830462000109/ COD 3/ CLOSE AT 20:12,REPLACE CUTOUT,/ VER/BOW
16807 | Paintsville | 3410602 | E.PRESTON | LANCER | 2019-02-20 07:19 | 2019-02-20 11:00 | 1 | 221 | 4810881 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | have called for big bucket & line crew to chg. cut outs & arrestors
16808 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-07-11 09:44 | 2020-07-11 13:25 | 1 | 221 | 4151051 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Center xfmr cutout failed. Replacing all three old type cutouts. Replaced three cutouts and two arresters on bank pole. Restored @ 13:25. sh
16809 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-01-22 18:36 | 2021-01-22 22:17 | 1 | 221 | 4885901 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a broke Neutral in Customers service drop,Customer had already Knocked main Breaker,Pulled Meter to make repairs..Restored service at 22:17.
16810 | Pikeville | 3413401 | GARRETT | GARRETT | 2019-06-22 17:29 | 2019-06-22 20:05 | 2 | 156 | 4569001 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t transformer fuse out and cutout broken abd hanging down the pole 89-52. will neet 8 foot cross arm cutout crew on the way//OPENED 3-300 AMP SB ON POLE 37830089000188 THIS OUTED 1 MORE CUST//OPENED opened switches on pole 89-188 at 19:00. closed switches back in at 20:05 everything ok Released by crew 074S11
16811 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-05-19 11:04 | 2015-05-19 14:45 | 1 | 221 | 4445231 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. REPLACED AND RESTORED @ 14:45 COD-1 ISO TF 3883090200030 VER/HFP L3/HFP
16812 | Hazard | 3303902 | LESLIE | WOOTON | 2014-01-23 06:54 | 2014-01-23 10:35 | 1 | 221 | 4302771 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED BAD 15KVA WITH 25 KVA 19.9 120/240 COD-1 ISO TF 37830389C00423 VER/HFP L3/HFP
16813 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-06-02 05:34 | 2021-06-02 09:15 | 1 | 221 | 4657221 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines.Trans fuse open 167-D-123,going to refuse and restore service..Trans fuse open 167-D-123,Fuse had broke into Replaced fuse and Restored @ 09:15.
16814 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-07-20 16:13 | 2010-07-20 19:54 | 1 | 221 | 54102-1 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER BAD - TRUCK ACCESSABLE-SEND TO JEFF COMBS RELEASED BY CREW 077S10 REPLACED TRANSFORMER AND ADDED AN GROUND GRID JKC//VER/CRB IDC XXXX
16815 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-01-20 14:44 | 2018-01-20 18:25 | 1 | 221 | 4759481 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | lid blew of xfmr on pole 698-162//need 25 kva 19.9 xfmr//1 man and big bucket///need xfmr bag to put old one in//repairs made//restored at 18:25//complete//em
16816 | Pikeville | 3421001 | BREAKS | CITY | 2008-12-04 19:34 | 2008-12-04 23:15 | 1 | 221 | 54566-1 | 221 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400901// REPLACED SERVICE DROP// VER/DBM L3/KEP L3/KEP IDC XXXX
16817 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2009-02-05 10:23 | 2009-02-05 14:04 | 1 | 221 | 55877-1 | 221 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE VER/KEP L3/KEP
16818 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2018-07-17 10:45 | 2018-07-17 14:26 | 1 | 221 | 4787021 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open on pole 1147-282, Dead end pole 1147-530 Burnt off. Should be able to lower everything. But bring bigger pole top extension just in case. Crew required, Trucks okay. Released by crew 078H04. Repairs made, closed line fuse on 1147-482 at 14:26. Ticket complete L3/HFP
16819 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-03-12 18:51 | 2022-03-12 22:32 | 1 | 221 | 4616571 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open at 73-B-4,Broke cutout has caused top of pole to Burn off at 73-B-683,Going to lower everything and restore service..Restored at 22:32.
16820 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-03-16 06:49 | 2018-03-16 10:30 | 1 | 221 | 4019071 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 secondary has burnt down, will need 100 of wire and man to help, power restored
16821 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2011-02-08 12:55 | 2011-02-08 16:36 | 1 | 221 | 55311-1 | 221 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 38737858 // NEED POWER TEMP INSTALLED RELEASED BY CREW 078S07 // ENTERED AED...HFPSTS WR # 38737858 // NEED POWER TEMP INSTALLED RELEASED BY CREW 078S07----POWER ON -- 16:36//VER/CRB IDC DCMT XXXX
16822 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-05-23 14:19 | 2012-05-23 18:00 | 1 | 221 | 4823621 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CREW ON-SITE TO LOCATE AND REPAIR FAULT IN UG SERVICE. RELEASED BY CREW 076S02//CREW ON SITE INSTALLING AUTO TRANSFORMER TILL WE GET LOCATE DONE FOR FAULTED CABLE TCM// ONLY ONE CUSTOMER AFFECTED PART POWER , PLEASE SEND A COPY TO CLIFF FREEMAN , SO TECH CAN COME AND LOCATE FAULT ON UG SEC,TCM// VER/KEP IDC XXXX
16823 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-05-13 21:39 | 2013-05-14 01:20 | 1 | 221 | 4111361 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | I THINK TRANS. FUSE MAY BE BLOWN. I AM GOING UP AND CHECK IT AND REFUSE IT IF IT IS BLOWN. BAD 15 KVA TRANSFORMER. I HAVE CALLED FOR HELP. WE CHANGED TRANS. TO A 25 KVA. VER ARN IDC XXXX
16824 | Hazard | 3303901 | LESLIE | HYDEN | 2009-02-09 16:19 | 2009-02-09 20:00 | 1 | 221 | 57205-1 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP OUTAGE TO MAKE REPAIRS CONTAINED IN ORDER 57194-1 WHEN LINE FUSE WAS OPENED. L3/HFP
16825 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-08-01 16:04 | 2008-08-01 19:45 | 1 | 221 | 63513-1 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSF BAD CALLED RANDELL MARCUM 17:33 RELEASED BY CREW 079S01//3202201 VER/ARN IDC XXXX
16826 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-03-25 06:07 | 2014-03-25 09:48 | 1 | 221 | 4523311 | 221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA, REPLACED TRANSFORMER, POWER RESTORED. VER/CRB
16827 | Whitesburg | 3409503 | BURDINE | JENKINS | 2010-12-14 20:10 | 2010-12-14 23:50 | 1 | 220 | 50292-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE INTO , ONE MAN AND A BIG BUCKET IS COMMING TO ME VER/ARN IDC XXXX
16828 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-03-15 16:25 | 2012-03-15 18:15 | 2 | 110 | 4585071 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 075H01 REPLACED TRANSFORMER VER/KEP IDC XXXX
16829 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-02-20 00:20 | 2010-02-20 01:04 | 5 | 44 | H59263-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 33949353 //, ON SITE, SECONDARIES DOWN, CALLED R MARCUM FOR HELP, XFORMER OFF AT 0020, BACK ON AT 0104 VER/JHM IDCC DUP TO OPEN TRANSF XXXX
16830 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-06-12 07:02 | 2010-06-12 10:42 | 1 | 220 | 60558-1 | 220 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008701/// POLE 115-456 BAD 25KVA 19.9 TRANS 120/208 USE LEFT BUSHING RELEASED BY CREW 078S08//COD 1// VER/DBM
16831 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-10-14 22:26 | 2011-10-14 23:10 | 5 | 44 | 4983921 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-7140 BAD CUTOUT 30T LINE FUSE COD-5 ISO LF 38830069D37140 VER/HFP L3/HFP IDC XXXX
16832 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2017-12-04 10:30 | 2017-12-04 12:20 | 2 | 110 | 4619131 | 220 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | burnt riser on bank feeding holiday inn. crew to replace/repair xfmer 0ff @ 10:30, on @ 12:20
16833 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-04-30 17:00 | 2014-04-30 20:40 | 1 | 220 | 4652391 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON 420-164 OPEN LOOP ON POLE 420-163 NEED 2 MEN OPEN LOOP AT 17:00 CLOSED AT 20:40 VER/CRB
16834 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-05-16 17:25 | 2016-05-16 21:05 | 1 | 220 | 4223691 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR OUT ON POLE 155A-296 , FUSE WAS BROKE . CLOSED XFMR BACK @ 21:05/ ISO 37830155A10296/ COD 1/ VER/BOW
16835 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-09-27 17:28 | 2019-09-27 17:50 | 10 | 22 | 4065661 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke, transformer back in at 17:50 L3/HFP
16836 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-06-11 12:05 | 2010-06-11 15:45 | 1 | 220 | 60068-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE. WILL REPLACE MONDAY MORNING. NO ONE LIVING HERE. RELEASED BY CREW 079H02 //DID NOT WAIT, REPLACED 15:45 6/11/10 //COD 1// VER/DBM
16837 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-04-03 22:15 | 2008-04-04 00:05 | 2 | 110 | 63642-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202201// CUTOUT BAD ON POLE 697-D-104 @ 2339 OPENED LF ON POLE 697-57 TO C/O CUTOUT.CC 5 TOTAL VER/PDP IDCC CNT5, TOF2339 XXXX
16838 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-09-09 14:58 | 2021-09-09 16:48 | 2 | 110 | 4227421 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans fuse open 190-D-343,cause UNKNOWN,going to try and get it back in.Trans fuse open 190-D-343,We have a broke cutout at 190-D-343,Will be making repairs..Trans fuse open 190-D-343,We have a broke cutout at 190-D-343,Will be making repairs..Restored at 16:48.
16839 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-04-04 07:46 | 2020-04-04 09:36 | 2 | 110 | 4559281 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Repaired bad transformer connection.
16840 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-12-01 07:50 | 2008-12-01 09:40 | 2 | 110 | 53412-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BROKE CUTOUT COD-2 L3/KEP IDC XXXX
16841 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-06-27 18:23 | 2010-06-27 22:03 | 1 | 220 | 58387-1 | 220 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END HAD BURNED INTO AT TRANS. POLE. I RESQUEEZED ALL CONNECTIONS.// VER/DBM
16842 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-01-26 13:40 | 2011-01-26 15:30 | 2 | 110 | 64753-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38583014 //.. BAD CUTOUT ON POLE 329-66... REPLACED CUTOUT RESTORED POWER AT 15:30 COD-2 ISO LF 37830329000066 VER/HFP L3/HFP IDC XXXX
16843 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2009-08-19 14:20 | 2009-08-19 14:30 | 22 | 10 | 51283-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3400702 SERVICER OPENED LINE FUSE TO REPAIR CUTOUT/ COD-22 ISO LF 37820147D00130 L3/HFP IDCC TOF1325 XXXX
16844 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2015-02-20 08:55 | 2015-02-20 10:45 | 2 | 110 | 4053241 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER OFF LINE, NOT TRUCK ACCESSIBLE. WILL NEED SERVICER TO TRY TO RESTORE. CREW AT SITE RESTORED AT 10:45 VER/HFP L3/HFP
16845 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-02-03 11:00 | 2014-02-03 11:55 | 4 | 55 | 4343101 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | BAD METER BASE OPENED TRANSFOMERS AT 1100 CLOSED THEM AT1155 VER/CRB
16846 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2009-03-26 10:30 | 2009-03-26 12:20 | 2 | 110 | 61699-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3010602//FOUND FUSE BLOWN ON POLE 1148-6537 A-PHASE ,PATROLED LINE FOUND NEWLY BLOWN ARRESTOR ON POLE 1148-6543 ,REPLACED 25-T LINE FUSE//ISO 39831148D26537//COD 2// VER/DBM IDC XXXX
16847 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-08-25 20:21 | 2021-08-25 22:11 | 2 | 110 | 4154551 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will be making repairs///Changed bad cutout and restored service @ 22:11//cod 2
16848 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2022-01-22 15:07 | 2022-01-22 16:57 | 2 | 110 | 4396661 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad XCO on pole 4-125, made repairs and restored
16849 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-12-13 11:51 | 2021-12-13 15:31 | 1 | 220 | 4191611 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 7200 cutout no trucks, linecrew only required Released by crew 078S11 Repairs made closed on 523-16 at 15:31. Ticket complete.KMG
16850 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-03-09 12:25 | 2009-03-09 13:20 | 4 | 55 | 56573-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP COD-4 3001003// LINE FUSE BLOWN ON POLE 38830183D00123, NO VISIBLE CAUSE, FOUND BAD ARRESTER ON POLE 183-251 IDCC FP123 XXXX
16851 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-12-18 10:50 | 2008-12-18 12:40 | 2 | 110 | 59775-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3401702// 350MCM SECONDARY RISER IS BURNED UP. RELEASED BY CREW 074S02//CREW REQUIRED//WILL HAVE OUTAGE ON THIS TRANSFORMER BANK WHEN CREWS GET HERE TO MAKE REPAIRS SAFELY//COD 2//***NOTE TO CREW: PLEASE NOTE START TIME OF OUTAGE WHEN XFMR BANK IS TAKEN OFFLINE***// VER/DBM L3/KEP IDC XXXX
16852 | South Williamson | 3411401 | DEWEY | INEZ | 2011-08-13 22:15 | 2011-08-14 00:05 | 2 | 110 | 4704411 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 766-100//BLEW LATERAL FUSE//CHANGED CUTOUT//RESTORED 00:05//COMPLETE//EM VER/KEP IDC XXXX
16853 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2017-08-16 12:00 | 2017-08-16 13:50 | 2 | 110 | 4267311 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKE FUSE LINK COD-2 ISO TF 38830272000196
16854 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-06-27 02:40 | 2008-06-27 04:30 | 2 | 110 | 55714-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT COD-2 VER/KEP IDC XXXX
16855 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-12-10 16:40 | 2009-12-10 20:20 | 1 | 220 | 66135-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE DOOR BURNT UP//REPLACED AND MADE HOT//COD 1// VER/DBM IDC XXXX
16856 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-02-08 08:16 | 2021-02-08 10:06 | 2 | 110 | 4948321 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Repaired connection on transformer. Power restored @ 10:06
16857 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-10-02 11:15 | 2009-10-02 12:10 | 4 | 55 | 64495-1 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE BURNT DOWN ON POLE IN DIFFICULT LOCATION. REPLACED SERVICE AND RE-WORKED SEC POLE. SH//VER/CRB IDCC TOF1047, CNT1 XXXX
16858 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2015-02-05 14:20 | 2015-02-05 15:15 | 4 | 55 | H4992881 | 220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON LINE FUSE 37830321B00047 (1 CUSTOMER)==== OPEN TRANSF 37830321B00047 UP TO CHANGE LINE CUTOUT AT 14:20 CLOSED AT 15:15 === REPLACED LINE CUTOUT POWER OK/ TRANSFROMER (4 CUSTOMERS)ISO 37830321B00047/ COD 5/ DUPLICATE IN HOIS/ VER/BOW // DUP OF 4992881 L3/HFP XXX
16859 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-04-01 15:47 | 2008-04-01 17:00 | 3 | 73 | 62873-1 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT VER/HFP IDCC CNT1 XXXX
16860 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-01-16 19:56 | 2009-01-16 23:35 | 1 | 219 | 56366-1 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401002// TRANSFORMER IS BAD. 19.9- 25 KVA. IS BAD ON POLE 166-198. WILLIE IS SENDING HELP. RELEASED BY CREW 074S01 // WORK REQUEST 28103785// VER/TOM L3/TOM
16861 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-03-27 06:00 | 2009-03-27 07:13 | 3 | 73 | 61999-1 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | VER/HFP COD-3 1 SPAN PRIMARY DOWN #4 COPPER, NO VISIBLE CAUSE1 SPAN PRIMARY DOWN #4 COPPER, #4 SLEEVE PULLED LOOSE FROM WIRE1 SPAN PRIMARY DOWN #4 COPPER, #4 SLEEVE PULLED LOOSE FROM WIRE, REPAIRED WIRE, ALL CUSTOMERS RESTORED L3/HFP IDC XXXX
16862 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2019-01-26 11:03 | 2019-01-26 14:42 | 1 | 219 | 4723871 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced service
16863 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2021-01-10 14:17 | 2021-01-10 15:30 | 3 | 73 | 4859851 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse link broke .refused xfmr.
16864 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2011-05-09 08:31 | 2011-05-09 12:10 | 1 | 219 | 4021061 | 219 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3 CUTOUTS HAVE FAILED-- NEED CREW--SEND TO B REYNOLDS RELEASED BY CREW 078S07..REPLACED THREE BAD CUTOUTS, ON POLE 1143-964 THE CORRECT CUSTOMER COUNT IS ONE, THAT WOULD BE THE PEOPLES BANK .BLR//VER/CRB IDCC PN502, CDC83 XXXX
16865 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2018-04-05 12:54 | 2018-04-05 16:33 | 1 | 219 | 4191331 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | SEVICER REQUIRED, TRLR HAS POWER, METER NOT LIT UP AT BROWN HOUSE, X-FMR FUSE IS IN. METER # 1902188959 Released by crew 077E10/ ISO 37830274000041/ COD 1
16866 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2018-05-19 13:32 | 2018-05-19 16:51 | 2 | 199 | 4377671 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Customer has bad leg on there underground. Need line crew, and power temp Released by crew 078H04--crew on site---Installed add-a-phase ( pwr temp)--volt ck good--forward copy to tech to have New UG installed appx. 120 4/0---tbl tkt comp---Opened xfmr at 16:31--closed at 16:51---rmv//SENT TO TECH
16867 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-03-04 13:11 | 2014-03-04 16:50 | 1 | 219 | 4451011 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL DOWN CUST SERVICE DROP LOOKS TO BE BROKEN WILL BE MAKING REPAIRS. HOT SEC RISER ON TRANSFORMER GOT TOGEATHER WITH THE PRIMARY NEUTRAL BURNT HOT CONDUCTOR INTO AND NEUTRAL DOWN REPAIRS MADE EVERYTHING OK LOOKS LIKE INSULATION HAD WORE OFF WHERE IT MADE CONTACT WITH NEUTRAL AND BURNT DOWN VER/CRB
16868 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-07-10 09:01 | 2012-07-10 12:40 | 1 | 219 | 4664021 | 219 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | I HAD TWO BAD TRANSFORMER IN 277/480 BANK FOR EXPRO, THEY ARE 50 KVA, SINGLE BUSHING, THE TWO BAD ONES ARE ON A AND C PHASE, NEED A CREW TO CHANGE THIS OUT, MIDDLE TRANSFORMER IS GOOD, HAVE BANK OPEN AND HOT TAP REMOVED, CREW REQ, CAN USE TRUCK RELEASED BY CREW 078S06//COD 1 IDC XXXX
16869 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-12-17 06:39 | 2009-12-17 10:18 | 1 | 219 | 51301-1 | 219 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONDUCTOR FROZE OUT OF SERVIN VER/HFP L3/HFP
16870 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2016-10-24 14:52 | 2016-10-24 18:31 | 1 | 219 | 4049561 | 219 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMERS LIGHTS WERE GOING DIM I FOUND TWO SECONDARY CONNECTIONS HEATING UP REPLACED CONNECTIONS VER/AWD L3/HFP XXXHFP
16871 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-11-10 18:20 | 2021-11-10 19:33 | 3 | 73 | 4075251 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRF IS OUT,WILL RE-FUSE//////////RE-FUSED&RESTORED,ALL OK AFTERWARDS////////FUSE APPEARED TO HAVE ROTTED INTO
16872 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-06-28 11:36 | 2022-06-28 15:15 | 1 | 219 | 4340031 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burnt up. repairs made
16873 | Whitesburg | 3312902 | JENKINS | JENKINS | 2015-10-15 14:37 | 2015-10-15 15:50 | 3 | 73 | 4351921 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT GATE BURNED UP ON POLE 405-296, IN THE PROCESS OF REPAIR. REPLACED CUTOUT AND RESTORED POWER AT 1550/ ISO 37830405C00296/ COD 3/ VER/BOW
16874 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-03-03 21:51 | 2017-03-04 01:30 | 1 | 219 | 4517931 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SECONDARY CONNECTIONS BURNTTOGETHER ON POLE 101-148 RESULTING IN BOTH LEGS OF CUSTOMERS SERVICE TO BE ENERGIZED ON SAME LEG OF TRANS I REPLACED CONNECTIONS CUSTOMER STATES HE HAS NO PROBLEMS NOW PLZ SEND COPY TO PEGGY WYNSONG SENT TO PEGGY/AWD 38821010000036 VER/AWD
16875 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-07-21 04:06 | 2020-07-21 07:45 | 1 | 219 | 4192631 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o have replaced all power is restored here at 0745
16876 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2021-04-27 21:05 | 2021-04-28 00:44 | 1 | 219 | 4486901 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced c/o--ds042821 // cod 1
16877 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-11-18 14:51 | 2014-11-18 18:30 | 1 | 219 | 4742721 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR , NO ONE LIVES HERE OK TO CHANGE OUT TOMORROW . POLE IS MANUEL . NEED 10KVA XFMR , CUTOUT & TBRACKET . MANUEL ROW CREW & LINE CREW . SEND TO GLEN C. TRANSFORMER WILL BE REPLACED ON OPS ORDER # 37578713 VER/HFP L3/HFP
16878 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2019-06-11 09:17 | 2019-06-11 10:30 | 3 | 73 | 4481361 | 219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing old arrestor also. repairs made. pls close. tre L3/HFP
16879 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-06-01 18:32 | 2015-06-01 22:10 | 1 | 218 | 4496291 | 218 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY RISER BURNT OUT OF XFM WILL REPLACE/// REPLACED BURNT UP RISER AND RESTORED SERVICE @ 22:10 VER/CRB
16880 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-04-28 07:06 | 2015-04-28 08:55 | 2 | 109 | 4371381 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE REPLACED POWER RESTORED AT THIS LOC AT 0855 VER/CRB
16881 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-12-28 00:11 | 2013-12-28 02:00 | 2 | 109 | 4206331 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CHANGED CUTOUT AND REFUSED //VER/GAH
16882 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2012-01-24 11:28 | 2012-01-24 15:06 | 1 | 218 | 4289371 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SECONDARY POLE (35-6) 1047-88 ROTTED OFF AT GROUND LINE AND PULLED 2/3 SECONDARY OFF OF XFMR POLE. NEED 35 FT POLE, SOME 2/3 TWIST, A 15 KVA XFMR AND ARRESTER. RELEASED BY CREW 076S02// REPLACED POLE AND TRANSFORMER // RESAGGED CONDUCTORS //COD 1 IDCC PN52 XXXX
16883 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-06-26 13:37 | 2016-06-26 17:15 | 1 | 218 | 4478741 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANFORMER ON POLE 38831052B00073FUSE LINK MUST HAVE BROKE RESTORED 17 :15 TOM MCCOWN VER/CRB
16884 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-08-12 14:38 | 2016-08-12 16:27 | 2 | 109 | 4767831 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S04//BAD CUT OUT,MISMAP VER/AWD
16885 | Hazard | 3303902 | LESLIE | WOOTON | 2016-07-04 14:56 | 2016-07-04 16:45 | 2 | 109 | 4522931 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1.6 FUSE BROKE --REPLACED OK--JIM/ ISO 37830318B00244/ COD 2/ VER/BOW
16886 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-06-20 15:25 | 2014-06-20 19:03 | 1 | 218 | 4124231 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 15 KVA XFORMER CUST SAID YOU CAN BRING TRUCK TO POLE , FORMAN NEEDS TO LOOK FIRST, RELEASED BY CREW 078S01/CREW ON SITE/FETR2030/VEM/XFMR REPLACED AND ALL CUST RESTORED 1903/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP
16887 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-10-05 11:57 | 2016-10-05 15:35 | 1 | 218 | 4961901 | 218 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED ON SECONDARY POLE. HAD TO GO TO PAINTSVILLE OFFICE TO GET PRESS AND CONNECTIONS FOR 500 SERVICE CONDUCTOR. RE-WORKED ALL SECONDARY CONNECTIONS AND RESTORED @ 15:35. SH VER/AWD L3/HFP XXXHFP
16888 | Pikeville | 3409502 | BURDINE | LEVISA | 2018-09-14 07:22 | 2018-09-14 11:00 | 1 | 218 | 4095001 | 218 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | found cutout broken on pri. metering..will make repairs.restored.
16889 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-12-12 15:22 | 2019-12-12 19:00 | 1 | 218 | 4148451 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on transformer at pole 552-155 open from 18:50-19:00. Couldnt get to the meter base for a loose bull dog. Everything checks good at the transformer, not sure if the customer has their breaker off but theres no lights at location. Cant reach customer but they are good to try their main breaker.
16890 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-01-23 18:46 | 2015-01-23 20:35 | 2 | 109 | 4953811 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSS ARM BRACES BROKE 37830198A00052/ DIDNT SEE ANYTHING THAT HIT LINE/ BRACE FELL INTO XFMR RISER/ CLEARED RISER MADE XFMR HOT/ WILL BE OK TONIGHT/ WILL NEED TO BE FIXED TOMORROW MORNING . WILL TAKE LINE CREW , SET OF BRACES , MAY BE ABLE TO GET BIG BUCKET TO POLE . WILL TAKE OUTAGE TO FIX . TOP OF CLEAR FORK MT. ON RT. ALL POWER BACK ON . PER RUSSEL AND HICKEY OK TO WAIT UNTIL MONDAY 1-26 VER/SEF
16891 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2009-10-10 18:21 | 2009-10-10 20:10 | 2 | 109 | 55966-1 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT DOOR BURNT UP. REPLACING CUTOUT AS I DONT HAVE CORRECT TYPE DOOR (OBSELETE CUTOUT). REPAIRS COMPLETE. SH /./ VER/TOM IDC XXXX
16892 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2019-04-16 14:33 | 2019-04-16 18:11 | 1 | 218 | 4122591 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 92A738. making repairs. fetr 18:30//cod 1// L3/HFP
16893 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-03-18 20:26 | 2008-03-18 22:15 | 2 | 109 | 58349-1 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409303// FOUND BROKE CUTOUT// COD 2// VER/TOM IDC XXXX
16894 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2022-10-16 17:42 | 2022-10-16 21:20 | 1 | 218 | 4033561 | 218 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop will need to be replaced, crew required Released by crew 078S11,repairs made cust restored @ 2120 please close ticket thanks.bt
16895 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-10-25 13:55 | 2009-10-25 15:44 | 2 | 109 | 53104-1 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CALLED DRT TO HELP--NEED WR#--ONLY 2 CUSTOMERS ON TRANSFORMER COD-2 ISO TF 38830093A00146 L3/HFP IDC MAPPING? XXXX
16896 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-10-28 18:58 | 2012-10-28 20:47 | 2 | 109 | 4179501 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DOOR IN TRANS. CUTOUT IS BURNED UP. TRANS. MAY BE BAD. I AM GOING TO PUT NEW DOOR IN CUTOUT AND TRY IT. 25 KVA-- 7200-- TRANS. IS BAD ON POLE 145-251. CUSTOMER SAID WE COULD WAIT UNTIL 1ST THING TOMORROW TO CHANGE TRANS. THIS IS TRUCK ACCESSIBLE. YOU CAN CLOSE THIS TICKETT. I WILL MAKE OPS ORDER ON OUTAGE. I TALKED TO DAVE SAMMONS AND HE SAID WE WOULD WAIT UNTIL TOMORROW. OPS#-035224112. EMAIL THIS TRB. TICKET TO D. SAMMONS. RELEASED BY CREW 074S01//ISO//COD 1//EMAILED TO CREW IDCC PN8, CNT4 XXXX
16897 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-12-15 21:56 | 2010-12-15 23:45 | 2 | 109 | 50872-1 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMIT FUSE BURNT UP WILL BE CHANGING. I HAVE MADE REPAIRS FUSED UP EVERYTHING OK.//COD 2// VER/DBM IDC XXXX
16898 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-06-16 14:43 | 2020-06-16 18:21 | 1 | 218 | 4028321 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad 10KVA 7200 xfm ////No truck/// Paul Layne is getting crew and xfm/// Changed bad xfm and installed new cutout and bracket///Restored service @ 18:21
16899 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-04-28 22:33 | 2017-04-29 02:11 | 1 | 218 | 4692961 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OPEN ON POLE 447-207, BAD ARRESTER ON POLE 447-98, OPENED RECLOSER ON POLE 446-180 AT 02:09 CLOSED IN AT 02:11.RESTORING POWER.
16900 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-06-15 13:31 | 2022-06-15 15:20 | 2 | 109 | 4125151 | 218 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | service drop burnt in 2 at splice, will have to open XFM to make repairs will keep up with times 1520
16901 | Hazard | 3309302 | VICCO | JEFF | 2013-08-14 09:22 | 2013-08-14 13:00 | 1 | 218 | 4664071 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PRIMARY SERVICE CONDUCTOR BURNED DOWN, NEED # 2 ACSR SLEEVE AND SHORT PIEC OF WIRE, REPAIRED CONDUCTOR, RESTORED POWER AT 13:00 VER/CRB L/3 CRB
16902 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-04-10 16:01 | 2015-04-10 17:50 | 2 | 109 | 4305731 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMER CUTOUT ON POLE 1125-743///NO TRUCK///CHANGING CUTOUT///REPAIRS MADE///CLOSED XFMER FUSE ON POLE 1125-743 @ 17:50///COMPLETE BR VER/CRB
16903 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2015-02-18 08:37 | 2015-02-18 12:15 | 1 | 218 | 4038221 | 218 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | REPLACED BURNED OUT CUTOUT DOOR,ALL OK AFTERWARDS//ISO//COD 1//PRIMARY METERING// VER/DBM L3/HFP XXX
16904 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2019-01-26 03:58 | 2019-01-26 05:47 | 2 | 109 | 4723471 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @24-A2-830, checking. Trans. fuse melted, refused @0547.//cod 2 L3/HFP
16905 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-10-24 03:31 | 2014-10-24 05:20 | 2 | 109 | 4657621 | 218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS FUSE IS OPEN ON P 132 CUTOUT DOOR BURNT .. ALL REPAIRS MADE VOLTAGE GOOD AT BOTH METERS PLEASE CLOSE TICKET LRM VER/KEP
16906 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2011-08-04 09:18 | 2011-08-04 12:55 | 1 | 217 | 4663051 | 217 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEC. RISER HAS BURNED OFF AT XFMR // POLE 37830048A30854// CONTACTED T. HALL FOR HELP// REPLACED SEC. LEAD/// POWER IS RESTORED CCC COD-1 ISO TF 37830048A30854 *)(*_)(*_)(*_)(*_)(*_)(*_)(*_)*( STC, LCD37830048A30765, PER PHONE CONF
16907 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-07-29 08:08 | 2012-07-29 11:45 | 1 | 217 | 4860071 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | MAY HAVE BAD XFMR,,, GOING TO ISOLATE UG,,BAD 15 KVA NEED 1 MAN BIG MAT. HANDLER (19.9) VER/KEP
16908 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-04-08 18:13 | 2020-04-08 21:50 | 1 | 217 | 4583381 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke cutout on pole 214-C-55 will make repairs,Restored service at 21:50,Need to send copy to Right Away Department Trees have almost Grown into Primary all around pole 214-C-55 at this address ASAP...
16909 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-11-12 07:29 | 2014-11-12 11:06 | 1 | 217 | 4721401 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE IS BURNT INTO IN A BUNCH OF VINES, VINES DIDNT CAUSE PROBLEM, 2/3 SERVICE BURNT INTO WHERE IT WAS SPLICED/ ISO 37830228000070/ COD 1// VER/BOW
16910 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-05-04 16:23 | 2012-05-04 20:00 | 1 | 217 | 4744861 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT//COD 1// VER/DBM IDC XXXX
16911 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-05-12 08:38 | 2011-05-12 12:15 | 1 | 217 | 4070711 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT //VER/GAH
16912 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-04-25 19:56 | 2011-04-25 23:33 | 1 | 217 | 64853-1 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39694230 //LOOKS LIKE MIGHT JUST BE AN XFR FUSE,WILL RE-FUSE/////XFR IS BAD,NEED 25 KVA 7200V,1 MAN,MAT BUCKET///REPLACED XFR,ALL OK AFTERWARDS COD-3 BASED ON CALLS ISO TF 388210117B20039 VER/HFP L3/HFP IDC XXXX
16913 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-02-03 13:36 | 2014-02-03 17:13 | 1 | 217 | 4345531 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT CLAMP BROKE VER/CRB IDC XXXX
16914 | Hazard | 3302703 | HAZARD | HAZARD | 2015-02-25 10:59 | 2015-02-25 11:30 | 7 | 31 | H4080051 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 PART OUT ORIGINALLY/ BAD CONNECTION AT SPLICE IN SERVICE. OPENED TRANSFORMER AT 10:59, REPAIRED SERVICE, CLOSED TRANSFORMER AT 11:30/ ISO 37830272B40320/ COD 8/ DUPLICATE IN HOIS/ RELATED TO 4080051/ VER/BOW
16915 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-10-03 15:25 | 2019-10-03 19:02 | 1 | 217 | 4091481 | 217 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug leg showing fed from pedestal 39831147D30788. checked voltage all good between xfmer & ped 1147d788. checked at meter base no voltage on one leg. crew reqd. need ataphase if cant restore tonight. ¦¦ R GREENE & D REDMOND///installed add a phase on at this loc.///send to tech to write job to replace UG Ser.///complete BR
16916 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-10-09 10:01 | 2008-10-09 13:38 | 1 | 217 | 54576-1 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP 3308002//SOMETYHING BAD IN SPAN TRACKING IT OUTBAD CONNECTION ON TRANNSFORMER OR MID SPAN OF SERVICE, GOT JIM MULLINS COMMING TO HELP ON THIS IDC XXXX
16917 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-11-08 11:08 | 2014-11-08 14:45 | 1 | 217 | 4713431 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP LOOP BURNT OFF @ POLE 350-42,NEED LINE CREW TO REPAIR NO TRUCK// ISO 38830350000042/ COD 1/ VER/BOW
16918 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-04-23 18:26 | 2012-04-23 18:57 | 7 | 31 | 4696081 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 371/2 CSP TRANSFORMER NEED S REPLACED,TRUCK TO POLE,ROOM FOR CUTOUT TO BE INSTALLED, SMALL OIL SPILL HAS KILLED THE GRASS,HOLD FOR MCCARTY RELEASED BY CREW 078S07// CHANGED 37.5 XFR ///VER/CRB
16919 | Pikeville | 3413401 | GARRETT | GARRETT | 2015-02-03 15:54 | 2015-02-03 16:25 | 7 | 31 | 4988611 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED AT 15:54 AND CLOSED AT 16:25, REPLACED 4/0 CU TRANSFORMER RISER . ALL WORK COMPLETE GXJ RELEASED BY CREW 074S03 VER/TOM L3/TOM
16920 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-09-10 12:21 | 2018-09-10 15:58 | 1 | 217 | 4076431 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Neutral connection burnt into/// replaced neutral and both hot leg connections/// everything ok now 124/124/248/// Send copy to Peggy Wysong
16921 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2019-05-20 12:08 | 2019-05-20 15:45 | 1 | 217 | 4305311 | 217 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | lose nuetrul connection acm/ds
16922 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2008-09-30 20:33 | 2008-10-01 00:10 | 1 | 217 | 52426-1 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3001202 BAD UNDERGROUND NEEDS LARGE TEMP. RELEASED BY CREW 078S08 CREW INSTALLED POWER TEMP POWER RESTORED AT 00:10 //// STS 26544933 IDC XXXX
16923 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2012-01-03 09:41 | 2012-01-03 13:18 | 1 | 217 | 4228121 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE LEG OUT ON SECONDARY WILL CHECK AND SEE WHAT THE PROBLEM IS.REPAIRED BAD CONNECTION AND RESTORED POWER. TIM MCCOY//ISO//COD 1// VER/DBM IDC XXXX
16924 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-10-31 17:48 | 2010-10-31 21:25 | 1 | 217 | 50500-1 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37558797....XFRMR FUSE OUT....ON HILLSIDE....ONLY 1 CUST OUT.....NO CUSTS FED FROM 2 SPANS OF SECONDARIES ANY MORE.....BROKE CUTOUT & CROSSARM BURNT OFF (DOUBLE ARMS)....WILL RUN A TEMP SERVICE TO THIS 1 CUST FROM XFRMR POLE ACROSS ROAD 1110-D-47....AND WILL MAKE ARRANGEMENTS TO HAVE CROSSARMS REMOVED, POLE TOP PIN INSTALLED, NUETRAL LOWERED, & CUTOUT REPLACED TOMORROW...//...TEMP SERVICE RUN TO CUST....JRV ....10/31/10 VER/PDP IDC CHANGED COUNT FROM 3 AND POLE NUMBER FROM 68 XXXX
16925 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-06-24 09:23 | 2011-06-24 13:00 | 1 | 217 | 4408441 | 217 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON URD CABLE, ISOLATED BAD LEG AND STOREROOM IS DELIVERING DRY XFMR FOR TEMP. 4/0 WITH 2/0 NEUTRAL. TRUCK OK IF DRY. ADD A PHASE INSTALLED, FULL POWER, NEED CREW TO REPAIR BAD URD AT LATER DATE. RESTORED AT 13:00, ONLY 1 CUSTOMER.//VER/CRB IDC XXXX
16926 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-07-05 09:21 | 2010-07-05 12:58 | 1 | 217 | 62253-1 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 75 KVA 19 .9 XFORMER ON POLE 164-199 , CONTRACTER IS CUTTING ROAD TO POLE . THIS JUST FEEDS TEMP, GO BACK 15 OR 25 KVA. NEED LINE CREW. RELEASED BY CREW 078S01//COD 2// VER/DBM IDCC PN196 XXXX AJBC CNT2
16927 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2019-10-20 21:23 | 2019-10-21 01:00 | 1 | 217 | 4174481 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 KVA CSP transformer. Can truck. Additional personnel enroute. Replaced xfmr and restored at 1:00. sh
16928 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2019-12-29 23:42 | 2019-12-30 00:13 | 7 | 31 | 4191511 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke, closed back in at00:13 power restored//cod 7 //
16929 | Hazard | 3311103 | STINNETT | WENDOVER | 2013-05-10 12:59 | 2013-05-10 16:36 | 1 | 217 | 4093741 | 217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 077S01 REPLACED TRANSFORMER AND RESTORED POWER AT 1636 COD-1 ISO TF 37830412A00428 VER/HFP L3/HFP IDC XXXX
16930 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2021-10-10 09:13 | 2021-10-10 12:50 | 1 | 217 | 4337661 | 217 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3 phase sec burnt up @ pole 39831124A20559/crew reqd bucket ok. opening bank @ pole 1124a480/cust wants called after completing work so he can get everything back to normal on his side. Released by crew 078S04 all pwr restored 12:50
16931 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2008-01-11 10:58 | 2008-01-11 14:35 | 1 | 217 | 55952-1 | 217 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | 3302701// 344-140 WE HAVE LEAD OUT OF PRIMARY METER. WILL CALL BRUCE FOR BIG BUCKET. BRUCE TO SEND BIG BUCKET AND MEN TO FIX THIS. SEND TO CALVIN WILLIAMS . RELEASED BY CREW 077S08// VER/DBM IDC XXXX
16932 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-04-23 21:33 | 2013-04-23 22:00 | 8 | 27 | 4040501 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | VOLTAGE NOT BALANCED, 129V AND 120, 250 ACROSS. ADVISED CUSTOMERS TO TURN BREAKERS OFF. THEY SAID IT HAD BEEN DOING IT FOR 2 DAYS./// NEUTRAL BUSHING ON XFMR WAS LOOSE CAUSING IRREGULAR VOLTAGE, RETIGHTENED BUSHING VOLYAGE OK. OPENED XFMR 21:33 CLOSED 22:00//COD 8//ISO 37830247D00331//MD FILED ON MISMAPPED CUSTOMERS// VER/DBM IDC CHANGED TIME OFF FROM 1912 XXXX
16933 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2011-08-23 07:45 | 2011-08-23 11:21 | 1 | 216 | 4746441 | 216 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP NEUTRAL BURNED OPEN AT TRANSFORMER DUE TO FAILED CONNECTION ( SERV-IN ) ON 120V LEG . REPLACED 4/3 SD WITH 2/3 . ALL WORK COMPLETE / GXJ //VER/CRB IDC XXXX
16934 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2013-03-28 09:10 | 2013-03-28 10:22 | 3 | 72 | 4963761 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 468-64, REPLACED CUTOUT RESTORED POWER AT 10:22//COD 3// VER/DBM IDC XXXX
16935 | Whitesburg | 3401301 | FLEMING | NEON | 2011-02-25 16:07 | 2011-02-25 17:55 | 2 | 108 | 62806-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD CUTOUT //VER/GAH IDCC CNT4 XXXX
16936 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-03-24 05:53 | 2014-03-24 07:05 | 3 | 72 | 4520821 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOOR WAS BURNT UP REPLACED DOOR APR AT 705 CLOSE TICKET VER/CRB
16937 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-09-23 14:28 | 2010-09-23 18:04 | 1 | 216 | 52856-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LID BLEW OFF 15 KVA XFMR ON POLE 746-297. TRUCK APPROACH// CREW REQUIRED//CREW ENROUTE///RESTORED AT 18:04//EM VER/CRB IDCC PN2, CNT5, MD COMPLETE XXXX
16938 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-09-06 09:15 | 2017-09-06 12:51 | 1 | 216 | 4334421 | 216 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SECONDARY CONNECTION COMPLETE VER/HFP L3/HFP
16939 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-04-15 19:03 | 2013-04-15 22:39 | 1 | 216 | 4011711 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFORMER, TRUCKS TO POLE NEXT TO ROAD.NEED LINE CREW. RELEASED BY CREW 078S01/CREW ON SITE/FETR 2315/VEM/XFMR CHANGED AND POWER RESTORED 2239/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB L/3 CRB IDC XXXX
16940 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-09-21 13:33 | 2014-09-21 14:45 | 3 | 72 | 4515991 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | I CHECKED AND REFUSED XFMR FUSE WAS BROKEN VERY OLD VER/KEP
16941 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-03-14 19:15 | 2016-03-14 19:51 | 6 | 36 | 4846981 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OPENING TRANSFORMER 38831074D00130 TO MAKE REPAIRS IN ORDER #4844491/ ISO 38831074D00130/ COD 6/ 1915-1951/ VER/BOW
16942 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-08 09:06 | 2011-01-08 10:54 | 2 | 108 | 59736-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED ... ELIMINATED CURRENT LIMITING FUSE ( NONE ON TRUCK ) AND REFUSED TRANSFORMER , ALL WORK COMPLETE / GXJ//VER/CRB IDC XXXX
16943 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-02-04 17:52 | 2013-02-04 19:40 | 2 | 108 | 4791191 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED SERVICE DUP IN HOIS FOR 3 FROM 1930 TO 1940 @ TR ISO TF 39831147C14063 SEE DUP H4791191 FOR 3 VER/HFP L3/HFP IDC XXXX
16944 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-04-06 12:27 | 2017-04-06 16:03 | 1 | 216 | 4622021 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830353000007 PRIMARY BROKE @ POLE TOP PIN FEEDING TOWRD 353-8,CREW REQUIRED, NO TRUCKS, NO TREE CREW,1 CUSTOMER OUT ,CREW WILL NEED TO OPEN LINE FUSE ON ARRIVAL TO MAKE REPAIRS RM ON SITE OPENING LINE FUSE ON POLE 376-58 TO MAKE REPAIRS OPENED FUSE ON ORDER 4622821.38830353000007 PRIMARY BROKE @ POLE TOP PIN FEEDING TOWRD 353-8,CREW REQUIRED, NO TRUCKS, NO TREE CREW,1 CUSTOMER OUT ,CREW WILL NEED TO OPEN LINE FUSE ON ARRIVAL TO MAKE REPAIRS VER/AWD L3/HFP XXXHFP
16945 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-02-11 08:54 | 2008-02-11 09:30 | 6 | 36 | 58975-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S08 ///HOT TAP BROKE OFF VER/HFP IDCC CNT1 XXXX
16946 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-11-15 16:45 | 2013-11-15 17:39 | 4 | 54 | H4041851 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 CUST OUT INITIALLY // OPENED XFMR ON POLE 1039-13 @ 16:45 (4 CUST) CLOSED BACK IN @ 17:39 SECONDARY BURNED DOWN GOING TO POLE 1039-62 . VER/HFP L3/HFP
16947 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-08-15 11:59 | 2019-08-15 15:35 | 1 | 216 | 4891361 | 216 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | crew reqd. need a power temp, looking at meter base the right leg is bad according to beast.. Released by crew 078H17///1 leg bad in UG sec. installed power temp///send copy to Tech///complete BR L3/HFP
16948 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-02-09 08:25 | 2018-02-09 12:01 | 1 | 216 | 4819801 | 216 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired secondary connection complete
16949 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-06-21 15:08 | 2021-06-21 16:20 | 3 | 72 | 4781891 | 216 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection between secondary and service had burnt open on pole 904-73. I made repairs and restored to full power @16:20
16950 | South Williamson | 3200302 | BELFRY | TOLER | 2021-12-28 08:42 | 2021-12-28 12:18 | 1 | 216 | 4231341 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 38821040A09002.transformer feeds a old garage and a DD light.garage has been disconnected but cust is paying for the light 7200 15kva..narrow dirt road.will either have to back in or back out Released by crew 079S03/// Replaced xfmr and restored @12:18
16951 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-01-25 08:09 | 2015-01-25 09:21 | 3 | 72 | H496207 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE ON FIRE PER 911 DISPATCH//CALLBACK NUMBER 606-435-6069//FD ENROUTE /STS/4 / 0 SERVICE BURNED INTO WERE SPLICE WAS, NEED 75 FEET SERVICE AND CREW OPEN TRANSFORMER 0809 AND CLOSED AT 0921//STEVE SAID ORIGINAL 1 OUT UNTIL HE OPENED//FIX IT IN HOIS// VER/ ADH
16952 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-09-07 12:44 | 2014-09-07 16:20 | 1 | 216 | 4477491 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR NEED LINE CREW TO REPLACE TRUCK OK RELEASED BY CREW 078S05/ CREW ON SITE/ REPAIRS COMP. POWER RESTORED AT 16:20/ JEH PLEASE CLOSE TICKET// VER/BOW
16953 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-01-17 10:26 | 2009-01-17 11:02 | 6 | 36 | 57324-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3409303//CHANGING BAD XFMR. OPENED AT 10:26. CLOSED AT 11:02. SH COD-6 L3/HFP
16954 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-04-12 17:12 | 2010-04-12 17:30 | 12 | 18 | 62475-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 34633275 // 10T ME FUSE LINK BROKE COD-12 VER/HFP L3/HFP IDC XXXX
16955 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2018-07-21 21:14 | 2018-07-21 21:50 | 6 | 36 | 4830991 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Had to open line fuse to change xfmr cutout on pole 37830492000036/ ISO 37830492000036/ COD 6/ 2115 to 2150 L3/HFP
16956 | Pikeville | 3402003 | KEYSER | MULLINS | 2018-01-15 03:20 | 2018-01-15 05:08 | 2 | 108 | 4747501 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | B phase l/f open @38831127B00254, patrolling. Fuse melted out, refused @0508. 8 customers
16957 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2011-04-26 14:56 | 2011-04-26 15:50 | 4 | 54 | 65611-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WIRE BROKE IN TOP OF CUTOUT === REPAIRED CUTOUT == POWER OK//COD 4// VER/DBM IDC XXXX
16958 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-01-14 23:32 | 2017-01-15 01:20 | 2 | 108 | 4299251 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SPOKE WITH CUSTOMER AND NO DISPLAY ON THEIR METER// CUT OUT BUSTED ON POLE 1129-B-337, WILL BE CHANGING. CHANGED C/O AND REFUSED @0120.//COD 2 L3/HFP
16959 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-04-27 08:49 | 2010-04-27 12:25 | 1 | 216 | 51894-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 410-31 AND BAD R/W ON OPEN SECONDARY NEEDS CUT RELEASED BY CREW 077S01 POWER RESTORED AT 1225 CREW 077H01 REPLACED CUTOUT //COD 1// VER/DBM IDC XXXX
16960 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-10-04 18:42 | 2008-10-04 20:30 | 2 | 108 | 53381-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT...CHG CUTOUT//3401102//VER/CRB IDC XXXX
16961 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-09-20 12:12 | 2009-09-20 14:00 | 2 | 108 | 55263-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP S&C CUTOUT BROKEN COD-2 ISO TF 39830925000031 L3/HFP IDC XXXX
16962 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-02-17 07:17 | 2010-02-17 10:53 | 1 | 216 | 58582-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE CUTOUT AND ARRESTER, NO TRUCK ACCESS ... REPLACED CUTOUT AND ARRESTER, ALL WORK COMPLETE / GXJ VER/KEP L3/KEP IDC XXXX
16963 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-05-13 10:24 | 2015-05-13 14:00 | 1 | 216 | 4425311 | 216 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD NEUTRAL CONNECTION AT CUSTOMERS WEATHERHEAD/// POWER RESTORED, JUST ONE CUSTOMER AFFECTED . VER/HFP L3/HFP
16964 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-08-25 10:04 | 2014-08-25 13:40 | 1 | 216 | 4421251 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 KVA 7200 XFORMER BAD ON POLE 166-252, NEED LINE CREW , TRUCKS TO POLE. LINE FUSE OPENED ON POLE 166-179.//COD 1// VER/DBM
16965 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-03-01 11:00 | 2016-03-01 11:27 | 8 | 27 | 4791281 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING CUTOUTS ON POLE 37830174A00031/ ISO 37830174A00031/ COD 8.OPEN FUSES AT 11:00 HRS, AND CLOSE THEM BACK IN AT 11:27 HRS..COMP P.HICKS/ VER/BOW
16966 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-05-30 08:11 | 2013-05-30 11:47 | 1 | 216 | 4197361 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT REPLACED BAD CUT-OUT POWER RESTORED//COD 1// VER/DBM IDC XXXX
16967 | Hazard | 3307301 | BULAN | ARY-HEINE | 2015-12-20 10:46 | 2015-12-20 11:40 | 4 | 54 | 4546691 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 177A-69 REPLACED CUTOUT , CLOSED BACK @ 11:40 VER/CRB
16968 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2019-07-17 09:11 | 2019-07-17 10:59 | 2 | 108 | 4720021 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout,,complete
16969 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-08-16 19:54 | 2018-08-16 21:42 | 2 | 108 | 4962301 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found cutout broken on pole 189-64..made repairs..customer still had power.lifted hot tap on xfm. cutout and it fell apart @ 21:30..made repairs and reattached hot tap @ 21:42..restored.
16970 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2020-04-04 10:55 | 2020-04-04 11:22 | 8 | 27 | 4559181 | 216 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TOP 12OV SEC WIRE IS DOWN,LOOKS LIKE IT MAY HAVE PULLED OUT OF A SLEEVE.NEED SMALL CREW,#4 COPPER WIRE.NO ACCESS W TRUCK Released by crew 074S06 OPENED X-FMR AT 10:55 CLOSED AT 11:22 SECONDARY LOOP GOT INTO METAL OF CLEVIS BURNING INTO
16971 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-10-15 14:19 | 2008-10-15 17:55 | 1 | 216 | 55937-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401002// TRANS. IS BAD ON POLE-284-90. CREW IS ON WAY TO HELP CHANGE IT OUT. WE CHANGED TRANSFORMER.. // VER/TOM IDC XXXX
16972 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2017-08-04 20:44 | 2017-08-05 00:20 | 1 | 216 | 4228051 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FUSE OUT ON PRI MTR, I LOOKED IT OVER, CUST HAS PRI AND NEUTRAL ABOUT 6 IN APART, ALSO LOTSA OF TREES AND VINES ON THIER SIDE, I OPEN UP SOLID BLADE ON CUST SIDE, THEN TRIED FUSE ON PRI MTR, IT DID NOT STAY IN, MAY HAVE A BAD PRI DEADEND INS, ON POLE 879-195, CREW REQ RELEASED BY CREW 078S06,FUSE IN @ 0020 CUST TO MAKE REPAIRS PLEASE CLOSE TICKET THANKS.BT VER/KEP
16973 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2009-04-01 09:55 | 2009-04-01 13:31 | 1 | 216 | 63711-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD 15 KVA GO BACK WITH 25 KVA TRUCKS OK DONNY GENTS CREW TO CHG 38830226000167 COD-1 L3/HFP IDC XXXX
16974 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-01-02 13:45 | 2016-01-02 17:21 | 1 | 216 | 4581431 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.BROKEN..851-754 FEEDING TO 851-722..2 CUTOUTS BROKEN ON 851-754..TOOK ALL 3 CUTOUTS OFF AT 16.30..IN THE PROCESS OF CHANGING 2 CUTOUTS./ ISO 38830851B00574/ COD 1/ VER/BOW
16975 | Pikeville | 3413401 | GARRETT | GARRETT | 2017-08-28 13:20 | 2017-08-28 13:47 | 8 | 27 | 4301091 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | WORK 08/28 NO CUSTOMERS OUT. X ARM IS SPLITTING OUT AT POLE 37830066B00109. SHOULD BE ABLE TO GO BACK WITH POLE TOP PIN & CLEVIS .CAN USE SIDE BY SIDE & GET WITHIN 200 FT .PLEASE SEND THIS TO STEVE RAY IN PIKEVILLE. RELEASED BY CREW 074S04..OPENED AT 13:20 CLOSED AT 13:47.. REPAIRS MADE/ ISO 37830066B00106/ COD 8/. VER/BOW L3/HFP XXXHFP
16976 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-11-01 21:19 | 2014-11-01 23:07 | 2 | 108 | 4690521 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT IS BREAKING DOWN WILL CHANGE//// CHANGED BAD CUTOUT AND RESTORED SERVICE @ 23:07//// ONLY 1 CUSTOMER AFFECTED (TIME MODIFIED BY DST CHANGE)
16977 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2013-04-05 08:24 | 2013-04-05 12:00 | 1 | 216 | 4980931 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT FAILED ON 38831003D00017. ISOLATING AND PUTTING FIRE OUT. FIRE IS OUT BUT POLE IS DAMAGED. NEED BIG BUCKET, THREE MEN, CUTOUT AND EITHER POLE EXTENSION OR CROSSARM TO REINFORCE IT. MAY REQUIRE OUTAGE ON RECLOSER 1003-10. RELEASED BY CREW 076S02REPAIRS MADE POWER ON ///VER/CRB L/3 /CRB IDCC CNT9 XXXX
16978 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-05-07 14:24 | 2008-05-07 14:30 | 36 | 6 | 57752-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001401//WHEN TRYING TO RESTORE ORDER 57724-1 THE TRANSFORMER CUTOUT FAILED AND FELL APART... THIS TOOK FUSE ON POLE 454-3005//COD 36//SERVICER REPAIRED FUSE DOOR AND RESTORED BOTH OUTAGES @ 1430// VER/DBM IDC XXXX
16979 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2020-10-21 16:09 | 2020-10-21 19:45 | 1 | 216 | 4574361 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv cutout and arrester. pole 1147-4189. 3 phase on arm Released by crew 078S07
16980 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-03-07 07:44 | 2016-03-07 08:11 | 8 | 27 | H4822341 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SECONDARY BURNT DOWN - MAKING REPAIRS @ 0737 //WILL WORK DURING NORMAL SHIFT.SECONDARY BURNT INTO ON POLE 444-18 SERVING POLE 444-124 DUE TO BAD SPLICE IN WIRE, OPENED XFMR AT 07:44 MADE REPAIRS , RESTORED POWER AT 08:11. VER/HFP L3/HFP AJB
16981 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-04-22 13:59 | 2011-04-22 17:35 | 1 | 216 | 62112-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT IS BROKE. DIFFICULT LOCATION. REPLACED CUTOUT, INSTALLED STIRRUP AND RE-FUSED 20T LINE FUSE ON 880-142 @ 17:35. SH//MADE A MD IDC XXXX
16982 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-09-04 17:52 | 2011-09-04 19:40 | 2 | 108 | 4809231 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT ON 1017B2-42..BURNT UP XFMR CUTOUT ON 1017B2-32..CAN REPLACE..//.REPLACED CUTOUT ON 1017B2-32..RE-FUSED LINE FUSE ON 1017B2-42..JRV..09/04/11//COD 7// VER/DBM IDCC CNT7 XXXX
16983 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-08-19 18:18 | 2018-08-19 19:30 | 3 | 72 | 4974411 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse door on c/o was burnted into, replaced door all power restored at this loc by amg at 1930 L3/HFP
16984 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-07-19 17:34 | 2015-07-19 18:10 | 6 | 36 | 4912251 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 45-5787 NEW HOT TAP FELL APART REPAIRED/ ISO 38830045C45787/ COD 6 CCC*****/ VER/BOW
16985 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-06-22 19:54 | 2010-06-22 20:48 | 4 | 54 | 55048-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUT OUT AND RESTORED POWER M.D.I. 06-22-10 IDC XXXX
16986 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-04-11 12:14 | 2008-04-11 12:50 | 6 | 36 | 66079-1 | 216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830327B00023, IT IS A LINE FUSE COD/HFP VER/HFP IDCC PN22 XXXX
16987 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-08-06 08:15 | 2015-08-06 11:50 | 1 | 215 | 4102751 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKE @ 351-65 CREW REQUIRED NO TRUCKS RELEASED BY CREW 078S05,REPAIRS MADE PLEASE CLOSE TICKET THANKS.BT// VER/ ADH
16988 | Whitesburg | 3312901 | JENKINS | KONA | 2009-08-04 17:35 | 2009-08-04 21:10 | 1 | 215 | 58588-1 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP REPLACED BAD CUTOUT L3/HFP IDC XXXX
16989 | Hazard | 3420001 | SOFT SHELL | VEST | 2011-09-06 17:55 | 2011-09-06 21:30 | 1 | 215 | 4838611 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GATE BURNED UP ON XFMR.///// CHANGED OUT POWER RESTORED //VER/CRB IDC XXXX
16990 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-05-13 14:05 | 2018-05-13 17:40 | 1 | 215 | 4344331 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | called customer multiple times no answer Arrester exploded and damaged xfmr cutout. Opened xfmr @ 17:00. Replaced bracket, cutout and arrestrer. Closed @ 17:40. sh/ ISO 38830830000023/ COD 1
16991 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2022-10-23 16:55 | 2022-10-23 20:30 | 1 | 215 | 4057261 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o--replaced-back on at20:30-allgood --ds102322
16992 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2020-01-30 09:56 | 2020-01-30 10:39 | 5 | 43 | 4348651 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replacing bad cutout, apr at 1039 close ticket. dwest
16993 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-04-22 07:18 | 2015-04-22 10:53 | 1 | 215 | 4351151 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED: CREW ENROUTE WITH MATERIAL . REPLACED 3 CUTOUTS AND ARRESTERS ON POLE 687 AND REPLACED 1 CUTOUT AND ARRESTER AND ADDED 3 - 30T FUSES TO POLE 38831074C00304 , ALL WORK COMPLETE / GXJ/ MD MADE/ADH// VER/ ADH
16994 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2022-01-20 05:54 | 2022-01-20 09:29 | 1 | 215 | 4389471 | 215 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | send to K. Griffith to change drop out. tre Released by crew 078S04 Repairs made ticket complete. Closed at 09:29
16995 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-03-12 18:05 | 2008-03-12 21:40 | 1 | 215 | 56683-1 | 215 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV END BURN OFF == REPLACED == POWER OK//3301101//VER/CRB IDC XXXX
16996 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-03-03 08:03 | 2014-03-03 11:38 | 1 | 215 | 4446271 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF 1/0 CONDUCTOR AT THE TRANSFORMER POLE. PLEASE SEND TO CLIFF FREEMAN TO HAVE POLE 38821037B00161 REPLACED, THE POLE IS ROTTEN WHERE IT IS IN A PINE THICKET. VER/SEF
16997 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-11-15 19:42 | 2010-11-15 20:25 | 5 | 43 | 55927-1 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT.....WILL RE-FUSE...//....FUSE LINK HAD JUST BROKE.....RE-FUSED....POWER ON.....JRV....11/15/10//VER/CRB IDC XXXX
16998 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-10-26 19:04 | 2013-10-26 19:47 | 5 | 43 | 4966651 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | X-FMR FUSE ON POLE 472-61 PULLED OUT - BROKE. REFUSED GATE AND RESTORED POWER AT 19:47. 10/26/2013. J.S.B. COD-5 VER/HFP L3/HFP
16999 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-04-23 09:46 | 2015-04-23 13:21 | 1 | 215 | 4358061 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BROKEN SECONDARY BUSHNING NO CREW REQUIRED// VER/ ADH
17000 | Hazard | 3303902 | LESLIE | WOOTON | 2009-06-24 08:50 | 2009-06-24 12:25 | 1 | 215 | 54145-1 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 30441004 // COD-1 ISO 3783051000179 L3/HFP IDC XXXX
17001 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-07-07 12:37 | 2014-07-07 16:12 | 1 | 215 | 4199461 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XMF FUSE, THINK XMF HAS TOOK A SHOT OF LIGHTNNING IN THE PAST BAD 25KVA 19.9 RELEASED BY CREW 078S11 WAITING ON TRANSFORMER FROM WAREHOUSE.GOING TO TAKE OLD ONE DOWN NEW TRANS# PP 14A251269 OLD #HI 1573190607 VER/CRB
17002 | Whitesburg | 3314401 | MAYKING | ERMINE | 2014-08-16 10:25 | 2014-08-16 14:00 | 1 | 215 | 4374141 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 NEED FLAGGERS BIG BUCKET 1 MAN POWER RESTORED@14:00 // COD-1 ISO TF 37830449D10528 VER/HFP L3/HFP
17003 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2017-06-03 18:32 | 2017-06-03 19:15 | 5 | 43 | 4902611 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 45-536 8T MELTED OUT SEND NOTE TO RAYBURN MIT NEED TO CHG 25KVA TO 37.5 OUT TWO TIMES SAT. 38830045A20536 SENT TO RAYBURN VER/AWD
17004 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2022-12-11 19:12 | 2022-12-11 19:55 | 5 | 43 | 4250611 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cracked cutout on pole 1108-19, will be making repairs opened 19:12 closed at 19:55
17005 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2010-12-20 04:05 | 2010-12-20 07:40 | 1 | 215 | 54429-1 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | DUE TO SPLICE THAT FAILED IN 2/3 SERVICE DROP I WILL BE CHANGING OUT DROP. SPLICE ON HOT CONDUCTOR HEATED UP AND BURNT NEUTRAL INTO. I PUT NEW 2/3 DROP IN. CUST SAID EVERYTHING GOT REAL BRIGHT AND HAD DAMAGE. 1 TV IN BED ROOM SMOKE COMING FROM ALSO DESK TOP COMPUTER. TV IN LIVING ROOM WONT WORK. 1 MICROWAVE. 1 VCR DVD PLAYER. NOT SURE ABOUT REFRIGERATOR. SHE THINKS IT MAY BE WORKING. SEND COPY OF THIS TO DAMAGE CLAIMS//EMAILED TO P WYSONG// VER/DBM IDC XXXX
17006 | Hazard | 3302704 | HAZARD | KENMONT | 2020-04-29 12:25 | 2020-04-29 16:00 | 1 | 215 | 4767901 | 215 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | pole 296-61 sec. pole, servin pulled loose part power. narrow road. 541 ashless st. Released by crew 077X05 Only one customer affected, power restored at 16:00
17007 | Cannonsburg | 3001401 | LOUISA | CITY | 2020-12-06 19:21 | 2020-12-06 22:56 | 1 | 215 | 4749661 | 215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout door was burnt up but its and older style cutout did not have corredct door. crew required Released by crew 078S11//ARRIVED RM xfm cutout replaced power on @ 22:56 please close tic RM
17008 | South Williamson | 3411401 | DEWEY | INEZ | 2008-06-03 13:26 | 2008-06-03 17:00 | 1 | 214 | 54962-1 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT BAD RELEASED BY CREW 079S01ON SITE REPLACING CUTOUT.//VER/CRB IDCC PN42 XXXX
17009 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-03-20 15:34 | 2012-03-20 17:21 | 2 | 107 | 4598811 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT TO REPLACE///////REPLACED BROKEN CUTOUT AND RESTORED//COD 2// VER/DBM IDC XXXX
17010 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2017-12-02 10:08 | 2017-12-02 11:55 | 2 | 107 | 4616411 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm fuse blown /// will refuseCutout broke/// will change and restore serviceCutout broke/// will change and restore service/// Changed bad cutout and restored service @ 11:55
17011 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-12-12 17:00 | 2017-12-12 18:47 | 2 | 107 | 4642931 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on 38820817D00018 replaced cutout restored power at 18:47
17012 | Whitesburg | 3312901 | JENKINS | KONA | 2022-10-09 10:13 | 2022-10-09 13:08 | 4 | 175 | 4008691 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | .Line fuse cutout broke on pole 404B-4. Cant reach with my truck. Need 2 men and big bucket. 7200 cutout only. 30t fuse. Opened transformer on pole 404B-4 at 12:55 close back at 13:08. Lf also restored at 13:08. Released by crew 077H15
17013 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-05-02 16:31 | 2020-05-02 20:05 | 1 | 214 | 4788291 | 214 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | one leg of underground service only has 97 volts on it. needs an auto xfmr installed or bad spot located and fixed Released by crew 078H03//DAE MADE// crew on site LRM fetr 20:15 all pwr restored @ 20:05 pleas close ticket LRM
17014 | Hazard | 3303903 | LESLIE | HALSFORK | 2021-03-17 09:33 | 2021-03-17 11:20 | 2 | 107 | 4342501 | 214 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Bad secondary connection. Opened transformer to repair connections @ 11:00 closed @ 11:20
17015 | Pikeville | 3408103 | SALISBURY | MARTIN | 2022-01-05 22:07 | 2022-01-05 23:54 | 2 | 107 | 4310131 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke on pole 38831099000014.//Replaced cutout and bracket.//Restored @ 23:54
17016 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-10-04 14:01 | 2022-10-04 17:35 | 1 | 214 | 4975821 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 15kva trucks ok/sent message to mullins for a crew/send to b morgan Released by crew 078S03/ REPAIRED AND RESTORED @1735
17017 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-12-07 05:13 | 2020-12-07 08:47 | 1 | 214 | 4750041 | 214 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | B and C phase cutout failed @ URD riser pole #37830024D31412 , will be making repairs. 1 cc Got all 3 cutouts changed and closed back in @0847.
17018 | Hazard | 3303901 | LESLIE | HYDEN | 2020-01-24 09:21 | 2020-01-24 12:55 | 1 | 214 | 4334241 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 364b-15, manuelpole no big trucks on hill, need 19.9 cutout arres t bracket, line fuse blown Released by crew 077S07 power restored at 12:55
17019 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-07-20 11:45 | 2009-07-20 13:32 | 2 | 107 | 64761-1 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN ON TRANSFORMER//COD 2// VER/DBM IDC XXXX
17020 | Whitesburg | 3401301 | FLEMING | NEON | 2019-10-21 20:03 | 2019-10-21 21:50 | 2 | 107 | 4179011 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Secondary burned pin hole on side of transformer. Need 1 man to help change out//COD 2//OFF @18:50 ON @21:50
17021 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-08-06 09:09 | 2013-08-06 12:43 | 1 | 214 | 4626631 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING OUT BAD POLE MOUNT XFMR////XFMR CHANGED OUT///VOLT CK GOOD VER/CRB L/3 CRB
17022 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-04-01 18:08 | 2014-04-01 19:55 | 2 | 107 | 4553641 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORM CUTOUT OPEN FUSE LINK BROKE REFUSE POWER RESTORED VER/ARN IDC XXXX
17023 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-12-17 12:22 | 2015-12-17 14:09 | 2 | 107 | 4539971 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DROP BURNT DOWN. SERVICER OPENED FUSES LAST NIGHT. REPAIRING NOW. REPAIRS COMPLETE, RESTORED AT 14:09 VER/HFP L3/HFP
17024 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2015-12-05 13:28 | 2015-12-05 15:15 | 2 | 107 | 4512331 | 214 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN @ XFMR REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT// VER/ ADH
17025 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2008-06-14 22:56 | 2008-06-15 02:30 | 1 | 214 | 65043-1 | 214 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 074S01 NEUTRAL WIRE IN 4/3 SERVICE DROP SHORTED OUT AT SPLICE AND BURNED NEUTRAL WIRE INTO IN MID SPAN. I AM GOING TO REPLACE S/DROP WITH A 2/3 DROP. I REPLACED S/DROP. CUSTOMER SAID HE HAD DAMAGES. A COMPUTER AND TV WOULD NOT COME ON. VER/PDP
17026 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-02-23 01:40 | 2020-02-23 03:27 | 2 | 107 | 4425221 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 span os #2 ACSR open wire burnt down between pole 191-21 and 191-22 catching fiber optics on fire/ 2cc out orginally///Opened CSP xfm @ 02:43 on pole 191-22 to de-energize ///Will make repairs/// Put wire back up and closed xfm back in @ 03:27 and restored service/// Send copy to Bill Johnson may need to write job up to set taller pole here///FIBER OPTICS CO has built new line and they are close to our facilities here/ ISO 37830191C00022/ COD 2 L3/HFP
17027 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-12-01 07:48 | 2015-12-01 11:22 | 1 | 214 | 4497931 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 318-A-128 RELEASED BY CREW 077H14 COD-1 ISO LF 37830318A00128 VER/HFP L3/HFP
17028 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-08-26 16:28 | 2009-08-26 18:15 | 2 | 107 | 51482-1 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1.6T FUSE BROKE. FUSED UP EVERYTHING OK.//COD 2// VER/DBM IDC XXXX
17029 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-05-28 08:59 | 2008-05-28 12:33 | 1 | 214 | 52065-1 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 473-188 HAS ROTTED AND FELL ON THE GROUND WILL NEED A CREW AND A 30 FT POLE I HAVE REMOVED WIRE OUT OF RD RELEASED BY CREW 074S07//3314401//VER/CRB IDC XXXX
17030 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2011-08-29 15:49 | 2011-08-29 19:23 | 1 | 214 | 4773091 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY BUSHING OVERHEATING & BURNING UP ON MIDDLE XFMR OF 167 KVA..277/480 BANK.NO FUSE BLOWN.WILL OPEN.CALLED CREW.THEY ARE ROUNDING UP XFMR TO REPLACE.OPENED LINE FUSES ON 893A235 @ 16:50..PLEASE SEND TO J REED..// RELEASED BY CREW 080S01. RESTORED AT 19:23. VER/KEP IDC XXXX
17031 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-01-02 12:30 | 2008-01-02 14:17 | 2 | 107 | 52739-1 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3410502/ FUSE BROKE IDCC CNT1 XXXX
17032 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-08-14 16:46 | 2009-08-14 20:20 | 1 | 214 | 58406-1 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK REQUEST # 31244464 //BAD 15KVA CREW REQUIRED TRUCKS OK/SEND TO REYNOLDS RELEASED BY CREW 078S03 VER/KEP L3/KEP IDC XXXX
17033 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-07-03 16:16 | 2013-07-03 19:50 | 1 | 214 | 4456181 | 214 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN NEUTRAL AND HOT LEG IN SERVICE DROP..LET SERVICE DOWN TO MAKE REPAIRS.CUSTOMER HAS APPARENT DAMAGE TO REFRIGERATOR AND POSSIBLY MORE. VER/KEP
17034 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-08-03 15:53 | 2012-08-03 17:40 | 2 | 107 | 4890271 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE OUT ON POLE 186-23 IT HELD ALSO XFR FUSE OUT ON POLE 186-175 FUSE LINK JUST BROKE NOT BLOWN TICKET COMPLETE LRM//MAPS INCORRECT, SERVICER TO COME IN AND DRAW IT OUT FOR MAPPING//APPROX COD 2// VER/DBM IDC XXXX
17035 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-06-27 10:59 | 2009-06-27 12:46 | 2 | 107 | 64594-1 | 214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACING CUTOUT DOOR
17036 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-09-05 13:22 | 2022-09-05 15:55 | 4 | 153 | 4840451 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CLAMP BURNT OFF POLE 37830421A40009//OPENED LINE AT 1535 ALL RESTORED AT 1555
17037 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-02-02 20:42 | 2010-02-03 00:15 | 1 | 213 | 62451-1 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT GATE CC 1 VER/PDP IDC XXXX
17038 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2014-01-28 16:14 | 2014-01-28 17:25 | 3 | 71 | 4320161 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE RM /XFM FUSE BROKE POWER BACK ON AT 17;25 PLEASE CLOSE TIC RM XMER FUSE WAS BROKEN, NOT BLOWN OR MELTED OUT, CUSTOMER SAID ELLIOT CHANGED C/O TODAY AND FUSE MUST HAVE BEEN BAD VER/SEF IDC XXXX
17039 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-04-30 07:08 | 2022-04-30 10:41 | 1 | 213 | 4817021 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 300 amp cutout broke on 784-79 in difficult location. Additional crew enroute. Replaced all three switches and restored @ 10:41. sh
17040 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2010-10-14 10:15 | 2010-10-14 13:48 | 1 | 213 | 59573-1 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37324029 //CUTOUT FAILURE,ALSO DAMAGED XARM.WILL OPEN XFR BANK,CLEAR HOT-TAPS....CREW ENROUTE WITH MATERIAL(STEVE RAY) OPENED TR TO CLEAR TROUBLE @ 1015CUTOUT FAILURE,ALSO DAMAGED XARM.WILL OPEN XFR BANK,CLEAR HOT-TAPS....CREW ENROUTE WITH MATERIAL(STEVE RAY) RELEASED BY CREW 074S06 NEED TO SEND COPY TO CLIFF FREEMAN IN PIKEVILLE HAVE TECH. COME OUT AND WORK TO STRAIGHTEN POLE. CHANGED OUT 3 C/O AND 9 FT. CROSSARM VER/HFP L3/HFP IDC XXXX
17041 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-02-14 09:47 | 2022-02-14 13:20 | 1 | 213 | 4480361 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans fuse open at 237-C-205,Will be trying to get it back in.Trans fuse open at 237-C-205,Have a broke cutout,Made repairs and restored at 13:20.
17042 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-01-15 10:04 | 2013-01-15 11:15 | 3 | 71 | 4606431 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE B53-35.. VER/KEP IDCC PN7, CNT1 XXXX
17043 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-01-26 06:47 | 2008-01-26 07:58 | 3 | 71 | 60054-1 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T TRANSFORMER FUSE IS OUT. IT APPEARS TO HAVE JUST BROKEN//VER/CRB IDC XXXX
17044 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-11-26 12:07 | 2008-11-26 15:40 | 1 | 213 | 52474-1 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP STS WR# 27455072 /// 19.9 50 KVA 120/208 XFMR BAD CALLING FOR A CREW TO REPLACE RELEASED BY CREW 077S04 IDC XXXX
17045 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-02-02 14:04 | 2009-02-02 15:15 | 3 | 71 | 54716-1 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER IS BURNED UP, POSSIBLY DUE TO LOAD VER/KEP L3/KEP
17046 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-07-12 11:55 | 2010-07-12 13:06 | 3 | 71 | 65408-1 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT COD-3 VER/HFP L3/HFP IDC XXXX
17047 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-12-28 17:58 | 2017-12-28 19:09 | 3 | 71 | 4686431 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door on 239-6 burnt up mmay be able to replace door if i have one that will fit found a cutout door that fit restored power at 19:09/ ISO 37830239000006/ COD 3
17048 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-01-13 08:39 | 2021-01-13 12:12 | 1 | 213 | 4865431 | 213 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad UG, 120 on one leg, 80 on the other. need power temp. crew reqd. send to R morgan Released by crew 078S04arrived RM testing & trouble shoothing UGarrived RM testing & trouble shoothing UG repaired ba UG leg power on @ 12:12 please close tic RM ..WO to be wrote to replace UG Released by crew 078H20
17049 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-06-24 20:37 | 2012-06-25 00:10 | 1 | 213 | 4958151 | 213 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | FOUND BAD UNDERGROUND, HAD 53 VOLTS ACROSS THE HOT ONE, AND PHASE TO GROUND HAD 123 ON ONE LEG AND 62 ON THE OTHER, WELL BE CREW REQ, MAY BE ABLE TO USE THE POWER TEMP, ALSO NEED BUCKET TREE CREW, BIG OAK TREE GROWN UP AROUND TRANSFORMER, MAY BE THERE I COULD NOT EVEN SEE TRANSFORMER TO TELL, BUT GROUND IS HARD ENOUGH TO USE TRUCKS ON THIS RELEASED BY CREW 078S06 (INSTALLED POWER TEMP ). VER/SDB
17050 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-05-14 07:07 | 2013-05-14 10:40 | 1 | 213 | 4111621 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFORM FUSE BLEW ,CHECK AN REFUSE ,XFORM BAD 25KVA 34.5 SINGLE BUSHING WITH CURRENT LIMIT FUSE 120-240 TR. OK LINE CREW REQUIRED RELEASED BY CREW 078S04/ CREW ON SITE/FETR 11:00/JEH/ POWER REST. @ 10:40 JEH//MADE MDC ///VER/CRB L/3 CRB IDCC CCU XXXX
17051 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-11-06 12:34 | 2013-11-06 13:45 | 3 | 71 | 4015081 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 20-5075 HOT TAP BROKE OFF REPAIRED ALSO REPLACED BAD CUTOUT DOOR 12T FUSE VER/CRB L3/HFP
17052 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-06-20 12:42 | 2008-06-20 16:15 | 1 | 213 | 51121-1 | 213 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | ENROUTE FROM SALYERSVILLE. GUY RUSTED IN TWO AND ALLOWED SECONDARY POLE TO LEAN BREAKING NEUTRAL IN SERVICE DROP. I PUT SLACK IN #4 SERVICE AND SLEEVED BACK TOGETHER. THERE IS A JOB TO REPLACE ANCHOR. PLEASE FORWARD TO PEGGY WYSONG (PROBABLE DAMAGE CLAIM). SH// VER/DBM
17053 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-07-28 04:57 | 2014-07-28 08:30 | 1 | 213 | 4298831 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER WILL CHECK THIS DURING DAYLIGHT HOURS////XFMR CUTOUT BROKE///REPLACED CUTOUT//RESTORED AT 8:30//COMPLETE VER/CRB
17054 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-06-19 08:06 | 2014-06-19 11:39 | 1 | 213 | 4109861 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT DOOR
17055 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-11-19 19:17 | 2009-11-19 20:28 | 3 | 71 | 57400-1 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP 10 T FUSE LINK BROKE RELEASED BY CREW 078S11 COD-3 L3/HFP IDCC CCO XXXX
17056 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2017-01-19 18:12 | 2017-01-19 21:45 | 1 | 213 | 4313331 | 213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 079H03 ONE LEG OF 4/3 SERVICE IS OPEN ON 945B41415 I CAN MAKE REPAIRS REPAIRED BAD CONNECTIONS ON POLE 415 RESTORED POWER AT 21;45 38830954B41415 COD 1 VER/AWD L3/HFP XXXHFP
17057 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2011-06-25 17:03 | 2011-06-25 20:35 | 1 | 212 | 4414391 | 212 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | POLE 68-934 BAD UNDERGROUND SEND TO JOE RELEASED BY CREW 078S08/TOOK AMP READING ISOLATED FAULTED HOT LEG/ OPENED @ 19:35 INSTALLED ADD-A-PASE CLOSED @ 20:35 GOOD VOLTAGE: SEND TO RAYBURN////////J. HEMLEPP 078H05 RELEASED BY CREW 078H05 /VER/CRB IDC XXXX
17058 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-11-10 15:38 | 2011-11-10 19:10 | 1 | 212 | 4065791 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ALSO INSTALLED ANIMAL GUARD ///VER/CRB IDC XXXX
17059 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-03-27 07:23 | 2008-03-27 10:55 | 1 | 212 | 61104-1 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000303/// SEND TO CREWS NO TRUCK BAD CUT 1 CUST OFF RELEASED BY CREW 078S08 VER/KEP IDC XXXX
17060 | Whitesburg | 3401301 | FLEMING | NEON | 2013-02-02 10:43 | 2013-02-02 14:15 | 1 | 212 | 4785731 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SLEEVE PULLED OUT AND BURNDT DOWN 2 SPANS OF OPEN WIRE SEC. BETWEEN POLES 332-45, 46, AND 48. WILL NEED 1 MAN AND SOME #4 COPPER TO PUT BACK UP. OPENED THIS TRANS. AT 12:05 AT POLE 46, WHILE MAKING REPAIRS.PUT SEC. BACK UP, CLOSED TRANS BACK IN AT 14:15 //VER/GAH IDCC TOF1205 XXXX
17061 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-02-28 19:23 | 2015-02-28 21:09 | 2 | 106 | 4087921 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR F IS OUT,WILL RE-FUSE/////////CORRECTION,BROKEN CUTOUT TO REPLACE////////////////REPLACED CUTOUT AND RESTORED,ALL OK AFTERWARDS VER/SEF
17062 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-05-04 09:04 | 2011-05-04 10:50 | 2 | 106 | 4006581 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON TRANSFORMER POLE 1111-31, GOT PAUL HICKMAN CREW COMMING TO CHANGE POLE AND I WILL GET THEM TO HELP ON THIS CUTOUT//COD 2// VER/DBM IDC XXXX
17063 | South Williamson | 3411401 | DEWEY | INEZ | 2022-01-06 10:03 | 2022-01-06 13:35 | 1 | 212 | 4311221 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke//making repairs//repairs made//restored at 13:35//complete//em
17064 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-09-08 11:33 | 2014-09-08 15:05 | 1 | 212 | 4479781 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST HAD HIGH VOLTAGE HAD 269 VOLTS PHASE TO PHASE, NEED CREW TO CHANGE TRANSFORMER, 25 KVA SINGLE BUSHING, CAN USE TRUCK ON THIS, CREW REQ RELEASED BY CREW 078S06/CREW ON SITE/FETR 1600/VEM/REPAIRS MADE AND POWER RESTORED 1505/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
17065 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2012-04-26 19:07 | 2012-04-26 20:00 | 4 | 53 | 4715191 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10T FUSE WAS BROKEN INTO. FUSED UP EVERYTHING OK///VER/CRB L/3 CRB IDC XXXX
17066 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2017-01-17 21:50 | 2017-01-17 23:36 | 2 | 106 | 4307101 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE XFM. CUTOUT ON POLE 217C-7...WILL MAKE REPAIRS..RESTORED @ 23:36 VER/KEP L3/HFP XXXHFP
17067 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-08-05 08:01 | 2011-08-05 11:33 | 1 | 212 | 4666681 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICE POLE DOWN BAD CUTOUT ON POLE REPAIRING// REPAIRS COMPLETE POWER RESTORED AT 1133//VER/CRB STC PER PHONE CONF
17068 | Pikeville | 3421001 | BREAKS | CITY | 2015-10-06 16:14 | 2015-10-06 18:00 | 2 | 106 | 4323171 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 079H03/////////CUT OUT DOOR BURNT UP WILL REPLACE/// REPLACED CUT OUT DOOR AND RESTORED SERVICE @ 18:00// VER/ ADH L3/HFP XXXHFP
17069 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-11-14 04:36 | 2012-11-14 06:22 | 2 | 106 | 4395631 | 212 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER. CC 1 VER/SDB IDC XXXX
17070 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-02-16 10:43 | 2012-02-16 14:15 | 1 | 212 | 4352991 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A PHASE PRIMARY METERING FUSE BLOWN , WILL NEED FLAGGERS BEFORE WE CAN CHECK PRIMARY METERING, SURGE ARRESTER BLOWN ON METERING ,CUT IN CLEAR RESTORED POWER AT 14:15 IDC XXXX
17071 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-08-03 14:53 | 2012-08-03 18:25 | 1 | 212 | 4889551 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL NEED TO REPLACE ALL 3 CUTOUTS ON POLE 478, NO TRUCK ACCESS ,. WILL OPEN LINE FUSES AT POLE 8831074C-94 TO REPLACE CUTOUTS . REPLACED CUTOUTS , ALL WORK COMPLETE / GXJ//COD 1// VER/DBM IDC XXXX
17072 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-06-01 09:37 | 2015-06-01 10:30 | 4 | 53 | 4492261 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 269C163 LINE FUSE NO CREW REQUIRED/ ISO 38830269C00163/ COD 4/ VER/BOW
17073 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-02-04 21:50 | 2020-02-04 23:36 | 2 | 106 | 4362871 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got bad 19.9 cutout 37830055000065/ xfmr already out and opened line fuse on pole 37830055000254 to isolate made job to change in the morning and wq # 75747912 and customer is ok with holding until the AM/ ISO 37830055000254/ COD 2
17074 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-04-21 16:32 | 2016-04-21 17:25 | 4 | 53 | 4112551 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE LINE FUSE OPEN ON POLE 70-B4-3590. SAME AS 411255170-3590 REPAIRED BASKET AND HOT TAP. VER/AWD
17075 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2017-12-11 13:05 | 2017-12-11 14:51 | 2 | 106 | 4639521 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | notified customer/ crew opening transformer to replace underground/ ISO 38830452000138/crew on site/vem/open xfmr 1400/restored at 1451/please close ticket/thanks/vem
17076 | Whitesburg | 3309301 | VICCO | REDFOX | 2008-03-23 14:19 | 2008-03-23 15:12 | 4 | 53 | 60082-1 | 212 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309301// PART POWER, BAD CONNECTION ON POLE,REPAIRED COD-HFP VER/HFP IDC XXXX
17077 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2012-10-17 10:35 | 2012-10-17 14:07 | 1 | 212 | 4148291 | 212 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAVE TO REPLACE 4/3 SERV W 2/3 SERV.//////////REPLACED SERV DROP,ALL OK AFTERWARDS.INSULATION FAILURE ON 4/3 DROP VER/KEP IDC XXXX
17078 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-02-08 18:13 | 2011-02-08 21:45 | 1 | 212 | 55409-1 | 212 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR#38742468REPLACED BAD CONNECTIONS//VER/CRB IDC XXXX
17079 | Whitesburg | 3401301 | FLEMING | NEON | 2011-04-12 14:22 | 2011-04-12 15:15 | 4 | 53 | H55673-1 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR 39534782 // BAD UNDERGROUND SERVICE NEED CREW TO CHANGE OUT RELEASED BY CREW 077S12 RELEASED BY CREW 075H01STS WR 39534782 // BAD UNDERGROUND SERVICE NEED CREW TO CHANGE OUT RELEASED BY CREW 077S12 SERVICE. REPLACED BAD URD. SERVICE WITH TEMP. OVERHEAD SERVICE. WILL CREATE JOB TO SEND TO TECH. DUPLICATE OF 55673-1 FOR TR OUTAGE OF 4 CUST VER/HFP L3/HFP IDC XXXX
17080 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-07-02 15:42 | 2022-07-02 17:28 | 2 | 106 | 4363521 | 212 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | secondary connection burnt, repairs made
17081 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-06-19 14:28 | 2013-06-19 18:00 | 1 | 212 | 4372821 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD TRANSFORMER HIGH VOLTAGE CHECK OTHER LOCATION NEXT DOOR VOLTAGE OK 25KVA CAN GO THRU CUT IN FENCE AT BOTTOM OF HILL AT OTHER HOUSE HORSES IN FIELD ALSO RELEASED BY CREW 078S03 VER/CRB L/3 CRB IDC XXXX
17082 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2021-05-03 08:53 | 2021-05-03 12:25 | 1 | 212 | 4514791 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST STATES PART POWER,,255-282 bad c phase 277 xfr Released by crew 078S05,repairs made all cust restored @ 1225 please close ticket thanks.bt
17083 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-05-13 14:52 | 2011-05-13 15:45 | 4 | 53 | 4084571 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CLOSED FUSE POWER RESTORED PR TOLLIVER PLEASE CLOSE TKT. VER/ARN
17084 | Pikeville | 3407103 | TOPMOST | KITE | 2020-07-10 18:34 | 2020-07-10 20:20 | 2 | 106 | 4146421 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 20t line fuse out pole 257-9. closed 20t fuse in @ 20:20 everything ok looks like fuse broke
17085 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-01-29 11:05 | 2014-01-29 14:37 | 1 | 212 | 4323791 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BURNED INTO ON SERVICE DROP..4-3 TRIPLEX DROP.REPLACED WITH 2-3 S/D.. VER/HFP L3/HFP
17086 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-11-19 12:54 | 2012-11-19 14:40 | 2 | 106 | 4408671 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT IS BROKEN INTO. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. COD-2 ISO TF 37830240000094 IDC XXXX
17087 | Hazard | 3309302 | VICCO | JEFF | 2022-07-14 15:27 | 2022-07-14 16:20 | 4 | 53 | 4489951 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DE-ENERGIZED CONDUCTOR LAYING DOWN FROM POLE 37830346C00075, WILL BE CUTTING IN THE CLEAR AND REMOVING ONCE R/W AND LINE CREW ARRIVES//OPENING L/F 37830346C00051 ( COD 4) ONCE THEY ARRIVE//OFF @ 1527 ON 1620
17088 | Hazard | 3310502 | HADDIX | CANOE | 2016-04-30 15:11 | 2016-04-30 18:43 | 1 | 212 | 4145031 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT ON POLE 37830049000121,NEED 72KV CUTOUT AND ARRESTER,AND 72KV BRACKET,MANUAL,NEED LINE CREW RELEASED BY CREW 077H07..ALL PWER RESTORED @ 18:43 HRS VER/AWD
17089 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2012-08-18 07:21 | 2012-08-18 09:07 | 2 | 106 | 4948941 | 212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN/DETERATED FUSE LINK////REPAIRED VOLT CK OK VER/KEP IDC XXXX
17090 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-08-16 15:19 | 2018-08-16 18:50 | 1 | 211 | 4961031 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | has old gap type arrester and box type c/o--need fiberglass t bracket, c/o, and arrester--crew big bucket req--ds081618 Released by crew 078S01,repairs made all cust restored @ 1850 please close ticket thanks.bt
17091 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-08-23 14:38 | 2017-08-23 18:09 | 1 | 211 | 4293731 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV 19.9 XFM. SINGLE BUSHING WILL NEED CREW TO MAKE REPAIRS..POSSIBLE NON-TRUCK/ ISO 37830260000085/ COD 1/ VER/BOW
17092 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-09-02 13:09 | 2011-09-02 16:40 | 1 | 211 | 4785541 | 211 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WE HAVE PARTIAL POWER COMING TO A PEDESTAL IN TRL. PARK. SECONDARY IS OPEN SOEWHERE. DENNIS IS SENDING HELP. WE OPENED TRANS. AT 15:50 AND CLOSED IT IN AFTER REPAIRS AT 16:40.//COD 15// VER/DBM IDCC TOF1550, CNT1 XXXX
17093 | Pikeville | 3407101 | TOPMOST | DEMA | 2018-11-29 00:34 | 2018-11-29 02:40 | 2 | 126 | 4488921 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2-3 service 1 of the hot conductors was burnt into and the neutral was burnt into 1 hot conductor still togeather holding the drop up. this was due to bad serv end that failed wire heated up burnting into the neutral and burning into. had the transformer open at 01:15 and closed back in at 02:40.everything ok. send copy to peggey in damage claims cust could possibly call in with damage du to open neutral
17094 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-03-17 19:49 | 2017-03-17 23:20 | 1 | 211 | 4565831 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV C/O, LA & STANDOFF. NO TRK. CAN CUT LOOP AND INSTALL HOT TAP OR LF @ 43-245. RELEASED BY CREW 078S07 SAME AS 4566321BAD 12 KV C/O, LA & STANDOFF. NO TRK. CAN CUT LOOP AND INSTALL HOT TAP OR LF @ 43-245. RELEASED BY CREW 078S07,CUT LOOP @ 43-245 @ 2230 ALLCUST RESTORED @ 2320 PLEASE CLOSE TICKET THANKS.BT RELEASED BY CREW 078H02 VER/KEP
17095 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2010-05-06 21:29 | 2010-05-07 01:00 | 1 | 211 | 56760-1 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 50T LINE FUSE OUT DUE TO BAD ARRESTER ROW WAS SO BAD I WAS NOT SURE WHAT PROBLEM WAS I CUT POLE TO POLE CHANGED BAD ARRESTER AND CUTOUT REWORKED TRANSFORMER POLE. FUSED UP EVERYTHING OK VER/PDP IDC XXXX
17096 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-05-29 14:03 | 2019-05-29 17:34 | 1 | 211 | 4362341 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFER 38830212000145transformer feeding grassland unitd meth church is bad no voltage on secondary side going to be line crew required truck ok 100kva 38830212000145transformer feeding grassland unitd meth church is bad no voltage on secondary side going to be line crew required truck ok 100kva 38830212000145 Released by crew 078H09,replaced xfmr all cust restored @ 1734 please close ticket thanks.bt
17097 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2017-12-08 10:29 | 2017-12-08 14:00 | 1 | 211 | 4630251 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10 kv 7200 xfmr.can use truck Released by crew 077S11. replaced xfmr and restored power
17098 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-11-16 01:44 | 2014-11-16 05:15 | 1 | 211 | 4731271 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNT UP.REPLACED IT. VOLTAGE GOOD.. VER/ARN
17099 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-12-14 16:11 | 2022-12-14 19:42 | 1 | 211 | 4260181 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse is open on 523-48, broken 19.9 cutout crew required Released by crew 078S11//arrived RM replaced LF cutout & xfm cutout power on @ 19:42 please close tic RM
17100 | South Williamson | 3411401 | DEWEY | INEZ | 2017-03-18 19:09 | 2017-03-18 22:40 | 1 | 211 | 4569261 | 211 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAD PART POWER//CHECKED METERBASE AND WEATHERHEAD AND REWORKED CONNECTIONS ON WEATHERHEAD//SAW ARCING AT XFMR WHEN CLOSING BACK IN//FOUND JOT LEG BUSHING LOSE ON XFMR//TIGHTENED LUG AND EVERTHING NOW WORKING//RESTORED AT 22:40//COMPLETE//EM VER/KEP
17101 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2020-09-10 09:20 | 2020-09-10 12:51 | 1 | 211 | 4447761 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | changed xfm
17102 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-10-08 12:59 | 2017-10-08 16:30 | 1 | 211 | 4421711 | 211 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON URD SERVICE WILL NEED 1 MAN WITH THE ADD A PHASE MACHINE TO HELP MAKE REPAIRS. RELEASED BY CREW 074S05BAD LEG ON URD SERVICE WILL NEED 1 MAN WITH THE ADD A PHASE MACHINE TO HELP MAKE REPAIRS. MADE REPAIRS @1630./ ISO 38831126B10449/ COD 1/ VER/BOW L3/HFP XXXHFP
17103 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2013-07-30 06:59 | 2013-07-30 10:30 | 1 | 211 | 4605761 | 211 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEC CABLE NEUTRAL SPLICE PULLED INTO,WILL REPAIR///////MADE NECESSARY REPAIRS,VERY LONG PIECE OF 2/3 SEC CABLE,SPLICE SIMPLY PULLED INTO VER/SEF IDC CUSTOMER TURNED OF BREAKER LEFT TIME AS IS XXXX
17104 | Hazard | 3303902 | LESLIE | WOOTON | 2020-03-05 05:54 | 2020-03-05 09:25 | 1 | 211 | 4453161 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout
17105 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-11-13 08:55 | 2014-11-13 12:26 | 1 | 211 | 4724561 | 211 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | WILL CHECK FOR PROBLEMS// C/L FUSE OR XFMR APPEARS BAD // CONTACTED T. HALL AND WILL WAIT UNTIL MONDAY TO REPAIR // CUST IS WORKING ON THE ROAD AND HE WILL BE OK WITH WAITING // THIS IS A GAS COMPRESSER I/O OPS #035428238// VER/BOW
17106 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-03-18 23:49 | 2011-03-19 03:20 | 1 | 211 | 55733-1 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39226850 // POLE 44-409 BAD CUTOUT NO TRUCK SEND TO CREWS LINE FUSE STILL IN RELEASED BY CREW 078S08 POWER RESTORED 03:20 0252-0320. VER/PDP IDCC CDC83, XXXX
17107 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-07-05 05:15 | 2022-07-05 08:46 | 1 | 211 | 4375091 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | tranformer fuse broke.. power restored at 8:46
17108 | Hazard | 3310502 | HADDIX | CANOE | 2018-02-13 08:49 | 2018-02-13 12:20 | 1 | 211 | 4836621 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | @ 0850 Accessing the problem for river crossing // CSX ON SITE //@ 0850 Accessing the problem for river crossing // on pole 37830052000133 anchor has pull out of ground and wire that is not broke is pin to the ground, need to burry new anchor and straighten pole Released by crew 077S05/ ISO 37830052000135 COD 1***per crew
17109 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-06-16 19:44 | 2013-06-16 23:15 | 1 | 211 | 4350521 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD 19.9 CUTOUT.//COD 1 IDC XXXX
17110 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-09-08 11:29 | 2015-09-08 15:00 | 1 | 211 | 4213431 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED CONNECTIONS// VER/ ADH
17111 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2019-11-13 15:14 | 2019-11-13 18:45 | 1 | 211 | 4031411 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 38830116A00077 broken 35 5 pole, trucks to pole. Asplund blocking traffic. Pole 38830116A00301 needs straightened as well. #2 alum, pole at an angle, main line still energized. No danger. Send to B tackett.pole 38830116A00077 broken 35 5 pole, trucks to pole. Asplund blocking traffic. Pole 38830116A00301 needs straightened as well. #2 alum, pole at an angle, main line still energized. No danger. Send to B tackett. Released by crew 078H04
17112 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2020-07-09 18:37 | 2020-07-09 22:08 | 1 | 211 | 4137151 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Smoking Pole near Lake38830139A16169. bad 50 kva xfmer on38830139A16169 Released by crew 078S07 crew on site FETR 22:45 all pwr restored @ 22:08
17113 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2022-02-09 15:54 | 2022-02-09 19:25 | 1 | 211 | 4462651 | 211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke on pole 37830043000005.//Replaced four 19.9 cutouts.//Restored @ 19:25
17114 | South Williamson | 3411401 | DEWEY | INEZ | 2010-08-22 18:20 | 2010-08-22 21:50 | 1 | 210 | 59359-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMER FUSE OPEN CHECKING NOW.BAD 15 KVA 72 XFMERCALLED MILLER GOING TO SEND SOME MEN AND XFMER RELEASED BY CREW 076H06 VER/ARN IDCC CNT2 XXXX
17115 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-03-25 03:15 | 2012-03-25 05:00 | 2 | 105 | 4614871 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK //VER/GAH IDC XXXX
17116 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-12-09 23:15 | 2010-12-10 01:00 | 2 | 105 | 64970-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEND TO CLIFF FREEMAN IN ENG. DEPT. WE NEED TO SET A SECONDARY POLE BESIDE ROAD IN FRONT OF CUSTOMERS HOUSE AND RUN SPAN OF SECONDARY OFF POLE 1128-159. EXISTING SERVICE IS ABOUT 125 LONG {4/3 SERVING A 200 AMP HOOKUP} OFF POLE 1128-6. WE CAN DO AWAY WITH OPEN SEC. HOT LEAD ON SECONDARY POLE IS BURNED INTO. I AM GOING TO REPAIR WIRE. I REPAIRED LEAD. IDC XXXX
17117 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-01-25 18:36 | 2021-01-25 22:06 | 1 | 210 | 4891791 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,NEED 1 MAN&LONG-REACHING BUCKET.WILL REPLACE CUTOUT///////BRANDON ISOM ENROUTE TO HELP////////REPLACED CUTOUT&RESTORED
17118 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-03-10 11:05 | 2012-03-10 12:15 | 3 | 70 | 4568631 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | APPEARS SERVE-END HAS WENT BAD IN DROP.GOING TO REPLACE DROP.ALSO FOUND BAD CURRENT LIMITING FUSE.REPAIRS COMPLETE @ 12:15// VER/DBM IDCC TOF0948 ESTIMATED TIME OFF XXXX
17119 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2021-10-07 17:47 | 2021-10-07 18:57 | 3 | 70 | 4329061 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changing bad cutout power restored at 18:57
17120 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-01-30 00:15 | 2010-01-30 01:25 | 3 | 70 | H61274-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUS.SER.SHORTED TOGETHER---REPAIRED SER. VER/LDA IDCC DUP TO OPEN TRANSFORMER XXXX
17121 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-12-26 14:40 | 2020-12-26 16:25 | 2 | 105 | 4825161 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customers service drop burned into, will have to open XFM to make repairs.. off at 15:45 on at 16:25// customer is restored//
17122 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-02-06 06:12 | 2015-02-06 09:42 | 1 | 210 | 4995361 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNED UP. VER/CRB L3/HFP XXX
17123 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-03-03 12:38 | 2013-03-03 12:45 | 30 | 7 | 4867861 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED LINE FUSE ON ORDER TO REPAIR BAD CUTOUT///SEE ORDER 4867651 // COD 30// VER/DBM IDC XXXX
17124 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-01-09 01:00 | 2017-01-09 04:30 | 1 | 210 | 4279081 | 210 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR GOT HOT AND BURNED SERVICE NEUTRAL AND ONE HOT WIRE IN TWO. REPAIRED AND RESTORED. SH VER/KEP L3/HFP HFPC MCCDL
17125 | Pikeville | 3403001 | PIKEVILLE | CITY | 2014-06-25 15:46 | 2014-06-25 16:28 | 5 | 42 | 4155751 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR LUG HAD HEATED UP AND BURNED OPEN// REPAIRED// OPENED @ 15:50//CLOSED @ 16:28
17126 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-09-21 09:10 | 2021-09-21 10:55 | 2 | 105 | 4262161 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, change transformer cutout
17127 | Pikeville | 3413402 | GARRETT | LACKEY | 2019-07-16 14:55 | 2019-07-16 18:25 | 1 | 210 | 4717321 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | cust service drop neutral pulled out of a tension splice made repairs everything ok
17128 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-21 12:25 | 2015-02-21 14:10 | 2 | 105 | 4063641 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENING FUSE TO CHANGE OUT BAD XMER OPENED AT 12:25, CLOSED BACK IN AT 14:10 RELEASED BY CREW 077S02 VER/SEF
17129 | Hazard | 3309302 | VICCO | JEFF | 2020-07-31 15:45 | 2020-07-31 19:15 | 1 | 210 | 4265261 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse must be out, going back off mtn, bad arresstor on xfmr pole. all power restored
17130 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2017-09-27 12:00 | 2017-09-27 12:30 | 7 | 30 | H4392811 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 39831072C45564 2 CUSTOMER OUT ORIGINALLY/ FOUND NEUTRAL AND HOTLEGS BURNTED INTO ON POLE 1072-5564, 1/0 SEC, NO CREW REQ TOOK CARE OF IT MYSELF, ALL REPAIRS ARE MADED AT THIS LOC AND EVERYONE IS BACK ON, OPENED XFMR 39831072C45564 TIME OFF WAS 1200 TIME ON WAS 1230 (7 ADD CUST) BY AMG/ DUPLICATE IN HOIS/ VER/BOW
17131 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-12-15 22:59 | 2016-12-16 02:29 | 1 | 210 | 4198951 | 210 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND NEUTRAL BROKE IN SERVICE DROP AND CONDUCTOR MELTED...MADE REPAIRS.. VER/KEP VER/HFP L3/HFP
17132 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-08-03 11:24 | 2020-08-03 14:54 | 1 | 210 | 4280551 | 210 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERV DROP ONLY PARTIAL POWER,COMES OFF MTN THRU DENSE BRUSH AND TREES.HAVE TO CUT PATH TO POLE.TODD MCCOY ENROUTE TO HELP//////SPLICE ABT 10FT OUT FRM POLE BURNED INTO/////////MADE NECESSARY REPAIRS&RESTORED,ALL OK AFTERWARDS
17133 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-06-21 11:00 | 2015-06-21 11:30 | 7 | 30 | 4627911 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING LINE FUSE 45-3638 FEEDING HIGHLAWN AVENUE TO REPAIR BAD CUTOUT/RELATED TO ORDER 4627631/OPENED 1100 CLOSED 1130// VER/ ADH L3/DKG
17134 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-12-02 17:30 | 2010-12-02 18:40 | 3 | 70 | 62577-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE, ONLY 1 CUSTOMER ON THIS XFMR /// COD-3 ISO TF 38830185000116 VER/HFP L3/HFP IDC XXXX
17135 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-11-22 07:25 | 2019-11-22 09:10 | 2 | 105 | 4055141 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRF IS OUT,WILL RE-FUSE//////////CUTOUT IS BROKEN,WILL REPLACE IT///////REPLACED BROKEN CUTOUT&RESTORED,ALL OK AFTERWARDS
17136 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-02-12 07:16 | 2012-02-12 09:01 | 2 | 105 | 4340831 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED SERVICE IDCC PN17, CNT4 XXXX
17137 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2016-08-16 14:20 | 2016-08-16 16:05 | 2 | 105 | 4794601 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED TRUCK OK BROKEN CUT OUT ON POLE 477-327 RELEASED BY CREW 078S02CREW REQUIRED TRUCK OK BROKEN CUT OUT ON POLE 477-327 CUT OUT CHANGED AND FUSE CLOSED IN AT 16:05 RESTORING CUSTOMERS PLEASE CLOSE TICKET THANKS T CANTRELL/ ISO 38830477000237/ COD 2/ VER/BOW
17138 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-12-22 17:56 | 2014-12-22 21:26 | 1 | 210 | 4875341 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN WILL REFUSE//// BAD 25 KVA 19.9 TRANSFORMER NEED 1 MAN /// CAN USE TRUCK//// CHANGED BAD TRANSFORMER AND CLOSED IN NEW TRANSFORMER @ 21:26 AND RESTORED SERVICE// COD 1// VER/ ADH
17139 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-02-12 13:38 | 2015-02-12 14:20 | 5 | 42 | 4010761 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR THAT WAS OUT WAS ON POLE #38831126B10020 NOT 19//MADE MDC// VER/CRB L3/HFP XXX
17140 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-12-01 15:20 | 2013-12-01 15:50 | 7 | 30 | 4090841 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | NEED 3 MAN PRC CREW--TRUCK TO POLE WITH PADS--NEED TO UPGRADE RISERS IN 50KVA TRANSFORMER--MELTED OUT ON SECONDARY SIDE RELEASED BY CREW 078S07.OPENING TRANS TO MAKE REPAIRS.BLR//COD 7//OPENED 1520 CLOSED 1550// VER/DBM L3/HFP
17141 | Whitesburg | 3314401 | MAYKING | ERMINE | 2021-01-07 15:30 | 2021-01-07 15:51 | 10 | 21 | 4854691 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | customers were experiencing light flickering. checked voltage , found open neutral. transformer neutral bushing was loose. tightened up and checked voltage good.. everything should be good to go now //off@1530 on@1540
17142 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2022-09-24 17:05 | 2022-09-24 20:35 | 1 | 210 | 4917701 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced bad srv drop 20:35- allgood-ds092422
17143 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-04-30 14:18 | 2018-04-30 15:00 | 5 | 42 | 4291311 | 210 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on one hot leg at weatherhead//i repaired connection//restored to normal///restored at 15:00//complete//em
17144 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2017-09-22 14:10 | 2017-09-22 14:40 | 7 | 30 | H4381291 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | GOT FUSE OUT ON POLE 38830785D20210..LOOKING IT OVER NOW. FUSE CAME BACK OUT.. GOING TO BE LOOKING OVER MORE..OPENED OTHER TWO RISER CUTOUTS ON POLE 785-210.. MADE UP SECONDARY LOOPS UP ON POLE 785-208. TWO FEED CUSTOMERS FROM POLE 785-207.. OPEN TRANSFORMER ON 207. AT 14;10 AND CLOSED BACK IN AT 14:40. TO RESTORE POWER.. CREATED 4382851 TO REFLECT 785-207 OUT. VER/AWD VER/ALB L3/HFP XXXHFP
17145 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-06-13 22:05 | 2011-06-13 23:15 | 3 | 70 | 4314561 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT. --- POWER RESTORED.//VER/CRB
17146 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2017-02-16 14:45 | 2017-02-16 16:30 | 2 | 105 | 4401611 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 120/240 CAN. 268 VOLTS PHASE TO PHASE. TRK OK GRAVEL DRIVEWAY BESIDE BRICK WALL. RELEASED BY CREW 078S07//NO OUTAGE TILL CREW ARRIVES//OPENED 1445 CLOSED 1630 VER/CRB L3/HFP XXXHFP
17147 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2018-04-18 11:15 | 2018-04-18 12:25 | 3 | 70 | 4250041 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW GOING TO REPLACE TRANSFORMER opened @ 1115 closed @ 1225
17148 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-05-14 19:50 | 2011-05-14 21:00 | 3 | 70 | 4094181 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | // BAD CUTOUT GATE BURNT INTO ON POLE 375-63... REPLACED GATE RESTORED POWER AT 21:00
17149 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-02-16 17:04 | 2014-02-16 18:14 | 3 | 70 | 4392571 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT LOOKS LIKE FUSE MELTED OR BROKE FUSE UP EVERYTHING OK. SEND COPY TO ENG PIKEVILLE CHECK LOAD COD-3 ISO TF 37830141000056 VER/HFP L3/HFP
17150 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-09-16 09:20 | 2010-09-16 10:30 | 3 | 70 | 50311-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 37830248B00146//REPLACED 7.2 KV CUTOUT VER/KEP L3/KEP IDCC PN147, CNT6 XXXX
17151 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2014-03-04 08:48 | 2014-03-04 09:30 | 5 | 42 | 4449921 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 449-255, REPLACED CUTOUT RESTORED POWER AT 09:30 VER/CRB
17152 | Pikeville | 3402003 | KEYSER | MULLINS | 2019-11-13 22:51 | 2019-11-13 23:21 | 7 | 30 | 4032191 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burndt into @ trans. pole 1127-A-175, will have to open trans. to make repairs, will keep track of times.Opened up trans. @2251, made repairs and closed back in @2321
17153 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-05-17 11:05 | 2017-05-17 11:40 | 6 | 35 | 4807681 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ALL SERVICES WERE MADE UP TO #4 OPEN-WIRE ON XFMR POLE WHEN POLE WAS REPLACED RECENTLY. THEY ARE MELTING OUT. OPENED XFMR @ 11:05, REWORKED ALL XFMR CONNECTIONS AND CLOSED XFMR @ 11:40. SH VER/CRB
17154 | Cannonsburg | 3001401 | LOUISA | CITY | 2013-11-01 03:08 | 2013-11-01 04:53 | 2 | 105 | 4986551 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XMF FUSE OUT. CUTOUT DOOR BAD, OLD DOOR. REPLACED CUTOUT AND ARRESTER. APR AT 0453 CLOSE TICKET. DEW //VER/GAH
17155 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-07-30 20:45 | 2020-07-30 22:30 | 2 | 105 | 4259391 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutot , changing
17156 | Hazard | 3309302 | VICCO | JEFF | 2008-09-15 18:20 | 2008-09-15 19:30 | 3 | 70 | 64407-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | VER/HFP LINE FUSE BLOWN ON POLE 298-4, REMOVED GUY WIRE POWER RESTORED. COD-3 IDC XXXX
17157 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2018-04-28 08:29 | 2018-04-28 09:11 | 5 | 42 | 4286141 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse open @230-283, patrolling.//FUSE BROKE L3/HFP
17158 | South Williamson | 3411401 | DEWEY | INEZ | 2021-03-18 14:22 | 2021-03-18 15:32 | 3 | 70 | 4348221 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke on 743-148//blew rise fuse on 743-29//repairs made//restored at 15:32/complete//em
17159 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-05-19 07:42 | 2008-05-19 11:12 | 1 | 210 | 65734-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3402002//NEUTRAL ON SERVICE DROP BURN INTO, WILL NEED TO BE REPLACE, HOT LEAD MELTED INTO NEUTRAL VER/HFP IDC XXXX
17160 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-02-04 11:48 | 2021-02-04 14:15 | 2 | 147 | 4937131 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TR fuse is open on pole 190-B-332,Going to try and get it back in.Will have to lift Hot Tap on 190-B-121 to clear up Cut out will keep up with time..LIFTED HOT CLAMP @1312 RESTORED @1415
17161 | Hazard | 3309003 | JEFF | VIPER | 2018-10-07 04:46 | 2018-10-07 08:16 | 1 | 210 | 4204931 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Dispatched in accordance with KYPCo Late Night Callout Guidelines cut arrester in clear L3/HFP
17162 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-10-18 06:30 | 2008-10-18 08:15 | 2 | 105 | 56783-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SPECTRUM NOT WORKING TODAY ::: SERVICER C/O BAD C/O VER/PDP IDC XXXX
17163 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-02-23 14:38 | 2021-02-23 16:23 | 2 | 105 | 4233081 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 482-B-244, power restored at 16:23.
17164 | Pikeville | 3421001 | BREAKS | CITY | 2015-08-13 14:30 | 2015-08-13 16:15 | 2 | 105 | 4132191 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE #221-5 WILL PATROL/// CUT OUT BROKE ON POLE # 221-154 WILL CHANGE/// CHANGED BAD CUTOUT //////CLOSED LINE FUSE IN @ 16:15 AND RESTORED SERVICE/ ISO 37820221000005/ COD 2/ VER/BOW
17165 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-02-01 18:51 | 2018-02-01 22:21 | 1 | 210 | 4790651 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester 38831031000087
17166 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-03-16 18:50 | 2014-03-16 20:00 | 3 | 70 | 4498251 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PUT POLE FIRE OUT AND REPLACED TRANSFORMER CUTOUT. VER/ARN
17167 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-03-23 18:20 | 2018-03-23 21:50 | 1 | 210 | 4046791 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout no truck linecrew required Released by crew 078S11/ ISO 38830668C10041/ COD 1
17168 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-10-28 16:18 | 2017-10-28 17:00 | 5 | 42 | 4505871 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SAID ALL NEIGHBORS OUT AS WELL. BAD 12KV DOOR, REPLACED DOOR VER/AWD L3/HFP XXXHFP
17169 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2016-10-14 13:54 | 2016-10-14 14:15 | 10 | 21 | 4017061 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | MAKING REP AIRS TO SEC,ON PL , OFF AT 13 54 FOR LESS THAN 10 MIN, POWER WILL BE RESTORED KWB BACK ON AT 1415 POWER RESTORED VER/AWD L3/HFP XXXHFP
17170 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-05-07 12:00 | 2009-05-07 15:30 | 1 | 210 | 66090-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP IKE GILKERSON REPAIRING BAD U/G L3/HFP
17171 | Hazard | 3303901 | LESLIE | HYDEN | 2021-08-19 13:15 | 2021-08-19 15:00 | 2 | 105 | 4120101 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | need cutout arrester t-bracket manuel, also need ROW crew manuel to clear around pole, cust also has to replace meterbase with inspection before reconnect, OPPS# 033934692
17172 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-04-28 13:20 | 2015-04-28 16:50 | 1 | 210 | 4373171 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 CUTOUT BAD NEED BIG BUCKET AND FLAGGERS VER/CRB
17173 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2013-04-30 14:51 | 2013-04-30 16:36 | 2 | 105 | 4060081 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE.REPLACED CUTOUT AND ARRESTOR.POWER RESTORED.//COD 2// VER/DBM IDC XXXX
17174 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-03-02 17:35 | 2010-03-02 18:45 | 3 | 70 | 62341-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE OPEN TRANSFORMER 17:35. NEED A FLAGMAN. PUT OUT FIRE AND REPLACED CUTOUT. ...DAH//VER/CRB IDC XXXX
17175 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-01-09 10:28 | 2014-01-09 12:13 | 2 | 105 | 4264561 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS FUSE BROKE ON POLE 478-16 SERVICER TO MAKE REPAIRS REPAIRS COMPLETE PLEASE CLOSE TICKET LRM VER/CRB
17176 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-12-10 21:09 | 2017-12-10 22:54 | 2 | 105 | 4637951 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout.changing
17177 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-10-10 10:09 | 2018-10-10 11:54 | 2 | 105 | 4214591 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broken on pole 263-49.will make repairs..repairs made.restored.. L3/HFP
17178 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2010-07-28 15:40 | 2010-07-28 16:10 | 7 | 30 | 58390-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GIVE TO CREW TO CHANGE OUT WHEN ONE COMES AVAILABLE,6- CUST ON AN 25 KVA NEEDS CHANGE TO BIGGER TRANS FORMER TRUCK OK RELEASED BY CREW 078S09 // OPENED TR @ 1540 CLOSED @ 1601 COD-7 VER/HFP L3/HFP IDC XXXX
17179 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-07-21 21:50 | 2008-07-21 22:25 | 6 | 35 | 56296-1 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3404302//JRV ON SITE @ 22:10....XFRMER FUSE OUT & BLOWN ARRESTER.....WILL CLEAR UP ARRESTER & RE-FUSE//...CLEARED BAD ARRESTER UP....RE-FUSED CUTOUT...POWER ON....PLEASE SEND COPY TO RON RYE @ PIKEVILLE ENGINEERING FOR ARRESTER REPLACEMENT...THANX....JRV...07/21/08 VER/ARN IDCC CNT1 XXXX
17180 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2014-07-28 17:50 | 2014-07-28 18:20 | 7 | 30 | 4303181 | 210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION ON XFMR, SMOKING, REPAIRED CONNECTION. OPENED XFMR AT 1750 AND CLOSED AT 1820 VER/CRB
17181 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-01-12 17:26 | 2014-01-12 20:55 | 1 | 209 | 4275671 | 209 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 074S05// WILL XFMR RISERS// REWORKED XFMR BANK // ONLY 1 CUST OUT// POWER IS RESTORED VER/KEP L3/HFP
17182 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-06-08 22:26 | 2019-06-09 01:55 | 1 | 209 | 4463911 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 A/material handler, 25kVa 7200 single bushing/will need an A lineman 25 kva single bushing 7200/120-240 & material handler that reaches farthest off the back.
17183 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-04-04 11:01 | 2022-04-04 14:30 | 1 | 209 | 4720061 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout changing..
17184 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-08-19 11:56 | 2010-08-19 15:25 | 1 | 209 | 58185-1 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT NEED BIG BUCKET//COD 1// VER/DBM IDC XXXX
17185 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-05-04 07:42 | 2010-05-04 11:11 | 1 | 209 | 55471-1 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SCTS WR # 34956570 // 120/208 ==7200 25KVA XFMR BAD CALLING FOR CREW TO REPLACE RELEASED BY CREW 077S04......CHANGED OUT BAD XFMER....ALL POWER RESTORED @ 11:11 HRS COD-1 VER/HFP L3/HFP IDC XXXX
17186 | South Williamson | 3411401 | DEWEY | INEZ | 2010-04-05 11:40 | 2010-04-05 15:09 | 1 | 209 | 58794-1 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW ON SITE STARTING REPAIRS TCM////VER/CRB IDC XXXX
17187 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-01-11 08:19 | 2017-01-11 11:48 | 1 | 209 | 4286041 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 19.9KV NEED 2 MEN AND CUTOUT AND FIBERGLASS BRACKET. RELEASED BY CREW 074S02 FUSE OPENED AT 1143-1148 VER/AWD L3/HFP XXXHFP
17188 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-12-11 07:31 | 2018-12-11 11:00 | 1 | 209 | 4550891 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Bad 19.9 kvprimary metering can I bypassed the bad metering.
17189 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-12-12 19:55 | 2020-12-12 22:04 | 5 | 129 | 4763951 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout on pole 32-116 broke will have to open line up on pole 32-B-22 to safely make repairs///opened fuse (4 COD) at 2144 and closed at 2204
17190 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-08-28 14:46 | 2008-08-28 18:15 | 1 | 209 | 57018-1 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408103// REPLACED CUTOUT AND LIGHTNING ARRESTER / GXJ//COD 1// VER/DBM IDC XXXX
17191 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-03-16 06:16 | 2009-03-16 09:45 | 1 | 209 | 58990-1 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTENING ARRESTER BROKE DOWN. I CLEARED IT UP AND IM GOING TO REFUSE LINE FUSE ON POLE 190-67. I CLOSED LINE FUSE IN AND IT STAYED.//COD 1// VER/DBM IDC XXXX
17192 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2018-02-12 10:58 | 2018-02-12 14:27 | 1 | 209 | 4834051 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9kv transformer cutout on pole 174-307 has broken,getting help to replace.all power restored @ 14:27 hrs..p.hicks/ ISO 37830174D00307/ COD 1
17193 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-03-20 11:51 | 2019-03-20 15:20 | 1 | 209 | 4003071 | 209 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection had meted open @ XFMR I deenergized service and made repairs also replaced all other conn. on service @ house and on pole//Voltage goob on our side but customer is still having issues I advised him to have electrician to come check his equipment///Customer off @ 14:17 and back on @ 15:20
17194 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-05-12 10:01 | 2011-05-12 13:30 | 1 | 209 | 4071371 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | TONY REPORTED A ROTTEN POLE ON POLE #902-24 AND IS GOING TO GET IT REPLACED. NO ONE IS OUT OF POWER, JUST CREATED A TICKET FOR CREW TO WORK UNDER.//GAB FOUND ROTTEN POLE, HAVE IT CHANGED OUT AND EVERYONE IS BACK IN POWER
17195 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-03-10 01:46 | 2010-03-10 05:15 | 1 | 209 | 64489-1 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE ;; REPLACED FUSE VER/ARN IDCC PN94 XXXX
17196 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2013-12-15 05:48 | 2013-12-15 09:17 | 1 | 209 | 4162621 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 3 MAN PRC CREW--TRUCK TO POLE NEED 3 CUTOUTS AND BIGGER BUCKET--BAD CUTOUT ON 3 PHASE PRIMARY UG POLE RELEASED BY CREW 078S07/CREW ON SITE/FETR0945/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0917/PLEASE CLOSE TICKET/THANKS/VEM VER/TOM L3/OM
17197 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-06-19 15:54 | 2014-06-19 19:23 | 1 | 209 | 4113291 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | R VIRGIN & RUGGLES & SIMMONS & GRIFFITH // 8 FOOT XARM BROKE ON POLE 188-204, NEED LINE CREW AND 8 FOOT XARM. TRUCKS TO POLE.8 FOOT XARM BROKE ON POLE 188-204, NEED LINE CREW AND 8 FOOT XARM. TRUCKS TO POLE. RELEASED BY CREW 078S01 RELEASED BY CREW 078H16 AJBC CDC82
17198 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-07-05 17:16 | 2016-07-05 20:45 | 1 | 209 | 4542021 | 209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER RISER BURNED OFF ON POLE 171-162 MADE REPAIRS AND RESTORED POWER AT 2045/ ISO 37830171000162/ COD 1/ VER/BOW
17199 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2017-01-24 18:07 | 2017-01-24 21:36 | 1 | 209 | 4328221 | 209 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NUETRAL BROKEN AT WEATHERHEAD I CAN MAKE REPAIRS NUETRAL AND ONE HOT SECONDARY BURNT IN TWO AT WEATHERHEAD I REPAIRED WIRE AND REPLACED ALL CONNECTIONS AT WEATHERHEAD/ ISO 37830139A30282/ COD 1/ VER/BOW L3/HFP HFPC CDC89 FEC46
17200 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-12-05 21:07 | 2009-12-06 00:35 | 1 | 208 | 59643-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SD BURNED APART ... REPLACED WITH 2/3 , ALL WORK COMPLETE / GXJ VER/LDA IDC XXXX
17201 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2011-10-20 06:54 | 2011-10-20 10:22 | 1 | 208 | H4002231 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CSP XFMR TRIPPED OFF ON 1012C2...BAD CONNECTION ON SPAN OF OPEN WIRE SECONDARIES GOING FROM POLE 1012C2 TO 1012C3..SECONDARIES HAVE BURNT DOWN..ALSO PHONE CABLE HAS BURNT & FELL...CAN ELIMINATE SPAN OF SECONDARIES...//..ALL SECONDARIES CUT DOWN.ALL SECONDARY & NUETRAL CONNECTIONS REMADE ON BOTH POLES..CSP BACK ON @ 09:35.//.ONE CUST STILL OFF.SPLICING SERVICE FOR THAT SERVICE..OPENED XFMR ON 1112C3 @ 09:55.CLOSED @ 10:20..//.JRV.10/20/11//COD 1 + 1 IDCC CNT4 XXXX
17202 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-01-03 08:20 | 2011-01-03 09:12 | 4 | 52 | 58111-1 | 208 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 10TH ST-MIDTOWN-BROKEN FUSE-1 FUSE OUT IN BANK//VER/CRB IDC XXXX
17203 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-08-27 07:12 | 2008-08-27 10:40 | 1 | 208 | 55752-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801//BAD CUTOUT, NO DAMAGE TO POLE VER/TOM
17204 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-04-03 21:56 | 2012-04-03 23:40 | 2 | 104 | 4645071 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, NEED 1 MAN AND BIG BUCKET. -- REPLACED CUTOUT AND ARRESTOR, POWER RESTORED. VER/KEP IDC XXXX
17205 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2021-03-31 08:16 | 2021-03-31 10:00 | 2 | 104 | 4405891 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 449-A2-37.. will need to open the other two transformers on bank to make repairs.. open @ 09:24 closed @ 10:00
17206 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2020-03-03 09:21 | 2020-03-03 11:05 | 2 | 208 | 4446641 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned up power restored at 11:05
17207 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-06-21 16:46 | 2011-06-21 18:30 | 2 | 104 | 4365441 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT, REPLACED, ALL POWER ON//COD 2// VER/DBM IDC XXXX
17208 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2010-02-13 20:27 | 2010-02-13 23:55 | 1 | 208 | 57508-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD URD SERVICE. CREW TO INSTALLL TEMP OVERHEAD SERVICE.UNDERGROUND SERVICE IN TROUBLE INSTALLED TEMPORARY OVERHEAD. VER/PDP IDCC CNT2 XXXX
17209 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-01-17 10:39 | 2009-01-17 14:07 | 1 | 208 | 57389-1 | 208 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP THIS IS THE PART POWER...SEE DUPLICATE FOR TR OUTAGE ///SERVICE NEUTRAL BROKEN IN MIDSPAN. I OPENED TRANSFORMER AT 1355 AND CLOSED BACK AT 1407 COD-3 L3/HFP AJBC TON13:55 SEE H57389-1.
17210 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-11-03 14:52 | 2022-11-03 18:20 | 1 | 208 | 4095121 | 208 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Doug Hall reported broken service neutral at 259 Ray Br. #4 service neutral was broke into @1011-A-40, made repairs and restored @1820.
17211 | Hazard | 3303901 | LESLIE | HYDEN | 2012-05-05 14:47 | 2012-05-05 18:15 | 1 | 208 | 4750741 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED 19.9 CUTOUT///VER/CRB L/3 CRB IDC XXXX
17212 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2010-10-06 20:22 | 2010-10-06 23:50 | 1 | 208 | 57603-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA XFMR (OIL SEEPING OUT OF TOP). DUTY SUPERVISOR NOTIFIED - CREW ENROUTE TO CHANGE. XFMR & RELATED MATERIAL LOADED. CREW ENROUTE TO JOBSITE. REPLACEMENT COMPLETE. RESTORED @ 23:50. SH IDC XXXX
17213 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2008-12-17 00:42 | 2008-12-17 04:10 | 1 | 208 | 59354-1 | 208 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | 3003702//SEC.RISER BURNT UP ON POLE#140-7535. RELEASED BY CREW 078S04. NEED 500MCM AND 4/0 RISER. 2/3 AL SERVICE. LMR--REPAIRED BAD CONNECTIONS //VER/GAH L3/KEP IDC XXXX
17214 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2008-03-31 13:37 | 2008-03-31 13:50 | 16 | 13 | 62409-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3403301// BAD SECONDARY RISER TO TRANSF // WILL HAVE TO OPEN TR TO MAKE REPAIRS // COD-16 //FOUND BAD SEC RISER COMING OUT OF 50 KVA ,WILL PULL OFF LONG ENOUGH TO REPLACE RISER TCM///OPEN 1337 - CLOSED 1350// VER/DBM IDC XXXX
17215 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2013-11-22 17:38 | 2013-11-22 21:06 | 1 | 208 | 4065931 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BELIEVE CUTOUT OR LA IS BREAKING DOWN,JACKSON ENROUTE TO HELP/////////REPLACED BAD CUTOUT,WAS BROKEN//COD 1// VER/DBM
17216 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-04-21 09:37 | 2021-04-21 13:05 | 1 | 208 | 4467181 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | reworked tran cons and weatherhead cons-allgood-ds042121
17217 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2019-07-05 19:43 | 2019-07-05 23:11 | 1 | 208 | 4662391 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on p 571-c2-136 all pwr restored @ 23:11
17218 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2022-04-25 12:57 | 2022-04-25 14:41 | 2 | 104 | 4797991 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection bad inside 3phase junction box. Made repairs
17219 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2014-11-24 13:05 | 2014-11-24 13:31 | 8 | 26 | H4759311 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 1147-436 30T UNDERGROUND FUSE OUT NEED LINE CREW AND DAYLIGHT---BAD PRIMARY CABLE BETWEEN XFMR 705 & 708---PARKED IN 705---OPENETD BLADE IN LIVE FRONT 708--TAGD IN BOTH XFMRS---OPENED RISER ON 691 @ 13:05 BACK IN @ 13:31---TBL TKT COMPLETED // COD-18 ISO @ 39831147A00436 N.O. HAD BEEN MOVED TO TR 1147-A3-697 - DUP H4759311 FOR 2ND OUTAGE VER/HFP L3/HFP
17220 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2013-01-10 09:28 | 2013-01-10 09:44 | 13 | 16 | 4582971 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEE 4582301 VER/KEP IDC XXXX
17221 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2014-04-25 17:36 | 2014-04-25 19:20 | 2 | 104 | 4635301 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNING @ 1077-235 /// WILL TRY TO PUT FIRE OUT AND CHANGE CUTOUT// REPLACED CUTOUT POWER IS RESTORED @ 19:20// 4-25// POLE WILL NEED TO BE CHANGED AT A LATER DATE, ITS BURNED ABOUT HALF TO TWO // SEND TO C. FREEMAN COD-2 ISO TF 38831077D00235 VER/HFP L3/HFP
17222 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2013-06-04 18:16 | 2013-06-04 20:00 | 2 | 104 | 4220441 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 138-199 BAD CUTOUT DOOR 8T TRANS FUSE//COD 2// VER/DBM
17223 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2012-01-10 20:43 | 2012-01-10 21:35 | 4 | 52 | 4246081 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSED OUT..CANT TELL WHY YET..WILL INSPECT & RE-FUSE..//.OLD FUSE LINK JUST BROKE..REPLACED & RE-FUSED..POWER ON..JRV..01/10/12 ///VER/CRB IDC XXXX
17224 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-01-03 08:27 | 2012-01-03 10:11 | 2 | 104 | 4227931 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON POLE 1123-4138 WILL ISOLATE, ON POLE 1123-4077 CALLED FOR HELP POWER RESTORED//ISO 39831123C14077 // COD 2// VER/DBM IDC XXXX
17225 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-03-06 10:19 | 2011-03-06 10:32 | 16 | 13 | 50449-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39052330 // BAD CUT OUT ON 421-10 WILL HAVE TO OPEN LINE FUSE ON 421-8BAD CUT OUT ON 421-10 WILL HAVE TO OPEN LINE FUSE ON 421-8... OPENED AT 10:19 REPLACED CUTOUT RESTORED POWER AT 10:32BAD CUT OUT ON 421-10 WILL HAVE TO OPEN LINE FUSE ON 421-8... OPENED AT 10:19 REPLACED CUTOUT RESTORED POWER AT 10:32 RELEASED BY CREW 077S11 COD-16 ISO LF 37830421A40008 VER/HFP L3/HFP IDC DCMT XXXX
17226 | Hazard | 3309003 | JEFF | VIPER | 2015-11-14 07:40 | 2015-11-14 09:24 | 2 | 104 | 4447001 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GATE VER/KEP
17227 | Hazard | 3303901 | LESLIE | HYDEN | 2019-12-17 21:51 | 2019-12-17 23:35 | 2 | 104 | 4164771 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
17228 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2011-10-20 06:54 | 2011-10-20 10:22 | 1 | 208 | 4002231 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CSP XFMR TRIPPED OFF ON 1012C2...BAD CONNECTION ON SPAN OF OPEN WIRE SECONDARIES GOING FROM POLE 1012C2 TO 1012C3..SECONDARIES HAVE BURNT DOWN..ALSO PHONE CABLE HAS BURNT & FELL...CAN ELIMINATE SPAN OF SECONDARIES...//..ALL SECONDARIES CUT DOWN.ALL SECONDARY & NUETRAL CONNECTIONS REMADE ON BOTH POLES..CSP BACK ON @ 09:35.//.ONE CUST STILL OFF.SPLICING SERVICE FOR THAT SERVICE..OPENED XFMR ON 1112C3 @ 09:55.CLOSED @ 10:20..//.JRV.10/20/11//COD 1 + 1 IDCC CNT4, PN3 XXXX
17229 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-01-04 12:34 | 2011-01-04 14:18 | 2 | 104 | 58586-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | TRANSFORMER OK REPLACED LUG ON SECONDARY BUSHING.//VER/CRB IDC XXXX
17230 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-10-25 14:02 | 2010-10-25 14:18 | 13 | 16 | H62665-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT GOT FRANK HURLEY COMMING TO HELP ON CUTOUT SERVICER OPENED LF AT POLE 288-68 15 CC OFF 1402 ON 1418 VER/KEP L3/KEP APPOX 15 MIN. IDCC PN57, CDC92 XXXX
17231 | Pikeville | 3409502 | BURDINE | LEVISA | 2018-06-17 17:10 | 2018-06-17 18:54 | 2 | 104 | 4611341 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse out @37830336000010, checking. Trans. fuse pulled into, only 2 customers were out, refused @1854.
17232 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-01-21 10:36 | 2010-01-21 12:20 | 2 | 104 | 57165-1 | 208 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SQUEEZE- ON CONNECTOR HAD FROZE OUT, REPLACED//VER/CRB IDC XXXX
17233 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-12-22 09:52 | 2013-12-22 13:20 | 1 | 208 | 4189591 | 208 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS///////BAD SERVE-IN CONNECTION 1 HOT LEG,REPLACED,ALL OK AFTERWARDS// VER/DBM L3/HFP
17234 | Pikeville | 3408101 | SALISBURY | PRINTER | 2022-03-26 12:08 | 2022-03-26 13:52 | 2 | 104 | 4677031 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | had a hot lead brunt off at xformer pole 1123-A-56. got restoed and back on at 13:50
17235 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2009-01-22 19:38 | 2009-01-22 20:30 | 4 | 52 | 59263-1 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3402802//TRANSFORMER FUSE BLOWN GIVING IT A SHOT// 6T FUSE BROKE REFUSED CUTOUT, COMPLETE TT....// COD 4 // VER/TOM L3/TOM
17236 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-03-03 23:31 | 2018-03-04 01:15 | 2 | 104 | 4958181 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE ON POLE 95-318////////////RE-FUSED & RESTORED @01:15/////////NO IDEA WHY FUSE WAS BLOWN
17237 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-05-08 08:47 | 2011-05-08 12:15 | 1 | 208 | 4018921 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | THINK SURGE ARRESTOR HAS GONE BAD,WILL REPLACE/////BAD XFR,CREW ENROUTE SHORTLY WITH ONE,PAUL LAYNE.//////REPLACED XFR AND RESTORED COD-1 ISO TF 38831102000006 VER/HFP L3/HFP IDC XXXX
17238 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-12-19 03:21 | 2013-12-19 05:05 | 2 | 104 | 4174811 | 208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMIT MADE REPAIRS EVERYTHING OK //VER/GAH L3/HFP
17239 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-07-21 10:03 | 2015-07-21 13:30 | 1 | 207 | 4925041 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DROP BURNT DOWN DUE TO BAD CONNECTION, REPAIRING NOW// REPAIRED OUR EQUIPMENT // LEFT TRANSFORMER CUTOUT OPEN PO POLE 853-33 SO CUTOMER COULD MAKE SOME REPAIRS // THEY WILL CALL IN WHEN READY // RDM VER/CRB
17240 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2016-04-15 14:24 | 2016-04-15 15:33 | 3 | 69 | 4094401 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE LINE FUSE GATE BURNDT UP ON POLE 351-31, CHECKED REST OF LINE AND FOUND NO TROUBLE. MADE REPAIRS AND CLOSED L/F AT 1533./ ISO 37830351C00031/ COD 3/ VER/BOW
17241 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-04-12 14:15 | 2008-04-12 17:42 | 1 | 207 | 50509-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD HOT LEG ON UNDERGROUND SERVICE. RELEASED BY CREW 078S01 CREW INSTALLED POWER TEMP WILL REPAIR UNDERGROUND AT LATER DATE FULL POWER RESTORED AT 17:42 VER/HFP IDC XXXX
17242 | Hazard | 3310502 | HADDIX | CANOE | 2010-11-01 19:43 | 2010-11-01 23:10 | 1 | 207 | 50798-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE TRANFORMER BAD GOING TO PUT 25 KVA AND GOT ONE COMMING//COD 1// VER/DBM IDC XXXX
17243 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-01-24 13:21 | 2015-01-24 14:30 | 3 | 69 | 4959341 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE,,,REFUSED POWER BACK ON VER/SEF
17244 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-04-01 17:58 | 2014-04-01 21:25 | 1 | 207 | 4553461 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORM FUSE BROKE REFUSE POWER RESTORED COD-1 ISO TF 38830402000069 VER/HFP L3/HFP IDC XXXX
17245 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-11-05 17:27 | 2010-11-05 17:50 | 9 | 23 | 53327-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE TO ADD CROSSARM TO BURNED POLE AT 17:27 ... ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03//COD 9// VER/DBM IDC XXXX
17246 | Hazard | 3309302 | VICCO | JEFF | 2014-06-27 10:38 | 2014-06-27 14:05 | 1 | 207 | 4162051 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === NEED BIG BUCKET TO CHANGE CUTOUT === CALLED FOR BIG BUCKET === REPLACED CUTOUT POWER OK//COD 1// VER/DBM
17247 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-03-07 12:33 | 2016-03-07 16:00 | 1 | 207 | 4823971 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ACROCC CREEK PICKUP ONLY GOOD POLE ALREADY FIBER T BR 7.2 COD-1 ISO TF 38831109000038 . VER/HFP L3/HFP
17248 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-06-19 13:43 | 2009-06-19 17:10 | 1 | 207 | 56326-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP WR # 30378070 // BAD U.G. SERVICE .LOW VOLTAGE ON ONE LEG AT THE HOUSE AND GOOD VOLTAGE AT THE POLE. CALLED FOR CREW. SEND TO B. LYNCH RELEASED BY CREW 078S04 COD-1 L3/HFP IDC XXXX
17249 | Hazard | 3309302 | VICCO | JEFF | 2010-12-14 07:28 | 2010-12-14 10:55 | 1 | 207 | 66423-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 SERV BURNED INTO == AT WEATHER HEAD == CHANGED SERV FROM 2/3 TO 1/0 == POWER OK//VER/CRB IDC XXXX
17250 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-06-29 11:48 | 2008-06-29 15:15 | 1 | 207 | 59320-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD 19.9 CUTOUT VER/PDP IDC XXXX
17251 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-03-17 03:46 | 2018-03-17 07:13 | 1 | 207 | 4021391 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830211000034 has a broke tran c/o --(marked driveway w/yellow ribbon)-crew req -ds031718 Released by crew 078S01/crew on site/FETR0745/vem/repairs made and power restored to all cust 0713/please close ticket/thanks/vem
17252 | Hazard | 3303902 | LESLIE | WOOTON | 2016-02-06 11:48 | 2016-02-06 15:15 | 1 | 207 | 4680751 | 207 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION TRANSFORMER PULL APART(SERV. END)REPAIR CONNECTION//EPON TRANSFORMER AT 15 :00 AND CLOSE AT 15:15// VER/ ADH
17253 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-02-18 17:38 | 2011-02-18 21:05 | 1 | 207 | 59000-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === CUST SAID BE ALL RIGHT TO CHANGE IN DAY LIGHT === GOES TO A SHOP == MADE OPS ORDER TO WORK OFF OF 031878607 RELEASED BY CREW 077S03//VER/CRB IDC XXXX
17254 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-11-02 09:03 | 2010-11-02 12:30 | 1 | 207 | 50883-1 | 207 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | TIME OF DAY METER IS BAD JAMES HOLIDAY HAS METER ORDERED AND WILL FIX THIS WHEN METER ARRIVES. VER/KEP L3/KEP IDC XXXX
17255 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-11-21 23:51 | 2022-11-22 03:18 | 1 | 207 | 4170771 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 19.9 cutout on pole 29-58broke 7200 cutout on pole 29-58
17256 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-02-04 04:53 | 2016-02-04 08:20 | 1 | 207 | 4674211 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK IN THE AM 2-4-16 REPLACED BAD CUTOUT DOOR./ VER/AWD
17257 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2016-06-28 16:11 | 2016-06-28 17:20 | 3 | 69 | 4496561 | 207 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I REPLAQCED A SPLIT BOLT CONNECTOR ON THE NEUTRAL AT THE WEATHERHEAD. VER/AWD
17258 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-01-16 13:18 | 2016-01-16 16:45 | 1 | 207 | 4625671 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 72 CUT OUT///REPLACE CUTOUT// VER/ ADH
17259 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-10-16 21:05 | 2011-10-16 22:14 | 3 | 69 | 4989171 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT. CC = 3. VER/SDB IDC XXXX
17260 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-07-31 17:03 | 2019-07-31 20:30 | 1 | 207 | 4818881 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 376-B-43. transformer replaced.. power restored @ 20:30
17261 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-06-08 19:42 | 2015-06-08 23:09 | 1 | 207 | 4536931 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BAD TRANSFORMER CREW ENROUTE RELEASED BY CREW 074S02// VER/ ADH
17262 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-12-11 13:03 | 2018-12-11 16:30 | 1 | 207 | 4552951 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | replace service drop L3/HFP
17263 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-02-22 07:48 | 2008-02-22 08:57 | 3 | 69 | 66165-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007904//FAILED CUTOUT//COD 3,,,,I CHANGED CUTOUT AND GOT LINE BACK ON// VER/DBM IDC XXXX
17264 | Whitesburg | 3401301 | FLEMING | NEON | 2010-09-27 15:23 | 2010-09-27 18:50 | 1 | 207 | 54317-1 | 207 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA IS BAD WILL NEED TRANSFORMER CUTOUT AND T BRACKETT BIG BUCKETT REPLACED TRANSFORMER //VER/CRB IDC XXXX
17265 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-03-08 08:33 | 2017-03-08 12:00 | 1 | 207 | 4534641 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ATTEMPTED TO CALL CUST BACK //CUTOUT BROKE//MAKING REPAIRS//CUTOUT REPLACED//RESTORED AT 12:00//COMPLETE//EM VER/HFP L3/HFP
17266 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-01-07 08:21 | 2022-01-07 11:48 | 1 | 207 | 4318881 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Released by crew 074S03Loose stirrup on bank of xmfrs// replaced and restore @11:48.
17267 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-02-24 14:11 | 2011-02-24 15:20 | 3 | 69 | 60770-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED//VER/CRB IDC XXXX
17268 | Pikeville | 3413402 | GARRETT | LACKEY | 2013-12-30 17:49 | 2013-12-30 21:16 | 1 | 207 | 4213721 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 1 CUST OUT DUE TO POLE 64-109 LAYED OVER AND PULLED SERVICE DROP LOOSE. WE HAVE A TEMPORARY GUY WIRE INSTALLED TO A TREE. SERVICE DROP REPAIRED. SEND COPY TO ENG PIKEVILLE NEED TO INSTALL ANCHOR MAY WANT TO REMOVE TWO TRANSFORMERS CUST NOT USING THREE PHASE. CUST NEXT DOOR MAY HAVE CAUGHT DROP WITH A BACKHOE//EMAILED TO ENGINEERING// VER/DBM
17269 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-09-30 01:07 | 2008-09-30 02:16 | 3 | 69 | 52068-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202202/// CUTOUT BURNED UP. REPLACED CUTOUT DOOR IDC XXXX
17270 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2010-03-12 18:08 | 2010-03-12 21:35 | 1 | 207 | 65800-1 | 207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT//COD 1// VER/DBM IDC XXXX
17271 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-04-24 07:21 | 2008-04-24 10:48 | 1 | 207 | 53706-1 | 207 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3008702//SENT TO IKE GILKERSON//IKE TO REPAIR//IKE TO REPAIR RELEASED BY CREW 078S07//VER/CRB IDC XXXX
17272 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-03-17 11:16 | 2020-03-17 14:42 | 1 | 206 | 4485241 | 206 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Customer had a hot leg almost burndt into at his weatherhead, replaced bad connection @1442. Only 1 customer was affected.
17273 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-10-08 14:04 | 2014-10-08 17:30 | 1 | 206 | 4574521 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR 25KVA, CREW IS ON SITE NOW RELEASED BY CREW 077S12 REPLACED 25 KVA POWER RESTORED AT 17:30 VER/CRB
17274 | Hazard | 3302703 | HAZARD | HAZARD | 2008-01-03 08:14 | 2008-01-03 09:57 | 2 | 103 | 53137-1 | 206 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 120 VOLT SECONDARY RISER CONNECTOR BURNED INTO AT XFMR PLEASE SEND EMAIL TO TECH TO CHECK LOAD NEIGHBOR ADDED HEAT PUMP//3302703//VER/CRB IDC XXXX
17275 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-12-12 07:24 | 2013-12-12 10:50 | 1 | 206 | 4155471 | 206 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE HOTLEG BAD ON UNDERGROUND SERVICE, BAD LEG IS ALREADY ISOLATED ON POLE & IN METERBASE. LINECREW REQUIRED AND POWERTEMP. RELEASED BY CREW 078S11 SENT COPY TO BOBBY REYNOLDS AND DID MD VER/SEF L3/HFP HFPC CDC89
17276 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2014-03-26 14:19 | 2014-03-26 17:45 | 1 | 206 | 4527101 | 206 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SECONDARY === REPLACED SECONDARY AND CHANGE METER BAD DAIL ON METER === POWER OK VER/SEF
17277 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2014-08-08 07:01 | 2014-08-08 10:27 | 1 | 206 | 4341291 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED LEAKING TRANSFORMER.//COD 1// VER/DBM
17278 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2019-02-18 12:04 | 2019-02-18 15:30 | 1 | 206 | 4804041 | 206 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on pole, repaired
17279 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-08-04 13:51 | 2014-08-04 17:17 | 1 | 206 | 4330201 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK//COD 1// VER/DBM
17280 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-01-17 16:36 | 2012-01-17 18:19 | 2 | 103 | 4270381 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD LEAD. ////VER/CRB IDCC PN7 XXXX
17281 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-06-23 07:59 | 2010-06-23 11:25 | 1 | 206 | 55477-1 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR# 35691888 // POLE 163-140 BAD 25KVA NO TRUCKS NEED CUTOUT TO RELEASED BY CREW 078S08//COD 1// VER/DBM IDC XXXX
17282 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-01-30 19:04 | 2009-01-30 22:30 | 1 | 206 | 52943-1 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ANOTHER CURRENT LIMITING FUSE BURNED COMPLETELY UP. NO OTHER TROUBLE. / COD-1 VER/LDA
17283 | Hazard | 3420001 | SOFT SHELL | VEST | 2022-01-22 14:02 | 2022-01-22 15:45 | 2 | 103 | 4396501 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke refused and power restored at 15:45
17284 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-05-13 07:12 | 2022-05-13 08:55 | 2 | 103 | 4884931 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp was broke,,,, repairs made,,, complete
17285 | South Williamson | 3411401 | DEWEY | INEZ | 2016-06-16 01:45 | 2016-06-16 03:28 | 2 | 103 | 4359541 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO WIRE DOWN//CUTOUT BROKE ON POLE 769-126//GOING TO REPLACE CUTOUT//CUTOUT REPLACED//RESTOREDAT 03:28//COMPLETE//EM VER/ARN
17286 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-02-13 12:00 | 2014-02-13 13:43 | 2 | 103 | 4382721 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT ON POLE 989-B-291. HAD TO OPEN FUSE ON POLE 989-A-139 AT 13:01 TO CHANGE BAD CUTOUT. SHOULD BE BACK ON BY 14:00. OPENED FUSE AT 13:01 AND CLOSED BACK IN AT 13:43. ENTERED MD // VER/HFP L3/HFP IDC XXXX
17287 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-06-03 15:10 | 2008-06-03 16:53 | 2 | 103 | 55071-1 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE ON POLE 402-122 I WILL NEED ONE MAN AND A CUTOUT TO REPAIR AND THIS IS MANUAL VER/HFP IDC XXXX
17288 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-01-11 06:04 | 2017-01-11 09:30 | 1 | 206 | 4285791 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKE.REPLACED--IN AT 09:30--ALLGOOD--DS011117 38830306000135 VER/AWD L3/HFP HFPC CDC96
17289 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2021-08-11 16:42 | 2021-08-11 20:08 | 1 | 206 | 4039911 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required ,,,254-6039 bad 15 kva xfr ,,truck to pole Released by crew 078S05//arrived RM replaced xfm volatge 120,121.242 /customer was getting high volatge before but is good now please close tic RM
17290 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-04-13 15:12 | 2022-04-13 16:55 | 2 | 103 | 4758541 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout at 269-9. replaced and restored power at 16:55
17291 | Whitesburg | 3312902 | JENKINS | JENKINS | 2019-09-09 08:49 | 2019-09-09 12:15 | 1 | 206 | 4994531 | 206 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad connection in service drop splice burnt into.made repairs restored power at 12:15..
17292 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-04-25 15:49 | 2013-04-25 19:15 | 1 | 206 | 4048141 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 302C108 ONLY ONE CUST. OUT RELEASED BY CREW 075H04..CREW ON SITE.P.HICKS..ALL POWER RESTORED 19:15.P.HICKS//COD 1// VER/DBM IDC XXXX
17293 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2019-09-16 10:47 | 2019-09-16 12:30 | 2 | 103 | 4023651 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had transformer off at pole 187-c-156 from 11:45 to 12:30 to replace bad cutout arrester and arm repairs made everything ok.
17294 | Pikeville | 3401001 | ELWOOD | DORTON | 2019-05-29 17:06 | 2019-05-29 20:32 | 1 | 206 | 4371361 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 239-266 will replace/// Replaced broken cutout and restored service @ 20:32
17295 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-07-05 17:29 | 2015-07-05 20:55 | 1 | 206 | 4724581 | 206 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | PART POWER ONE HOT LEG NO VOLTAGE.BLANKED METER BASE.CREW NEEDS TO PUT POWER TEMP. RELEASED BY CREW 078S05,REPAIRED HOT LEG CUST RESTORED @ 0855 PLEASE CLOSE TICKET.BT VER/KEP
17296 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-12-14 17:59 | 2013-12-14 21:25 | 1 | 206 | 4162081 | 206 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SQWEEZON CONNECTION ON TRANSFORMER BURNT UP. WILL REPLACE...CUSTOMER IS TOTAL ELECTRIC, HEAT PUMP, ADDITIONAL ELECTRIC HEAT, LARGE HOUSE, ..15 KVA XFMR, AND LONG, 1/0 UG SERVICE,..PLEASE SEND COPY TO DOUG CHRISTAIN, MAY WANT TO UPGRADE FACILITIES..HAS BURNT SEC. LEEDS INTO HERE BEFORE..P.HICKS VER/HFP L3/HFP
17297 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-03-23 18:24 | 2017-03-23 21:50 | 1 | 206 | 4581231 | 206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | METER BLANK//CUTOUT BROKE ON 818-180//REPAIRS MADE//RESTORED AT 21:50//COMPLETE//EM VER/KEP
17298 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-01-31 10:11 | 2018-01-31 13:36 | 1 | 205 | 4787181 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer no 220/ 1336/ ISO 37830236000005/ COD 1
17299 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-10-05 15:50 | 2017-10-05 19:15 | 1 | 205 | 4413381 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED TRUCKS OK NEED 25KVA RELEASED BY CREW 078S03,REPAIRS MADE ALL CUST RESTORED @ 1915 PLEASE CLOSE TICKET THANKS.BT 38830268D00148 VER/AWD L3/HFP XXXHFP
17300 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2016-06-16 17:00 | 2016-06-16 20:25 | 1 | 205 | 4365001 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 20-5645 BAD 12 KV CO. WILL NEED FLAGGERS. NRO ALSO RELEASED BY CREW 078S07,,CREW ON SITE,,NRO ISSUED,,,ALL REPAIRS COMPLETE,,ALL POWER RESTORED VER/CRB
17301 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-12-08 01:15 | 2010-12-08 04:40 | 1 | 205 | 64246-1 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE OUT. BROKEN CUTOUT. -- POWER RESTORED. //VER/GAH IDC XXXX
17302 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-10-11 17:05 | 2013-10-11 20:30 | 1 | 205 | 4931031 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1099-66 BAD 10KVA TRANS NEED 25KVA TRUCK TO POLE ALSO PRI. NU. LOOP ON SAME POLE BURNT OPEN NEEDS REPAIRED // TACKETT & HICKS & MCCOY,,CREW ON SIGHT //COMPLETE PLEASE CLOSE TICKET COD-1 ISO TF 39831099D40066 VER/HFP L3/HFP
17303 | Whitesburg | 3312901 | JENKINS | KONA | 2008-12-05 19:55 | 2008-12-05 23:20 | 1 | 205 | 54784-1 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3312901// 2/3 SERVICE DROP BURNT INTO REPLACED DROP VER/KEP L3/KEP IDC XXXX
17304 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2022-11-15 14:33 | 2022-11-15 15:14 | 5 | 41 | 4145251 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | contractor reports pole 1123-360 iis on fire.. cracked cutout .. changed cutout. complete..
17305 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-07-26 11:09 | 2022-07-26 14:34 | 1 | 205 | 4583441 | 205 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke in service drop, will be making repairs
17306 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-02-24 07:35 | 2016-02-24 11:00 | 1 | 205 | 4753731 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY 1 CUSTOMER OUT TILL FUSE 518 OPENED AT 0836_GROUNDED AND TAGGED FOR TIM THOMAS ON 875-518..OPEN CUTOUTS AT 836GROUNDED AND TAGGED FOR TIM THOMAS ON 875-518..OPEN CUTOUTS AT 836.. RELEASED BY CREW 076S01// REPAIRS MADE RESTORED POWER AT 1100 // 30T FUSES ON POLE 518//MADE MDC TO SHOW L/F AS 30T// VER/CRB
17307 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-07-14 06:05 | 2018-07-14 09:30 | 1 | 205 | 4771881 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | spoke with customer//meter is blank//---c/o broke--replced-allgood-ds071418
17308 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-11-19 08:29 | 2013-11-19 11:54 | 1 | 205 | 4056231 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BURNT UP CUTOUT DOOR VER/CRB IDCC FEC49 XXXX
17309 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-12-27 06:49 | 2011-12-27 10:14 | 1 | 205 | 4203881 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REW REQUIRED--TRUCK TO POLE--BAD CUTOUT RELEASED BY CREW 078S07//PT ON SITE//COMPLETE AT 10:14 PRT ALL POWER RESTORED// ////VER/CRB IDC XXXX
17310 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2020-06-15 05:15 | 2020-06-15 08:40 | 1 | 205 | 4019661 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.. cutout gate burnt up. replaced gate power restored @ 08:40
17311 | Paintsville | 3410602 | E.PRESTON | LANCER | 2021-03-09 10:10 | 2021-03-09 10:51 | 5 | 41 | 4318151 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | OPENING TO SAFLEY REPLACE GUY WIRE // COD 5 // OFF@1010 ON@1051 // OFF AT 10:10,SHOULD TAKE LESS THAN AN HOUR
17312 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-12-17 20:38 | 2013-12-18 00:03 | 1 | 205 | 4170841 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CHECKED VOLTAGE AT METER BASE, 10 VOLTS ON ONE SIDE AND 5 VOLTS ON THE OUTHER. NEED LINE CREW. RELEASED BY CREW 078S01/CREW ON SITE/ONE CUST OUT/INSTALLING TEMP OVERHEAD/FETR0130 12-18-13/VEM/INSTALLED TEMP OVERHEAD/ POWER RESTORED 0003/PLEASE COPY TICKET TO B REYNOLDS AND L RAYBURN/THANKS/VEM //VER/GAH L3/HFP
17313 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-05-31 16:30 | 2019-05-31 19:55 | 1 | 205 | 4401051 | 205 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral & hot leg into in 2/3 service , there has been a house fire here in last few days . service has got hot neutral & hot leg got together . repaired service . only 1 cust. with part power .
17314 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-01-09 10:32 | 2011-01-09 13:57 | 1 | 205 | 60103-1 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE HANGING DOWN STS BAD TRANSFORMER ON POLE 1108-75 GOING TO MOVE SERVICE TO POLE 1108-653. GOT HELP COMMING WHEN THEY CLEAR UP ON TROUBLE//MAP DESC MADE//VER/CRB IDC XXXX
17315 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-12-05 14:19 | 2013-12-05 15:00 | 5 | 41 | 4101881 | 205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT ON 525-178, APR AT 1500 CLOSE TICKET. DEW PLEASE SEND TO MAPPING FUSE ON 525-178 IS NOT ON MAPS 25T FUSE.//ISO 38830525000178//COD 5//MD FILED// VER/DBM L3/HFP
17316 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-01-20 22:10 | 2009-01-21 01:34 | 1 | 204 | 58705-1 | 204 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED SPLICE IN SERVICE DROP VER/ARN L3/KEP
17317 | South Williamson | 3411401 | DEWEY | INEZ | 2018-08-18 15:37 | 2018-08-18 16:45 | 3 | 68 | 4970031 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke and arrestor blown on pole 768-39//i replaced cutout and arrestor//restored at 16:45//complete//e L3/HFP
17318 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-07-27 20:17 | 2008-07-27 21:25 | 3 | 68 | 60892-1 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601 /// CUTOUT DOOR BURNT UP 8T FUSE VER/JHM IDC XXXX
17319 | Hazard | 3303901 | LESLIE | HYDEN | 2012-01-21 14:48 | 2012-01-21 16:30 | 2 | 102 | 4280931 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT/// REPLACED XFMR CUTOUT, POWER RESTORED. ///VER/CRB IDC XXXX
17320 | Hazard | 3308001 | JACKSON | S.JACKSON | 2016-09-23 15:50 | 2016-09-23 16:24 | 6 | 34 | 4921091 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOT BAD 50 KVA 7200 TRANSFORMER ON POLE 38831083D30487 OPEN TRANSFORMER BANK AT 1550 AND CLOSED AT 1624 38831083D30487 6 VER/AWD
17321 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-02-17 15:32 | 2020-02-17 16:40 | 3 | 68 | 4413501 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Replacing bad xfer rstored @ 1640 L3/HFP
17322 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-07-28 20:17 | 2013-07-28 21:25 | 3 | 68 | 4601521 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CHANGED OUT BAD CUTOUT VER/ARN IDC XXXX
17323 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2019-02-11 13:19 | 2019-02-11 16:43 | 1 | 204 | 4778121 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | enroute eta 14:30 bad cutout on p# 429-297 crew required mopads to pole 50ft off driveway Released by crew 078H06
17324 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-05-05 18:21 | 2013-05-05 21:45 | 1 | 204 | 4074031 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT & XFMR ON POLE 447-186, REPLACED CUTOUT & XFMR ,RESTORED POWER AT 21 :45. THIS XFMR SERVES METER # 533104330.// MAP DIS ENTERED// VER/TOM L3/TOM IDC XXXX
17325 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-03-11 09:21 | 2017-03-11 12:45 | 1 | 204 | 4548121 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER 0931---BROKE TRAN C/O--REPLACED--ALLGOOD--DS031117 38830308A40161 VER/AWD
17326 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-12-04 16:26 | 2009-12-04 17:34 | 3 | 68 | 54721-1 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK// CORRECT POLE# FOR CUSTOMER IS 38830044C24531//ISO//COD 3 PER SERVCER//MD FILED ON MISSMAPPED PREMISE// VER/DBM IDC XXXX
17327 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2019-01-21 17:23 | 2019-01-21 18:31 | 3 | 68 | 4701281 | 204 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | insulink gone bad. repairs made. pls close. tre L3/HFP
17328 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-05-09 21:11 | 2014-05-10 00:35 | 1 | 204 | 4679861 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT GATE BURNT UP..PATROLED LINE AND REPLACED GATE AND FUSE.ALL POWER RESTORED @ 0035 HRS .P.HICKS VER/ARN
17329 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-04-22 15:32 | 2021-04-22 16:40 | 3 | 68 | 4471991 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | going to install new down guy on pole to tryto straighten pole will have xfmr off while doing so LRM send copy to pat to get ahold of phone co LRM//SENT TO TE CH
17330 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2014-06-11 12:06 | 2014-06-11 15:30 | 1 | 204 | 4047361 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT 19.9KV TRUCK ACCESSABLE MWL. BAD C/O ON POLE 351-384, WILL BE MAKING REPAIRS. CHANGED C/O AND CLOSED BACK IN AT 15:30. //CAN CLOSE MWL VER/HFP L3/HFP
17331 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-12-17 06:13 | 2008-12-17 09:37 | 1 | 204 | 59391-1 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3008701 -NEED CREW RELEASED BY CREW 078S07/CREW ON SITE/FETR1000/REPAIRED DROP/RESTORED POWER 0937/PLEASE COPY TICKET TO ENG /NEED WORK ORDER TO RELOCATE DROP/VEM//SENT TO S MARTIN DBM// VER/DBM L3/KEP IDC XXXX
17332 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-05-16 20:20 | 2012-05-16 21:11 | 4 | 51 | 4802031 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE OUTBROKE CUTOUT ///VER/CRB L/3 CRB IDC XXXX
17333 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2019-11-27 12:36 | 2019-11-27 16:00 | 1 | 204 | 4079161 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 351-177,,riser came out of xfr lugs ,,,,repaired lugs complete
17334 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-07-16 14:06 | 2021-07-16 17:30 | 1 | 204 | 4920821 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | vines caused fuse to blow on pole 47-C-392// bad 50kva transformer
17335 | South Williamson | 3200302 | BELFRY | TOLER | 2012-07-09 11:43 | 2012-07-09 13:25 | 2 | 102 | 4642011 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BOKE//COD 2 IDC XXXX
17336 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-01-25 17:17 | 2014-01-25 18:25 | 3 | 68 | 4312811 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BAD AT POLE 402-11, CHANGED OUT AND CLOSED BACK IN AT 18 25. COD-3 ISO TF 37830402D00011 VER/HFP L3/HFP
17337 | Pikeville | 3421002 | BREAKS | GRASSY | 2019-01-10 00:07 | 2019-01-10 01:15 | 3 | 68 | 4654411 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will try to get bucket in to change///Changed bad cutout and restored service @ 1:15
17338 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-04-29 17:48 | 2018-04-29 19:30 | 2 | 102 | 4289241 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIS-MAPPED CUST PREMISE //MADE MD TO SHOW TRANS ON POLE 37830016C00011 AND PREMISE MAPPED TO IT//COD 2// // 6t fuse out due to bad cutout. changed cutout closed 6t fuse in everything ok L3/HFP
17339 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2017-05-28 19:14 | 2017-05-28 20:05 | 4 | 51 | 4877351 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//L/F OPEN ON POLE 37830177D30498///// VER/DKM
17340 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2021-02-22 17:08 | 2021-02-22 18:50 | 2 | 102 | 4222901 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate burned up. Replaced and power restored at 18:50
17341 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2015-05-16 10:06 | 2015-05-16 11:48 | 2 | 102 | 4434881 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT REPAIRS MADE POWER RESTORED KWB/ ISO 38830042000171/ COD 2/ VER/BOW
17342 | Pikeville | 3421001 | BREAKS | CITY | 2018-02-25 12:39 | 2018-02-25 13:30 | 4 | 51 | 4881641 | 204 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open in secondary @ Xfm /// Repaired bad connection and restored service//COD 4 AFFECTED
17343 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-05-24 17:27 | 2010-05-24 19:09 | 2 | 102 | 50393-1 | 204 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED REPAIRED NEUTRAL//VER/CRB IDC XXXX
17344 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-05-01 22:27 | 2016-05-01 23:35 | 3 | 68 | 4155811 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 79-8 . BAD ARRESTER ON POLE 79-61 , ARRESTER IN CLEAR . CLOSED FUSE ON POLE79-8 @ 23:35 , POWER BACK ON . 3 CUST. ON XFMR . WILL NEED FLAGERS TO CHANGE ARRESTER , CAN WORK WITH BUCKET .// VER/ ADH
17345 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-08-12 12:51 | 2013-08-12 13:25 | 6 | 34 | 4654061 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND ARRESTOR ON XFRM POLE 70-3050//OPENED LINEFUSE ON 70-1565 TO CHANGE//APPX TIME ON 13:57////OPENED LF @ 12:51///PWR BACK ON @ 13:25///RMV //CO D 6// VER/DBM
17346 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2012-05-29 12:37 | 2012-05-29 16:01 | 1 | 204 | 4841021 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 XFORMER , NEED LINE CREW, TRUCKS TO POLE. NEED OIL BAG FOR XFORMER. RELEASED BY CREW 078S01/CREW ON SITE/FETR1630/VEM/REPAIRS MADE AND POWER RESTORED 1601/PLEASE CLOSE TICKET/THANKS/VEM COD-1 ISO TF 38830283000108 VER/HFP L3/HFP IDC XXXX
17347 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-11-19 19:13 | 2013-11-19 20:55 | 2 | 102 | 4058091 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE HAD BROKE. REPLACED FUSE AND POWER IS BACK ON.//COD 2// VER/DBM
17348 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-03-21 12:50 | 2018-03-21 13:24 | 6 | 34 | 4036521 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | opened line fuse @851-360 @ 12:50 TO MAKE SAFE.WE HAVE WIRE BURNT IN A STIRRUP ON POLE 851-161 MAKING REPAIRS NOW /// SEE 4034691 CUSTOMERS IN THAT ORDER NOT RESTORED UNTIL REPAIRS MADE IN THIS ORDER - 37 CUST // 6 CUST OFF FROM 1250 - 1324
17349 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-07-18 10:51 | 2013-07-18 14:15 | 1 | 204 | 4547811 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TOM CANTRELL REPORTS FUSE OPEN ON TRANSFORMER BANK. NO UNDERGROUND 19.9 ARRESTER ON TRUCK, CLEARED LIGHTING ARRESTER BUT POTHEAD IS NOT SEALED AT TOP AND APPEARS TO BE TRACKING TO GROUND FUSE WAS MELTED NOT BLOWN, NO SILICON TAPE OR CALCK ON TRUCK TO FIX TOP OF POTHEAD OR NEED NEW POTHEAD HOLD TAG ON POLE TAGGED TO DDC RELEASED BY CREW 078H08 GAVE PERM TO REMOVE DDC TAG AND TAG TO SELF VER/KEP IDCC CDC83 XXXX
17350 | Hazard | 3309302 | VICCO | JEFF | 2009-11-14 22:54 | 2009-11-15 00:02 | 3 | 68 | 57825-1 | 204 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTOR ON SECONDARY XFMR RISER VER/PDP IDC XXXX
17351 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-02-19 12:32 | 2014-02-19 14:14 | 2 | 102 | 4401411 | 204 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION MELTED APART AT WEATHERHEAD//I REWORKED BOTH HOT CONNECTIONS///RESTORED AT 14:12//COMPLETE//EM VER/KEP
17352 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-01-10 17:42 | 2009-01-10 18:50 | 3 | 68 | 54056-1 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3116702//STS WR# 28011301//3116702// 10T ME FUSE LINK BROKE//COD 3// VER/DBM L3/KEP IDC XXXX
17353 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2018-07-22 10:54 | 2018-07-22 11:45 | 4 | 51 | 4833731 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broke cutout, apr at 1145 close ticket
17354 | Hazard | 3303902 | LESLIE | WOOTON | 2016-06-21 19:28 | 2016-06-21 21:10 | 2 | 102 | 4401381 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE LINE FUSE ON POLE 415-10 .REPLACED CUTOUT CLOSED FUSE BACK @ 21:10 VER/CRB
17355 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-07-09 23:57 | 2010-07-10 01:05 | 3 | 68 | 64571-1 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT FAILED ON POLE 37830152000013 IDC XXXX
17356 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-12-29 15:17 | 2018-12-29 16:25 | 3 | 68 | 4613011 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on pole, power restored 16:25
17357 | Paintsville | 3401802 | INDEX | HOSPITAL | 2016-06-02 19:52 | 2016-06-02 21:00 | 3 | 68 | 4288451 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHANGING. VER/KEP L3/HFP XXXHFP
17358 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-05-13 22:07 | 2020-05-13 23:15 | 3 | 68 | 4833401 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | copper came loose out of hot line clamp on load side of 423-B-255 A phase.. will need to isolate cutout in order to make repairs. repairs made.., power restored @ 23:15 A phase 3 customers
17359 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2009-12-31 07:56 | 2009-12-31 11:20 | 1 | 204 | 51743-1 | 204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON THIS XFMR// AT 0827 , CALLED TIM HALL BAD CUT OUT ERIC MCKINNEY POWER RESTORED 1120 IDC XXXX
17360 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-11-26 08:25 | 2020-11-26 11:48 | 1 | 203 | 4724281 | 203 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 1 OF 3 FUSES OUT@XFR BANK///////NEED 1MAN,BUCKET,3 19.9 CUTOUTS.1 LOOKS BAD,WILL REPLACE ALL SINCE POWER IS ALREADY OUT////REPLACED 3 CUTOUTS&ARRESTORS,CLOSED&RESTORED@11:48
17361 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-10-06 14:07 | 2011-10-06 17:30 | 1 | 203 | 4952881 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA ON POLE 38830206C02153, TRUCK OK, MAY HAVE TO CUT SMALL TREES OUT OF WAY. SEND TO B FRALEY RELEASED BY CREW 078S05 VER/KEP IDC XXXX
17362 | Hazard | 3309301 | VICCO | REDFOX | 2021-08-05 09:16 | 2021-08-05 12:39 | 1 | 203 | 4007121 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse out, bad xfmr , power restored
17363 | South Williamson | 3202201 | LOVELY | LOVELY | 2015-09-04 13:47 | 2015-09-04 17:10 | 1 | 203 | 4198061 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION FAILED ON POLE723-A-17 THAT FED SOME D D LIGHTS AND ROAD SIGN FOR SCHOOL ZONE REPLACED CONNECTION RESTORED POWER AT17:10 VER/CRB
17364 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-03-31 06:17 | 2017-03-31 09:40 | 1 | 203 | 4600551 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT IS BROKEN ON POLE 204-45, CALLING FOR HELP. POWER RESTORED COD-1 ISO LF 37830204000045 VER/HFP L3/HFP
17365 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-11-05 09:19 | 2019-11-05 12:42 | 1 | 203 | 4293141 | 203 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | customer had connection burnt into on xfm. pole..
17366 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2010-10-21 18:02 | 2010-10-21 21:25 | 1 | 203 | 61931-1 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RISER BURNT OUT OF HOT LINE CLAMP ON TOP OF LATERAL CUTOUT....WILL HAVE TO CLIMB & REPAIR....CALLED FOR ONE MAN TO HELP....FETR 22:00....//......REPAIRS MADE.....POWER ON @ 21:25.....JRV & E MATNEY.....10/20/10 COD-1 VER/HFP L3/HFP IDC XXXX
17367 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-05-04 20:02 | 2012-05-04 23:25 | 1 | 203 | 4745381 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 TRANSFORMER NEED 1 MAN BIG BUCKET POWER RESTORED@23:25 IDC XXXX
17368 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-12-09 19:08 | 2013-12-09 22:31 | 1 | 203 | 4142241 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S01// BAD 15 KVA NEEDS REPLACED WITH A 25 KVA-NEED CUTOUT--MATERIAL HANDLER OK-4MAN PRC CREW 2 MEN TO FLAG RELEASED BY CREW 078S07/CREW LOADING NEW XFMR/FOREMAN ON SITE/FETR2300/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2231/PLEASE CLOSE TICKET/THANKS/VEM//ISO//COD 1// VER/DBM L3/HFP
17369 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-12-21 10:04 | 2012-12-21 13:27 | 1 | 203 | 4499481 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE ////VER/CRB L/3 CRB
17370 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-07-21 08:34 | 2010-07-21 11:57 | 1 | 203 | 54841-1 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR TO RE-FUSE,MAY HAVE TO CHANGE MTRXFR CUTOUT TO REPLACE,,,LIFTED TAP AT 1081-176,RESTORED AT 11:57 AFTER REPLACING CUTOUT ON POLE 1081-105//COD 1//ISO 38821081D00176// VER/DBM IDC XXXX
17371 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2015-04-26 20:20 | 2015-04-26 23:43 | 1 | 203 | 4368091 | 203 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | B AD SEC. UNDERGROUND SEND CREW WITH TEP. RELEASED BY CREW 078S08/CREW ON SITE/SHOULD HAVE FULL POWER BY 0030/VEM/POWER TEMP INSTALLED /FULL POWER TO CUST 2343/PLEASE COPY TICKET TO B REYNOLDS FOR PERMANENT REPAIRS/THANKS/VEM COD-1 VER/KEP
17372 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-08-11 14:22 | 2015-08-11 17:45 | 1 | 203 | 4124061 | 203 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | WILL NEED 1 MAN AND BIG BUCKET . ( VIRGIL HURTS BUCKET ) WILL NEED EXTRA REACH . BAD CUTOUT IS ON POLE 173B-155 THIS IS PRIMARY MEETERING POLE . CLOSED FUSE @ 17:45// VER/ ADH
17373 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-04-20 13:42 | 2011-04-20 17:05 | 1 | 203 | 61299-1 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE DOWN AND BURNT POLE THREE FORTHS OF THE WAY IN TWO. NO TRUCK ACCESS. DUTY SUPERVISOR NOTIFIED AND CREW IS ENROUTE FROM SALYERSVILLE TO MAKE REPAIRS. HOT LINE CLAMP LIFTED AT 904-54 AND GROUND PLACED. REPAIRS COMPLETE. RESTORED @ 17:05. SH//COD 1//ISO 38830904000054// VER/DBM IDC XXXX
17374 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-11-05 11:22 | 2009-11-05 14:45 | 1 | 203 | 62960-1 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ,WILL NEED BIG BUCKET TO MAKE REPAIRS RELEASED BY CREW 077S11 MD FILED CUSTOMER MAPPED TO WRONG TRANS VER/KEP L3/KEP IDC XXXX
17375 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-08-07 14:12 | 2020-08-07 17:35 | 1 | 203 | 4299631 | 203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t fuse out due to cutout door burnt into i dont have a door like this. we will be replacing cutouts replaced 3 cutouts fused up everything ok.
17376 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-03-15 10:59 | 2019-03-15 14:22 | 1 | 203 | 4988591 | 203 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection onxfmr pole, repaired connection
17377 | Paintsville | 3401802 | INDEX | HOSPITAL | 2019-01-25 14:07 | 2019-01-25 17:30 | 1 | 203 | 4722341 | 203 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug , roger maynard en route..put portable xfmr on meterbase, underground to be replaced later. cust. has power now.. ¦¦ L3/HFP
17378 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-08-23 15:50 | 2018-08-23 19:12 | 1 | 202 | 4994041 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED L/F 38830983000048 TO SAFELEY REPLACE CUTOUT ON POLE 38830983000096//cutout failed on 983-96.replaced cutout. restored power at 19:12
17379 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-10-31 08:11 | 2020-10-31 09:52 | 2 | 101 | 4609141 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Center fuse blown in xfmr bank will check// Fuse link was broke inside cutout door. Installed new fuse and restored @09:52
17380 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2015-04-21 13:59 | 2015-04-21 15:40 | 2 | 101 | 4348961 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 21-84 BAD CUTOUT CREW REQUIRED/ POLE 21-84 BAD CUTOUT CONN BROKE TRUCK TO POLE NEED CUTOUT/ POLE 21-84 BAD CUTOUT CONN BROKE TRUCK TO POLE NEED CUTOUT RELEASED BY CREW 078S08,,CREW ON SITE,,REPLACED CUTOUT,,ALL POWER RESTORED/ ISO 38830021D20084/ COD 2/ VER/BOW
17381 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-01-08 06:59 | 2021-01-08 08:40 | 2 | 101 | 4855641 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester failed causing fuse to blow. arrester cut in clear, power restored
17382 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-05-18 20:09 | 2018-05-18 21:50 | 2 | 101 | 4373851 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse back in at 21:50
17383 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-02-28 13:19 | 2022-02-28 15:00 | 2 | 101 | 4552901 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 38821057D00129//COD 2//BROKEN C/O ON PLE 1057-129///REPAIRS MADE AND RESTORED @ 15:00
17384 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-09-14 17:19 | 2009-09-14 19:00 | 2 | 101 | 56482-1 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT. .......DAH VER/KEP L3/KEP IDC XXXX
17385 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-04-12 19:24 | 2022-04-12 21:05 | 2 | 101 | 4755191 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout.changing.p-851-339
17386 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-03-14 13:17 | 2014-03-14 16:39 | 1 | 202 | 4492421 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE////////BAD 15 KVA 19.9 XFR,NEED MAT BUCKET,CREW(1 MAN)//////////REPLACED AND RESTORED//COD 1// VER/DBM
17387 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-02-25 18:49 | 2009-02-25 22:11 | 1 | 202 | 51551-1 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 FUSE OUT IN 3 PHASE BANK--922-1377--SEND TO V MULLINS//2 BAD TRANSFORMERS IN BANK--LEAKING OIL--37/5 RELEASED BY CREW 078S07/CREW ON SITE/FETR2300/VEM/CHANGED TWO XFMRS/POWER RESTORED 2211/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
17388 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-07-31 12:23 | 2022-07-31 15:45 | 1 | 202 | 4642501 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva trucks ok Released by crew 078S03///Complete BR
17389 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-11-14 19:35 | 2020-11-14 22:57 | 1 | 202 | 4676281 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfm fuse blown on pole 195-1///Bad 25KVA 7200 xfm ///Can use truck will need line crew///Changed bad xfm and restored service @22:57//cod 1//ISO
17390 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-06-15 10:48 | 2015-06-15 14:10 | 1 | 202 | 4573301 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUTON PRIMARY METERING POLE--CALLED FOR BIG BUCKET RELEASED BY CREW 077S06////ON SITE CHANGING CUT OUT////OFF AT 1340 AND BACK ON AT 1410// VER/ ADH
17391 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-04-24 20:28 | 2018-04-24 22:09 | 2 | 101 | 4275281 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout L3/HFP
17392 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2017-08-16 20:04 | 2017-08-16 21:45 | 2 | 101 | 4269411 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 1064-C-114 REPLACED CUTOUT RESTORED POWER AT 21:45 38821064C00114 VER/AWD
17393 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-06-13 10:54 | 2009-06-13 12:35 | 2 | 101 | 60404-1 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE DOOR BURNED UP, SEND TICKET TO ENGINEERING TO GET TELEPHONE TO RAISE CABLE CROSSING ROAD WIRE IS LOW VER/KEP L3/KEP
17394 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-09-18 19:50 | 2018-09-18 21:31 | 2 | 101 | 4128611 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on 770D150.i opened line fuse on 770D70 at 21:06.made repairs.restored power at 21:31.line fuse on 770D70 is a 12..//iso 38820770D00070//cod 2
17395 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2013-06-09 06:28 | 2013-06-09 09:50 | 1 | 202 | 4241131 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT // NEED 1 MAN @ BIG BUCKET/// CUTOUT CHANGED// POWER IS RESTORED VER/KEP IDC XXXX
17396 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-02-07 10:18 | 2022-02-07 12:00 | 6 | 102 | 4452811 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I replaced a damaged secondary connection and replaced a XFMR lead. XFMR off at 11:40 closed back in a 12.
17397 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-11-25 18:33 | 2019-11-25 21:55 | 1 | 202 | 4067381 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection made repairs full power restored at 21:55/ ISO 38830478D10396/ COD 1
17398 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-06-23 07:14 | 2012-06-23 10:36 | 1 | 202 | 4952891 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED ARRESTER AND REFUSED XMF APR CLOSE TICKET
17399 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-04-29 19:19 | 2010-04-29 21:00 | 2 | 101 | 52912-1 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TRANSFORMER . CUST AGREED TO WAIT UNTIL TOMORROW MORNING TO CHANGE. I WILL CREATE AN IW 70 ORDER TO CHANGE TRANS AND DROP TO DAVE SAMMONS. THIS ORDER COMPLTED. COMPLTED 21:00 RELEASED BY CREW 074S11//VER/CRB IDC XXXX
17400 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-03-01 20:37 | 2018-03-01 23:59 | 1 | 202 | 4900631 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout on 38831056C00101 failed opened line fuse on 38831056A00026 to make repairs at 22:48 NO ADDITIONAL CUSTOMERS made repairs restored power at 23:59/ ISO 38831056C00101/ COD 1
17401 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-02-13 01:58 | 2022-02-13 05:00 | 2 | 182 | 4478431 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | line fuse out on pole 37830482C00207 // cutout cracked, had to open xfmr on same pole in order to replace// opened @ 0440 closed @ 0500 //cod 1 +1
17402 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-04-09 10:03 | 2022-04-09 13:25 | 1 | 202 | 4743161 | 202 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | hotleg burned in 2 in a splice, will be making repairs// XCO also failed, made repairs and restored customers
17403 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-02-18 09:03 | 2017-02-18 12:25 | 1 | 202 | 4405781 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CALLED 911 WITH ETA: 0945, SERVICE DROP BURNT DN MIDSPAN, REPLACED SERVICE APR CLOSE TICKET. OPENED XMF AT 0950 CLOSED AT 1225 CLOSE TICKET 38830453000183 VER/AWD // SEE DUP FOR XFMR OUTAGE L3/HFP XXXHFP
17404 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-12-17 09:28 | 2010-12-17 12:50 | 1 | 202 | 53189-1 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN WIRE SECONDARIES BURNT DOWN....ONE HOT LEG DOWN....BURNT DOWN UNDER A CONNECTION ON POLE 32-C-47...HAVE BURNT PHONE CABLE DOWN ALSO....WILL PULL XFMR OFF ON POLE 32-C-46....CAN PROB REPAIR WITH OUT CREW...//....PULLED OFF @ 11:45....REPAIRED CONDUCTORS...CLOSED XFMR @ 12:50....JRV...12/17/10//VER/CRB IDC CHANGED TIME OFF FROM 1145 AND CREATED ORDER FOR OPENING TRANSFORMER XXXX
17405 | Hazard | 3311103 | STINNETT | WENDOVER | 2008-06-11 21:09 | 2008-06-11 22:50 | 2 | 101 | 62879-1 | 202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311103//RERPLACED BAD CUTOUT// COD 2 // VER/TOM IDC XXXX
17406 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2009-06-08 12:32 | 2009-06-08 15:53 | 1 | 201 | 55762-1 | 201 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | A CUTOUT FAILED AT THE PRIMARY METERING. VER/KEP L3/KEP IDCC PN517 XXXX
17407 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2020-09-19 11:49 | 2020-09-19 15:10 | 1 | 201 | 4478331 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Customer @ 1012 aberdeen pl has one hot leg out on there UG service. Unable to locate Pedistal in back yards. Customer states a few weeks back that fencing company dug through telephone cables in back yard. Need dry cell transformer to restore service until repairs can be made. Released by crew 078S02
17408 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-11-21 15:09 | 2022-11-21 18:30 | 1 | 201 | 4169441 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 transformer need a 25kva cutout and t bracket bucket truck access Released by crew 077H05 Released by crew 077H13/// xmfr on pole 134-B-200 and cutout replaced.work complete and power restored @ 18:30.
17409 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-12-04 10:04 | 2011-12-04 13:25 | 1 | 201 | 4139551 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP// CREW ENROUTE//REPLACED XFMR// OFF 12:48 BACK ON 13:25//POWER IS RESTORED VER/HFP L3/HFP IDC CUSTOMER STATES POWER WAS OFF CHANGED FROM 1248 XXXX
17410 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2008-07-31 14:43 | 2008-07-31 15:50 | 3 | 67 | 62970-1 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD AND WILL NEED TOREPLACE IT I REPLACED CUTOUT AND REFUSED TRANSFORMER//3309101//VER/CRB IDC XXXX
17411 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-01-21 17:40 | 2016-01-21 21:01 | 1 | 201 | 4639281 | 201 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD HOTLEG LINECREW REQUIRED, LINECREW WILL NEED TO INSTALL POWERTEMP RELEASED BY CREW 078S11/CREW ON SITE/FETR2115/VEM//AED MADE FOR POWER TEMP INSTALLATIONBAD HOTLEG LINECREW REQUIRED, LINECREW WILL NEED TO INSTALL POWERTEMP RELEASED BY CREW 078S11/CREW ON SITE/FETR2115/VEM/POWER TEMP INSTALLED/FULL POWER RESTORED 2101/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
17412 | Whitesburg | 3312901 | JENKINS | KONA | 2012-06-01 16:39 | 2012-06-01 20:00 | 1 | 201 | 4866711 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | X-FMR FUSE OPEN ON POLE 403-205. X-FMR CHECKED BAD. NEED ONE MAN, BIG BUCKET, 15KVA 7200 X-FMR, CUT-OUT AND BRACKET. POWER RESTORED AT 20:00 6/01/2012 COD-1 ISO TF 37830403C00205 VER/HFP L3/HFP IDC XXXX
17413 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2013-09-14 10:54 | 2013-09-14 14:15 | 1 | 201 | 4854101 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRUCK TO POLE CHURCH AT SANDSUCK RD. EAST PARK RD. RELEASED BY CREW 078S08/CREW ON SITE/FETR1445/VEM/REPAIRS MADE AND POWER RESTORED 1415/PLEASE CLOSE TICKET/THANKS/VEM VER/SEF
17414 | Hazard | 3303902 | LESLIE | WOOTON | 2011-04-28 21:29 | 2011-04-29 00:50 | 1 | 201 | 52067-1 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S01REPLACED BAD CUTOUT //VER/GAH IDC XXXX
17415 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-02-16 18:19 | 2018-02-16 21:40 | 1 | 201 | 4852951 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replacing bad cutout Restored at 2140
17416 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-02-12 23:40 | 2013-02-13 00:47 | 3 | 67 | 4815191 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE WAS BROKEN CC 3 IDC XXXX
17417 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-04-30 05:29 | 2009-04-30 08:50 | 1 | 201 | 59541-1 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3103101/// WELL DISPATCH IN THE MORNING/NO CREW REQUIRED REPLACING CUTOUT DOOR//COD 1// VER/DBM L3/WHV IDCC FEC49 XXXX
17418 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-01-18 09:08 | 2010-01-18 12:29 | 1 | 201 | 55796-1 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ON SITE, CHECKING TROUBLE, SPLICE IN SERVICE FAILED// VER/DBM IDCC CNT2 XXXX
17419 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-11-22 12:54 | 2014-11-22 14:01 | 3 | 67 | 4753871 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN // WILL REFUSE // FUSE LINK APPEARS TO HAVE BROKEN // POWER RESTORED @ 14:01// COD 3//VER/ ADH
17420 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-07-01 06:54 | 2022-07-01 10:15 | 1 | 201 | 4354141 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | riser broken out of transformer.. climber, changing
17421 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-05-26 00:43 | 2010-05-26 04:04 | 1 | 201 | 50880-1 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AT 0140 , SERVICER OPENED LINE FUSE ON POLE 164-B-171 TO ISOLATE FAULT POLEBAD 19.9 CUTOUT.BAD 19.9 CUTOUT. NO TRUCKS TO POLE.BAD 19.9 CUTOUT. NO TRUCKS TO POLE. RELEASED BY CREW 078S01 IDC XXXX
17422 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-06-03 18:54 | 2018-06-03 22:15 | 1 | 201 | 4551441 | 201 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad leg UG. Need power temp.,,crew on site,,installed power temp..send ticket to rayburn please..only one customer was part power
17423 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-01-27 07:09 | 2022-01-27 10:30 | 1 | 201 | 4408151 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | serve end connection melted out causing s/d to burn down..replacing s/d.
17424 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2013-02-04 07:44 | 2013-02-04 11:05 | 1 | 201 | 4789101 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FROZE OPEN. REPLACING WITH SQUEEZE-ON TYPE CONNECTION. REPLACED BOTH CONNECTIONS. RESTORED @ 11:05. SH//COD 1// VER/DBM IDC XXXX
17425 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2021-10-10 15:29 | 2021-10-10 18:50 | 1 | 201 | 4338271 | 201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required a bad 15kva trucks ok Released by crew 078S03 all pwr restored18:50 pleaseclose ticket LRM
17426 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2018-02-03 11:24 | 2018-02-03 14:45 | 1 | 201 | 4797961 | 201 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | one hot leg and neutral burned into on 1/0 secondary at xfmr pole///repairs made//restored at 14:45//complete//em
17427 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-02-16 13:50 | 2015-02-16 15:30 | 2 | 100 | H4032841 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TREE HAS GROWN INTO S/D SHORTING OUT SER // WILL CHANGE SER.// WILL HAVE TO CHANGE OUT SEC. ALSO// SPLICE BAD// REPAIRS MADE //OPENED @ 13:50 CLOSED @ 15:30/// DUPLICATE IN HOIS/ ISO 38831127B10172/ COD 3*****THIS IS FOR 2 CUSTOMER / SEE 4032841 FOR OTHER 1 CUSTOMERS / VER/BOW L3/HFP XXX
17428 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-06-24 14:10 | 2013-06-24 14:50 | 5 | 40 | 4391281 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACE TRANSFORMER VER/CRB L/3 CRB
17429 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2020-11-15 19:00 | 2020-11-15 20:40 | 2 | 100 | 4691591 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | riser burnt off top of transformer. Repaired, back on @ 20:40
17430 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-09-07 12:55 | 2018-09-07 14:35 | 2 | 100 | 4053751 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed at weatherhead and another one on sec pole 38830882D30927. Opened xfmr 882-113 @ 14:15 to make repairs. Made repairs and closed xfmr @ 14:35. sh
17431 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-02-05 17:58 | 2011-02-05 18:18 | 10 | 20 | 54624-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW INSTALLED 35T FUSE ON POLE 3883081B00303//ISO//THIS WAS TO ISOLATE TRBL 54459-1//COD 10///MD FILED// VER/DBM IDC XXXX
17432 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-12-05 15:55 | 2014-12-05 16:45 | 4 | 50 | 4837091 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 1625// FOUND BAD CUTOUT ON POLE 1024-145 HAVE MADE REPAIRS AND EVERYTHING IS DONE AT THIS LOC TIME ON 1645 // CCC COD-4 ISO TF 39831024B00145 VER/HFP L3/HFP
17433 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-09-16 11:20 | 2014-09-16 14:40 | 1 | 200 | 4503151 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON TRANSFORMER NEED BIG BUCKET TO CHANGE CUTOUT RELEASED BY CREW 077S05 VER/CRB
17434 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-12-25 14:40 | 2010-12-25 18:00 | 1 | 200 | 55676-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 074S03// FOUND SERVICE DROP BURNT INTO SPLICING BACK NOW TCM // EMAILED TO P WYSONG // VER/DBM IDC XXXX
17435 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2009-06-05 10:50 | 2009-06-05 14:10 | 1 | 200 | 64265-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, POLE#964-7, NEED BIG BUCKET, SEND TO JOEY REED RELEASED BY CREW 080S01//VER/CRB IDC XXXX
17436 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-05-06 12:56 | 2022-05-06 14:36 | 2 | 100 | 4845261 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line cutout broken on p-925-7.need flaggers and big bucket.
17437 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-09-02 09:30 | 2011-09-02 10:20 | 4 | 50 | 4783851 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGE BAD 25 KVA TO 37.5 KVA.. M.PHELPS//COD 4// VER/DBM IDC XXXX
17438 | Paintsville | 3409302 | KENWOOD | AUXIER | 2013-02-21 06:40 | 2013-02-21 10:00 | 1 | 200 | 4836231 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK APPEARS TO HAVE BROKE. RE-FUSED @ 10:00. SH VER/KEP IDC XXXX
17439 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-04-12 21:30 | 2013-04-12 22:20 | 4 | 50 | 4005881 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TWO CUSTOMERS FED FROM 737-11 WERE HAVING BRIGHT & DIM. XFMR SECONDARY NEUTRAL CONNECTION BAD. OPENED XFMR @ 21:30, CLEANED NEUTRAL BUSHING, RE-WORKED XFMR CONNECTIONS AND CLOSED XFMR @ 22:00. SH COD-4 ISO TF 38830737000011 VER/HFP L3/HFP IDCC TON2221 XXXX
17440 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2022-10-08 18:45 | 2022-10-08 19:25 | 5 | 40 | 4007261 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored 19:25
17441 | Hazard | 3309302 | VICCO | JEFF | 2013-03-09 12:53 | 2013-03-09 13:33 | 5 | 40 | 4893481 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN//// FUSE BROKE, REFUSED POWER RESTORED. COD-5 ISO TF 37830322A00024 VER/HFP L3/HFP IDC XXXX
17442 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2022-08-08 15:20 | 2022-08-08 16:10 | 4 | 50 | 4705361 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored fuse burnt into
17443 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-04-23 22:25 | 2016-04-24 00:05 | 2 | 100 | 4120581 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. CHANGED ALL 3 CUTOUTS ON THIS TRANSFORMER BANK FUSED UP EVERYTHING OK//COD 2
17444 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2008-12-16 11:08 | 2008-12-16 12:48 | 2 | 100 | 58902-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3404301//, ON SITE, POLETOP BURNT OFF, MAKING REPAIRS COD-2 L3/HFP IDC XXXX
17445 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-02-22 22:55 | 2018-02-23 00:35 | 2 | 100 | 4874291 | 200 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutraland broke midspan in secondery coming from pole 1102-15, had to open trans. to make repairs. Opened @2358, made repairs and closed back @0035, only 1 customer was affected until I opened trans.
17446 | Pikeville | 3413401 | GARRETT | GARRETT | 2020-09-26 21:05 | 2020-09-26 22:45 | 2 | 100 | 4499271 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | a span of #2 open wire secondary is down.. need crew.. will have to open xfm on pole 16-C-42 to make repairs. opened xfm @ 21:05 repairs made
17447 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-09-17 15:40 | 2019-09-17 17:20 | 2 | 100 | 4028731 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kv xfm. 19.9 single bushing///will need big bucket and one man to make repairs..checked voltage @ xfm and getting incorrect reading.opened xfm @ 15:40..repairs made.closed back in @ 17:20.//NO OUTAGE TILL TRANSFORMER OPENED
17448 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2009-12-11 10:22 | 2009-12-11 11:02 | 5 | 40 | 63849-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | VER/HFP CREW OPENED LINE FUSE (STEPDOWN TR) TO ALLOW THEM TO CLIMB POLE (NO TRUCK ACCESS) TO REPAIR LOOP THAT BURNT OPEN IN ORDER 60871-1 L3/HFP
17449 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-06-24 12:21 | 2021-06-24 15:41 | 1 | 200 | 4802961 | 200 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad 4/0 underground hot leg Released by crew 078H03////Repairs made///Complete BR
17450 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2018-12-27 10:20 | 2018-12-27 12:00 | 2 | 100 | 4600971 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on 38830214000108 NBT will need crew// crew on site FETR 12:00 LRM L3/HFP
17451 | Pikeville | 3402003 | KEYSER | MULLINS | 2018-07-03 09:54 | 2018-07-03 10:44 | 4 | 50 | 4716181 | 200 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | B phase trans. open on bank pole 1127-B-481, checking. Fuse pulled into, was not blowed, refused @1044. COD-4 ISO TF 38831127B00481
17452 | Hazard | 3303901 | LESLIE | HYDEN | 2017-01-02 10:50 | 2017-01-02 14:10 | 1 | 200 | 4261901 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 315-52 , NEED 1 MAN AND BIG BUCKET .BIG BUCKET MAY REACH POLE IF NOT WILL BE MANUEL . 37830315000052 VER/AWD L3/HFP XXXHFP
17453 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-11-10 20:22 | 2017-11-10 23:42 | 1 | 200 | 4548131 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called cust multiple times no answer/ replaced cutout and restored power at 1142
17454 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-05-17 09:39 | 2010-05-17 12:59 | 1 | 200 | 63730-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT; WAITING ON OBSERVER BEFORE I CHANGE IT OUT; CHANGED CUTOUT; PWR RESTORED AT 1259 HRS VER/HFP L3/HFP IDC XXXX
17455 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-01-06 09:55 | 2014-01-06 13:15 | 1 | 200 | 4235931 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKED VOLTAGE AT MTR BASE 1 LEG HAS NO POWER SUPECT BAD CONNECTION AT TRANSFORMER, TRUCK ACC. RELEASED BY CREW 077E02, REPLACED CONNECTIONS ON XFMR POLE. COMPLETE// VER/DBM
17456 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-04-11 16:05 | 2012-04-11 16:25 | 10 | 20 | 4666421 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND SECONDARY LUG BURNT-UP ON 882-498. OPENED XFMR @ 16:05, REPLACED LUG AND CLOSED XFMR @ 16:25. SH COD-10 ISO TF 38830882A00498 VER/HFP L3/HFP OOO
17457 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-04-15 22:55 | 2009-04-15 23:35 | 5 | 40 | H55174-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3003701//PART OF 55174-1//PRIMARY OPEN AT POLE 38830184C00042//ISO//COD 6//LIFTED TAP ON POLE 38830184C00075 IN ORDER TO MAKE REPAIRS @ 2255//INTERRUPTED 5 MORE CUSTOMERS//BROKEN RISER ON HOT LINE CLAMP, REPAIRED WIRE. SEVERAL TREES BURNING IN LINE, NOT FUSED AT 3 PHASE, NEED CUTOUT AT POLE 184-75. ANY FAULTS ON THIS LINE WILL TAKE OUT 3 PHASE RECLOSURE.//EMAILED TO LLOYD RAYBURN// VER/DBM IDC XXXX
17458 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-05-16 14:00 | 2015-05-16 17:20 | 1 | 200 | 4434791 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WE HAVE A XFMR POLE ROTTEN AND FELL OVER HELD UP BY WIRE AND GUY./// MANUAL POLE, CREW REQUIRED// MATERIAL 40/4 POLE, 15KV XFMR, 1=COMPLETE DEADEND, 2 CLEVIS AND SPOOLS, CUTOUT AND BRKT, 1 GUY ATTACHMENT 12KV. NO POWER OUT AT THE MOMENT. RELEASED BY CREW 077S08// OPENED 1400 CLOSED 17:20/ ISO 37830225D00271/ COD 1/ VER/BOW
17459 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2016-02-05 22:38 | 2016-02-05 23:18 | 5 | 40 | 4680251 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE APR AT 2318 CLOSE TICKET/ ISO 38830454D16035/ COD 5/ VER/BOW
17460 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-03-11 14:00 | 2011-03-11 14:50 | 4 | 50 | 53474-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP INTO MID SPAN//VER/CRB IDC XXXX
17461 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-05-01 19:53 | 2010-05-01 21:33 | 2 | 100 | 53456-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | NO CREW REQUIRED REPAIRED GUY AND REPLACED 6T TRANS. FUSE //VER/GAH IDC XXXX
17462 | South Williamson | 3411401 | DEWEY | INEZ | 2010-06-15 09:02 | 2010-06-15 10:42 | 2 | 100 | 64886-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN DOOR DID NOT DROP OUT LOOKS BURNT.LOOKING LINE OVER.PUT NEW DOOR IN STAYED IN!!! ALSO FUSE WAS 25 T ENTERED MD COD-2 VER/HFP L3/HFP
17463 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-12-03 14:40 | 2022-12-03 18:00 | 1 | 200 | 4225301 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 19.9 cutout, needcutout only truck acess Released by crew 077S07 changed cutout power restored at 18:00
17464 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-07-25 23:10 | 2012-07-26 02:30 | 1 | 200 | 4829611 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLOWN. CHANGING CUTOUT AND ARRESTER. LINECREW REQUIRED VER/ARN
17465 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-01-31 00:28 | 2019-01-31 02:08 | 2 | 100 | 4741711 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | servicer ETA approx/////xfm. blew pri. bushing out and sprayed oil on ground and side of home..home is vacant and only serves this one home.removed tap feeding xfm. and removed meter..please send copy to PR about changing out and cleaning spill up in the a.m..home is by itself on side of hill this is truck access..15kv 7200 xfm.. Released by crew 074S01//iso 37830119000099// WILL BE WORKED ON OPS # 032024460 - REST @ 0208
17466 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-09-09 21:15 | 2008-09-09 22:55 | 2 | 100 | 60941-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3413402//POLETOP BURNING. ABOUT 2/3S OF THE POLE TOP HAS BURNED AND STILL BURNING......DAH RELEASED BY CREW 074S08/I OPENED LINE FUSE AT 21:15 AND RESTORED POWER AFTER REPAIR BURNT POLE AT 23:00 /ISO 37830159000525 // TIM MCCOY // COD 2//SENT MD ON MISSING 20T FUSE DBM// VER/DBM IDCC IDC TOF1618 XXXX
17467 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2020-05-16 21:11 | 2020-05-16 22:51 | 2 | 100 | 4844131 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse out on pole 23-D-74 will refuse.. restored at 2251
17468 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2011-11-18 20:00 | 2011-11-18 20:40 | 5 | 40 | 4091881 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL ROTTEN REPLACED FUSE 6T VER/ARN IDC XXXX
17469 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-01-18 07:37 | 2017-01-18 10:57 | 1 | 200 | 4307691 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O 7200 BROKEN 38830187000147, NBT, CONDUIT ON POLE--CREW REQ--DS011817 RELEASED BY CREW 078S01/CREW ON SITE/FETR1130/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1057 @38830187000050 /PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830187000147/ COD 1/ VER/BOW L3/HFP XXXHFP
17470 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-02-24 20:31 | 2014-02-24 21:21 | 4 | 50 | 4431431 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 37.5(MAP SHOWS 75) KVA ON POLE 286-124 TRUCK TO POLE GETTIN HIGH VOLTAGE AT SERVERAL METERS SEND TO V.MULLINS // NO CUST OUT AT THIS TIME WILL BE OUTAGE TO REPLACE XFMR //OPENED XFMR @2031/FETR 2130/VEM/XFMR BACK IN AT 2121/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
17471 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-07-19 12:55 | 2011-07-19 16:15 | 1 | 200 | 4562801 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED, BAD 15KVA 2 BUSHING 7200 120/240 ON POLE 38830206B02091, B PHASE, LIGHTNING ARRESTER BLOWN ON A PHASE, TRUCK OK. RELEASED BY CREW 078S05////COD 1// VER/DBM
17472 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-15 23:30 | 2011-06-16 01:10 | 2 | 100 | 4324321 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFORM CUTOUT BAD NEED LINE CREW AND TREE CREW BIG BUCKET CUTOUT BROKEN ONE PIECE ALREADY FELL TO THE GROUND PINE TREE NEEDS CUTOUT TO GROUND IN ORDER TO SEE CUTOUT AND XFORM OPENED LINE FUSE ON 165-264 RELEASED BY CREW 078S04XFORM CUTOUT BAD NEED LINE CREW AND TREE CREW BIG BUCKET CUTOUT BROKEN ONE PIECE ALREADY FELL TO THE GROUND PINE TREE NEEDS CUTOUT TO GROUND IN ORDER TO SEE CUTOUT AND XFORM OPENED LINE FUSE ON 165-264 POLE COVERED UP TREE CREW WORKING @ 1130 VER/ARN
17473 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-06-27 17:05 | 2016-06-27 18:45 | 2 | 100 | 4487531 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, REPLACED CUTOUT AND ARRESTER, POWER RESTORED VER/HFP L3/HFP
17474 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-02-02 18:09 | 2009-02-02 21:29 | 1 | 200 | 54873-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP CALLE BRUCE LINDON FOR CREW TO REPLACED BAD 167 KVA TR. L3/HFP AJB
17475 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-07-12 18:30 | 2022-07-12 21:50 | 1 | 200 | 4472431 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout, replaced.
17476 | Hazard | 3308002 | JACKSON | PANBOWL | 2021-08-17 12:06 | 2021-08-17 13:46 | 2 | 100 | 4086421 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | refused transformer
17477 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2013-07-02 12:00 | 2013-07-02 15:20 | 1 | 200 | 4445941 | 200 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDER GROUND NEED TO PLACE POWER TEMP RELEASED BY CREW 078S05BAD UNDER GROUND NEED TO PLACE POWER TEMP,ALL CUST RESTORED PLACE,IN ABNORMAL NEED CREW TO REPLACE UNDERGROUND SERV,PLEASE CLOSE TICKET THANKS.BT//MTR 533677962 VER/CRB L/3 CRB
17478 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-06-25 02:12 | 2014-06-25 03:02 | 4 | 50 | 4151771 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW OPENED TO SAFELY REPLACE TRANSFORMER ON POLE#71-69 ON PO#4150961 VER/KEP
17479 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-11-13 22:20 | 2013-11-13 23:10 | 4 | 50 | 4037381 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE BURNED DOWN IN MIS SPAN AT A SPLICE. I AM GOING TO RESPLICE CONDUCTOR.//SERVICE BURNED DOWN IN MIS SPAN AT A SPLICE. I AM GOING TO RESPLICE CONDUCTOR. I OPENED TRANS. ON POLE 37830167D00275 AT 22:20 AND CLOSED IT BACK IN AT 23:10. VER/CRB
17480 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-01-08 17:00 | 2015-01-08 17:40 | 5 | 40 | 4921091 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLINE CLAMP BURNT OFF ON 834-105/ OPEN TRANSFORMER 834-104 TO SAFELY MAKE REPAIRS/HOTLINE CLAMP BURNT OFF ON 834-105. OPENED XFMR 834-104 @ 17:00. REPAIRED PHASE B HOTLINE CLAMP AND RESTORED XFMR @ 17:40. SH RELEASED BY CREW 076S02// VER/ ADH
17481 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-04-21 20:27 | 2009-04-21 21:17 | 4 | 50 | 65961-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-4 L3/HFP IDC XXXX
17482 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-10-02 19:25 | 2009-10-02 22:45 | 1 | 200 | 65761-1 | 200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3116102//, 1 LEG OF URD WENT BAD THURSDAY, INSTALLED POWER TEMP, OTHER LEG IS NOW BAD, INSTALLING TEMP OVERHEAD SERVICE, ONLY 1 CUSTOMER AFFECTED VER/TOM IDCC CNT6 XXXX
17483 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-10-27 11:10 | 2017-10-27 14:30 | 1 | 200 | 4502761 | 200 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED ON SEC POLE 806-127. REPLACED ALL CONNECTIONS ON SEC POLE AND RESTORED @ 14:30. SH VER/AWD L3/HFP HFPC MCCDL
17484 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2019-04-04 08:41 | 2019-04-04 12:00 | 1 | 199 | 4056121 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 7200 cutout on 237-43/ making repairs/customer restored @ 1200/ please close ticket/ MLH L3/HFP
17485 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-01-12 06:23 | 2009-01-12 09:42 | 1 | 199 | 54355-1 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WR # 28021348 //...BAD SERVE END..SHORTED OUT AND BURNED DOWN #2/3 SERVICE DROP...BB//VER/CRB L3/KEP IDC XXXX
17486 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2015-05-03 17:01 | 2015-05-03 20:20 | 1 | 199 | 4386261 | 199 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 1-BAD LEG ON UG SERVICE. CREW REQD. RELEASED BY CREW 078S07//1012 ABERDEEN PLACE//220 BREAKERS ARE OPEN PER CUST// PLACED POWER TEMP VER/CRB
17487 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-01-30 16:51 | 2018-01-30 20:10 | 1 | 199 | 4785071 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tran and lat c/os broke--crew req-ds013018 Released by crew 078S01/on site RM power on at 20:10 please close tic RM
17488 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-06-17 16:26 | 2009-06-17 19:45 | 1 | 199 | 63701-1 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TRANSFORMER-CALLED FRALEYS CREW-SEND TO BILL RELEASED BY CREW 078S07//VER/CRB IDC XXXX
17489 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2012-07-10 06:56 | 2012-07-10 10:15 | 1 | 199 | 4661671 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 25T POLE 190-27 RESTORED @10:15 MP//COD 1 IDC XXXX
17490 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-10-06 10:20 | 2011-10-06 13:39 | 1 | 199 | 4951901 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN,WILL REPLACE,ALSO LOT OF TREES AROUND XFR I HAVE TO CUT////CUT TREES,REPLACED CUTOUT,RESTORED POWER VER/KEP IDC XXXX
17491 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2021-10-09 07:46 | 2021-10-09 11:05 | 1 | 199 | 4334651 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1062-69 IS 2/3 BURNED INTO,NEED CREW&XARM TO BAND-AID TEMPORARILY TO KEEP FRM CHANGING POLE OUT///MYLES ENROUTE/////////MADE REPAIRS&RESTORED@11:05
17492 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2021-12-12 11:56 | 2021-12-12 15:15 | 1 | 199 | 4188111 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bottom side riser to cutout burnt up/crew reqd for covering & observing/truck ok w service bucket Released by crew 078S04 Closed on 138-D0-052 at 15:15. Ticket complete KMG
17493 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-12-08 14:11 | 2009-12-08 17:30 | 1 | 199 | 56560-1 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD PRIMARY INSULAGTOR BAD & NEUT WIRE DOWN TOO == NEED LINE CREW & ROW CREW == LINE FUSE OUT == RELEASED BY CREW 077S03 REPLACED INSULATOR RESSAGGED NEUTRAL RESTORED POWER AT 1730 077H01//COD 1 IDC XXXX
17494 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-01-24 05:16 | 2009-01-24 08:35 | 1 | 199 | 59560-1 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3408103 - 10 KVA TRANSFORMER BAD, CREW WILL BE ENROUTE AT 08:00 / GXJ... REPLACED WITH 15KVA, ALL WORK COMPLETE / GXJ VER/ARN MD FILED L3/KEP
17495 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-06-22 15:11 | 2011-06-22 18:30 | 1 | 199 | 4394171 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON PRIMARY METERING POLE === CHANGED CUTOUT == ALSO HAD HOT LINE CLAMP BAD ON POLE 37830324000250 === REPAIRED IT ALSO === POWER OK//COD 1//ISO//FEEDER//3309301 //
17496 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2010-11-14 12:51 | 2010-11-14 16:10 | 1 | 199 | 55538-1 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEVICE NUETRAL BROKEN IN MID SPAN,... CUSTOMER HAS SOME DAMAGE TO FLORECENT LGHT BALASTS IN THE CHURCH.....P.HICKS//EMAILED TO P WYSONG // VER/DBM IDC XXXX
17497 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-06-30 16:41 | 2015-06-30 20:00 | 1 | 199 | 4698011 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFORM CUTOUT BAD 6T FUSE ,REPLACE POWER RESTORED 1 CUST VER/CRB
17498 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-06-07 06:41 | 2009-06-07 10:00 | 1 | 199 | 52063-1 | 199 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP REPAIRING BAD PLACE IN WIRE COD- 1 ISO 38830472D30124 L3/HFP IDC XXXX
17499 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-02-28 08:26 | 2015-02-28 11:45 | 1 | 199 | 4086971 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED BURNT UP CUTOUT DOOR 38830278000207 VER/CRB L3/DKGXXXX VERIFIED WITH VOICE RECORDER THAT SERVICER THOUGHT IT WAS FAILED EQUIPMENT. SQUIRREL AT BASE OF POLE HAD BEEN THERE A LONG TIME, PRETTY DECAYED.
17500 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2015-02-01 18:54 | 2015-02-01 22:13 | 1 | 199 | 4979391 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRECT LIMING FUSE CALL CREW NO TRUCK FRIST HOUSE ON RIGHT PAST COBB FK. 15T FUSE///REPLACED CURRENT LIMIT FUSE///PWR CK GOOD///TBL TKT COMP/ ISO 38830114000035/ COD 1/ VER/BOW L3/HFP XXX
17501 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2011-06-16 08:46 | 2011-06-16 12:05 | 1 | 199 | 4326751 | 199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED--INSTALLED TAG AND GROUND ON POLE 38830045A31130--TOP OF TRANSFORMER POLE 38830045C14013 IS BURNT OFF-NEED FIBERGLASS EXTENSION INSTALLED--TRUCK OK-ONLY 1 CUSTOMER RELEASED BY CREW 078S07//COD 1// VER/DBM
17502 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-01-20 08:25 | 2020-01-20 11:43 | 1 | 198 | 4322281 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad con at weatherhead--replaced section of drop and repaired con--allgood-ds012020 L3/HFP
17503 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-12-21 22:15 | 2014-12-22 01:33 | 1 | 198 | 4873751 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 37830270A00421, NEED 1 MAN, BIG BUCKET, 19.9 CUTOUT, LT. ARR AND TEE BRACKET. VER/KEP
17504 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-12-06 13:49 | 2021-12-06 14:55 | 3 | 66 | 4154591 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required fuse broken
17505 | Pikeville | 3413402 | GARRETT | LACKEY | 2011-07-07 12:36 | 2011-07-07 14:15 | 2 | 99 | 4481461 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE BAD CUTOUT CHANGED CUTOUT FUSED UP EVERYTHING OK//COD 2// VER/DMB IDCC PN47 XXXX
17506 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-02-19 09:14 | 2014-02-19 10:20 | 3 | 66 | 4400151 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CHANGED BAD CUTOUT ***CHANGE ISO POLE**** TO 181 COD 3. VER/SEF
17507 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2016-05-10 09:12 | 2016-05-10 09:45 | 6 | 33 | 4192031 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AD 7200 C/O DOOR, RESTORED VER/CRB
17508 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-03-27 19:16 | 2009-03-27 20:55 | 2 | 99 | 62216-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. REPLACED. SH//3409002//VER/CRB IDC XXXX
17509 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2016-12-22 12:15 | 2016-12-22 15:33 | 1 | 198 | 4228971 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SEC. POLE 37830272A30420, ROTTED OFF @ GROUND AND FELL IN BACKYARD, 1/0 LASH LAYING ON ROOF OF HOME SECONDARY CUT IN CLEAR @ POLE 37830272A30238 RELEASED BY CREW 077S04 POLE REPLACED REPAIRS MADE VER/CRB
17510 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-05-13 17:04 | 2022-05-13 18:43 | 2 | 99 | 4886811 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | old pole has retted off at the ground and leaned against new pole. that pulled service to tight and a neutral sleeve gave out. repairs made but the equipment needs transfered. is accessable with small bucket Released by crew 078S12. crew on site to make repairs. opened transformer on pole 44-235 @ 17:04 to replace pole. pole replaced all repairs made and transformer in @ 18:43. complete
17511 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-12-26 18:34 | 2021-12-26 19:40 | 3 | 66 | 4228471 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke, restored transformer on 39831123B00540 @ 19:40
17512 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-06-10 11:27 | 2021-06-10 14:45 | 1 | 198 | 4705271 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr fuse had blown and caused cutout door to burn up. Did not have replacement door due to it being older style cutout so I had to replace entire cutout. Restored @14:45
17513 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-03-16 13:23 | 2016-03-16 15:02 | 2 | 99 | 4855291 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 308-23 WILL REPAIR...REPAIRED. VER/ARN
17514 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2016-04-28 20:29 | 2016-04-28 21:35 | 3 | 66 | 4140001 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRIED TO CALL CUSTOMER BUT NO ANSWER.. BAD CUTOUT GATE ON TRANSFORMER CUTOUT, REPLACED FUSE GATE POWER RESTORED @ 21:35/ ISO 37830177D00369/ COD 3/ VER/BOW
17515 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-05-04 11:54 | 2015-05-04 13:00 | 3 | 66 | 4388151 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE LINK BROKE. RESTORED @ 13:00. SH/COD 3// VER/ ADH
17516 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-07-09 11:12 | 2022-07-09 14:30 | 1 | 198 | 4442421 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RESTORED AT 1430
17517 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-02-22 14:51 | 2019-02-22 16:30 | 2 | 99 | 4844621 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER R. MAGGARD BAD XFMR ON POLE 37830375A00125 COD-2 replacer transformer an cutout
17518 | Hazard | 3309302 | VICCO | JEFF | 2013-03-20 07:17 | 2013-03-20 10:35 | 1 | 198 | 4925541 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND === 4/0 ALM === NEED CREW AND 4/0 ALM UNDERGROUND CABLE === RELEASED BY CREW 077S03 ON SITE WORKING REPLACED UNDERGROUND POWER RESTORED VER/KEP IDC XXXX
17519 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-12-18 14:43 | 2008-12-18 18:01 | 1 | 198 | 59930-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3300602// == WIRE BURNED DOWN FROM POLE 296A2-611 TO 296A2-1477 == CALLED CUST SAID BE OK TO PUT BACK UP 12-19-2008 == CALLED GEN COMBS AND TOLD HIM ABOUT IT == RELEASED BY CREW 077S03// SERVICER CREATED OPS ORDER TO GO BACK ON THIS//OPS ORDER #038363060 VER/KEP L3/KEP IDC XXXX
17520 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2020-03-09 06:27 | 2020-03-09 09:45 | 1 | 198 | 4461761 | 198 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power bad connection at xfmr, made repairs restored power at 09:45..
17521 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-12-07 14:56 | 2011-12-07 16:35 | 2 | 99 | 4149881 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEC. BURNED DOWN//DONNIE AND I WILL REPAIR// REPAIRED 2/3 SEC // POWER IS RESTORED COD-2 ISO TF 38821011B00016 VER/HFP L3/HFP IDC XXXX
17522 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-12-25 18:34 | 2009-12-25 20:13 | 2 | 99 | 60261-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ORDER COMPLETED PER LOCAL OFFICE/DKG/2015 HRS/122509
17523 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-10-14 14:30 | 2008-10-14 17:48 | 1 | 198 | 55703-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3000701//HAVE A BAD 10 KVA CSP TRANSFORMER, NEED CREW TO CHANGE THIS OUT, ALSO NEED A CUTOUT, HAVE RISER AND EVERYTHING TAKEN LOOSE FROM TRANSFORMER, TALKED TO MR. MCCARTY, SAID THEY WOULD BE HERE IN ABOUT A HOURHAVE A BAD 10 KVA CSP TRANSFORMER, NEED CREW T COD-1 IDCC TOF1344 ESTIMATED TIME OFF XXXX
17524 | Pikeville | 3408103 | SALISBURY | MARTIN | 2013-09-16 10:42 | 2013-09-16 14:00 | 1 | 198 | 4857211 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER 25KVA..CHANGED OUT TRANSFORMER TO 15KV.RESTORED AT 14:00 VER/CRB L/3 CRB
17525 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-08-27 14:42 | 2016-08-27 18:00 | 1 | 198 | 4841171 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV TRANSFORMER 72 KV,MIGHT BE ABLE TO USE BIG BUCKET,IF NOT MANUAL.NEED 4 MAN LINE CREW RELEASED BY CREW 077H07 REPLACED TRANSFORMER ;;POWER RESTORED AT 18:00 VER/CRB
17526 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-03-12 12:50 | 2013-03-12 14:29 | 2 | 99 | 4901421 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MDC //COD 2//BAD CUTOUT GATE ///VER/CRB L/3 CRB IDCC PN265 XXXX
17527 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-10-11 18:15 | 2008-10-11 18:48 | 6 | 33 | 55094-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001203//BROKEN FUSE LINK / COD 6 // VER/TOM IDC XXXX
17528 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-06-06 12:17 | 2008-06-06 12:35 | 11 | 18 | 59108-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3309103 POWER WENT BACK OUT/PERSONNEL STILL IN AREA CHECKING BAD FUSE
17529 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-05-08 18:17 | 2013-05-08 21:35 | 1 | 198 | 4087921 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BURNT UP, NEED 1 MAN AND BIG BUCKET 19.9 CUTOUT AND ARR AND TEE BRACKET.----- POWER RESTORED AT 21:35, ONLY 1 CUST. OUT. ///VER/CRB L/3 CRB IDC XXXX
17530 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-07-11 11:59 | 2014-07-11 12:21 | 9 | 22 | 4228791 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR POLE. WILL CHANGE RISER & REDO CONNECTIONS PULLED XFMR OFF @ 11:59 BACK ON @ 12:21 VER/CRB VER/DKG L3/DKG ORIGINAL CALL WAS FOR A FLICKERING LIGHTS
17531 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-02-16 08:56 | 2018-02-16 10:35 | 2 | 99 | 4848581 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 10:35. sh
17532 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-04-20 08:54 | 2016-04-20 10:00 | 3 | 66 | 4106781 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, REPLACED, POWER RESTORED/ ISO 37830202000023/ COD 3
17533 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2017-07-29 12:12 | 2017-07-29 13:18 | 3 | 66 | H4202081 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP OPEN ON POLE 37830208000059 -- LINE CREW AND ROW === MANUAL UP ON HILL === 2 CUST OUT RELEASED BY CREW 077S03 OPEN LOOP TO DO REPAIRS 37830208000052 1212 TILL1318 RELEASED BY CREW 077H04 ****SEE OUTAGE 4202081*** VER/CRB
17534 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2009-04-08 21:39 | 2009-04-08 22:45 | 3 | 66 | 50641-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE, CUTOUT AND FUSE WERE CHANGED TODAY PER REPLACEMENT PROGRAM.COD-3 VER/KEP L3/KEP IDC XXXX
17535 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2012-06-22 07:49 | 2012-06-22 11:07 | 1 | 198 | 4944131 | 198 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TRUCK OK RELEASED BY CREW 078S08/CREW CUTTING XFMR OVER FOR 208/FETR 1200/VEM/REPAIRS MADE AND POWER RESTORED 1107/PLEASE CLOSE TICKET/THANKS/VEM COD-1 ISO TF 38830138D20490 VER/HFP L3/HFP
17536 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-05-20 18:11 | 2015-05-20 19:50 | 2 | 99 | 4450501 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE # 101-30 WILL CHANGE//// CHANGED BAD 19.9 CUTOUT AND RESTORED SERVICE @ 19:50// VER/ ADH
17537 | Hazard | 3302704 | HAZARD | KENMONT | 2021-09-26 10:20 | 2021-09-26 13:38 | 1 | 198 | 4292381 | 198 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke in service calling help repaired neutral cust. has good voltage he has a breaker went bad inside home
17538 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-06-03 02:12 | 2019-06-03 02:45 | 6 | 33 | 4417331 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | pole 1123-7627 found a couple melted connections going to need to replace 4 conections time off 0212 back on at 0245/ ISO 39831123D47627/ COD 6
17539 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-08-17 15:57 | 2012-08-17 19:15 | 1 | 198 | 4947731 | 198 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | METERBASE ONLY GETTING 120V APPEARS 1 HOT LEG HAS BURNT OPEN ON XFMR POLE GOING TO MAKE REPAIRS VOLTAGE CHECKS GOOD IN METERBASE TOP OF TREE HAS BROKEN OUT AND TORE DOWN 1/0 LASH AND BUSTED SECONDARY BUSHINGS IN XFMR PLEASE SEND TO ENGINEERING TO GET JOB TO REMOVE WIRE AND REPLACE LEAKING XFMR//EMAILED TO TECH IDC XXXX
17540 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2008-07-21 15:33 | 2008-07-21 17:12 | 2 | 99 | 55944-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP. REPLACED DOOR AND RE-FUSED XFMR. SH//VER/CRB IDCC FEC49 XXXX
17541 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2021-04-27 11:42 | 2021-04-27 15:00 | 1 | 198 | 4483881 | 198 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad UG leg feeding apt 4, unable to locate secondary pedestal. Crew required, power temp required. Easiest access on right side of apt 4. Released by crew 078S02 installed pwr temp pleaseclose ticekt LRM//PUT IN DAE
17542 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2016-01-28 12:48 | 2016-01-28 13:10 | 9 | 22 | 4656571 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENING LINE FUSE TO REPAIR CONDUCTOR ABOUT BROKE/BURNT INTO/ ISO 37830134C00035/ COD 9 0PENED AT12:48 CLOSED AT 13:10/ VER/AWD
17543 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-11-12 16:54 | 2013-11-12 20:12 | 1 | 198 | 4033161 | 198 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD SERVICE , I HAD TO CHANGE OUT SERVICE VER/CRB
17544 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-05-05 12:49 | 2010-05-05 13:00 | 18 | 11 | 56028-1 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CREW OPENED LINE FUSE TO ALLOW THEM TO SAFELY REPLACE A DEFECTIVE LIGHTENING ARRESTOR /// COD-18 VER/HFP L3/HFP IDC XXXX
17545 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-06-24 14:12 | 2016-06-24 17:30 | 1 | 198 | 4463021 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | ZIGGY REPLACED 25KVA XFRM--RESTORED POWER AT 17:30--BK/ CAN CLOSE MWL VER/AWD
17546 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2019-05-22 12:06 | 2019-05-22 13:45 | 2 | 99 | 4315121 | 198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad Arrester changed power restored at 13:45
17547 | Hazard | 3302703 | HAZARD | HAZARD | 2011-04-16 11:43 | 2011-04-16 15:00 | 1 | 197 | 58326-1 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BAD ON HSE, REPAIRED VER/HFP L3/HFP IDC XXXX
17548 | Hazard | 3311103 | STINNETT | WENDOVER | 2016-07-21 06:10 | 2016-07-21 09:27 | 1 | 197 | 4662461 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE BURNT DOWN === CONNECTION ON TRANSF BURNED OFF ==== REPAIRED CONNECTION === POWER OK VER/CRB
17549 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-09-26 16:08 | 2013-09-26 19:25 | 1 | 197 | 4890621 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 141-158 NEED 25KVA TRANS LEAKING OIL RELEASED BY CREW 078S08//WORK REQ 51091097/ FETR 20:00 JEH/REPAIRS COMP. POWER REST. @ 19:25/JEH/ PLEASE CLOSE TICKET VER/SEF IDC XXXX
17550 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-02-18 12:07 | 2008-02-18 15:24 | 1 | 197 | 64810-1 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000301// REPLACED BAD CONNECTOR// VER/TOM IDC XXXX
17551 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-09-22 11:51 | 2013-09-22 15:08 | 1 | 197 | 4877481 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT DOOR19.9 OLDER STYLE SHORTER THAN NEW ONESCALLING OTHER SERVICER FOR PARTS, CHANGE OUT CUT-OUT VER/CRB L/3 CRB
17552 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-04-03 05:08 | 2015-04-03 08:25 | 1 | 197 | 4261971 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT. WILL CHANGE. POWER IS RESTORED/ ISO 37830095000063/ COD 1 L3/DKGXXX
17553 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-05-13 12:48 | 2020-05-13 16:05 | 1 | 197 | 4832081 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | service drop tore from house//i put service back up and lights came on for split second//no voltage on sec.side ///need 15kva 19.9 xfmr//paul muncy going to replace xfmr// Released by crew 079S01
17554 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-04-08 20:28 | 2013-04-08 23:45 | 1 | 197 | 4989601 | 197 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND SEND TO JIM LINKOUS RELEASED BY CREW 078S08 // JIM LINKOUS & CHAD STONE & MIKE PHELPS (BAD CONNECTIONS IN SEC. PED. NEEDS REPLACED; INSTALLED POWER TEMP; SEND TICKET TO BOB REYNOLDS POWER RESTORED AT 23:45) --- SDB / REYNOLDS EMAILED. VER/SDB IDC CHANGED COUNT FROM 2 XXXX
17555 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2010-01-05 19:03 | 2010-01-05 22:20 | 1 | 197 | 62312-1 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER CALLED FROM DIFFERENT ADDRESS. 322 RT 993 IN WITTENSVILLE IS ACCT HE WAS CALLING ABOUT. FOUND FAILED CONNECTION ON XFMR POLE. ((ONLY ONE CUST AFFECTED)) RE-SQUEEZED CONNECTIONS ON XFMR POLE, REMOVED LARGE LIMB FROM SEC POLE AND CHANGED 100 WHPS ODL. RESTORED @ 10:20. SH RELEASED BY CREW 076S02 // CHANGE CUSTOMER CNT TO 1 VER/TOM IDCC SC, PN273 XXXX
17556 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2020-07-22 17:18 | 2020-07-22 20:35 | 1 | 197 | 4204331 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Vernon Checked and fuse is out on 38830164B13552 will need new current limiting fuse and can get truck to. bad 25kva. crew reqd. 19.9 Released by crew 078S04//on site RM xfm fuse in @20:35 please close tic RM
17557 | Pikeville | 3402002 | KEYSER | STONECOAL | 2019-05-29 11:19 | 2019-05-29 14:36 | 1 | 197 | 4359981 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kva / 7200 trans. on pole 1128-176, going to change this out on 5-30-19, no one lives at the cabin and customer is ok with this, going to work off ops #034297269.
17558 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2016-01-07 13:08 | 2016-01-07 16:25 | 1 | 197 | 4592831 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV CUTOUT, CREW REQUIRED. TRUCK OK RELEASED BY CREW 078S07 POWER RESTORED 16:25/ ISO 38830162C00030/ COD 1/ VER/BOW
17559 | Hazard | 3303901 | LESLIE | HYDEN | 2011-01-20 05:33 | 2011-01-20 08:50 | 1 | 197 | 62901-1 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / SPOKE W/ CUSTOMER, THEY REPORTED XFMR IS ARCING.//SERVICER STATES LOOKS LIKE CUTOUT HAD FAILED//SERVICER TO CHANGE CUTOUT//COD 1// VER/DBM IDCC TOF0511. ASSUMING SECOND CALL MAY BE OUTAGE NOT SURE XXXX
17560 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-03-01 13:43 | 2011-03-01 17:00 | 1 | 197 | 65492-1 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN, BAD C/O////REPLACED C/O, POWER RESTORED COD-1 ISO TF 37830203000093 VER/HFP L3/HFP IDC XXXX
17561 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-08-14 09:03 | 2020-08-14 12:20 | 1 | 197 | 4324081 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 25t out on pole 851-b-742 due to bad cutout tommy on the way with 3 new cutouts. cutouts replaced closed fuses back in @ 12:20
17562 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-12-30 05:33 | 2008-12-30 08:50 | 1 | 197 | 65072-1 | 197 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3001401// THIS WELL BE DIPATCHED AT 0730,,,,,BAD SERVICE CONNECTION ON POLE,,,,I MADE REPAIRS L3/HFP IDC XXXX
17563 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-03-21 21:58 | 2013-03-22 01:15 | 1 | 197 | 4946641 | 197 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND LEFT SERVICE OFF TRUCK TO POLE BRING TEMP. // TOLLIVER & MCCOY & YOUNGMAN//INSTALLED POWER TEMP NEED TO REPAIR UG ASAP SEND COPY TO L RAYBURN CLOSE TKT PRT// //VER/GAH IDC XXXX
17564 | Hazard | 3310502 | HADDIX | CANOE | 2009-02-16 19:48 | 2009-02-16 23:05 | 1 | 197 | 62784-1 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE#37830169C00072// 3310502 // SLEEVE PULLED LOOSE CREW WORKING ON LARGER OUTAGE NOW WILL CHECK THIS ASAP TONIGHT. VER/KEP L3/KEP
17565 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-06-10 11:43 | 2021-06-10 15:00 | 1 | 197 | 4705461 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 351-C-339.. will need 15 kva and 7200 cutout and bracket Released by crew 077S11 // repaired and restored @1500
17566 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2019-01-21 11:03 | 2019-01-21 14:20 | 1 | 197 | 4699841 | 197 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad insulink on hill/ repairs made/ please close ticket/ MLH
17567 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-01-16 18:51 | 2020-01-16 22:08 | 1 | 197 | 4314191 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse out, bad xfmr, will need big bucket and 25 kva , 19.9 kv Released by crew 077S02
17568 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2022-10-16 19:03 | 2022-10-16 22:20 | 1 | 197 | 4033691 | 197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout on pole 221-240 broke.blew line fuse on pole 221-020.will need a big bucket to make repairs..changes cutout on pole 221-240 and got line fuse on pole 201-020 closed in nd power restored at 22:20.
17569 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-10-27 08:14 | 2018-10-27 11:30 | 1 | 196 | 4331681 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout xfmr.in back yard.climber.changing
17570 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-01-30 08:29 | 2008-01-30 11:45 | 1 | 196 | 61961-1 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 27 KV CUTOUT----REPLACED COD-1 VER/KEP IDC XXXX
17571 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-03-28 09:17 | 2021-03-28 10:55 | 2 | 98 | 4390101 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//repairs made//restored at 10:55//complete//em/ 38830912D00012
17572 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-06-10 17:28 | 2009-06-10 19:06 | 2 | 98 | 53120-1 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANSF === CHANGED OUT CUTOUT & ARRESTER & T BRACKET == POWER OK//VER/CRB IDC XXXX
17573 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2016-12-28 22:19 | 2016-12-28 23:57 | 2 | 98 | 4247001 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOUD NOISE/DD LIGHTS OUT. OPENING GATE. FUSE IN @ 23:55 PLEASE SEND TO BRADSHAW FOR SOME TREES TO GET CUT UP HILL FROM FUSE POLE//SENT TO FORESTRY/AWD VER/AWD
17574 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-05-12 05:11 | 2015-05-12 08:27 | 1 | 196 | 4417711 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TALKED TO CUSTOMER AND HE SAID IT WAS O.K. TO WAIT UNTIL REG. SHIFT. BAD CUTOUT ON POLE 402-15, REPLACED CUTOUT RESTORED POWER AT 08:27.. ONLY ONE CUSTOMER AFFECTED./ ISO 37830402D00015/ COD 1/ VER/BOW
17575 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-04-30 08:14 | 2014-04-30 11:30 | 1 | 196 | 4650131 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6T FUSE OUT DUE TO BAD TRANSFORMER. NEED 25KVA 7200 CAN USE TRUCK. CALLED TIM HALL CREW WILL BE HEADED THIS WAY SEND ORDER TO TIM MCCOY RELEASED BY CREW 074S11 RELEASED BY CREW 074H10//COD 1// VER/DBM
17576 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-05-09 19:23 | 2018-05-09 19:51 | 7 | 28 | 4328921 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr//opened trans @ 1923 closed 1951//no outage till trans opened
17577 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-04-21 17:35 | 2021-04-21 20:51 | 1 | 196 | 4469061 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on pole 37830069000193 and burned the top of the pole off, paul layne is sending 2 men and big bucket to help with repairs//cutout failed on pole 69-103 and burned the top of the pole off, paul layne is sending 2 men and big bucket to help with repairs
17578 | Hazard | 3309302 | VICCO | JEFF | 2022-11-27 11:41 | 2022-11-27 14:57 | 1 | 196 | 4184161 | 196 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I replaced a bad XFMR lug on manual pole 37-9, power restored at 14:57.
17579 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-11-15 10:42 | 2011-11-15 12:20 | 2 | 98 | 4078601 | 196 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | A PHASE ONLY OPEN ON 120/240 TRANSFORMER BANK , NO SINGLE PHASE CUSTOMERS AFFECTED, TWO 3 PHASE CUSTOMERS LOST HIGH VOLTAGE LEG . FUSE LINK BROKEN, REFUSED TRANSFORMER , ALL WORK COMPLETE / GXJ ///VER/CRB IDC XXXX
17580 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2013-06-30 22:43 | 2013-07-01 00:21 | 2 | 98 | 4432941 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 424-201, REPLACED CUTOUT RESTORED POWER AT 00:21 ONLY 2 CUSTOMERS AFFECTED. VER/TOM L3/TOM
17581 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-08-11 14:14 | 2011-08-11 17:30 | 1 | 196 | 4697491 | 196 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER ,SECONDARY LEAD BURNT INTO AT XFMR BANK.. MADE REPAIRS RESTORED POWER AT 17:30 COD-1 ISO TF 37830399000327 VER/HFP L3/HFP IDC XXXX
17582 | Hazard | 3303902 | LESLIE | WOOTON | 2009-05-04 13:14 | 2009-05-04 14:52 | 2 | 98 | 51463-1 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303902//BAD 25KVA 120/240 XFMR RELEASED BY CREW 077S01 VER/KEP L3/KEP IDC XXXX
17583 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2014-08-20 20:49 | 2014-08-21 00:05 | 1 | 196 | 4392411 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON 902-499 DOOR BURN UP REPLACE CUTOUT DOOR 10T POWER RESTORED.PRI DOWN GUY BROKE ON SAME POLE WILL NEED NEW ANCHOR INSTALLED NO TR. SEND COPY TO RAYBURN// EMAILED RAYBURN ADH// COD 1// VER/ ADH
17584 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-06-30 09:05 | 2020-06-30 12:21 | 1 | 196 | 4092841 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection heated up burning down drop replacing.
17585 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2015-04-23 16:27 | 2015-04-23 18:05 | 2 | 98 | 4360161 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED INTO AT POLE 329-65, REFUSED AT 1805, ALL POWER RESTORED. VER/CRB
17586 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-03-22 10:34 | 2012-03-22 13:50 | 1 | 196 | 4605271 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER BUD JOHNS TRANSFORMER ON POLE 38830452000157 IS BAD NEEDS REPLACED. COD-1 ISO TF 38830452000157 VER/HFP L3/HFP IDC XXXX
17587 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-02-05 15:07 | 2011-02-05 16:45 | 2 | 98 | 54395-1 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT AT LIN E FUSE OPEN LINE AT 20-284 AT 16;28 BACK ON AT 16;45 BAD CUT OUT IS CHANGE ALL POWER RESTORED FUSE 15-T//COD 2//MD FILED// IDCC CNT5, PN346 XXXX
17588 | Pikeville | 3421001 | BREAKS | CITY | 2014-03-29 15:51 | 2014-03-29 16:40 | 4 | 49 | 4534741 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37820243D00034 NEED 3 CUTOUTS AND 2 8 ARMS AND BRACES. WILL NEED A 3 MAN CREW, NO TRUCK ACCESS. THE CHURCH IS OK WITH US DOING THIS NEXT WEEK RELEASED BY CREW 074S02 VER/KEP
17589 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-10-28 20:45 | 2010-10-29 00:01 | 1 | 196 | 66419-1 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFORMER. RELEASED BY CREW 078S01 POWER RESTORED AT 00:01 CC 1 VER/PDP IDC XXXX
17590 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-09-08 10:07 | 2015-09-08 13:23 | 1 | 196 | 4212991 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | GOING TO CHANGE ARRESTORS AND TWO CUTOUTS// VER/ ADH
17591 | Whitesburg | 3312902 | JENKINS | JENKINS | 2018-12-04 15:09 | 2018-12-04 18:25 | 1 | 196 | 4507451 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 382-169,manual pole on hillside.restored power at 18:25 L3/HFP
17592 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-01-10 07:38 | 2020-01-10 10:54 | 1 | 196 | 4229681 | 196 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | red-red serve-in pulled apart ,I replaced it
17593 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-02-18 11:17 | 2016-02-18 14:33 | 1 | 196 | 4732761 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION ON TRANSFORMER/ ISO 37830195000151/ COD 1/ VER/BOW
17594 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2020-10-11 11:49 | 2020-10-11 15:05 | 1 | 196 | 4544881 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | big bucket required lead broke on top of cutout /send to b tackett Released by crew 078S03,repairs made all cust restored @ 1505 please close ticket thanks.bt
17595 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-09-12 12:11 | 2014-09-12 13:00 | 4 | 49 | 4493681 | 196 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY CONNECTION ON TRANSFORMER LEAD. VER/CRB
17596 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-11-28 16:06 | 2016-11-28 16:55 | 4 | 49 | 4134711 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE ON 1077-D-348 FAILED DUE TO AGE RESTORED POWER AT 16:55 VER/CRB
17597 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-12-21 00:12 | 2022-12-21 01:50 | 2 | 98 | 4282161 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke Trans Cutout at pole 335-D-231,Will be making repairs.Restored at 01:50.
17598 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-06-23 23:39 | 2008-06-24 01:17 | 2 | 98 | 53308-1 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED XFMR. SH VER/ARN IDCC CNT1 XXXX
17599 | Hazard | 3308001 | JACKSON | S.JACKSON | 2016-01-12 16:14 | 2016-01-12 19:30 | 1 | 196 | 4612521 | 196 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LEAD FROZE OUT ON TR POLE -100 KVA NEED 1 MAN BUCKET--FETR 1930-V HURT COMING OUT/ ISO 38831108A00271/ COD 1/ VER/BOW
17600 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-09-25 18:48 | 2015-09-25 19:37 | 4 | 49 | 4271131 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED CONNECDTION// VER/ ADH
17601 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-09-26 15:34 | 2018-09-26 18:50 | 1 | 196 | 4162291 | 196 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connector on hot line clamp broke ,I replaced it
17602 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-06-23 13:52 | 2015-06-23 15:30 | 2 | 98 | 4644931 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT 37830328D00187/ ISO 37830328D00187/ COD 2/ BAD 19.9 CUTOUT POWER RESTORED OPEN LINE FUSE AT 15:10 CLOSED AT 15:30 L3/DKG THISOUTAGE FOR ORIGINAL TRANSFORMER ..SEE H4644931 FOR OPENING OF LINE FUSE
17603 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-06-27 14:29 | 2015-06-27 17:45 | 1 | 196 | 4679431 | 196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR OUT ON POLE 174B-100 . FUSE BROKE , CLOSED XFMR @ 17:45 VER/KEP
17604 | South Williamson | 3411401 | DEWEY | INEZ | 2009-06-02 19:00 | 2009-06-02 20:05 | 3 | 65 | 61393-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT BROKE L3/HFP
17605 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2010-12-09 15:50 | 2010-12-09 16:55 | 3 | 65 | 64899-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT ON POLE 139A40. LOOKS LIKE FUSE WAS BROKEN. FUSED TRANSFORMER UP EVERYTHING OK.//VER/CRB IDC XXXX
17606 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2014-10-25 09:53 | 2014-10-25 13:08 | 1 | 195 | 4660701 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | ELBOWE POPED OFF IN UG XFMR .CANNOT USE HOT STICK BECAUSE OF FENCE IS TOO CLOSE. HAVE A MAN & MATERIAL HANDLER ON THE WAY TO PULL PRIMARY RISER OFF . VER/CRB
17607 | Pikeville | 3421001 | BREAKS | CITY | 2009-06-12 14:35 | 2009-06-12 17:50 | 1 | 195 | 57245-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 37820243B00014, BROKEN CUTOUT ON POLE 37820243B00179, WILL REPLACE AND REFUSE/////POWER RESTORED @ 17:50 VER/KEP L3/KEP
17608 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-01-22 17:45 | 2010-01-22 21:00 | 1 | 195 | 58266-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33562550 BAD CUTOUT COD-1 VER/HFP L3/HFP IDC XXXX
17609 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-09-27 21:28 | 2010-09-27 22:33 | 3 | 65 | 54491-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#37072328 POLE 19-63 BAD CUTOUT OPENED REC. ON POLE 1147-187 22;10 CLOSED 22;33//SEE OTHER OUTAGE FOR 152 COD//VER/CRB IDC XXXX
17610 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-04-29 06:12 | 2013-04-29 09:27 | 1 | 195 | 4055161 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK AT NORMAL START TIME XFORM FUSE, AN CURRENT LIMIT FUSE REPLACED ON 113-54 POWER RESTORED 09;27 1 CUST//COD 1//ISO 38830113000054//MD FILED// VER/DBM IDC XXXX
17611 | Hazard | 3310502 | HADDIX | CANOE | 2016-02-15 13:55 | 2016-02-15 15:00 | 3 | 65 | 4697541 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS OLD & BROKE VER/CRB L/3 CRB
17612 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-03-22 15:55 | 2018-03-22 19:10 | 1 | 195 | 4043281 | 195 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | splice in service drop 1 leg pilled apart/ ISO 37830127000003/ COD 1
17613 | Hazard | 3309302 | VICCO | JEFF | 2017-02-04 09:57 | 2017-02-04 11:02 | 3 | 65 | 4358371 | 195 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ***SEE H4358371*** OPEN TRANSFORMER AT 10:50 AND CLOSE AT 11:02///TRANSFORMER LEAD CONNECTION FAILED AT OPEN SECONDARY POINT DUE TO LOAD/ PER SERVICER THERE WAS 3 CUSTOMERS PART POWER ORIGINALLY/ ISO 37830348A00135/ COD 10/ VER/BOW L3/HFP HFPC MCCDL
17614 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-03-21 15:27 | 2010-03-21 16:06 | 5 | 39 | 52240-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ,,,,BACK ON MAY HAVE BEEN A BAD FUSE EARLIER ON TICKET 52208,,,//COD 5// VER/DBM IDC FUSE PULLED APART XXXX
17615 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2017-02-28 13:39 | 2017-02-28 13:52 | 15 | 13 | 4428601 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD LINE CUT-OUT ON POLE 469-01 ON CIRCUIT INSPECTION. CHANGED CUT-OUT BEFORE IT CAUSED A PROBLEM. OPENED LINE FUSE AT 13:39 AND CLOSED BACK IN AT 13:52 VER/CRB
17616 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-10-14 17:45 | 2010-10-14 21:00 | 1 | 195 | 59697-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE TO BE CHANGED TODAY, PAT STAMPER PREPARING WO.YARD DOG JOB. LMR. WINDSTREAM POLE 40-4. 25 KVA D/E./REPAIRS COMPLETE CUST OUT FROM 17:45 TILL 21:00 J. HEMLEPP RELEASED BY CREW 078H05// VER/DBM IDCC TOF1253 XXXX
17617 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2012-12-26 08:20 | 2012-12-26 11:35 | 1 | 195 | 4519161 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE A BAD 10 KVA SINGLE BUSHING TRANSFORMER, CREW REQ, CAN GET TRUCK TO POLE, FIRST GRAVEL DRIVE WAY ON LEFT AFTER TURNING OFF 503 UP ON HILL RELEASED BY CREW 078S06,ALL CUST RESTORED @1135 PLEASE CLOSE TICKET THANKS.BT //VER/GAH
17618 | Hazard | 3303902 | LESLIE | WOOTON | 2016-10-27 16:36 | 2016-10-27 19:51 | 1 | 195 | 4058741 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 077H07////FUSE BROKE VER/AWD L3/HFP XXXHFP
17619 | Hazard | 3302704 | HAZARD | KENMONT | 2009-03-14 19:20 | 2009-03-14 20:25 | 3 | 65 | 58557-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3302704 -// BAD 7200 CUTOUT ON XFMR AT POLE 37830296C41348// OPENED LINE FUSE ON POLE 37830296C41348 AT 19:20 AND CLOSED AT 20:25 // VER/TOM L3/TOM IDCC CNT1 XXXX
17620 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-02-27 22:30 | 2011-02-27 23:35 | 3 | 65 | 63591-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN WILL REFUSE---FUSE BROKE. CC=3 VER/SDB IDC XXXX
17621 | Hazard | 3310502 | HADDIX | CANOE | 2012-06-12 10:40 | 2012-06-12 11:45 | 3 | 65 | 4905801 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REMADE CONNECTIONS AT THE TRANSFORMER//COD 3// VER/DBM IDC XXXX
17622 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2022-07-03 15:21 | 2022-07-03 16:00 | 5 | 39 | 4371061 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Broken fuse, restored @ 16:00
17623 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-11-08 06:16 | 2009-11-08 07:21 | 3 | 65 | 50725-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001203//-BROKEN FUSE LINK VER/PDP IDC XXXX
17624 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-01-30 15:51 | 2008-01-30 19:06 | 1 | 195 | 62440-1 | 195 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTOMER HAS PART POWER - ONE LEG OF SECONDARY BURNT DOWN, CUSTOMER HAS AGREED TO WAIT UNTIL TOMORROW 01/31/08 FOR REPAIRS. EMAILED DAVID SAMMONS & JACKIE ADKINS THE TROUBEL CALL PER DONNIE JACKSON, HE HAS MADE DAVID AWARE OF WHAT IS NEEDED TO MAKE REPAIRS TOMORROW. VER/HFP IDCC MCCNI XXXX
17625 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2013-03-01 20:00 | 2013-03-01 23:15 | 1 | 195 | H4865831 | 195 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 SIDE OF UNDERGROUND SER. IS ONLY GETTING 105 VOLTS///CREW ENROUTE // MASSEY & LAYNE & RICK RAY1 SIDE OF UNDERGROUND SER. IS ONLY GETTING 105 VOLTS///CREW ENROUTE// SPLICE FAILED INSIDE CONDUIT// REPAIRED SPLICE// POWER IS RESTORED// NEEDS R2D2 SET AT FOOT OF POLE TO GET OLD SPLICES OUT OF CONDUIT UP POLE DUP OF 4865831 FOR 1 CUST WHEN TR WAS OPENED //// VER/HFP L3/HFP
17626 | Hazard | 3303902 | LESLIE | WOOTON | 2014-10-10 11:40 | 2014-10-10 14:55 | 1 | 195 | 4602191 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER FOUND BROKE OUT ON POLE 437-17 RELEASED BY CREW 077S01SERVICER FOUND BROKE OUT ON POLE 437-17 REPLACED 19.9 CUTOUT// COD 1// VER/ ADH
17627 | Hazard | 3309301 | VICCO | REDFOX | 2018-05-23 11:15 | 2018-05-23 14:30 | 1 | 195 | 4401641 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr on cap bank, ..repaired p.hicks//REMOVED FROM AED
17628 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2018-12-11 09:30 | 2018-12-11 12:45 | 1 | 195 | 4551341 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | SCEDULE OUTAGE TO REPLACE PADMOUNT XFER OFF @ 0930 ON @ 1245 replaced bad pad mt xfrm an under ground primary L3/HFP
17629 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2008-08-27 16:55 | 2008-08-27 18:00 | 3 | 65 | 56480-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3402202// B PHASE LINE FUSE OUT ON POLE 42C184. FILD VIEW SHOWES TO BE 80T.BUT IT HAD A 50T FUSE. REPLACED BAD ARRESTER ON POLE 42-346. FUSED UP AT POLE 42C184 E VERYTHANG OK.//COD 3//ISO 37830042C00184// VER/DBM IDC XXXX
17630 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2014-03-08 22:26 | 2014-03-08 23:05 | 5 | 39 | 4462291 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/KEP IDC XXXX
17631 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-02-05 14:30 | 2014-02-05 15:09 | 5 | 39 | 4358301 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER TO SAFELY RE-WORKL SECONDARY VER/TOM L3/TOM
17632 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-12-26 11:15 | 2016-12-26 14:30 | 1 | 195 | 4237881 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NO TRUCKS CREW REQUIRED, 12KV CUTOUT RELEASED BY CREW 078S11,REPAIRS MADE ALL CUST RESTORED @ 1430 PLEASE CLOSE TICKET THANKS.BT VER/CRB
17633 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2009-04-10 08:14 | 2009-04-10 11:29 | 1 | 195 | 50934-1 | 195 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD 1/0 UG--CALLING CREW--SEND TO V MULLINS RELEASED BY CREW 078S07 **** AT 1109 SERV OPENED TR TO INSTALL AUTO TR.BAD 1/0 UG--CALLING CREW--SEND TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE/INSTALLED TEMP XFMR/PLEASE COPY D.HUFF TO SCHEDULE U/G REPAIR/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
17634 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-04-23 11:50 | 2010-04-23 12:05 | 13 | 15 | 66641-1 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED RECLOSER TO ALLOW THEM TO SAFELY REPLACE CUTOUT // SEE 66618-1 VER/HFP L3/HFP IDC XXXX
17635 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-01-14 12:30 | 2012-01-14 13:35 | 3 | 65 | H4260541 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ALL 3 RECLOSERS SEEM TO BE IN ON POLE 263-377. I AM GOING BACK ON MOUNTAIN AND MAKE SURE THE TRANS. SERVING THE AEP TOWER IS ENERGIZED. OPENED "A" PHASE SWITCH AT POLE 264-49 TO ISOLATE BROKEN INSULATOR ON POLE#264-50 . WE OPENED THE OTHER 2 PHASES ON POLE 264-49 AT 12:30, CHANGED INSU VER/KEP IDC XXXX
17636 | Whitesburg | 3312902 | JENKINS | JENKINS | 2011-07-13 20:10 | 2011-07-13 23:25 | 1 | 195 | 4544031 | 195 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CHECKING. BAD CSP TRANS. ON 382-275, WILL NEED ONE MAN, BIG BUCKET, C/O, AND BRACKET AND ALSO 25 KVA TRANS.CHANGED TRANS., RESTORED BOTH CUST. AT 23:25//COD 1//ISO 37830382A20275// VER/DBM IDC XXXX
17637 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2012-06-20 13:25 | 2012-06-20 14:30 | 3 | 65 | H4935161 | 195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER WILL BE DISPATCHED AT REG WK TIME. FOUND BAD ENCLOSED WESTING HOUSE CUTOUT ON POLE 903-28, WELL NEED CREW TO CHANGE THIS ON HILLSIDE, NO TRUCKS TO THIS POLE, WELL HAVE ONE CUST STILL OFF, CREW REQ 39830903000028 HAVE POWER RESTORED AT THIS TIME TO ALL CUST BUT ONE, TIME ON WAS 1000 RELEASED BY CREW 078S06..OPENED FUSE ON 903-2 @ 13:25 TO SAFELY MAKE REPAIRS.OPENED FUSE ON 903-2 @ 13:25 TO SAFELY MAKE REPAIRS.POLE 903-28 IS ROTTEN AT THE TOP AND THE BOTTOM.NEEDS ATTN VERY SOON..BLR RELE IDC XXXX
17638 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-03-23 10:47 | 2022-03-23 14:02 | 1 | 195 | 4661011 | 195 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a bad connection at weatherhead Hot leg burned into also burning Neutral into,Going to Pull Meter and make repairs..Restored at 14:02.
17639 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-03-28 18:48 | 2009-03-28 22:02 | 1 | 194 | 62500-1 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT VER/PDP IDC XXXX
17640 | South Williamson | 3200302 | BELFRY | TOLER | 2012-08-28 22:03 | 2012-08-28 23:40 | 2 | 97 | 4982091 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE..FUSE LINK JUST BROKE...//.REPLACED FUSE..JRV..08/28/12 IDC XXXX
17641 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-07-29 20:07 | 2015-07-29 23:21 | 1 | 194 | 4957641 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 44-4556 BAD 10-12 TRANS. SER 3353821 REMOVED OLD CUTOUT AND LA INSTALLED NEW CUTOUT RELEASED BY CREW 078S08/CREW WORKING ON OUTAGE/FETR0030/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2321/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830044C24556/ COD 1/ VER/BOW
17642 | South Williamson | 3202201 | LOVELY | LOVELY | 2016-12-24 16:36 | 2016-12-24 19:50 | 1 | 194 | 4235361 | 194 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE IN SERVICE DROP BURNED OUT MADE REPAIRS AND RESTORED POWER/ ISO 38820746D30324/ COD 1/ VER/BOW
17643 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-11-04 12:45 | 2021-11-04 14:22 | 2 | 97 | 4057281 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse droped out. Closed tranformer @ 14:22
17644 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-04-19 07:41 | 2018-04-19 09:18 | 2 | 97 | 4254341 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE 3-71 CUTOUT BROKEN,WILL REPLACE COD-2 ISO LF 37820003000037LINE 3-71 LINE CUTOUT BROKEN,WILL REPLACE//////////REPLACED CUTOUT&RESTORED POWER
17645 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-10-01 10:01 | 2011-10-01 13:15 | 1 | 194 | 4937191 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE APPEARS TO HAVE MELTED OUT. MAY HAVE BEEN A WEAK FUSE - WILL TRY TO RE-FUSE. RE-FUSED @ 13:15. ADVISED CUSTOMER TO CALL IF IT GOES BACK OUT AND WE WOULD CHANGE XFMR BUT I THINK IT WAS JUST FUSE FAILURE. BEEN ON OVER 10 MINUTES. SH COD-1 ISO TF 38830801000164 VER/HFP L3/HFP IDC XXXX
17646 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2021-03-06 14:01 | 2021-03-06 15:52 | 2 | 111 | 4310051 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | One of hot legs has burned into on service drop going to open Trans on 73-D-231 and replace service wire will keep up with Time.Opened at 14:29 made repairs and restored at 15:52..//part power from the beginning
17647 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-05-12 10:23 | 2022-05-12 12:00 | 2 | 97 | 4880941 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broken. changing..
17648 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2019-11-18 16:08 | 2019-11-18 17:45 | 2 | 97 | 4045171 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | METERING 480 PT FAILED HAD TO OPEN UP TRANSFORMER TO MAKE REPAIRS POWER OFF AT 1608 AND ON AT 1745, CUSTOMER WAS AWARE OF OUTAGE
17649 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-10-26 13:20 | 2019-10-26 16:34 | 1 | 194 | 4198921 | 194 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | changd out drop--????--allgood-ds102619
17650 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2016-09-17 10:31 | 2016-09-17 13:45 | 1 | 194 | 4900781 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1.6T FUSE BROKE. FUSED UP EVERYTHING OK. LEFT CUST METER BASE CONECTIONS IN METER BASE AND DISCONNECT ARE NOT VERY GOOD AT SOME POINT HE IS GOING TO CHANGE EVERYTHING OUT WANTED POWER LEFT ON FOR NOW VER/CRB
17651 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2021-03-31 12:58 | 2021-03-31 14:35 | 2 | 97 | 4407841 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke line fuse cutout on pole 171-C-8,got it opened up and fire put out on pole,Going to change cutout and restore service..Restored at 14:35.
17652 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2011-04-06 10:11 | 2011-04-06 11:48 | 2 | 97 | 50415-1 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WR#39460374 POLE 70-1011 HOT TAP BROKE OFF 6T TRANS. FUSE MELTED OUT REPAIRED//VER/CRB
17653 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2016-02-06 11:03 | 2016-02-06 12:40 | 2 | 97 | 4680691 | 194 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAD ONE BAD CONN AT WEATHER HEAD, REPLACED BOTH CONN, APR AT 1240 CLOSE TICKET// VER/ ADH
17654 | Pikeville | 3421001 | BREAKS | CITY | 2013-03-06 08:22 | 2013-03-06 11:36 | 1 | 194 | 4879171 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED OFF LINE ON PRI. METERING. WE ARE GOING TO REPLACE HOT TAP. WE REPLACED HOTTAP. VER/TOM L3/TOM IDC XXXX
17655 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-09-26 11:36 | 2011-09-26 14:50 | 1 | 194 | 4918011 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BROKEN 6-T FUSE LINK POWER RESTORED COD-1 ISO TF 38830044C24546 VER/HFP L3/HFP IDC I BELIEVE THIS IS INCORRECT POLE NUMBER CHANGE FROM 38830044C24546 XXXX
17656 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-06-28 13:16 | 2020-06-28 16:30 | 1 | 194 | 4084331 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke line fuse cutout,Will have to climb pole to make repairs,To wet to get truck into pole,Will get back with u on restoration time..Got line fuse back in at 16:30..
17657 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-10-19 10:41 | 2018-10-19 12:18 | 2 | 97 | 4269771 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t transformer fuse broke pole 1148-320 fused up everything ok
17658 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-09-26 16:20 | 2009-09-26 19:34 | 1 | 194 | 63647-1 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, OPEN TRANSFORMER AT 1620 RELEASED BY CREW 077S05 VER/KEP L3/KEP IDCC TOF0950 XXXX
17659 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2019-01-27 06:07 | 2019-01-27 09:21 | 1 | 194 | 4725561 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burnt down will make repairs/// Replaced service drop and restored service @ 09:21/// good voltage now 124/124/248/// only 1 customer affected
17660 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-07-14 08:03 | 2010-07-14 09:40 | 2 | 97 | 66665-1 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD ARRESTOR ON POLE # 109-5, GOING TO LINE FUSE NOW//VER/CRB IDC XXXX
17661 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2019-08-07 10:00 | 2019-08-07 11:37 | 2 | 97 | 4852401 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse tail broken, refused txmf apr at 1137 close ticket. dwest
17662 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-04-06 21:23 | 2012-04-06 23:00 | 2 | 97 | 4653221 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK ROTTED AND BROKE I REPLACED FUSE AND POWER IS RESTORED AT THIS LOC //VER/GAH IDC XXXX
17663 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-02-06 18:51 | 2018-02-06 22:05 | 1 | 194 | 4810071 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer- customer see cutout hanging open on transformer. cutout broke, crew reqd. truck accessible. cutout isolated. Released by crew 078H17. cutout changed, power restored at 22:05/ ISO 38830526000010/ COD 1
17664 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-03-08 12:46 | 2009-03-08 16:00 | 1 | 194 | 56208-1 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15VA TRANSFORMER ON POLE 1197-78. TRANSFORMER FEEDS SMALL CHURCH ONLY. SHOULD REPLACE WITH 25KVA RELEASED BY CREW 078S04/VER/CRB IDCC PN152 XXXX
17665 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2020-04-19 08:33 | 2020-04-19 10:10 | 2 | 97 | 4719351 | 194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burned up will replace
17666 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-03-01 18:57 | 2016-03-01 22:10 | 1 | 193 | 4794191 | 193 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER//HOT LEG CONECTION BURNED INTO ON SEC. POLE//REWORKED CONNECTIONS//RESTORED TO NORMAL AT 22:10// VER/KEP
17667 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-07-01 18:07 | 2021-07-01 21:20 | 1 | 193 | 4839961 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cut-out on 37840528000088. Power restored @ 21:20
17668 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-01-27 09:16 | 2010-01-27 12:29 | 1 | 193 | 60295-1 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER BUD JOHNS, THIS IS A BAD 15KVA 7200 XFMR// NO TRUCK TO POLE //MCCARTY TO ASSIGN CREW// STS WR# 33618787 // 1521 WILLIAMS CR OFF OF RT 1654//COD 1// VER/DBM IDC XXXX
17669 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-12-21 12:02 | 2014-12-21 15:15 | 1 | 193 | 4873201 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | HAD A BAD CURRENT LIMTING FUSE..REPAIRED 15:15/ ISO 37830190B00178/ COD 1/ VER/BOW
17670 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-12-16 08:12 | 2017-12-16 11:25 | 1 | 193 | 4652751 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse broken, replaced fuse and restored power at 1125/ ISO 37830379B00486/ COD 1
17671 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-01-12 14:09 | 2018-01-12 17:22 | 1 | 193 | 4736911 | 193 | PARTIAL POWER | EQUIPMENT FAILURE | POLE | Send Copy of complted ticket to T. Hall : pole 37830041B00123 is rotted and leaning and guy wire broken, breaking neutral in 4/3 sd , added slack to 1/0 lash secondary and 3 4/3 sds , added guy marker for insulation to one sd contacting metal roof, pole appears to be stable enough to replace next week . Truck Access: will need 35 - 5 pole, 50 ft guy wire and anchor, 1/0 triplex and 2/3 triplex for splicing / GXJ//SENT TO LINE DEPT
17672 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-12-16 14:46 | 2009-12-16 17:59 | 1 | 193 | 66344-1 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33104694 // NEED A 10 KVA 7.2 KV TRANSFORMER , CUTOUT & ARRESTOR - TRUCK CAN REACH ADDRESS IS 245 3 MILE CREEK RD TURN RT THRU GREEN GATE ON THREE MILE RD UP STEEP HILL CUSTOMER WILL SHOW YOU THE LOCATION OF TRANSFORMER./CREW ON SITE/FETR1855/VEM/REPAIRS MADE/BAD CUTOUT ONLY LIGHTS OUT/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP L3/HFP
17673 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2018-01-06 23:32 | 2018-01-07 02:45 | 1 | 193 | 4714051 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 service burndt down mid span off of pole 98-A-273, may have to open trans. to maqke repairs, only 1 cust. out right now, will keep track of times. Opened trans. on 273 @0130, cleared service and put back on @0135, made repairs to last customer @0245.
17674 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-12-28 16:30 | 2017-12-28 19:43 | 1 | 193 | 4686311 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN AM/ not sure if xfmr is bad could not refuse bad cutout gate fiberglass type, fuse was blown,need cutout arrester t-bracket, would bring 15 kva xfmr just in case truck acess ,compresser station just past hollins frk 12kv Released by crew 077H14/ Spoke with customer and they were ok with waiting until in the morning to restore/ Ops Order #033978838 in V. Hurt spectrum crew
17675 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-08-30 11:12 | 2016-08-30 14:25 | 1 | 193 | 4851851 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DUE TO PRIMARY NEUTRAL DOWN BETWEEN POLE 140-103 AND 140-94. BURNT HOT WIRE INTO ON SERVICE DROP CREW ON THE WAY. TO PUT WIRE BACK UP. WE HAVE WIRE UP REPAIRS MADE EVERYTING OK 37830140B00103 VER/AWD
17676 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-08-23 23:47 | 2010-08-24 03:00 | 1 | 193 | 59796-1 | 193 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | SERVE END BURNED INTO IDC XXXX
17677 | Hazard | 3303901 | LESLIE | HYDEN | 2021-03-08 16:47 | 2021-03-08 20:00 | 1 | 193 | 4316671 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
17678 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-01-23 15:17 | 2020-01-23 18:30 | 1 | 193 | 4332821 | 193 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer stated he was having dim lights.customers service drop had several splices in it. replaced service drop/ ISO 37820035A00011/ COD 1
17679 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2008-04-10 05:47 | 2008-04-10 09:00 | 1 | 193 | 65609-1 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3400602//TRANSFORMER ON 212 IS NOT OUT, RECENTLY INSTALLED TRANSFORMER WITH 1 CUSTOMER IS OUT ON POLE 188-2 / GXJ .....FUSE BROKEN, REPLACED 6T FUSE, ALL WORK COMPLETE / GXJ//ISO// VER/DBM IDC XXXX
17680 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-11-15 16:02 | 2022-11-15 19:15 | 1 | 193 | 4145701 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse on pole 37830490A30182 broke, tap feeds one cust.cust not home but will need an A lineman and a big bucket to replace line fuse cutout. repairs made.got power restored @19:15
17681 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2013-11-12 13:32 | 2013-11-12 16:45 | 1 | 193 | 4032341 | 193 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELOCATED SERVICE TO MIDSPAN VER/CRB
17682 | Pikeville | 3413402 | GARRETT | LACKEY | 2013-06-28 11:02 | 2013-06-28 14:15 | 1 | 193 | 4420611 | 193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP FELL OFF OF PRIMARY GOING TO TRANSFORMER CUTOUT. REPLACED CUTOUT RISER EVERYTHING OK. VER/CRB L/3 CRB
17683 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2020-07-11 17:11 | 2020-07-11 18:15 | 3 | 64 | 4153301 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced door
17684 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-06-09 23:28 | 2013-06-10 02:40 | 1 | 192 | 4246811 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED OFF// WILL TRY TO REPAIR// REPLACED HOT TAP & STIRRUP ON 38831152000128// POWER IS RESTORED. VER/SDB
17685 | South Williamson | 3411401 | DEWEY | INEZ | 2014-06-14 23:56 | 2014-06-15 01:00 | 3 | 64 | 4092391 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 792-23//REPAIRS MADE//RESTORED AT 1:00/COMPLETE//EM
17686 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-02-14 09:26 | 2013-02-14 10:30 | 3 | 64 | 4819001 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNED UP CLIMBING POLE TO REPAIR//COD 3// VER/DBM IDCC PN201 XXXX
17687 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-04-02 21:18 | 2015-04-03 00:30 | 1 | 192 | 4260861 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARM BURNT OFF AT POLE963C134 PHASE IS HANGING IN MIDAIR NEED CREW AND BIG BUCKET CUSTOMER SAID WE CAN GET IN THEIR YARD TO MAKE REPAIRS .// NO POWER OUT UNTIL 2118 WHEN B PHASE RECL OPENED DUE TO PHASE ON TELEPHONE CABLE (50 CUST) // OPENED A & C PHASE @ 2330 (83 CUST) /// ALL ON @ 0030 04/03
17688 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2017-04-07 16:02 | 2017-04-07 19:14 | 1 | 192 | 4628841 | 192 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER//NO OUTAGE TILL FUSE OPENED @ 1809//CLOSED 1914// VER/CRB /// DUPLICATING FOR LINE FUSE OUTAGE - PER 1ST CALL CUST HAD PART POWER = L3/HFP HFPC DUP
17689 | South Williamson | 3411401 | DEWEY | INEZ | 2008-09-06 13:14 | 2008-09-06 14:50 | 2 | 96 | 59952-1 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD//3411401//VER/CRB IDC XXXX
17690 | South Williamson | 3411401 | DEWEY | INEZ | 2016-05-30 16:12 | 2016-05-30 17:48 | 2 | 96 | 4272631 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 671-540//I RPALCED CUTOUT//RESTORED AT 17:48//COMPLETE//EM VER/CRB
17691 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2016-02-22 10:15 | 2016-02-22 10:27 | 16 | 12 | 4746081 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 785-772.OPENED CUTOUTS ON P-785-587 AT 10.15 AM..BACK ON AT..10.27.. ISO 38830785D20772 COD 16. VER/AWD
17692 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-12-05 20:51 | 2009-12-06 00:03 | 1 | 192 | 59581-1 | 192 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN 2/3 SERV WENT BAD == REPAIRED SERV == POWER OK VER/LDA IDC XXXX
17693 | South Williamson | 3411401 | DEWEY | INEZ | 2015-12-06 06:56 | 2015-12-06 08:00 | 3 | 64 | 4513161 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 0702 DDC CALLED CUSTOMER, NO RESPONSE//CUTOUT BROKE ON 744-323//REPAIRS MADE//RESTORED AT 8:00//COMPLETE//EM//COD 3// VER/DBM
17694 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2021-03-10 05:21 | 2021-03-10 06:57 | 2 | 96 | 4321101 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt up/repairs made. pls close. tre
17695 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2016-01-31 15:19 | 2016-01-31 16:55 | 2 | 96 | 4661651 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ 271-249 BAD CUTOUT @ 271-249 REPAIRS MADE ALL CUST RESTORED @ 1655 PLEASE CLOSE TICKET THANKS.BT VER/CRB
17696 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-11-29 09:55 | 2020-11-29 12:01 | 2 | 126 | 4727961 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Secondary burned into on pole 37820121D20371,Opened Transformer on pole 121-360 to safely squeeze back up secondary to service drop.Secondary burned into on pole 121-371,Opened Transformer on pole 121-360 to safely squeeze back up secondary to service drop.Opened Trans at 10:55 made repairs and restored at 12:01...
17697 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-12-12 13:54 | 2020-12-12 15:30 | 2 | 96 | 4763331 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
17698 | South Williamson | 3200302 | BELFRY | TOLER | 2015-11-27 19:11 | 2015-11-27 20:15 | 3 | 64 | 4488831 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST THEY REPORT NUMEROUS OTHERS OUT// BAD TRANSFORMER CUTOUT ON POLE 38821015A00019. ONLY THREE CUSTOMERS OUT. CUTOUT REPLACED, POWER RESTORED.//MADE MDC TO SHOW MIS-MAPPED CUST// VER/CRB
17699 | Hazard | 3307301 | BULAN | ARY-HEINE | 2020-05-07 08:07 | 2020-05-07 09:43 | 2 | 96 | 4808701 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BBad arrester power on
17700 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-12-02 04:07 | 2014-12-02 05:11 | 3 | 64 | 4824501 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TICKET 4824151 3CC VER/ARN
17701 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2013-11-01 12:20 | 2013-11-01 13:56 | 2 | 96 | 4996761 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR WAS BURNT UP. APR AT 1356. CLOSE TICKET FUSE NEVER OUT OPENED IT TO BE ABLE TO CLOSE ORDER - POWERON DID NOT RESTORE TR COD-2 ISO TF 38830454B22565 VER/HFP L3/HFP
17702 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-02-23 17:05 | 2016-02-23 17:53 | 4 | 48 | 4751751 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, BAD CUTOUT, CROSSARM IS BURNTED MAY NEED TO CHANGE CROSSARM, 8 FT CROSSARM AND CUTOUT, WILL NEED AWP RELEASED BY CREW 078S06/CREW ON SITE/NO OUTAGE AT THIS TIME/OPENING XFMR 1121-B-23 FOR REPAIRS/3 CUST/VEM/OPENED XFMR AT 1705/REPAIRS MADE AND ALL CUST RESTORED 1753/PLEASE CLOSE TICKET/THANKS/VEM/ DID NOTIFY CUSTOMERS THEY WERE GOING TO BE OUT BEFORE OPENING SO WE SCHEDULED IT./ ISO 39831121B00023/ COD 4/ VER/BOW
17703 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-06-18 21:24 | 2010-06-18 23:00 | 2 | 96 | 51154-1 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 KVA 19.9 120/208 Y XFMR IS BAD CUSTOMER SAID OK TO CHANGE IN THE MORNING// WILL WORK THIS OFF WR# 35639525 PLEASE CLOSE TICKET VER/KEP L3/KEP
17704 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-01-19 04:33 | 2012-01-19 07:45 | 1 | 192 | 4274461 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE ROTTED OUT LAYING ON PRIMARY LEAD WILL NEED TO REPLACE ANCHOR AND GUY TRUCK ACCESSIBLE VER/KEP IDC XXXX
17705 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-02-17 14:00 | 2009-02-17 14:48 | 4 | 48 | 63289-1 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE PULL OUT OF SLEEVE OPEN TRANS, 1400 BACK ON 1448 VER/KEP L3/KEP
17706 | Hazard | 3303902 | LESLIE | WOOTON | 2019-05-21 16:50 | 2019-05-21 17:38 | 4 | 48 | 4311521 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Released by crew 077S01bad insulator on pole 37830365C00008 replaced 2 cutouts and cut loop out to isoulate bad insulator power restored at 17 :38//off @ 1650 on @ 1738//NO OUTAGE TILL 1650
17707 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-09-01 07:08 | 2008-09-01 10:20 | 1 | 192 | 58196-1 | 192 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3401101 //...GOING TO TOP OF HILL...CUST. TAKING ME IN RHINO.....BAD CUTOUT...CHG CUTOUT...BB//VER/CRB IDC XXXX
17708 | South Williamson | 3411401 | DEWEY | INEZ | 2008-06-01 21:24 | 2008-06-01 23:00 | 2 | 96 | 54195-1 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT BAD ON POLE 648-B-59//VER/CRB IDC XXXX
17709 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-11-02 15:42 | 2019-11-02 18:54 | 1 | 192 | 4285111 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced 2/3 service
17710 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2022-10-31 07:48 | 2022-10-31 11:00 | 1 | 192 | 4080041 | 192 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Customer has been doing alot of digging in back yard to relocate UG for pool, One leg 50v in meter base. Crew required with power temp. Released by crew 078S02/ Power temp installed/ MLH
17711 | Hazard | 3303902 | LESLIE | WOOTON | 2018-01-28 13:27 | 2018-01-28 14:30 | 4 | 63 | 4779171 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | meter no. 533772128//MD filed//cod 1//opened line fuse 37830365D00249 to make repairs// open at 13:47 on at 14:30///cod + 3//
17712 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-01-18 10:57 | 2018-01-18 14:09 | 1 | 192 | 4755001 | 192 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | cutout is broke, T Smith coming to help. opened xfmrs at 01:15, put back on at 01:45. cust trouble with bad disc//PARTIAL POWER TILL OTHER TRANSFORMERS OPENED
17713 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-12-29 21:33 | 2013-12-30 00:45 | 1 | 192 | 4211221 | 192 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP HAS A SHORT IN IT SOMEWHERE. I WILL NEED HELP TO CHANGE DROP. IT COMES OFF SIDE OF HILL. I AM CALLING FOR HELP. //E.MCKINNEY TO ASSIST // //VER/GAH
17714 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-05-27 08:24 | 2015-05-27 10:00 | 2 | 96 | 4470721 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED BROKEN FUSE LINK VER/CRB
17715 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-05-19 18:46 | 2012-05-19 19:50 | 3 | 64 | 4809941 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7200. TRUCK OK. BRING XMF BAG OIL LEAKING FROM SEC BUSHINGS BUT NOT BAD. LINECREW REQUIRED. RELEASED BY CREW 078S11 INITIAL CALL 4809751 VER/KEP IDC XXXX
17716 | Hazard | 3303902 | LESLIE | WOOTON | 2012-08-09 12:36 | 2012-08-09 13:40 | 3 | 64 | 4915741 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED APART. VER/KEP IDC XXXX
17717 | Hazard | 3303902 | LESLIE | WOOTON | 2019-08-16 18:32 | 2019-08-16 20:08 | 2 | 96 | 4898301 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Woo reports transformer fuse broke and he had it restored at 2008
17718 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-06-13 13:15 | 2011-06-13 14:51 | 2 | 96 | H4310131 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BAD XARM ON POLE 358-89, TRUCKS TO POLE OK. C PHASE LINE FUSE IS OPENED ON POLE 358-42, NEED TO OPEN A (3 CUST) . NEED LONE CREW, AND 8 FOOT X ARM AND BRACES. OPENED B & C (2 CUST)@ 1315 DUP FROM 4310131 VER/HFP L3/HFP IDC XXXX
17719 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-08-22 17:34 | 2021-08-22 19:10 | 2 | 96 | 4136171 | 192 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | secondary connection was failing. repairs made 1910
17720 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2016-01-18 11:58 | 2016-01-18 12:30 | 6 | 32 | H4628041 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ****SEE 4628041*** PRIMARY HAS PULLED OUT OF A SLEEVE AT POLE 38820987A00045.(1 CUST)/ ALSO PRIMARY IS HOT UP TO THIS POLE AND WILL NEED TO OPEN FUSE AT POLE 38820987A00033 (6 CUST) TO MAKE REPAIRS. LINE CREW IS EN-ROUTE./ OPENED LINE FUSE 38820987A00033 @ 1158 TO 1230/ ISO 38820987A00033/ COD7/// DUPLICATE IN HOIS/ VER/BOW
17721 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-10-17 19:47 | 2015-10-17 20:35 | 4 | 48 | 4357611 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR RUSE OUT WILL REFUSE.FUSE LINK BROKE. VER/CRB
17722 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-07-18 12:04 | 2021-07-18 13:40 | 2 | 96 | 4930691 | 192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pulled into
17723 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2014-04-06 15:49 | 2014-04-06 19:00 | 1 | 191 | 4579791 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ 37830048A30550// WILL REPLACE// POWER IS RESTORED 19:00//4-6//COD 1// VER/DBM
17724 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-05-22 10:05 | 2010-05-22 13:16 | 1 | 191 | 66277-1 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35235790 // CUTOUT HAS BROKEN. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. COD-1 VER/HFP L3/HFP IDC XXXX
17725 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-11-27 10:34 | 2015-11-27 13:45 | 1 | 191 | 4487831 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND NEED PWR TEMP AND EXTRA LONG GROUND CONCRETE AROUND MTR BASE. ISOLATED BAD LEG. DR PINGSTONS HOUSE RELEASED BY CREW 078H06.. CREW ON SITE TO INSTALL POWER TEMP.. ETR 14:30.. POWER TEMP INSTALLED AND CUSTOMER RESTORED.. CUST SAID WIRE WAS IN CONDUIT ALL THE WAY.. NEED NEW SERVICE INSTALLED TICKET COMPLETE VER/CRB
17726 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-03-07 08:21 | 2016-03-07 11:32 | 1 | 191 | 4822661 | 191 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SECONDARY CONNECTION ON ONE LEG AT POLE 37820033C09002. POWER RESTORED AT 11:32. . VER/HFP L3/HFP
17727 | South Williamson | 3411401 | DEWEY | INEZ | 2012-12-10 08:19 | 2012-12-10 11:30 | 1 | 191 | 4455841 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ONE PRIMARY RISER FUSE BLOWN DUE TO ARRESTOR FAILURE// GOING TO CLEAR UP ARRESTOR AND REFUSE//RESTORED AT 1130//COMPLETE//EM //VER/GAH
17728 | Hazard | 3311401 | REEDY STATION | DEANE | 2020-03-21 01:44 | 2020-03-21 04:55 | 1 | 191 | 4498371 | 191 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | DOL 1002603 // suspect station outage at Reedy // Beaver Cr - Fleming 69kV line operated @ 0144 and started receiving outage calls at reedy // Distribution servicer and Station servicer enroute// found Blown arrestor on 34kv bus regulator ph 3//cod 400
17729 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2008-05-23 11:19 | 2008-05-23 14:30 | 1 | 191 | 50734-1 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000302//RESEND ORDER RELEASED BY CREW 078S073000302//RESEND ORDER /BROKEN FUSE LINK-HAD TO TRIM TREE AN REPLACE CUTOUT DOOR// COD 1 // VER/TOM IDC XXXX
17730 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-02-22 07:19 | 2022-02-22 10:30 | 1 | 191 | 4526581 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Fuse open on 37830459B00086. Broken cut-out on 37830459B00262Replaced broken cut-out. Power restored @ 10:30
17731 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-07-06 16:29 | 2022-07-06 19:40 | 1 | 191 | 4402091 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CURRENT LIMITING FUSE WAS BAD IN XFMR RISER. HAD TO CLIMB POLE AND REPLACE//POWER RESTORED @19:40
17732 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-09-18 11:13 | 2020-09-18 14:24 | 1 | 191 | 4475651 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replacd fuse
17733 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-06-21 07:29 | 2013-06-21 10:40 | 1 | 191 | 4379971 | 191 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PRI. LEAD ON RECLOSER HAS BURNED OFF MAIN LINE. CREW IS ON THE WAY TO REPLACE WITH LARGER WIRE. COD 1 ISO REC 238-182PRI. LEAD ON RECLOSER HAS BURNED OFF MAIN LINE. CREW IS ON THE WAY TO REPLACE WITH LARGER WIRE WE CHANGED LEADS AND RESTORED POWER AT 10:40. COD- 1 ISO PO @ 37830238000182 VER/HFP L3/HFP
17734 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-11-26 06:49 | 2008-11-26 10:00 | 1 | 191 | 52384-1 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | VER/HFP STS WR# 27450532 // STS BAD CONNECTION ON TRANSFORMER UP ON SIDE OF HILL IDC XXXX
17735 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-03-08 22:49 | 2009-03-09 02:00 | 1 | 191 | 56382-1 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 28836857 //CUTOUT BAD. NEED BIG BUCKETCUTOUT BAD. NEED BIG BUCKET RELEASED BY CREW 079S01.WAITING FOR BUCKET VER/JHM IDC XXXX
17736 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-12-01 16:14 | 2021-12-01 19:25 | 1 | 191 | 4139221 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfrm lid blew off on pole 375A-7. Need a 19.9 25KVA transformer. Bucket access. Need to bring transformer bag just incase you cant get lid back on. Tim Smiths crew is in enroute. Power restored at 19:25.
17737 | Pikeville | 3421001 | BREAKS | CITY | 2022-05-29 14:49 | 2022-05-29 18:00 | 1 | 191 | 4979911 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans fuse open on Bank of Trans,Will be trying to get it back in.Trans fuse open on Bank of Trans,Have a Bad Trans on pole 234-D-240 120-208 Bank,Spoke with Paul Layne and he is on the way to Help make repairs.Trans fuse open on Bank of Trans,Have a Bad Trans on pole 234-D-240 Bank,Spoke with Paul Layne and he is on the way to Help make repairs.Restored at 18:00.
17738 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2016-05-13 18:49 | 2016-05-13 22:00 | 1 | 191 | 4214891 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER. BAD 25KVA VER/AWD
17739 | Hazard | 3303902 | LESLIE | WOOTON | 2021-12-11 17:54 | 2021-12-11 21:05 | 1 | 191 | 4183361 | 191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken transformer cutout, will replace. p.hicks. all power restored @ 21:05 hrs p.hicks
17740 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-01-05 06:26 | 2011-01-05 09:37 | 1 | 191 | 58780-1 | 191 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38322405 // BAD SPLICE IN MID SPAN 1/0 SERVICE VER/HFP L3/HFP IDC XXXX
17741 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2022-05-16 15:12 | 2022-05-16 15:50 | 5 | 38 | 4898901 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew rquired 6t
17742 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-06-30 16:55 | 2021-06-30 18:30 | 2 | 95 | 4829641 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cut-out. Power resoted @ 18:30
17743 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2008-11-19 10:20 | 2008-11-19 11:55 | 2 | 95 | 66599-1 | 190 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309102// SECONDARY LEAD BURNED OFF AT TRANSFORMER SECONDARY RISER VER/KEP IDC XXXX
17744 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-11-11 08:25 | 2018-11-11 10:00 | 2 | 95 | 4388851 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout L3/HFP
17745 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2018-03-27 14:50 | 2018-03-27 15:00 | 19 | 10 | 4130321 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Load Side Connection on the cutout is almost burnt in half/ Have to open line fuse 38830044C45521 to make repairs/ ISO 38830044C45521/ COD 19/ 1450-1500
17746 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2020-12-15 17:43 | 2020-12-15 18:02 | 10 | 19 | 4772361 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replacing bad c/o///open@17:43 Closed@18:02///complete BR
17747 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-03-25 17:25 | 2009-03-25 17:44 | 10 | 19 | 61483-1 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NO OUTAGE AT THIS TIME, PULLING LINE OFF AT POLE#941-B-171 TO STABILIZE POLE//3417602NO OUTAGE AT THIS TIME, PULLING LINE OFF AT POLE#941-B-171 TO STABILIZE POLE, OFF AT 1725, BACK ON AT 1744//VER/CRB IDC XXXX
17748 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2017-12-29 15:06 | 2017-12-29 16:41 | 2 | 95 | 4687851 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o failed-replaced-ds122917
17749 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-09-29 11:10 | 2020-09-29 13:46 | 2 | 156 | 4508071 | 190 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | tree has grown around service drop & corrosion has caused wire to come into.pulled xfmr. off @ 13:12 on @ 13:46
17750 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-11-22 14:52 | 2011-11-22 15:30 | 5 | 38 | 4101441 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 118-4033 15T TRANS. FUSE BROKE//COD 5// VER/DBM IDC XXXX
17751 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-06-15 10:15 | 2017-06-15 11:50 | 2 | 95 | 4972261 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 140-2016 2T 19,9 TRANS. FUSE OUT INSTALLED CL FUSE NONE ON TRANS./ ISO 38830140B02016/ COD 2/ VER/BOW
17752 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2022-02-03 08:08 | 2022-02-03 09:43 | 2 | 95 | 4426701 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40t lf open @ 1072-5637. bad 12 kv co @ 1072-5736. crew reqd. big bucket ok Released by crew 078S0740t lf open @ 1072-5637. bad 12 kv co @ 1072-5736///Complete BR
17753 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2014-06-13 08:52 | 2014-06-13 09:30 | 5 | 38 | 4084151 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 46-179 BAD CUTOUT AND LA REPLACED VER/HFP L3/HFP
17754 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-10-18 19:10 | 2016-10-18 20:45 | 2 | 95 | 4026721 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | L/F OUT IN BAD LOC, UP HILLSIDE, BUT I HAVE IT BACK IN AND POWER IS RESTORED AT THIS LOC AT 2045 BY AMG, VER/CRB L3/HFP XXXHFP
17755 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2015-03-20 12:08 | 2015-03-20 15:18 | 1 | 190 | 4213301 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE#38831027D00587 LINE FUSE OUT ON POLE#38831027D00586. WILL REPLACE CUTOUT ALSO.NETURAL LUG IN XFMR IS BURNED INTO.T HALL IS TO BRING A REPLACEMENT. COD-1 ISO LF 38831027D00586 VER/HFP L3/HFP
17756 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-02-10 10:53 | 2010-02-10 14:03 | 1 | 190 | 55071-1 | 190 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION//VER/CRB IDC XXXX
17757 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-07-28 10:25 | 2008-07-28 12:00 | 2 | 95 | 61033-1 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3202202// CONN BURNED INTO ON TRANSF POLE IDC XXXX
17758 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-08-14 14:02 | 2009-08-14 17:12 | 1 | 190 | 58205-1 | 190 | PARTIAL POWER | EQUIPMENT FAILURE | PEDESTAL | VER/HFP CORRSION ON NEUTRAL BAR L3/HFP IDC XXXX
17759 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2022-01-19 18:50 | 2022-01-19 20:25 | 2 | 95 | 4387151 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connections burnt into @ xfm//Opened xfm @ 18:50 made repairs and restored @ 20:25
17760 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-02-20 11:20 | 2013-02-20 12:55 | 2 | 95 | 4834211 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN TRANSFORMER FUSE ON POLE 38830279000101, REPLACED FUSE, ALL POWER RESTORED COD-2 ISO TF 38830279000101 VER/HFP L3/HFP IDC XXXX
17761 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-01-07 20:25 | 2012-01-07 22:00 | 2 | 95 | 4240371 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR OPEN. HAD THIS XFMR OPEN ON 12-24-11 WITH NO CAUSE FOUND. 10 KVA XFMR IS GOING BAD. WILL HAVE CREW CHANGE MONDAY, 1-9-12. CLOSED IT BACK IN AT 22:00 AND ADVISED CUSTOMER TO CALL US IF IT GOES BACK OUT THIS WEEKEND AND WE WILL GO AHEAD AND CHANGE IT. SH VER/PDP IDC XXXX
17762 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2015-03-06 16:55 | 2015-03-06 20:05 | 1 | 190 | 4150011 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-6117 CUTOUT DOOR BURNT UP REPLACED DOOR AND 10T FUSE L3/DKGXXXX
17763 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-12-23 11:15 | 2016-12-23 14:25 | 1 | 190 | 4230421 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, HELP ON THE WAY TO CHANGE IT OUT/ ISO 37830450C00185/ COD 1/ VER/BOW
17764 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2021-11-30 11:55 | 2021-11-30 13:30 | 2 | 95 | 4134861 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | had arrestor go bad on pole 200-465 change arrestor // cod 2 // closed in @1330
17765 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2016-03-08 09:10 | 2016-03-08 10:45 | 2 | 95 | 4826161 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S03 COD-3 ISO LF 38830227000018 VER/HFP L3/HFP
17766 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-10-26 11:41 | 2019-10-26 14:51 | 1 | 190 | 4198501 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | lightning arrester bad, changed 2 cutouts & arrester. pls close. tre
17767 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-12-31 08:20 | 2012-12-31 11:30 | 1 | 190 | 4559131 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | INSULINK CONNECTION FROZE OUT IN SERVICE SPLICE. RE-WORKED CONNECTIONS. SH COD-1 VER/HFP L3/HFP
17768 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2009-09-28 13:53 | 2009-09-28 14:12 | 10 | 19 | 50373-1 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON SERVICE--OPENED TRANSFORMER AT 13:53 BACK IN AT 14:12-REPAIRED SERVICE//VER/CRB
17769 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-09-01 17:53 | 2018-09-01 21:03 | 1 | 190 | 4032041 | 190 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION@XFR&ALSO IN MTR BASE.REPLACED POLE CONNECTION&TIGHTENED MTR BASE CONNECTION.MTR BASE WILL PROBABLY GIVE PROBLEMS UNTIL IT IS REPLACED.CUST SAID HE WILL REPLACE BASE.WILL CALL BACK FOR DISC.IS OK FOR THE TIME BEING.
17770 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2010-07-06 11:12 | 2010-07-06 14:22 | 1 | 190 | 62570-1 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE NEUTRAL WAS BROKE AT POLE; REPAIRED WIRE; PWR RESTORED AT 1422 HRS; POSSIBLE DAMAGE CLAIM, CUSTOMERS WINDOW AIR CONDITIONER SMOKING; CLOSE TICKET// VER/DBM IDCC PN6034 XXXX
17771 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-03-20 11:54 | 2014-03-20 15:04 | 1 | 190 | 4512781 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | METER READER REPORTED POLE TOP BROKE OUT AND HELD BY CONDUCTOR//. BURNOFF POLE ACROSS RR TRACKS POSSIBLY CAN LOWER POLE RELEASED BY CREW 078H25///REMOVED RR CROSSING TO MAKE SAFE//TECH TO MAKE W.O. TO HAVE PRIMARY TAP REPLACED///TBL TKT COMPLETED//COD 1//ISO 38830190C00101// VER/DBM
17772 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2018-07-17 07:09 | 2018-07-17 10:19 | 1 | 190 | 4785631 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required ,,replace broke cutout ,,,with big bucket Released by crew 078S05 Repairs made closed xfmr at 10:19. Ticket complete L3/HFP
17773 | Hazard | 3303901 | LESLIE | HYDEN | 2013-05-01 19:50 | 2013-05-01 21:25 | 2 | 95 | 4063971 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT GATE COD-2 PO 37830290000034 VER/HFP L3/HFP IDC XXXX
17774 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-03-27 11:25 | 2017-03-27 13:00 | 2 | 95 | 4588061 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM. CUTOUT BROKE DOWN AND BURNT TOP OF POLE OFF AT CUTOUT.POLE 214-462.LIFTED HOT TAP ON POLE 214C-57.WILL INSTALL FIBERGLASS PIN TOP EXTENSION AND MAKE REPAIRS.LIFTED HOT TAP @ 11:25 AND CLOSED BACK IN @ 13:00...//NO OUTAGE TILL HT LIFTED VER/CRB
17775 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-05-29 15:46 | 2011-05-29 17:21 | 2 | 95 | 4206881 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BROKE 19.9 CUTOUT ALL POWER RESTORED AT 1721 CLOSE TICKET COD-2 ISO TF 38830454B22504 VER/HFP L3/HFP IDC XXXX
17776 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-12-31 10:05 | 2008-12-31 13:15 | 1 | 190 | 66075-1 | 190 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3007904//SD OPEN ON 1 LEG//VER/CRB L3/KEP IDC XXXX
17777 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-04-14 18:50 | 2014-04-14 22:00 | 1 | 190 | 4604321 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA XFMR , NEED SOMEONE TO BRING A 25KVA XFMR 7200 POWER BACK ON @ 22:00//COD 1// VER/DBM
17778 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-03-21 14:12 | 2010-03-21 14:50 | 5 | 38 | 52208-1 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ,,,FOUND BAD CUTOUT ON POLE 621-226 I REPLACED CUTOUT,,,,,,,POWER RESTORED//COD 5//ISO 38830621C40226 // VER/DBM IDC XXXX
17779 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-11-07 22:30 | 2021-11-08 00:05 | 2 | 95 | 4065391 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. cutout busted @72-A-77, will be changing.Got cutout replaced and power restored @0005.
17780 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-04-17 19:30 | 2014-04-17 22:40 | 1 | 190 | 4615851 | 190 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND SECONDARY BAD NEED LINE CREW TO REPLACE RELEASED BY CREW 074H17/// REPLACED BAD U.G. CABLE AND RESTORED POWER AT 22:40 TIM MCCOY RELEASED BY CREW 074H10//COD 1// VER/DBM
17781 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2010-10-20 15:27 | 2010-10-20 16:05 | 5 | 38 | 61383-1 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BLOWN XFMR FUSE, FUSE LOOKED TO BE BROKE, NOT 100% SURE. NO OTHER VISIBLE CAUSES //VER/CRB IDC XXXX
17782 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-05-04 16:53 | 2022-05-04 18:28 | 2 | 95 | 4837841 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fuse to Blow at pole 336-41..EQUIPMENT FAILURE CUTOUT RESTORED @1828
17783 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-03-26 11:45 | 2021-03-26 13:20 | 2 | 95 | 4380171 | 190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT.chgd cutout
17784 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2016-07-29 09:16 | 2016-07-29 12:25 | 1 | 189 | 4707141 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL WAS BROKEN IN 4/3 DROP RUNING THROUGH SOME TREES IT WAS BROKEN AT THE END OF A TENSION SLEVE REPAIRED CONDUCTOR EVERYTHING OK CUST SAID IT HAD DAMAGED TWO TVS. SND COPY TO PEGGY IN DAMAGE CLAIM CUST COULD POSSIBLE CALL IN NOT SURE WHAT CAUSED CONDUCTOR TO BREAK MAY HAVE BEEN DAMAGED AT SOMETIME THROUGH A STORM/ VER/BOW
17785 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2016-10-19 14:57 | 2016-10-19 16:00 | 3 | 63 | 4028491 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 140-542 6T TRANS FUSE BROKE VER/AWD L3/HFP HFPC CCU FEC57 FP
17786 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-03-04 10:45 | 2016-03-04 11:48 | 3 | 63 | 4814651 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BREAKING DOWN ON POLE 237C-189.WILL HAVE TO OPEN FUSES ON POLE 237C-15 TO MAKE REPAIRS...REPLACED TWO CUTOUTS AND TWO HOT TAP LEADS ON POLE 237C-189.OPENED LINE FUSES ON POLE 237C-15 @ 10:45 CLOSED AND RESTORED @ 11:48../ ISO 37830237C00015/ COD 3/ VER/BOW
17787 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-01-23 10:09 | 2017-01-23 10:30 | 9 | 21 | 4321211 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREWS OPENING FUSE ON 38831056A00047 TO SAFELY REPLACE CUTOUT ON POLE 38831055000015OPENED STEPDOWN 1056-47 AT 10:09 TO REPLACE CUTOUT ON 1055-15,REPLACED CUTOUT,RESTORED AT 10:30 VER/AWD L3/HFP HFPC TOF1003
17788 | South Williamson | 3411401 | DEWEY | INEZ | 2010-09-11 22:22 | 2010-09-11 23:25 | 3 | 63 | 65676-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFORMER CUTOUT BROKE ON POLE 720-26 BLOWING FUSE ON SIDE TAP. XFORMER DOESNOT FEED ANYTHING GOING TO CLEAR UP AND REFUSE TAP// CLEARED XFORMER CUTOUT, CLOSED TAP CUSTOMERS RESTORED AT 23:25 1 OUTAGE HOIS ADJ. IDCC CNT4 , TON234 XXXX
17789 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-10-10 07:56 | 2020-10-10 11:05 | 1 | 189 | 4541271 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A Broke cutout on crossarm on pole 1148-31,Will need help to change,,Paul brought me a stand off bracket,Going to move cutout down the pole(Making repairs).Restored at 11:05...
17790 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2008-02-25 08:23 | 2008-02-25 11:32 | 1 | 189 | 50097-1 | 189 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3001204//BAD UG SERVICE. HAVE ISOLATED BAD LEG ON POLE. RE-ENERGIZED TRANSFORMER. LEFT LEG IN METERBASE IS HOT......CAUSTION!!!!!! RELEASED BY CREW 078S04.// VER/TOM IDC XXXX
17791 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-01-11 08:21 | 2010-01-11 11:30 | 1 | 189 | 52306-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308503// RELEASED BY CREW 077S03//10 KVA 19.9 BAD AT POLE 37830247A00454 CALLING FOR A CREW AND A 25 KVA RELEASED BY CREW 077S04 INSTALL NEW XFMR RESTORED POWER AT 1135 CREW 077H01 VER/HFP L3/HFP IDCC PN202 XXXX
17792 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-08-11 22:53 | 2009-08-11 23:14 | 9 | 21 | 59122-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NEUTRAL BROKE OPENED TRANS TO REPAIR VER/KEP L3/KEP IDC XXXX
17793 | South Williamson | 3200301 | BELFRY | BELFRY | 2010-01-09 21:16 | 2010-01-10 00:25 | 1 | 189 | 51564-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 0N SITE, CHECKING TROUBLE, BAD CONNECTION AT WEATHERHEAD //VER/GAH IDCC CNT4 XXXX
17794 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-10-05 15:32 | 2015-10-05 16:35 | 3 | 63 | 4319321 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMER CUTOUT FUSE BROKE ON POLE 785-561///REFUSED AT 16:35///COMPLETE BR VER/CRB L3/HFP XXXHFP
17795 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2019-11-18 09:41 | 2019-11-18 12:50 | 1 | 189 | 4043571 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout changed, power restored at 12:50
17796 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-10-15 15:12 | 2018-10-15 16:15 | 3 | 63 | 4255701 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse out,broke fuse L3/HFP
17797 | Pikeville | 3408103 | SALISBURY | MARTIN | 2017-04-04 17:21 | 2017-04-04 20:30 | 1 | 189 | 4613791 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED XFMR CUTOUT AND ARRESTER / ALL WRK COMPLETE / GXJ VER/CRB L3/HFP XXXHFP
17798 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-09-23 18:21 | 2009-09-23 19:24 | 3 | 63 | 60703-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WR # 31867529 // NO CREW REQUIRED BROKEN FUSE LINK 10T IDC XXXX
17799 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2022-12-29 09:51 | 2022-12-29 13:00 | 1 | 189 | 4374131 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, bad location, waiting for flaggers
17800 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-04-17 12:21 | 2014-04-17 15:30 | 1 | 189 | 4614761 | 189 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION VER/HFP L3/HFP
17801 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-04-16 16:24 | 2008-04-16 19:33 | 1 | 189 | 51651-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3314402//TRANSFORMER IS BAD WILL NEED ONE MAN AND TRANSFORMER REPLACED BAD TEANSFORMER// VER/TOM IDC XXXX
17802 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-01-04 23:36 | 2016-01-05 02:45 | 1 | 189 | 4585481 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR. REPLACED XFMR AND CLOSED @ 2:45. SH VER/KEP
17803 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2019-10-23 08:26 | 2019-10-23 11:35 | 1 | 189 | 4186671 | 189 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Hot leg burndt into on a 4/0 URD service off pole 24-B2-655, Paul Reed getting lined up to help with repairs. Only 1 customer affected. Installed Add-A-Phase until crew can get out and find bad spot in the URD service, restored @1135.
17804 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-07-07 13:00 | 2019-07-07 16:09 | 1 | 189 | 4673331 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | J CAUDILL/// bad xfmr , we need two men and a material handler 25 kva 7200bad xfmr , we need two men and a material handler 25 kva 7200. we changed out the xfmr
17805 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2018-10-23 16:51 | 2018-10-23 20:00 | 1 | 189 | 4316271 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer/ ISO 39831148B10225/ COD 1replaced a bad 25 kva transformer
17806 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-05-11 15:49 | 2016-05-11 18:58 | 1 | 189 | 4201411 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4202871***/ BAD TRANSFORMER CUTOUT ON POLE 37820151000075/ ISO 37820151000075/ COD 1REPLACED FAILED CUTOUT ON POLE 151-75// VER/ ADH
17807 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-01-21 17:41 | 2017-01-21 20:50 | 1 | 189 | 4317721 | 189 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON OVERHEAD SECONDARY 117-384, ARCOS 2 MEN TO HELP. RELEASED BY CREW 078S07. REPAIRED BAD SECONDARY CONNECTION. COD-1 VER/KEP L3/HFP XXXHFP
17808 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-12-26 01:24 | 2017-12-26 02:27 | 3 | 63 | 4678401 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse melted out @1053-A-145, refused @0227.
17809 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-04-15 07:30 | 2009-04-15 10:39 | 1 | 189 | 53600-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING CUT OUT........NOT ACCESABLE BY TRUCK..... BLR COD-1 VER/KEP L3/KEP IDC XXXX
17810 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2017-12-07 10:46 | 2017-12-07 13:55 | 1 | 189 | 4628271 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTS//--7200 c/o broken--fuse blown/broke--tree crew req (head high brush around pole)--crew req-ds12071.note pickup over bridge (no where to turn around) Released by crew 078S01,replaced cutout all cust restored @ 1355 please close ticket thanks.bt
17811 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-09-13 12:10 | 2017-09-13 13:13 | 3 | 63 | 4358281 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT ON POLE 1077-A-485 LIFTED HOTTAP ON POLE 1077-A-442 TO ISOLATE AND MAKE REPAIRS 1210 TO 1330BAD XFMR CUTOUT ON POLE 1077-A-485 LIFTED HOTTAP ON POLE 1077-A-442 TO ISOLATE AND MAKE REPAIRS..REPLACED CUTOUT..LIFTED HOT TAP @ 12:10 & RESTORED POWER @ 13:13 SEND COPY OF THIS TO CLIFF FREEMAN TO HAVE POLE REPLACED COD-3 ISO PO @ 38831077A00442 VER/HFP L3/HFP
17812 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-09-23 17:13 | 2010-09-23 20:22 | 1 | 189 | 52908-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER PHIL HICKS, THIS TRANSFORMER APPEARS TO BE BAD//HE`S CHECKED OTHER TRANSFORMER ON THIS LINE AND ITS READINGS ARE GOOD//THIS ONE IS PUTTING OUT 134/268 // CUSTOMER HAS ALREADY OPENED DISCONNECTS AND IS RUNNING OFF OF GENERATOR//CUST DID NOT EXPECT US TO FIX UNTIL TOMORROW // PER SHEENA HENSLEY, WE WILL GET A CREW ON THIS TOMORROW// ELECTRONIC GATE WILL BE OPEN PER PROPERTY OWNER // ISO 37830223A21195 // COD 1//OPS ORDER CREATED TO GO OUT //OPS # 035745774 //CLOSING TRBL ORDER// VER/DBM IDC XXXX
17813 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-07-16 08:51 | 2009-07-16 12:00 | 1 | 189 | 64588-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT IDC XXXX
17814 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-08-02 09:22 | 2012-08-02 10:25 | 3 | 63 | 4883431 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKED XFMR AND REFUSED CUTOUT BROKEN FUSE VER/KEP IDC XXXX
17815 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-06-04 00:01 | 2008-06-04 03:10 | 1 | 189 | 55628-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT AT 229-13 RELEASED BY CREW 077H03 ***VER/PDP
17816 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2020-03-30 11:02 | 2020-03-30 14:11 | 1 | 189 | 4543141 | 189 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad insulink. replaced connection, all good pls close. tre
17817 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-11-24 17:16 | 2013-11-24 20:25 | 1 | 189 | 4070991 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 75 KVA 19.9 TRANSF === NEED TRANSF LINE TRUCK AND BIG BUCKET AND 3 MEN ==== CHANGED TRANSF POWER OK VER/CRB
17818 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-11-19 23:42 | 2011-11-20 00:45 | 3 | 63 | 4093921 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE CURRENT LIMITING FUSE HAS FAILED. VER/ARN IDC XXXX
17819 | Pikeville | 3451201 | BEEFHIDE | BEEFHIDE | 2021-06-07 01:11 | 2021-06-07 04:20 | 1 | 189 | 4677461 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 138/34kV TR 1 tripped from service affecting 205 CC, Station & Line Enroute no cause at this time /// Crews found failed L/A on 34kV Bus FETR 0430161/34kV TR 1 tripped from service affecting 205 CC, Station & Line Enroute no cause at this time Released by crew 074S01
17820 | Pikeville | 3407103 | TOPMOST | KITE | 2010-04-21 16:09 | 2010-04-21 17:12 | 3 | 63 | 66093-1 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE LOOKS TO BE BAD AT GROUND LINE AND PROBLEY HAD HELP FALLING OVER BY ROCK TRUCKS IN AREA. NEED 8 FOOT ARM 2 STEEL PINS 2 INSULATORS SET SMALL BRACES. 40-4 POLE. LINE TRUCK BUCKET TRUCK. SEND COPY TO JOE HUBBARD NEED TO CONTACT THACKER AND GRIGSBY PHONE COMP. NEED TO CONNECT CABLE TO NEW POLE. POLE NBR 258-35. CABLE LOW OVER ROAD.//VER/CRB IDC XXXX
17821 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-11-09 12:46 | 2021-11-09 15:55 | 1 | 189 | 4070431 | 189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required ,424-10,,xfr cutout broke on x arm ,, Released by crew 078S05,repairs made al cust rest @ 1555 please close ticket thanks.bt
17822 | South Williamson | 3411401 | DEWEY | INEZ | 2021-02-24 11:11 | 2021-02-24 12:45 | 2 | 94 | 4240291 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//repairs made//restored at 12:45//complete//em
17823 | South Williamson | 3411401 | DEWEY | INEZ | 2020-12-23 20:36 | 2020-12-23 22:10 | 2 | 94 | 4798381 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F cutout on 744-A4-107 has failed and broke causing outage. I can access with truck and will replace// Replaced cutout and restored at 22:10
17824 | Whitesburg | 3314401 | MAYKING | ERMINE | 2009-08-05 16:26 | 2009-08-05 18:00 | 2 | 94 | 64961-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY SPLICE BURNED INTO. MADE REPAIRS RESTORED POWER AT18:00 VER/KEP L3/KEP IDC XXXX
17825 | Pikeville | 3421001 | BREAKS | CITY | 2008-09-02 11:42 | 2008-09-02 14:50 | 1 | 188 | 58526-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400901// TRANSFORMER HAS FAILED. CREW IS ENROUTE FROM PIKEVILLE WITH A REPLACEMENT.//COD 1// VER/DBM IDC XXXX
17826 | Hazard | 3303901 | LESLIE | HYDEN | 2019-02-03 10:07 | 2019-02-03 13:15 | 1 | 188 | 4749931 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 cutout broke
17827 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-07-27 00:16 | 2008-07-27 01:50 | 2 | 94 | 60664-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401001 TRANSFORMER CUTOUT IS BURNED UP. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT.VER/JHM IDC XXXX
17828 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2012-07-31 14:32 | 2012-07-31 17:40 | 1 | 188 | 4871401 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMER FUSE OUT SERV TO TRY FUSE,BAD XFMER 277-480 50KVA CREW REQ //COD 1// CREW ON SITE@ 1640//COD 1// VER/DBM
17829 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-02-06 07:34 | 2008-02-06 09:08 | 2 | 94 | 50717-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38831121000331. WILL BE CHANGING OUT.// VER/TOM IDC XXXX
17830 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2016-01-19 21:34 | 2016-01-20 00:42 | 1 | 188 | 4634601 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFR HERE,LEAKING OIL,ALSO STEAMING HOT.NEED 25,1MAN,MATERIAL HANDLER,ALSO HAS LEAKED OIL ON ROAD UNDER XFR//////////REPLACED XFR AND RESTORED//COD 1// VER/DBM
17831 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2018-01-09 20:56 | 2018-01-09 21:43 | 4 | 47 | 4725501 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Crews opened transformer cutout on 37820049000077 to safely repair downed conductor. Order 4725061. 2056-2143
17832 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2022-02-16 14:16 | 2022-02-16 17:24 | 1 | 188 | 4487961 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap burnt into// power restored 17:24
17833 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-05-17 11:59 | 2009-05-17 13:33 | 2 | 94 | 60962-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREES HAVE GROWN UP CLOSE TO TRANS. LIMBS ARE BLOWING INTO TRANS. RISER, BLOWING TRANS. FUSE. I AM GOING TO REFUSE TRANS.TRANS. CUTOUT IS BROKEN ON POLE 214-360. I AM GOING TO CHANGE CUTOUT.TRANS. CUTOUT IS BROKEN ON POLE 214-360. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT AND REFUSED TRANS. AND IT STAYED IN..//VER/CRB IDC XXXX
17834 | Pikeville | 3421001 | BREAKS | CITY | 2011-01-05 13:49 | 2011-01-05 16:57 | 1 | 188 | 58982-1 | 188 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL INVESTIGATE COMPLAINT/////BAD CONS AT WEATHERHEAD,RE-WORKED THOSE,ALL OK AFTERWARDS.CUSTS EQUIPMENT IN VERY BAD SHAPE THOUGH,ALSO HAD TO CHANGE MTR,WILL CREATE ORDER FOR THAT VER/HFP L3/HFP IDC XXXX
17835 | Whitesburg | 3314401 | MAYKING | ERMINE | 2018-04-13 20:26 | 2018-04-13 22:00 | 2 | 94 | 4222821 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no reading on meter. cutout broke pole 450-91.. replaced cutout power restored @ 2200/ ISO 37830450B00091/ COD 2
17836 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-11-15 07:41 | 2008-11-15 09:15 | 2 | 94 | 65075-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | 3409303 PRIMARY CONDUCTOR CAME OFF PIN AND POSSIBLY SLAPPED SERVICE WIRE OPENING CSP XFMR. DIFFICULT LOCATION - CREW ENROUTE. RESET XFMR BREAKER. SH VER/KEP IDC XXXX
17837 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-12-02 13:01 | 2019-12-02 14:35 | 2 | 94 | 4116201 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse
17838 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2017-11-19 11:58 | 2017-11-19 15:06 | 1 | 188 | 4584061 | 188 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired service drop connection complete
17839 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2010-12-11 17:41 | 2010-12-11 19:15 | 2 | 94 | 65398-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE HAD BROLKEN, I REPLACED FUSE AND POWER IS RESTORED AT THIS LOC VER/TOM IDC XXXX
17840 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-02-04 05:56 | 2011-02-04 07:30 | 2 | 94 | 53941-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BAD//COD 2//ISO// VER/DBM IDC XXXX
17841 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2016-12-15 12:02 | 2016-12-15 15:10 | 1 | 188 | 4196581 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED ON 762-23. DIFFICULT LOCATION AND OLD POLE TO CLIMB. RDM IS ENROUTE TO ASSIST. REPLACED CUTOUT AND RESTORED @ 15:10. SH VER/CRB L3/HFP XXXHFP
17842 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-01-25 10:56 | 2018-01-25 12:30 | 2 | 94 | 4772651 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout ,,changing..
17843 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2017-02-07 13:11 | 2017-02-07 14:45 | 2 | 94 | 4365061 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-6089 BAD CUTOUT NO TRUCK BEHIND 1226 CRESTVIEW POLE 1123-6032 0N 14:45 RELEASED BY CREW 078S08--CREW ON SITE TO CHANGE BAD CUTOUT--OPEN ON 1123D1-6032 TO SAFELY CHANGE GND/TAG TO CREW-- OUTAGE APPX 30MIN--OPENED AT 16:51--1123-6032 IN AT 17:21--TBL TKT COMP OPENED FUSE ON 4367901. COD 2 VER/AWD L3/HFP XXXHFP
17844 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-12-01 07:15 | 2021-12-01 08:49 | 2 | 94 | 4136441 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired connections on 184-292
17845 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-04-01 11:32 | 2014-04-01 14:40 | 1 | 188 | 4550781 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONE CUSTOMER AFFECTED BAD UG SERVICE. CREW ENROUTE TO LOCATE AND REPAIR FAULT. OPENED XFMR 809-796 @ 14:22, REPAIRED 4/0 UG SERVICE AND CLOSED XFMR @ 14:40. SH//COD 1 + 10 IDCC CNT11 XXXX
17846 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-06-03 09:34 | 2014-06-03 12:42 | 1 | 188 | 4964361 | 188 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE PULLED APART IN S/D// REPLACED S/D// VER/DBM AJB
17847 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2021-03-09 21:56 | 2021-03-09 23:30 | 2 | 94 | 4320961 | 188 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connections/ ISO 38830251000121/ COD 2
17848 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-06-03 09:02 | 2020-06-03 12:10 | 1 | 188 | 4947791 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 50kva on pole 375-2784. dropped leads and checked. crew required, big bucket Released by crew 077S11. all power restored @ 12:10 hrs p.hicks
17849 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2009-10-01 13:33 | 2009-10-01 14:20 | 4 | 47 | 62423-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-130 6T TRANS. FUSE BAD CUTOUT INSTALLED ANIMAL GUARD VER/KEP L3/KEP IDC XXXX
17850 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-04-05 13:22 | 2021-04-05 16:30 | 1 | 188 | 4420051 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7200// TRUCK OK,repairs made all cust restored@ 1630 please close ticket thanks.bt
17851 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2018-06-22 17:05 | 2018-06-22 18:39 | 2 | 94 | 4647231 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Released by crew 079H03, fuse broken, refused xfmr cutout, ALL WORK COMPLETE / GXJ
17852 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-12-15 15:02 | 2017-12-15 18:10 | 1 | 188 | 4651901 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout Released by crew 077H14/ ISO 37830157000009/ COID 1
17853 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-09-26 18:21 | 2009-09-26 19:55 | 2 | 94 | 64473-1 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN ON POLE 1104-99. I AM GOING TO CHANGE CUTOUT. I CLOSED TRANS. IN AT 19:55 VER/KEP L3/KEP IDC XXXX
17854 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-08-18 11:50 | 2015-08-18 13:24 | 2 | 94 | 4148181 | 188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT // POWER RESTORED @ 13:24// VER/ ADH
17855 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-02-25 05:44 | 2022-02-25 08:51 | 1 | 187 | 4543251 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required
17856 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-10-24 16:26 | 2016-10-24 19:33 | 1 | 187 | 4050071 | 187 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUSTOMER FOR MORE INFO/NO ANSWER. CONNECTOR BURNDT INTO AT TRANS. POLE, WILL BE MAKING REPAIRS. REPLACED SERVICE DROP, RESTORED @1933. VER/AWD L3/HFP XXXHFP
17857 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-12-27 12:08 | 2009-12-27 15:15 | 1 | 187 | 55421-1 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED TRANFORMER, KEPT BLOWING FUSE, POWER RESTORED AT 1515 122709 MWL
17858 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-03-10 05:13 | 2019-03-10 08:20 | 1 | 187 | 4966411 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines Broken xfmr cutout on pole 187-175. Repairs made, closed at 08:20 Ticket complete L3/HFP
17859 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-03-02 09:39 | 2018-03-02 12:46 | 1 | 187 | 4924841 | 187 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PER FRED MANNING CUSTOMER HAS PART POWER AND CAN'T FIND ANYTHINGPER FRED MANNING CUSTOMER HAS PART POWER AND CANT FIND ANYTHING-1 cust out, bad connector spliced ser. drop made repairs power
17860 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2009-05-30 20:23 | 2009-05-30 23:30 | 1 | 187 | 52011-1 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TREE FELL TAKING DOWN SERVICE DROP, NEEDS LINE CREW TO HELP PUT BACK UP. VER/PDP
17861 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-07-28 10:08 | 2017-07-28 13:15 | 1 | 187 | 4193441 | 187 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER//BAD 25 TRANS IN BANK// CHANGING TRANS. BACK TO NORMAL VER/CRB
17862 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2017-09-12 12:14 | 2017-09-12 15:21 | 1 | 187 | 4352341 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED CONNECTION 38830250000219 VER/AWD L3/HFP XXXHFP
17863 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2014-06-05 19:09 | 2014-06-05 19:20 | 17 | 11 | H4987791 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 600 AMP HOT TAP BURNT IN CLEAR B PH OPEN REC, TO CLEAR UP FAULT 1909 POWER RESTORED AT 1920 CHECK CUST WHO CALLED IN OUTAGE THIS ORDER IS FOR THE 3 PHASE CUST WHO HAD PART POWER. NEED TO DUP IN HOIS FOR 17 CUST OUT FROM 1909 - 1920 THAT WERE OUTAGED WHEN RECL OPENED //// ISO OCR 38830190000146 VER/HFP L3/HFP
17864 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-06-19 07:30 | 2014-06-19 10:37 | 1 | 187 | 4109661 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ POLE 112-4,REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT COD-1 ISO TF 38830112000004
17865 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2019-05-28 12:13 | 2019-05-28 15:20 | 1 | 187 | 4354111 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFm cutout broke will make repairs// Replaced cutout and restored service @ 15:20
17866 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-07-19 16:53 | 2012-07-19 20:00 | 1 | 187 | 4773611 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 354-111 WILL NEED ONE MAN AND BIG BUSKET TO REPLACE. BRING ONE 34KV CUTOUT, BRACKET,& ARRESTOR. RELEASED BY CREW 075H01CUTOUT BROKE ON POLE 354-111 WILL NEED ONE MAN AND BIG BUSKET TO REPLACE. BRING ONE 34KV CUTOUT, BRACKET,& ARRESTOR. POWER RESTORED AT 2000 VER/ARN
17867 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-04-18 20:33 | 2019-04-18 23:40 | 1 | 187 | 4131601 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 trans on 96-C-172.trk app need 1 man and mat handler replaced trans restored power at 23;40
17868 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2014-06-25 11:38 | 2014-06-25 14:45 | 1 | 187 | 4154391 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CLEAN VINES OFF POLE & REFUSE.WILL NEED 15 KVA 120/240-7200. IS TRUCK ACCESSABLE. RELEASED BY CREW 074S04// CREW ON SITE TCM// VER/CRB
17869 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-07-10 09:35 | 2014-07-10 12:42 | 1 | 187 | 4224831 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE XFMR LEAKING CT METERING BURNT UP CHANGING ALL SD RAY COMPLETE TICKET COD1// VER/ADH
17870 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-06-11 10:38 | 2011-06-11 13:45 | 1 | 187 | 4292461 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP ON POLE 1011-518 CENTER PHASE,,,,, REPLACED DOOR POWER BACK ON//ISO//COD 1// VER/DBM IDC XXXX
17871 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-10-22 14:05 | 2009-10-22 17:12 | 1 | 187 | 64945-1 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD. R. MARCUM TO CHANGE CUTOUT RELEASED BY CREW 079S01. REPLACED CUTOUT AND CURRENT LIMITING FUSE.//COD 1// VER/DBM IDC XXXX
17872 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-03-10 19:16 | 2015-03-10 22:23 | 1 | 187 | 4180181 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND LINE FUSE OPEN ON POLE 39831072C45688, ON POLE TAP, TO POLE 39831072D37058 WHICH HAS BAD CUTOUT, NEED CRERW NO TRUCKS HAVE LINE GROUNDED AND TAGGED TO DDC ON POLE 1072-5688 RELEASED BY CREW 078S06//MADE MDC VER/CRB
17873 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-12-13 13:24 | 2018-12-13 16:31 | 1 | 187 | 4562161 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER//,,COD 1 L3/HFP
17874 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2011-11-15 11:03 | 2011-11-15 14:10 | 1 | 187 | 4078201 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 236-94. I CALLED TIM HALL HE IS SENDING CREWW THIS WAY RELEASED BY CREW 074S11 ///VER/CRB IDC XXXX
17875 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-04-03 17:13 | 2008-04-03 17:30 | 11 | 17 | 63544-1 | 187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402802// HAD TO OPEN LINE FUSE ON POLE 738-27 TO SAFELY REPLACE BROKEN CUTOUT ON POLE 738-348// + 1 CUSTOMER THAT WAS MISMAPPED// VER/TOM IDC XXXX
17876 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2019-08-16 18:59 | 2019-08-16 22:06 | 1 | 187 | 4898361 | 187 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | called customer-no answer///,,,repaired secondary connections complete
17877 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-01-13 13:57 | 2020-01-13 15:30 | 2 | 93 | 4298511 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRF IS OUT,WILL RE-FUSE////////XFR CUTOUT WAS BROKEN,REPLACED IT&RESTORED POWER
17878 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-11-28 23:31 | 2009-11-29 01:04 | 2 | 93 | 50520-1 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008702// BAD C/O DOOR, REPLACE DOOR M.P. RELEASED BY CREW 078H12 IDCC CDC83 XXXX
17879 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2013-04-07 12:09 | 2013-04-07 15:15 | 1 | 186 | 4985151 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HAS BEEN HEATING UP ON SERVICE POLE. RE-WORKED CONNECTIONS BUT NOT SURE THEY WERE THE PROBLEM. ADVISED CUSTOMER TO CALL BACK IF PROBLEM REOCCURS. <<ONLY ONE CUSTOMER AFFECTED>> SH ///VER/CRB L/3 CRB IDC XXXX
17880 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-04-16 15:47 | 2010-04-16 17:20 | 2 | 93 | 63913-1 | 186 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BUSHING ON ONE OF THE HOT LEADS ON TRANSFORMER HAD LOOSENED UP AND HOT LEAD FELL OUT AND WAS HANGING DOWN POLE. I REPLACED LEAD AND TIGHTENED BUSHING. CUSTOMER SAID SHE COULD NOT GET TV TO COME ON. THIS FAULT SHOULD NOT HAVE AFFECTED HER APPLIANCES THOUGH. VER/HFP L3/HFP IDC XXXX
17881 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2010-08-30 00:54 | 2010-08-30 04:00 | 1 | 186 | 61742-1 | 186 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE DROP //VER/GAH IDCC CDC92, WIRE DOWN POLE TO HOUSE XXXX
17882 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2021-07-09 11:21 | 2021-07-09 12:23 | 3 | 62 | 4878501 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout. apr at 1223 close ticket
17883 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-07-21 11:27 | 2009-07-21 13:00 | 2 | 93 | 53761-1 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, REPLACING BAD CUTOUT//COD 2// VER/DBM IDC XXXX
17884 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-04-22 19:06 | 2018-04-22 20:08 | 3 | 62 | 4263061 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called customer no reading on meter Fuse link broke. Restored @ 20:08. sh/ ISO 38830811B00059/ COD 3 L3/HFP
17885 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-07-09 12:37 | 2016-07-09 14:10 | 2 | 93 | 4596131 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PH ONLY//65T FUSE OUT DUE TO BAD CUTOUT CLEARED FAULT UP. FUSED UP EVERYTHING OK/ ISO 38831126A00737/ COD 2/ VER/BOW
17886 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2015-10-02 11:35 | 2015-10-02 12:37 | 3 | 62 | 4302571 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38820942B20025. LINE CREW IS EN-ROUTE. POWER RESTORED AT 12:37.// VER/ ADH
17887 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2021-04-28 17:16 | 2021-04-28 20:22 | 1 | 186 | 4489881 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Transformer fuse out//Bad lightning arrester. Made repairs. Power restored at 20:22.
17888 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-06-06 08:39 | 2016-06-06 11:45 | 1 | 186 | 4313051 | 186 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIREDREPAIRED CONNECTIONS COD-1 ISO TF 38830247A30375 VER/HFP L3/HFP
17889 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-03-30 13:45 | 2019-03-30 16:51 | 1 | 186 | 4038201 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans. fuse open @1-A2-284, checking. Bad 15kva 7200 trans. here, will be changing. Got trans. changed and power restored @1651.
17890 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2019-10-18 21:04 | 2019-10-18 22:06 | 3 | 62 | 4167681 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse link
17891 | Hazard | 3309003 | JEFF | VIPER | 2019-02-02 19:23 | 2019-02-02 20:25 | 3 | 62 | 4749551 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
17892 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-10-09 16:46 | 2015-10-09 19:52 | 1 | 186 | 4333681 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN FEEDING UNDERGROUND RISER ON 37820008C000115 REPLACED ROAD SIDE CUTOUT ON 37820008C00115 RESTORED POWER AT 19:52//MADE MDC TO SHOW 100T L/F//A PHASE COD 207
17893 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-12-26 13:57 | 2022-12-26 15:30 | 2 | 93 | 4362121 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew requird bad cutout door
17894 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-07-27 09:39 | 2010-07-27 12:45 | 1 | 186 | 57774-1 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE//////////XFR IS BAD,WILL HAVE TO REPLACE IT.WILL CONTACT CREW RELEASED BY CREW 074S06//REPLACED TRANSFORMER AND CLOSED IN AT 1245 COD-1 VER/HFP L3/HFP IDC XXXX
17895 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-09-17 17:24 | 2008-09-17 20:30 | 1 | 186 | 64982-1 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3117601// STS WR # 26325592 BAD 10 KVA SEND NOTE TO TECK TO REMOVE OLD TRANS AND SEC. COD-1 //SENT NOTE TO ENGINEERING --HFP IDC XXXX
17896 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2016-07-28 18:54 | 2016-07-28 22:00 | 1 | 186 | 4702841 | 186 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/0 LEAD BURNT IN TWO ON TRANSFORMER BANK, NEED 2 MEN AND BIG BUCKET WITH FLAGMEN, 4/0 COPPER WIRE RELEASED BY CREW 077S04//BANK NEEDS RE-BUILT//SEND TO DOUG//SENT TO TECH VER/CRB
17897 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-12-21 10:44 | 2014-12-21 13:50 | 1 | 186 | 4873151 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT WILL MAKE REPAIRS...MADE REPAIRS CLOSED CUTOUT IN AT 13:50/ ISO 37830166000265/ COD1/ VER/BOW
17898 | Whitesburg | 3401301 | FLEMING | NEON | 2009-09-09 09:18 | 2009-09-09 10:20 | 3 | 62 | 57822-1 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED REPLACED CUTOUT RESTORED POWER AT 10:20// VER/TOM L3/TOM IDC XXXX
17899 | Pikeville | 3421001 | BREAKS | CITY | 2019-08-05 13:26 | 2019-08-05 16:32 | 1 | 186 | 4842361 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Meter burnt up will replace/// Replaced bad meter restored service @ 16:32
17900 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2021-05-05 17:57 | 2021-05-05 19:30 | 2 | 93 | 4541491 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BURNED UP,WILL REPLACE IT/////////ACTUALLY,DOOR WAS BURNED OUT,REPLACED IT&RESTORED POWER.ALL OK AFTERWARDS
17901 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-09-16 20:58 | 2018-09-16 22:00 | 3 | 62 | 4108851 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned up ,I replaced it
17902 | South Williamson | 3411401 | DEWEY | INEZ | 2022-09-15 12:37 | 2022-09-15 14:10 | 2 | 93 | 4886041 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Found bad connection at xfmr. Reworked all connections and restored @ 14:10. sh
17903 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2021-02-04 18:24 | 2021-02-04 19:57 | 2 | 93 | 4938231 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout repaired and restored @ 1957 // line fuse only out COD 2
17904 | Pikeville | 3421001 | BREAKS | CITY | 2020-12-04 12:15 | 2020-12-04 13:17 | 3 | 62 | 4744811 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse blown on pole 220-269 due to broke cutout///will make repairs/// Replaced broken line fuse cutout on pole 220-269 and restored @ 13:17
17905 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2021-07-02 22:47 | 2021-07-03 00:20 | 2 | 93 | 4852201 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke @ 38830954B40825.//Replaced cutout and restored @ 00:20/ ISO 38830954B40825/ COD 2
17906 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-08-27 19:19 | 2016-08-27 22:25 | 1 | 186 | 4842361 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE PULLED INTO, REFUSED @ 2225. VER/KEP
17907 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2009-07-11 07:34 | 2009-07-11 10:40 | 1 | 186 | 57808-1 | 186 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3001102//-BAD CONNECTION-TRUCK BROKEDOWN-CALLED MECHANIC L3/HFP IDCC PN23 XXXX
17908 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-08-11 23:04 | 2021-08-11 23:35 | 6 | 31 | 4039031 | 186 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Found a broke Neutral in service drop,Pulled Meter to make repairs,Pulled at 23:04 and restored at 23:35..
17909 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-07-03 21:04 | 2014-07-04 00:10 | 1 | 186 | 4191461 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | UNSURE WHAT BLEW FUSE BUT CUTOUT DOOR WAS DAMAGED. CHANGING CUTOUT SO I CAN TRY XFMR FUSE. DIFFICULT LOCATION. REPLACED CUTOUT AND RESTORED @ 00:10. SH VER/KEP
17910 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-02-09 12:24 | 2016-02-09 15:30 | 1 | 186 | 4685381 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED ON SERVICE POLE. OOONLY ONE CUSTOMER AFFECTEDOO REPLACED SERVICE TO ELIMINATE SEVERAL CONNECTIONS. SH VER/CRB
17911 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-06-27 09:45 | 2020-06-27 12:51 | 1 | 186 | 4079331 | 186 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 service drop neutral burndt into @weatherhead, got spliced back out and restored @1251. Only 1 customer was affected.
17912 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-07-20 09:10 | 2017-07-20 10:12 | 3 | 62 | 4145441 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND TRANSFORMER WITH SMALL LEAK : REPLACED AND POWER RESTORED AT 10:12 COD-3 ISO TF 37830270D00360 SJGC MCCDIS
17913 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-09-02 17:54 | 2017-09-02 21:00 | 1 | 186 | 4324991 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUSTOMER ANSWERING MACHINE 6T FUSE OUT DUE TO BAD TRANSFORMER. NO ONE LIVES IN THIS HOUSE TALKED TO CUST AND HE SAID TO COME BACK ONE DAY NEXT WEEK TO CHANGE OUT. I CREATED AN OPS ORDER # 037207120 FOR TRANSFORMER CHANGE. CAN CLOSE THIS ORDER OUT RELEASED BY CREW 074S11 VER/KEP
17914 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-01-29 23:08 | 2008-01-30 02:14 | 1 | 186 | 60837-1 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3401102//REPLACED BROKEN 6T FUSE TCM//COD 1// VER/DBM IDC XXXX
17915 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-11-25 14:56 | 2020-11-25 15:58 | 3 | 62 | 4723171 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required blown fuse
17916 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-09-13 11:30 | 2010-09-13 14:36 | 1 | 186 | 65996-1 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE////////BAD XFR,CREW WILL BE REPLACING IT SHORTLY,NOTE NEW FETR///////REPLACED XFR AND RESTORED//VER/CRB IDC XXXX
17917 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-10-22 08:06 | 2021-10-22 09:39 | 2 | 93 | 4001801 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Cutout door burnt up will replace///Replaced burnt up door and restored service @ 09:39
17918 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-03-17 09:37 | 2015-03-17 11:10 | 2 | 93 | 4202811 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 448-382, OPENED LINE FUSE ON POLE 448-86 AT 10:26(SEE 4203041) REPLACED CUTOUT RESTORED POWER AT 11:10.//COD 2// VER/DBM
17919 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-06-10 23:42 | 2017-06-11 01:15 | 2 | 93 | 4930141 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 38830223000137, BAD LIGHTNING ARRESTOR. ARRESTOR CUT IN CLEAR, POWER RESTORED AT 01:15./// VER/DKM
17920 | Hazard | 3309301 | VICCO | REDFOX | 2017-08-12 11:14 | 2017-08-12 12:47 | 2 | 93 | 4253171 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR FUSE OUT, BAD LIGHTNING ARRESTOR ON XFMR, REPLACED ARRESTER/ ISO 37830350000007/ COD 2/ VER/BOW
17921 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-06-19 11:54 | 2014-06-19 15:00 | 1 | 186 | 4111351 | 186 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CUST. HAS PART POWER// WILL CHECK/// CUST. UG IS BAD// CREW ENROUTE TO MAKE REPAIRS/// CREW INSTALLED ADD-A-PHASE// WIIL REPAIR LATER
17922 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-04-24 12:43 | 2016-04-24 13:45 | 3 | 62 | 4121411 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT DOOR VER/CRB
17923 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-12-17 15:42 | 2019-12-17 18:48 | 1 | 186 | 4163971 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, replaced cutout restored power at 18:48..
17924 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-01-02 14:57 | 2022-01-02 16:30 | 2 | 93 | 4261741 | 186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Line fuse blown on 169-70///primary pulled out of sleeve and blowed line fuse//will be making repairs///Repairs made restored @ 16:30
17925 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2020-10-17 07:55 | 2020-10-17 11:00 | 1 | 185 | 4563611 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Released by crew 078S01. xfmr cutout broke, cutout replaced power on at 1100
17926 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-05-18 10:25 | 2010-05-18 13:30 | 1 | 185 | 64581-1 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP == REPLACED GATE == REFUSED POWER OK COD-1 VER/HFP L3/HFP IDC XXXX
17927 | Hazard | 3307301 | BULAN | ARY-HEINE | 2022-05-27 05:03 | 2022-05-27 08:08 | 1 | 185 | 4958391 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Held for daylight per KPCO late night callout guidelines. A guy wire rusted off and made contact with a XFMR riser, blowing the fuse on pole . I repaired the guy wire and restored power at 8:08.
17928 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-01-13 11:28 | 2012-01-13 14:33 | 1 | 185 | 4257571 | 185 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND A BAD SERVE END ON SERVICE DROP, HAVE IT REMOVED AND SQUEEZED UP WITH A GOOD SQUEEZON, AND EVERYTHING IS FINE AT SUBWAY NOW, VER/KEP IDCC PN13 XXXX
17929 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-12-30 20:40 | 2014-12-30 23:45 | 1 | 185 | 4893821 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TRANSFORMER LEAD BURNT IN TWO, MANUAL, NEED 1 MAN... REPLACED LEADS, POWER RESTORED. VER/ARN
17930 | Hazard | 3303902 | LESLIE | WOOTON | 2020-02-08 12:53 | 2020-02-08 15:58 | 1 | 185 | 4384361 | 185 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad secondary conn on weatherhead. all power restored @ 15:58 hrs p.hicks
17931 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-06-24 11:45 | 2010-06-24 12:22 | 5 | 37 | H56254-1 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE DOWN FROM POLE 185-66 TO 185-137, POLE 185-200 REPLACED ARRESTER ON CSP TRANSFORMER, 30T FUSE POLE 185-176 OPEN RELEASED BY CREW 074S03/// WHEN CREW ARRIVES WILL HAVE TO TAKE THE OTHER 2 PHASES OUT TO PULL DOWNED WIRE. TIM MCCOY//ONLY B PHASE OPEN//COD 12//OPENED OTHER TWO PHASES INTERRUPTING 5 MORE CUST @ 1145//RESTORED ALL CUST AS OF 1222// IDCC DUP FOR OTHER FUSES XXXX
17932 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-05-27 16:03 | 2022-05-27 19:08 | 1 | 185 | 4968641 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Have a Broke Line fuse cutout on Pole 263-C-329 will be making repairs..This is Mauual Pole Jason is on the way to help make repairs..Restored at 19:08.
17933 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-11-07 12:40 | 2019-11-07 15:45 | 1 | 185 | 4006361 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I changed out one bad cutout
17934 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-12-09 17:35 | 2012-12-09 20:40 | 1 | 185 | 4454801 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830248B00585 NEED 1 MAN AND BUCKET TRUCK.//COD 1//ISO// // VER/TOM L3/TOM IDCC PN147 XXXX
17935 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-03-09 09:35 | 2010-03-09 12:40 | 1 | 185 | 64154-1 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTOMER HAS SERVICE DROP BURNT OPEN I WILL REPLACE THERE IS ALSO A SILVER TOP CUT OUT AND PORCELIN L/A I WILL REPLACE THOSE AS WELL.TIM MCCOY RELEASED BY CREW 074H10//VER/CRB IDC XXXX
17936 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-10-07 16:52 | 2011-10-07 17:29 | 5 | 37 | 4956411 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 5// VER/DBM IDC XXXX
17937 | Pikeville | 3408101 | SALISBURY | PRINTER | 2008-04-04 09:00 | 2008-04-04 12:05 | 1 | 185 | 63751-1 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408101//TRANSFORMER CUTOUT BROKEN....REPLACED 2 CUTOUTS AND 1 ARRESTER, ALL WORK COMPLETE / GXJ//COD 1// VER/DBM IDC XXXX
17938 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-02-22 13:01 | 2016-02-22 13:38 | 5 | 37 | 4746581 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY NETURAL IS BROKEN MID SPAN WILL NEED HELP TO REPLACE. HAVE CALLED TIM HALL & HE IS TO GET HELP. PULLED XFMR OFF @113:01 BACK ON @13:38 ISO 37830069000034 COD 5
17939 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2022-06-08 19:29 | 2022-06-08 22:34 | 1 | 185 | 4040881 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | servicesplice resqueezed
17940 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2018-07-07 07:45 | 2018-07-07 10:50 | 1 | 185 | 4746781 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10kva transformer called crew will be on the way. need 15kva 7200. changed transformer everything ok
17941 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2011-11-23 08:00 | 2011-11-23 11:05 | 1 | 185 | 4106361 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE TRANSFORMER CUTOUT HAS FAILED. VER/KEP IDC XXXX
17942 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-03-23 20:22 | 2012-03-23 23:27 | 1 | 185 | 4610341 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 501-275 PATROLLING. BROKEN 19.9 CUTOUT ON 501-137 LINECREW REQUIRED RELEASED BY CREW 078S11/CREW ON SITE/FETR 0030 3/24/12/VEM/REPAIRS MADE AND POWER RESTORED 2327/PLEASE CLOSE TICKET/THANKS/VEM //VER/GAH IDC XXXX
17943 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-05-11 12:35 | 2016-05-11 15:40 | 1 | 185 | 4200311 | 185 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IS SPLICE IN #2 SERVICE DROP BURNED INTO. I TOLD CUSTOMER TO TURN BREAKER OFF UNTIL SERVICE DROP COULD BE CHANGED. HE THOUGHT HE HAD DAMAGES. I TOLD HIM TO CALL IN DAMAGE COMPLAINT IF SO. STEVE RAY IS SENDING HELP. RELEASED BY CREW 074H21 TREE HIT LINE NEXT TO HOUSE NEUTRAL HAD PULLED OUT OF CONNECTION VER/AWD
17944 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-07-28 13:58 | 2014-07-28 14:35 | 5 | 37 | 4302231 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT OFF POWER RESTORED AT 14:35 VER/CRB
17945 | Paintsville | 3409302 | KENWOOD | AUXIER | 2009-07-21 20:10 | 2009-07-21 23:15 | 1 | 185 | 57312-1 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER/// REPLACED XFMR AND CHECKED VOLTAGE// RDM VER/TOM L3/TOM IDC XXXX
17946 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-09-09 12:55 | 2009-09-09 16:00 | 1 | 185 | 59300-1 | 185 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BELEIVED TO HAVE A BAD CONNECTION ON SECONDARY POLE. WE ARE GOING BACK ON TOP OF MOUNTAIN TO CHECK. WILLIE ROBINSON IS WITH ME. L3/HFP IDC XXXX
17947 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-06-20 16:25 | 2015-06-20 19:30 | 1 | 185 | 4620031 | 185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR C/O BROKE WILL HAVE TO REPLACE, //// REPLACED C/O POWER RESTORED.//COD 1// VER/DBM
17948 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-12-18 11:36 | 2015-12-18 14:40 | 1 | 184 | 4542291 | 184 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION @ WEATHERHEAD FAILED.. VER/CRB
17949 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-06-03 23:40 | 2010-06-04 01:12 | 2 | 92 | 56292-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 19.9 CUTOUT//COD 2// VER/DBM IDC XXXX
17950 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-06-15 19:43 | 2010-06-15 21:15 | 2 | 92 | 65629-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED VER/KEP L3/KEP
17951 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2020-11-23 09:51 | 2020-11-23 12:55 | 1 | 184 | 4717591 | 184 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Found a Neutral connection that was into,Got it connected back up and everything is working like its suppose to.12:55.
17952 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-05-20 17:34 | 2015-05-20 18:20 | 4 | 46 | 4450411 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN ON POLE 426-88. FUSE BROKEN, REFUSED AND RESTORED POWER AT 1820//COD 4// VER/ ADH
17953 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-11-12 09:33 | 2016-11-12 11:05 | 2 | 92 | 4095621 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE. DUE TO OLD CUTOUT CHANGED CUTOUT ALSO. FUSED UP EVERYTHING OK/ ISO 38830876D00138/ COD 2/ VER/BOW
17954 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-12-20 17:26 | 2013-12-20 20:30 | 1 | 184 | 4179961 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED LINE CREW 3-CUTOUTS 40T FUSE RELEASED BY CREW 078S08, CREW ON SITE, CHANGED CUTOUTS, ALL POWER RESTORED COD 1 ISO LF 38830070A31053 VER/HFP L3/HFP
17955 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-05-04 07:12 | 2021-05-04 10:16 | 1 | 184 | 4519701 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT FAILED REPAIRED AND RESTORED @1016
17956 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-10-08 13:59 | 2021-10-08 14:45 | 4 | 46 | 4331581 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cut out power restored 14:45
17957 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-09-12 22:58 | 2017-09-13 00:30 | 2 | 92 | 4356481 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR F OUT,WILL RE-FUSE///////CUTOUT IS BROKEN,WILL REPLACE IT////////REPAIRS COMPLETED,RESTORED,ALL OK AFTERWARDS/2 COD - 38820985000055/// VER/DKM L3/HFP XXXHFP
17958 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-11-03 07:26 | 2014-11-03 10:30 | 1 | 184 | 4694871 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHANGING.CHG BACK ON 10.30..// ISO 38830901B11025// COD 1// VER/BOW
17959 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2010-11-25 13:58 | 2010-11-25 15:30 | 2 | 92 | 59594-1 | 184 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE ON TRANSF POLE WENT BAD == REPAIRED == POWER OK COD-2 VER/HFP L3/HFP IDC XXXX
17960 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-03-27 16:21 | 2014-03-27 19:25 | 1 | 184 | 4529451 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED MAT BUCKET & 15KVA 19.9KV TR // COD-1 ISO TF 37830531C00053 VER/HFP L3/HFP
17961 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-03-31 11:56 | 2010-03-31 13:28 | 2 | 92 | 56471-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. FUSE LINK BROKE. I REFUSED TRANS. COD-2 VER/HFP L3/HFP AJB
17962 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2018-04-11 15:28 | 2018-04-11 17:00 | 2 | 92 | 4211671 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, replaced cutout, power restored/ ISO 37830274000103/ COD 2
17963 | Hazard | 3303902 | LESLIE | WOOTON | 2009-04-07 15:48 | 2009-04-07 17:20 | 2 | 92 | 50300-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//3303902/VER/CRB IDCC MCCDIS XXXX
17964 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-11-07 13:31 | 2011-11-07 15:03 | 2 | 92 | 4057331 | 184 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT GOING TO REFUSED FUSE PULL INTO COD-2 ISO TF 38831059A00292 VER/HFP L3/HFP IDC XXXX
17965 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-12-01 13:13 | 2011-12-01 14:45 | 2 | 92 | 4133431 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN// CUTOUT DOOR BURNED UP// REPLACED DOOR//REFUSED //POWER IS RESTORED144//COD 2// VER/DBM IDC XXXX
17966 | Hazard | 3311103 | STINNETT | WENDOVER | 2019-04-04 10:41 | 2019-04-04 13:45 | 1 | 184 | 4056731 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT WILL NEED CREW MAY CAN REACH WITH BIG BUCKET Released by crew 077S01 L3/HFP
17967 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-06-03 10:48 | 2018-06-03 12:20 | 2 | 92 | 4549921 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse broke, refused and power restored at 12:27Transformer fuse broke, refused and power restored at 12:20
17968 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2008-11-19 08:58 | 2008-11-19 10:30 | 2 | 92 | 66563-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3311701// CONNECTOR BURNED INTO ON XFMR SECONDARY RISER MAY BE OVERLOADED ON 1/0 TWIST SENDING NOTE TO TECH VER/KEP IDC XXXX
17969 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-06-30 11:44 | 2008-06-30 14:48 | 1 | 184 | 60131-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NOTHING VISIBLY WRONG ,BUT 4/3 SERV HAS ABT 4 SPLICES IN IT.WILL CHANGE IT OUT WHEN RAIN STOPSREPLACED 4/3 SERV WITH 2/3,ALL OK AFTERWARDS VER/ARN IDC XXXX
17970 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2017-03-20 12:16 | 2017-03-20 15:20 | 1 | 184 | 4572311 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FAILED DEADEND INSULATOR BLEW 40T LINE FUSE. CREW ENROUTE TO ASSIST. RESTORED @ 15:20. SH 38830954D20719 VER/AWD
17971 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-02-04 13:44 | 2021-02-04 16:48 | 1 | 184 | 4937601 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | busted c/o--crew req-(new c/o on hood of tractor by pole and cust has tracktor and can pull you out if needed.i had no problem in and out)-ds020421 Released by crew 078S01/ changed broken cutout time restored 1648
17972 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2018-02-12 16:58 | 2018-02-12 18:30 | 2 | 92 | 4835631 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad c/o on transformer pole 1096-12, have chged, power restored at this loc at 1830 by amg/ ISO 39831096000012/ COD 2
17973 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-02-19 19:04 | 2020-02-19 22:08 | 1 | 184 | 4419431 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cracked c/o pole 38830308000127--10t lat fuse in at 22:08-ds021920 L3/HFP
17974 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2010-10-27 15:40 | 2010-10-27 17:12 | 2 | 92 | 65799-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL PULLED OUT OF SLEEVE AT XFMR POLE. DOZER HAS BEEN WORKING AROUND POLE AND PROBABLY HIT GUY WIRE AGAIN AS THEY DID YESTERDAY. OPENED XFMR ON 38830809000282 @ 15:40, REPAIRED SERVICE AND CLOSED @ 17:12. SH//COD 2// VER/DBM IDC XXXX
17975 | Hazard | 3303902 | LESLIE | WOOTON | 2009-08-11 10:53 | 2009-08-11 12:25 | 2 | 92 | 50301-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | VER/HFP LEAD BURNT OUT OF XFMR. REPAIRED LEAD. COD-2 ISO TF 37830365C00098 L3/HFP IDC XXXX
17976 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-03-14 14:26 | 2013-03-14 17:30 | 1 | 184 | 4906091 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | 34.5 KV PRIMARY METERING FAILED. NO REPLACEMENT AVAILABLE. CREW ENROUTE TO BYPASS IT. 37820098B00378 COD-1 VER/KEP IDC XXXX
17977 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-12-07 23:53 | 2014-12-08 01:25 | 2 | 92 | 4845371 | 184 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE SECONDARY PHASE WIRES. ONLY ONE CUSTOMER AFFECTED.
17978 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2017-06-06 02:46 | 2017-06-06 04:18 | 2 | 92 | 4913921 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | B PHASE TRANS. FUSE OUT ON BANK POLE 48-A4-1269, EVERYTHING CHECKED OUT OK, REFUSED @0418./// VER/DKM
17979 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2017-08-30 18:22 | 2017-08-30 18:45 | 8 | 23 | H4311081 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN. OPENED TRANSFORMER FUSE AT 1822-1845 38830020D37013REPAIR BAD SD. OPEN XFMER @ 20-7013 @ 18:22 CLOSED @ 18:45 VER/AWD VER/HFP L3/HFP
17980 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-12-24 18:25 | 2008-12-24 21:29 | 1 | 184 | 63637-1 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3110903//CHANGING CUTOUT TO TRY XFMR/FETR2200/XFMR BACK IN AT 2129/PLEASE CLOSE TICKET/THANKS/VEM // COD 1// VER/DBM L3/KEP IDC XXXX
17981 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2016-10-20 19:59 | 2016-10-20 23:03 | 1 | 184 | 4033901 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O ON TRANSFORMER WILL NEED CREW, AND TRAFFIC CONTROL, IN BAD CURVE ON 503, CAN USE TRUCK, RELEASED BY CREW 078S06--CREW ON SITE--REPLACED CUTOUT AND ARRESTOR---BACK ON AT 23:03---RMV VER/CRB L3/HFP XXXHFP
17982 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-04-08 07:01 | 2009-04-08 10:05 | 1 | 184 | 50398-1 | 184 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | CUST TRANSF POLE NO IS NOT RIGHT SHOULD BE 270D-230 == LEAD ON TRANSF BURNED OFF == REPAIRED == POWER STORE//MD FILED ON MISSMAPPED PREMISE// VER/DBM IDCC PN494 XXXX
17983 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-05-28 09:08 | 2019-05-28 10:40 | 2 | 92 | 4352631 | 184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 305-13. cutout replaced. power restored @ 10:40
17984 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2018-06-05 12:31 | 2018-06-05 15:35 | 1 | 184 | 4558121 | 184 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | crew req, need to install power temp at this loc, bad 4/0 urd, 120v on one side, 78 v on the other side phase to grd, ph to ph 178 Released by crew 078S06 ,install power temp cust restored ,need to send to tech to replace ug cable please close ticket thanks.bt//SENT TO TECH AND LINE SUPER
17985 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-11-06 20:52 | 2020-11-06 23:55 | 1 | 183 | 4650031 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a broke Neutral in service drop,Will have to climb pole to make repairs. Spliced Neutral and Customer has Perfect Voltage.
17986 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2019-08-11 17:04 | 2019-08-11 18:05 | 3 | 61 | 4872191 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke L3/HFP
17987 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-10-24 14:42 | 2022-10-24 17:45 | 1 | 183 | 4060401 | 183 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | neutral come out of crimp sleeve and customer was getting bad voltage.got connection fixed and power restored @ 17:45
17988 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-09-20 14:07 | 2009-09-20 17:10 | 1 | 183 | 55502-1 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 15KVA TRANS IS BURNED UP ON POLE 237-32. I AM CALLING FOR HELP. WE CHANGED TRANS. AND GOT POWER BACK ON AT 17:10. COD-? POWERON SHOWS - 0 - CUSTOMERS ON THIS TRANSFORMER L3/HFP IDC XXXX
17989 | South Williamson | 3411401 | DEWEY | INEZ | 2009-11-05 08:15 | 2009-11-05 11:18 | 1 | 183 | 62260-1 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411401// CONN BURNED 4/3 SERVICE NEUTRAL INTO. CUST HAS DAMAGE. CHANGED 4/3 SERVICE DROP TO 2/3// VER/DBM IDC XXXX
17990 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-10-10 09:07 | 2008-10-10 12:10 | 1 | 183 | 54788-1 | 183 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP THIS CUST HAS A 60 AMP METER BASE. 4-3 SERVICE DROP SERVED CUST. THIS DROP SHOULD BE ABLE TO HANDLE 60AMP OR 100AMP. BUT NEUTRAL WAS BURNT INTO ABOUT 3 FOOT FROM DEAD END AT HOUSE. NOT SHURE IF CUST HAS UPGRADED BREAKER BOX ON INSIDE OF HOME IF SO THEY COULD....SENT EMAIL TO PEGGY WYSONG..HFP IDC XXXX
17991 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-30 16:23 | 2019-06-30 19:26 | 1 | 183 | 4622991 | 183 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Broken neutral in service drop
17992 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-07-03 17:34 | 2008-07-03 18:35 | 3 | 61 | 61784-1 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3401103//...BROKEN XFMR FUSE....CHG. FUSE...BB// COD 3// TRANS OUTAGE // VER/TOM IDC XXXX
17993 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2019-02-10 13:57 | 2019-02-10 17:00 | 1 | 183 | 4774981 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 span of open wire burnt down at a connection at the transformer. will be making repairs. replaced span of sec got repairs made closed transformer back in at 17:00 everything ok
17994 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2018-02-26 21:26 | 2018-02-26 22:27 | 3 | 61 | 4885451 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Cutout door burnt up will replace// Replaced bad door and fuse //Restored service @ 22:27/ ISO 37820151000063/ COD 3
17995 | Paintsville | 3409302 | KENWOOD | AUXIER | 2020-12-26 14:34 | 2020-12-26 15:35 | 3 | 61 | 4825111 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link had broke inside of cutout door causing outage. I refused and restored @15:35
17996 | South Williamson | 3411401 | DEWEY | INEZ | 2018-04-02 06:07 | 2018-04-02 09:10 | 1 | 183 | 4163331 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with late night callout guidelines////customer mismapped///line fuse cutout broke on pole 815-18///i replaced cutout and arrestor//restored at 9:10//complete//em
17997 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-06-28 12:09 | 2022-06-28 13:10 | 3 | 61 | 4340321 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer had a lead brunt off at the xformer got spilced and full power restored
17998 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2021-01-02 07:42 | 2021-01-02 10:45 | 1 | 183 | 4843281 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout riser is damaged on pole 490-A3-305 but customer has full power. This cutout is manual behind a double wide. Customer said it was ok to leave for the morning and so did the duty supervisor. .Released by crew 077H20.changed manual cutout, all power restored @ 10:45 hrs p.hicks
17999 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2010-07-15 17:23 | 2010-07-15 20:26 | 1 | 183 | 50686-1 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED BAD TRANSFORMER VER/KEP L3/KEP IDC XXXX
18000 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-02-14 19:24 | 2008-02-14 20:25 | 3 | 61 | 63370-1 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3116102//6T FUSE BROKE// VER/TOM IDC XXXX
18001 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-02-26 20:51 | 2022-02-26 22:30 | 4 | 99 | 4549291 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Melted lug in a pole mounted underground UG pedestal, calling for help. I made a temporary fix for this customers UG cable but this needs to have a crew come replace all of this damaged equipment on Monday. The XFMR on pole 37830223B00207 was opened at 22:02 and closed back at 22:30./ 1 customer out part out opened transformer 3 additional customers
18002 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-02-24 13:12 | 2021-02-24 16:15 | 1 | 183 | 4241951 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LF blown on 38831101D30033 will try fuse// opened up other 2 phases at 15:40, cut arrester in the clear, closed all 3 phases at 16:15// customers power was surging on arrival caused by back feed from a bank of XFMs, customer at 123 Steele Rogers ln. said that her laptop was damaged from the surge
18003 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-03-26 11:57 | 2015-03-26 15:00 | 1 | 183 | 4230121 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..CHANGING COD-1 ISO TF 38830655B00152 VER/HFP L3/HFP
18004 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2010-01-21 13:32 | 2010-01-21 14:33 | 3 | 61 | 57271-1 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK HAD ROTTED INTO,RELACED AND RESTORED,ALL OK AFTERWARDS VER/TOM L3/TOM IDCC MCCPP XXXX
18005 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-12-17 21:05 | 2014-12-17 22:06 | 3 | 61 | 4867711 | 183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE38821058D00132 ////RE-FUSED AND RESTORED,BELIEVE FUSE ROTTED INTO,AT LEAST THATS THE WAY IT APPEARED VER/CRB
18006 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-10-31 08:28 | 2009-10-31 11:31 | 1 | 183 | 53437-1 | 183 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SQUEEZE ON VER/KEP L3/KEP IDCC MCCDL XXXX
18007 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2013-08-31 13:21 | 2013-08-31 16:23 | 1 | 182 | 4805461 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG/CREW TO INSTALL POWER TEMP/VEM/POWER TEMP INSTALLED/PLEASE COPY TICKET TO BOB REYNOLDS AND L RAYBURN/VEM VER/HFP L3/HFP
18008 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-03-17 14:55 | 2016-03-17 15:21 | 7 | 26 | H4858501A | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CREW REQUIRED BAD SECTION OF UNDERGROUND SECONDARY BETWEEN ADDRESS 310 AND 523 RELEASED BY CREW 078S03 OPENING SECONDARY LINE FUSE ON 206-2552 1445. WILL NOTIFY CUSTOMERS..OPENED TRANSFORMER AT 14:55, CLOSED IN AT 15:21..NEED WORK ORDER TO REPLACE THE SECONDARY SENT TO PAT STAMPER.ISO 38830206A42552 COD 9 VER/AWD IDC NEEDED SECOND OUTAGE XXXX AJB
18009 | Pikeville | 3402002 | KEYSER | STONECOAL | 2015-12-26 11:34 | 2015-12-26 13:05 | 2 | 91 | 4561921 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTIONS @ XFMR WERE HEATING UP // REWORKED ALL CONNECTIONS // POWER RESTORED// VER/ ADH
18010 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-03-12 03:29 | 2019-03-12 05:00 | 2 | 91 | 4973001 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required fuse link/MD Filed customer mis-mapped add 1cc/
18011 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-09-16 09:25 | 2010-09-16 12:27 | 1 | 182 | 50319-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 36910456 //TRANSFORMER BUSHING ON FIRE TRANSFORMER NEEDS REPLACED, 25KVA 19.9 TRUCK ACCESSIBLE,,,,,,BROADLEAF IS OFF OF ISAAC PARK RD. TURN ON BROADLEAF WILL BE FIRST DRIVEWAY ON THE LEFT BRICK HOME RELEASED BY CREW 078S02/CREW ON SITE/FETR 1330/REPAIRS MADE AND POWER RESTORED 1227/PLEASE CLOSE TICKET/THANKS/VEM /// COD-1 VER/HFP L3/HFP IDCC PN531 XXXX
18012 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2017-06-12 12:29 | 2017-06-12 14:00 | 2 | 91 | 4953201 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD FUSE LINK REPLACED POWER IS RESTORED AT THIS LOC AT 1400 BY AMG VER/CRB
18013 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-10-16 21:44 | 2013-10-16 23:15 | 2 | 91 | 4941561 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 1146-170, HAVE REPLACED AND CLOSED IN 20T LINE FUSE AT 2315 RESTORING POWER OT ALL CUST
18014 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-06-22 09:34 | 2020-06-22 11:05 | 2 | 91 | 4058151 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We had a broke XFM cutout on 166-240,Changed cutout and restored service at 11:05.
18015 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2011-01-13 18:00 | 2011-01-13 21:02 | 1 | 182 | 61141-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4-3 SERVICE DROP BURNT DOWN. I WILL HAVE TO CHANGE OUT TO 2-3. 4-3 SERVICE DROP BURNT INTO IN MID SPAN IN A SPLICE CUST HAD 200AMP SERVICE ENTRANCE. WIRE BURNT ALL THE WAY INTO. I HAVE REPLACED EVERYTHING OK. SEND COPY OF THIS TO PEGGY WYSONG. JUST IN CASE CUST CALLS IN DAMAGE COMPLAINT. // SENT EMAIL TO PEGGY WYSONG AS REQUESTED.... HFP VER/HFP L3/HFP IDC XXXX
18016 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-02-07 20:42 | 2011-02-07 22:13 | 2 | 91 | 55139-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT , GOING TO TRY FUSE BAD CUTOUT//VER/CRB IDC XXXX
18017 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-06-24 07:28 | 2014-06-24 10:30 | 1 | 182 | 4145521 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEU. BROKEN AT POLE ON SER. DROP ,REPLACE WITH 2/3 SER. DROP POWER RESTORED//COD 1// VER/DBM
18018 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-07-28 12:10 | 2008-07-28 15:12 | 1 | 182 | 61085-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3300602///120/208 7200 VOLT 50 KVA OVERHEAD XFMR BAD ON C PHASE JEFF COMBS CREW WILL RESPOND I ADVISED CUSTOMER OF A 16:30 ETR RELEASED BY CREW 077S04 REPLACED TRANSFORMWER AND RESTORED POWER CUSTOMER SAID EVERYTHING OK BUT SHE HAD PROBLEMS. JEFF COMBS IDC XXXX
18019 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-07-14 11:22 | 2011-07-14 12:53 | 2 | 91 | 4546131 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CLF BAD/// REPAIRED//POWER RESTORED COD-2 ISO TF 37830117000170 VER/HFP L3/HFP IDC XXXX
18020 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2012-10-22 19:41 | 2012-10-22 22:43 | 1 | 182 | 4164351 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA BRING 15KVA TRUCK TO POLE 25TH AND US 23 CATLETTSBURG SEND TO BILL F. /// FRALEY & RUGGLES & MCCANNBAD 10KVA BRING 15KVA TRUCK TO POLE 25TH AND US 23 CATLETTSBURG SEND TO BILL F. RELEASED BY CREW 078S08 COD-1 ISO TF 38830094D26582 VER/HFP L3/HFP IDC XXXX
18021 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2010-09-11 07:29 | 2010-09-11 09:00 | 2 | 91 | 65401-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN ... REPLACED CUTOUT, ALL WORK COMPLETE / GXJ COD-2 VER/HFP L3/HFP IDC XXXX
18022 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2014-12-16 21:17 | 2014-12-16 22:48 | 2 | 91 | 4865591 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 6T FUSE MAY HAVE BROKE INTO. WILL BE OUT OF THE TRUCK FUSING UP ISO POLE 37830188B00239 //MADE MDC TO SHOW THE RIGHT TRANS/LOOKS LIKE 6T FUSE MAY HAVE BROKEN INTO. WILL BE OUT OF THE TRUCK FUSING UP. FUSED UP EVERYTHING OK. VER/CRB
18023 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-02-18 06:39 | 2014-02-18 08:10 | 2 | 91 | 4396321 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER, BAD SPLICE IN SERVICE MADE REPAIRS RESTORED POWER AT 8:10//COD 2// VER/DBM
18024 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-05-21 14:14 | 2010-05-21 17:16 | 1 | 182 | 66045-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED SECONDARY CONNECTIONS VER/HFP L3/HFP IDC XXXX
18025 | Pikeville | 3408401 | KIMPER | LONGFORK | 2009-08-16 21:44 | 2009-08-16 23:15 | 2 | 91 | 59825-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3408401//DETERMINED XFR WAS BAD SEVERAL NIGHTS AGO BY DANNY H,BUT NO ACCESS TO POLE DUE TO ITS LOCATION AND ABT 100 FT OF JUNK METAL BETWEEN IT AND WHERE WE WOULD HAVE TO SET UP.TOLD CUST TO GET US REASONABLE ACCESS AND WE WOULD PROBABLY BE ABLE TO HELP HIM THEN.ALSO A VERY SNAKY PLACE //VER/GAH IDC XXXX
18026 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2008-01-05 15:09 | 2008-01-05 16:40 | 2 | 91 | 54058-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3302701// SECONDARY BURNT INTO// VER/TOM IDC XXXX
18027 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-12-03 10:33 | 2010-12-03 13:35 | 1 | 182 | 62709-1 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 1 LEG BAD ON URD CABLE FROM POLE TO HOUSE, CREW REQUIRED, 4/0, NEED POWER TEMP. CABLE NOT IN CONDUIT. RELEASED BY CREW 078S05/CREW ON SITE/ XFMER OFF 13:20 ON 13:30 ADD A PHASE INSTALLED VOLTAGE GOOD 123/247 RESTORED @ 13:35 J. HEMLEPP/ SEND INFO ON BAD UNDG LOCATION TO L. RAYBURN.//COD 3//EMAILED TO L RAYBURN// VER/DBM IDC XXXX
18028 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-04-05 21:27 | 2008-04-05 22:58 | 2 | 91 | 64352-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3401001TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS.TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. FUSE LINK BROKE. I REFUSED TRANS. VER/PDP IDC XXXX
18029 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-12-18 14:13 | 2015-12-18 17:15 | 1 | 182 | 4542751 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUSTOMER AFFECTED CONNECTION BURNT OPEN IN SERVICE ON XFMR POLE. REPAIRED AND RESTORED @ 17:15. SH// VER/ ADH
18030 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-03-06 05:08 | 2012-03-06 08:10 | 1 | 182 | 4555201 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE AT WEATHERHEAD PULLED APART, REPAIRS MADE, ALL POWER RESTORED. ONLY 1 CUSTOMER WAS OUT// VER/DBM IDC XXXX
18031 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-10-13 09:16 | 2018-10-13 12:18 | 1 | 182 | 4246641 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE Released by crew 077S01 repairs made and power restored at 1218 L3/HFP
18032 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-11-07 08:48 | 2008-11-07 11:50 | 1 | 182 | 62953-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3401001// SERVE-END MELTED DOWN ON POLE. I AM GOING TO RESPLICE S/DROP. I RESPLICED S/DROP. VER/KEP IDC XXXX
18033 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-03-18 16:37 | 2010-03-18 18:08 | 2 | 91 | 51566-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE, CHECKING TROUBLE, FUSE BROKE VER/HFP L3/FHP IDC XXXX
18034 | Whitesburg | 3312901 | JENKINS | KONA | 2017-01-30 07:28 | 2017-01-30 10:30 | 1 | 182 | 4341171 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED TO RED SEREVE END BAD IN SERVICE DROP REPAIRS MADE POWER RESTORED/ ISO 37830404A00093/ COD1/ VER/BOW L3/HFP XXXHFP
18035 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-03-29 17:19 | 2021-03-29 18:50 | 2 | 91 | 4401331 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | copper burned out of the hot tap on line fuse cutout, made repairs and restored customers
18036 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2021-12-03 13:38 | 2021-12-03 16:40 | 1 | 182 | 4146261 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | crew reqd. bad ug #2 neut 1/0 hot legs. tre Released by crew 078S04,installed power temp cust restored please close ticket thanks.bt///DAE 1000062716 created
18037 | Whitesburg | 3309302 | VICCO | JEFF | 2012-08-03 17:58 | 2012-08-03 21:00 | 1 | 182 | 4891081 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY VOLTAGE HIGH == 135 V 270 V === CHECK VOLTAGE DOWN THE LINE IT CHECKS OK === NEED 1 TRANSF 7200 V 10 KVA === THIS TRANSF IS A REMAN ONE === 1 MAN AND BIG BUCKET AND A 10 KVA === CHANGED TRANSF === POWER OK COD-1 ISO TF 37830373A20371 VER/HFP L3/HFP IDC XXXX
18038 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-10-11 10:58 | 2014-10-11 14:00 | 1 | 182 | 4605911 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEC TROUBLE WILL NEED BIG BUCKET TO MAKE REPAIRS BAD CONNECTION AT XFMR POLE FIXED POWER RESTORED // COD-1 ISO TF 39831120000018 VER/HFP L3/HFP
18039 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-05-16 14:28 | 2014-05-16 17:30 | 1 | 182 | 4715791 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT.IN THE PROCESS OF CHANGING.COMPLETE.17.30.//COD 1 VER/HFP L3/HFP
18040 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-09-02 17:09 | 2013-09-02 18:40 | 2 | 91 | 4813801 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @POLE 160-97 SERV TO REPAIR,REPAIRS MADE ALL CUST RESTORED@1840 PLEASE CLOSE TICKET THANKS.BT//COD 2 VER/HFP L3/HFP IDC XXXX
18041 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2008-04-12 18:33 | 2008-04-12 21:35 | 1 | 182 | 50684-1 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | TRAVIS TO HELP// REPLACED BAD CUTOUT//30080021//VER/CRB IDCC PN3780 XXXX
18042 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2018-02-18 14:23 | 2018-02-18 17:25 | 1 | 182 | 4858511 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | one of the hot legs pulled out of insulink in service drop midspan//will have to let drop down and make repairs//repairs made//restored at 17:25//complete//em/ 38820820B00313/ cod 1
18043 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-01-05 08:59 | 2022-01-05 10:30 | 2 | 91 | 4304591 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | Part power replaced bad connection at txmf apr at 1030 close ticket
18044 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2019-02-05 18:16 | 2019-02-05 21:18 | 1 | 182 | 4756841 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | called no answer primary riser broken on 195-1.i can make repairs// primary riser broken on 195-1.i can make repairs .made repairs. restored power at 21:18
18045 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-06-17 14:39 | 2012-06-17 16:10 | 2 | 91 | 4923161 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUIND BAD CUTOUT ON THIS POLE, I REPLACED CUTOUT AND POWER IS RESTORED AT THIS LOC AT 1610//COD 2// VER/DBM IDC XXXX
18046 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-09-18 23:18 | 2012-09-18 23:32 | 13 | 14 | 4066741 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP ON LINE FUSE CUTOUT ON POLE 494-35 IS ARCHING WILL HAVE TO OPEN FUSE TO MAKE REPAIRS ALSO TRANSFORMER ON THE POLE //COD 13HOT LINE CLAMP ON LINE FUSE CUTOUT ON POLE 494-35 IS ARCHING WILL HAVE TO OPEN FUSE TO MAKE REPAIRS.. OPENED AT 23:18 REPLACED CLAMP RESTORED POWER AT 23:32 ///VER/CRB L/3 CRB IDC XXXX
18047 | Hazard | 3303902 | LESLIE | WOOTON | 2019-10-08 15:43 | 2019-10-08 18:45 | 1 | 182 | 4120901 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 437-43 replaced cut out
18048 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-01-28 09:31 | 2019-01-28 12:33 | 1 | 182 | 4727471 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Center xfmr fuse blown on bank I will check.center and outside cutouts have failed and broke will be changing.. Myles Robinette is enroute with big bucket to assist..replaced all 3 cutouts and restored power @12:33
18049 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-10-09 15:28 | 2009-10-09 18:30 | 1 | 182 | 52011-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA 7200 XFMR, TRUCK OK, CREW REQUIRED, HAVE TO SET UP IN ROAD TO WORK. RELEASED BY CREW 078S05 /./ VER/TOM IDC XXXX
18050 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-05-31 20:59 | 2014-05-31 22:30 | 2 | 91 | 4957731 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SERVICER TO PATROLBROKEN FUSE LINK,,,CHG XFMR FUSE
18051 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2013-06-18 17:14 | 2013-06-18 18:45 | 2 | 91 | 4368631 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. IDCC CDC83 XXXX
18052 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-08-08 16:33 | 2010-08-08 18:04 | 2 | 91 | 51335-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRMR FUSE OUT....POLE 1086-A-145....2 CUSTOMERS ON THIS XFRMR.....LOOKS LIKE FUSE JUST BROKE...WILL RE-FUSE....//....REPLACED BROKEN FUSE....POWER ON....JRV...08/08/10 // COD 1 VER/HFP L3/HFP IDCC PN144, CNT1 XXXX
18053 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-09-26 08:58 | 2009-09-26 12:00 | 1 | 182 | 63600-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION ON XFMR POLE RESTOPRED 1200 VER/KEP L3/KEP IDC XXXX
18054 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-08-09 20:39 | 2017-08-09 22:10 | 2 | 91 | 4245141 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLOWN ON XFMR , REPLACED ARRESTER RESTORED POWER AT 22:10.. VER/KEP
18055 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2013-01-19 08:49 | 2013-01-19 10:20 | 2 | 91 | 4688881 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER SERVICE NEUTRAL BROKE, ONLY ONE CUSTOMER AFFECTED MADE REPAIRS RESTORED POWER AT 10:20.//COD 2// VER/DBM IDC XXXX
18056 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2016-08-25 08:38 | 2016-08-25 11:40 | 1 | 182 | 4834011 | 182 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NU, BROKE REPAIRED VER/HFP L3/HFP
18057 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-08-26 17:26 | 2022-08-26 20:28 | 1 | 182 | 4799391 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25KVA 7200 XFM, Brandon Isom is coming to help change it out
18058 | South Williamson | 3411401 | DEWEY | INEZ | 2021-04-07 20:53 | 2021-04-07 23:55 | 1 | 182 | 4428591 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed. Replaced and restored @ 23:55. sh//cod 1
18059 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-08-14 18:13 | 2010-08-14 21:15 | 1 | 182 | 54816-1 | 182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PATROLING NOW-----ON POLE 1148-16 THERES A HOT TAP BURNED OFF VER/HFP L3/HFP
18060 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-06-05 23:16 | 2008-06-06 02:17 | 1 | 181 | 58830-1 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLEG REPAIRED AT XFORMER RELEASED BY CREW 078S11 VER/KEP
18061 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-09-07 10:59 | 2021-09-07 14:00 | 1 | 181 | 4216971 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed on 925-187. Replaced cutout and restored @ 14:00. sh
18062 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-06-04 19:59 | 2018-06-04 23:00 | 1 | 181 | 4556251 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad hot leg in urd service will need portable xfm advised customer to turn off all 240 appliances Released by crew 078H01power temp installed cust rest please close ticket thanks.bt // Abnormal created JEM // KY060418-1036-9287
18063 | Hazard | 3303901 | LESLIE | HYDEN | 2013-07-26 20:54 | 2013-07-26 23:55 | 1 | 181 | 4596421 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CAN 25 KVA 19.9 316-70 COD 1 ISO TF 316-70 VER/ARN IDC XXXX
18064 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-12-12 19:52 | 2009-12-12 22:53 | 1 | 181 | 65671-1 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 7200 XFMR, TALKED TO CREW, PLEASE SEND TO V MULLINS RELEASED BY CREW 078S05/CREW ON SITE/FETR2345/VEM/XFMR CHANGED AND POWER RESTORED 2253/PLEASE CLOSE TICKET/THANKS/VEM
18065 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-06-15 11:57 | 2016-06-15 14:58 | 1 | 181 | 4350231 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CRFEW REQUIRED 15 KVA BAD ROAD/CAN WAIT A FEW DAYS RELEASED BY CREW 078S03 CLOSED PER LLOYD RAYBURN VER/HFP L3/HFP
18066 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-12-01 07:20 | 2008-12-01 10:21 | 1 | 181 | 53403-1 | 181 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3411802//SEC COND BURNED OFF AT XFR,WILL HAVE TO REPLACE ITREPAIRED BURNED OFF SECONDARY CONNECTION AND RESTORED SERVICE,ALL OK AFTERWARDS // VER/TOM L3/TOM IDC XXXX
18067 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-10-15 13:09 | 2014-10-15 16:10 | 1 | 181 | 4633661 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 SEND TO B FRALEY. 3336 RELEASED BY CREW 078H06// COD 1// VER/ ADH
18068 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2017-07-05 11:02 | 2017-07-05 14:03 | 1 | 181 | 4074931 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE BAD C/O ON TRANSFORMER BANK POLE FEEDING GREENUP CO DANCE BUILDING IN ALL BEHIND APPLEGATES, NEED TO REPLACE ALL 3 C/O AT THIS LOC, WILL BE CREW REQ, CAN USE TRUCKS, POLE 1073-7175 RELEASED BY CREW 078S06/CREW ON SITE/FETR 1430/VEM/OPEN XFMR BANK AT 1337/REPAIRS MADE AND ALL CUST RESTORED 1403/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 39831073B17175/ COD 1/ VER/BOW
18069 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-09-16 12:02 | 2009-09-16 15:03 | 1 | 181 | 61587-1 | 181 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | JERRY SMITH REPORTS ONE PHASE IS COMING AND GOING// LOOKS LIKE LOOSE CONNECTION //WILL DETERMINE PROBLEM IF ANYSPLIT-BOLT CONNECTIONS BURNED UP,GOING TO REPLACE THEM.MASSEY IS BRINGING MATERIAL FOR REPAIRS.WILL OPEN XFR BANK AT 1058-230 WHEN READY TO MAKE REPAIRS.NOTE NEW FETRREPLACED BAD CONNECTIONS,RESTORED SERVICE TO CUST,ALL OK AFTERWARDS// COD 1// VER/DBM IDC XXXX
18070 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2018-06-24 09:42 | 2018-06-24 12:43 | 1 | 181 | 4656091 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xform cutout broke on bank 20-5506 open other cutout need big bucket crew to replace 2- cutouts Released by crew 078S04---crew on site--made repairs--pwr restored at 12:43---tbl tkt comp--rmv/ ISO 38830020C45506/ COD 1
18071 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-01-08 13:59 | 2010-01-08 17:00 | 1 | 181 | 50295-1 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED. 25 KVA { 7200 } TRANS. IS BAD. TRUCK ACCESSIBLE. I CALLED TIM AND HE IS SENDING CREW. VER/TOM IDC XXXX
18072 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2012-05-03 15:09 | 2012-05-03 18:10 | 1 | 181 | 4739021 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER CREW ENROUTE. COD-1 ISO TF 37820197000056 VER/HFP L3/HFP IDC XXXX
18073 | Pikeville | 3421001 | BREAKS | CITY | 2019-03-08 16:49 | 2019-03-08 19:50 | 1 | 181 | 4962891 | 181 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | secondary connection failed on 220-38.replaced connections.restored power at 19:36 L3/HFP
18074 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-01-31 18:49 | 2009-01-31 21:50 | 1 | 181 | 53686-1 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT MLR MCC DIS
18075 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-08-20 09:49 | 2016-08-20 12:50 | 1 | 181 | 4817571 | 181 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED A BAD SECONDARY CONNECTION AT THE TRANSFORMER./ ISO 37830239000017/ COD 1/ VER/BOW
18076 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-10-12 18:09 | 2021-10-12 21:10 | 1 | 181 | 4344771 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required no trucks Released by crew 078S03 crew on site FETR 22:30 LRM all pwr restored 22:10please close ticket LRM // cod 1
18077 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-08-30 12:29 | 2013-08-30 15:30 | 1 | 181 | 4801911 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT SERV TO TRY,BAD 10KVA XFMR NEED LINE CREW 4X4 TRUCK TO POLE RELEASED BY CREW 078S05 OLD BARN CUSTOMER SAID OK TO WORK NEXT WEEK VER/KEP IDC XXXX
18078 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2020-12-22 10:59 | 2020-12-22 14:00 | 1 | 181 | 4794531 | 181 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connections @ weatherhead. Turned customers breaker off to make repairs
18079 | Hazard | 3308001 | JACKSON | S.JACKSON | 2016-09-13 13:09 | 2016-09-13 16:10 | 1 | 181 | 4890521 | 181 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN NEUTRAL IN SERVICE . REPAIRED NEUTRAL . ONLY 1 CUET. WITH PART POWER/EMAILED P WYSONG ABOUT POSSIBLE CLAIM/AWD. L3/HFP HFPC MCCNI CCAE CDC85 FEC57 CNT14
18080 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-08-16 14:08 | 2010-08-16 17:09 | 1 | 181 | 56504-1 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 36458944 // PO LE 20-6007 40/ CLASS 7 TELEPHONE POLE BURNT OFF NEED CROSS ARM OR POLE 37.5 TRANS TRUCKS TO POLE SEND TO BILL FRALEY RELEASED BY CREW 078S08 RELEASED BY CREW 078H01//COD 1// VER/DBM IDC XXXX
18081 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-12-07 21:50 | 2008-12-08 00:51 | 1 | 181 | 55274-1 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008701//CREW ON SITE WILL HAVE TO OPEN TRANSFORMER TO REPAIR BAD CLF//POLE #188-146//REPAIRED CLF AND REWORKED GROUNDS ON TRANSFORMER COMPLETE PR TOLLIVER COD 1 VER/KEP IDC XXXX
18082 | Pikeville | 3413402 | GARRETT | LACKEY | 2010-11-01 08:59 | 2010-11-01 12:00 | 1 | 181 | 50567-1 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT OFF AT PRIMARY METERING POLE. COAL COMP HAD CUT TREES AT METERING POLE MAY HAVE GOT TREE INTO SOMETHING. WILL BE MAKING REPAIRES. 40T FUSE OUT. HAVE REPAIRES MADE FUSED UP EVERYTHING OK IDCC PN11 XXXX
18083 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-10-02 12:29 | 2012-10-02 15:30 | 1 | 181 | 4107671 | 181 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | I FOUND NOTHING YOUR METER TO BE BLANK, NO READING ON IT, I OPEN UP 240/480 BANK AND CHECK ALL CONNECTIONS, THEY WERE GOOD, THEN I REFUSE ALL CUTOUT AND CHECK VOLTAGE ON EACH TRANSFORMER WE HAD GOOD VOLT, THE ONLY THING I CAN FIGURE IS THE METERING IS BAD, SEND TO METER ELEC. RELEASED BY CREW 078S06. CHANGED PT AND METERING IS WORKING FINE.// VER/DBM IDCC CCU XXXX
18084 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-02-05 12:29 | 2013-02-05 15:30 | 1 | 181 | 4793201 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER BAD -- BIG BUCKET 15 KVA WITH CUTOUT 7200 RELEASED BY CREW 077S10//COD 3// VER/DBM IDCC PN94 XXXX
18085 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2020-07-30 19:44 | 2020-07-30 22:45 | 1 | 181 | 4258681 | 181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke down on pole 1151-204 and has burnt hole near top close to pole top pins.replaced cutout..pole will need replaced.please send copy to tech and PR to have job written up../ Truck Accessible//SENT TO TECH
18086 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2014-03-11 14:58 | 2014-03-11 16:28 | 2 | 90 | 4468481 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 352-92, REPLACED CUTOUT RESTORED POWER AT 16:28 ***CHANGE ISO POLE*** VER/SEF
18087 | Hazard | 3310502 | HADDIX | CANOE | 2008-09-06 11:40 | 2008-09-06 12:40 | 3 | 60 | 59874-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT CRACKED, WILL HAVE TO CHANGE IT OUT//3310502//CUTOUT CRACKED, WILL HAVE TO CHANGE IT OUT,/// REPLACED C/O POWER RESTORED//VER/CRB IDC XXXX
18088 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-03-30 16:40 | 2014-03-30 19:40 | 1 | 180 | 4543741 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV NEUTRAL PULLED INTO AT SPLICE,WILL REPAIR/////4/3 SERV TO 200A INST ,NEEDS 2B 2/3,NEED 1 MAN,BIG BUCKET,CANT REACH,XS CREEK AND ROAD,ABT 100FT LONG OPENED SER LOOPS. VER/PDP IDCC CNT3 XXXX
18089 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-09-14 13:15 | 2020-09-14 13:45 | 6 | 30 | 4461051 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot leg burndt into on sec. pole 191-D-172, will have to open trans. @191-D-203 to make repairs, will keep track of times. Opened trans. @1315 closed back in @1345, 1 customer is still having problems on his side here, he is getting electrician to come check, everything good on our side.
18090 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-09-18 17:15 | 2014-09-18 17:45 | 6 | 30 | 4509751 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOW SERVICE DROP WILL NEED TO OPEN TRANS. OPEN TRANS. AT17:15 CLOSED AT 17:45 RESAGED SERVICE VER/CRB
18091 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-04-19 08:35 | 2010-04-19 09:35 | 3 | 60 | 64899-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED TAP THAT IS NOT IN USE AND REFUSED LINE COD-1 VER/HFP L3/HFP IDC XXXX
18092 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2014-06-21 14:39 | 2014-06-21 15:15 | 5 | 36 | 4135601 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1147-4632 10T BAD CUTOUT DOOR REPLACED. VER/CRB
18093 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2008-02-05 15:30 | 2008-02-05 17:00 | 2 | 90 | 66564-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3451202// TRANSFORMER LEAKING OIL REPLACED TRANSFORMER 0FF @ 1530 ON AT 1700// IDCC TOF1409 XXXX
18094 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2016-02-11 14:39 | 2016-02-11 15:15 | 5 | 36 | 4689501 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL BROKE, POWER RESTORED.//COD 5
18095 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-04-24 09:15 | 2018-04-24 10:15 | 3 | 60 | 4271711 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | changing out old 25 kva xfmr due to flickering lights// opened xfmr at 09:15//COD 3//changing out old 25 kva xfmr due to flickering lights// opened xfmr at 09:15// work complted, restored at 10:15
18096 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2014-05-28 19:55 | 2014-05-28 20:15 | 9 | 20 | 4946151 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY WAS BURNTED OFF ONE LEG ON TRANSFORMER I HAVE REPAIRS MADED AND POWER IS RRESTORED TO ALL CUST AT 2015, TIME OFF WAS 1955//COD 9// VER/DBM
18097 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-04-20 07:42 | 2014-04-20 09:12 | 2 | 90 | 4619381 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUTOUT DOOR ALL CUST RESTORED @ 0912 //VER/GAH IDCC CNT13, PN35, FEC58 XXXX
18098 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-05-26 17:41 | 2017-05-26 19:11 | 2 | 90 | 4868411 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 14. REPAIRS MADE 38830956000014 VER/AWD
18099 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2018-12-02 01:10 | 2018-12-02 02:40 | 2 | 90 | 4499011 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened transformer on pole 115-161 at 01:10 due to bad cutout. changed bad cutout and arrester. closed transformer back in at 02:40 everything ok.//cod 2// L3/HFP
18100 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-02-03 14:15 | 2017-02-03 15:15 | 3 | 60 | 4356631 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO WIRE DOWN,BUT A REALLY BAD PLACE IN A SERV DROP I NEED TO REPAIR,WILL OPEN XFR TO MAKE REPAIR.MADE REPAIRS////OFF 14:15,ON 15:15/ ISO 37820004000048/ COD 3 ***CODC MD DONE/ VER/BOW L3/HFP XXXHFP
18101 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-12-07 14:11 | 2009-12-07 17:11 | 1 | 180 | 51723-1 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CREW NEEDED; BAD UG CONDUCTOR; LEFT CUSTOMER WITH 120V UNTIL TEMP PWR ARRIVES; DISENGAGED BAD CONDUCTOR IN PEDISTAL BOX AT BASE OF POLE AND MARKED HOUSE SERVICE CONDUCTORS WITH RED TAPE; NOT TRUCK / SEND COPY TO DAN HUFF TO SENDACCESSABLE; APPROX. 140 UG 1/0 WIRE; CANT TELL IF THERE IS CONDUIT BETWEEN PEDISTAL AND METER BASE RELEASED BY CREW 078S12// INSTALLED POWER TEMP SEND COPY TO DAN HUFF TO SEND CONTRACTOR BACK TO FIND BAD UG // VER/DBM IDC XXXX
18102 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-07-10 13:56 | 2020-07-10 14:26 | 6 | 30 | 4141231 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2 primary has 1 strand holding @ pole 148-73/// will have to lift hot tapon pole 172-46 to make repairs///Opened @ 13:56/// Spliced primary and energized @ 14:26 and restored service
18103 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-22 20:35 | 2011-06-22 21:20 | 4 | 45 | 4396741 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | XFMER RISER DAMAGED // BURNT FROM CONTACT WITH XFMER CASE ///OPENED @20:35 MAKING REPAIRS //// REPLACED 1/0 RISER. POWER RESTORED @ 21:20 J. HEMLEPP 078H05 ( 4 CUST. ONLY)// VER/DBM
18104 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2011-03-01 10:00 | 2011-03-01 10:45 | 4 | 45 | 65349-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | STS WR # 38976642 // CREW OPENED RECLOSERS TO ALLOW THEM TO SAFELY REPAIR TIE WIRE THAT IS BROKEN (PHASE FLOATING) /// COD-4 3 TIEWIRES BROKE 1 COND. FLOATING.OPENED UP AT 10:00 VER/HFP L3/HFP IDC XXXX
18105 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-05-07 10:55 | 2012-05-07 13:55 | 1 | 180 | 4754921 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BURNED UP ON POLE 335-197. I AM GOING TO REPLACE CUTOUT. IT STARTED STORMING AND GOT TOO SLICK TO GET TRUCK TO POLE. CUSTOMER SAID WE COULD WAIT UNTIL THURSDAY TO FIX PROBLEM. I MADE OPS ORDER AND PUT OUTAGE # ON IT. POLE 335-42 // OPS # 036147730// VER/DBM IDC XXXX
18106 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-22 21:30 | 2011-01-22 22:15 | 4 | 45 | 63666-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 38537748 /// BAD CURRENT LIMIT FUSE WILL BE CHANGING OUT . I CHANGED CURRENT LIMIT FUSE AND PUT ARRESTER ON LINE SIDE OF FUSE. SEND COPY TO BOB SHURTLEFF PIKEVILLE AND TOM MAMING PIKEVILLE. VER/PDP IDCC TOF2027 FULL POWER ARCING, ESTIMATED TIME OFF XXXX
18107 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2008-12-31 12:30 | 2008-12-31 15:30 | 1 | 180 | 66469-1 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | == LEAD IN TOP OF CUTOUT IS BURNING == NEED TO CHANGE CUTOUT & ARESTOR TOO == NEED LINE CREW == RELEASED BY CREW 077S03 REPLACED CUOUTS AND BRACKETS RESTORED POWER AT 1530 JEFF COMBS//3302701//VER/CRB L3/KEP IDC XXXX
18108 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-02-08 22:00 | 2013-02-08 23:00 | 3 | 60 | 4803381 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. BUSHING IS LOOSE AND LEAKING OIL. CUSTOMERS LIGHTS ARE FLICKERING ON AND OFF. WE NEED TO CHANGE A 15 -12 KV TRANS TO A 25 KVA. I AM CALLING FOR HELP. R WORRIX COMING TO HELP CHANGED TIME OFF TO APPROXIMATE TIME CREW ARRIVED TO REPLACE IT COD-3 ISO TF 37830335B00101 VER/HFP L3/HFP IDC XXXX
18109 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-12-10 20:35 | 2011-12-10 22:05 | 2 | 90 | 4167911 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 397-158, REPLACED CUTOUT RESTORED POWER AT 22:05. ONLY TWO CUSTOMERS AFFECTED. CC 2. VER/SDB IDC XXXX
18110 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-01-11 11:55 | 2022-01-11 14:55 | 1 | 180 | 4335921 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Failed cutout gate. Power restored at 14:55.
18111 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-10-17 12:00 | 2015-10-17 15:00 | 1 | 180 | 4354461 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSF LEAKING OIL NEEDS REPLACED ==== WILL TRY TO REPLACE 10-17- RELEASED BY CREW 077S03 REPLACED TRANSFORMER VOLTAGE OK VER/KEP
18112 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-12-11 19:39 | 2020-12-11 22:39 | 1 | 180 | 4762401 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | crew required need adaphase been fixed once where lowes dug into it 1/0 ug phase on right in base Released by crew 078S03///installed ADD A PHASE cust has full power now///will fix bad UG leg at later date///complete BR
18113 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-05-25 17:05 | 2011-05-25 20:05 | 1 | 180 | 4168861 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3200202--PGD PORTER @1719 RELEASED BY CREW 080S02XFMR FUSE OUT.....WILL RE-FUSE...//XFMR FUSE OUT.....WILL RE-FUSE...//....RE-FUSED XFMR....POWER ON....OLD FUSE JUST BROKE....NO FAULT....JRV.....05/24/11
18114 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2014-06-29 00:40 | 2014-06-29 03:40 | 1 | 180 | 4166641 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED BURNING 1/0 SERVICE IN TWO. ALSO, CONTRACTORS FAILED TO INSTALL XFMR CUTOUT ON THIS 25 KVA DURING STORM RESTORATION A COUPLE OF YEARS AGO. INSTALLED XFMR CUTOUT, REPAIRED SERVICE AND RESTORED @ 3:40. SH VER/ARN
18115 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-08-08 15:30 | 2010-08-08 15:50 | 9 | 20 | H51322-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR 36344935 //SERVICE DROP BURNT DOWN //OPENED TRAN. 15;30 TO 15;50//COD 10// VER/DBM IDC XXXX
18116 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-06-14 16:00 | 2022-06-14 19:00 | 1 | 180 | 4113431 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection failed in a mid span splice at pole 1101-C1-308, Shawn is sending one man and big bucket to help with repairs
18117 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2013-08-29 10:15 | 2013-08-29 11:45 | 2 | 90 | 4717751 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | JOEY TO REPLACE XMER. OPENED TRANSFORMER AT 10:15. CLOSED ATN11:45 VER/SEF IDC XXXX
18118 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-02-07 13:00 | 2022-02-07 16:00 | 1 | 180 | 4454121 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Changed bad4/3 service///Replaced with 75 of 2/3///Everything ok now 123/123/246//Restored @ 16:00///Only 1 customer affected
18119 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-04-01 14:22 | 2014-04-01 14:40 | 10 | 18 | H4550781 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONE CUSTOMER AFFECTED BAD UG SERVICE. CREW ENROUTE TO LOCATE AND REPAIR FAULT. OPENED XFMR 809-796 @ 14:22, REPAIRED 4/0 UG SERVICE AND CLOSED XFMR @ 14:40. SH//COD 1 + 10 IDC DUP TO OPEN TRANSFORMER XXXX
18120 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2014-01-03 13:30 | 2014-01-03 14:30 | 3 | 60 | 4224141 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED TRANSFORMER ON POLE 163-98 AT 13:30 DUE TO DAMAGE. INSTALLED NEW TRANSFORMER AND CLOSED BACK IN AT 14:30 VER/CRB IDCC FEC57 XXXX
18121 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2012-07-03 14:50 | 2012-07-03 15:35 | 4 | 45 | 4274741 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-382 BAD CUTOUTS AND LA TIME OFF 14;50 TO 15;35 ///VER/CRB L/3 CRB
18122 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2016-07-09 13:24 | 2016-07-09 16:24 | 1 | 180 | 4596811 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 1016D139 I CAN MAKE REPAIRS//REPLACED CUTOUT RESTORED POWER AT 16:24/ ISO 38821016D00139/ COD 1/ VER/BOW
18123 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-07-25 00:29 | 2011-07-25 03:29 | 1 | 180 | 4614901 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT, VER/ARN IDC XXXX
18124 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-01-12 17:45 | 2018-01-12 20:45 | 1 | 180 | 4737971 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced and restored @ 20:45. sh
18125 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-05-27 09:27 | 2009-05-27 09:57 | 6 | 30 | 55547-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE ON POLE 38830206C02034, NO VISIBLE HAZARDSLINE FUSE ON POLE 38830206C02034, 40T FUSE AND CUTOUT DOOR BROKE, REPLACED FUSE AND DOOR//VER/CRB
18126 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2015-05-29 18:15 | 2015-05-29 19:00 | 4 | 45 | 4481501 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SECONDARY @ XFM //// WILL HAVE TO OPEN XFM TO MAKE REPAIRS/// OPENED XFM @ 18:15 TO MAKE REPAIRS//////// MADE REPAIRS CLOSED XFM IN @ 19:00 AND RESTORED SERVICE/ ISO 37830022000060/ COD 4/ VER/BOW
18127 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2010-10-26 19:00 | 2010-10-26 22:00 | 1 | 180 | 64925-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURN POLE 215-77, FUSE POLE OPENED 215-9029 @ 19:00. RELEASED BY CREW 078H12 IDCC CNT2, TOF1814 XXXX
18128 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-06-17 09:25 | 2009-06-17 09:55 | 6 | 30 | 51922-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3411802// CUTOUT 19.9 NEED TO REPLACE. SEND THIS TICKET TO TIM HALL HE WILL GIVE TO A CREW WITH A BIG BUCKET TRUCK RELEASED BY CREW 074S05 SDRAY ONSITE CHANGED C/O&L/A AND BRACKET ISO 37820074000038 COD-6 L3/HFP IDCC IDC CHANGED TIME OFF FROM 0502 XXXX
18129 | Pikeville | 3413402 | GARRETT | LACKEY | 2022-02-20 16:00 | 2022-02-20 17:30 | 2 | 90 | 4520901 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XCO on pole 41-B-78 failed, made repairs and restored customers
18130 | Whitesburg | 3314401 | MAYKING | ERMINE | 2016-10-25 11:48 | 2016-10-25 13:18 | 2 | 90 | 4052061 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2 SERVICE DROP BURNT DOWN SERVING DRS OFFICE, WILL REPLACE WITH 1/0 SERVICE ..RESTORED POWER AT 13:18.. VER/AWD
18131 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-05-16 13:30 | 2018-05-16 16:30 | 1 | 180 | 4361051 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o-replaced-ds051618/ ISO 38830211B40313/ COD 1
18132 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2011-02-25 14:00 | 2011-02-25 15:30 | 2 | 90 | 62537-1 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER. REPLACED 25KVA WITH 50KVA//COD 2// VER/DBM IDC XXXX
18133 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-11-08 13:17 | 2019-11-08 14:47 | 2 | 90 | 4012011 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout going bad. changed cutout & arrestor. pls close. tre
18134 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2011-06-23 14:30 | 2011-06-23 15:00 | 6 | 30 | 4400261 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 21-3526 HOT TAP BROKE OFF CUTOUT REPAIRED // COD-6 38830021B43526 VER/HFP L3/HFP IDC XXXX
18135 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-07-31 19:30 | 2011-07-31 22:30 | 1 | 180 | 4648781 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NUETRAL LEG BURNDT UP ON URD SERVICE, CONTACTED DUTY SUPERVISOR , OPENED TRANS. AT POLE 426-441 AT 19:30. INSTALLED OVERHEAD TEMP., CLOSED BACK IN AT 22:30 IDCC TOF1826 XXXX
18136 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2013-11-07 08:40 | 2013-11-07 09:40 | 3 | 60 | 4018071 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER FAILED AND BLEW XFMR FUSE. CLEARED AND RESTORED @ 9:40. SH VER/CRB
18137 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-15 16:15 | 2011-01-15 17:00 | 4 | 45 | 61613-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | I OPENED 1.6T FUSE DUE TO BAD CURRENT LIMIT FUSE. I WILL BE MAKING REPAIRS.I REPLACED CURRENT LIMIT FUSE AND MADE THE ARRESTER UP ON THE LINE SIDE OF THE CURRENT LIMIT FUSE. ALL OF THE ARRESTERS ARE MADE UP ON THE LOAD SIDE OF THE CURRENT LIMIT FUSE. ON THE BEAVER CREEK LIGON CKT. THESE SEEM TO BE GOING BAD EVERYOTHER DAY. CUST WERE CONCERENED ABOUT REAL LOW VOLTAGE ON THIS BEFORE CURRENT FUSE BURNT INTO. SEND COPY OF THIS TO PEGGY WYSONG BOB SHURTLEFF AND TOM MAMING//COD 4// VER/DBM IDCC TOF1505 XXXX
18138 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-03-27 09:30 | 2018-03-27 10:00 | 6 | 30 | 4125731 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cod 6 iso 38830069C35109 // bad 12kv c/o,open xfmer @ 69-5109, @ 09:30. bad 12kv c/o, restored 10:00
18139 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-07-02 09:15 | 2017-07-02 10:15 | 3 | 60 | 4066801 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-293 BAD CUTOUT CHGED/ ISO 38830091D00293/ COD 3/ VER/BOW
18140 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-06-26 16:15 | 2009-06-26 19:15 | 1 | 180 | 63372-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401703// ACTUAL ISO POLE IS 266-256 ONLY ONE CUSTOMER OUTAGED.//COD 37820266000224//COD 1// VER/DBM
18141 | Whitesburg | 3401301 | FLEMING | NEON | 2014-01-14 15:00 | 2014-01-14 18:00 | 1 | 180 | 4281271 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | POLE 37830355D40461 HAS CROSSARMS BURNT OFF. REPLACED CROSSARMS AND CUTOUTS AND RESTORED POWER, ONLY 1 CUST OFF COD-1 ISO PO @ 37830355D40461 VER/HFP L3/HFP
18142 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-05-02 12:45 | 2015-05-02 14:15 | 2 | 90 | 4383951 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN LIGHTING ARRESTER ON POLE38830259000079 , CUT IN CLEAR NO TRUCKS TO POLE.//MADE AED// VER/CRB
18143 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-11-08 13:18 | 2022-11-08 13:38 | 9 | 20 | 4114091 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout on pole 37830031000041 broke (COD 1) OPENING SB ON POLE 37830031000023 ( COD 8) TO MAKE REPAIRS OFF @ 1318 ON @ 1338
18144 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-09-22 12:12 | 2013-09-22 12:57 | 4 | 45 | 4877561 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE VER/CRB L/3 CRB
18145 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-07-23 14:15 | 2013-07-23 15:45 | 2 | 90 | 4581781 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 15KVA 7200 TRANSFORMER, CUTOUT AND ARRESTOR AND SOMETHING TO PUT SMALL AMOUNT OF DIRT TO CLEAN UP OIL RELEASED BY CREW 077S05 REPLACED TRANSFORMER AND CLEANED UP SMALL OIL SPILL//COD 2// VER/DBM IDC XXXX
18146 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-07-12 10:15 | 2010-07-12 11:45 | 2 | 90 | 65338-1 | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR IS BLOWN UP ALSO XFR FUSE IS OUT,WILL REPAIR////////MADE REPAIRS AND RESTORED.ALL OK AFTERWARDS VER/HFP L3/HFP IDC XXXX
18147 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2012-03-14 15:12 | 2012-03-14 15:30 | 10 | 18 | H4578681A | 180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PART OF 4578681//OPENED OTHER TWO PHASES ON SECTIONALLIZER POLE @ 1512//COD +10//, TIM SMITH MADE REPAIRS ON SWITCH POLE 539-77 DURING THIS TIME//RESTORED LAST 28 @ 1530// VER/DBM IDCC TOF1325 XXXX
18148 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-11-03 16:55 | 2012-11-03 18:25 | 2 | 90 | 4351091 | 180 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL WAS MADE UP ON 6 A PRIMARY NEUTRAL AND BURNED IT DOWN. I MADE REPAIR AND VOLTAGE IS GOOD NOW. COD-2 ISO TF 37820033A00049 VER/HFP L3/HFP IDC XXXX
18149 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-11-30 13:56 | 2009-11-30 16:55 | 1 | 179 | 51781-1 | 179 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR FAILED AT SERVICE LOOPS// VER/DBM IDC XXXX
18150 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-08-01 17:31 | 2021-08-01 20:30 | 1 | 179 | 4991251 | 179 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad 4/0 hot leg on ug service Released by crew 078S12 crew on site Power temp installed
18151 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-10-24 11:51 | 2011-10-24 14:50 | 1 | 179 | 4014911 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ///VER/CRB IDCC PN113 XXXX
18152 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-06-05 17:46 | 2008-06-05 20:45 | 1 | 179 | 58540-1 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 199-120/240. TRANSFORMER HAS 1 LEG OUT.....DAH//3401702//VER/CRB
18153 | Whitesburg | 3401301 | FLEMING | NEON | 2009-12-08 18:54 | 2009-12-08 21:53 | 1 | 179 | 58027-1 | 179 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER CLAIMS TV IS BURNT UP//SAYS HE HAS DAMAGES//REPLACING CONNECTION ON WEATHER HEAD // CONNECTION FAILED AT THE WEATHERHEAD // SENT TO PEGGY WYSONG //// VER/DBM IDC XXXX
18154 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-07-21 03:52 | 2010-07-21 06:51 | 1 | 179 | 54651-1 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER GOT CREW COMMING TO CHANGE//COD 1// VER/DBM IDC XXXX
18155 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2022-05-21 17:13 | 2022-05-21 20:12 | 1 | 179 | 4921891 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1123-635 bad 37.5 xfmer. 7200 120-240. trk ok. to levi howard Released by crew 078S07/ changed cutout & Xfmr on 1123-635 in @ 2012/ please close ticket/ MLH
18156 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-04-29 12:16 | 2011-04-29 15:15 | 1 | 179 | 52307-1 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR# 39761367 //SER BURNT INTO//SPLICED SER ALL BACK TO NORMAL// VER/DBM
18157 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-07-10 00:26 | 2010-07-10 03:25 | 1 | 179 | 64583-1 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED ONE MAN TO HELP OPENED LINE FUSE AT 250 CLOSED IT AT 325 IDC XXXX
18158 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-11-07 07:27 | 2013-11-07 10:26 | 1 | 179 | 4017761 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT. WAITING ON CREW VER/CRB
18159 | Hazard | 3311103 | STINNETT | WENDOVER | 2016-07-22 15:07 | 2016-07-22 18:06 | 1 | 179 | 4667981 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT , VER/AWD
18160 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-08-15 17:31 | 2010-08-15 20:30 | 1 | 179 | 56045-1 | 179 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | STS WR # 36445048 // RICHARD BLEVINS @ 606-232-6009 BAD CUTOUT DOOR NU. BURNT INTO COD-1 VER/HFP L3/HFP
18161 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-05-04 09:34 | 2018-05-04 12:33 | 1 | 179 | 4305431 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT // CALLING FOR ASSISTANCE TO REPLACE IT // COD-1 ISO TF 37830220000102got broke cutout, need new cutout and arrestor for 19.9 kv
18162 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-12-12 04:46 | 2014-12-12 07:45 | 1 | 179 | 4855651 | 179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TREE LIMBS IN SECONDARY OUT FROM POLE 851-159 CAUSED ONE HOT LEG AND NEUTRAL TO BURN OPEN///MADE REPAIRS/// THIS ONLY EFFECTED 1 CUST.///GOT CUST. BACK ON @ 07:45///COMPLETE BR// VER/ ADH
18163 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-05-14 09:41 | 2012-05-14 12:40 | 1 | 179 | 4790741 | 179 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION AT XFMR. CLEANED CONNECTIONS AND TIGHTENED LUGS, ALL POWER RESTORED VER/KEP IDC XXXX
18164 | Hazard | 3309302 | VICCO | JEFF | 2019-01-10 23:00 | 2019-01-11 01:58 | 1 | 178 | 4657861 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Had red to red go bad burning netural into and one hot leg
18165 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-02-10 17:58 | 2018-02-10 19:27 | 2 | 89 | 4824341 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 214-227...made repairs..restored
18166 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-01-24 10:53 | 2020-01-24 13:18 | 2 | 145 | 4334931 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot leg burndt into on customers service drop and burndt neutral into also, will have to open trans. @312-187 to make repairs, will keep track of times. Opened trans. @1245, made repairs and closed back in @1318.
18167 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-05-02 15:52 | 2019-05-02 18:50 | 1 | 178 | 4200911 | 178 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Bad neutral in service drop, repaired
18168 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-02-13 18:32 | 2020-02-13 21:30 | 1 | 178 | 4404301 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout door burnt into///Replaced cutout door and restored service @ 21:30/ ISO 37820147D00074/ COD 1
18169 | Whitesburg | 3312902 | JENKINS | JENKINS | 2009-05-16 10:21 | 2009-05-16 11:50 | 2 | 89 | 58416-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT I AM GOING TO REPLCE IT//3312902//VER/CRB IDC XXXX
18170 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-01-24 17:56 | 2009-01-24 19:25 | 2 | 89 | 59652-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401001// CUTOUT FAILED. THE DOOR WAS BURNED UP. I REPLACED THE DOOR.//COD 2// VER/DBM L3/KEP
18171 | Paintsville | 3401102 | FALCON | SALYERSVI | 2021-04-16 06:18 | 2021-04-16 09:16 | 1 | 178 | 4455401 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Dispatched in accordance with KYPCo Late Night Callout Guidelines.//replaced connection at the weather head //cod 1
18172 | Hazard | 3303901 | LESLIE | HYDEN | 2013-07-26 12:02 | 2013-07-26 15:00 | 1 | 178 | 4595121 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR ON POLE 413A-401. ONLY ONE CUST. ON THIS XFMR , POWER BACK ON @ 15:00//COD 2// VER/DBM IDCC PN8, CNT2 XXXX
18173 | Pikeville | 3402003 | KEYSER | MULLINS | 2017-11-28 01:13 | 2017-11-28 02:42 | 2 | 89 | 4605841 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called customer// states neighbor and streetlights are out , meter is blank//. Trans fuse melted out @1127-A-258, refused @0242.//cod 2
18174 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-11-19 07:40 | 2011-11-19 10:38 | 1 | 178 | 4092351 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PRIMARY BUSHING LOOSE, BUSHING LOOKS BLACK MAY HAVE TO CHANGE CAN. RELEASED BY CREW 078S11 /// VER/CRB IDCC PN NULL XXXX
18175 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-09-22 07:57 | 2018-09-22 10:55 | 1 | 178 | 4140541 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Released by crew 077S02 xfmr fuse is out, power restored, looked like fuse broke/ ISO 37830246D00101 / COD1 L3/HFP
18176 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-03-03 00:25 | 2010-03-03 03:23 | 1 | 178 | 62401-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN AND CAUGHT POLE 50-76 ON FIRE. I OPENED TRANS. AND LIFTED HOTTAP AT 00:25. WE WILL HAVE TO OPEN ALL 3 LINE FUSES ON POLE 50-29 WHEN CREW GETS HERE TO LOWER CROSSARM AND NEW CUTOUT. THERE IS JUST 1 CUST. OUT FOR NOW. RELEASED BY CREW 074S01 VER/PDP IDCC PN177 XXXX
18177 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-12-07 15:42 | 2019-12-07 18:40 | 1 | 178 | 4133861 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke--B Tackett headed to--ds120719 Released by crew 078S01,repairs made all cust restored @ 1840 please close ticket thanks.bt
18178 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-07-28 09:57 | 2010-07-28 12:55 | 1 | 178 | 58378-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFOMER OUTAGE DUE TO BAD CUTOUT DOOR. REPLACED DOOR FUSED UP 6T EVERYTHING OK. COD-1 VER/HFP L3/HFP IDC XXXX
18179 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-01-06 12:02 | 2021-01-06 15:00 | 1 | 178 | 4852021 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required connections bad
18180 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-12-25 14:21 | 2009-12-25 15:50 | 2 | 89 | 55390-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CUTOUT /ORIGINAL WR#33198345 /
18181 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-04-25 10:31 | 2021-04-25 12:00 | 2 | 89 | 4478281 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT///////////REPLACED BROKEN CUTOUT&RESTORED POWER,ALL OK AFTERWARDS
18182 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-02-02 14:16 | 2011-02-02 17:14 | 1 | 178 | 53510-1 | 178 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE END REPLACED CONNECTION... VER/KEP IDC XXXX
18183 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-08-06 18:27 | 2022-08-06 21:25 | 1 | 178 | 4695721 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad connection on service ,, all power restored @21:25 p.hicks
18184 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-07-01 10:31 | 2021-07-01 12:00 | 2 | 89 | 4834401 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Burnt up meter, changed out
18185 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-03-04 07:07 | 2015-03-04 10:05 | 1 | 178 | 4096621 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE IS OUT. WILL REFUSE. XFMR IS BAD WILL NEED TO BE CHANGED.CAN BE RELOCATED TO POLE#38831077B00106. TO BE TRUCK ACCESSABLE.HAVE CREW ON THE WAY WITH XFMR VER/CRB L3/DKGXXXX
18186 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-06-28 18:31 | 2010-06-28 20:00 | 2 | 89 | 59690-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD ON POLE #38831151D00663 VER/ARN
18187 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-11-18 05:11 | 2013-11-18 06:40 | 2 | 89 | 4050691 | 178 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, CLAMP BURNT OFF ON XFMR BANK AT POLE 424-289, MADE REPAIRS RESTORED POWER AT 06:40//COD 2//ISO// VER/DBM
18188 | Pikeville | 3407101 | TOPMOST | DEMA | 2012-05-16 10:34 | 2012-05-16 13:32 | 1 | 178 | 4800501 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLEW ON TRANSFORMER BUT GATE DID NOT OPEN , GATE CARRIED CURRENT AND WAS BURNED . REFUSED AND REPLACED CUTOUT GATE , ALL WORK COMPLETE / GXJ //COD 1// VER/DBM IDC XXXX
18189 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2022-04-07 15:16 | 2022-04-07 16:45 | 2 | 89 | 4737821 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout on pole 492-29. Replaced cutout. Power restored at 16:45
18190 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2015-05-03 10:52 | 2015-05-03 13:50 | 1 | 178 | 4385431 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED 100 FT SPAN 2/3 SECONDARY FROM POLE 38831146000077 TO POLE 1146-277, ALL WORK COMPLETE / GXJ VER/CRB
18191 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-03-05 17:26 | 2009-03-05 18:55 | 2 | 89 | 55450-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP COD-2 WR # 28807591 // XFMR FUSE BLOWN, FUSE PULLED INTO L3/HFP IDCC CCO XXXX
18192 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-02-24 20:11 | 2010-02-24 21:40 | 2 | 89 | 60705-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT, POWER RESTORED VER/KEP L3/KEP IDC XXXX
18193 | Pikeville | 3401001 | ELWOOD | DORTON | 2012-06-14 21:07 | 2012-06-15 00:05 | 1 | 178 | 4916941 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOWN HAS BURNT UP ON POLE 37830261000098 /// GOING TO REPLACE /// POWER RESTORED @ 00:05 IDC XXXX
18194 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-10-29 09:32 | 2012-10-29 12:30 | 1 | 178 | 4181531 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830248A00788, CREW AND FLAGGERS ENROUTE. OPENED FUSE ON POLE 37830248A00788 AT 1140(11 CUSTOMERS) TO REPLACE CUTOUTS ON POLE 37830248A00788BAD CUTOUT ON POLE 37830248A00788, CREW AND FLAGGERS ENROUTE.--- OPENED LINE ON POLE 37830248A00788 AT 11:40, CLOSED AT 12:30 SEE DUP H4181531 FOR 10 CUST VER/HFP L3/HFP IDCC FP766 XXXX
18195 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-10-28 01:17 | 2009-10-28 04:15 | 1 | 178 | 59862-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY ONE CUSTOMER ON THIS XFMR. XFMR CUTOUT BROKE. REPLACED. SH //VER/GAH IDC XXXX
18196 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-20 08:37 | 2009-06-20 11:35 | 1 | 178 | 61587-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN-----CHANGED BAD CUTOUT
18197 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-02-06 18:47 | 2012-02-06 21:45 | 1 | 178 | 4324291 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LEADS BURNT AT TRANSFORMER, SERVICE NEUTRAL BROKEN IN ONE SERVICE.--- REMADE CONNECTIONS AT TRANSFORMER, REPLACED SERVICE.// VER/DBM IDC XXXX
18198 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-11-03 07:57 | 2014-11-03 09:26 | 2 | 89 | 4694911 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RESTORED @ 9:26. SH/ ISO 38830882A00425/ COD 2// VER/BOW
18199 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-03-31 20:36 | 2020-03-31 22:05 | 2 | 89 | 4550501 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse melted out refusing
18200 | Hazard | 3303902 | LESLIE | WOOTON | 2018-04-08 16:41 | 2018-04-08 18:10 | 2 | 89 | 4201701 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse was rotten and broke
18201 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-10-25 17:31 | 2017-10-25 19:00 | 2 | 89 | 4498461 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER NO DISPLAY ON METER//FUSE BROKE/ ISO 37830222C00242/ COD 2/ VER/BOW L3/HFP XXXHFP
18202 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-01-06 10:46 | 2022-01-06 12:15 | 2 | 89 | 4311551 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6 T FUSE BROKE..REPLACING...
18203 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-08-20 16:12 | 2012-08-20 19:10 | 1 | 178 | 4956031 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKEN ON POLE 37820146000161  GOING TO REPLACE  POWER RESTORED @ 19:10 VER/KEP IDC XXXX
18204 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-02-07 06:12 | 2022-02-07 09:10 | 1 | 178 | 4452021 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection at the XFMR, power restored at 09:10.
18205 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2010-03-02 12:27 | 2010-03-02 15:25 | 1 | 178 | 62209-1 | 178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAD SERVE ENDS ON SECODARY POLE I REPLACED THE SERVENDS POWER WAS GOOD 120/120/240 WE DO HAVE A SMALL XFMR ON THIS POLE 37820148000132 NEED TO SEND A NOTE TO RON RYE TO HAVE CUT OUT AND ARRESTOR, AND TRANSFORMER CHANGED TO 25 KVA TRUCK APPROACH. TIM MCCOY RELEASED BY CREW 074H10 VER/KEP L3/KEP IDC XXXX
18206 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-12-19 14:36 | 2008-12-19 15:35 | 3 | 59 | H60361-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401101// OPENED PRIMARY TAP THAT FEEDS XFMRS 903-39, 903-38 AND FAULT POLE 44 AT 14:36 TO ISOLATE BROKEN CUTOUT. REPLACED CUTOUT AND RESTORED AT 15:35. SH VER/KEP L3/KEP IDCC PN44 XXXX
18207 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-04-10 22:26 | 2008-04-11 01:23 | 1 | 177 | 65941-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308002 BROKE CUTOUT ON UNDERGROUND POLE VER/JHM IDC XXXX
18208 | Pikeville | 3410602 | E.PRESTON | LANCER | 2018-04-03 13:25 | 2018-04-03 16:22 | 1 | 177 | 4168971 | 177 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 277 / 480 wye service , one leg open due to loose connection . replaced connection / ALL WORK COMPLETE / GXJ
18209 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-05-31 17:49 | 2013-05-31 18:48 | 3 | 59 | 4203631 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK ADDED 1 CUST FOR MISMAPPED VER/KEP IDC XXXX
18210 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-11-10 12:01 | 2008-11-10 13:00 | 3 | 59 | 63644-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601// E MAIL TO MARTIN TO HAVE TECH CHECK POLE FOR REPLACEMENT--TOP OF POLE IS BAD--REPLACED CUTOUT//COD 3//EMAILED TO S MARTIN DBM// VER/DBM IDC XXXX
18211 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2013-06-03 15:20 | 2013-06-03 18:17 | 1 | 177 | 4214101 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER HAS BAD SECONDARY BUSHING, WILL REPLACE . OPENED TRANSFORMER AT 15:20 ..REPLACED TRANSFORMER AND CLOSED AT 18:17, ALL WORK COMPLETE / GXJ ///VER/CRB L/3 CRB
18212 | Hazard | 3309302 | VICCO | JEFF | 2009-09-29 18:41 | 2009-09-29 19:40 | 3 | 59 | 56780-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED DOOR ON XFMR FUSE ON POLE 37830347D00114 // 4 COD
18213 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-12-24 13:03 | 2015-12-24 16:00 | 1 | 177 | 4557261 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS////XTREMELY LONG 4/3 DROP BURNED INTO.COMES OFF MTN TO HSE.NEED 1 MAN TO HELP CHANGE TO 2/3///////MADE NECESSARY REPAIRS,ALL OK AFTERWARDS VER/CRB
18214 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-02-23 21:00 | 2015-02-23 23:57 | 1 | 177 | 4076601 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP CONNECTIONS BAD ON POLE,SER DROP BURN INTO .REPAIRED POWER RESTORED VER/ARN L3/HFP HFPC CCO CNT2
18215 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-07-21 03:31 | 2018-07-21 06:28 | 1 | 177 | 4818281 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced c phase cutout,,,customer restored complete
18216 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2010-06-26 20:38 | 2010-06-26 23:35 | 1 | 177 | 57924-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 35746022 / C PHASE FUSE OUT ON PRIMARY METERING POLE 38830070A31096- CALLED CREW RELEASED BY CREW 078S07 VER/LDA IDC XXXX
18217 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2019-02-01 05:57 | 2019-02-01 08:54 | 1 | 177 | 4745531 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK FOR PROBLEMS//////LINEF CUTOUT BROKEN WHICH ALSO TOOK XFR POWER OUT.REPLACED BOTH PORCELINE-TYPE CUTOUTS SINCE I WAS THERE.RESTORED POWER // only a DD light fed from line fuse no outage // Xfer COD 1
18218 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2017-07-26 14:28 | 2017-07-26 17:25 | 1 | 177 | 4182271 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED OFF AT CUSTOMERS POLE. REPAIRED AND RESTORED POWER AT 1725/ ISO 37830494000147/ COD 1/ VER/BOW
18219 | Hazard | 3308001 | JACKSON | S.JACKSON | 2017-11-20 08:36 | 2017-11-20 11:33 | 1 | 177 | 4587931 | 177 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | one cutout is broke on pole 108-114, calling for help//one cutout is broke on pole 108-114, calling for help, please send to Jeff Combs Released by crew 077S02 replaced cutouts and restored power at 1133
18220 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-10-04 19:00 | 2008-10-04 19:59 | 3 | 59 | 53383-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN, REFUSED POWER RESTORED. FUSE TAIL BROKE//3300601//VER/CRB IDC XXXX
18221 | Hazard | 3303903 | LESLIE | HALSFORK | 2021-01-29 18:58 | 2021-01-29 21:55 | 1 | 177 | 4919231 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt into. replaced service
18222 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-05-12 11:33 | 2017-05-12 14:30 | 1 | 177 | 4786481 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 2 7.2KV CUTOUTS AND REFUSED, ALL WORK COMPLETE / GXJ 38831077D00637 VER/AWD
18223 | Hazard | 3303902 | LESLIE | WOOTON | 2012-07-16 18:28 | 2012-07-16 21:25 | 1 | 177 | 4742821 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ARM BRACES BROKE ON POLE 37830487000013, CAUSING XFMR FUSE TO BLOW. ALSO HAVE LINE FUSE ON POLE 37830487000062 BLOWN THAT SERVES A GAS WELL . REMOVED ARM AND BRACES, PUT NEW BRKT, CUTOUT AND ARRESTOR. POWER RESTORED. VER/KEP
18224 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-01-09 06:15 | 2018-01-09 09:12 | 1 | 177 | 4723241 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse link broke. Restored @ 9:12. sh COD-1 ISO TF 38830782000036
18225 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2019-01-05 19:56 | 2019-01-05 20:55 | 3 | 59 | 4634361 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST TWICE//VOICEMAIL/broke fuse
18226 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-11-24 14:03 | 2008-11-24 17:00 | 1 | 177 | 51640-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANS. RELEASED BY CREW 078S08//3001203// STS W/R 27422354// HAVING TROUBLE GETTING NEW XFR ON BOLTS POLE LEANING//3001203 //VER/CRB IDC XXXX
18227 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-01-01 12:31 | 2015-01-01 13:30 | 3 | 59 | 4896701 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 38830115D00192 8T TRANS FUSE BROKE REPLACED FUSE VER/CRB VER/DKG L3/DKGXXXX
18228 | Hazard | 3309301 | VICCO | REDFOX | 2009-04-11 12:41 | 2009-04-11 15:38 | 1 | 177 | 51486-1 | 177 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S04 ...SPLICE IN SERVICE FAILED, MADE REPAIRS RESTORED POWER AT 15:38/VER/CRB IDC XXXX
18229 | Hazard | 3303902 | LESLIE | WOOTON | 2013-02-02 18:25 | 2013-02-02 21:22 | 1 | 177 | 4787191 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE WIRE BURN,T INTO LAYING IN CREEK WILL OPEN XFMR AND SPLICE SERVICE AND TRY TO GET IT ACROSS CRK//// XFMR OPENED 19:54 CLOSED 21:22. RE-PULLED SERVICE POWER RESTORED. COD-6 VER/KEP IDC XXXX
18230 | Pikeville | 3408101 | SALISBURY | PRINTER | 2011-01-07 18:56 | 2011-01-07 19:55 | 3 | 59 | 59644-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE. PUT NEW 6T FUSE IN EVERYTHING OK//COD 3// VER/DBM IDC XXXX
18231 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2013-09-15 08:16 | 2013-09-15 09:15 | 3 | 59 | 4855521 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING CUTOUT DOOR VER/SEF
18232 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-02-05 09:18 | 2010-02-05 12:15 | 1 | 177 | 63295-1 | 177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 VOLT CUTOUT BAD WILL REQUIRES TWO MEN SEND TO HICKMAN CREW AS PER GLEN C. RELEASED BY CREW 077S04 POWER RESTORED RR//VER/CRB IDC XXXX
18233 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-12-25 16:09 | 2017-12-25 17:37 | 2 | 88 | 4677901 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfr fuse broke complete
18234 | Whitesburg | 3409503 | BURDINE | JENKINS | 2015-08-30 00:07 | 2015-08-30 00:51 | 4 | 44 | 4182991 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEE PO#4182921/FAILED CUTOUT POLE#358-D-91/ OPENED FUSE POLE#382-A3-162 TO REPLACE/ VER/KEP
18235 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2012-05-12 19:17 | 2012-05-12 20:45 | 2 | 88 | 4784901 | 176 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TENSION SLEAVE PULLED OUT IN SECONDARY 1/0 CAUSING BRIGHT AND DIM LIGHTS. CUSTOMER SAID SMOKE CAME OUT OF HIS TV. SEND TO DAMAGE CLAIMS DEPT. JUST TO GIVE HER HEADS UP. RESPLICED POWER RESTORED. IDC XXXX
18236 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-04-28 13:26 | 2022-04-28 14:10 | 4 | 44 | 4812171 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Neutral pulled out of a splice at pole 199-B-27 and is hanging very close to open wire secondary. The XFMR on 199-B-27 off at 13:36 and back on at 14:10.
18237 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-02-26 19:16 | 2014-02-26 20:00 | 4 | 44 | 4436641 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE WAS BAD HAVE REPLACED AND POWER IS RESTORED AT THIS LOC AT 2000 VER/CRB
18238 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-01-18 20:32 | 2012-01-18 22:00 | 2 | 88 | 4274271 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN.. REFUSED TRANSFORMER//COD 2// VER/DBM IDC XXXX
18239 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-10-27 18:16 | 2009-10-27 19:00 | 4 | 44 | 59084-1 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD FUSE LINK. IDC XXXX
18240 | Hazard | 3309003 | JEFF | VIPER | 2022-05-22 11:59 | 2022-05-22 14:55 | 1 | 176 | 4926261 | 176 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Cleaned up meter base and replaced conn.
18241 | South Williamson | 3411401 | DEWEY | INEZ | 2011-06-01 13:02 | 2011-06-01 14:30 | 2 | 88 | 4219041 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR MELTED OUT ON POLE 697-7//CHANGED OUT DOOR//RESTORED AT 14:30//COMPLETE//EM COD-2 ISO TF 38820697B00097 VER/HFP L3/HFP IDC XXXX
18242 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2015-12-03 09:59 | 2015-12-03 12:55 | 1 | 176 | 4506851 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 20-5114 BAD 15KVA TRANS. TRUCK TO POLE BEHIND GOLDEN CORRAL REST. NO ONE OUT OF POWER FEEDING OUTSIDE LIGHTS RELEASED BY CREW 078S08 COMPLETE PLEASE CLOSE TICKET VER/CRB
18243 | Hazard | 3302704 | HAZARD | KENMONT | 2010-12-12 14:39 | 2010-12-12 17:35 | 1 | 176 | 65628-1 | 176 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 4/3 SERV BURN INTO AT TOP OF TRL POLE AND SPLICE == REPLACED SERV WITH 2/3 SERV == POWER OK AT THIS TIME VER/HFP L3/HFP IDC XXXX
18244 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-07-28 10:52 | 2016-07-28 13:48 | 1 | 176 | 4698311 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA.NEED CREW.15 KVA XFMR.TRUCK ACCESS. RELEASED BY CREW 076S01// REPAIRS COMPLETE, RESTORED AT 13:48 VER/AWD
18245 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-07-16 18:02 | 2020-07-16 19:30 | 2 | 88 | 4172191 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
18246 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-01-20 14:42 | 2011-01-20 16:10 | 2 | 88 | 63064-1 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE DOOR BURNT OUT ON POLE 697-28//CHANGING DOOR//RESTORED AT 16:10//COMPLETE//EM // COD 2// VER/DBM IDC XXXX
18247 | South Williamson | 3411401 | DEWEY | INEZ | 2020-03-19 13:30 | 2020-03-19 14:58 | 2 | 88 | 4492461 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 38830743D00078//repairs made//restored at14:58
18248 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-08-27 14:42 | 2012-08-27 16:10 | 2 | 88 | 4977041 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 901-7044, LINE FUSE WAS NOT OPENED UP, JUST TRANSFORMER FUSE, HAVE REPAIRS MADE AND POWER IS RESTORED AT THIS LOC AT 1610 COD-2 ISO TF 39830901D37044 VER/HFP L3/HFP IDC XXXX
18249 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-02-11 21:22 | 2008-02-11 22:50 | 2 | 88 | 60533-1 | 176 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3310501// CONNECTION WENT BAD ON TRANSF POLE == REPAIRED VER/ARN IDC XXXX
18250 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-01-30 06:54 | 2012-01-30 09:50 | 1 | 176 | 4304411 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED K BROWN TO ASSIST VER/KEP IDC XXXX
18251 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2022-12-24 03:01 | 2022-12-24 04:29 | 2 | 88 | 4338211 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | refused and back in at 4:29. complete
18252 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2013-07-14 21:56 | 2013-07-14 22:40 | 4 | 44 | 4523391 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE VER/PDP IDCC PN278 XXXX
18253 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-10-25 08:22 | 2012-10-25 09:50 | 2 | 88 | 4170131 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK APPEARS TO HAVE BROKEN ON 856-15. RESTORED @ 9:50. SH VER/KEP IDC XXXX
18254 | Hazard | 3307301 | BULAN | ARY-HEINE | 2015-09-29 20:12 | 2015-09-29 21:40 | 2 | 88 | 4291811 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 154-123 , BAD CUTOUT ON POLE 154-130 , REPLACED CUTOUT . POLE WILL NEED CHANGED OUT TOMORROW , PUT POLE FIRE OUT SHOULD BE OK FOR TONIGHT . WILL NEED 45 POLE, FIBERGLASS TBRACKET & ARRESTER . ..POLE IS DEAD END XFMR POLE . CAN WORK POLE WITH TRUCKS . CLOSED LINE FUSE BACK @ 21:40 ./ ISO.. 37830154000123/ COD 2..CREW ON SITE, OPEN 154-123 @ 09:51 HRS..CLOSED BACK IN @ 11:53 HRS..ALL POWER RESTORED AND POLE CHANGED OUT.P.HICKS RELEASED BY CREW 077H09 VER/CRB
18255 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-01-01 07:34 | 2017-01-01 10:30 | 1 | 176 | 4260041 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. VER/CRB L3/HFP
18256 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-08-09 13:32 | 2014-08-09 15:00 | 2 | 88 | 4347581 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED UP..CHG CUTOUT// VER/DBM
18257 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-07-26 08:02 | 2012-07-26 08:24 | 8 | 22 | 4830221 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 4317 SOUTHVIEW--GREGG SUTPHIN--324 4331--CAL BEFORE GOING OUT--CUSTOMERS NEEDS TO RESTAIN DOG AND MOVE VECHILES--CAN REACH WITH MID SIZE BUCKET--CUTOUT NEEDS REPLACED--OLD STYLE CUTOUT FELL OPEN--WORKING FOR NOW--E MAIL TO RAYBURN///COD 8//EMAILED TO L RAYBURN// VER/DBM
18258 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-09-08 21:35 | 2016-09-08 23:03 | 2 | 88 | 4878731 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S07--BURNT UP C/O DOOR--REPLACED--ALLGOOD--IN AT 23:03--DS090816 VER/CRB
18259 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2012-06-06 13:39 | 2012-06-06 16:35 | 1 | 176 | 4887711 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA TRANSF === CALLED FOR 15 KVA TRANSF AND BIG BUCKET === CHANGED TRANSF REM 10 KVA INST 15 KVA == OK VER/KEP IDC XXXX
18260 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2018-11-20 15:37 | 2018-11-20 18:33 | 1 | 176 | 4464761 | 176 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | sec connection L3/HFP
18261 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-02-20 14:50 | 2010-02-20 15:34 | 4 | 44 | 59349-1 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SER NEUT. BROKE CHANGE OUT 4/3 TO 2/3//OPENED TRANSFORMER TO MAKE REPAIRS @ 1450//CLOSED @ 1534//COD 4// VER/DBM IDC XXXX
18262 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2012-10-13 13:59 | 2012-10-13 16:55 | 1 | 176 | 4137021 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. COD-1 ISO TF 37820054000140 VER/HFP L3/HFP IDC XXXX
18263 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-12-09 10:24 | 2013-12-09 13:20 | 1 | 176 | 4135291 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CO 19.9 ON POLE 79-58 SHEP COMING TO HELP --FETR 1430----REPLACED CO VER/CRB L3/HFP HFPC PN78-58
18264 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-01-06 12:16 | 2014-01-06 15:12 | 1 | 176 | 4237281 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER LOCATION AND POLE NUMBERS ARE WRONG HE LIVES ON CHAVIES DUNRAVEN ROAD HIS XFMR POLE IS 197-28 LINE FUSE POLE IS 197-23 LINE CUTOUT ON THIS POLE WASBROKEN FUSE ALSO BLOWN ON POLE 197-17 POWER RESTORED AT 1512 CREW 077H01//NO MD ENTRY REQUIRED, CSC TIED CALL TO WRONG ACCT//ISO 37830197000017//COD 1// VER/DBM
18265 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2017-10-10 18:14 | 2017-10-10 19:42 | 2 | 88 | 4443701 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED DOOR 38830272000196 VER/AWD L3/HFP XXXHFP
18266 | Paintsville | 3401101 | FALCON | FALC-OILS | 2020-04-02 14:24 | 2020-04-02 17:20 | 1 | 176 | 4555681 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed and burned service neutral in two. Replaced #4 service with #2. Restored @ 17:20. sh
18267 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-04-20 11:19 | 2018-04-20 14:15 | 1 | 176 | 4258731 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insalink bad on pole, customer back on at 14:15
18268 | Pikeville | 3402003 | KEYSER | MULLINS | 2019-03-28 12:13 | 2019-03-28 15:09 | 1 | 176 | 4032771 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans. fuse open @1127-B-426, checking. Bad 15kva 7200 trans., will be changing out. Got trans. changed and closed back in @1509.
18269 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-12-25 09:10 | 2017-12-25 12:06 | 1 | 176 | 4676651 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfm. bad on pole 143-18////will need 25 kva. 19.9 xfm single bushing and one man with bucket to make repairs..restored.
18270 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-02-04 08:34 | 2018-02-04 11:30 | 1 | 176 | 4799141 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv cutout, trk to pole, in approach need observer//38830141A00156 MADE MD TO SHOW TRANS ON THIS POLE AND 1 CUST ON IT//COD 1//bad 12 kv cutout, trk to pole, in approach need observer, restored @ 11:30. mismapped xfmer pole is 141-156, 25 kva
18271 | Hazard | 3309003 | JEFF | VIPER | 2017-02-17 16:32 | 2017-02-17 18:00 | 2 | 88 | 4405231 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKE FUSE/ ISO 37830345C00372/ COD 2/ VER/BOW L3/HFP XXXHFP
18272 | Whitesburg | 3312901 | JENKINS | KONA | 2008-01-22 05:09 | 2008-01-22 08:05 | 1 | 176 | 58830-1 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3312901- @ 0520CONTACTED D/S FOR CREW TO REPLACE BAD XFMR... CONTACTED *** SERVICER **** WAS OUT ON THIS CALL LAST NIGHT AND RE-FUSED TR ... //VER/CRB... IDC XXXX
18273 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-11-12 07:49 | 2019-11-12 10:45 | 1 | 176 | 4023531 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | nuetral connection was broke in service and bad hot leg.. repairs made.. power restored @ 10:45
18274 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2011-12-20 19:54 | 2011-12-20 22:50 | 1 | 176 | 4192011 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST MAPPED WRONG...THEY ARE ON XFMR POLE 989A206..XFMR FUSE OUT ON THAT POLE..WILL RE-FUSE..//BAD XFMR.NEED 2 MEN, MATERIAL HANDLER & 25KVA 7.2 KV XFMR.//.XFMR REPLACED.POWER ON NOW.JRV.12/20/11 //VER/CRB IDC XXXX
18275 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-03-02 14:24 | 2010-03-02 14:40 | 11 | 16 | 62277-1 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW IS CHANGING POLE THAT CUSTOMERS SERVICE COMES FROM. T MILLER HAD KNOCKED ON CUSTOMERS DOOR AND NO ONE ANSWERED. MILLER WILL ATTEMPT TO NOTIFY CUSTOMER AGAIN. SH VER/KEP L3/KEP IDC XXXX
18276 | Paintsville | 3401802 | INDEX | HOSPITAL | 2015-11-11 11:06 | 2015-11-11 14:02 | 1 | 176 | 4427801 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON POLE38830654A00189.. AND OIL SPILL. CALLED ROGER MAYNARD HE IS GETTING PLAN TO COME ADN CHANGE TRANSFORMER AND FOR SPILL.. DENZIL FROM ELLIOT IS COMING TO CHANGE TRANSFORMER.. SEND TICKET TO HIM.. RELEASED BY CREW 076H03 VER/CRB
18277 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-05-17 11:39 | 2019-05-17 14:35 | 1 | 176 | 4281861 | 176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Found bad connection on xfmr secondary riser. Reworked all sec connections and replaced old xfmr cutout. Restored @ 14:35. sh
18278 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-10-10 13:50 | 2009-10-10 16:45 | 1 | 175 | 55163-1 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED/REPLACED CONNECTIONS /./ VER/TOM IDC XXXX
18279 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-07-14 09:50 | 2008-07-14 12:45 | 1 | 175 | 52304-1 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3310501// STS TRANSFORMER FUSE HANGING DOWN, FUSE BROKE INTO // VER/TOM IDC XXXX
18280 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2012-08-25 12:11 | 2012-08-25 12:36 | 7 | 25 | 4971231 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 7// VER/DBM IDC XXXX
18281 | Hazard | 3301101 | CHAVIES | CHAVIES | 2020-06-07 15:05 | 2020-06-07 15:30 | 7 | 25 | 4975731 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service connection burnt out. made repaires. xfm at 37830171000104 open from 15:05 to 15:30
18282 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2012-07-20 10:50 | 2012-07-20 13:45 | 1 | 175 | 4784171 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ==REPLACED CUTOUT == REFUSED == POWER OK COD-1 ISO LF 37830395000014 VER/HFP L3/HFP
18283 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-05-21 15:38 | 2011-05-21 16:03 | 7 | 25 | 4120621 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4120621 // CREW HAD TO OPEN FUSE IN ORDER TO REPLACE XFMR CUTOUT//COD 7// MD FILED// VER/DBM IDC XXXX
18284 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-09-09 16:23 | 2018-09-09 19:18 | 1 | 175 | 4065911 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad Cutout, will need a 19.9 cutout power restored at 19:18
18285 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-03-15 13:57 | 2022-03-15 16:52 | 1 | 175 | 4628421 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans fuse open on pole 237-A-145,Will be trying to get it back in..Trans fuse open on pole 237-A-145,Have a broke cutout,Will be making repairs..Trans fuse open on pole 237-A-145,Have a broke cutout,Will be making repairs..Restored at 16:52.
18286 | Hazard | 3310502 | HADDIX | CANOE | 2015-07-21 11:07 | 2015-07-21 14:02 | 1 | 175 | 4925501 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANS VER/CRB
18287 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2012-04-26 19:37 | 2012-04-26 22:32 | 1 | 175 | 4715351 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 CSP XFMR, TRACK MACHINE, WILL NEED CUTOUT AND BRACKET, CREW ON SITE RELEASED BY CREW 078S05///VER/CRB L/3 CRB IDC XXXX
18288 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-01-24 09:03 | 2015-01-24 11:58 | 1 | 175 | 4957621 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | UG RISER FUSE CUTOUT BROKE. CREW ENROUTE TO REPLACE. REPLACED CUTOUT AND RESTORED @ 11:58. SH// COD 1// VER/ ADH
18289 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-03-23 20:45 | 2011-03-23 21:20 | 5 | 35 | 58160-1 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT, STS FUSE BROKE INTO//VER/CRB IDC XXXX
18290 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2014-07-08 18:35 | 2014-07-08 21:30 | 1 | 175 | 4212501 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT NTA//COD 1// VER/DBM
18291 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2017-09-18 20:24 | 2017-09-18 23:19 | 1 | 175 | 4372421 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-7256 BAD 25KVA TRANS. TRUCK TO POLE RELEASED BY CREW 078S08---CREW ON SITE---CHANGED OUT BAD 25KVA---VOLT CK GOOD 122-122-245---TBL TKT COMP---RMV VER/ARN L3/HFP XXXHFP
18292 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2016-01-12 17:21 | 2016-01-12 20:16 | 1 | 175 | 4613671 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN ON 1139-A-258 REFUSED CUROUT RESTORED POWER AT 20:16/ ISO 38821139A00258/ COD 1/ VER/BOW
18293 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-11-24 08:31 | 2008-11-24 11:26 | 1 | 175 | 51497-1 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3000202// CARL REPORTED BAD UG// SEND TO VERNON//CREW INSTALLING TEMP XFMR/FETR 1200/ ADD-A-PHASE INSTALLED/11:30 POWER RESTORED///// SEND COPY TO DAN HUFF NEED NEW RIVER TO LOCATE AND REPAIR ASAP V MULLINS & CREW//VER/CRB IDC CUSTOMER TURNED OFF BREAKER SO POWER WAS OUT XXXX
18294 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2015-11-10 08:39 | 2015-11-10 09:14 | 5 | 35 | 4423831 | 175 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | FUSE HAD BROKEN OLD FUSE, REFUSED XMF APR AT 0914 CLOSE TICKET VER/ARN
18295 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-06-03 00:30 | 2016-06-03 01:05 | 5 | 35 | H4289511 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOLID CUTOUT BROKEN ON 876-367..CHANGING.. MIDDLE PHASE (33) OUT ORIGINALLY. OPENED OTHER 2 PHASES (5) AT 1230. CLOSED ALL IN AT 0105. 38830876B00367 VER/AWD L3/HFP HFPC FPNONE CDC83
18296 | South Williamson | 3411401 | DEWEY | INEZ | 2021-04-11 14:20 | 2021-04-11 17:15 | 1 | 175 | 4442401 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Bad current limiting fuse on 815-442. Xfmr fuse out also. Restored @ 17:15. sh
18297 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-03-06 11:00 | 2014-03-06 13:55 | 1 | 175 | 4457021 | 175 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | OFF 1100 ON 1355//////TRANSFORMER FAILURE - PRIMARY FUSE DID NOT BLOW, CUSTOMER ONLY RECEIVING 88 VOLTS ON B PHASE OF 3 PHASE 208 BANK. COD=1 ISO TF 37830072D00030 VER/HFP L3/HFP
18298 | South Williamson | 3411401 | DEWEY | INEZ | 2008-03-18 10:50 | 2008-03-18 13:45 | 1 | 175 | 58146-1 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411401// CONN BAD ON SERV DROP ON POLE// VER/DBM IDC XXXX
18299 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2021-01-18 09:00 | 2021-01-18 11:55 | 1 | 175 | 4874681 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed. Replaced 75 ft 4/3 service with 2/3. Restored at 11:55. ooONE CUSTOMER AFFECTEDoo. sh
18300 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2013-07-12 13:31 | 2013-07-12 16:26 | 1 | 175 | 4513561 | 175 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 2/3 SD NEEDS REPAIRED. RELEASED BY CREW 078H122/3 SD NEEDS REPAIRED. REPAIRS MADE MP VER/HFP L3/HFP IDC XXXX
18301 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2015-07-23 13:00 | 2015-07-23 15:55 | 1 | 175 | 4935421 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE PULLED INTO. REFUSED AT 1555. VER/HFP L3/HFP
18302 | Pikeville | 3421001 | BREAKS | CITY | 2022-07-22 17:08 | 2022-07-22 20:03 | 1 | 175 | 4550131 | 175 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a Hot leg into on service Drop,Will be making repairs..Restored service at 20:03.
18303 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2008-06-03 16:43 | 2008-06-03 19:38 | 1 | 175 | 55170-1 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR BLOWED ON METERING I CUT IT IN THE CLEAR AND REFUSED METERING VER/HFP IDC XXXX
18304 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-01-21 18:15 | 2016-01-21 18:50 | 5 | 35 | 4639021 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | NEED 1 MAN AND RISER FOR 50 KVA . OPENED XFMR AT 18:15 AND CLOSED AT 18:50, REPLACED ALL CONNECTIONS ON XFMR , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03//NO OUTAGE TILL TRANSFORMER OPENED VER/CRB
18305 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-12-23 06:57 | 2022-12-23 09:52 | 1 | 175 | 4298971 | 175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout
18306 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-04-03 18:41 | 2017-04-03 21:35 | 1 | 174 | 4610191 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR FUSE OUT , CON AT XFMR BAD . REPLACED CONN. CLOSED FUSE BACK @ 21:35. VER/CRB L3/HFP XXXHFP
18307 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-10-02 23:45 | 2011-10-03 01:12 | 2 | 87 | 4941481 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 400-232, REPLACED CUTOUT RESTORED POWER AT 01:12 //VER/GAH IDCC TOF2234 FLICKERING ESTIMATED TIME OFF XXXX
18308 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-03-07 11:36 | 2015-03-07 14:30 | 1 | 174 | 4157691 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVIN FROZE OUT ON SECONDARY AT XFMR. WILL MAKE REPAIRS// VER/ ADH
18309 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-05-11 14:51 | 2022-05-11 17:45 | 1 | 174 | 4878441 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25KVA 7200 on pole 222-D-245, truck access. A crew will have to set up and partially block Flat Gap RD to make repairs. Released by crew 077S04 replaced transformer power restored at 17:45
18310 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-03-04 10:46 | 2009-03-04 13:40 | 1 | 174 | 54921-1 | 174 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3400301// HAD TO MAKE NEW CONNECTIONS AT TRANSFORMER. EVERYTHING OK.// VER/DBM IDC XXXX
18311 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-06-12 09:51 | 2012-06-12 12:45 | 1 | 174 | 4905511 | 174 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVE END HAS BURNT OPEN ON SERVICE POLE /// GOING TO REPLACE /// ONLY ONE CUSTOMER AFFECTED /// REPAIRS MADE AND VOLTAGE CHECKS GOOD// VER/DBM IDC XXXX
18312 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-02-21 16:18 | 2010-02-21 17:45 | 2 | 87 | 59560-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA XFMR BAD..RE HOOKED BOTH HOUSES ON SEC FROM POLE-851-57..TIM MILLER WILL CHANGE XFMR TOMORROW..BB//COD 2 (NOT 8 PER SERVICER)// VER/DBM IDC XXXX
18313 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2014-11-23 02:38 | 2014-11-23 03:36 | 3 | 58 | 4754791 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE, REPLACED FUSE AND THE POWER IS BACK ON. VER/KEP
18314 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2008-10-06 17:16 | 2008-10-06 20:10 | 1 | 174 | 53734-1 | 174 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3410601// SERVIN BURNED APART IN SERVICE DROP, ALL WORK COMPLETE / GXJ// VER/DBM IDC XXXX
18315 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-02-11 15:16 | 2013-02-11 18:10 | 1 | 174 | 4810621 | 174 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT INTO NEED CREW RELEASED BY CREW 078S08SERVICE BURNT INTO NEED CREW REPLACED 4/3 DROP WITH 2/3 ///VER/CRB L/3 CRB IDC XXXX
18316 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-03-27 08:06 | 2010-03-27 11:00 | 1 | 174 | 54888-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 SECONDARY CABLE BURNT-INTO //VER/GAH IDCC CCCF XXXX
18317 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-09-05 13:37 | 2019-09-05 14:35 | 3 | 58 | 4984381 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | leaking xfmr on p# 1148-347 LRM FETR 15:00 times 13:37 to 14:35 please close ticket LRM
18318 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-12-25 10:11 | 2022-12-25 13:05 | 1 | 174 | 4354221 | 174 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | burnt up hotleg only 1 customer effected power restored to customer 13:05
18319 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-03-07 06:20 | 2014-03-07 09:14 | 1 | 174 | 4458221 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL BE WORKED AT START OF SHIFT CURRENT LIMITING FUSE BURNED UP. VER/CRB IDC XXXX
18320 | Hazard | 3303902 | LESLIE | WOOTON | 2020-10-15 20:19 | 2020-10-15 21:17 | 3 | 58 | 4560321 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
18321 | Hazard | 3303902 | LESLIE | WOOTON | 2015-06-26 09:17 | 2015-06-26 12:11 | 1 | 174 | 4661431 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === REPLACED CUTOUT ==== POWER OK/ ISO 37830487000192/ COD 1/ VER/BOW
18322 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-02-07 18:51 | 2011-02-07 20:18 | 2 | 87 | 55105-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT... REPLACED CUTOUT RESTORED POWER AT 20:18//VER/CRB IDC XXXX
18323 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-10-01 14:13 | 2018-10-01 17:07 | 1 | 174 | 4185901 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout complete
18324 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-12-28 15:21 | 2020-12-28 18:15 | 1 | 174 | 4831421 | 174 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | tree had grown up and into secondary//hot leg and neutral into//repaires made//restored at 18:15//complete//em
18325 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-07-26 16:06 | 2012-07-26 19:00 | 1 | 174 | 4834831 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | EMAIL THIS TO TIM HALL. HE IS GOING TO HAVE SOMEONE CHANGE THIS 25KVA TO A 50 KVA { 7200 } TOMORROW. WILL NEED CUTOUT AND ARRESTER. THIS IS TRUCK ACCESSIBLE. SERVES 3643 DRY FK. OF SHELBY CUSTOMER SAID WE COULD BRING TRUCK ACROSS CULBERT. SERVICE DROP BURNED DOWN. I AM GOING TO REPLACE 4/3 DROP WITH 2/3. I CHANGED DROP.//EMAILED TO T HALL// VER/DBM
18326 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-02-25 17:18 | 2020-02-25 18:45 | 2 | 87 | 4432131 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | cutout fuse broken L3/HFP
18327 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2010-08-25 16:27 | 2010-08-25 17:25 | 3 | 58 | 60524-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT UP CUTOUT DOOR ON XFMR.....OLD CUTOUT...WILL HAVE TO CHANGE OUT......//....CHANGED CUTOUT.....RE-FUSED....POWER ON...TROUBLE POLE WAS 967-A-89.....ONLY 3 CUSTS ON THIS XFRMR.....JRV...08/25/10//MADE A MD IDC XXXX
18328 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-05-11 15:06 | 2016-05-11 18:00 | 1 | 174 | 4201171 | 174 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ***H4201171*** BAD CONNECTION MID-SPAN IN LASH SECONDARY, T MORRIS AND CREW COMING TO HELP. ONLY 1 CUST WITH PART POWER, OPENED TRANSFORMER @ 17:15, CLOSED @ 18:00, POWER RESTORED./ ISO 37830223B00042/ COD 1/ VER/BOW
18329 | South Williamson | 3200302 | BELFRY | TOLER | 2010-07-03 22:49 | 2010-07-04 01:43 | 1 | 174 | 62033-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRMER FUSE MELTED OUT.....PROB BECAUSE CAP WAS NOT TIGHTENED ON OLDER TYPE CUTOUT DOOR....WILL RE-FUSE...//...BAD XFRMER....CALLED CREW...THEY ARE GETTING XFRMER & ARE ENROUTE....RELEASING...SEND TO R MARCUM.... RELEASED BY CREW 079H08 //VER/GAH IDC XXXX
18330 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-07-02 17:52 | 2016-07-02 18:50 | 3 | 58 | 4515691 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR CHGED VER/AWD
18331 | Hazard | 3302704 | HAZARD | KENMONT | 2011-09-19 17:27 | 2011-09-19 20:21 | 1 | 174 | 4885191 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR C/O ON POLE 37830296D11102/// CHANGED XFMR C/O. POWER RESTORED /// COD-1 ISO TF 37830296D11102 VER/HFP L3/HFP IDC XXXX
18332 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-10-25 12:37 | 2008-10-25 13:35 | 3 | 58 | 58969-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3010602 -BROKEN FUSE LINK //VER/GAH IDCC CNT1 XXXX
18333 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-05-27 08:26 | 2021-05-27 11:20 | 1 | 174 | 4630621 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR fuse was blown on pole 223-B-566. I refused this cutout and upon closing back in, this XFMR exploded. Need a crew to come replace this XFMR, 10 or 25KVA truck access, 19.9. Released by crew 077S04 replaced transformer and restored power at 11:20
18334 | Hazard | 3308001 | JACKSON | S.JACKSON | 2021-12-08 23:22 | 2021-12-09 00:20 | 3 | 58 | 4163451 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Attempted to contact customer: no answer fuse had pull into
18335 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-12-13 17:49 | 2018-12-13 19:16 | 2 | 87 | 4563071 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//NO ANSWER//replaced broke line fuse cutout @ 279_100 complete L3/HFP
18336 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-11-24 08:26 | 2008-11-24 11:20 | 1 | 174 | 51489-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007903////VER/CRB IDC XXXX
18337 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-09-09 12:03 | 2009-09-09 13:30 | 2 | 87 | 58887-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFME CUTOUT ON POLE 38830182D06052, 1 PHASE ON 3 PHASE BANK, CREW REQUIRED, TRUCK OK. RELEASED BY CREW 078S05 RESTORED 1330 VER/KEP L3/KEP IDC XXXX
18338 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-05-24 09:03 | 2022-05-24 11:57 | 1 | 174 | 4940281 | 174 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a Hot Leg Burned into at weaherhead,going to pull Meter and resqueeze connections.. restored @ 1157
18339 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2015-10-02 18:01 | 2015-10-02 19:28 | 2 | 87 | 4304751 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED FUSE/ CUTOUT DOOR ITSELF BORKE DUE TO OLD AGE/ ISO 38830295000065/ COD 2/ VER/BOW L3/HFP XXXHFP
18340 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2012-04-12 08:57 | 2012-04-12 09:55 | 3 | 58 | 4667971 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND SECONDARY BURNTED OPEN ON TRANSFORMER RISER, I HAVE MADE REPAIRS AND EVERYTHING IS FINE AT THIS LOC NOW COD-3 ISO TF 39831000B00224 VER/HFP L3/HFP
18341 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-06-19 10:54 | 2010-06-19 13:48 | 1 | 174 | 51243-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP XFMR..NEED LIGHTNING ARRESTOR AND CUTOUT ALSO..I TALKED TO CUST. GEORGE REED HE SAID IT WAS OK TO CHG MONDAY MORNING..CREATED IO ORDER VER/HFP L3/HFP
18342 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-12-20 17:27 | 2014-12-20 18:25 | 3 | 58 | 4872631 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN. ONLY THREE CUSTOMERS AFFECTED. BOTH OF THESE CUSTOMERS ARE SERVED FROM XFMR 38830785A21315. RESTORED @ 18:25. SH RELEASED BY CREW 076S02/ ISO 38830785A21315/ COD 3/ VER/BOW
18343 | South Williamson | 3411401 | DEWEY | INEZ | 2022-04-24 09:54 | 2022-04-24 12:48 | 1 | 174 | 4794551 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke//repairs made//restored at 12:48//complete//em
18344 | Paintsville | 3401102 | FALCON | SALYERSVI | 2011-12-24 12:50 | 2011-12-24 13:48 | 3 | 58 | H4200141 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | S/D BURNED INTO.SERVE END HEATED UP.POLE HAD BEEN CHG OUT YEARS AGO AND CONTRACTOR SPLICED WIRE.CUST HAD DAMAGE TO HOOD OF CAR.///. OPENED TR @ 1250 TO REPAIR/REPLACE SERVICE DROP /// COD-4 ISO TF 38830875A00150 DUP IN HOIS FROM 4200141 FOR 3 CUST VER/HFP L3/HFP IDC XXXX
18345 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-04-10 19:03 | 2020-04-10 20:30 | 2 | 87 | 4618011 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hot leg and netural broke in service /open transformer one other customer was notified off at repairs made voltage check good open xformer 19:30 closed at 20:30
18346 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-12-10 08:33 | 2012-12-10 10:00 | 2 | 87 | 4455901 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER COULD NOT RECEIVE ON SPEC REPLACED CUTOUT RESTORED POWER VER/KEP
18347 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-05-28 18:08 | 2018-05-28 21:02 | 1 | 174 | 4511381 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on 188-541/ making repairs/changed cutout xfmer on 188-541 back in @ 2102/ please close ticket/MLH //cod 1
18348 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2016-10-21 09:06 | 2016-10-21 10:33 | 2 | 87 | 4037171 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CAR HAS HIT PRIMARY POLE 38821065A00061. POLE IS OK, WE DO NOT HAVE ANY DAMAGES. KSP IS ON SITE. CUTOUT ON POLE 38821065A00063 WAS ALREADY CRACKED AND FELL APART WHEN THE CAR HIT POLE 1065-A-61. I REPLACED THE CUTOUT AND POWER WAS RESTORED AT 10:30./ ISO 38821065A00063/ COD 2/ VER/BOW
18349 | South Williamson | 3411401 | DEWEY | INEZ | 2008-09-20 17:32 | 2008-09-20 18:59 | 2 | 87 | 65875-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT BROKE POLE 624-C-532//COD 1//ISO// VER/DBM IDCC CNT1 XXXX
18350 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-10-21 07:27 | 2011-10-21 08:25 | 3 | 58 | 4006631 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | GOT ONE LINE FUSE OUT TO ONE POLE TAP GOING TO REFUSE IT STS FUSE BROKE INTO COD-3 ISO LF 38831108D00081 VER/HFP L3/HFP IDC XXXX
18351 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-03-25 09:02 | 2009-03-25 10:00 | 3 | 58 | 61301-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT OK 1000 IDC XXXX
18352 | Hazard | 3310502 | HADDIX | CANOE | 2018-01-08 18:36 | 2018-01-08 20:03 | 2 | 87 | 4722241 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | got bad insulator on pole 37830051000029 going to change out
18353 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-02-10 06:51 | 2009-02-10 09:45 | 1 | 174 | 57230-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311101//CHANGED 19.9KV CUTOUT//COD 1// VER/DBM L3/DKG
18354 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-05-21 19:11 | 2016-05-21 22:05 | 1 | 174 | 4245331 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | P 236-47 JUMPER CAME LOOSE FROM HOT TAP. SERVICER TO MAKE REPAIRS. NOT BY TRUCK LRM REPAIRS MADE PWR RESTORED @ 22:05 PLEASE CLOSE TICKET//COD 1// VER/DBM
18355 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2021-12-21 15:32 | 2021-12-21 16:30 | 3 | 58 | 4217941 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @23-113, checking. Fuse melted out, refused @1630.
18356 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-03-27 22:12 | 2017-03-27 23:39 | 2 | 87 | 4590061 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT ON 1125C3663 RESTORED POWER AT 23:39/// VER/DKM
18357 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2018-01-06 09:30 | 2018-01-06 09:59 | 6 | 29 | 4711521 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot tap lead burnt off of recloser on pole #79-180/// Company is trying to move trucks so i can make repairs/// Opened recloser @ 09:30 to make repairs/// made repairs and closed recloser in @ 09:59 and restored service. Power ON shows only part out at 0652, changed time off from comments.
18358 | Hazard | 3309302 | VICCO | JEFF | 2009-07-15 16:14 | 2009-07-15 17:41 | 2 | 87 | 62834-1 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP HOT LINE CLAMP BURNED OFF AT POLE 321-343 L3/HFP IDC XXXX
18359 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-01-20 20:09 | 2020-01-20 21:36 | 2 | 87 | 4324141 | 174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced xfr connections L3/HFP
18360 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-02-26 08:27 | 2014-02-26 11:20 | 1 | 173 | 4435011 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FROZE OUT IN SERVICE DROP SPLICE. RE-WORKED CONNECTIONS. SH// VER/DBM
18361 | South Williamson | 3411401 | DEWEY | INEZ | 2021-06-08 19:12 | 2021-06-08 22:05 | 1 | 173 | 4691921 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | L/F blown on 744-B-26 will check/// Fuse had pulled apart inside cutout door. Installed new fuse and restored @ 22:05
18362 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-11-09 13:57 | 2009-11-09 16:50 | 1 | 173 | 53605-1 | 173 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP HAD BURNED OFF LINE AT PRI. METERING POLE#-1102-149. I REPLACED HOT TAP.// VER/DBM IDC XXXX
18363 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-02-18 12:42 | 2019-02-18 15:35 | 1 | 173 | 4804201 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on sec pole 828-164 affecting 1 customer. Replaced connection and restored @ 15:35. sh
18364 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-08-12 13:16 | 2009-08-12 16:09 | 1 | 173 | 64910-1 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402002//HOT TAP STIRRUP BURNED OFF AT 1105-47,NEED CREW TO REDUCE OUTAGE TIME,WILL HAVE TO OPEN LINE TO REPAIR// VER/DBM IDC XXXX
18365 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2013-03-10 18:02 | 2013-03-10 20:55 | 1 | 173 | 4895641 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | B & C LINE FUSES BLOWN ON UNDERGROUND POLE 449-581, BAD PAD MOUNT XFMR# 449-1009, 300 KVA 7200 ISOLATED LINE FUSES WILL HOLD FOR CREW TOMORROW. CREATED OPS ORDER #035365527 C0D-1 ISO DF 37830449A20581 VER/HFP L3/HFP IDCC CNT10 XXXX
18366 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-12-29 14:07 | 2020-12-29 17:00 | 1 | 173 | 4833691 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Svc neutral broken // splice pulled out of service neutal repaired and restored 1 customer out
18367 | Hazard | 3309302 | VICCO | JEFF | 2013-09-03 10:17 | 2013-09-03 13:10 | 1 | 173 | 4816011 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN//// 15KVA XFMR BAD, 19.9KV. CAN REACH WITH BUCKET TRUCK. THIS SERVES CELL TOWER WERE MICHAEL COMBS HOUSE IS. RELEASED BY CREW 077S08//COD 1// VER/DBM IDC XXXX
18368 | South Williamson | 3200302 | BELFRY | TOLER | 2011-06-26 17:15 | 2011-06-26 20:08 | 1 | 173 | 4417101 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE FROM BAD XFMR CUTOUT ON 1063A113..LATERAL FUSE ON 1063A76...THAT CUTOUT BAD ALSO.CALLED CREW.THEY ARE ENROUTE..BOTH CUTOUTS NEED REPLACED & POLE 1063A113 NEEDS BAYONETTED..//...POLE TOP SECURED..BOTH CUTOUTS REPLACED..RESTORED POWER..JRV & S WMSN CREW..06/26/11//VER/CRB IDC XXXX
18369 | Hazard | 3303902 | LESLIE | WOOTON | 2020-09-26 10:37 | 2020-09-26 13:30 | 1 | 173 | 4498271 | 173 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on transformer lead
18370 | South Williamson | 3411401 | DEWEY | INEZ | 2014-08-22 22:17 | 2014-08-23 01:10 | 1 | 173 | 4409121 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ONPOLE 745-62//NEED BIG BUCKET//RESTORED AT1:10 RELEASED BY CREW 079S01// COD 1// VER / ADH
18371 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-08-31 14:08 | 2015-08-31 17:01 | 1 | 173 | 4185901 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFRM.37830387B00250 BAD XFRM.CHANGED OUT TRANSFORMER, ALL POWER RESTORED @17:01HRS.P.HICKS VER/CRB
18372 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-01-30 13:43 | 2022-01-30 16:36 | 1 | 173 | 4416701 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Fuse door has Broke on Trans at pole 263-C-233,Going to replace Door and restore service..Fuse door has Broke on Trans at pole 263-C-233,.Going to Lift Hot Tap and Ground tap to climb pole 263-C-233 and repalce cutout..Fuse door has Broke on Trans at pole 263-C-233,.Going to Lift Hot Tap and Ground tap to climb pole 263-C-233 and repalce cutout..Restored @ 16:36.
18373 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-06-28 11:01 | 2009-06-28 13:54 | 1 | 173 | 65882-1 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3110902//FIXED SER, DROP COMP
18374 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-03-08 18:27 | 2010-03-08 21:20 | 1 | 173 | 64051-1 | 173 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUSTOMER AFFECTED, HE HAD OPEN NEUTRAL ON POLE 227-35, RECONNECTED NEUTRAL VOLTAGE OK.// VER/DBM IDC XXXX
18375 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2016-12-01 13:47 | 2016-12-01 16:40 | 1 | 173 | 4158701 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | HELD FOR PM SERVICER. ARRESTOR BURNT UP ON 966-B-2754 REPLACED ARRESTOR RESTORED POWER AT 16;40 LINE FUSE ON 966-B-722 IS 10T VER/AWD L3/HFP HFPC FP38820966B02754
18376 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2008-12-17 11:34 | 2008-12-17 14:27 | 1 | 173 | 59534-1 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400302// HAVE A BAD 50 KVA XFMR , CREW IS COMING OUT OF PIKEVILLE TO CHANGE.//WR 27720229// VER/DBM L3/KEP IDC XXXX
18377 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-02-06 15:46 | 2018-02-06 18:39 | 1 | 173 | 4809771 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broken in service drop. making repairs. some receptacles and bulbs were blown, informed customer to call 800 number on bill. repairs made, pls complete. thanks tre//call center filled out personal injury form
18378 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-09-26 21:02 | 2009-09-26 23:55 | 1 | 173 | 64722-1 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKEN APART. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. IDC XXXX
18379 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-03-30 11:02 | 2020-03-30 13:55 | 1 | 173 | 4543111 | 173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Riser cutout failed on 850-356. Replacing all three. Restored @ 13:55. sh
18380 | Hazard | 3309003 | JEFF | VIPER | 2018-11-25 08:53 | 2018-11-25 11:45 | 1 | 172 | 4475011 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout gate,replace cutout gate,/ ISO 37830394B20455/ COD 1 L3/HFP
18381 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-07-19 06:14 | 2011-07-19 09:06 | 1 | 172 | 4560771 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL FAILED//MADE REPAIRS//COD 1// VER/DBM
18382 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-04-28 12:22 | 2014-04-28 13:05 | 4 | 43 | 4640481 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT NO TRUCK LINE FUSE AT LOCK HOLLEN 90-69 RELEASED BY CREW 078S08 REPLACED CUTOUT AND FUSE POWER OFF 12:22 TIME ON 13:05 COD-4 ISO TF 38830114000085 VER/HFP L3/HFP
18383 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-12-21 16:38 | 2018-12-21 19:30 | 1 | 172 | 4587721 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 170-9, power restored at 19:30 L3/HFP
18384 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2017-06-26 10:00 | 2017-06-26 12:52 | 1 | 172 | 4046091 | 172 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | FOUND BAD SPLICE IN SERVICE DROP THAT WAS RESULTING IN ONLY 94V PHASE TO GROUND/REPAIRED SPLICE AND RECHECKED VOLTAGE/ SERVICE ACTUALLY COMES OFF OF POLE 38821089D00064/ ISO 38821089D00064/ COD 1/ VER/BOW
18385 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2013-11-09 18:32 | 2013-11-09 19:15 | 4 | 43 | 4025011 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 44-4630 6T TRANS FUSE BROKE INSTALLED 8T 37.5 TRANS. ON POLE//COD 4// VER/DBM
18386 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-10-13 21:53 | 2015-10-13 22:36 | 4 | 43 | 4346961 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE ON 38830929000018 @ 21:53 TO REPLACE CUTOUT. REPLACED CUTOUT AND RESTORED @ 22:36. SH RELEASED BY CREW 076S02/MD MDE/ADH// VER/ ADH
18387 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2017-12-31 17:14 | 2017-12-31 18:40 | 2 | 86 | 4690511 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out door was broken replaced with new
18388 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-01-07 09:13 | 2013-01-07 12:05 | 1 | 172 | 4574091 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S10 LEAD BURNED OUT OF CUTOUT VER/KEP IDC XXXX
18389 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2019-11-15 21:14 | 2019-11-15 22:48 | 7 | 94 | 4038931 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer no answer and cant leave message. Hot leg burndt into @trans. pole 1125-D282, will have to open to make repairs will keep track of times. Opened up @2235, made repairs and closed back in @2248./ ISO 38831125D00282/ COD 7
18390 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-06-12 07:37 | 2018-06-12 09:03 | 2 | 86 | 4588821 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE IT//////////REPLACED BROKEN CUTOUT&RESTORED,ALL OK AFTERWARDS
18391 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2017-05-30 08:35 | 2017-05-30 11:27 | 1 | 172 | 4880901 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT.CHANGING 38830930D10841 VER/AWD
18392 | Hazard | 3310502 | HADDIX | CANOE | 2015-07-27 13:03 | 2015-07-27 15:55 | 1 | 172 | 4947271 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 075H04// VER/ ADH
18393 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-01-12 14:17 | 2016-01-12 15:43 | 2 | 86 | 4609571 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | KEVIN BROWN REPORTED UNSAFE CONDITION, OPEN WIRE SECONDARY BETWEEN POLES 38830020D47604 TO 38830020D47610. NEED ROLL 1 AU TWIST./WILL NEED TO OPEN XFMR@20-D4-7617 TO REPLACE TWO SPANS OF WIRE/APROX 1.5 HOUR OUTAGE/FETR 1600/VEM/OPEN XFMR@1417/REPAIRS MADE AND ALL CUST RESTORED 1543/PLEASE CLOSE TICKET/THANKS/VEM// VER/ ADH
18394 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-07-02 16:30 | 2015-07-02 17:56 | 2 | 86 | 4709301 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 38830752000045. BROKE AT TELEPHONE CABLE. CALLED TIM MILLER GAVE HIM MATERIAL NEEDED AND HE IS GATHERING IT UP TO HEAD THIS WAY.. NO OUTAGE YET BUT WILL OPEN UP AT POLE 752- 22 WHEN CREW ARRIVES/ POLE 38830752000045. BROKE AT TELEPHONE CABLE. CALLED TIM MILLER GAVE HIM MATERIAL NEEDED AND HE IS GATHERING IT UP TO HEAD THIS WAY.. NO OUTAGE YET BUT WILL OPEN UP AT POLE 752- 22 WHEN CREW ARRIVES.. OPENED LINE FUSE AT 16:30 AND CLOSED BACK IN AT 17:56./ ISO 38830752000022/ COD 2/ VER/BOW
18395 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2008-12-02 22:54 | 2008-12-03 00:20 | 2 | 86 | 54076-1 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3403301// FUSE LINK BROKE. RE-FUSED XFMR. SH VER/KEP L3/KEP IDC XXXX
18396 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2008-12-29 14:08 | 2008-12-29 17:00 | 1 | 172 | 64972-1 | 172 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3401703//HAD BAD CONNECTION ON TRANFORMER POLE. ONE LEG WAS OUT......DAH VER/TOM L3/TOM IDC XXXX
18397 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2017-05-10 13:23 | 2017-05-10 16:15 | 1 | 172 | 4776851 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRIMARY TAP RISER HAS BURNED OUT OF THE BOTTOM OF THE CUTOUT THAT GOES TO DEAD END POLE 38820989A00229.. REPAIRS MADE, AND POWER IS RESTORED.//MADE MD TO SHOW L/F COD 1//TRANS IS ON THE SOURCE SIDE OF L/F VER/CRB
18398 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2020-06-08 09:53 | 2020-06-08 12:45 | 1 | 172 | 4979231 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout on 966-A3-2759.i can make repairs.replace Cphase trans cutout on966--A3-2759.RESTORED POWER AT 12;45
18399 | South Williamson | 3411401 | DEWEY | INEZ | 2014-11-13 19:25 | 2014-11-13 20:51 | 2 | 86 | 4726161 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE IN XFMER CUTOUT BROKE///REFUSED @ 20:51///COMPLETE BR// COD 2// VER/ ADH
18400 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-08-29 08:18 | 2008-08-29 11:10 | 1 | 172 | 57204-1 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WORK REQUEST # 26022463 // IDC XXXX
18401 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-05-23 11:32 | 2016-05-23 14:24 | 1 | 172 | 4251371 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNED DOWN . WILL NEED HELP TO REPLACE . WILL CONTACT TIM HALL./ ISO 38831148000055/ COD 1/ VER/BOW
18402 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-10-12 11:02 | 2015-10-12 12:28 | 2 | 86 | 4341051 | 172 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR , OPENED XFMR AT 11:57 REPLACED ALL CONNECTIONS RESTORED POWER AT 12:28. VER/CRB L3/HFP HFPC MCCDL
18403 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-12-06 20:54 | 2019-12-06 23:46 | 1 | 172 | 4132551 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester failed, replaced & refused
18404 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-11-19 08:04 | 2008-11-19 09:30 | 2 | 86 | 66535-1 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY CONNECTION BURNED IN TWO. REPAIRED CONNECTION VER/KEP IDC XXXX
18405 | Pikeville | 3407101 | TOPMOST | DEMA | 2016-05-07 13:43 | 2016-05-07 16:35 | 1 | 172 | 4184961 | 172 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RELEASED BY CREW 074S02//ONE HOT LEG OUT IN SERVICE DROP//INSULINK HAD MELTED OUT//I REPAIRED SERVICE//RESTORED TO NORMAL AT 16:35//COMPLETE//EM/ ISO 37830162000077 / COD 1/ VER/BOW
18406 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-10-03 16:59 | 2014-10-03 18:25 | 2 | 86 | 4548691 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUTREPLACED BAD 19.9 LINE FUSE CUTOUT. VER/DKG L3/DKGXXXX
18407 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-09-12 17:16 | 2011-09-12 18:42 | 2 | 86 | 4862331 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR VFUSE BLOWN/// CONNECTOR ON XFMR WAS BAD CHANGED OUT, REFUSED POWER RESTORED. VER/CRB IDC XXXX
18408 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-09-16 08:38 | 2011-09-16 11:30 | 1 | 172 | 4876041 | 172 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER. --- POWER RESTORED. //VER/CRB IDC XXXX
18409 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-03-21 11:57 | 2013-03-21 14:49 | 1 | 172 | 4945191 | 172 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | MAP DISCREPANCY.XFMR POLE IS 1014B1-213.(THERE IS A 25 KVA THERE)..PART POWER..ONLY ONE CUST AFFECTED..BURNT UP INSULINK CONNECTOR SPLICE ON ONE HOT LEG OF 2/3 TWIST SECONDARY BETWEEN XFMR POLE & SEC POLE 1014B349.//..REPLACED SPLICES ON BOTH HOT LEGS WITH SQUEEZE-ON CONNECTORS..CUST HAS FULL POWER NOW..JRV.03/21/13 VER/KEP IDC XXXX
18410 | Hazard | 3303902 | LESLIE | WOOTON | 2015-02-27 23:14 | 2015-02-28 00:40 | 2 | 86 | 4086711 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//REPLACED BAD 19.9 KV CUTOUT VER/SEF
18411 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-06-28 09:48 | 2013-06-28 12:40 | 1 | 172 | 4420071 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFER--NEED TO REPLACE WIYH 25KVA--7200--TRUCK TO POLE--OIL SPILL--SEND TO B TACKET RELEASED BY CREW 078S07, CREW ON SITE, REPLACED XFMR, WEAVERTOWN ENVIRONMENTAL ON SITE, ALL POWER RESTORED VER/CRB L/3 CRB
18412 | Pikeville | 3413401 | GARRETT | GARRETT | 2015-07-20 15:03 | 2015-07-20 17:55 | 1 | 172 | 4918111 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REFUSED TRANSFORMER, COMPLETE / GXJ VER/HFP L3/HFP
18413 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-01-24 09:13 | 2012-01-24 12:05 | 1 | 172 | 4288641 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 400-121 RELEASED BY CREW 077S11//COD 1 IDC XXXX
18414 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-03-26 17:34 | 2014-03-26 19:00 | 2 | 86 | 4527471 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED BROKEN FUSE COD-2 ISO TF 38830269D00065 VER/HFP L3/HFP IDC XXXX
18415 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-02-19 17:54 | 2008-02-19 19:20 | 2 | 86 | 65499-1 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001002/BROKEN XFMR FUSE// COD 2// ISO/FLT SAME// VER/TOM IDC XXXX
18416 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2015-08-20 22:49 | 2015-08-21 01:41 | 1 | 172 | 4160231 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 69-4649 NEED TO CHG. SHORT PIECE OF 1/0 AND CHG. 1/0 SERVICE METER BASE SHORTED OUT BURNT SEC. DOWN NEED ROW OF 1/0 SERVICE WIRE( ( WIRE NEEDS CHGED)) MELTED TOGETHER IN PLACES RELEASED BY CREW 078S08///ON @ 01:41///TBL TKT COMP VER/HFP L3/HFP
18417 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-04-27 09:55 | 2018-04-27 11:21 | 2 | 86 | 4283791 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Byron Combs and Mike Lewis reported broken cutout at pole 37830318C00017 L3/HFP
18418 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-08-01 17:48 | 2016-08-01 20:40 | 1 | 172 | 4720051 | 172 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG U.G SERV. NEED BIG POWER TEMP. RELEASED BY CREW 078S07 CREW ON SITE POWER TEMP INSTALLED PLEASE CLOSE TICKET. RM VER/AWD
18419 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2016-01-10 15:41 | 2016-01-10 18:33 | 1 | 172 | 4603101 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER INTO ON CSP-BUCKET JOB BE CAREFUL ROLLING UP TO REMOVE CLAMP--I TOLD CUSTOMER WOULD BE LATTER TONIGHT--MAILBOX NUMBERED--NO DOG ON THAT END OF TRAILER RELEASED BY CREW 077S06//TRANSFORMER HAS A HOLE IN IT, PLUGGED HOLE NEEDS REPLACED ON 1-11-2016//SENTTO LINE DEPT// VER/CRB
18420 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-06-03 22:25 | 2008-06-04 01:17 | 1 | 172 | 55586-1 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000303//BAD 50KVA TRANS/CREW ON SITE/FETR0200/VEM/POWER RESTORED 0117/PLEASE CLOSE TICKET/VEM IDC XXXX
18421 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-12-08 14:02 | 2015-12-08 16:54 | 1 | 172 | 4518601 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | // REMOVED HOT TAP ON SIDE TAP AT 1642 ALL RESTORED AT 1654 RELEASED BY CREW 074S02 VER/CRB
18422 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-03-20 01:54 | 2008-03-20 03:20 | 2 | 86 | 59209-1 | 172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001002//BROKEN 6T FUSE VER/KEP IDC XXXX
18423 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-10-01 13:30 | 2019-10-01 16:21 | 1 | 171 | 4080651 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt up. replacing service drop.. complete. pls close. tre
18424 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2019-07-22 09:00 | 2019-07-22 11:51 | 1 | 171 | 4756421 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830808B40234 SHOWING A SWITCH ON MAP BUT IT IS A LINE FUSELine fuse blown on 808-B4-234 due to bad xfmr cutout on pole 808-179.We will be making repairs///Line fuse blown on 808-B4-234 due to bad xfmr cutout on pole 808-179.We will be making repairs///Replaced cutout and restored power @ 11:51
18425 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-08-27 17:17 | 2016-08-27 20:08 | 1 | 171 | 4841821 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200=120/240 NEED 2 MEN 50 KVA & MATERIAL MANDLER.COMPLTED POWER IS RESTORED VER/KEP
18426 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2010-06-04 18:23 | 2010-06-04 21:14 | 1 | 171 | 56882-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 1// VER/DBM IDC XXXX
18427 | Whitesburg | 3314401 | MAYKING | ERMINE | 2012-12-31 00:18 | 2012-12-31 01:15 | 3 | 57 | 4558511 | 171 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | CONNECTION ON XFMR POLE WAS BAD , I REPAIRED CONNECTION VER/ARN
18428 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-11-12 18:50 | 2019-11-12 21:41 | 1 | 171 | 4027111 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Customer has hot leg burnt into on one side, will have to open trans. to make repairs, will keep track of times. Opened trans. on 6-29 @2112, made repairs and closed back in @2141./ ISO 37820006000153/ COD 1
18429 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-05-13 19:19 | 2009-05-13 20:16 | 3 | 57 | 53886-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008001// BAD CUTOUT--POLE TOP BURNT--E MAIL TO S MARTIN FOR POLE REPLACEMENT // SENT TO MARTIN IDC XXXX
18430 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-07-14 17:14 | 2012-07-14 20:05 | 1 | 171 | 4725851 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN SERVICE DROP HAS BROKEN. I AM GOING TO OPEN TRANS/ LONG ENOUGH TO SPLICE NEUTRAL. WE OPENED TRANS. AT 19:50 AND CLOSED IT BACK IN AT 20:05.//COD 1//
18431 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2020-05-25 16:59 | 2020-05-25 19:50 | 1 | 171 | 4904671 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kV transformer 37830150A40635, replaced xfmr restored power at 19:50..
18432 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-01-17 17:00 | 2010-01-17 17:57 | 3 | 57 | 55606-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK IDC XXXX
18433 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-11-27 21:51 | 2010-11-27 22:48 | 3 | 57 | 60193-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | HAD FUSE BREAK INTO ON POLE 1084-43 THAT SERVICE THREE CUST VER/PDP IDCC PN35 XXXX
18434 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-04-10 22:08 | 2022-04-11 00:59 | 1 | 171 | 4746181 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 7200, 15kva has a hole in the bottom with oil leaking out. by truck. crew on site to make repairs. repairs made transformer in @ 00:59
18435 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-08-24 19:00 | 2008-08-24 21:51 | 1 | 171 | 54565-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400301//WILL DETERMINE PROBLEM IF ANYHAVE TO REPLACE SPAN OF 4/3 WITH 2/3,DALE IS GETTING HELP.NOT FETR CHANGE VER/JHM IDC CHANGED START TIME, BRIGHT DIM CALL, ESTIMATED TIME OFF XXXX
18436 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2013-02-05 13:54 | 2013-02-05 16:45 | 1 | 171 | 4793521 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON THE PRIMARY METERING POLE. // COD-1 ISO LF 37820055000035 VER/HFP L3/HFP IDC XXXX
18437 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-01-21 15:13 | 2009-01-21 18:04 | 1 | 171 | 58893-1 | 171 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP PARTIAL POWER,,WAITING ON TIM THOMAS...HE IS BRINGING 350 LEAD AND SQUEESONS AND HY PRESS...BB...COMPLETE...6.00..BB L3/HFP
18438 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-10-10 05:52 | 2020-10-10 08:43 | 1 | 171 | 4540931 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole 250C/145 bad cutout power on
18439 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-08-28 05:39 | 2022-08-28 08:30 | 1 | 171 | 4804031 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cut out door.. replaced..restored
18440 | Hazard | 3303902 | LESLIE | WOOTON | 2013-01-16 11:51 | 2013-01-16 14:42 | 1 | 171 | 4611351 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT ,ARR & BRKT RESTORED POWER AT 1442 JKC VER/KEP IDC XXXX
18441 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2008-06-15 08:21 | 2008-06-15 08:30 | 19 | 9 | 65126-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3001202 // SERVICER OPENED TRANSFORMER TO REPLACE BAD TRANSFORMER RISER // 20 MINUTE OUTAGE// COD-19 // SEND NOTE TO ENGR TO HAVE LOAD SPLIT UP DUE TO # OF CUSTOMERS ON SINGLE TRANSF. VER/LDA DKG/L3
18442 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-05-25 09:54 | 2020-05-25 12:45 | 1 | 171 | 4902871 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kv transformer 7200 trucks ok Released by crew 078H09
18443 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-04-22 17:54 | 2019-04-22 20:45 | 1 | 171 | 4148341 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse failed on 117-36.restored power at 20:45
18444 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-08-13 14:39 | 2010-08-13 17:30 | 1 | 171 | 54315-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING BAD CUTOT... COD-1 VER/HFP L3/HFP
18445 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-12-19 09:30 | 2018-12-19 12:21 | 1 | 171 | 4579151 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfm. cutout on pole 165-47..made repairs..restored.. L3/HFP
18446 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-12-16 09:30 | 2018-12-16 10:27 | 3 | 57 | 4570321 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.no outage until we started making repairs,looks like it may be a bad dead-end insulator on pole 1082-200,eric mck is bringing one,will replace when he arrivesno outage until we started making repairs,looks like it may be a bad dead-end insulator on pole 1082-200,eric mck is bringing one,will replace when he arrives///////MADE NECESSARY REPAIRS&RESTORED ALL CUSTS///OPENED XFRS@09:30,CLOSED@10:27 to change cutout ¦¦¦¦ PER VOICE RECORDER INITIALLY NO OUTAGE // OPENED ADDITIONAL XFMR L3/HFP
18447 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2016-06-02 06:24 | 2016-06-02 09:15 | 1 | 171 | 4282601 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT POWER RESTORED AT 09;15/ ISO 37830110B40006/ COD 1/ VER/BOW
18448 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2013-01-30 12:34 | 2013-01-30 15:25 | 1 | 171 | 4758471 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED ON SERVICE. REWORKED ALL CONNECTIONS ON SECONDARY POLE. RESTORED @ 15:25. SH ///VER/CRB L/3 CRB IDC XXXX
18449 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-12-03 11:15 | 2019-12-03 14:06 | 1 | 171 | 4119661 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 140-232 bad 19.9 current limiting fuse & 19.9 arrestor Released by crew 078S07///repairs made///complete BR
18450 | Pikeville | 3413402 | GARRETT | LACKEY | 2013-05-28 16:34 | 2013-05-28 19:25 | 1 | 171 | 4192121 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 1 MAN , 25KVA, TRUCK ACCESS AARON SANDERS TO HELP CHANGE CANNEED 1 MAN , 25KVA, TRUCK ACCESS . REPLACED TRANSFORMER, ALL WORK COMPLETE / GXJ VER/KEP IDC XXXX
18451 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-02-04 16:14 | 2011-02-04 19:05 | 1 | 171 | 54087-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38701339 // BAD CON. ON XFMR COD-1 ISO TF 37830482C00108 VER/HFP L3/HFP IDC XXXX
18452 | Whitesburg | 3312901 | JENKINS | KONA | 2011-04-27 17:07 | 2011-04-27 19:58 | 1 | 171 | 66512-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39732623 //BAD C/O, AT POLE 405-420, ISOLATED C/O RICK M. TO MAKE REPAIRS RELEASED BY CREW 075H01.. REPLACED CUTOUT RESTORED POWER AT 19:58 IDCC PN49 XXXX
18453 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-08-22 18:37 | 2020-08-22 21:28 | 1 | 171 | 4358741 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad conn. on pole only 1 cust. had trouble //
18454 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-11-10 09:39 | 2012-11-10 12:30 | 1 | 171 | 4378911 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAVE 3 PHASE SERVICE BURNED DOWN . WILLIREPLACE. METER # 436009535 WAS THE ONLY COUSTOMER OUT ///VER/CRB L/3 CRB IDC XXXX
18455 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-07-26 14:50 | 2009-07-26 17:41 | 1 | 171 | 52461-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TREE FELL AND TOOK SECONDARY AND SERVICE OUT WILL HAVE TO REPLACE.REPAIRED SERVICE AND SECONDARY AND RESTORED POWER. TIM MCCOY 7/26/9 RELEASED BY CREW 074H10 VER/KEP L3/KEP IDC XXXX
18456 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-01-29 23:14 | 2015-01-30 02:05 | 1 | 171 | 4974071 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WILL CHECK VOLTAGE & LOOK FOR PROBLEM.SERVICE NETURAL BURNED IN TWO AT SPLICE. WILL CHANGE SERVICE OUT. NEED 1 A LINEMAN VER/SEF L3/HFP
18457 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-06-10 14:54 | 2022-06-10 17:45 | 1 | 171 | 4054981 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva 7200 xfm. help on the way. restored 17:45
18458 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2014-01-11 23:39 | 2014-01-12 02:30 | 1 | 171 | 4274201 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.IN THE PROCESS OF CHANGING.CLIMBER.. VER/KEP L3/HFP
18459 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2018-03-26 14:00 | 2018-03-26 14:57 | 3 | 57 | 4117711 | 171 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr on pole 449-207 , made repairs restored power at 14:57// ISO 37830449A20207/ COD 3*** per servicer 3 meters on building/ maps doesnt show secondary or customers off of pole 37830449A20207
18460 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-12-04 22:59 | 2009-12-05 01:50 | 1 | 171 | 55140-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR BURNED UP WILL NEED MATERIAL HANDLER 15 KVA 19.9/120/240 & 2 MEN/ COD-1 / VER/LDA IDC XXXX
18461 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-08-18 08:09 | 2015-08-18 11:00 | 1 | 171 | 4146721 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE IS OUT ON POLE 37830020000009 WILL PATROL LINE. CLEARED ARRESTOR & REFUSED LINE// VER/ ADH
18462 | Pikeville | 3402002 | KEYSER | STONECOAL | 2019-02-28 22:23 | 2019-03-01 01:14 | 1 | 171 | 4940221 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT,WILL RE-FUSE////////XFR IS BAD,NEED 1 MAN,25 KVA 7.2 XFR,MATERIAL HANDLER///////////REPLACED BAD XFR&RESTORED
18463 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-08-06 07:39 | 2008-08-06 10:30 | 1 | 171 | 65857-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER SHAWN HAMMONS NEED TO REPLACE TRANSFORMER ON POLE 477-414 WHICH FEEDS WAL MARTS PARKING LOT LIGHTS..TRANSFORMER IS BAD.//CREW ON SITE AT 09:15//REPLACED TRANSFOMER FOUND BAD METER DAMAGED BY LIGHTING P R TOLLIVER REPLACED OLD MTR 534086797 WITH NEW MTR 190228756 RDG 00000 VER/HFP IDC XXXX
18464 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2009-07-09 11:53 | 2009-07-09 12:50 | 3 | 57 | 65522-1 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED CUTOUT DOOR//COD 3// VER/DBM IDC XXXX
18465 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-05-17 16:19 | 2016-05-17 19:10 | 1 | 171 | 4227251 | 171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT .CHANGING/ ISO 38830924000019/ COD 1/ VER/BOW
18466 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-04-19 06:10 | 2008-04-19 07:35 | 2 | 85 | 52258-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20-7096 CUTOUT DOOR BURNT UP 6T TRANS FUSE VER/LDA IDC XXXX
18467 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2022-10-26 11:10 | 2022-10-26 14:00 | 1 | 170 | 4067491 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crw required replaccred door
18468 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-12-09 10:05 | 2011-12-09 12:55 | 1 | 170 | 4164251 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | HAD SPLICE IN MIDDLE OF SERVICE BAD ///VER/CRB IDC XXXX
18469 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-03-23 09:15 | 2013-03-23 10:40 | 2 | 85 | 4949781 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD LINE FUSE CUTOUT ON POLE 1121-44, I HAVE IT CHANGED AND POWER IS RESTORED AT THIS LOC AT 1040//COD 2// VER/DBM IDC XXXX
18470 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-11-10 14:10 | 2013-11-10 15:35 | 2 | 85 | 4026261 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE////////RE-FUSED AND RESTORED,BELIEVE FUSE WAS DETERIORATED AS THIS XFR WAS RE-ENERGIZED RECENTLY AFTER BEING OFF-LINE FOR ABT 3 YRS//COD 2// VER/DBM
18471 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-08-25 10:43 | 2013-08-25 13:33 | 1 | 170 | 4705151 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT MAST REPLACE 3 CONNECTIONS AT MAST PIPE POWER OK VER/SEF IDC XXXX
18472 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-05-08 16:52 | 2010-05-08 19:42 | 1 | 170 | 58288-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE OUT. GOT BAD CUTOUT ON TRANSFOMER POLE. CALLED FOR HELP.//VER/CRB IDC XXXX
18473 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-04-30 08:54 | 2010-04-30 11:44 | 1 | 170 | 52999-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITED FUSE BURNT IN TWO. REPLACE FUSE VER/KEP L3/KEP IDC XXXX
18474 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-04-12 12:23 | 2019-04-12 13:48 | 2 | 85 | 4085931 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 120-143..19.9 xfm. cutout broken on pole 120-273..will need one man to help.. ON @ 1348
18475 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-06-17 12:10 | 2020-06-17 15:00 | 1 | 170 | 4034031 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfm. and cutout bad on pole 37830120D00237..replaced cutout 7200 and noticed pri. bushing is broke on 25kv xfm..will need replaced by crew truck access..feeds only one customer here and building is vacant.can replace @ later date..please send copy to PAUL KEESEE
18476 | Whitesburg | 3309302 | VICCO | JEFF | 2011-01-11 14:40 | 2011-01-11 17:30 | 1 | 170 | 60672-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY BROKE ON TRANSF POLE == CALLED FOR 1 MAN AND 6 WHEELER TO GET TO IT ==//COD 1// VER/DBM IDCC PN63 XXXX
18477 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-06-11 14:10 | 2021-06-11 15:35 | 2 | 85 | 4715661 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 37830246B00083. broke cut out at 246-131. restored power at 15:35 Released by crew 077S10
18478 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-02-10 19:45 | 2014-02-10 22:35 | 1 | 170 | 4371911 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TAPE WRAPPED AROUND ALL 3 CONDUCTORS IN A SPLICE CAUSING HEAT RETENTION MELTING INSULATION RESULTING IN A PHASE TO GROUND FAULT, BURNING THE SERVICE NEUTRAL DOWN.// VER/DBM
18479 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-11-13 11:35 | 2019-11-13 14:25 | 1 | 170 | 4030601 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad hot leg on a URD service, P.R. gonna get someone to help install add-a-phase until we can get this located. Got add-a-phase installed @1425, power restored.
18480 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-04-14 15:50 | 2008-04-14 18:40 | 1 | 170 | 51079-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN...REPLACED CUTOUT & ARRESTER, ALL WORK COMPLETE / GXJ // VER/TOM IDC XXXX
18481 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-01-26 13:00 | 2010-01-26 15:50 | 1 | 170 | 60087-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33603661 // VER/HFP L3/HFP IDC XXXX
18482 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2017-04-18 09:50 | 2017-04-18 11:15 | 2 | 85 | 4654091 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , I CHANGED IT OUT 37830449A41494 VER/AWD L3/HFP XXXHFP
18483 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-06-13 13:19 | 2017-06-13 16:09 | 1 | 170 | 4959011 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 2 CONNECTIONS BURNDT INTO @ THE METERING OFF OF TRANS. POLE 75-214, WILL HAVE TO OPEN THE BANK TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED THAT BANK @1530, MADE REPAIRS AND PUT BACK IN @1609. VER/CRB
18484 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-03-11 18:40 | 2008-03-11 21:30 | 1 | 170 | 56337-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON TRANSFORMER POLE.......DAH//3413402//VER/CRB IDC XXXX
18485 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-05-16 12:15 | 2012-05-16 15:05 | 1 | 170 | 4800461 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD NETURAL IN UNDER GROUND SERVICE, GOT PHILIP HICKS COMMING WITH LOCATOR FOR SERVICE RELEASED BY CREW 077S05//COD 1// VER/DBM IDCC TOF1018 ESTIMATED TIME OFF XXXX
18486 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-06-18 10:57 | 2018-06-18 13:47 | 1 | 170 | 4615881 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | B phase primary metering open @1057-A-262, checking. Lid was blowed off on B phase metering, bypassed metering and tagged to DDC, bypassed @1347, please send a copy to Tim Hall to get this changed out./ ISO 38821057A00262/ COD 1
18487 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2016-04-28 17:27 | 2016-04-28 18:01 | 5 | 34 | 4139411 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ON SITE///CHANGED CUTOUT--LF IN ON 44D3-7006 AT 18:01---TBL TKT COMP
18488 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-06-09 10:20 | 2015-06-09 11:45 | 2 | 85 | 4543291 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED WITH AN ETA OF 1100//BAD CUTOUT ON POLE 326C-108 , REPLACED CUTOUT . VER/CRB
18489 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2021-09-29 14:25 | 2021-09-29 17:15 | 1 | 170 | 4303001 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Replaced broken clamp on transformer riser. Power restored @ 17:15
18490 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-11-11 09:10 | 2012-11-11 12:00 | 1 | 170 | 4381411 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | I THINK WE HAVE A BAD UNDERGROUND SERVICE . I PUT IN TEMPORY OVERHEAD SERVICE , UNDERGROUND SERVICE WILL HAVE TO BE REPAIRED OR CHANGED OUT. SEND TO GLEN COMBS ///VER/CRB L/3 CRB IDC XXXX
18491 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-09-18 09:19 | 2009-09-18 12:09 | 1 | 170 | 50643-1 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST HAS PART POWER, CHECKING CONNECTIONS, REPLACED BAD CONNECTION ON XFMR POLE//VER/CRB IDC XXXX
18492 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-02-17 10:50 | 2013-02-17 13:40 | 1 | 170 | 4824891 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED SERVICE DROP, IT HAD SEVERAL BAD PLACES IN IT AND WAS NOT CARRYING FULL VOLTAGE. VER/KEP IDC XXXX
18493 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2022-04-06 11:45 | 2022-04-06 14:35 | 1 | 170 | 4730021 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | found faulty TR, changes out xfmr, all power restored @ 14:35 p.hicks
18494 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2016-11-11 14:01 | 2016-11-11 16:51 | 1 | 170 | 4093981 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED BROKEN # 4 SECONDARY NUETRAL ON 1113C186 CUSTOMER SAYS THEY HAVE DAMAGES IT IS PROBABLY 250 FT SPAN OF #4 TRIPLEX PLEASE SEND COPY TO ENGINEERING AND MAYBE SET A CLEARANCE POLE AND ALSO SEND COPY TO PEGGY WYNSONG//SENT ON VER/CRB
18495 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-06-23 13:00 | 2015-06-23 14:25 | 2 | 85 | 4644621 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT DUE TO BROKEN FUSE. REPLACED FUSE EVERYTHING OK/ ISO 38831098D00434/ COD 2/ VER/BOW
18496 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-01-04 19:22 | 2017-01-04 22:12 | 1 | 170 | 4270151 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS CUTOUT ON 32-C-126 FAILED I REPLACED CUTOUT RESTORED POWER AT 22:12/ ISO 37820032C00126/ COD 1/ VER/BOW
18497 | Whitesburg | 3401301 | FLEMING | NEON | 2014-11-22 09:08 | 2014-11-22 11:58 | 1 | 170 | 4753401 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE HOT LEG OF SERVICE IS BURNT IN TO ON POLE 332-57. GOING TO CLIMB POLE AND REPAIR. FULL POWER RESTORED AT 11:58. 11/22/2014 VER/TOM L3/TOM
18498 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2020-03-22 09:42 | 2020-03-22 11:07 | 2 | 85 | 4500511 | 170 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | changed 2 cutouts & arrestor all power restored. pls close tre
18499 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2011-12-27 18:00 | 2011-12-27 18:34 | 5 | 34 | 4207521 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 139-238. HAD TRANSFORMER OPEN FROM 18:00 TO 18:34. CHANGED CUTOUT EVERYTHING OK. SEND COPY TO ENG PIKEVILLE POLE HAS A PLACE BURNT BACK IN IT.//ISO//FEEDER 3403202//COD 5//EMAILED TO TECH// VER/DBM IDC XXXX
18500 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-02-07 10:18 | 2018-02-07 11:43 | 2 | 85 | 4811711 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t xfmer fuse restored 11:43 pls close. thanks, tre.
18501 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-08-22 18:39 | 2010-08-22 18:56 | 10 | 17 | H59326-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP BURNT OPEN ON 954-86 - XFMRS UP TO AND INCLUDING 86 HAVE NOT BEEN OUT. OPENED FUSE ON 954-83 @ 18:39 TO MAKE REPAIRS. REPAIRS COMPLETE. CLOSED FUSE ON 954-83 @ 18:56 RESTORING ALL CUSTOMERS. SH//VER/CRB IDCC DUP TO OPEN FUSE XXXX
18502 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2009-06-03 13:53 | 2009-06-03 16:43 | 1 | 170 | 50542-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3309902// CONNECTION BAD ON SECONDARY POLE == REWORKED CONNECTION === POWER OK == IDC XXXX
18503 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-03-03 09:40 | 2011-03-03 12:30 | 1 | 170 | 66068-1 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMER CREW ENROUTE TO CHANGEBAD 5 KVA TRANSFORMER, CREW ENROUTE.BAD 5 KVA TRANSFORMER, CREW ENROUTE. TRANSFORMER CHANGED, POWER NOT RESTORED, CUST, HAS TO MAKE SOME REPAIRS, WILL CALL WHEN READY. INSP REQUIRED VER/KEP IDC XXXX
18504 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-01-21 20:10 | 2019-01-21 23:00 | 1 | 170 | 4701661 | 170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | serve end pulled loose creating open neutral on service drop.. removed serve ends and replaced them with 506 connections.//cod 1 L3/HFP
18505 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-02-28 21:18 | 2022-03-01 00:07 | 1 | 169 | 4554361 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv cut out. line crew. trk maybe Released by crew 078S07 crew on site FETR 00:30LRM
18506 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2012-10-16 12:11 | 2012-10-16 15:00 | 1 | 169 | 4145801 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | <<ONLY ONE CUSTOMER AFFECTED>> BAD 4/0 TO #6 CU CONNECTION ON 978-248. REPAIRING. REPAIRED CONNECTION AND RESTORED BUT CUSTOMERS MAIN BREAKER STUCK OPEN WHEN SHE ATTEMPTED TO RESET IT WHEN THE OUTAGE FIRST OCCURRED. LEFT METER DISCONNECTED AND ADVISED CUSTOMER TO CALL BACK AFTER ELECTRICIAN MAKES REPAIRS. SH VER/KEP IDC XXXX
18507 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-03-06 00:38 | 2019-03-06 03:27 | 1 | 169 | 4955081 | 169 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | customer said large appliances will not run, has gas fireplace but it is small and not enough to heat house until morning//advised cust to turn off main breaker to avoid damage to customer equipment//. bad servends in 1/0 service drop 1 had burnt completly off. cut them out and made new connections everything ok L3/HFP
18508 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-02-13 10:31 | 2014-02-13 13:20 | 1 | 169 | 4381771 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE ON 881-187 (CUSTOMERS DAUGHTERS HOUSE) APPEARS TO HAVE BROKEN OR MELTED OUT. RESTORED @ 13:20. SH VER/HFP L3/HFP
18509 | Paintsville | 3409302 | KENWOOD | AUXIER | 2020-03-21 12:26 | 2020-03-21 14:53 | 3 | 147 | 4499681 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Door in xfmr cutout has burnt up. I will replace cutout. Opened L/F @ 14:42 to safely replace C/O. Made repairs and restored all customers @ 14:53
18510 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-04-19 07:56 | 2018-04-19 10:45 | 1 | 169 | 4254421 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on transformer cod 1 iso 37830247B00573
18511 | Whitesburg | 3312902 | JENKINS | JENKINS | 2010-05-11 13:29 | 2010-05-11 16:18 | 1 | 169 | 59545-1 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONE PHASE IS OUT ON SECONDARY SIDE I COULD NOT GET DOOR OPENED ON THE PRIMARY SIDE OF TRANSFORMER TO CHK PLEASE SEND THIS TO CECIL SEXTON REPLACED CUTOUT /// COD-1 VER/HFP L3/HFP IDCC CDC83 XXXX
18512 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-01-04 23:09 | 2011-01-05 01:58 | 1 | 169 | 58751-1 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOKS LIKE CUST SERVICE DORP IS JUST ABOUT BURNT INTO. I WILL HAVE TO CHANGE OUT. I CHANGED OUT 4/3 DROP AND PUT 2/3 DROP IN .THIS WAS A 200AMP METER BASE. I INSTALLED METER AND KNOCKED ON DOOR TO CHECK WITH CUST NO ONE COME TO DOOR LIGHTS AND HEAT PUMP WERE ON. SEND COPY OF THIS TO PEGGY WYSONG CUST COULD HAVE DAMAGE. 4/3 DROP BURNT ONE HOT SIDE AND NEUTRAL INTO ABOUT 5 FOOT FROM POLE IN SPLICE. //VER/GAH IDCC CNT4, FEC57 XXXX
18513 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-06-09 13:31 | 2011-06-09 16:20 | 1 | 169 | 4275341 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED, BAD 37.5 CSP, NEED 37.5 7200 XFMR, CUTOUT, BRACKET, TRUCK OK. SEVERAL INACTIVE SERVICES, COULD POSSIBLY GO BACK WITH SMALLER XFMR. SEND TO B FRALEY. RELEASED BY CREW 078S05/VER/CRB IDC XXXX
18514 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-12-10 14:09 | 2019-12-10 16:58 | 1 | 169 | 4142191 | 169 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | had splice froze out in service
18515 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2014-04-28 18:48 | 2014-04-28 21:37 | 1 | 169 | 4643641 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ POLE 207-103 NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05//CREW ON SITE//REPLACED XFMR CUTOUT AND ARRESTOR///PWR RESTORED 21:37//TBL TKT COMPLETED VER/CRB
18516 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-05-24 12:51 | 2011-05-24 15:40 | 1 | 169 | 4158931 | 169 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 40093464 // ONE LEG OF UNDERGROUND BAD NEED CREW TO BRING ADD-A-PHASE TO HOOK UP TO RESTORE FULL POWER ELLINGTON RUN CT. AT MIDDLE OF HILL DRIVEWAY TO THE RIGHT BROWN A FRAME HOUSE 720 RELEASED BY CREW 078H18ONE LEG OF UNDERGROUND BAD NEED CREW TO BRING ADD-A-PHASE TO HOOK UP TO RESTORE FULL POWER ELLINGTON RUN CT. AT MIDDLE OF HILL DRIVEWAY TO THE RIGHT BROWN A FRAME HOUSE 720 RELEASED BY CREW 078H18/CREW ON SITE OPENED XFMER TO INSTALL ADD-A-PHASEONE LEG OF UNDERGROUND BAD VER/HFP L3/HF
18517 | Hazard | 3302703 | HAZARD | HAZARD | 2019-09-29 21:36 | 2019-09-30 00:25 | 1 | 169 | 4072911 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr opened xfmr 23:33 closed at 00:25
18518 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-01-30 10:36 | 2013-01-30 13:25 | 1 | 169 | 4756831 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP HAD BURNED OFF LINE CUTOUT THAT SERVED BANK OF TRANSFORMERS AT POLE 190-427. I AM GOING TO REPLACE HOT TAP. I REPLACED HOT TAP ON POLE 190-427. COD-AT LEAST 1 (0 PER POWERON) ISO PO @ 37830190D30427 VER/HFP L3/HFP IDC XXXX
18519 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-06-18 09:11 | 2018-06-18 11:15 | 2 | 124 | 4615291 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | service has burn into.open trans on pole 853-19 @ 1030 (1cc) to make repairs.repairs make.trans on at 11:15/ ISO 38830853000057/ COD 2
18520 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-05-15 13:51 | 2018-05-15 16:40 | 1 | 169 | 4352211 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cut arrestor in clear,
18521 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-08-21 13:31 | 2019-08-21 16:20 | 1 | 169 | 4921341 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | bad current limiting fuse on xfmr pole 503a3-78 all pwr restored @ 16:20 please close ticket LRM
18522 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-06-13 13:56 | 2010-06-13 16:45 | 1 | 169 | 62789-1 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR OPENED UP//// BAD 10KVA CSP XFMR. NEED XFMR, C/O AND BRACKET, LONG BRIDGE TO CROSS NOT SURE WE CAN TAKE BIG TRUCKS OVER THERE. RELEASED BY CREW 077S08 CHANGED TRANSFORMER JKC//COD 1// VER/DBM
18523 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-07-28 15:28 | 2015-07-28 18:17 | 1 | 169 | 4952501 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT ON POLE#522-85 FAILED/FUSE NOT ON MAP/SERVICER TO CHG CUTOUT/FETR1830/VEM/OPEN XFMR @522-85 AT 1753/REPAIRS MADE AND ALL CUST RESTORED 1817/NOTE TO MAPPING 10T LINE FUSE FEEDING 522-118/PLEASE CLOSE TICKET/THANKS/VEM// VER/ ADH
18524 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-03-31 10:56 | 2021-03-31 13:45 | 1 | 169 | 4407151 | 169 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad service splice at pole. Repairs made
18525 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-06-23 23:44 | 2015-06-24 02:33 | 1 | 169 | 4648591 | 169 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 HOT LEG AND NEUTRAL BURNT INTO IN SERVICE WILL REPAIR/// REPAIRED BROKEN CONDUCTORS AND RESTORED SERVICE @ 2:33/// ONLY 1 CUSTOMER AFFECTED VER/KEP
18526 | Pikeville | 3402002 | KEYSER | STONECOAL | 2020-08-11 09:11 | 2020-08-11 12:00 | 1 | 169 | 4309221 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad splice.. will be changing service drop out to #2.. customer is restored
18527 | Hazard | 3303901 | LESLIE | HYDEN | 2022-08-12 20:12 | 2022-08-12 20:25 | 13 | 13 | 4734711 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary and neutral sagging low at pole # 314-25 to pole # 314-27, re-sagged wire. Opened line fuse at pole # 314-25 at 20:12, closed back in at 20:25.//NO OUTAGE TILL L/F OPENED @ 2012
18528 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-12-20 20:44 | 2012-12-20 20:57 | 13 | 13 | 4490681 | 169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON TRANSFORMER AND CUTOUT IS LAYING ON GUY WIRE, GOING TO OPEN UP LINE FUSE TO CHANGE CUTOOUT BECAUSE OF A FLASH OPEN LINE FUSE ON POLE 29-70 AT 2044 AND CLOSED AT 2057 FUSE HAD 13 CC FOR HOIS. VER/PDP
18529 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-03-24 18:48 | 2020-03-24 19:30 | 4 | 42 | 4506941 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | lightning arrrestor when bad on the transformer, have cut in the clear, power restored at this loc at 1930
18530 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-10-08 11:27 | 2018-10-08 12:09 | 4 | 42 | 4207191 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Released by crew 078S07/this is an on going power quality issue/spoke with cust/will be doing some trouble shooting/vem/will need to open xfmr aprox one hour outage/vem/opened xfmr 1127/restored 1209/please close tickrt/thanks/vem L3/HFP
18531 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-05-08 13:32 | 2013-05-08 16:20 | 1 | 168 | 4086811 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONLY ONE CUSTOMER AFFECTED HERE..ONE LEG OF UNDERGROUND SERVICE BAD.ADDED ADD-A-PHASE FOR TEMPORARY SERVICE.TOOK TRANSFORMER OFF AT 15:56 AND BACK ON AT 16:20.WILL MAKE REPAIRS TOMORROW. ///VER/CRB L/3 CRB IDCC TOF1556, CNT4, MCCDL XXXX
18532 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-07-18 13:57 | 2011-07-18 16:45 | 1 | 168 | 4558761 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED BIG BUCKET-ONE MAN AND 7200 CUTOUT--HELP IS ON THE WAY//COD 1// VER/DBM
18533 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-08-03 14:14 | 2014-08-03 15:10 | 3 | 56 | 4327691 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED INTO AND CUTOUT MAY BE DAMAGED. I AM GOING TO TRY TO REFUSE CUTOUT. I JUST HAD TO CHANGE CUTOUT DOOR. VER/CRB
18534 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-12-06 10:31 | 2022-12-06 11:55 | 2 | 84 | 4233381 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 19.9 cutout on pole 1064-95 . power restored @ 11:55
18535 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-03-09 09:12 | 2008-03-09 12:00 | 1 | 168 | 55629-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308502//SERV BURNED DOWN == REPAIRED SERV == MADE A IO ORDER TO REPLACE SERV WITH 4/0 LATER ==// VER/DBM IDC XXXX
18536 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-10-12 15:31 | 2014-10-12 16:55 | 2 | 84 | 4609231 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SINGLE TRANS, BROKEN FUSE LINK REPAIRED AND POWER RESTORED KWB COD-2 ISO TF 38830018000163 VER/HFP L3/HFP
18537 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-01-18 22:09 | 2022-01-18 23:05 | 3 | 56 | 4383901 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse out on pole 37830472000180. Power restored at 23:05./ ISO 37830472000180/ COD 3
18538 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2012-07-30 13:27 | 2012-07-30 16:15 | 1 | 168 | 4865691 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON TRANSF BURNED OFF == REPLACED SERV == POWER OK COD-1 ISO TF 37830419D00108 VER/HFP L3/HFP
18539 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-03-19 08:35 | 2013-03-19 09:31 | 3 | 56 | H4917761 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER AFTER HOURS DISPATCH GUIDE LINES WILL BE CHECKED THE MORNING OF 03/19/13 // BROKEN CUTOUT// COD-4 OPENED LINE FUSE ON 91-309 AT 0835 CLOSED AT 0931 COD-3 VER/KEP IDC XXXX
18540 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-05-14 10:10 | 2013-05-14 10:52 | 4 | 42 | 4111981 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER BURNED NEUTRAL INTO. I REPLACED SERVICE DROP. ///VER/CRB L/3 CRB IDCC TOF 0905 ESTIMATED TIME OFF FOR REPAIR XXXX
18541 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-12-13 15:02 | 2009-12-13 17:50 | 1 | 168 | 52408-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV BURN INTO ABOUT 2 FT FROM TRANSF == 2/3 SEVR REPLACED WITH 1/0 SERV == UNKNOWN == POWER CHECKED OK == NEUT BURNED == VER/KEP L3/KEP
18542 | Pikeville | 3402003 | KEYSER | MULLINS | 2016-01-11 19:04 | 2016-01-11 21:52 | 1 | 168 | 4608061 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SECONDARY CONNECTION ON TRANS 1103-17 CLIMBED POLE REMADE CONNECTION/ ISO 38831103000017/ COD 1/ VER/BOW
18543 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2011-06-18 14:35 | 2011-06-18 14:56 | 8 | 21 | 4337821 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | HAD TO OPEN UP CSP TRANSFORMER AT 1435, TO CHECK EVERYTHING, DID NOT FIND ANYTHING LOOSE OR THAT WAS FLASHED OVER, DID HAVE A VERI STAR ARRESTOR ON THE SIDE OF TANK, I CUT IT IN THE CLEAR, HOPEFULLY THAT WAS IT, ALSO CHECK POLE TOP INS, SEEM TO BE OK, ALSO COD-8 ISO 39830901C35010 VER/HFP L3/HFP
18544 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2009-05-27 15:09 | 2009-05-27 17:57 | 1 | 168 | 56824-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 30002840 //MAYBE ABLE TO LOWER PHASES POLETOP BURNT NO TRUCKS WILL NEED MANUAL TREE CREW IF THEY DECIDE TO LOWER PHASES RELEASED BY CREW 078S11/ HILL SIDE WORK NEED TO SEND NOTE TO MARTIN TO WRITE JOB TO CHANGE POLE WITH TRACK DIGGER AND BUCKET/ POLE 66-15 AND 66-16 NEEDS CHANGED DUE TO POLE FIRE BOTH POLES SAFE FOR NOW COD=1 ISO 38830066000015 L3/HFP IDC XXXX
18545 | Paintsville | 3401101 | FALCON | FALC-OILS | 2021-04-30 14:24 | 2021-04-30 15:20 | 3 | 56 | 4503251 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Splice had pulled out insecondary & service neutral causing flickering lights. I opened xfmr @ 14:24 to make repairs/// Repaired conductor and restored @ 15:20
18546 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2018-03-28 16:08 | 2018-03-28 18:56 | 1 | 168 | 4140891 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SPLICE IN SD
18547 | Hazard | 3301401 | COMBS | COMBS | 2011-03-05 13:18 | 2011-03-05 14:00 | 4 | 42 | 50074-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39051199 // BAD CUTOUT // COD-4 ISO TF 37830271C00110 VER/HFP L3/HFP IDC XXXX
18548 | Whitesburg | 3314401 | MAYKING | ERMINE | 2011-04-06 19:48 | 2011-04-06 21:12 | 2 | 84 | 51044-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39469933 // BAD CUTOUT ...MADE REPAIRS RESTORED POWER AT 21:12 // COD-2 ISO TF 37830450B00110 VER/HFP L3/HFP IDC XXXX
18549 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-04-29 11:16 | 2009-04-29 12:40 | 2 | 84 | 57760-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE #205-532, 2 CUST OUT//MD FILED ON INCORRECT PLACEMENT OF FUSE//ISO 37830205D10532//COD 2// VER/DBM IDC XXXX
18550 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-08-11 16:06 | 2009-08-11 17:30 | 2 | 84 | 55009-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP 1.6 FUSE BROKE.....DAH COD-2 ISO TF 37820098C00227 L3/HFP IDC XXXX
18551 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-07-06 12:06 | 2009-07-06 14:54 | 1 | 168 | 52843-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | VER/HFP OPEN 3 DISC ON PRIMARY METER POLE 1052-311 ONE CT;S BAD, BLEW LINE FUSE ON POLE 1053-8 65T ...ENTERED MD...HFP L3/HFP IDC XXXX
18552 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-06-18 08:57 | 2018-06-18 11:45 | 1 | 168 | 4615201 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew requiredbad connection/ ISO 38830247A30375/ COD 1
18553 | Pikeville | 3403001 | PIKEVILLE | CITY | 2013-07-20 08:12 | 2013-07-20 11:00 | 1 | 168 | 4560781 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | APPARENTLY THE PRIMARY HERE WAS DOWN A FEW DAYS AGE DUE TO A TREE FALLING. I BELIEVE THAT THE SERVICE NEUTRAL HERE PULLED OUT OF A SLEEVE WHEN THAT HAPPENED. ONLY ONE CUSTOMER AFFECTED. VER/CRB L/3 CRB
18554 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-07-27 22:27 | 2012-07-28 01:15 | 1 | 168 | 4854101 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CUST HAD FULL POWER,,FUSE MELTED OUT BUT WAS CARRYING LOAD THROUGH DOOR,,REFUSED POWER BACK ON//DALE SHOULD THIS BE "NO INTERRUPTION" ?// VER/DBM
18555 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-01-25 15:12 | 2016-01-25 16:36 | 2 | 84 | 4649621 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS AT THE TRANSFORMER// VER/ ADH
18556 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2016-11-05 20:34 | 2016-11-05 21:30 | 3 | 56 | 4078951 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED THE TRANSFORMER FUSE THAT BROKE. ONLY ONE CUSTOMER WAS OFF.//COD 1//
18557 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-03-11 12:55 | 2015-03-11 13:19 | 7 | 24 | 4182861 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | NEEDS NEW ANCHOR OLD ANCHOR RUSTED INTO; CREW ON SITE; WILL HAVE TO OPEN XMFER TO STRAIGHTEN POLE HAND DIGGING NEW ANCHOR; OFF AT 12:55; ON AT 13:19 VER/KEP L3/DKGXXXX
18558 | Hazard | 3303902 | LESLIE | WOOTON | 2015-07-09 09:34 | 2015-07-09 10:30 | 3 | 56 | 4749801 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7.2 KV CUTOUT VER/CRB
18559 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-02-11 01:29 | 2016-02-11 02:25 | 3 | 56 | 4688411 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN TO ISOLATE ARCING CUTOUT - ASSOCIATED WITH 4688381//TOM OPEN @ 0129// CLOSED @0225//TOM VER/TOM L3/TOM
18560 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-11-18 12:59 | 2008-11-18 15:47 | 1 | 168 | 66241-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP STS WR# 27340328 // PLEASE DONT FORGET THE FETR...THANKS IDC XXXX
18561 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-08-25 16:09 | 2012-08-25 17:05 | 3 | 56 | 4971671 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// WILL REFUSE/// FUSE LINK APPEARED TO HAVE BROKEN// REFUSED // POWER IS RESTORED//COD 3// VER/DBM IDC XXXX
18562 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-08-06 15:57 | 2014-08-06 18:45 | 1 | 168 | 4337201 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT ON TRANSFORMER RELEASED BY CREW 077S05 // COD-1 ISO TF 37830030000027 VER/HFP L3/HFP
18563 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-10-27 09:03 | 2018-10-27 10:27 | 2 | 84 | 4331871 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Changing broke cutout, replaced cutout, apr at 1027 close ticket L3/HFP
18564 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-09-07 08:17 | 2013-09-07 09:41 | 2 | 84 | 4826991 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT SERV TO TRY,BAD CUT OUT SERV TO CHANGE,FUSE IN@0941 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/KEP
18565 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2010-11-26 10:54 | 2010-11-26 11:36 | 4 | 42 | H59709-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HARVEY MARTIN ENROUTE TO ASSIST GREG.NEED 25KVA 7.2KV 120/240, LINE TRUCK , 3 MEN... NO TRUCK ACCESS RELEASED BY CREW 074S03//WR#37888713// TOOK TAP OFF AT 10:54 ALL BACK ON AT 11:36 D SAMMONS//VER/CRB IDCC DUP TO OPEN TAP XXXX
18566 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2021-05-29 10:12 | 2021-05-29 13:00 | 1 | 168 | 4646041 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1ST XFR ON LFT@MOUTH OF HOLLOW.HAVE CUT LIMBS AWAY TWICE.XFR MUST HAVE SOMETHING WRONG WITH IT.NEED 25 19.9&MATERIAL BUCKET Released by crew 074S06// replaced xfmr and c/o// repairs made at 13:00
18567 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2021-08-25 18:45 | 2021-08-25 21:33 | 1 | 168 | 4153371 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ::RESET BREAKERS DOG:Directions-N ON 119 TO JUNCT 3154 AT CANADA//TURN RT ON GOMIE THACKER 6063534055//cust service had one hot lead and neutral broke mid span..made repairs and got cust back in proper service
18568 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2016-01-18 09:42 | 2016-01-18 12:30 | 1 | 168 | 4628041 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ****SEE H4628041*** PRIMARY HAS PULLED OUT OF A SLEEVE AT POLE 38820987A00045.(1 CUST)/ ALSO PRIMARY IS HOT UP TO THIS POLE AND WILL NEED TO OPEN FUSE AT POLE 38820987A00033 (6 CUST) TO MAKE REPAIRS. LINE CREW IS EN-ROUTE./ OPENED LINE FUSE 38820987A00033 @ 1158 TO 1230/ ISO 38820987A00033/ COD7/// DUPLICATE IN HOIS/ VER/BOW
18569 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-12-01 13:15 | 2018-12-01 14:39 | 2 | 84 | 4497081 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | cutout door failed on pole 71-159..replaced..restored L3/HFP
18570 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2015-07-08 12:36 | 2015-07-08 14:00 | 2 | 84 | 4745731 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT UP CUTOUT DOOR. VER/CRB
18571 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-10-09 17:21 | 2015-10-09 18:45 | 2 | 84 | 4333981 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O ON POLE 447-13, WILL BE CHANGING. CHANGED C/O, CLOSED BACK IN AT 1845. VER/CRB L3/HFP XXXHFP
18572 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-06-10 09:32 | 2011-06-10 12:20 | 1 | 168 | 4283111 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD WILL CHANGE ALSO CUST. HAS A BAD BREAKER// CHANGED C/O //ALSO LEFT CUST. DISC. UNTIL REPAIRS ARE MADE VER/KEP IDC XXXX
18573 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-05-30 14:52 | 2011-05-30 17:40 | 1 | 168 | 4210351 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | # 4 SER. DROP HAS BURNED DOWN// IM GOING TO REPLACE WITH #2 SER.// CREW ON THE WAY//REPLACED S/D ALL BACK TO NORMAL//VER/CRB IDC XXXX
18574 | Pikeville | 3402003 | KEYSER | MULLINS | 2019-04-24 14:30 | 2019-04-24 17:18 | 1 | 168 | 4154531 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200 trans. on pole 1127-A-393, will need 2 men with material handler and a cutout w/ fiberglass bracket. Joey Reed coming to make repairs. Released by crew 074S05..made repairs ON @ 1718
18575 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-12-17 07:04 | 2009-12-17 09:52 | 1 | 168 | 51400-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION IN MID SPAN OF SERVICE, GOT FRANK HURLEY COMMING TO HEIP. GOING TO CLIMB POLE AND LET FRANK FIX SERVICE AND PULL IT BACK UP TO ME VER/HFP L3/HFP
18576 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-02-04 15:59 | 2018-02-04 17:23 | 2 | 84 | 4803031 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse link broken, refused xfmr, ALL WORK COMPLETE / GXJ
18577 | South Williamson | 3411401 | DEWEY | INEZ | 2021-05-27 16:01 | 2021-05-27 17:25 | 2 | 84 | 4633131 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfmr cutout//repairs made//restored at 17:25//complete//em
18578 | Cannonsburg | 3001401 | LOUISA | CITY | 2020-01-24 10:42 | 2020-01-24 13:30 | 1 | 168 | 4334881 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Only one customer affected. replaced service drop. and trimmed tree. apr at 1330 close ticket
18579 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-09-03 16:12 | 2017-09-03 19:00 | 1 | 168 | 4327331 | 168 | PARTIAL POWER | EQUIPMENT FAILURE | POLE HARDWARE | CALLED CUSTOMER NO ANSWER/////XFR F OUT ON DELTA XFR BANK,NEED BIG BUCKET,1 A LINEMAN//////IS UP ON HILL,CANT REACH////////RE-FUSED&RESTORED,POSSIBLY A BIRD GUARD DETERIORATED AND BLEW FUSE.PIECES LAYING AROUND SEVERAL PLACES/ ISO 38821082000203/ COD 1/ VER/BOW
18580 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-12-28 12:39 | 2011-12-28 15:27 | 1 | 168 | 4211191 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEND THIS TO TIM HALL. HE SAID SOMEONE WILL CHANGE THIS FRIDAY MORNING. CUSTOMER SAID THIS WAS FINE. TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. IS BAD. IT IS A 25 KVA, CONVENTIONAL, 12KV TRANS. ON POLE 80-1. TRUCK ACCESSIBLE. POLE IS 12 STEPS FROM BLACTOP. ALSO NEED NEW CUTOUT , ARRESTER, AND FIBER GLASS BRACKET. RELEASED BY CREW 074S01 VER/KEP IDC XXXX
18581 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-01-08 11:02 | 2015-01-08 13:50 | 1 | 168 | 4919591 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER OPENING TRANSFORMER FUSE 38830115C00493/POLE 115-493 BAD 19.9 25KVA XFMER. RELEASED BY CREW 078H12,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED// COD 1/MADE MAP DESPREANCY/ADH// VER/ ADH
18582 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-03-03 16:55 | 2017-03-03 19:43 | 1 | 168 | 4515991 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 279-97 LINE FUSE CUTOUT BROKE,CREW ON SITE REPLACING,,,CUTOUT REPLACED COMPLETE
18583 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-04-10 14:59 | 2009-04-10 16:23 | 2 | 84 | 51100-1 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008702//BAD XFMR CUTOUT DOOR/FETR1649/VEM/REPLACED XFMR DOOR /POWER RESTORED 1623/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDCC FEC49 XXXX
18584 | Hazard | 3303902 | LESLIE | WOOTON | 2018-01-11 23:28 | 2018-01-12 00:52 | 2 | 84 | 4732541 | 168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrester on xfmr cut in clear truck acess big bucket
18585 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2012-08-27 14:38 | 2012-08-27 17:25 | 1 | 167 | 4977031 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTORS BAD ON BOTH HOT LEGS OF LASH CABLE FEEDING OFF XFMR..ONE BURNT UP.THE OTHER ONE CAME LOOSE..//..REPLACED BOTH WITH BETTER CONNECTORS..JRV..08/27/12 VER/HFP L3/HFP IDC XXXX
18586 | Hazard | 3309003 | JEFF | VIPER | 2019-02-13 16:23 | 2019-02-13 19:10 | 1 | 167 | 4791951 | 167 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Split bolt went bad reworked conns.
18587 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-03-10 12:26 | 2008-03-10 15:13 | 1 | 167 | 55893-1 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN ABT 3-4 POLES UP HOLLOW.NEED #2,RIDGE-PIN & INS,CHAINSAW,TIE WIRES.POSSIBLY SEVERAL POLES TO WORK(2 SETS TOOLS)OPEN @ 934-9,DOWN @ 934-20 RELEASED BY CREW 074S06 /// SENT EMAIL TO DENNIS MASSEY & TIM HALL CUSTOMER AGREED TO WAIT UNTIL 03/11/08 TERRY TALKED TO DENNIS ABOUT THIS..HFP VER/HFP IDC CHANGED FROM NO INTERRUPTION AEP EQUIPMENT XXXX
18588 | Hazard | 3310502 | HADDIX | CANOE | 2008-02-03 07:13 | 2008-02-03 10:00 | 1 | 167 | 65808-1 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3310502// SERVICE BURNT DOWN, REPLACED SERVICE/ ONLY 1 CUSTOMER OUT - FUSE WAS NO OUT// ISO/FLT - 37830073000116 - COD 1//// VER/TOM IDCC CNT2 XXXX
18589 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-06-15 11:23 | 2011-06-15 14:10 | 1 | 167 | 4320931 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 1// VER/DBM
18590 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2011-09-16 06:05 | 2011-09-16 08:52 | 1 | 167 | 4875761 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CUSTOMER WAS PART OF OUTAGE THAT WAS RESTORED @ 0510 - WILL HAVE SERVICER CHECK AT REGULAR START TIME /// XFMR FUSE BLOWN// FUSE LINK APPEARED TO HAVE BROKE// REFUSED// POWER IS RESTORED //VER/CRB IDC XXXX
18591 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-07-29 08:58 | 2016-07-29 11:45 | 1 | 167 | 4706971 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV CO ON ARM. CREW REQD. B. TACKETT RELEASED BY CREW 078S07,,CREW ON SITE,,REPLACED CUTOUTS,,ALL POWER RESTORED/ ISO 38830094A31012/ COD 1/ VER/BOW
18592 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-11-02 15:58 | 2020-11-02 17:15 | 16 | 77 | 4635691 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection & wire burnt up. repairs made. opened xfmer @ 17:09 closed in @ 17:15. pls close. tre
18593 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2016-04-07 07:40 | 2016-04-07 10:27 | 1 | 167 | 4062481 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | POLE 68-1217 CROSSARM BURNT OFF OPENED 3-100T LINE FUSES ON POLE 68-325 08:20 AM SEND TO RON VIRGIN RELEASED BY CREW 078S08---CREW ON SITE--TAGD AND GNDS AT LOCATION TO CREW--CHANGED 2 SETS OF CROSSARMS---REENERGIZED AT 10:27--VOLT CK GOOD---TBL TKT COMP--RMV VER/CRB
18594 | Hazard | 3310502 | HADDIX | CANOE | 2022-10-30 08:28 | 2022-10-30 11:15 | 1 | 167 | 4078141 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke 19/9 cutout... replaced.
18595 | Hazard | 3303901 | LESLIE | HYDEN | 2017-04-26 10:18 | 2017-04-26 13:05 | 1 | 167 | 4683841 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 340-104 . BAD CUTOUT -15KVA 7200 37830340000011. MD ENTERED. 37830340000104LINE FUSE OUT ON POLE 340-104 . BAD CUTOUT ON POLE 340-11 . REPLACED CUTOUT . VER/AWD L3/HFP XXXHFP
18596 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2019-05-26 09:13 | 2019-05-26 12:00 | 1 | 167 | 4335861 | 167 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at transformer
18597 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-03-23 09:33 | 2021-03-23 12:20 | 1 | 167 | 4365041 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | hot tap lifted at 38830379000126. tap energized up to xfmr on 379/142 failed cutout (1 CC)
18598 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-12-31 11:58 | 2019-12-31 14:45 | 1 | 167 | 4199561 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad con on sec--repaire allgood-ds123119
18599 | Pikeville | 3421001 | BREAKS | CITY | 2011-01-05 09:43 | 2011-01-05 12:30 | 1 | 167 | 58862-1 | 167 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUSTOMER AFFECTED. THE SERVICE DROP BURNED APART IN A SPLICE. I MADE REPAIRS. VER/HFP L3/HFP IDC XXXX
18600 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-01-01 11:13 | 2014-01-01 14:00 | 1 | 167 | 4216911 | 167 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEM// WILL NEED TO REPAIR SD // REPAIRS MADE VER/SEF
18601 | Hazard | 3303901 | LESLIE | HYDEN | 2015-03-10 07:28 | 2015-03-10 10:15 | 1 | 167 | 4175291 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASES OUT INITALLY - 4 CUST OUTREPLACED BAD 19.9 CUTOUT ON CROSSARM COD-4 ISO LF 37830388B00368
18602 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-08-04 15:43 | 2011-08-04 18:30 | 1 | 167 | 4665081 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER SINGLE PHASEING CHECKING CONNECTIONS FOUND 3 BAD CONNECTION REPLACED CONNECTION//COD 1// VER/DBM IDC XXXX
18603 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2013-01-26 09:48 | 2013-01-26 12:35 | 1 | 167 | 4742481 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BROKE AT BAD SPLICE DUE TO TREE IN SERVIC DROP//THERE IS A 100 AMP METER BASE// ALSO EDDIE REQUESTED CLIFF FREEMAN BE NOTIFIED OF NEEDING A SECONDARY POLE SET// VER/TOM L3/TOM IDC XXXX
18604 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-03-30 10:13 | 2009-03-30 13:00 | 1 | 167 | 62967-1 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUT BAD ARRESTER IN CLEAR.//COD 1// VER/DBM IDC XXXX
18605 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-11-06 11:35 | 2015-11-06 14:22 | 1 | 167 | 4415241 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT, NO TRUCK ACCESS. TIM HALL IS GETTING ME SOME HELP TO REPLACE IT. POWER RESTORED AT 14:22. VER/CRB
18606 | Hazard | 3309301 | VICCO | REDFOX | 2012-09-24 08:18 | 2012-09-24 11:05 | 1 | 167 | 4081491 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SMALL SERVICE HAS BURNT DOWN, WILL REPLACE WITH 2/3 TWIST ///VER/CRB L/3 CRB IDC XXXX
18607 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-08-03 17:27 | 2021-08-03 20:14 | 1 | 167 | 4998951 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | bad fuse cell. restored
18608 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-10-23 12:13 | 2019-10-23 15:00 | 1 | 167 | 4188731 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | will replace broken cutout
18609 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-08-04 11:23 | 2021-08-04 14:10 | 1 | 167 | 4003111 | 167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 7200 cutout, pole 68-916. Crew required, no truck. Released by crew 078S02 crew on site going to lift hot tap on pole 68-915 tag and ground to myself all pwr restored @ 14:10 please close ticket LRM
18610 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-11-21 08:23 | 2011-11-21 11:10 | 1 | 167 | 4096221 | 167 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION AT WEATHERHEAD, ALL REPAIRS MADE.// VER/DBM IDC XXXX
18611 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-04-07 16:47 | 2015-04-07 18:10 | 2 | 83 | 4285331 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTIONS BURNT OPEN ON POLE # 122-212 //// REPAIRED BAD CONNECTIONS AND RESTORES SERVICE @ 18:10// VER/ ADH
18612 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-09-24 09:47 | 2010-09-24 11:10 | 2 | 83 | 53051-1 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN 6T FUSE POLE 66D184. FUSED UP EVERYTHING OK VER/ARN IDCC FP NONE XXXX
18613 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-04-29 12:34 | 2022-04-29 15:20 | 1 | 166 | 4815151 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1126-B1-116, checking. Fuse had pulled into, refused @1520.
18614 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-06-16 14:31 | 2008-06-16 17:17 | 1 | 166 | 65696-1 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409002//CUT OUT BROKE IN PROSSES OF CHANGING // VER/TOM
18615 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-05-24 21:29 | 2015-05-25 00:15 | 1 | 166 | 4461431 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FAILED IN TWO XFMR BANK. CREW ENROUTE TO REPLACE. CHANGED XFMR AND RESTORED @ 00:15. SH VER/SEF
18616 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-06-13 14:58 | 2018-06-13 16:21 | 2 | 83 | 4597701 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 17-126 no truck will make repairs/// Changed broken 19.9 cutout and restored service @ 16:21
18617 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-05-20 15:14 | 2018-05-20 18:00 | 1 | 166 | 4382861 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER//NO ANSWER//. 6t fuse out due to cutout door burnt into replaced with new door and 6t fuse closed in everything ok
18618 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-01-15 14:39 | 2012-01-15 16:02 | 2 | 83 | 4262671 | 166 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION ON TRANSFORMER, GOING TO OPEN TRANSFORMER TO FIX.GOT TO CLIMB POLE TAKE 30 MIN VER/KEP IDC XXXX
18619 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2009-05-18 07:59 | 2009-05-18 10:45 | 1 | 166 | 61802-1 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT BROKE ON XFMR BANK. POLE IS 38830930B00253 NOT 233 AS TICKET SHOWS. ONLY ONE CUSTOMER AFFECTED. DUTY SUPERVISOR NOTIFIED - T THOMAS ENROUTE TO BRING MATERIAL TO CHANGE ALL 3 CUTOUTS. CUTOUTS REPLACED AND SERVICE RESTORED AT 10:45. SH ENTERED MD---HFP L3/HFP IDC XXXX
18620 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-10-17 13:44 | 2010-10-17 16:30 | 1 | 166 | 60427-1 | 166 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS/////SERVE-IN CONNECTION HEATED UP AND OPENED 1 LEG OF SERVICE UP,MADE NECESSARY REPAIRS,ALL OK AFTERWARDS//VER/CRB IDC XXXX
18621 | Pikeville | 3402002 | KEYSER | STONECOAL | 2016-01-27 11:44 | 2016-01-27 14:30 | 1 | 166 | 4654051 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE BAD CUT OUT WILL REPLACE BOTH/ VER/AWD
18622 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-07-12 10:29 | 2014-07-12 13:15 | 1 | 166 | 4231811 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER CAME LOOSE OUT OF THE HOT TAP.MAKING REPAIRES NOW.REPAIRES MADE. VER/CRB
18623 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-01-03 10:07 | 2020-01-03 11:30 | 2 | 83 | 4207341 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout changing
18624 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-10-28 06:51 | 2019-10-28 09:37 | 1 | 166 | 4208691 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service has burnt down, bad connections, power restored
18625 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2019-09-24 11:29 | 2019-09-24 14:15 | 1 | 166 | 4053501 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced and restored @ 14:15. sh
18626 | Pikeville | 3402003 | KEYSER | MULLINS | 2013-11-30 07:44 | 2013-11-30 10:30 | 1 | 166 | 4088791 | 166 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL NEED TO CHANGED CUST S/D// S/D HAD 3 DIFFERENT SPLICES IN IT COMMING OFF THE HILL//POWER IS RESTORED// ALSO VINES NEEDS CUT OFF SEC TO POLE 38831103000276// VINES HAS SEC. PULLED DOWN TO ABOUT 8 FROM THE GROUND// SEND TO R/W VER/PDP
18627 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-03-23 19:37 | 2011-03-23 21:00 | 2 | 83 | 58048-1 | 166 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON POLE IDCC MCCDL XXXX
18628 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-01-26 21:50 | 2018-01-26 23:13 | 2 | 83 | 4776321 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//VOICEMAIL Xfmr fuse link appears to have broke. Restored @ 23:13. sh
18629 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-08-23 10:44 | 2020-08-23 13:30 | 1 | 166 | 4360561 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broke cutout and changed bad connections @ xfm///Low voltage 116/116/132 @ meter ////Station is coming to adjust LTC @ station/// control is in the abnormal/// Changed bad cutout and connections and restored service @ 13:30///Adjusted LTC and checked voltage @ meter 118/118/ 236/ opened at 1300 closed at 1330/ 37820170000048/ cod 1
18630 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2016-02-15 09:14 | 2016-02-15 12:00 | 1 | 166 | 4696911 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE BROKEN CUTOUT, NEED CREW TO REPLACE, STEEP DRIVEWAY SNOW COVERED, WILL NEED SIX WHEELER TO GET UP DRIVEWAY, JUST ONE CUST RELEASED BY CREW 078S06. CUTOUT CHANGED, POWER RESTORED AT 12:00. VER/CRB L/3 CRB
18631 | South Williamson | 3411401 | DEWEY | INEZ | 2021-06-24 10:07 | 2021-06-24 11:30 | 2 | 83 | 4802271 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | current limit fuse bad//repirs made//restored at 11:30//complete/em
18632 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-07-24 20:04 | 2011-07-24 22:50 | 1 | 166 | 4613351 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKEN IN TWO. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT.//COD 1// VER/DBM IDC XXXX
18633 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-05-21 12:34 | 2012-05-21 15:20 | 1 | 166 | 4813451 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR LEAKING A LOT OF OIL,WILL CHANGE IT.DID NOT RE-FUSE IT///////SEND TO DAVE SAMMONS PER TIM HALL RELEASED BY CREW 074S06 XFMR CHANGED ON AT 15:20 D SAMMONS ///VER/CRB L/3 CRB IDC XXXX
18634 | Pikeville | 3409502 | BURDINE | LEVISA | 2016-10-18 19:17 | 2016-10-18 22:03 | 1 | 166 | 4026771 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKCEN CUTOUT ON 3110-25 CANT REACH IT WITH MY TRK NEED CLASS A LINEMAN AND BIG BUCKET 7200 CUTOUT CREW ARRIVED REPLACED CUTOUT RESTORE POWER AT 22:03 VER/CRB L3/HFP XXXHFP
18635 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2020-10-03 15:03 | 2020-10-03 16:26 | 2 | 83 | 4523461 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Looked like fuse had just broke. refused txmf apr at 1626 close ticket
18636 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-06-01 21:17 | 2008-06-01 22:40 | 2 | 83 | 54191-1 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000301// BAD WESTINGHOUSE CUTOUTAND LA 6T//VER/CRB IDC XXXX
18637 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-10-18 12:29 | 2018-10-18 15:15 | 1 | 166 | 4266251 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | looks like serv end heated up melting insulation on hot wire making contact with neutral burning service drop down. i changed out service drop everything ok. send copy to peggy in damage claims cust could possibly call in//SENT TO CLAIMS//COD 1
18638 | Hazard | 3310502 | HADDIX | CANOE | 2015-03-15 15:37 | 2015-03-15 17:00 | 2 | 83 | 4196881 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT . FUSE BROKE ./ ISO 37830074000018/ COD 2/ VER/BOW
18639 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2019-01-24 13:17 | 2019-01-24 14:40 | 2 | 83 | 4717991 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broked silvertop cutout on 453-107, waiting on assistance. apr at 1440 close ticket dwest
18640 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-07-30 19:37 | 2011-07-30 21:00 | 2 | 83 | 4644731 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 117-181 15T LINE FUSE OUT POLE 116-534 BAD LA SEND NOTE TO RAYBURN TRUCK TO POLE//AED CREATED // VER/DBM IDC XXXX
18641 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-09-06 16:58 | 2015-09-06 18:21 | 2 | 83 | 4209851 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED 2 CONNECTIONS FROM LOAD//2 CUSTS AFFECTED VER/CRB
18642 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2016-01-02 00:22 | 2016-01-02 01:45 | 2 | 83 | 4580721 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 138-488 BAD CUTOUT//COD 2// VER/DBM
18643 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2020-05-23 13:44 | 2020-05-23 16:30 | 1 | 166 | 4892271 | 166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT,WILL RE-FUSE//////////XFR ACTUALLY ON POLE 965-34,IT IS BAD.SHOWS TO BE A 10KVA,1 200A SERV ON IT///////NO ACCESS W TRUCK Released by crew 074S06//MADE MDC//COD 1//
18644 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-03-09 15:14 | 2019-03-09 18:00 | 1 | 166 | 4964111 | 166 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr, all power restored @ 18:00 p.hicks L3/HFP
18645 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2015-04-28 19:35 | 2015-04-28 19:50 | 11 | 15 | 4373881 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 LASH SEC BOKE @ POLE 70-41 TO 42. LINE CREW, FLAGGERS, TRK OK. RELEASED BY CREW 078S07-----TIME OFF 19:35 TIME ON 19:50 VER/KEP L3/HFP XXX
18646 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-11-04 11:50 | 2014-11-04 12:45 | 3 | 55 | 4698481 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ETA 1 HOUR INSULINK CONNECTOR FAILED AND BURNT BOTH HOT CONDUCTORS OPEN AT WEATHERHEAD. OPENED XFMR 787-30 @ 11:50. REPLACED SERVICE AND CLOSED XFMR @ 12:45. SH/ ISO 38830787000030/ COD 3// VER/BOW
18647 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-01-30 13:32 | 2011-01-30 14:27 | 3 | 55 | 52292-1 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED UP...REPLACED CUTOUT DOOR POLE 728-85...//COD 3//VER/CRB IDCC CNT25 XXXX
18648 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-08-25 13:40 | 2011-08-25 13:55 | 11 | 15 | H4755501 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT PL#1073/2036---CREW REQ.---TRUCK TO POLE---CHANGE ALL 3 CUTOUTS WHILE HERE--CHANGED 3CUTOUTS---XFMR BANK PL#1073/2035 OFF @ 13:40 TO 13:55 VER/KEP IDC XXXX
18649 | South Williamson | 3411401 | DEWEY | INEZ | 2012-09-28 09:20 | 2012-09-28 12:05 | 1 | 165 | 4095151 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 672-21///ONLY ONE CUSTOMER OUT///NO TRUCK///CREW ENROUTE TO HELP//REPAIRS MADE//RESTORED AT 1205//COMPLETE//EM//MADE MDC ///VER/CRB L/3 CRB IDC XXXX
18650 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2016-01-20 19:45 | 2016-01-20 22:30 | 1 | 165 | 4637431 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CORRECT POLE # 37830212D00027 6T FUSE OUT DUE TO BAD CUTOUT CHANGED CUTOUT EVERYTHING OK. VER/CRB
18651 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2015-06-27 07:03 | 2015-06-27 07:58 | 3 | 55 | 4672971 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | "B" PHASE ONLY COD-3B PHASE ONLY COD-3///CUT ARRESTOR IN THE CLEAR ON POLE 206-2122B PHASE ONLY COD-3///CUT ARRESTOR IN THE CLEAR ON POLE 206-2122/// ALL CUST. RESTORED COMPLETE/ ISO 38830206B02094/ COD 3/ VER/BOW
18652 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2011-03-28 13:40 | 2011-03-28 16:25 | 1 | 165 | 59969-1 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR ON 494-135 WILL GET CREW TO REPLACE TOMORROW CUSTOMER AGREES TO THIS... OPS # 037217521 //COD 1// VER/DBM IDC XXXX
18653 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-02-07 12:46 | 2014-02-07 15:31 | 1 | 165 | 4366271 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTER VER/SEF
18654 | Pikeville | 3401001 | ELWOOD | DORTON | 2010-02-02 00:15 | 2010-02-02 03:00 | 1 | 165 | 62179-1 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE CURRENT LIMITING FUSE WAS BURNED UP. CC 1 LINK FAILED VER/PDP IDC XXXX
18655 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-12-17 17:45 | 2019-12-17 20:30 | 1 | 165 | 4164001 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER 37830246D00101 IS BAD//OPENED TRANSFORMER @ 17:45
18656 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2015-04-22 18:45 | 2015-04-22 21:30 | 1 | 165 | 4356471 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BROKEN CUTOUT/NO CREW REQUIIRED VER/CRB
18657 | Hazard | 3309301 | VICCO | REDFOX | 2010-12-31 17:25 | 2010-12-31 20:10 | 1 | 165 | 57412-1 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38258050 // CHECKED VOLTAGE AT METER BASE , THEN CHECKED VOLTAGE ON POLE BEST I COULD TELL THAT IT WAS GOING BAD , WILL CHANGE ON 010111 JKC OPS # 039401811 --- WR #39258229 RELEASED BY CREW 077H03 COD-1 ISO TF 37830300B00121 VER/HFP L3/HFP IDC XXXX
18658 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-06-12 20:18 | 2014-06-12 23:03 | 1 | 165 | 4081581 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT UP ON XARM IS BROKEN,NEED 1 MAN,BUCKET.NEED TO COVER TO REPLACE/////////REPLACED CUTOUT/RESTORED VER/CRB
18659 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-10-31 06:40 | 2022-10-31 09:25 | 1 | 165 | 4079891 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 XFMR C/O broken // making repairs // RESTORED @ 09:25
18660 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-03-13 20:35 | 2014-03-13 23:20 | 1 | 165 | 4490991 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPEN NEUTRAL IN SERVICE AT XFMR DUE TO BAD CONNECTION, MADE REPAIRS RESTORED POWER AT 23:20, ONLY ONE CUSTOMER AFFECTED VER/SEF
18661 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-12-28 10:40 | 2012-12-28 13:25 | 1 | 165 | 4545041 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IS BROKEN IN SERVICE DROP AT SECONDARY POLE. I AM GOING TO SPLICE NEUTRAL. I SPLICED NEUTRAL.// VER/DBM
18662 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-12-03 12:09 | 2013-12-03 14:54 | 1 | 165 | 4095851 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN NEUTRAL IN S/D MID-SPAN.REPLACED SERVICE DROP. VER/SEF L3/HFP
18663 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-03-11 15:21 | 2010-03-11 16:16 | 3 | 55 | 65114-1 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 34220777 //NO CREW REQUIRED REPLACING CONNECTIONS ON POLE COD-3 IDC XXXX
18664 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-01-08 13:46 | 2019-01-08 16:31 | 1 | 165 | 4640601 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced secondary connections/only one meter off/please close ticket/thanks/vem
18665 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2017-08-16 16:00 | 2017-08-16 18:45 | 1 | 165 | 4268541 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQUIRED 6A COPPER OPEN WIRE SECONDARY TRUCKS OK OPEN FUSE AT 225-27 AT 1600 HRS 2 CUSTOMERS OFF,,REPAIRED OPEN WIRE,,ALL POWER RESTORED 38830225000027 VER/AWD
18666 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-02-20 21:22 | 2015-02-21 00:07 | 1 | 165 | 4059521 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTIONS HAS BURNED UP AT THE WEATHER HEAD. I REPLACED AL THE CONNECTIONS AND POWER IS BACK ON. VER/CRB
18667 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-05-23 07:40 | 2022-05-23 10:25 | 1 | 165 | 4931171 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans fuse open at 285-110.Will be trying to get it back in..Have a Broke Trans cutout on 285-110,This is a Manual pole,Paul Layne is on the way to help make repairs..Have a Broke Trans cutout on 285-110,This is a Manual pole,Paul Layne is on the way to help make repairs..Restored at 10:25.
18668 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-04-21 18:05 | 2020-04-21 20:50 | 1 | 165 | 4731621 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke in service drop. made repaires
18669 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2018-06-22 14:15 | 2018-06-22 17:00 | 1 | 165 | 4645141 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xform cutout broken ,replaced power restored
18670 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-09-15 21:12 | 2011-09-15 21:45 | 5 | 33 | 4874981 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TOP OF CUTOUT ARCING THIS IS LINE FUSE ON POLE 834-289 WILL HAVE TO OPE TO MAKE REPAIRS ///CHANGED LINE FUSE OUT ON POLE 834-289 WASNT ON MAP HAD 20T FUSE IN IT///OPENED AT 21:12///CLOSED AT 21:45///COMPLETE BR//COD 5//ISO 38830834B00289 // MD FILED IDC XXXX
18671 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2012-03-07 17:29 | 2012-03-07 18:24 | 3 | 55 | 4561801 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE HOT TAP VER/HFP L3/HFP IDC XXXX
18672 | South Williamson | 3200302 | BELFRY | TOLER | 2016-05-14 13:27 | 2016-05-14 16:12 | 1 | 165 | 4216961 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE F IS OUT,WILL PTRL//////////NOTHING EVIDENT,WILL RE-FUSE//////////RE-FUSED AND RESTORED,FUSE APPEARED TO HAVE SIMPLY BROKEN VER/CRB
18673 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-03-03 16:30 | 2014-03-03 17:25 | 3 | 55 | 4447661 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SEC POLE 189-180 BAD LEG ON U.G. SER. CREW AND POWER TEMPREPAIR SEC. RISER POLE 189-129. FULLY RESTORED TIME OFF 16:30 ON 17:25 MP NO BAD UG VER/CRB
18674 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-02-09 11:35 | 2018-02-09 14:20 | 1 | 165 | 4820591 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | current limiting fuse burnt up will repair/// replaced bad current limiting fuse and restored service @ 14:20
18675 | Hazard | 3308002 | JACKSON | PANBOWL | 2014-01-07 13:36 | 2014-01-07 16:21 | 1 | 165 | 4252411 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CUSTOMER HAS LOST NEUTRAL ON UNDERGROUND SERVICE. WILL HAVE TO DID UP PEDISTAL TO GET TO OUR WIRES/// WILL HAVE TO REPLACE SERVICE UNDERGROUND WE ARE GOING TO USE AUTO XFMR TO WORK TONIGHT REPLACE TOMORROW. RELEASED BY CREW 077S08INSTALLED AUTOTRANSFORMER UNTIL CAN GET BACK TO CUSTOMER RESTORED 1621 VER/HFP L3/HFP
18676 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-02-23 22:30 | 2015-02-24 01:15 | 1 | 165 | 4076851 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED APART AT WEATHERHEAD ON ONE OF THE SECONDARY PHASE WIRES. ONLY ONE CUSTOMER AFFECTED. VER/ARN
18677 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-02-25 09:02 | 2014-02-25 11:47 | 1 | 165 | 4432741 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | RISER MELTED OUT ON TRANSFORMER WILL NEED BIG BUCKET TO MAKE ,GIVE TO ROB COMPFER RELEASED BY CREW 078S09 MADE REPAIRS CLOSED BACK IN AT 1148 VER/HFP L3/HFP
18678 | South Williamson | 3411401 | DEWEY | INEZ | 2015-12-23 06:30 | 2015-12-23 09:15 | 1 | 165 | 4551491 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT LEG ON SERVICE BURNED INTO///CHANGED OUT 4/3 SERVICE DROP TO 2/3 DROP//RESTORED AT 9:15//COMPLETE//EM VER/CRB
18679 | South Williamson | 3411401 | DEWEY | INEZ | 2021-06-03 16:20 | 2021-06-03 17:15 | 3 | 55 | 4663221 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke in 1/0secondary midspan//no truck //will have to let down secondary to make repairs//will have to open xfmr//crew enroute to assist//repairs made//restored at 17:15//complete//em//OPENED 1620
18680 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-12-01 15:05 | 2016-12-01 17:50 | 1 | 165 | 4158961 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR CHANGING. VER/CRB L3/HFP XXXHFP
18681 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-01-20 08:00 | 2008-01-20 10:45 | 1 | 165 | 57903-1 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CALLED FOR CREW 1/0 WIRE CALLED FOR ADD A PHASE RELEASED BY CREW 078S03 INSTALLED POWER TEMP. WILL FIX UNDERGROUND AT LATER DATE POWER RESTORED AT 1045 VER/KEP IDC XXXX
18682 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2013-08-14 20:10 | 2013-08-14 21:05 | 3 | 55 | 4666521 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VENTURINO OPENING FUSE TO PUT OUT POLE FIRE VER/SEF
18683 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-01-11 00:47 | 2012-01-11 03:32 | 1 | 165 | 4246161 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED DRT TO ASSIST// UPGRADED SERVICE // VER/TOM L3/TOM IDCC CNT14 XXXX
18684 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-03-14 16:55 | 2011-03-14 17:50 | 3 | 55 | 54342-1 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 127//CHANGING NOW//REPAIRED//RESTORED AT 17:50//COMPLETE//EM//COD 3// VER/DBM IDC XXXX
18685 | Hazard | 3307301 | BULAN | ARY-HEINE | 2018-01-31 09:26 | 2018-01-31 10:21 | 3 | 55 | 4786701 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse out on pole37830177C00229,not line fuse on pole37830177C00109/fuse broke/ ISO 37830177C00229/ COD 3
18686 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-04-30 20:30 | 2016-04-30 21:25 | 3 | 55 | 4145871 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED. OPENED XFMR @ 20:30, REPLACED CUTOUT AND RESTORED @ 21:25. SH VER/ARN
18687 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2022-11-16 15:45 | 2022-11-16 18:30 | 1 | 165 | 4151281 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | had a pine tree laying on lash at pole 115-86 and it had the neutral broke.. call for a tree crew and got tree removed off lash and got the neutral spliced out.. got xformer at pole 115-86 restored at a time of 18:30
18688 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-10-06 22:32 | 2012-10-07 01:17 | 1 | 165 | 4120281 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD K-MATE ON XFMR WILL SEE IF CAN REMOVE REMOVED VER/ARN IDC XXXX
18689 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-04-05 07:42 | 2018-04-05 10:27 | 1 | 165 | 4189631 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout, arrester, and bracket, added animal cover-up . ALL WORK COMPLETE / GXJ/ ISO 38831125D00191/ COD 1
18690 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-01-02 10:30 | 2012-01-02 13:15 | 1 | 165 | 4224661 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOSE CONN ON POLE---BAD TRANSFORMER//COD 1// VER/DBM IDCC TOF0959 ESTIMATED TIME OFF XXXX
18691 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-03-20 13:01 | 2015-03-20 13:56 | 3 | 55 | 4213431 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER CONNECTION @ HOT LEG COD-3 ISO SO @ 39831148D26527 VER/HFP L3/HFP
18692 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-11-23 08:30 | 2010-11-23 11:15 | 1 | 165 | 58896-1 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKEN, 19.9 KV...WILL REPLACE NOW..P.NICKS...CHANGED C/O , ALL POWER RESTORED @ 11:15 HRS. P.HICKS,//VER/CRB IDC XXXX
18693 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2016-04-14 16:39 | 2016-04-14 19:24 | 1 | 165 | 4092111 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT 72KV,NEED 2 LINE MEN AND BIG BUCKET RELEASED BY CREW 077H07 VER/CRB
18694 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-12-25 22:50 | 2016-12-25 23:45 | 3 | 55 | 4237121 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER ON SITE//EMERGENCY OPEN ON TRANSFORMER TO ISOLATE AND REPLACE CUTOUT THAT IS BREAKING DOWN//TOM. OPENED TRANSFORMER POLE 141-54 AT 22:50 DUE TO BAD CUTOUT POLE SMOKING WILL BE OUT OF TRUCK MAKING REPAIRS. CHANGED BAD CUTOUT CLOSED TRANSFORMER FUSE BACK IN AT 23:45
18695 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-03-18 10:30 | 2014-03-18 13:15 | 1 | 165 | 4504921 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE . TIME RESTORED 1315 WDR VER/SEF IDC XXXX
18696 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-01-18 20:44 | 2016-01-18 23:29 | 1 | 165 | 4629961 | 165 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | PART POWER, BAD LEG UG SERVICE RELEASED BY CREW 078S07//MADE AED TO SHOW POWER TEMP INSTALLED//PART POWER, BAD LEG UG SERVICE RELEASED BY CREW 078S07/CREW ON SITE/ONE CUST PART POWER/INSTALLING POWER TEMP/FULL POWER BY 0045/PROBABLE DIG IN/VEMPART POWER, BAD LEG UG SERVICE RELEASED BY CREW 078S07/CREW ON SITE/ONE CUST PART POWER/INSTALLING POWER TEMP/FULL POWER BY 0045/PROBABLE DIG IN/VEM/CUST HAS FULL POWER 2329/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
18697 | Paintsville | 3401102 | FALCON | SALYERSVI | 2021-05-28 10:15 | 2021-05-28 13:00 | 1 | 165 | 4635531 | 165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hotleg and neutral was burnt up and n2 mid span of service. This was #4 service with several splices so we removed and installed new #2 service. Power restored @ 13:00
18698 | South Williamson | 3411401 | DEWEY | INEZ | 2015-12-16 16:47 | 2015-12-16 18:09 | 2 | 82 | 4538181 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE XFMER CUTOUT ON POLE 744-118///REPLACED BAD CUTOUT AND REFUSED AT 18:09////COMPLETE BR VER/CRB
18699 | Hazard | 3303902 | LESLIE | WOOTON | 2020-04-08 14:46 | 2020-04-08 17:30 | 1 | 164 | 4573541 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew will come to replace cutout, ned manuel right of way crew, cust saidok to cut span out while power is off Released by crew 077S07.crew on site, changed cutout, all power estored @17:30 hrs.p.hicks
18700 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-06-20 20:01 | 2014-06-20 22:45 | 1 | 164 | 4130561 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT.//COD 1// VER/DBM
18701 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2021-06-30 16:46 | 2021-06-30 19:30 | 1 | 164 | 4829581 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200 25kva, 277 voltage. 1 pri. bushing, 2 sec. bushings. // crew on site FETR 19:45 LRM//cod 1
18702 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-11-01 09:34 | 2009-11-01 12:18 | 1 | 164 | 54608-1 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED TO REPLACE SERVICE DROP, NEUTRAL BROKE. CUSTOMER HAS EQUIPMENT DAMAGE. REPLACE SERVICE DROP //VER/GAH IDC XXXX
18703 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-09-23 10:03 | 2021-09-23 11:25 | 2 | 82 | 4282981 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 leg of open wire burnt down due to back connection///Put open wire back up and restored full power @ 11:25
18704 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2010-05-09 20:38 | 2010-05-09 22:00 | 2 | 82 | 58753-1 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RESQUEXED CONNECTORS * NEED TREE TICKET. VER/PDP IDCC PN1574 XXXX
18705 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-04-23 09:16 | 2014-04-23 12:00 | 1 | 164 | 4626681 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED BAD TRANS VER/CRB
18706 | South Williamson | 3411401 | DEWEY | INEZ | 2010-07-30 16:57 | 2010-07-30 19:41 | 1 | 164 | 59638-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE ON XFMR CUTOUT. RE-FUSED. SH//COD 1// VER/DBM IDC XXXX
18707 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-10-29 12:07 | 2014-10-29 14:51 | 1 | 164 | 4671331 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED LINE CREW TO REPLACE @ POLE 472-101 RELEASED BY CREW 078S05--CHANGED CUTOUT---PWR CK OK---TBL TKT COMP---RMV VER/CRB
18708 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-07-12 21:55 | 2020-07-12 23:17 | 2 | 82 | 4156451 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout // made repairs and restored @ 2317
18709 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-11-06 08:49 | 2015-11-06 11:33 | 1 | 164 | 4414411 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHANGE CONNECTION ON SERVICE ENTRANCE//SHOULD BE JOB TO REROUTE SECONDARY//SENT TO LINE DEPT VER/CRB
18710 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-12-01 07:47 | 2011-12-01 09:09 | 2 | 82 | 4132061 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 2// VER/DBM IDC XXXX
18711 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-12-02 04:51 | 2014-12-02 07:35 | 1 | 164 | 4824341 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK DURING NORMAL HOURS/POLE#185-25 FUSE BLOWN/CUST MIS MAPPED/POLE#185-272 BURNT OFF/VEM/FETR0830/VM/LIFTED HOTAP @185-269/TAGGED FOR DDC/ONE CUST RESTORED 0735/NO OTHER ACTIVE SERVICES ON THIS TAP/PLEASE COPY TO ENG TO WRITE JOB REPAIR OR REMOVE/VEM//MADE SWITCHING ORDER 4824781//MADE AED VER/CRB
18712 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-10-25 10:07 | 2018-10-25 12:51 | 1 | 164 | 4321171 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | old cons failed and heated up srv causing multi melted spots and one burnt drop down--replaced drop--allgood--ds10251838830852000229
18713 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-07-12 17:06 | 2022-07-12 19:50 | 1 | 164 | 4470271 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse out on pole 793D-95.back in at 19:50
18714 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2020-08-09 15:12 | 2020-08-09 16:34 | 2 | 82 | 4303791 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
18715 | Hazard | 3303902 | LESLIE | WOOTON | 2009-02-03 10:11 | 2009-02-03 11:33 | 2 | 82 | 55075-1 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3303902// BAD CONNECTION ON XFMR POLE VER/KEP L3/KEP
18716 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-02-06 10:16 | 2009-02-06 13:00 | 1 | 164 | 56149-1 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3103101//REPAIRED NEUTRAL VER/KEP L3/KEP IDC XXXX
18717 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-11-01 14:38 | 2017-11-01 16:00 | 2 | 82 | 4522831 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad hot leg on URD secondery off pole 38831126C00273, customer agreed to wait till 11-2-17 to make repairs, only feeds a barn, OPS ORDER # 035237666.
18718 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-12-18 06:27 | 2019-12-18 09:11 | 1 | 164 | 4165231 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | replaced service drop, multiple splices, bad insulink. pls close. tre
18719 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-01-15 16:21 | 2010-01-15 19:05 | 1 | 164 | 54824-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1.6 FUSE BROKEN.......DAH//COD 1// VER/DBM IDC XXXX
18720 | Whitesburg | 3312901 | JENKINS | KONA | 2015-08-21 08:10 | 2015-08-21 09:32 | 2 | 82 | 4160471 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , RICK MAGGARD IS COMMING TO HELP ME CHANGE IT// VER/ ADH
18721 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-07-23 14:16 | 2017-07-23 17:00 | 1 | 164 | 4165141 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | C PHASE CUTOUT BAD ./ ISO 37830029000129/ COD 1/ VER/BOW
18722 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2010-10-08 14:28 | 2010-10-08 15:50 | 2 | 82 | 58119-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CSP XFMR. HOT-LINE-CLAMP FAILURE CAUSED STIRRUP TO BURN IN TWO ON PRIMARY RISER. POLE INACCESSIBLE BY TRUCK. WILL HAVE TO CLIMB UP AND INSTALL HOT STICK TYPE STIRRUP AND CHANGE HOT-LINE-CLAMP. REPAIRS COMPLETE. RESTORED @ 15:50. LEFT NOTE FOR CUSTOMER TO STRAIGHTEN SERVICE POLE WITHIN TWO WEEKS. SERVICE IS LOW OVER PORCH. SH COD-2 ISO PO 38830737000048 VER/HFP L3/HFP IDC XXXX
18723 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2021-04-23 08:24 | 2021-04-23 11:08 | 1 | 164 | 4473161 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad primary insulator @ pole 1000-30 truck okay crew required Released by crew 078S06///complete BR
18724 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-03-08 19:25 | 2015-03-08 20:47 | 2 | 82 | 4169601 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION AT WEATHERHEAD VER/ARN
18725 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2009-01-04 08:20 | 2009-01-04 09:42 | 2 | 82 | 51201-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3403202// 6T TRANSFORMER FUSE BROKE ON POLE 139A129. VER/TOM L3/TOM IDCC CNT1 XXXX
18726 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-02-11 23:23 | 2008-02-12 00:45 | 2 | 82 | 60605-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3116703/// BROKEN FUSE LINK VER/ARN IDCC CNT1 XXXX
18727 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2014-05-27 11:42 | 2014-05-27 14:26 | 1 | 164 | 4933311 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT HAS BURNED OFF THE CROSSARM. NEED EIGHT FOOT ARM, THREE CUTOUTS AND ARRESTERS AND ARM BRACKETS. CAN USE BUCKET TRUCK. RELEASED BY CREW 079S02 VER/CRB
18728 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-07-26 21:23 | 2021-07-26 22:45 | 2 | 82 | 4963381 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broken on pole 170-144..will make repairs..repairs made.restored..
18729 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-10-31 19:03 | 2019-10-31 20:25 | 2 | 82 | 4258501 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad c/o, on transformer, have chg all power restored at this loc at 2025 by amg
18730 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-06-10 22:57 | 2008-06-11 00:19 | 2 | 82 | 62325-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3401801//825-96...BAD 6 INCH DISC....CHG DISC...REFUSED LINE BB COD-2 VER/LDA IDCC PN28, FP10 XXXX
18731 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-11-11 12:03 | 2008-11-11 14:47 | 1 | 164 | 63933-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401103//..BAD XFMR... I CALLED MILLER TO COME CHG.... RELEASED BY CREW 076S01/// REPLACED 15KVA TRANSFORMER WITH 25 KVA.//COD 1// VER/DBM IDC XXXX
18732 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-05-18 12:56 | 2008-05-18 15:40 | 1 | 164 | 65456-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | 3008701// VER/HFP IDC XXXX
18733 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-06-22 10:38 | 2010-06-22 12:00 | 2 | 82 | 54382-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 93-115 6T ME FUSE LINK BROKE//THIS IS COMPLETE-PLEASE CLOSE-PRB VER/ARN IDCCPN152 XXXX
18734 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2018-08-10 17:58 | 2018-08-10 19:20 | 2 | 82 | 4938791 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ISO 38830738D00017/ COD 2 Released by crew 076S02/ fuse broke
18735 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-12-01 07:00 | 2008-12-01 07:41 | 4 | 41 | 53396-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401103 -....901-7 NEED POLE CHG OUT ..TOP OF POLE BADLY BURNED..I CHANGED CUTOT BUT POLE NEEDS WRITTEN UP TO CHG OUT...BB // COD 4 // SENT TO RON RYE // VER/TOM L3/TOM IDC CHANGED START TIME FROM 0511, ESTIMTAED TIME OFF XXXX
18736 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2022-01-18 19:16 | 2022-01-18 22:00 | 1 | 164 | 4383601 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broken 2 spans back on the hill. climber.. changing
18737 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-06-07 15:30 | 2015-06-07 16:52 | 2 | 82 | 4521161 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | PART POWER DUE TO BAD CUTOUT ON XFMR BANK, REPLACED CUTOUT RESTORED POWER AT 16:52../ ISO 37830424000289/ COD 2/ VER/BOW
18738 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2012-08-10 20:53 | 2012-08-10 22:15 | 2 | 82 | 4926561 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE IT VER/KEP IDCC FP NULL XXXX
18739 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-12-22 09:58 | 2008-12-22 11:20 | 2 | 82 | 62422-1 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEC LOOP BURNT OPEN//3001101/VER/CRB L3/KEP IDC XXXX
18740 | Hazard | 3302704 | HAZARD | KENMONT | 2017-12-03 15:46 | 2017-12-03 18:30 | 1 | 164 | 4618611 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 1630//BAD CUTOUT ON POLE 37830296C21008ETA 1830// bad cutout on pole 296c-1008 will need to change all three cutouts//THIS CAUSED THE HAZARD-KENMONT BREAKER TO OPERATE
18741 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2018-11-29 01:08 | 2018-11-29 02:30 | 2 | 82 | 4488941 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout burnt up will replace bad cutout/// Replaced bad cutout and restored service @ 02:30
18742 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-10-14 10:36 | 2011-10-14 13:20 | 1 | 164 | 4978191 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-5175 BAD CUTOUT REPAIRED//COD 1// VER/DBM IDC XXXX
18743 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-01-07 09:46 | 2009-01-07 12:30 | 1 | 164 | 52406-1 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000201//,,,,,BEEN TO THIS TRANSFORMER 3 TIMES WE WILL NEED TO UPGRADE TRANSFORMER BEFORE NEXT COLD SPELL FRALEY IS ON HIS WAY WITH A 37.5 NOW.. VER/KEP L3/KEP IDC XXXX
18744 | Hazard | 3311103 | STINNETT | WENDOVER | 2019-04-15 16:21 | 2019-04-15 19:05 | 1 | 164 | 4118551 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | splice in service wire failed. repaires made.all power restored @ 19:05.p.hicks
18745 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-02-12 11:56 | 2017-02-12 13:18 | 2 | 82 | 4387551 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MD TO SHOW TRANS ON LOAD SIDE OF L/F ON POLE 37820032C00086//COD 2// VER/CRB
18746 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2011-10-08 12:04 | 2011-10-08 14:48 | 1 | 164 | 4957841 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL BROKE ON XFMR ON AT 14:48 ///VER/CRB IDC XXXX
18747 | Hazard | 3302704 | HAZARD | KENMONT | 2015-10-13 07:43 | 2015-10-13 10:27 | 1 | 164 | 4343311 | 164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON PADMOUT TRANSF CALLED FOR LINE CREW TO REPLACE ALL 3 CUTOUTS === RELEASED BY CREW 077S03.CREW REPLACED ALL CUTOUTS/ARR/ AND T BRKTS ALL POWER RESTORED @ 10:27HRS VER/CRB
18748 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2011-02-13 15:26 | 2011-02-13 18:10 | 1 | 164 | 56578-1 | 164 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SERV === REPAIRED == POWER OK VER/KEP IDC XXXX
18749 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2010-07-01 08:52 | 2010-07-01 11:35 | 1 | 163 | 61179-1 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | CENTER PHASE BLOWN ON PRIMARY METERING DUE TO GUY WIRE WRAP RUSTING OFF AND ALLOWING GUY TO CONTACT PRIMARY RISER. OPENED OTHER TWO PHASES AT 10:30 TO ELIMINATE BACKFEED WHILE I MAKE REPAIRS. ANCHOR FOUND - INSTALLING GUY INSULATOR. RE-ATTACHED GUY AND RESTORED SERVICE @ 11:35. SH VER/KEP L3/KEP IDCC PN846, CNT11 XXXX
18750 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-06-28 19:16 | 2017-06-28 21:59 | 1 | 163 | 4055831 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE ROTTED//CLOSED 2159 VER/CRB
18751 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2019-07-19 16:12 | 2019-07-19 18:55 | 1 | 163 | 4735351 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on xfmr 785-568 and burnt neutral in two. Opening xfmr to safely clear vines and make repairs. Reworked all secondary connections, replaced cutout & arrester and restored @ 18:55. sh
18752 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-03-02 19:22 | 2013-03-02 22:05 | 1 | 163 | 4867321 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN FROZE OUT////REPLACED SPLICE, POWER OK VER/ARN IDC XXXX
18753 | Hazard | 3302704 | HAZARD | KENMONT | 2014-02-24 11:31 | 2014-02-24 14:14 | 1 | 163 | 4430471 | 163 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN SER WENT BAD ==== REPAIRED ==== POWER OK VER/HFP L3/HFP
18754 | Hazard | 3303902 | LESLIE | WOOTON | 2010-08-20 16:47 | 2010-08-20 19:30 | 1 | 163 | 58800-1 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPLACED HOT LINE CLAMP VER/ARN IDC XXXX
18755 | Pikeville | 3408102 | SALISBURY | BLACK DIAMOND | 2014-03-20 12:57 | 2014-03-20 15:40 | 1 | 163 | 4512981 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | BAD PRIMARY METERING. ISOLATED PRIMARY METERING PLACED TAGS FOR DDC. CLOSED IN 600AMP BYBASSES NEEDS PLACED IN ABNORMAL. SEND COPY TO ENG. PIKEVILLE//COD 1//AED CREATED// VER/DBM
18756 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-06-16 10:11 | 2010-06-16 12:54 | 1 | 163 | 66134-1 | 163 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | THIS IS AT MOUNTAIN ENTERPRIZE, ACROSS FROM CHEVRON, GO THRU PILES OF SLAG, TURN LEFT, WILL SEE A RED BUILDING BY THE RIVER, CAN GET TRUCKS TO THIS, WELL NEED CREW TO MAKE REPAIRS, WELL NEED 3 CUTOUTS AND 3 ARRESTORS, AND LOOKS LIKE ON ARM PINS HAS FLASH OVER, BUT THIS IS CREW REQUIRED I OPEN THE OTHER TWO CUTOUTS ON THIS BANK POLE //COD 1//RESTORED 1254 // VER/DBM
18757 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-12-06 17:55 | 2020-12-06 20:38 | 1 | 163 | 4749541 | 163 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SQUEEZON CONNECTION@XFR BURNED INTO. PARTIAL POWER TO RESTAURANT ONLY.REPLACED CONNECTION,ALL OK AFTERWARDS.NOT 12 CUSTS OUT EITHER
18758 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-09-21 18:02 | 2018-09-21 20:45 | 1 | 163 | 4139711 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Actual address: 1146 Gifford near 38830873000003.open neutral,repaired.back on at 20:45 on pole 873-09//cod 1//iso
18759 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-12-08 16:07 | 2014-12-08 18:50 | 1 | 163 | 4848131 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRUCK OK.. SEND TO BRENT TACKET RELEASED BY CREW 078H06,,CREW ON SITE,,REPLACED XFMR, AND CUTOUT, ALL POWER RESTORED/ ISO 38830189000060/ COD 1/ VER/BOW
18760 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-04-17 15:52 | 2015-04-17 18:35 | 1 | 163 | 4330181 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED BIG BUCKETT TO REACH BAD BCUTOUT. TRUCK TO POLE. RELEASED BY CREW 078S01/ CREW ON SITE/ REPAIRS COMPLETE POWER RESTORED @ 18:35// CLOSE TICKET/JEH/ ISO 38830142A00379/ COD 1/ VER/BOW
18761 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-01-08 16:50 | 2009-01-08 19:33 | 1 | 163 | 53512-1 | 163 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP STS WR# 27989196 //BAD UG-MCARTY TO CALL CREW RELEASED BY CREW 078S07/PUTTING ON POWER TEMP L3/HFP IDC XXXX
18762 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-08-25 21:02 | 2010-08-25 23:45 | 1 | 163 | 60611-1 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED TRANSFORMER CUTOUT.//COD 1// VER/DBM IDC XXXX
18763 | Hazard | 3309302 | VICCO | JEFF | 2012-10-06 08:32 | 2012-10-06 11:15 | 1 | 163 | 4119261 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN///// CUTOUT GATE BAD, CHANGED OUT, POWER RESTORED.//COD 1// VER/DBM IDCC PN121 XXXX
18764 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2019-11-17 07:17 | 2019-11-17 10:00 | 1 | 163 | 4041501 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP TO REPLACE////////SERV DROP SHORTED INTO,HAD TO REPLACE IT.APPEARS TO HAVE BEEN AN INSULATION FAILURE THAT CAUSED THIS PROBLEM
18765 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-02-06 23:24 | 2009-02-07 02:07 | 1 | 163 | 56346-1 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3103101// RELEASED BY CREW 078S033103101// REPAIRED SERVICE NO CREW REQUIRED L3/DKG IDC XXXX
18766 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-04-01 17:05 | 2009-04-01 19:48 | 1 | 163 | 63848-1 | 163 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | OUTAGE TO REPAIR CONNECTION ON TRANSFORMER POLE IN ORDER 63860-1POSSIBLE OPEN NEUTRAL GOING TO OPEN TRANSFORMER TO RESQUEEZ CONNECTIONS MANUEL POLEPOSSIBLE OPEN NEUTRAL GOING TO OPEN TRANSFORMER TO RESQUEEZ CONNECTIONS MANUEL POLE GOING TO INSTALL TEMPERARY SERVICE DROPPOSSIBLE OPEN NEUTRAL GOING TO OPEN TRANSFORMER TO RESQUEEZ CONNECTIONS MANUEL POLE GOING TO INSTALL TEMPERARY SERVICE DROP CUSTOMER HAS EQUIPEMENT DAMAGE - OTHER OUTAGE CREATED TO SHOW TRANSFORMER OUTAGE// VER/TOM L3/TOM IDC XXXX
18767 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2011-04-30 19:17 | 2011-04-30 22:00 | 1 | 163 | 52959-1 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, GROUNDING | TRANS. FUSE OUT///WR 39771522 //. REPLACE BAD TRANSFORMER //VER/GAH
18768 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2009-05-28 16:36 | 2009-05-28 19:19 | 1 | 163 | 61002-1 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP 3301701// I HAVE FOUND A BAD LTNG ARRESTOR ON POLE 468-9. I WILL BE AWAY FROM TRUCK FOR APROX 45 MINUTES COD-1 37830468000002 L3/HFP
18769 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-19 12:12 | 2011-05-19 14:55 | 1 | 163 | 4113851 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA TRANSFORMER 19.9 POLE 142-387 OLD SCHOOL AND TRAINING YARD NEAR WAFFLE HSE CREW HAS BEEN CALLED RELEASED BY CREW 078S09/CREW ON SITE MAKING REPAIRS/REPAIRS COMPLETE POWER RESTORED @ 14:55 J. HEMLEPP & CREW 078H05 VER/KEP IDC XXXX
18770 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-08-18 16:02 | 2012-08-18 18:45 | 1 | 163 | 4950031 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O ON XFMR. MANUAL WILL BE AWAY FROM TRUCK FOR AWHILE////REPLACED C/O, POWER RESTORED. VER/KEP IDC XXXX
18771 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-11-11 07:31 | 2022-11-11 10:14 | 1 | 163 | 4124721 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout, arrester and bracket. Restored @ 10:14. sh
18772 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-08-22 10:00 | 2016-08-22 12:43 | 1 | 163 | 4824431 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED BAD TRANSFORMER POWER BACK ON RM PLEASE CLOSE TIC//MADE MDC TO SHOW 15KVA TRANS// VER/CRB
18773 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-04-21 09:56 | 2020-04-21 12:39 | 1 | 163 | 4725981 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | neut & hot legs burnt up. repairs made. pls close. tre.
18774 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-11-12 12:12 | 2020-11-12 14:55 | 1 | 163 | 4670211 | 163 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEND TO DAMAGE CLAIMS.SERV DROP NEUTRAL BROKEN INTO AT MAST,WILL REPAIR//////MADE NECESSARY REPAIRS.CUST SAID A TREE WAS CUT LAST YEAR&THIS MIGHT HAVE HAPPENED THEN,BUT NOT SURE.WILL PROBABLY BE HEARING FRM THEM.SOME DAMAGES PER CUST//SENT TO CLAIMS
18775 | Hazard | 3309301 | VICCO | REDFOX | 2011-01-01 08:37 | 2011-01-01 11:20 | 1 | 163 | 57561-1 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38258482 // RELEASED BY CREW 077H03 .. BAD CONNECTION AT XFMR MADE REPAIRS RESTORED POWER AT 11:20 COD-1 ISO TF 37830300B00121 VER/HFP L3/HFP IDC XXXX
18776 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-02-08 18:05 | 2011-02-08 20:48 | 1 | 163 | 55407-1 | 163 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED DRT TO HELP--BAD CONECTION ON CUSTOMERS MEALTED SERVICE DROP//VER/CRB IDC XXXX
18777 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-12-01 17:22 | 2018-12-01 20:05 | 1 | 163 | 4497931 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Correct xfmr pole for this customer is 38830784C00120. Transformer cutout is broke - this is the only customer affected. Replaced cutout and restored @ 20:05. sh L3/HFP
18778 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2009-12-17 14:32 | 2009-12-17 17:15 | 1 | 163 | 54080-1 | 163 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 CUSTOMER WAS PART OUT. SPLICE AT POLE WAS BAD. REPLACED.....DAH RELEASED BY CREW 074S08//COD 1// VER/DBM
18779 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-10-22 09:29 | 2011-10-22 12:12 | 1 | 163 | 4009771 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL CHECK FOR PROBLEMS////4/3 SERV HAD BURNED INTO,MADE NECESSARY REPAIRS,ALL OK AFTERWARDS TR OFF FROM 1125 TO 1212 FOR 3 CUST.... DUP IN HOIS ... COD-4 ISO TF 38831056C00053 SEE H4009771 FOR 3 CUST VER/HFP L3/HFP IDC XXXX
18780 | Hazard | 3307301 | BULAN | ARY-HEINE | 2015-10-08 16:55 | 2015-10-08 19:38 | 1 | 163 | 4329231 | 163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR FUSE BLOWN, MAY HAVE BAD ARRESTOR.//// REPLACE ARRESTOR MOVED IT FROM XFMR TO T-BRAKET, POWER RESTORED VER/CRB L3/HFP XXXHFP
18781 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2010-10-12 10:18 | 2010-10-12 13:00 | 1 | 162 | 58899-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | HAVE C PHASE FUSE OUT ON PRIMARY METERING POLE, INVESTATED IT AND FOUND BAD PRIMARY METERING, WAITING FOR METER ELECTRICAN, TO ARRIVE TO SEE ABOUT CHANGING THE PRIMARY METERING OUT, IF SO WILL NEED CREW, CAN USE BUCKET. AT THE PRESENT I HAVE ALL 3 CUTOUTS OPEN ON PRI METERING POLE FUSE WAS OUT ON POLE 901-5503, NOT 5504 MR. ADIKINS SHOWED UP, WE BY PASS THE BAD METERING, AND WE HAVE POWER RESTORED TO THE BRICKYARD, NEEDS TO BE PUT IN ABNORMAL, WE REPAIR AT LATER DATE MADE AN AED //VER/CRB IDC XXXX
18782 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-12-27 12:07 | 2010-12-27 14:49 | 1 | 162 | 56212-1 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38206644 //NO CREW REQUIRED REPLACING SERVICE VER/HFP L3/HFP IDC XXXX
18783 | Hazard | 3302703 | HAZARD | HAZARD | 2015-02-20 18:36 | 2015-02-20 19:30 | 3 | 54 | 4058791 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS BROKE REFUSED POWER RESTORED VER/CRB L3/DKGXXXX
18784 | South Williamson | 3411401 | DEWEY | INEZ | 2008-06-12 16:04 | 2008-06-12 17:25 | 2 | 81 | 63227-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT BROKE WHEN CLOSED IN DOOR TIM MILLER WILL SEND SOMEONE TO CHANGE CUTOUT RELEASED BY CREW 079S01// SENT COPY TO TCMILLER VIA EMAIL// VER/TOM
18785 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-10-16 15:48 | 2011-10-16 18:30 | 1 | 162 | 4988351 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG., 107.3 PHASE TO GROUND AND 125.3 PHASE TO GROUND. PUT POWER ON, NEED REPAIRED LATER.//COD 1//EMAILED TO B REYNOLDS// VER/DBM IDC XXXX
18786 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2013-12-03 22:54 | 2013-12-04 00:15 | 2 | 81 | 4097201 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTIONS BAD AT WEATHERHEAD.-----REMADE CONNECTIONS AT WEATHERHEAD. ONLY 2 CUST. OUT VER/ARN L3/HFP
18787 | Hazard | 3309301 | VICCO | REDFOX | 2022-11-10 19:23 | 2022-11-10 20:17 | 3 | 54 | 4123631 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke power restored at 20:17
18788 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-02-01 12:48 | 2012-02-01 15:30 | 1 | 162 | 4312821 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH VOLTAGE ON TRANSFORMER 38830254D00120, 143/285, CREW REQUIRED, FLAGGERS REQUIRED, 25KVA 7200. TRANSFORMER CHANGED, VOLTAGE 123/246, POSSIBLE DAMAGE CLAIM. VER/KEP IDC XXXX
18789 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-01-24 06:33 | 2014-01-24 09:15 | 1 | 162 | 4306011 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN THE SERVICE DROP WENT BAD AND BURNED THE DROP DOWN. ONLY ONE CUSTOMER WAS OUT. VER/HFP L3/HFP
18790 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2017-06-10 08:12 | 2017-06-10 09:33 | 2 | 81 | 4928501 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ***SEE H4928501*** 2 CUST PART OUT ORIGINALLY/ OPENED XMF AT 0906 APR AT 0933 (2 ADD CUST)/, FOUND SEVERAL BAD CONN ON XMF, PLEASE SEND COPY TO STEVE M XMF AND RISER, ALSO A SHORT SPAN OF SEC NEEDS UPGRADED, POSSIBLY REPLACEING POLE ALSO. APR AT 0933 CLOSE TICKET/ ISO 38830428000180/ COD 4/ VER/BOW
18791 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-06-05 16:39 | 2013-06-05 18:00 | 2 | 81 | 4223681 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 295-241//CUT IN CLEAR//TRUCK TO POLE//COD 2//ISO 37830295A00173//AED CREATED// VER/DBM
18792 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-05-20 14:16 | 2009-05-20 15:10 | 3 | 54 | 52540-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | VER/HFP OLD SERVICE WIRE WAS CRACKED AT DRIP LOOP, RESAGGED SERVICE AND CUT OUT BAD SPOTS. L3/HFP
18793 | Pikeville | 3413401 | GARRETT | GARRETT | 2014-05-24 18:43 | 2014-05-24 21:25 | 1 | 162 | 4928651 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | REPAIRED SD , ALL WORK COMPLETE / GXJ //VER/GAH
18794 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-05-18 09:13 | 2016-05-18 10:34 | 2 | 81 | 4229101 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON 38831126C30958B AM PATROLLING LINE. REPLACE BAD XFMR CUTOUT ON POLE 38831126C00668// VER/ ADH
18795 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-10-31 11:03 | 2020-10-31 13:45 | 1 | 162 | 4609621 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required bad fuse door
18796 | Pikeville | 3413401 | GARRETT | GARRETT | 2013-07-01 16:19 | 2013-07-01 19:01 | 1 | 162 | 4439331 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/KEP IDC XXXX
18797 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-12-08 07:58 | 2013-12-08 10:40 | 1 | 162 | 4114851 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN ON POLE 37830295B00066, LINE FUSE BLOWN ON POLE 37830295B00347 --- REPLACED CUTOUT, POWER RESTORED.. VER/SEF L3/HFP
18798 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-12-07 07:48 | 2022-12-07 10:30 | 1 | 162 | 4237001 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer had both hot legs burnt up at xformer pole 90-C2-142 had to open xformer and make repires got power restored at a time of 10:30
18799 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-06-02 18:36 | 2009-06-02 21:18 | 1 | 162 | 61202-1 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTION ON POLE VER/KEP L3/KEP
18800 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-11-05 14:52 | 2011-11-05 15:10 | 9 | 18 | 4052811 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NEUTRAL PROBLEM ON UNDERGROUND. NEED CREW// OPENED XFMR AT 14:52 CLOSED AT 15:10, POWER RESTORED//COD 9// VER/DBM IDC XXXX
18801 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2017-07-25 12:28 | 2017-07-25 15:10 | 1 | 162 | 4178081 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CON AT TRAN--REPAIRED--ALLGOOD--DS072517 VER/CRB L3/HFP XXXHFP
18802 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2011-05-23 15:09 | 2011-05-23 16:30 | 2 | 81 | 4146171 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR #40076636 POLE 45-5638 BAD LA POLE 45-5884 10T COD-2 ISO LF 38830045C45638 VER/HFP L3/HFP
18803 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2022-01-26 08:23 | 2022-01-26 09:44 | 2 | 81 | 4405391 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken transformer cutout on pole 38830046B12131, repaired and restored @ 09:44
18804 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2012-09-09 11:43 | 2012-09-09 14:25 | 1 | 162 | 4033701 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN ON XFMR POLE. <<ONE CUSTOMER AFFECTED>> REPAIRED. SH ///VER/CRB L/3 CRB IDC XXXX
18805 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-04-09 09:55 | 2009-04-09 10:22 | 6 | 27 | 50709-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3309001//PRIMARY HAD COME OFF OF INSULATOR... SERVICER OPENED LINE FUSE IN ORDER TO MAKE REPAIRS//COD 6// VER/DBM IDC XXXX
18806 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-11-12 20:09 | 2013-11-12 21:30 | 2 | 81 | 4033641 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/CRB
18807 | Hazard | 3302703 | HAZARD | HAZARD | 2012-12-26 11:48 | 2012-12-26 14:30 | 1 | 162 | 4526671 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSFORMER, CREW WILL REPLACE 12-27-12 OPS ORDER 030751968 CREATED AND SENT TO G SHOUSE, PLEASE CLOSE THIS TICKET.--- OK,D BY CUSTOMER TO WAIT. //VER/GAH
18808 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-10-20 19:14 | 2014-10-20 20:35 | 2 | 81 | 4647631 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RESTORED @ 20:35. SH//COD 2// VER/ ADH
18809 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-12-29 03:33 | 2016-12-29 06:15 | 1 | 162 | 4247531 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. DIFFICULT LOCATION. REPLACED AND RESTORED @ 6:15. SH/// VER/DKM
18810 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-08-28 10:41 | 2019-08-28 11:35 | 3 | 54 | 4955991 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burned up, transformer fuse back in at 11:35. Transformer on 20-c2-4559 leaking bad. Will need changed out, and oil spill clean up at later date. Please email copy to Vernon Mullins. 25kva 7200, trucks to pole. Need flaggers//SENT TO TECH AND LINE
18811 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-06-24 05:58 | 2011-06-24 08:40 | 1 | 162 | 4407121 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHG CUTOUT//VER/CRB IDC XXXX
18812 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2008-08-30 19:46 | 2008-08-30 22:28 | 1 | 162 | 57893-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURN UP.REPLACED CUTOUT DOOR. VER/PDP IDC XXXX
18813 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-11-24 15:23 | 2010-11-24 18:05 | 1 | 162 | 59384-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE LEAD BURN IN CLEAR///MADE NEW CONNECTION..//COD 1// VER/DBM IDC XXXX
18814 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2019-12-02 14:26 | 2019-12-02 17:08 | 1 | 162 | 4116601 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt down at pole 45-4537, connections at sec pole. no trks. behind 924 ashland ave Released by crew 078S07///installed new 2/3 drop///complete BR
18815 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-05-01 18:39 | 2019-05-01 20:00 | 2 | 81 | 4196231 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | XFRF IS OUT,WILL RE-FUSE/////////SPAN OF IA 4/2 DD CABLE HAD SHORTED OUT,BLEW XFRF.I REMD 4/2 CABLE,RE-FUSED&RESTORED POWER//COD 2 PER SERVICER L3/HFP
18816 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-05-20 17:27 | 2009-05-20 18:21 | 3 | 54 | 53680-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE ON XFMR, REPLACED FUSE//VER/CRB
18817 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-02-28 22:54 | 2014-02-28 23:48 | 3 | 54 | 4439581 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DUE TO BAD CURRENT LIMIT FUSE BURNING. I OPENED TRANSFORMER ON POLE 140-22 AT 22:54 CLOSED TRANSFORMER BACK IN AT 23:48 REPAIRS MADE EVERYTHING OK TR NEVER OPEN TWICE ... HOIS. IDCC CNT6, TOF2254 2/27 XXXX
18818 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-03-20 12:20 | 2015-03-20 13:14 | 3 | 54 | 4213331 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD BROKEN INTO COD-3 ISO TF 37830054000001 VER/HFP L3/HFP
18819 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-06-14 13:41 | 2008-06-14 14:35 | 3 | 54 | 64693-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN DUE TO AGE / GXJ//3402204//VER/CRB
18820 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-05-03 07:37 | 2010-05-03 10:19 | 1 | 162 | 54790-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP IDC XXXX
18821 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2022-01-30 10:29 | 2022-01-30 11:50 | 2 | 81 | 4416211 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | lead burned out of xfmr.. chg lead.
18822 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-02-25 07:28 | 2013-02-25 10:10 | 1 | 162 | 4843631 | 162 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER AT 10:00, REMADE CONNECTIONS AT TRANSFORMER, RESTORED POWER AT 10:10, ONLY 1 CUSTOMER WITH PART POWER. VER/KEP IDC XXXX
18823 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-01-05 17:38 | 2012-01-05 20:20 | 1 | 162 | 4236141 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN COD-1 ISO TF 39831123A41523 VER/HFP L3/HFP IDC XXXX
18824 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2010-04-13 12:03 | 2010-04-13 14:45 | 1 | 162 | 62718-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT MAY BE BAD. I AM GOING TO REFUSE TRANS. I JUST HAD TO CHANGE CUTOUT DOOR. VER/KEP L3/KEP IDC XXXX
18825 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-02-23 10:18 | 2009-02-23 13:00 | 1 | 162 | 50608-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE IN HOT LEG OF SERVICE REPAIRED ON AT 13:00 D SAMMONS 2/23/09 // VER/TOM L3/TOM IDC XXXX
18826 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-02-02 12:39 | 2011-02-02 14:00 | 2 | 81 | 53436-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 140-449 BAD 19.9 CUTOUTS AND LA VER/KEP IDC XXXX
18827 | South Williamson | 3411401 | DEWEY | INEZ | 2011-06-05 11:30 | 2011-06-05 14:12 | 1 | 162 | 4236401 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER OUT ON POLE 38830601C00233// CUTOUT BROKEN// CHANGING NOW// SERVICE RESTORED AT 14:12// CHECKING ANOTHER HAZARD//VER/CRB IDC XXXX
18828 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-03-06 17:33 | 2008-03-06 20:15 | 1 | 162 | 54387-1 | 162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308503 /// BAD CONNECTION ON XFMR POLE --- ELECTRICIAN PULLED METER BEFORE SERVICER ARRIVED//HFP VER/HFP IDC XXXX
18829 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2020-05-13 14:46 | 2020-05-13 17:10 | 2 | 144 | 4832631 | 161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Netural and 1 hot wire brunt into mid span calling for help opened at 16:53 closed at 17:10 repaired secondary
18830 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-10-27 11:58 | 2015-10-27 14:39 | 1 | 161 | 4380051 | 161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | FOUND A BAD CONNECTION WHERE SERVICE WAS SPLICED MID SPAN . HAVE REPLACED SERVICE/ ISO 38831125C10258/COD 1/ VER/BOW
18831 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-03-26 14:12 | 2014-03-26 14:35 | 7 | 23 | 4526931 | 161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CRACKED LINE FUSE CUTOUT ON POLE 37830296C21122, OPENED LINE FUSE AT 14:12, CLOSED AT 14:35 VER/SEF
18832 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2009-02-17 08:14 | 2009-02-17 10:55 | 1 | 161 | 63010-1 | 161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 50 KVA XFMR 120/240 7200 NEEDS REPLACED CALLING FOR CREW TO ASSIST//RESTORED COMPLETE L3/HFP
18833 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-06-21 10:14 | 2016-06-21 12:55 | 1 | 161 | 4394871 | 161 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEURTAL BROKE IN SECONDARY, HAVE RESAGGED AND REPAIRED SEC, AT THIS LOC, BY AMG VER/CRB
18834 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2008-02-26 17:12 | 2008-02-26 17:35 | 7 | 23 | 50625-1 | 161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410601// CUTOUT IS CRACKED. WILL HAVE TO ISOLATE XFMR BANK ON THIS POLE TO CHANGE. OTHER TWO CUTOUTS ARE DEFECTIVE TYPE - WILL CHANGE THEM ALSO. OPENED AT 17:12. CLOSED AT 17:35. REPAIRS COMPLETE. SH// VER/TOM IDC XXXX
18835 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-07-23 21:44 | 2010-07-24 00:25 | 1 | 161 | 56213-1 | 161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOOKS LIKE BAD CUTOUT DOOR. I AM GOING TO PUT NEW DOOR IN CUTOUT. VER/ARN IDC XXXX
18836 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-01-03 06:19 | 2008-01-03 09:00 | 1 | 161 | 53086-1 | 161 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3402002///CONNECTION AT TRANSFORMER BURN IN TWO//VER/CRB IDC XXXX
18837 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-11-09 10:39 | 2014-11-09 13:20 | 1 | 161 | 4714851 | 161 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND/ SEND CREW/ NEED TEP INSTALLED/ SEND COPY TO BOBBY REYNOLDS/ ISO 38830091C00454/ COD 1/ VER/BOW
18838 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-03-07 06:02 | 2012-03-07 08:43 | 1 | 161 | 4559131 | 161 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP NEEDS YO BE REPAIRED///////BAD SERVE-IN CONNECTION HEATED UP,BURNED 1 LEG AND NEUTRAL INTO,MADE NECESSARY REPAIRS AND RESTORED,NOBODY HOME //VER/CRB IDC XXXX
18839 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-04-03 12:49 | 2019-04-03 15:30 | 1 | 161 | 4053971 | 161 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr leads, cant use split bolts anymore so i have to sit here and wait on crew, connections being brought from storeroom, all power restored L3/HFP
18840 | South Williamson | 3411401 | DEWEY | INEZ | 2015-06-28 15:49 | 2015-06-28 18:30 | 1 | 161 | 4687981 | 161 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD SPOT IN SERVICE/NEUTRAL//MAKING REPAIRS///MADE REPAIRS///CUST BACK ON AT 18:30///COMPLETE BR/ ISO 38830648A00552/ COD 1/ VER/BOW
18841 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-11-17 11:24 | 2008-11-17 14:05 | 1 | 161 | 65935-1 | 161 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP SECONDARY CONNECTION BURNED INTO IDC XXXX
18842 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2019-09-21 22:19 | 2019-09-22 01:00 | 1 | 161 | 4045351 | 161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced/ tree did fall and brush line but didnt cause line to break. conducttor ha 6 splices in conductor that were burnt up and needed changed./ ISO 39830901C45586/ COD 1
18843 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-01-28 09:59 | 2018-01-28 11:19 | 2 | 80 | 4778671 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | take clamp off at10 40 and back on at 1119 got pole put out and change cutout/ ISO 37830124000105/ COD 2
18844 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-04-17 19:22 | 2013-04-17 20:42 | 2 | 80 | 4020351 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE////////////REPLACED CUTOUT AND RESTORED,ALL OK AFTERWARDS ///VER/CRB L/3 CRB IDC XXXX
18845 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-03-26 19:37 | 2014-03-26 20:57 | 2 | 80 | 4527571 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED BROKEN FUSE LINK COD-2 ISO TF 38830202000079 VER/HFP L3/HFP IDC XXXX
18846 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-03-14 20:30 | 2008-03-14 20:50 | 8 | 20 | 57274-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFOMER//3308602//VER/CRB IDC CHANGED TOF FROM 1912, FIRST CALL FLICKERING XXXX
18847 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-08-10 11:15 | 2011-08-10 12:35 | 2 | 80 | 4692171 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL REPLACE CONNECTIONS AT SERVICE POLE VER/KEP IDC XXXX
18848 | Hazard | 3302704 | HAZARD | KENMONT | 2018-01-18 16:35 | 2018-01-18 19:15 | 1 | 160 | 4755901 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole/ ISO 37830296C20603/ COD 1
18849 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-07-10 11:16 | 2016-07-10 12:36 | 2 | 80 | 4604011 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS BROKEN NOT BLOWN REFUSED XMF APR AT 1236 CLOSE TICKET/ ISO 38830478A31044/ COD 2/ VER/BOW
18850 | Pikeville | 3413401 | GARRETT | GARRETT | 2017-03-14 13:45 | 2017-03-14 14:25 | 4 | 40 | 4555811 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO INTERRUPTION UNTIL XFMR OPENED AT 13:45, REPLACED CUTOUT AND ARRESTER AND RESTORED SERVICE AT 14:25 , ALL WORK COMPLETE / GXJ/ ISO 37830065A00515/ COD 4/ VER/BOW
18851 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2018-06-22 15:25 | 2018-06-22 16:45 | 2 | 80 | 4645331 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire // 738-416 // repairing now// had xfrms on 738-32 and 738-416 open from 15:25 to 16:45 // repairs complete// 2 customers out
18852 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-04-04 17:05 | 2013-04-04 18:25 | 2 | 80 | 4979511 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGE OUT BAD 19.9 KV CUTOUT COD-2 ISO PO 37830387D00492 VER/HFP L3/HFP IDC XXXX
18853 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2011-04-20 11:16 | 2011-04-20 13:56 | 1 | 160 | 61178-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39646292 // BROKEN TRANSFORMER CUTOUT. MAKING REPAIRS VER/KEP IDC XXXX
18854 | Hazard | 3309302 | VICCO | JEFF | 2022-10-21 09:34 | 2022-10-21 12:14 | 1 | 160 | 4050571 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva 19.9 transformer on pole 37830323C40751 Released by crew 077H05..replaced xfmr
18855 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2010-11-06 08:54 | 2010-11-06 10:14 | 2 | 80 | 53427-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT //VER/CRB IDC XXXX
18856 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2014-07-04 12:16 | 2014-07-04 14:56 | 1 | 160 | 4192791 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VERY POOR CONNECTIONS ON UG SERV AT XFR RISERS,REPLACED,ALL OK AFTERWARDS COD-1 ISO SO @ 38820991D40263 VER/HFP L3/HFP
18857 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-01-25 22:30 | 2022-01-25 22:50 | 8 | 20 | 4404801 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Opened xfm @ 22:30 to replace burnt up piece of 1/0 secondary///Replaced burnt section and restored @ 22:50////Send copy to Ryan Thornberry to write up job to change 1/0 secondary may need upgraded
18858 | Hazard | 3309302 | VICCO | JEFF | 2013-07-09 10:51 | 2013-07-09 11:23 | 5 | 32 | 4491541 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ASSOCIATED WITH ORDER 4490341 // OPENED TAP TO SAFELY REPLAE TRANSFORMER// 1052 -1116 IDCC CNT6 XXXX
18859 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2016-09-30 11:20 | 2016-09-30 14:00 | 1 | 160 | H4947021 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | 480V METER BLOWN OUT OF METERBASE POLE 39830878D34679 (1 CUST ORIGINALLY) SERVICE OUTAGE, NEED TO GET METER ELECTRICAN TO LOOK AT THIS AND SEE WHAT WE NEED TO DO/ ISO 39830878D34703/ COD 2/ OPENED LINE FUSE 39830878D34703 (1 ADD CUST) @1120 HAVE ALL REPAIRS MADED AND HAVE CHECK EVERYTHING OUT, ALL IS GOOD AT THIS LOC BY AMG, 39830878D34703 TIME ON WAS 1400/ DUPLICATE IN HOIS/ VER/BOW
18860 | Pikeville | 3413402 | GARRETT | LACKEY | 2010-01-14 17:28 | 2010-01-14 20:08 | 1 | 160 | 54295-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE IN OPEN WIRE SEC. SPAN OF OPEN WIRE DOWN. I HAVE WIRE UP EVERYTHING OK.// VER/DBM IDC XXXX
18861 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-03-21 08:45 | 2008-03-21 09:05 | 8 | 20 | 59646-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3409301/ SECONDARY BURNED DOWN AT XFMR RISER CONNECTION. REPAIRS COMPLETE. SH//COD 8// VER/DBM IDC CHANGED TIME OFF FROM 0725 ALLOWED 20 MIN FOR REPAIR XXXX
18862 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-05-01 18:40 | 2009-05-01 20:00 | 2 | 80 | 62657-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN COD-2 VER/KEP L3/KEP IDC XXXX
18863 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-02-09 07:00 | 2011-02-09 09:40 | 1 | 160 | 55505-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER OUT DUE TO BAD CURRENT LIMIT FUSE. I WILL BE MAKING REPAIRS. ARRESTER WAS ON THE LINE SIDE OF THIS CURRENT LIMIT FUSE. NOT SURE IF IT MAKES A DIFFERENCE IF ON LINESIDE OF CURRENT FUSE OR LOAD SIDE. THESE CURRENT LIMIT FUSE HAVE BEEN CAUSING PROBLEMS FROM THE TIME THEY WERE INSTALLED. SEND COPY TO BOB SHURTLEFF PIKEVILLE. AND TOM MAMING PIKEVILLE.//COD 1// VER/DBM IDCC PN128 XXXX
18864 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-05-08 17:40 | 2022-05-08 19:00 | 2 | 80 | 4866641 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfmr cutout/ replaced power restored 1900
18865 | Hazard | 3303902 | LESLIE | WOOTON | 2013-08-20 19:05 | 2013-08-20 21:45 | 1 | 160 | 4684211 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN, CHANGED OUT, POWER RESTORED. SPECTRUM SHUT DOWN AGAIN, SORRY I COULDNT SEND UP DATE. VER/CRB L/3/CRB IDC XXXX
18866 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-07-31 20:45 | 2012-07-31 21:05 | 8 | 20 | 4874361 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED LINE FUSE TO REPLACE BROKEN CUTOUT THAT HE FOUND ON ORDER 4871741 // COD-8 ISO LF 38830955B00557 - OPENED AT 2045 AND CLOSED AT 2105 VER/TOM L3/TOM
18867 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-03-05 00:25 | 2008-03-05 00:33 | 20 | 8 | 53548-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007904/// CREW OPENING RECLOSER TO ALLOW THEM TO MAKE UP LOOPS ON ORDER 52622-1// VER/HFP IDC XXXX
18868 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-10-26 19:59 | 2013-10-26 20:39 | 4 | 40 | 4966681 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON POLE 472-219, X-FMR CUT-OUT GATE IS BLOWN IN-TO. GOING TO GO UP AND LOOK SITUATION OVER. REPLACED CUT-OUT GATE AND RESTORED POWER AT 20:39. X-FMR CHECKED GOOD AND CUT-OUT AND ARRESTER LOOKED GOOD AS WELL. 10/26/2013. J.S.B. COD-4 ISO TF 37830472000219 VER/HFP L3/HFP
18869 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-12-09 12:05 | 2013-12-09 14:45 | 1 | 160 | 4137131 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY NUETRAL BURNT INTO GOING TO REPAIR.REPAIRED SECONDARY GOOD VOLTAGE 125/125/250 COMPLTED VER/CRB L3/HFP
18870 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-08-22 16:14 | 2022-08-22 17:34 | 2 | 80 | 4781251 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o.. replaced
18871 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-01-24 14:37 | 2016-01-24 17:17 | 1 | 160 | 4647381 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | INSTALLED ALL NEW DROP AT THIS LOC, IN ORDER TO SOLVE THIS PROBLEM, PROBLEM IS SOLVE AT THIS LOC// ISO 3983104800008/ COD 1/ VER/BOW
18872 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-02-10 02:55 | 2013-02-10 04:15 | 2 | 80 | 4805711 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SEC/ SPLICE HAS BURNED OPEN// WILL REPAIR// OPENED TR FUSE AT 0255 //REPAIRED SEC.// ALSO REPAIRED CUST HSE. KNOBTHAT WAS PULLED OUT// POWER IS RESTORED.// THIS IS 2 LONG SPANS OF 2/3 SEC. THAT FEEDS CUST. MAY NEED TO BE CHANGED TO 1/0 ///PLEASE SEND TO C. FREEMAN //VER/GAH IDC XXXX
18873 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2010-09-07 15:05 | 2010-09-07 17:45 | 1 | 160 | 64315-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 36771580 // BAD 50 KVA, 7200 RELEASED BY CREW 078H12/J. HEMLEPP & CREW ON SITE///XFMER CHANGE OUT COMPLETE CUST. RESTORED @17:45 078H05 J. HEMLEPP // COD-1 VER/HFP L3/HFP IDC XXXX
18874 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2021-01-16 17:02 | 2021-01-16 19:42 | 1 | 160 | 4873151 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Travis Burton called and reports customer is getting 140/280 voltages and the transformer is bad // 15 KVA 7200 120/240 and truck accesscrew onsite to change xfmr on 1098-3145/crew onsite to change xfmr on 1098-3145/ opened LF on 1098-3059 @1930/ closed in @ 1942/ voltage on mtr # 533 744 727 @ 125/250v/ please close ticket/ MLH
18875 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-04-13 09:50 | 2016-04-13 10:30 | 4 | 40 | H4087421 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/0 SECONDARY BURNED INTO.OPENED XFMR ON 875-198..AT 09.50 CLOSED BACK IN AT.10.30.// VER/ ADH
18876 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2014-12-21 09:30 | 2014-12-21 12:10 | 1 | 160 | 4872981 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER CSP NEED A LINEMAN AND BUCKET...7200 CUTOUT AND 50 KVA TRANS./ ISO 37820125000124/ COD 1/ VER/BOW
18877 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-02-09 11:45 | 2010-02-09 12:25 | 4 | 40 | 54251-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNING DUE TO BAD CUTOUT. I WILL BE CHANGING OUT .I HAVE CUTOUT CHANGED OUT EVERYTHING OK. SEND COPY TO ROW PIKEVILLE TREE NEEDS TO BE CUT BETWEEN POLE 67A2 AND 67A3 1/0 LASH RUNS THROUGH TREE.//VER/CRB IDCC , TOF1035, NOT SURE IF POLE 73 OR POLE 2 WAS THE ONE OPENED XXXX
18878 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-12-26 11:40 | 2019-12-26 12:00 | 8 | 20 | 4182481 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found cutout cracked on pole 261-129..this is what customer was hearing making buzzing sound..replaced and restored.
18879 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2012-04-04 09:35 | 2012-04-04 12:15 | 1 | 160 | 4645861 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED/REPLACED CONNECTIONS// VER/DBM IDC XXXX
18880 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-01-05 07:40 | 2011-01-05 09:00 | 2 | 80 | 58804-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 38322525 //C/L FUSE BAD VER/KEP L3/KEP IDC XXXX
18881 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2013-05-27 09:01 | 2013-05-27 11:41 | 1 | 160 | 4187691 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1123-1100 BAD 25 KVA TRUCK TO POLE // LINKOUS & MCCOY & VIRGIN //CHANGED 25KVA///PWR CK GOOD//124/124/248V/// COD-1 ISO TF 39831123A31100 VER/SEF IDC XXXX
18882 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-11-22 12:08 | 2020-11-22 12:40 | 5 | 32 | 4714901 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Splice went bad and burndt a service down going to a storage building, will have to open trans. to make repairs, will keep track of times. Opened trans. @1208, made repairs and closed back in @1240. Only 1 customer out until I opened trans.
18883 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-12-03 13:30 | 2018-12-03 14:50 | 2 | 80 | 4504511 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm. cutout on pole 190B-314..will make repairs..restored..//MADE MD TO SHOW MIS-MAPPED CUST//COD 2// L3/HFP
18884 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-09-29 14:00 | 2009-09-29 16:40 | 1 | 160 | 55740-1 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN SD, REPAIRED MP RELEASED BY CREW 078H12.//VER/CRB
18885 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-03-30 08:25 | 2008-03-30 11:05 | 1 | 160 | 62085-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308603//TRANSFORMER RISER WAS LOOSE AND FELL OF (HOTLINE CLAMP WAS BAD) VER/LDA IDC XXXX
18886 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-10-02 16:10 | 2009-10-02 17:30 | 2 | 80 | 65442-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER WENT BAD ON TRANSFORMER//VER/CRB IDC XXXX
18887 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-06-20 18:19 | 2018-06-20 18:39 | 8 | 20 | 4630281 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opened @ 18:19 restored at 18:39. hot leg burnt down against guy wire. pls close. tre.
18888 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-06-13 18:13 | 2019-06-13 19:33 | 2 | 80 | 4501911 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | current limiting fuse gone bad. repairs made. pls close. tre
18889 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-09-26 12:25 | 2014-09-26 13:05 | 4 | 40 | 4530671 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING TRANSFORMER @ 39831024A00186///PWR OFF @ 12:25---BACK ON @ 13:05--OPENED SECONDARY LOOP TO MAKE REPAIRS-TBL TKT COMP// NO SWITCH ON 39831024A00186// VER/BOW
18890 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-04-02 10:56 | 2018-04-02 11:36 | 4 | 40 | 4164391 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | wire down at pole 57 opened at 10:56 to make repairs closed back at 11:36
18891 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-03-18 11:30 | 2022-03-18 12:50 | 2 | 80 | 4638621 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored at 12:50
18892 | Hazard | 3301101 | CHAVIES | CHAVIES | 2014-02-06 11:50 | 2014-02-06 14:30 | 1 | 160 | 4362691 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE HAVE BROKEN C/O, GOT JIM MULLINS COMMING TO GRUNT FOR ME, MANUAL,//// C/O CHANGED OUT POWER RESTORED IDC XXXX
18893 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-09-21 09:49 | 2019-09-21 11:09 | 2 | 80 | 4044211 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate had burndt into @4-241, got replaced @1109.
18894 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-02-19 18:04 | 2016-02-19 18:20 | 10 | 16 | 4737761 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND TRANSFORMER SECONDARY BUSHING ARCING. OPENED XFMR 834-135 @ 18:04, REWORKED XFMR CONNECTIONS AND CLOSED @ 18:20. SH// TREE THROUGH ALL 3 PHASES AT POLE 834-A-134/EMAILED ROW/ADH
18895 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2015-07-07 23:55 | 2015-07-08 00:05 | 16 | 10 | 4741521 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON POLE ..OPENED @23:55 CLOSED @00:05/ ISO 38830954B40040/ COD 16/ VER/BOW L3/DKG
18896 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-04-06 12:18 | 2015-04-06 14:58 | 1 | 160 | 4280401 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT BROKE 19.9 CUTOUT ON BANK OF TRANSFORMER CUTOUT WAS ON POLE37830005000040 NOT 5-39 AND THIS SERV ONE CUST VER/CRB
18897 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-04-28 18:05 | 2011-04-28 20:45 | 1 | 160 | 51897-1 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG. NEED POWER TEMP. RELEASED BY CREW 078S01 //VER/GAH IDC XXXX
18898 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-10-02 10:55 | 2012-10-02 12:15 | 2 | 80 | 4107301 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AM WAITING ON COVER UP TO CHANGE BAD CUTOUT.//COD 2// VER/DBM IDC XXXX
18899 | Hazard | 3310502 | HADDIX | CANOE | 2018-10-18 08:28 | 2018-10-18 11:08 | 1 | 160 | 4265161 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | service netural pull out of splice
18900 | Paintsville | 3401802 | INDEX | HOSPITAL | 2018-02-02 12:40 | 2018-02-02 15:20 | 1 | 160 | 4795211 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired loose connection at xfmr , ALL WORK COMPLETE / GXJ
18901 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-11-16 00:10 | 2013-11-16 00:30 | 8 | 20 | 4043011 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 245-22. OPENED XFMR @ 00:10 , CLOSED BACK IN @ 00:30 VER/HFP L3/HFP
18902 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2020-04-28 21:35 | 2020-04-28 22:55 | 2 | 80 | 4764011 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 2 paddles burndt up on 1 phase of customers 3 phase paralel service coming from padmount 1151-D3-889, will have to open up 3 URD risers @1151-D3-960 to isolate trouble, Miles Robinette coming to make repairs, opened all 3 risers @2135. Made repairs and closed all 3 risers back @2255.
18903 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-06-19 15:50 | 2009-06-19 18:30 | 1 | 160 | 57605-1 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | VER/HFP LYNCHS CREW TO WORK RELEASED BY CREW 078S07 L3/HFP IDC XXXX
18904 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-07-18 18:19 | 2015-07-18 20:59 | 1 | 160 | 4908161 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE GOING TO CHANGE OUT/ ISO 38831111000034/. COD 1
18905 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-06-25 10:10 | 2019-06-25 12:50 | 1 | 160 | 4591991 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changing bad c/o //power restored at12:50/ ISO 38821081000190/ COD 1
18906 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-06-23 15:50 | 2020-06-23 18:30 | 1 | 160 | 4064711 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke into, need one or two men to change out cutout. I have talked to George Whitaker duty superviser
18907 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-10-18 12:10 | 2021-10-18 13:30 | 2 | 80 | 4362371 | 160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service connection burnt out. replaced
18908 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2014-09-20 19:50 | 2014-09-20 22:30 | 1 | 160 | 4515071 | 160 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 HOT LEG WAS XTREMELY LOOSE AT XFR BUSHING,TIGHTENED,ALL OK AFTERWARDS VER/ARN
18909 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2014-01-07 12:37 | 2014-01-07 13:30 | 3 | 53 | 4251591 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ONLY THREE CUSTOMERS AFFECTED. XFMR FUSE THATS BLOWN IS 38830785D20764. FUSE LINK APPEARS TO HAVE BROKE. WILL TRY NEW FUSE AND SEE IF IT HOLDS. RESTORED @ 13:30. SH //VER/GAH IDC XXXX
18910 | Pikeville | 3413402 | GARRETT | LACKEY | 2013-12-17 11:11 | 2013-12-17 13:50 | 1 | 159 | 4167971 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 6T FUSE BROKE FUSED UP EVERYTHING OK//COD 1 VER/HFP L3/HFP
18911 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-09-14 16:44 | 2020-09-14 17:37 | 3 | 53 | 4463181 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 17:37. sh
18912 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-09-02 08:36 | 2015-09-02 11:15 | 1 | 159 | 4189901 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, BAD CUTOUT. POWER RESTORED/ ISO 37830228000096/ COD 1/ VER/BOW
18913 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-08-18 17:52 | 2022-08-18 18:45 | 3 | 53 | 4762001 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored 18:45
18914 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-01-05 21:27 | 2018-01-05 22:20 | 3 | 53 | 4710811 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
18915 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2021-06-27 18:36 | 2021-06-27 19:45 | 10 | 69 | 4812451 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEGS BURNT IN SECONDARY//WILL HAVE TO OPEN TRANSFORMER TO MAKE REPAIRS//OFF @ 1935 ON @ 1945
18916 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2013-08-07 19:30 | 2013-08-07 20:23 | 3 | 53 | 4633801 | 159 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 3// VER/DBM
18917 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2021-05-20 12:09 | 2021-05-20 14:48 | 1 | 159 | 4603511 | 159 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad CSP XFMR on pole 249-D-72. Ive called for a line crew and they are on their way with a new XFMR.3 and they are on their way with a new XFMR. XFMR replaced and power restored at 14:48.
18918 | South Williamson | 3411401 | DEWEY | INEZ | 2022-03-26 09:16 | 2022-03-26 11:55 | 1 | 159 | 4675881 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN C/O ON POLE 838-A-165&838-C-91////REPAIRS MADE
18919 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-05-01 13:25 | 2008-05-01 14:18 | 3 | 53 | 56001-1 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINK BROKE ON XFMR FUSE//3308502//VER/CRB IDC XXXX
18920 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2017-03-06 19:16 | 2017-03-06 21:55 | 1 | 159 | 4527731 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN / COMPLETE/ ISO 37830020D10217/ COD 1/ VER/BOW
18921 | Hazard | 3303902 | LESLIE | WOOTON | 2011-06-18 17:07 | 2011-06-18 19:46 | 1 | 159 | 4339761 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED C/O. COD-1 IS0 TF 37830366C00243 VER/HFP L3/HFP
18922 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-07-02 14:06 | 2020-07-02 16:45 | 1 | 159 | 4104501 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1.6t fuse out due to bad cutout i will be making repaires. replaced bad cutout everything ok
18923 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2011-08-04 17:16 | 2011-08-04 19:55 | 1 | 159 | 4665351 | 159 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUSTOMER AFFECTED. I RELPLACED A BAD SPLICE IN THE SERVICE DROP.// VER/DBM IDC XXXX
18924 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-01-29 13:17 | 2017-01-29 15:56 | 1 | 159 | 4339861 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE HAS SEVERAL SPLICES WHERE ITS BEEN REPAIRED IN THE PAST. REPLACING WIRE. ONE CUSTOMER AFFECTED. REPLACED AND RESTORED @ 15:50. SH 38830875A00160 38830875A00167 VER/AWD L3/HFP XXXHFP
18925 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-12-27 14:28 | 2022-12-27 15:21 | 3 | 53 | 4367491 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg connection had failed and was smoking, repaired @1521.
18926 | Hazard | 3303902 | LESLIE | WOOTON | 2013-07-01 13:06 | 2013-07-01 15:45 | 1 | 159 | 4437251 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED CUTOUT RESTORED POWER AT 15:45 COD-1 ISO TF 37830510A30232 VER/SEF
18927 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2019-01-27 11:16 | 2019-01-27 13:55 | 1 | 159 | 4725851 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST TWICE & NO ANSWER , bad cutout on pole 351-435, replaced cutout restored power at 13:55..
18928 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-03-31 17:07 | 2015-03-31 18:00 | 3 | 53 | 4251121 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT/ ISO 38830187000106/ COD 3/ VER/BOW
18929 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2015-08-17 16:23 | 2015-08-17 19:02 | 1 | 159 | 4143681 | 159 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER , BAD SD NEED HELP TO REPAIR/ BROKE NEUTRAL AND BAD HOT LEG/ PART POWER RESTORED @ 19:02 PLEASE CLSOE TICKET LRM/ ISO 38830045C24716/ COD 1/ VER/BOW
18930 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-05-27 17:46 | 2012-05-27 20:25 | 1 | 159 | 4835781 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE BURNT DOWN REPLACED WITH 2/3 SERVICE ON //VER/CRB L/3 CRB IDC XXXX
18931 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2017-12-01 07:47 | 2017-12-01 08:40 | 3 | 53 | 4613871 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse link appears to have broke. Restored @ 8:40. sh
18932 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2018-02-07 16:51 | 2018-02-07 19:30 | 1 | 159 | 4814251 | 159 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired loose connection/ ISO 39831099B20067/ COD 1
18933 | Pikeville | 3421001 | BREAKS | CITY | 2021-02-07 09:00 | 2021-02-07 09:53 | 3 | 53 | 4943761 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Secondary connections burnt up///Opened xfm @ 09:00 to make repairs///Replaced burnt up secondary connections and restored service @ 09:53
18934 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-09-04 13:09 | 2018-09-04 15:48 | 1 | 159 | 4041621 | 159 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | looks like 6t transformer fuse broke 1 transformer was out in 3 phase transformer bake. put in new 6t fuse everything ok
18935 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-02-25 13:39 | 2009-02-25 16:18 | 1 | 159 | 51421-1 | 159 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY SHORTED OUT,BURNED NEARLY INTO.MADE REPAIRS AND RESTORED,ALL OK AFTERWARDS // VER/TOM L3/TOM IDC XXXX
18936 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-01-13 16:00 | 2010-01-13 18:39 | 1 | 159 | 53669-1 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, CALLING FOR HELP 3308402 POLE # 255-111 RELEASED BY CREW 077S02 REPLACED TRANSFORMER AND RESTORED POWER JKC//COD 1 IDCC CHANGED TOF FROM 1445 XXXX
18937 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2018-06-05 18:43 | 2018-06-05 19:36 | 3 | 53 | 4559801 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse failed on 991-D4-213.re fused cutout restored power at 19;36
18938 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2018-10-03 07:30 | 2018-10-03 08:23 | 3 | 53 | 4191931 | 159 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke line cutout @ 206-2724,,all customers restored @ 08:23 complete
18939 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-02-23 11:47 | 2015-02-23 14:25 | 1 | 158 | 4075031 | 158 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVE END GOT HOT IN SPLICE IN SERVICE DROP AND BURNED NEUTRAL INTO. I AM GOING TO RESQUEEZE CONNECTIONS. 37830263C00167 //SERVE END GOT HOT IN SPLICE IN SERVICE DROP AND BURNED NEUTRAL INTO. I AM GOING TO RESQUEEZE CONNECTIONS. I RESQUEEZED CONNECTIONS. SEND TO PEGGY WYSONG. CUSTOMER MAY HAVE DAMAGES.2 VER/CRB L3/HFP XXX
18940 | Whitesburg | 3309301 | VICCO | REDFOX | 2008-03-11 16:34 | 2008-03-11 17:53 | 2 | 79 | 56297-1 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 351-348 CUT IN CLEAR/./3309301//VER/CRB IDC XXXX
18941 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2013-03-06 11:47 | 2013-03-06 14:25 | 1 | 158 | 4881531 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE. THIS FUSE IS NOT ON THE MAPS BUT I WILL REPORT SIZE AND POLE # WHEN I GET THEM. CUSTOMER COUNT IS CORRECT - ONE AFFECTED. REPLACED CUTOUT AND CLOSED 30T FUSE ON 678-208 @ 14:25. PLEASE ADD LINE FUSE TO MAPS. SH MD FILED VER/KEP IDC XXXX
18942 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-10-28 13:47 | 2014-10-28 16:25 | 1 | 158 | 4668111 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SERVICER OPENING LINE FUSE 1107-12 TO SAFELY REPLACE POLE 1107-13//COD 1// VER/ ADH AJB CCO FEC57
18943 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-06-06 13:07 | 2017-06-06 15:45 | 1 | 158 | 4916211 | 158 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I INSTALLED A NEW SERVICE DROP/ ISO 37820289A00004/ COD 1/ VER/BOW
18944 | Hazard | 3310502 | HADDIX | CANOE | 2021-10-17 11:04 | 2021-10-17 13:42 | 1 | 158 | 4359231 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on 60 power on
18945 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-02-21 08:51 | 2016-02-21 10:10 | 2 | 79 | 4742141 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW RREQUIRED REPLACED CUTOUT VER/CRB
18946 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-12-21 10:07 | 2017-12-21 12:45 | 1 | 158 | 4662181 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202201//Darren found bad c/o//need crew////////
18947 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-06-26 12:07 | 2016-06-26 14:45 | 1 | 158 | 4478301 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUT OUT ON POLE 817-61. CHANGED CUT OUT AND RESTORE POWER AT 2:45.. TRYING TO FIND AWAY TO SERVICE POLE TO CHECK VOLTAGE.. CALLED CUSTOMER HE SAID WHEN HE WENT BACK OVER THERE DOWN RAILROAD TRACK HE WOULD CHECK VOLTAGE ON HIS SIDE BEFORE TURNING BREAKER BACK ON.. SERVICE LOOKED GOOD GOING TO SERVICE POLE.. COMPLETE RN VER/CRB
18948 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-06-21 09:47 | 2012-06-21 12:25 | 1 | 158 | 4939471 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE TRANSFORMER CUTUT HERE HAS FAILED. CREW ENROUTE. DARRELL CAMPBELL IS ENROUTE TO MAKE REPAIRS HERE. HE WILL LOG IN WHEN HE ARRIVES. // DARRELL CAMPBEL (DHE 859-221-3316) TO MAKE REPAIRS HERE// VER/DBM
18949 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-10-12 10:31 | 2021-10-12 11:50 | 2 | 79 | 4342881 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crack cutout, change cutout
18950 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-12-21 14:27 | 2019-12-21 17:05 | 1 | 158 | 4175111 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on transformer
18951 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-02-21 10:11 | 2009-02-21 11:30 | 2 | 79 | 66502-1 | 158 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | VER/HFP COD-1 REPLACED FUSE ON TRANSFORMER BANK ON A PHASE 6T/BROKE/ L3/HFP IDC XXXX
18952 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-11-16 07:37 | 2011-11-16 10:15 | 1 | 158 | 4081301 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..POLE FIRE..1036C133..TOOK CUTOUT OFFLINE @ 09:50..CAN EXTINGUISH POLE & REPLACE CUTOUT..POLE WILL BE OK UNTIL LATER ..//...FIRE OUT.POLE OK.LOWERED & REPLACED CUTOUT...WILL GENERATE ORDER TO HAVE POLE REPLACED LATER..JRV...11/16/11 VER/KEP IDC XXXX
18953 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-06-20 09:44 | 2016-06-20 12:22 | 1 | 158 | 4390411 | 158 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BURNT IN TWO DUE TO INSULINK CONNECTION FAILURE. REPLACED CONNECTIONS AND REPAIRED NEUTRAL. SH VER/CRB
18954 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2019-11-05 09:22 | 2019-11-05 12:00 | 1 | 158 | 4293171 | 158 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired onnections on pole
18955 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-03-07 09:27 | 2015-03-07 12:05 | 1 | 158 | 4156101 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. WILL BE OUT OF TRUCK CHANGING CUTOUT. DUE TO BAD CUTOUT I OPENED 3 POLE SIDE TAP ON POLE 810-C-42 AT 11:22 AND CLOSED SIDE TAP BACK IN AT 12:05/FIX IT IN HOIS/ LINE FUSE THEN HARVEY OPENED TRANSFORMER AND SIDE TAP TO FIX BAD CUTOUT// VER/ ADH
18956 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-01-10 17:21 | 2021-01-10 18:40 | 2 | 79 | 4860001 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 18:40. sh
18957 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-11-23 10:31 | 2021-11-23 11:50 | 2 | 79 | 4118471 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1150xfmr fuse melted out.re fusing
18958 | Whitesburg | 3401301 | FLEMING | NEON | 2015-09-12 15:23 | 2015-09-12 16:42 | 2 | 79 | H4231761 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O ON POLE 355-321, WILL HAVE TO OPEN 3 L/F AT POLE 355-27 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED L/F AT 1523. MADE REPAIRS AND CLOSED LINE FUSES AT 1642.// VER/ ADH
18959 | Hazard | 3310502 | HADDIX | CANOE | 2011-06-26 11:42 | 2011-06-26 13:01 | 2 | 79 | 4415931 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION ON TRANSFORMER//VER/CRB IDC XXXX
18960 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2012-01-02 21:41 | 2012-01-02 23:00 | 2 | 79 | 4227011 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR ON BOX TYPE CUTOUT, CHANGED CUTOUT, ALL POWER ON VER/ARN IDC XXXX
18961 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-10-21 09:22 | 2013-10-21 12:00 | 1 | 158 | 4950831 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN ON WEATHERHEAD. REPAIRED AND RESTORED @ 12:00. SH VER/HFP L3/HFP
18962 | Pikeville | 3413401 | GARRETT | GARRETT | 2020-12-03 10:46 | 2020-12-03 12:05 | 2 | 79 | 4741591 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t fues out looks like fuse ha broke . fused up everything ok
18963 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2019-12-02 09:04 | 2019-12-02 10:23 | 2 | 79 | 4115061 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Power on replaced cutout on pole 37830443000008
18964 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-06-17 14:15 | 2020-06-17 16:53 | 1 | 158 | 4035201 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | line fuse on 1126-71 is out. wire down from 1126-71 to 1126-284
18965 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-07-27 11:11 | 2018-07-27 12:30 | 2 | 79 | 4862661 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke, back in at 12:30
18966 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-08-16 10:23 | 2016-08-16 11:42 | 2 | 79 | 4792901 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CASE 680180 LOAD TRANSFER TO REPLACE POLE 205-123 SEE PO 4783201 VER/KEP
18967 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-01-25 19:11 | 2018-01-25 20:30 | 2 | 79 | 4773971 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//NEIGHBORS ALSO OUT// Transformer fuse link broke. Restored @ 20:30. sh
18968 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-12-13 12:56 | 2018-12-13 14:15 | 2 | 79 | 4562021 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm door burnt up L3/HFP
18969 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2016-09-03 21:14 | 2016-09-03 22:33 | 2 | 79 | 4867251 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | X-2 SEC. NETRUAL BUSHING WAS BROKE,LOSS OF GROUND..REPLACE BUSHING ..CUSTOMER STATES LIGHTS BULBS BLOWN AND COULD SMELL WIRES OF REFRIGERATOR LIKE IT WAS BURNT,KICK TV OFF,,ALSO TREE BEHIND TRANSFORMER POLE IS LEANING AND HOLLOW, NEED TO BE CUT ,CAN PULL BUCKET TRUCK TO TREE,,SEND COPY OF TICKET TO JONATHAN WATTS IN HAZARD.. OPEN TRANSFORMER AT 22:18 // EMAILED TO WYSONG VER/TOM L3/TOM
18970 | Pikeville | 3421001 | BREAKS | CITY | 2014-10-15 00:25 | 2014-10-15 01:44 | 2 | 79 | 4629771 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE ON POLE #243-B-131 WILL CHANGE/// LIFTED HOT TAP ON POLE 243-B-19 @ 1:25 MADE REPAIRS AND PUT HOT TAP BACK ON @ 01:44 AND RESTORED SERVICE VER/CRB L3/HFP HFPC CDCPO
18971 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2016-04-10 18:55 | 2016-04-10 21:33 | 1 | 158 | 4078191 | 158 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SECONDARY CONNECTIONS ON 81-D-515 REPLACED CONNECTIONS HAD 1 CUSTOMERS POWER OFF FROM 21:09 TO 21:33
18972 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-09-16 21:11 | 2018-09-16 22:30 | 2 | 79 | 4108941 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, made repairs restored power at 22:30..
18973 | Hazard | 3310502 | HADDIX | CANOE | 2021-08-31 14:22 | 2021-08-31 17:00 | 1 | 158 | 4185501 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout on pole 168-20. replaced and restored power at 17:00
18974 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-09-20 09:07 | 2020-09-20 10:26 | 2 | 79 | 4479611 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repair servie
18975 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-02-21 14:26 | 2010-02-21 17:04 | 1 | 158 | 59531-1 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTING ARRESTOR BAD ON POLE 172-59 GOING TO CUT IN CLEAR// COD 1// VER/DBM IDC XXXX
18976 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2022-09-29 12:06 | 2022-09-29 13:25 | 2 | 79 | 4936901 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Working on with meter electrians on meterering. Opening xfrm bank on pole 328C-165 to safely do work. Opened up at 12:06 and closed at 13:25.
18977 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2009-02-18 14:00 | 2009-02-18 15:19 | 2 | 79 | 64163-1 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2206403// POLE TOP BURNT OFF 40/5 SHOULD BE ABLE TO LOWER CONDUCTORS AND XFORMER TRUCK OK 3 MEN RELEASED BY CREW 078S11//OPENED FUSE ON POLE 214-18 TO ISOLATE FAULT POLE//COD 2//FUSE NOT ON MAP//MD FILED//ISO 38830214000018//CREW ON SITE/RELOCATING XFMR/FETR// VER/DBM IDCC TOF1138 ESTIMATED TIME OFF XXXX
18978 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-12-05 14:33 | 2016-12-05 15:52 | 2 | 79 | 4166841 | 158 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN. @ WEATHERHEAD BAD . REPAIRED CONN. ONLY 1 CUST. WITH PART POWER . 37830248A00117 1 VER/AWD
18979 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-10-02 12:01 | 2009-10-02 13:20 | 2 | 79 | 64727-1 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ...CHG CUTOUT..BB//VER/CRB IDC XXXX
18980 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-09-17 07:36 | 2011-09-17 08:55 | 2 | 79 | 4878921 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. //VER/CRB IDC XXXX
18981 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2020-07-13 08:01 | 2020-07-13 09:20 | 2 | 79 | 4157871 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad cutout. apr at 0920 close ticket
18982 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-06-08 23:08 | 2019-06-09 00:27 | 2 | 79 | 4464191 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE IT///////////REPLACED BROKEN XFR CUTOUT&RESTORED,ALL OK AFTERWARDS////////WAS ACTUALLY ON POLE 51-159
18983 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2022-05-31 08:12 | 2022-05-31 10:50 | 1 | 158 | 4986231 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required ,,bad cutout in back yard, no truck 206-2276 Released by crew 078S05.complete time on 10:50
18984 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-06-02 09:22 | 2012-06-02 12:00 | 1 | 158 | 4872531 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PER CARLENE JARVIS, PART POWER AT 3426 PIGEON ROOST RD//.. TRUCK DIDNT HAVE VOLT METER WENT TO SHOP TO GET ONE.. BAD CONNECTION ON SERVICE POLE 258-82 MELTED NEUTRAL WIRE INTO.. REPAIRED AND COMPLETE AT 12:00 //COD 1//ISO 258-72// VER/DBM IDC XXXX
18985 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2013-07-08 14:17 | 2013-07-08 16:55 | 1 | 158 | 4487921 | 158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR..NEED 2 MEN & MATERIAL HANDLING BUCKET & 25 KVA 7.2 KV XFMR...//..CREW ENROUTE..//.XFMR REPLACED & RE-FUSED.POWER ON.JRV..07/08/13 COD-1 ISO TF 38820893A00256 VER/HFP L3/HFP IDC XXXX
18986 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-01-26 11:33 | 2019-01-26 14:10 | 1 | 157 | 4723931 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken 19.9 cut out on pole 771-B1-433 restored at 14:10 // COD 1 ISO 38820771B30433
18987 | Hazard | 3302703 | HAZARD | HAZARD | 2013-08-05 09:08 | 2013-08-05 11:45 | 1 | 157 | 4623071 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN GOING TO CHURCH, NO APPARRENT REASON. NEED FLAGMEN TO REPLACE SERVICE.---- FLAGMEN ENROUTE. REPLACED SERVICE. POWER RESTORED. ONLY 1 CUST. OUT. VER/CRB L/3 CRB
18988 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-06-28 21:02 | 2010-06-28 23:39 | 1 | 157 | 59997-1 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | MTR HAD FAILED,HAD OPENED INTERNALLY.CHANGED MTR,ALL OK// VER/DBMIDC XXXX
18989 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-05-01 18:08 | 2018-05-01 20:45 | 1 | 157 | 4295411 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva xfmr truck accessible,replaced xfmr all cust restored @ 2045 please close ticket thanks.bt/ iso 38830116A00500/ cod 1
18990 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2015-09-22 08:40 | 2015-09-22 11:17 | 1 | 157 | 4259091 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED LINE CREW TO CHANGE BAD CUTOUT ON POLE 262-109. TRUCK TO POLE , RELEASED BY CREW 078S01.. CREW ON SITE CHANGING CUTOUT ETR 12:00.. CUTOUT CHANGED AND LINE RESTORED AT 11:17 PLEASE CLOSE TICKET CAY // COD-1 ISO LF 38830262000109 VER/HFP L3/HFP
18991 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-03-21 18:03 | 2011-03-21 20:40 | 1 | 157 | 56476-1 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT WILL NEED TO REPLACE//VER/CRB IDC XXXX
18992 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-03-23 10:33 | 2015-03-23 13:10 | 1 | 157 | 4218871 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT ON POLE 188-127 JUST AS YOU TURN IN GOLF COURSE ON LEFT. NO TRUCKS TO WET. NEED LINE CREW. RELEASED BY CREW 078S01,,REPLACED CUTOUT..ALL POWER RESTORED// VER/ ADH L3/DKGXXXX
18993 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2013-02-13 19:43 | 2013-02-13 22:20 | 1 | 157 | 4818331 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POSSIBLE BAD CONNECTION AT SECONDARY POLE CAUSED SERVICE DROP TO HEAT UP, MELT INSULATION AND BURN NEUTRAL IN TWO.I DID KEEP CONNECTION FROM POLE, THIS WILL PROBABLY BE A DAMAGE CLAIM., REPLACED SERVICE DROP AND RESQUEEZED ALL CONNECTIONS ON POLE, ONLY 1 CUSTOMER WAS PART POWER ///VER/CRB L/3 CRB IDC XXXX
18994 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2022-08-15 10:14 | 2022-08-15 12:51 | 1 | 157 | 4743671 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | POLE | I repaired a broken service neutral on pole 151-C-293 that resulted from pole 151-C-297 being broken during the recent flooding. Pole 151-C-297 will need to be replaced with a new outdoor light and a span of 4/2 to be installed. Need a tech to create a job to have this DD light pole replaced.////emailed Rob Pigman for follow up
18995 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-08-09 18:23 | 2010-08-09 21:00 | 1 | 157 | 51743-1 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD BARREL LINK AT WEATHERHEAD, SERVICE HAD ABOUT 5 SPLICES IN NEUTRAL, UPGRADED SERVICE FROM #4 TO #2 DROP. ONLY 1 CUSTOMER AFFECTED. //VER/CRB IDC XXXX
18996 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-11-14 09:09 | 2016-11-14 11:46 | 1 | 157 | 4099171 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE - DNP CUSTOMER, NO INTERRUPTION. REPLACED CUTOUT AND CONNECTED METER. SH VER/CRB
18997 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-07-15 18:17 | 2009-07-15 20:54 | 1 | 157 | 63319-1 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR C/O BROKE, WILL HAVE TO REPLACE, GOT JEFF AND PHILLIP TO COME AND HELP ME. FETR- SAME/// XFMR C/O CHANGED OUT POWER RESTORED//COD 1// VER/DBM IDC XXXX
18998 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-02-17 10:03 | 2010-02-17 12:40 | 1 | 157 | 58637-1 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | I HAVE A TRANSFORMER LEAD BURNT INTO ON POLE 37830072B00072 I WILL REPLACE BOTH LEADS, BAD TRANSFORMER CREW ENROUTE TO REPLACE/// I RESTORED POWER AT 12:40 I WILL HAVE TO DE-ENERGIZE AGAIN WHEN CREW ARRIVES TO CHANGE TRANSFORMER OUT./// PULLED OFF AT 14:15 BACK ON AT 14:48 TIM MCCOY RELEASED BY CREW 074H10 VER/KEP L3/KEP IDC THE COUNT IS CORRECT PER DISPATCHER XXXX
18999 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-03-08 17:38 | 2008-03-08 20:15 | 1 | 157 | 55406-1 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3311401// RED-RED SERVICE SPLICE BAD.// VER/DBM IDC XXXX
19000 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-04-15 09:13 | 2016-04-15 11:50 | 1 | 157 | 4093351 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION PULLED LOOSE @ WEATHER HEAD..MADE REPAIRS./ ISO 37830167D00067/ COD 1/ VER/BOW
19001 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2012-12-26 13:53 | 2012-12-26 16:30 | 1 | 157 | 4528691 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CUST HAD PART POWER, THEY HAVE A BAD LEG IN THERE UNDERGROUND SERVICE, 4/0, NEED TO SEND CREW TO INSTALL POWER TEMP TILL WE CAN FIX THIS UNDERGROUND RELEASED BY CREW 078S06/ FETR 17:30 JEH/ POWER TEMP INSTALLED CUST. HAS CORRECT VOLTAGE. @ 16:30 JEH ///VER/CRB L/3 CRB
19002 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2016-03-31 15:48 | 2016-03-31 18:25 | 1 | 157 | 4010991 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUT-OUT ON POLE 305-131. REPLACED CUT-OUT AND RESTORED POWER AT 18:25. VER/HFP L3/HFP
19003 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-07-14 08:38 | 2010-07-14 11:15 | 1 | 157 | 50023-1 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND THIS TO BE A PART POWER NOT A ALL OUT, FOUND SERVE ENDS PULLED LOOSE ON TRANSFORMER BANK POLE, HAVE ALL REPAIRS MADED AND ALL POWER IS RESTORED TO DAWSON POOL//VER/CRB IDC XXXX
19004 | Pikeville | 3413402 | GARRETT | LACKEY | 2014-06-18 07:38 | 2014-06-18 10:15 | 1 | 157 | 4104551 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN FAILED IN 4/3 SERVICE DROP SPLICE . REPLACED 4/3 SD WITH 2/3 SD, ALL WORK COMPLETE / GXJ VER/HFP L3/HFP
19005 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-05-16 18:08 | 2017-05-16 20:45 | 1 | 157 | 4805781 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | FUSE BROKE ON P-875-505.RE FUSED ALL GOOD VER/CRB
19006 | Pikeville | 3407101 | TOPMOST | DEMA | 2022-03-09 08:43 | 2022-03-09 11:20 | 1 | 157 | 4592031 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 37830114A00069
19007 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2016-08-02 08:46 | 2016-08-02 11:23 | 1 | 157 | 4722221 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CREW ON SITE/VEM/REPLACED ALL CUTOUTS,ARR.AND HOTAPS ON PRIMARY METERING POLE 878-76/FULL POWER RESTORED 1123/PLEASE CLOSE TICKET/THANKS/VEM /// COD-1 ISO LF 39830878000076 VER/HFP L3/HFP
19008 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-07-11 11:28 | 2017-07-11 14:05 | 1 | 157 | 4104441 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REPLACED POLE PER JIM MULLINS 37830221D30284 VER/AWD
19009 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2017-04-05 14:03 | 2017-04-05 16:40 | 1 | 157 | 4617001 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | INSULINK CONNECTION FAILED AND BURNT SERVICE DOWN. OOONE CUSTOMER AFFECTEDOO TRIMMED LIMBS FROM SEC POLE, REATTACHED SERVICE AND MADE NEW CONNECTIONS. SH VER/CRB L3/HFP XXXHFP
19010 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-08-30 17:13 | 2022-08-30 19:50 | 1 | 157 | 4818491 | 157 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | talked w/cust can work on dayshift--broke c/o on three can bank pole 38830381000115--replace all three--ds083022---ops order 033537613 Released by crew 078S01
19011 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2022-05-06 07:08 | 2022-05-06 09:45 | 1 | 157 | 4842501 | 157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 1036D-46..going to be making repairs.replaced cutout and got transformer fuse on pole 1036D-46 back in at 09:45
19012 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-07-21 21:39 | 2019-07-21 22:57 | 2 | 78 | 4753981 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrester on 103-86bad arrestor on 37830103000086 cut it in the clear refused line fuse
19013 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-02-18 21:08 | 2014-02-18 22:00 | 3 | 52 | 4399331 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE, DID NOT BLOW. VER/PDP
19014 | Hazard | 3309302 | VICCO | JEFF | 2015-11-22 13:42 | 2015-11-22 15:00 | 2 | 78 | 4478321 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE GOT OLD AND BROKE . CLOSED XFMR @ 15:00,, ISO 37830299C00118/ COD 2/ VER/BOW
19015 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-12-02 19:53 | 2008-12-02 20:45 | 3 | 52 | 54050-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3311401// TRANSFORMER FUSE IS BLOWN. NO CAUSE VISIBLE, I AM GOING TO REPLACE 6T FUSE LINK. FUSE LINK HAD DETERRIORATED AND BROKE, IT WAS NOT BLOWN//COD 3// VER/DBM L3/KEP IDC XXXX
19016 | Hazard | 3303902 | LESLIE | WOOTON | 2017-01-12 19:24 | 2017-01-12 22:00 | 1 | 156 | 4293141 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE REPLACED IT VER/CRB L3/HFP XXXHFP
19017 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-06-15 17:42 | 2016-06-15 18:34 | 3 | 52 | 4354951 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEC. LEAD HAS COME OUT OF BUSHING WILL TRY AND MAKE REPAIRS..OPENED XFM. ON POLE 239-06 @ 18:15 CLOSED BACK IN @ 18:34... COD-3 ISO TF 37830239000006 VER/HFP L3/HFP
19018 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2022-11-19 23:15 | 2022-11-19 23:21 | 26 | 6 | 4163331 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 183-100 wire almost burnt into arcing at hot line clamp,,,opened recloser 183-80 @ 23:15 to make repairs ,,closed @ 23:21,,,customers restored complete
19019 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-03-14 08:24 | 2008-03-14 11:00 | 1 | 156 | 57052-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401001//I AM GOING TO REPLACE SERVICE DROP WITH A 2/3 DROP. A 4/3 DROP BURNED DOWN SERVING A 200 AMP METER BASE. I REPLACED DROP.// ISO-FLT 37830263D00100 SINGLE CUSTOMER AFFECTED/// VER/TOM IDC XXXX
19020 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-04-18 18:50 | 2018-04-18 21:26 | 1 | 156 | 4252431 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired secondary connection complete
19021 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2022-11-23 15:04 | 2022-11-23 17:40 | 1 | 156 | 4177001 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hotleg and neutrul burnt up repairs made power restored 17:40
19022 | Hazard | 3303902 | LESLIE | WOOTON | 2008-02-07 18:15 | 2008-02-07 20:51 | 1 | 156 | 52549-1 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3303902// BAD CONNECTION ON TRL POLE VER/HFP IDC XXXX
19023 | Pikeville | 3407101 | TOPMOST | DEMA | 2017-05-27 19:58 | 2017-05-27 20:50 | 3 | 52 | 4873081 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REFUSED LINE CUTOUT, WILL NEED TO REPLACE ARRESTER AT LATER DATE, COMPLETE / GXJ/ ISO37830138000023/ COD 3/ VER/BOW
19024 | Whitesburg | 3409503 | BURDINE | JENKINS | 2008-01-04 10:17 | 2008-01-04 12:53 | 1 | 156 | 53698-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409503// CUST HAS A #4 SERVICE DROP AND IT HAS BURNED INTO I WILL REPLACE WITH 2/3 AND INSTALL A MID SPAN REPLACED SERVICE DROP AND INSTALLED MID SPAN VER/KEP
19025 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-01-30 10:04 | 2012-01-30 12:40 | 1 | 156 | 4304941 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD INSULINK CONNECTOR ON SERVICE.(1 CUST ONLY)..BURNT ONE HOT LEG & NUETRAL IN TWO..//..SPLICED SERVICE WITH BETTER CONNECTORS & RESAGGED..//...NOTE..CUST DID NOT MENTION, BUT THEY COULD POSSIBLY HAVE DAMAGES.THANX.JRV.01/30/12 VER/KEP IDC XXXX
19026 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-12-07 08:07 | 2009-12-07 09:25 | 2 | 78 | 65463-1 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | VER/HFP STS TRANSFORMER FUSE DOWN LOOK LIKE FUSE BROKE INTO COD-2 ISO TF 38831084A00207 L3/HFP IDC XXXX
19027 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-11-14 18:09 | 2012-11-14 19:01 | 3 | 52 | 4398351 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE ... COD - 3 ISO TF 38830020A41563 VER/HFP L3/HFP IDC XXXX
19028 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2016-01-05 20:36 | 2016-01-05 20:42 | 26 | 6 | 4588321 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED CUTOUT TO SAFELY REPLACE FAILING DOOR RELATED TO 4588141 VER/KEP AJB
19029 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-03-11 13:07 | 2009-03-11 14:25 | 2 | 78 | 57254-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-2 WR # 28884718 // TRANS FUSE OUT BROKE CUTOUT L3/HFP IDC XXXX
19030 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-03-30 23:02 | 2022-03-31 00:20 | 2 | 78 | 4695141 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad cutout, apr at 0020 close ticket. dwest
19031 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2015-06-17 20:04 | 2015-06-17 21:22 | 2 | 78 | 4590521 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNT UP WILL REPLACE//// REPLACED BAD CUTOUT AND RESTORED SERVICE @ 21:22/ ISO 37830188C00329/ COD 2/ VER/BOW
19032 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-01-18 16:12 | 2022-01-18 17:30 | 2 | 78 | 4383001 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout
19033 | Hazard | 3303901 | LESLIE | HYDEN | 2020-05-06 12:27 | 2020-05-06 15:03 | 1 | 156 | 4806121 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broken neutral in sec, opened xfmr at 14:38 closed at 14:56
19034 | Whitesburg | 3314401 | MAYKING | ERMINE | 2019-11-18 18:06 | 2019-11-18 20:42 | 1 | 156 | 4045691 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection in secondary at pole 449-891 , made repairs restored power at 20:42..
19035 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-02-09 11:24 | 2021-02-09 13:00 | 3 | 96 | 4951591 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV APPEARS TO HAVE BURNED INTO,WILL MAKE REPAIRS/////////MADE NECESSARY REPAIRS&RESTORED.OFF@12:30ON13:00
19036 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-01-18 04:39 | 2014-01-18 07:15 | 1 | 156 | 4291451 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OOONLY ONE CUSTOMER AFFECTEDOO CONNECTION FAILED IN A MIDSPAN SPLICE IN SERVICE. REPLACED SERVICE. SH //VER/GAH L3/HFP
19037 | South Williamson | 3411401 | DEWEY | INEZ | 2010-12-25 18:29 | 2010-12-25 21:05 | 1 | 156 | 55705-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVE-IN CONNECTION FROZE OUT AT WEATHERHEAD. RE-SQUEEZED BOTH HOT CONNECTIONS @ WEATHERHEAD. SH VER/PDP IDC XXXX
19038 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2018-12-09 08:54 | 2018-12-09 11:30 | 1 | 156 | 4520411 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | POSSIBLE BAD UG//NEED POWER TEMP//,bad leg on ug sec installed power temp will need to replace ug sec,place in abnormal. please close ticket thanks.bt//MADE AED AND SENT TO LINE DEPT L3/HFP
19039 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-07-31 20:46 | 2016-07-31 23:22 | 1 | 156 | 4716521 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN IN SERVICE. REPAIRED AND RESTORED AT 23:10. SH
19040 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-01-21 13:42 | 2011-01-21 15:00 | 2 | 78 | 63379-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE CURRENT LIMITING FUSE WAS BURNED UP. CHANGE CUSTOMER COUNT TO REFLECT THE EXTRA CUSTOMER THAT I DID A MD FOR...HFP COD-2 ISO 37830189B00193 VER/HFP L3/HFP IDC XXXX
19041 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2018-06-16 16:24 | 2018-06-16 19:00 | 1 | 156 | 4608571 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | srv to house burnt up appro 3 from pole--replaced --allgood-ds061618
19042 | Whitesburg | 3312901 | JENKINS | KONA | 2008-12-06 11:09 | 2008-12-06 12:27 | 2 | 78 | 54893-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3312901// TRANSFORMER FUSE IS BLOWN WITH NO VISIBLE CAUSE. IT IS LOCATED ON SIDE OF HILL. FUSE WAS NOT BLOWN, IT WAS DETERRIORATED AND BROKEN VER/TOM L3/TOM IDC XXXX
19043 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-12-25 18:26 | 2008-12-25 19:18 | 3 | 52 | 63939-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP COD - 3 CCC STS WR # 27805369 // 6T FUSE BROKE 0N POLE 111-152. FUSED UP EVERYTHING OK. L3/HFP IDC XXXX
19044 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2011-01-09 09:04 | 2011-01-09 11:40 | 1 | 156 | 60102-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN //VER/GAH IDC XXXX
19045 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-06-05 20:24 | 2020-06-05 23:00 | 1 | 156 | 4967241 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate brunt replaced gate power on
19046 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-02-05 21:47 | 2022-02-05 23:05 | 2 | 78 | 4448281 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse broken, re fusing
19047 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-07-09 21:57 | 2015-07-09 23:15 | 2 | 78 | 4760001 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARCOSING RICK MAGGARD OUT. BAD CUTOUT REPLACED CUTOUT, RESTORED POWER AT 23:15 VER/KEP
19048 | South Williamson | 3411401 | DEWEY | INEZ | 2020-09-26 10:14 | 2020-09-26 12:50 | 1 | 156 | 4498181 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing
19049 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-07-08 11:36 | 2012-07-08 14:12 | 1 | 156 | 4595981 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 10T FUSE OUT DUE BAD CUTOUT. I HAVE CUTOUT REPLACED FUSED UP EVERYTHING OK//COD 1
19050 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-03-10 15:07 | 2021-03-10 16:25 | 2 | 78 | 4323541 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cut out is broke. Will climb pole and replace/// Replaced cutout and restored @16:25
19051 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-04-29 21:42 | 2013-04-29 23:00 | 2 | 78 | 4058041 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN// WILL REFUSE// CUTOUT BROKEN// REPLACED CUTOUT// POWER IS RESTORED COD-2 ISO TF 38831125C10264 VER/HFP L3/HFP IDC XXXX
19052 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2018-02-20 15:39 | 2018-02-20 18:15 | 1 | 156 | 4865771 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on primary metering
19053 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2011-03-07 21:13 | 2011-03-07 23:49 | 1 | 156 | 51543-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND 4/3 SERVICE DROP BURNTED INTO ON TRANSFORMER POLE, HAVE MADE REPAIRS AND EVERYTHING IS OK AT THIS LOC// VER/DBM IDC XXXX
19054 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-08-15 10:55 | 2016-08-15 11:47 | 3 | 52 | 4778071 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE IN @ 1147 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT/ ISO 38830206B02688/ COD 3/ VER/BOW
19055 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-04-08 22:56 | 2009-04-08 23:48 | 3 | 52 | 50646-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT, FUSE BROKE COD-3 VER/KEP L3/KEP IDC XXXX
19056 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-02-06 20:31 | 2014-02-06 21:23 | 3 | 52 | 4365061 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE APPEARED TO HAVE BROKE. NOT BLOWN COD-3 VER/HFP L3/HFP IDC XXXX
19057 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-12-27 08:14 | 2016-12-27 10:50 | 1 | 156 | 4241211 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT, ALL WORK COMPLETE / GXJ VER/CRB
19058 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-12-14 09:10 | 2021-12-14 10:28 | 2 | 78 | 4194251 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout 351-113 complete
19059 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2013-10-26 13:38 | 2013-10-26 14:30 | 3 | 52 | 4965741 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 21-2137 BAD CUTOUT DOOR REPLACED HOT TAP BURNTOFF REPLACED CROSSARMS VERY BAD ON POLE NEED TO SEND NOTE TO TEC. NEEDS CHGED ASAP B/ PHASE COD - 3 ISO LF 38830046B12137 VER/HFP L3/HFP
19060 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-07-22 18:39 | 2015-07-22 21:15 | 1 | 156 | 4933131 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BURNDT INTO ON CUSTOMERS SERVICE, WILL BE REPLACING. HAD TO CUT TREES AND REPLACE SERVICE, RESTORED POWER AT 2115. VER/KEP
19061 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2016-11-01 14:43 | 2016-11-01 15:35 | 3 | 52 | 4068291 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-4141 BAD CUTOUT VER/AWD
19062 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-09-16 09:12 | 2011-09-16 10:30 | 2 | 78 | 4876231 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT. //VER/CRB IDC XXXX
19063 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2021-11-29 16:39 | 2021-11-29 19:15 | 1 | 156 | 4133151 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 3882966B20571.made repairs and got the fuse back in at 19:15..only one cust on this transformer
19064 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-11-25 14:24 | 2014-11-25 17:00 | 1 | 156 | 4781131 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP FROM SECONDARY POLE 38821089D00462 TO GARAGE BURNED DOWN. CUSTOMER RUNS A WELDER HERE AND I THINK IT WAS OVERLOAD. THE GARAGE AND A DOUBLE WIDE ARE AT THE END OF THIS SECONDARY EXT. SEND TO CLIFF FREEMAN TO HAVE THE SECONDARY UPGRADED. VER/CRB
19065 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-07-23 16:52 | 2020-07-23 19:28 | 1 | 156 | 4219731 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout on 21-2616/ making repairs/ xfmr on 21-2616 in @ 1928
19066 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-08-04 15:35 | 2018-08-04 16:53 | 2 | 78 | 4908751 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 38830162D00333. all restored, pls close. tre
19067 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-12-27 19:42 | 2016-12-27 21:00 | 2 | 78 | 4244011 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER (1750) POLE 91-233 BAD CUTOUT REPAIRED VER/AWD
19068 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2011-04-05 18:53 | 2011-04-05 19:32 | 4 | 39 | 50010-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLEW APART AND GROUND WIRE FELL INTO XFMR RISER. CLEARED BAD ARRESTER AND RE-FUSED XFMR @ 19:32. SH//COD 4// VER/DBM IDC XXXX
19069 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-04-20 16:43 | 2022-04-20 19:19 | 1 | 156 | 4784381 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15KVA 7200 XFM
19070 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-06-28 11:29 | 2022-06-28 14:05 | 1 | 156 | 4339981 | 156 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | CUST ISOLATED TROUBLED EQ // RESTORED METERING @ 14:05
19071 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2017-12-03 19:42 | 2017-12-03 20:21 | 4 | 39 | 4618851 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t xfr fuse broke ,,,customers restored complete
19072 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2009-07-20 18:41 | 2009-07-20 19:59 | 2 | 78 | 50620-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 796-88 VER/TOM L3/TOM IDC XXXX
19073 | Paintsville | 3401802 | INDEX | HOSPITAL | 2020-04-24 12:33 | 2020-04-24 15:09 | 1 | 156 | 4746101 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing
19074 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-02-12 18:18 | 2015-02-12 19:10 | 3 | 52 | 4011701 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LF CUTOUT 139C19, RESTORED/ ISO 38830139C00019/ COD 3/ VER/BOW L3/HFP XXX
19075 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-07-19 21:42 | 2012-07-19 23:00 | 2 | 78 | 4779541 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830199000129, OUT OF CUTOUTS, GOING HOME TO GET ANOTHER ONE. CUTOUT CHANGED, ALL POWER RESTORED, BT VER/KEP
19076 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2009-05-01 20:23 | 2009-05-01 21:41 | 2 | 78 | 62750-1 | 156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BROKE COD-2 VER/KEP L3/KEP IDC XXXX
19077 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-06-16 12:00 | 2008-06-16 14:35 | 1 | 155 | 65432-1 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VOLTAGE IS HIGH 286 CONTACTED R MAYNARD GOING TO SEND CREW TO CHANGE// RELEASED BY CREW 076H04 // VER/TOM IDC ESTIMATED TIME OFF XXXX
19078 | Hazard | 3310502 | HADDIX | CANOE | 2009-10-23 06:10 | 2009-10-23 08:45 | 1 | 155 | 65562-1 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP TRANSFORMER FUSE DOWN /// COD-1 ISO TF 37830075C30204 L3/HFP IDC XXXX
19079 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-11-21 01:35 | 2008-11-21 04:10 | 1 | 155 | 50461-1 | 155 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3002001// FOUND 4/3 SERVICE DROP BURNTED UP, HAVE REPAIRS MADE AND THIS CUST HAS FULL POWER NOW VER/LDA IDC XXXX
19080 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-11-20 11:55 | 2012-11-20 14:30 | 1 | 155 | 4410971 | 155 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BRUNT INTO ,WILL HAVE TO OPEN XFMR ON POLE 397-66 TO MAKE REPAIRS. REPLACED SERVICE RESTORED POWER AT 14:30 COD-1 ISO TF 37830397000066 VER/HFP L3/HFP IDC XXXX
19081 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-07-13 10:39 | 2011-07-13 11:10 | 5 | 31 | 4540451 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW REPLACING INSULATOR AND CUT/OUT /// TIME OFF 10:39-- TIME ON 11:10 WORK COMPLETE PR TOLLIVER COD-5 ISO TF 38830247000117 VER/HFP L3/HFP IDC XXXX
19082 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2020-12-10 08:35 | 2020-12-10 11:10 | 1 | 155 | 4757881 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burnt into blowing xfm fuse/// will make repairs///Repairs made refused xfm @ 11:10 and restored service
19083 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-03-11 08:45 | 2021-03-11 11:20 | 1 | 155 | 4325191 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers service drop burndt into in 2 places, gonna change out 4/3 drop to 2/3. Got service changed out and power restored @1120. Only 1 customer was affected.
19084 | Paintsville | 3409302 | KENWOOD | AUXIER | 2011-10-27 09:25 | 2011-10-27 12:00 | 1 | 155 | 4025581 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CUSTOMER HAS BAD NEUTRAL IN UG SERVICE. INSTALLED TEMPORARY NEUTRAL FROM JUNCTION BOX TO METERBASE. ALL OK FOR NOW - WILL SEND JOB TO ENGINEERING TO REPLACE. <<ONLY ONE CUSTOMER AFFECTED>> SH VER/KEP IDC XXXX
19085 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-06-16 12:25 | 2022-06-16 15:00 | 1 | 155 | 4135781 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | had to open XFM secondary bushing was burnt and leaking oil, opened @ 12:25, Shawn Goble is coming to change XFM// 15KVA 19.9 Released by crew 074S09/// REPLACED XFMR AND CUTOUT.POWER RESTORED @15:00
19086 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-09-03 07:14 | 2010-09-03 09:49 | 1 | 155 | 63091-1 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CHECKING SCHOOL POWER IS ON , GENATOR IS RUNNING, WILL OPEN UP SWITCHES ON POLE 875-7 LONG ENOUGH TO REPLACE THREE TWO BOLT CONNECTORS ON POLE 850-5, MASSEY,S LEAD EQUIPMENT SHOWED BAD READING ON THIS POLE, COULD BE LOSING A PHASE HERE. TCM// PLEASE SEND COPY TO TOM MAMING TO PLACE RECORDING METER AT SCHOOL TO CHECK ON PHASE OUT CONDITION, THANKS// VER/DBM IDC XXXX
19087 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-05-19 10:43 | 2011-05-19 13:18 | 1 | 155 | 4113171 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT TO REPLACE///////REPLACED BROKEN 19.9 CUTOUT AND RESTORED IDC XXXX
19088 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2013-01-22 07:23 | 2013-01-22 09:58 | 1 | 155 | 4726371 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4/3 SERVICE DROP BURNTED DOWN BEHIND HOUSE, HAVE REPAIRS MADE AND POWER IS RESTORED AT THIS LOC, ON THE RIVER BANK, VER/HFP L3/HFP IDC XXXX
19089 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-11-10 14:57 | 2016-11-10 17:32 | 1 | 155 | 4091161 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SECONDARY, WILL HAVE TO LET DOWN, CALLED FOR HELP VER/CRB
19090 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-01-08 11:40 | 2011-01-08 14:15 | 1 | 155 | 59834-1 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT. WILL CHANGE.. P.HICKS //VER/GAH IDC XXXX
19091 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-11-29 07:35 | 2019-11-29 10:10 | 1 | 155 | 4101611 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 12t back in at 10:10
19092 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2015-01-22 13:50 | 2015-01-22 14:21 | 5 | 31 | 4951711 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED BROKEN CUTOUT DOOR //38830207A00200//COD 5// VER/CRB
19093 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-04-23 18:14 | 2022-04-23 20:49 | 1 | 155 | 4793541 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Line fuse open at 165-47..Old CSP Trans on pole 165-51 has a bad Arrester no Meter off it,Lift Hot Tap and isolated and restored Line fuse at 20:49.//cod 1
19094 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-05-11 08:46 | 2010-05-11 11:21 | 1 | 155 | 59359-1 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 35062570 // POLE 115-229 BAD 19.9 CUTOUT NO TRUCK CAN OPEN LINE ON POLE 115-592 RELEASED BY CREW 078S08//COD 1// VER/DBM IDC XXXX
19095 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-03-03 10:15 | 2013-03-03 12:50 | 1 | 155 | 4867651 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD SEC WIRE//COD 1// VER/DBM IDCC TOF814, ESTIMATED TIME OFF XXXX
19096 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-11-23 06:25 | 2020-11-23 09:00 | 1 | 155 | 4716951 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o door, replaced door, restored
19097 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-06-24 11:35 | 2021-06-24 14:10 | 1 | 155 | 4802741 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 7200 cutout, big bucket required, this is behind Tim Yates garage where he parks all his big trucks. Released by crew 078S11///Complete BR
19098 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-01-31 10:26 | 2010-01-31 13:01 | 1 | 155 | 61669-1 | 155 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 33667931 FOUND 2/3 SECONDARY BURNTED INTO AND SERVICE DROP, HAVE ALL REPAIRS MADE AND POWER IS OK AT THIS LOC VER/HFP L3/HFP IDC XXXX
19099 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-01-23 06:10 | 2021-01-23 08:45 | 1 | 155 | 4886271 | 155 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | neutral burnt on our side causing customers high voltage.. this burnt up several things in house.. bad neutral on our side.. repairs made, power restored
19100 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2022-03-21 12:25 | 2022-03-21 15:00 | 1 | 155 | 4653711 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burned into off secondary pole 73-D-307,Going to pull Meter and make repairs..Restored service at 15:00..
19101 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-02-09 23:19 | 2021-02-10 01:54 | 1 | 155 | 4953211 | 155 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | resqueezed connections at transformer and house. complete/ ISO 38830399000022/ COD 1
19102 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-03-29 17:10 | 2013-03-29 19:45 | 1 | 155 | 4967071 | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED COD-1 ISO TF 37820193A00422 VER/HFP L3/HFP IDC XXXX
19103 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2020-03-04 12:55 | 2020-03-04 15:30 | 1 | 155 | 4451921 | 155 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Crew required ,1 bad hot leg underground Released by crew 078S05 CREW ON SITE FETR 16:00 all pwr restored @ 15:30 LRM Released by crew 078H06//ADIPHASE ADDED //DAE ENTERED 1000047696
19104 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2008-10-17 09:55 | 2008-10-17 12:10 | 2 | 135 | Z | 155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000304// CALLED CREW OPENED AT 0955 ON POLE 38830021B10036 CLOSED BACK IN AT 10:15/ SEND TO P TOLLIVER RELEASED BY CREW 078S07//JOB COMPLETE @12:10 REPLACED 500KVA STEPDOWN VER/KEP IDC XXXX
19105 | Whitesburg | 3409503 | BURDINE | JENKINS | 2011-05-04 17:36 | 2011-05-04 20:10 | 1 | 154 | 4009511 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE CONDUCTOR WAS PULLED INTO DUE TO LEANING POLE//VER/CRB IDCC CCO XXXX
19106 | South Williamson | 3411401 | DEWEY | INEZ | 2009-03-08 21:57 | 2009-03-08 22:19 | 7 | 22 | 56356-1 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP ARRESTER BAD L3/HFP IDC XXXX
19107 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-07-28 09:56 | 2012-07-28 12:30 | 1 | 154 | 4856171 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 076S01//NEUTRAL BROKE IN CUSTOMERS SERVICE DROP//REPAIRING NOW//REPAIRS MADE//CUSTOMER THINKS THEY HAVE DAMAGES//MAY BE FILING CLAIM///RESTORED AT 1230//COMPLETE/EM VER/KEP
19108 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-10-30 14:16 | 2009-10-30 14:30 | 11 | 14 | H52798-1 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIM BROKE IN CLEAR AT POLE 1061-20,LINE FUSE NOT OUT BUT WILL HAVE TO OPEN IT WHEN READY TO PUT WIRE UP.#4 COPPER PRIM COND.WILL TRY TO GET HELP AND WIRE COD-17 PRIM BROKE IN CLEAR AT POLE 1061-20,LINE FUSE NOT OUT BUT WILL HAVE TO OPEN IT WHEN READY TO PUT WIRE UP.#4 COPPER PRIM COND.WILL TRY TO GET HELP AND WIRE/OPENED 1061-14 AT 14:16,CLOSED AT 14:30 AFT REPAIRS WERE COMPLTED VER/KEP L3/KEP IDCC PN149 XXXX
19109 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-09-07 14:32 | 2016-09-07 17:06 | 1 | 154 | 4874371 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REQUEEZED SERVICE AND CUSTOMER MADE REPAIRS COMPLETE VER/AWD
19110 | Hazard | 3310502 | HADDIX | CANOE | 2012-06-01 14:56 | 2012-06-01 17:30 | 1 | 154 | 4864401 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD RED TO RED--- VER/HFP L3/HFP IDC XXXX
19111 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-10-01 12:58 | 2022-10-01 15:32 | 1 | 154 | 4959591 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 25kva/crew reqd. truck ok. Released by crew 078S04/arrived RM replaced xfm volatge good please close tic RM
19112 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-08-18 17:13 | 2016-08-18 18:30 | 2 | 77 | 4812271 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CUTOUT DOOR BURNT UP DUE TO FUSE LINK BREAKING. REPLACED DOOR, 6T XFMR FUSE AND RESTORED @ 18:30. SH VER/CRB
19113 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-08-19 08:11 | 2022-08-19 10:45 | 1 | 154 | 4763221 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke power restored at 10:42
19114 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2020-07-09 22:48 | 2020-07-10 00:05 | 2 | 77 | 4138211 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse door burnt up. replaced door apr at 0005 close ticket
19115 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2015-11-17 00:43 | 2015-11-17 02:00 | 2 | 77 | 4453241 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1148-393 BAD CUTOUT 10T TRANS FUSE VER/TOM L3/TOM
19116 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-02-11 07:44 | 2019-02-11 10:18 | 1 | 154 | 4776781 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38831064000112 FUSE ONLY FEEDS THIS TAP TO POLE 38831064000112 = NEED MD had transformer cutout broke and took out line fuse on pole 1064-111 ¦¦ ENTERED MD
19117 | Hazard | 3302704 | HAZARD | KENMONT | 2018-06-27 16:02 | 2018-06-27 18:36 | 1 | 154 | 4680791 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | fuse out on UG riser pole...bad U.G. TERMINATION ON POLE, 34.5 KV..REPLACED TERMINATION, ALL POWER RESTORED @18:36 HRS.P.HICKS
19118 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2022-11-20 21:21 | 2022-11-20 23:55 | 1 | 154 | 4166891 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | large appliances not working // bad underground hot leg/ needs power temp or repaired// crew required. Released by crew 078S09,repairs made cust restored @ 2355 please close ticket thanks.bt
19119 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-03-10 17:23 | 2010-03-10 18:40 | 2 | 77 | 64779-1 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HAVE A TRASNSFORMER FUSE OUT ON POLE 37830023D40068 IT HAS A SILVER TOP CUTOUT IM GOING TO CHANGE OUT WHILE IM HERE. /// REPLACED C/O L/A AND RESTORED POWER.//COD 2// VER/DBM IDC XXXX
19120 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-01-19 20:38 | 2013-01-19 21:55 | 2 | 77 | 4702151 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. I HAVE CUTOUT CHANGE FUSED UP EVERYTHING OK VER/PDP IDC XXXX
19121 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-09-04 11:06 | 2013-09-04 11:28 | 7 | 22 | 4819321 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CONDUCTOR CAME OFF BROKEN INSULATOR VER/CRB L/3 CRB IDC XXXX
19122 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2018-11-16 19:24 | 2018-11-16 20:41 | 2 | 77 | 4445801 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse was broke, power restored at 20:41 L3/HFP
19123 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-06-01 23:11 | 2018-06-02 01:45 | 1 | 154 | 4543581 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout door burned up, replaced and all power restored at 01:45//cod 1
19124 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-07-09 11:18 | 2019-07-09 13:52 | 1 | 154 | 4684321 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout
19125 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-04-28 08:47 | 2015-04-28 11:21 | 1 | 154 | 4371721 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON POLE 38830043000143 VER/CRB
19126 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-08-12 21:16 | 2015-08-12 23:50 | 1 | 154 | 4129641 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE XFMER CUTOUT ON POLE 830-176///REPLACED CUTOUT///BACK ON AT 23:50///COMPLETE BR VER/ARN
19127 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-07-31 19:25 | 2016-07-31 21:59 | 1 | 154 | 4716271 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE IN @ 0959 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT
19128 | Hazard | 3309002 | JEFF | JEFF | 2018-06-06 08:36 | 2018-06-06 11:10 | 1 | 154 | 4560831 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse broke/ ISO 37830345C20398/ COD 1
19129 | Pikeville | 3421001 | BREAKS | CITY | 2011-12-19 14:41 | 2011-12-19 17:15 | 1 | 154 | 4189121 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S01 TRANSFORMER CUTOUT IS BURNED UP ON POLE 220-376. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. COD-1 ISO TF 37820220C20376 VER/HFP L3/HFP IDC XXXX
19130 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-05-05 12:18 | 2018-05-05 14:52 | 1 | 154 | 4310391 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT TO REPLACE/////////REPLACED CUTOUT&RESTORED POWER
19131 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2019-01-28 15:42 | 2019-01-28 18:16 | 1 | 154 | 4729431 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole, repaired connection // only one customer ¦¦ L3/HFP
19132 | Hazard | 3309003 | JEFF | VIPER | 2016-03-01 12:26 | 2016-03-01 15:00 | 1 | 154 | 4791891 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE === NEED LINE CREW THIS IS UP ON HILL SIDE MANUAL === CALLED FOR 1 MAN CHANGED CUTOUT POWER OK/ ISO 37830393D00045/ COD 1/ VER/BOW
19133 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-02-19 09:59 | 2015-02-19 12:33 | 1 | 154 | 4042431 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER GOT ERIC PRATT CHANGE IT OUT COD-1 ISO TF 38831132000122 VER/HFP L3/HFP
19134 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-01-02 05:53 | 2012-01-02 07:10 | 2 | 77 | 4224131 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000901 - ED - CSX - 923-8928 REPORTS SINGLE PHASING-REPLACED BAD HOT TAP AT CTS VER/PDP IDCC PN8012 XXXX
19135 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2018-04-15 01:13 | 2018-04-15 02:30 | 2 | 77 | 4225971 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I replaced a bad secondary connection at the transformer pole.
19136 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-01-22 14:30 | 2009-01-22 14:52 | 7 | 22 | 59196-1 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | VER/HFP WR # 28180183 // TIE WIRE BROKE AND CREW NEEDED TO OPEN UP LINE TO MAKE REPAIRS SAFELY L3/HFP
19137 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2013-01-30 17:13 | 2013-01-30 18:30 | 2 | 77 | 4761711 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT. FUSE WAS BROKEN. FUSED UP EVERYTHING OK. COD-2 ISO TF 37830067A00135 VER/HFP L3/HFP IDC XXXX
19138 | Hazard | 3303902 | LESLIE | WOOTON | 2013-03-17 21:56 | 2013-03-17 22:10 | 11 | 14 | 4913661 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT IDC XXXX
19139 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-11-03 19:48 | 2010-11-03 22:22 | 1 | 154 | 51472-1 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED TO REPLACE SERVICE DROPWILL NEED HELP// VER/DBM IDC XXXX
19140 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-09-11 23:13 | 2018-09-12 00:30 | 2 | 77 | 4085921 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop low about on the ground will make repairs/// opened xfm @ 00:10 to make repairs/// repairs made closed xfm in @ 00:30 and restored service
19141 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-01-05 19:07 | 2015-01-05 20:24 | 2 | 77 | 4909041 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT, FUSE HAD PULLED INTO, NOT BLOWN. POWER RESTORED 37830279000183 VER/CRB
19142 | Paintsville | 3401802 | INDEX | HOSPITAL | 2021-03-08 15:09 | 2021-03-08 16:26 | 2 | 77 | 4316201 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link appears to have broke. Restored @ 16:26. sh
19143 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2018-06-25 16:06 | 2018-06-25 18:40 | 1 | 154 | 4664341 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT//
19144 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2021-03-20 09:51 | 2021-03-20 12:25 | 1 | 154 | 4357321 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection on transformer lead bad.
19145 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2018-04-11 10:19 | 2018-04-11 11:36 | 2 | 77 | 4210161 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | old span of open wire down didnt serve anything had transformer open on pole 67-c-234 at 11:12 cleared wire up and close transformer back in at 11:26 everything ok//COD 2 PER SERVICER
19146 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-01-22 08:28 | 2014-01-22 11:02 | 1 | 154 | 4300621 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE-IN FROZEN APART AT ENTRANCE,MADE NECESSARY REPAIRS.ALL OK AFTERWARDS VER/HFP L3/HFP
19147 | South Williamson | 3411401 | DEWEY | INEZ | 2020-09-24 12:26 | 2020-09-24 15:00 | 1 | 154 | 4492061 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up on transformer made repairs all good now
19148 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2019-09-28 15:21 | 2019-09-28 17:55 | 1 | 154 | 4069131 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot legs melted in the clear repairs made back in at 17:55
19149 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2013-07-06 12:23 | 2013-07-06 13:40 | 2 | 77 | 4474521 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN ON 1110C3..//.FUSE LINK BROKEN.REPLACED & RE-FUSED XFMR.POWER ON NOW.JRV..07/06/13//COD 2// VER/DBM IDC XXXX
19150 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-06-03 22:00 | 2014-06-03 22:22 | 7 | 22 | 4968041 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | REMOVED BROKEN GUY WIRE AND CHANGED BROKEN CUT-OUT OPENED TRANSFORMER @22:00 AND CLOSED BACK IN @22:20 /// COD- 7 ISO TF 37820097000144 VER/HFP L3/HFP
19151 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-02-07 16:37 | 2017-02-07 19:11 | 1 | 154 | 4367631 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE OLD AN BROKE , CLOSED XFMR BACK @ 19:11 VER/CRB L3/HFP XXXHFP
19152 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-10-30 07:43 | 2011-10-30 09:00 | 2 | 77 | 4036591 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// FUSE LINK HAD BROKE//REFUSEC// POWER IS RESTORED///VER/CRB IDC XXXX
19153 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2013-05-12 01:08 | 2013-05-12 02:25 | 2 | 77 | 4106361 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT, REPLACED CUTOUT, ALL POWER RESTORED //VER/GAH IDC XXXX
19154 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-04-27 09:56 | 2008-04-27 12:30 | 1 | 154 | 54517-1 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501// BAD CUTOUT .... REPLACED CUTOUT RESTORED POWER AT 12;30....... RM// COD 1 - ISO/FLT SAME // VER/TOM IDC XXXX
19155 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-04-21 21:29 | 2010-04-22 00:03 | 1 | 154 | 66181-1 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR.......DAH //VER/GAH IDC XXXX
19156 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2021-04-24 20:26 | 2021-04-24 23:00 | 1 | 154 | 4477441 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | found bad servend connecting at weatherhead replaced connections all power restored
19157 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-11-06 22:56 | 2012-11-07 01:30 | 1 | 154 | 4369571 | 154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | <<ONLY ONE CUSTOMER AFFECTED>> INSULINK CONNECTION BURNT OPEN IN SERVICE. REPAIRED AND RESTORED @ 1:20. SH //VER/GAH IDC SECOND CALL WAS OUTAGE FIRST ONLY ARCING. CHANGED TIME OFF FROM 2236 XXXX
19158 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2020-09-04 16:31 | 2020-09-04 19:05 | 1 | 154 | 4432821 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | nuetrul and hot leg burnt up in service got repaired and and full power restored at 19:05
19159 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-12-21 21:58 | 2022-12-21 23:15 | 2 | 77 | 4285141 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Got a Hot leg into on secondary pole pulled Meter to make repairs..Restored at 23:15.
19160 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-01-13 11:38 | 2020-01-13 14:12 | 1 | 154 | 4297691 | 154 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot leg in secondary has burned into and there looks to be 2 other bad spots in span I m going to replace wire// Replaced span of #2 secondary and restored customer to full power@ 14:12
19161 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-12-01 08:12 | 2010-12-01 10:45 | 1 | 153 | 61832-1 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 37830249B00077-- PATROLLING LINE---- BAD CUTOUT ON POLE 37830249B00141 30T FUSE MD FILED VER/KEP L3/KEP IDC XXXX
19162 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-05-04 23:59 | 2011-05-05 00:50 | 3 | 51 | 4010411 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMIT FUSE. I WILL BE MAKING REPAIRS. I HAVE REPAIRS MADE EVERYTHING OK IDC CHANGED TIME OFF FROM 2251 XXXX
19163 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-09-23 11:23 | 2009-09-23 13:56 | 1 | 153 | 60375-1 | 153 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIR BROKEN NEUT. AND 1 HOT LEG M.P. RELEASED BY CREW 078H12 IDC XXXX
19164 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2010-12-14 08:29 | 2010-12-14 09:20 | 3 | 51 | 66456-1 | 153 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 FUSE BLOWN IN BANK----FUSE APPEARED TO HAVE BROKEN//VER/CRB IDC XXXX
19165 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2010-10-13 07:57 | 2010-10-13 10:30 | 1 | 153 | 59135-1 | 153 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTIONS BAD AT WEATHERHEAD VER/HFP L3/HFP IDC XXXX
19166 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-04-16 09:37 | 2021-04-16 12:10 | 1 | 153 | 4455991 | 153 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection o transformer fuse.. redid connection
19167 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2015-02-05 12:42 | 2015-02-05 15:15 | 1 | 153 | 4992881 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON LINE FUSE 37830321B00047 (1 CUSTOMER)==== OPEN TRANSF 37830321B00047 UP TO CHANGE LINE CUTOUT AT 14:20 CLOSED AT 15:15 === REPLACED LINE CUTOUT POWER OK/ TRANSFROMER (4 CUSTOMERS)ISO 37830321B00047/ COD 5/ DUPLICATE IN HOIS/ VER/BOW // SEE H4992881 L3/HFP HFPC CDC92
19168 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-08-20 16:07 | 2014-08-20 18:40 | 1 | 153 | 4391161 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2 CUTOUTS BROKE ON THIS POLE GOING TO CHANGE ALL 3 /// CHANGED BAD CUT OUTS AND RESTORED SERVICE @ 18:40/// ISO 38831099000108/// COD 1// VER/BOW
19169 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-03-04 07:00 | 2018-03-04 09:33 | 1 | 153 | 4958541 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o-replaced-ds030418
19170 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-02-20 13:45 | 2019-02-20 16:18 | 1 | 153 | 4816721 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole37830271B00215,bad manual,need line crew will have to walk up hollow and creek about 1/2 mile then pole up on hillside,19.9 kv Released by crew 077S04 power restored at 16:18
19171 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-04-22 09:03 | 2012-04-22 11:36 | 1 | 153 | 4693801 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BURNT DOWN AT HOUSE--REPAIRED 1/0 DROP// VER/DBM IDC XXXX
19172 | South Williamson | 3200301 | BELFRY | BELFRY | 2016-01-05 11:15 | 2016-01-05 13:48 | 1 | 153 | 4586671 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS/////////1 LEAD AT XFR BURNED INTO,MADE REPAIRS.ALL OK AFTERWARDS.HAD ALUMINUM RISERS,REPLACED W COPPER RISERS VER/CRB
19173 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-11-20 12:27 | 2009-11-20 15:00 | 1 | 153 | 59242-1 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP WENT BAD == REPLACED CLAMP == POWER OK VER/KEP L3/KEP IDC XXXX
19174 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-09-23 07:57 | 2020-09-23 10:30 | 1 | 153 | 4488101 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout changing
19175 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-06-05 17:26 | 2008-06-05 18:17 | 3 | 51 | 58526-1 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN, REFUSING IT, BAD ARRESTER ON POLE# 1012-C-222//3404302//VER/CRB
19176 | Hazard | 3303902 | LESLIE | WOOTON | 2010-11-24 08:06 | 2010-11-24 08:23 | 9 | 17 | 59224-1 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CREW OPENED RECLOSER TO ISOLATE TROUBLE IN ORDER 59201-1 VER/HFP L3/HFP IDC XXXX
19177 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-06-03 12:22 | 2021-06-03 14:55 | 1 | 153 | 4663211 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced door
19178 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-01-31 07:39 | 2014-01-31 10:12 | 1 | 153 | 4332311 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN 27 KV CUTOUT ON POLE 37830247B00525, NEED LINE CREW AND BUCKET TRUCK.//COD 1// VER/DBM
19179 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-01-08 07:51 | 2015-01-08 10:24 | 1 | 153 | 4918341 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | APPEARS TO BE A XFR TO RE-FUSE////////RE-FUSED AND RESTORED,FUSE APPEARED TO HAVE MELTED OUT,BUT ALSO COULD HAVE BEEN EXCESSIVE SPRING TENSION OF CUTOUT DOOR/COD1// VER/ ADH
19180 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2021-03-29 02:45 | 2021-03-29 03:36 | 3 | 51 | 4395571 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | oo 3 CUSTOMERS AFFECTEDoo Bad ug cable on 785-388. Crew enroute with equipment to repair. Opened line fuse 785-1733 @ 2:45 to complete repairs. Restored @ 3:36. sh
19181 | Pikeville | 3408401 | KIMPER | LONGFORK | 2011-08-20 12:12 | 2011-08-20 14:45 | 1 | 153 | 4733421 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV. END MELTED OUT REPAIRS BEING MADE,,ALL REPAIRS ARE MADE ON OUR END, CUST DISC STILL GETTING HOT, CUST DOES NOT WANT TO BE DISC FOR REPAIRS UNTIL MONDAY,,WILL CALL WITH TIME VER/HFP L3/HFP IDC XXXX
19182 | Paintsville | 3401802 | INDEX | HOSPITAL | 2014-09-08 13:57 | 2014-09-08 16:30 | 1 | 153 | 4480191 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN XFMR FUSE VER/CRB
19183 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-05-03 04:59 | 2011-05-03 05:50 | 3 | 51 | 53872-1 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | W/R # 39799479 OPENED XFMR @ 5:25 TO CHANGE BAD CUTOUT. REPLACED CUTOUT AND CLOSED AT 5:50. SH VER/PDP IDC XXXX
19184 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-10-14 12:39 | 2010-10-14 13:30 | 3 | 51 | 59661-1 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/P FRANK AT 1158 UNTIED CONDUCTORS MOUNTED THE CUTOUT ON THE POLE. ALL CUSTOMERS RESTORED. WE WILL NEED TO REPLACE THIS POLE. COD-3 VER/HFP L3/HFP IDCC TOF1153 ESTIMATED TIME OFF XXXX
19185 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2017-08-30 16:12 | 2017-08-30 18:45 | 1 | 153 | 4311081 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN. OPENED TRANSFORMER FUSE AT 1822-1845 38830020D37013REPAIR BAD SD. OPEN XFMER @ 20-7013 @ 18:22 CLOSED @ 18:45 VER/AWD // SEE H4311081 FOR XFMR OUTAGE VER/HFP L3/HFP
19186 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-04-24 18:57 | 2016-04-24 19:48 | 3 | 51 | 4121871 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY HAS GOTTEN INTO CATV & TRIPPED CSP BREAKER RELEASED BY CREW 074S04OPEN WIRE SECONDARY WAS SHORTED OUT WITH CATV MESSANGER. RESAGGED SECONDARY & CLOSED CSP BREAKER VER/CRB
19187 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-06-06 13:47 | 2008-06-06 16:20 | 1 | 153 | 59155-1 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER CREW ENROUTE VER/HFP
19188 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-03-22 14:14 | 2013-03-22 15:05 | 3 | 51 | 4948231 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE, I CHECKED AND REFUSED XFMR // COD 3// VER/DBM IDC XXXX
19189 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2016-04-27 16:48 | 2016-04-27 17:05 | 9 | 17 | 4133661 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | HENDRIX SPACER SLID DOWN MESSENGER AND ALLOWED SLACK TO FALL CLOSE TO SECONDARY AT POLE. LIFTED HOT-LINE CLAMPS ON 38830954B40093 AT 16:48 THIS OUTAGED XFMRS ON POLES 38830954B40107, 1430 AND 93. MADE REPAIRS AND RESTORED ALL OUTAGED CUSTOMERS AT 17:05. SH VER/HFP L3/HFP
19190 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-02-13 17:17 | 2008-02-13 19:50 | 1 | 153 | 62791-1 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3007904// REPLACED BAD SERVICE SPLICE// VER/TOM IDC XXXX
19191 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-09-04 22:42 | 2022-09-05 01:15 | 1 | 153 | 4837331 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Trans open 167-D-440,Will be trying to get back in..Trans was changed during flood and crew left arrester laying against Guy wire will have to climb pole and move arrester,Restored 01:15.
19192 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-12-08 10:09 | 2017-12-08 11:00 | 3 | 51 | 4630171 | 153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout, idc changed count from 2 and the clearing pole will need changed to 3 in DOVS.
19193 | Cannonsburg | 3001401 | LOUISA | CITY | 2018-01-12 15:24 | 2018-01-12 17:56 | 1 | 152 | 4737361 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva 7200, trucks ok, linecrew required Released by crew 078S11repairs made all cust restored @1756 please close ticket thanks.bt
19194 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-11-25 18:04 | 2018-11-25 20:36 | 1 | 152 | 4475951 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replace connections customer does seem to have damages L3/HFP
19195 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-04-24 08:28 | 2017-04-24 11:00 | 1 | 152 | 4674331 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAD PART POWER//FOUND BAD CONNECTION AT XFMR//I REWORKED CONNECTION AND SERVICE IS BACK TO NORMAL//RESTORED AT 11;00//COMPLETE//EM/ ISO 38820747B10445/ COD 1/ VER/BOW L3/HFP XXXHFP
19196 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-09-12 18:59 | 2014-09-12 21:31 | 1 | 152 | 4494661 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | POLE 67-598 BAD UNDERGROUND NEED TEP. SET CALL LINE CREW RELEASED BY CREW 078S08/BAD UG/POWER TEMP INSTALLED/PLEASE COPY L RAYBURN AND B REYNOLDS/VEM// COD 1// EMAILED LLYOD AND BOBBY ADH//VER/ ADH
19197 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-02-02 14:52 | 2011-02-02 15:30 | 4 | 38 | 53521-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 45-6559 HOT TAP BROKE OFF IN WIND VER/KEP IDC XXXX
19198 | South Williamson | 3411401 | DEWEY | INEZ | 2018-03-29 10:46 | 2018-03-29 13:18 | 1 | 152 | 4146671 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Bad arrester on 38830815B00018. Opened 1308-1315.
19199 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-02-23 09:13 | 2019-02-23 11:45 | 1 | 152 | 4847671 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | primary responder should call Shawn Sumner for more details (606-213-5782)//this is actually fed from hurley-racefork per shawn, but is handled by KY.please send copy to PR..lightening arrester blowed in clear on pri. metering pole 127-132.pri. meter is energized and will need arrester changed out in near future.road to metering will need maintained in order to get truck access.
19200 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2018-06-24 09:58 | 2018-06-24 10:36 | 4 | 38 | 4655941 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I opened line fuse on pole 38821086C00059 at 09:58 so the FD get put pole fire out at pole 38821086C00428. I got cutout replaced and closed back in at 10:36. Send to Cliff Freeman to have this pole replaced ASAP there is not much holding the pole top./ ISO 38821086C00059/ COD 4
19201 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-11-02 11:43 | 2021-11-02 14:15 | 1 | 152 | 4049211 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burndt into @ trans. 1150-340, got repaired @1415.
19202 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-03-10 15:24 | 2020-03-10 16:40 | 2 | 76 | 4466271 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service barrel burnt out. made repaires
19203 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-05-12 08:54 | 2011-05-12 10:10 | 2 | 76 | 4070801 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 XFORMER ON POLE 287-129. TRUCKS TO POLE. VER/KEP
19204 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-02-21 09:25 | 2013-02-21 10:41 | 2 | 76 | 4836961 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING BAD WILL TO OPEN OTHER TWO FUSES ON BANK POLE139-353 VER/KEP IDC XXXX
19205 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-09-12 09:26 | 2016-09-12 11:58 | 1 | 152 | 4887101 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION ON POLE..REPAIRED VER/CRB
19206 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-09-04 09:48 | 2020-09-04 12:20 | 1 | 152 | 4430161 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power i think due to bad connection at trasformer. replaced bad connections at transformer checked voltage everything ok. put cust meter back in @ 12:20
19207 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-02-21 09:03 | 2015-02-21 11:35 | 1 | 152 | 4061571 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NO TRUCKS TO POLE NEED LINE CREW. RELEASED BY CREW 078S01//COD 1// VER/DBM LE/DKG VERIFIED TTIME WITH VOICE RECORDER
19208 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-05-14 20:19 | 2010-05-14 21:35 | 2 | 76 | 62350-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35131921 //, CUTOUT IS BROKE ON XFMR CCC COD-2 ISO TF 37830230D00189 VER/HFP L3/HFP IDC XXXX
19209 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2008-11-18 14:19 | 2008-11-18 16:51 | 1 | 152 | 66271-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP STS WR # 27342191 ///BAD UG--L MACARTY TO INSTALL POWER TEMP RELEASED BY CREW 078S07 IDC XXXX
19210 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-06-05 07:44 | 2013-06-05 09:00 | 2 | 76 | 4221201 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE, I CHECKED AND REFUSED XFMR ////VER/CRB L/3 CRB IDC XXXX
19211 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-04-11 14:32 | 2018-04-11 15:10 | 4 | 38 | 4211481 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout open transformer at 14 49 and closed at 1510/ ISO 37830004C00082/ COD 4
19212 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2014-07-11 14:29 | 2014-07-11 17:01 | 1 | 152 | 4230051 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN // WILL REFUSE/// BAD 50 KVA// T. HALL ROUNDING UP CREW//REPLACED XFMR// POWER RESTORED @ 17:01 VER/CRB
19213 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-07-02 20:14 | 2008-07-02 22:46 | 1 | 152 | 61393-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3110902// POLE LEANING VERY BADLY, NEED A LINE TRUCK TO STRAIGHTEN THIS POLE, AM WAITING FOR TRUCK NOW RELEASED BY CREW 078S06/ POLE ROTTED OFF WILL HAVE 1 CUSTOMER OFF AFTER WE GET POLE SET/ HAVE PRI. TRASFERED @ 10:14 PM WORKING ON XFR// // VER/TOM IDC XXXX
19214 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2022-07-14 21:29 | 2022-07-14 22:45 | 2 | 76 | 4492491 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Cutout door burnt up will replace///replaced door and restored service @ 22:45
19215 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-11-05 18:54 | 2013-11-05 20:10 | 2 | 76 | 4013141 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-234 BAD CUTOUT AND LA CHGED VER/HFP L3/HFP
19216 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-09-01 17:15 | 2012-09-01 17:34 | 8 | 19 | H4992321 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER/// OPENED XFMR FUSE ON POLE 172-51, TO SEC. LEADS WERE RUBBING TOGETHER AND BURN,T ONE INTO. FIXED LEAD, POWER RESTORED. OPENED XFMR AT 17:15 CLOSED XFMR AT 17:34. DUPLICATE IN HOIS FOR THIS ONE COD-9 ISO TF 37830172A00051 DUP FROM 4992321 FOR 8 CUST ---- VER/HFP L3/HFP IDC XXXX
19217 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-09-18 16:43 | 2018-09-18 19:15 | 1 | 152 | 4127791 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 7200 CUTOUT
19218 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2017-05-31 08:23 | 2017-05-31 10:55 | 1 | 152 | 4884731 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING BAD XFMR @ POLE 37830163B20385. DUE TO BAD TRANSFORMER POLE 163-385 I OPENED 30T LINE FUSE ON POLE 163-228 AT 08:35 PLACED TAG FOR MYSELF AND PLACED GROUND AT POLE 163-228 // CLOSED 30T FUSE BACK IN AT 10:55 AT POLE 163-228 COD-1 ISO LF37830163B10228
19219 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-03-18 16:45 | 2014-03-18 19:17 | 1 | 152 | 4506341 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 38830068A00965 ROTTEN AND FELL OVER--NEED 3 MAN CREW 30 CL 6 POLE--1/0 SERVICE FOR SPLICING--TRUCK TO POLES--OPENED TRANSFORMER AT 16:45 /// MULLINS & CANTRELL & MCCOY/CREW ON SITE/FETR2015/VEM/REPAIRS MADE POWER RESTORED TO ALL CUST 1917/PLEASE CLOSE TICKET/VEM COD-1 ISO TF 38830068A00073 VER/HFP L3/HFP
19220 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-04-06 20:09 | 2008-04-06 21:25 | 2 | 76 | 64726-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409302// 6T FUSE OUT ON POLE 882B7 . 6T FUSE BROKE. REFUSED EVERYTHANG OK. VER/PDP IDC XXXX
19221 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2016-03-13 14:10 | 2016-03-13 14:29 | 8 | 19 | 4840561 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BREAKING DOWN ON FUSE POLE 37820172000061 // @ 1410 SERVICER ISOLATING TO MAKE REPAIRS / ON @ 1429 COD-8 (5 ON FUSE & 3 ON XFMR) ISO LF @ 37820172000061 VER/HFP L3/HFP
19222 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-08-23 07:14 | 2014-08-23 08:30 | 2 | 76 | 4411361 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT. VER/KEP
19223 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-03-16 15:45 | 2020-03-16 17:05 | 4 | 80 | 4483281 | 152 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Secondary burned apart mid span at pole 205A-223, going to open this XFMR to make repairs. XFMR opened from 16:41 to 17:05
19224 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2019-04-06 22:52 | 2019-04-06 23:30 | 4 | 38 | 4065021 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Secondary connection failed at xfmr riser. Opened xfmr 784-403 @ 22:52 to make repairs. Reworked sec connections and restored @ 23:30. ooMAP DISCREPANCYoo 1/0 secondary to 38830784A00255 is fed from 38830784A00403..not 784-254. Was re-routed during storm repairs a few years back. sh/ no power out originally/ iso 38830784A00403 cod 4 L3/HFP
19225 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2008-06-12 11:48 | 2008-06-12 14:20 | 1 | 152 | 63111-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000601//REPLACING SERVICE IDC XXXX
19226 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-04-17 18:43 | 2014-04-17 21:15 | 1 | 152 | 4615781 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA XFMR BAD ON 737-209. CREW ENROUTE TO CHANGE. REPLACED BAD XFMR AND RESTORED @ 21:15. SH//COD 1// VER/DBM
19227 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-01-24 08:52 | 2015-01-24 10:08 | 2 | 76 | 4957561 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR HAS BURNED UP. I AM GOING TO REPLACE CUTOUT DOOR. I CHANGED CUTOUT DOOR// COD 2// VER/ ADH
19228 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-03-28 05:48 | 2021-03-28 08:20 | 1 | 152 | 4388891 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held per KYPCO late night callout guidelines. Will be worked in daylight hours//,,replaced xfr cutout complete
19229 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2022-02-24 09:22 | 2022-02-24 11:54 | 1 | 152 | 4539181 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer cut out on pole 1036C-34 broke.will be making repairs .replace cutout and got transformer fuse back in at 11:54
19230 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-01-28 23:09 | 2011-01-29 00:25 | 2 | 76 | 51690-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. CHECKED SECONDARY AND RE-FUSED @ 0025. SH VER/ARN IDC XXXX
19231 | Hazard | 3309301 | VICCO | REDFOX | 2019-03-14 10:14 | 2019-03-14 12:46 | 1 | 152 | 4979991 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | pole 326-20 had a guy breaker to fail burning down primary tap going to pole 132, will ned crew, can work with big bucket
19232 | Hazard | 3303902 | LESLIE | WOOTON | 2008-04-10 13:13 | 2008-04-10 15:45 | 1 | 152 | 65755-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE ROTTED OUT//3303902//VER/CRB IDC XXXX
19233 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2022-06-08 16:27 | 2022-06-08 16:46 | 8 | 19 | 4038751 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | No outage till LF 402-D-18 was opened (1627)bad cutout on pole 402-D-18. cutout replaced. power restored. closed @ 16:46
19234 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-02-13 07:24 | 2008-02-13 09:56 | 1 | 152 | 62148-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3110902// BROKE CUTOUT//COD 1// VER/DBM IDC XXXX
19235 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-01-29 18:06 | 2008-01-29 18:25 | 8 | 19 | 60749-1H | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601// LOOKS LIKE STEPDOWN OUT @ POLE 38830092B00187 COD 86//B AN C PHASE LOAD SIDE FUSES BLOWN/PATROLING LINE/PATROLING LINE/ B-PHASE CUTOUT BAD/CALLED DRT TO HELP/ OPENED A PHASE AT 18:06B AN C PHASE LOAD SIDE FUSES BLOWN/PATROLING LINE/ B-PHASE CUTOUT BAD/CALLED DRT TO HELP/ OPENED A PHASE AT 18:06/ REPLACED 2 CUTOUTS ON TRANSFORMER BANK/ A AN B PHASE// THIS OUTAGE ACCOUNTS FOR A/C PHASES BEING IDC XXXX
19236 | South Williamson | 3200301 | BELFRY | BELFRY | 2010-04-08 12:35 | 2010-04-08 13:51 | 2 | 76 | 60908-1 | 152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE#1013-C-54, SEND TO JOEY REED RELEASED BY CREW 080S01 COD-2 VER/HFP L3/HFP IDCC PN320 XXXX
19237 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-12-23 09:44 | 2008-12-23 12:15 | 1 | 151 | 62996-1 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3103101/BAD 10 KVA TRUCKS OK/TURN AT CAR WASH AT GLOBE REEVES LN. GO TO LAST HOUSE UP HILL 468 ON HOUSE/SEND TO PAUL STEVENS/WR#27788774/UPGRADE TO 15KVA MD FILED/ VER/KEP L3/KEP IDC XXXX
19238 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2015-11-19 02:14 | 2015-11-19 04:45 | 1 | 151 | 4468731 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED ON 954-129 AND BLEW LINE FUSE. FRAMED DOWN ON POLE, REPLACED CUTOUT AND RESTORED LINE FUSE @ 4:45. SH// . VER/TOM L3/TOM
19239 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2020-12-06 17:19 | 2020-12-06 19:50 | 1 | 151 | 4749491 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connections
19240 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-19 18:04 | 2009-06-19 20:35 | 1 | 151 | 58765-1 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED UP-----REPACED CUTOUT DOOR IDC XXXX
19241 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2012-02-28 19:49 | 2012-02-28 22:20 | 1 | 151 | 4515731 | 151 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL AND 1 HOT LEG BURNT INTO AT SERVICE POLE.GOING TO REPLACE DROP.ONLY ONE CUSTOMER WAS EFFECTED POWER RESTORED @ 22:20// VER/DBM IDC XXXX
19242 | Hazard | 3311103 | STINNETT | WENDOVER | 2009-03-02 12:14 | 2009-03-02 14:45 | 1 | 151 | 53964-1 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 5 KVA 7.2KV RELEASED BY CREW 077S01//3311103// REPLACED XFRM CHECKED VOLTAGE RESTORED POWER AT 1445 P HICKMAN//VER/CRB IDC XXXX
19243 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-04-14 17:14 | 2015-04-14 19:45 | 1 | 151 | 4318861 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100 KVA XFM 7200 120/208 BANK 2 BUSHING/// CAN USE TRUCK THIS IS SHONEYS BELW THE COMPANY//// NEED LINE CREW ////I HAVE TALKED TO TIM MCCOY ON THIS RELEASED BY CREW 074H17/// CHANGED BAD XFMR AND RESTORED POWER AT 19:45 TIM MCCOY RELEASED BY CREW 074H10// VER/ ADH
19244 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-06-16 14:29 | 2011-06-16 17:00 | 1 | 151 | 4328521 | 151 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY LUG LOOSE ON XFORM CAUSING SERVICE DROP TO ALMOST BURN INTO REWORKED SER. AND LUG RESQUEEZE SERVICE ON XFORM POWER RESTORED 17:00 // COD 1// VER/DBM
19245 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-10-01 13:45 | 2022-10-01 16:16 | 1 | 151 | 4960131 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connections
19246 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-12-10 21:13 | 2018-12-10 23:44 | 1 | 151 | 4549521 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Changed connections @ xfm and weatherhead/// everything ok now 120/120/240 L3/HFP
19247 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2011-03-01 16:54 | 2011-03-01 19:25 | 1 | 151 | 65590-1 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION BURNT OPEN MIDSPAN. WILL HAVE TO LET 2/3 SECONDARY DOWN TO REPAIR. REPLACED 100 FT OF 2/3 TWIST. RESTORED @ 19:25. SH.//VER/CRB IDC XXXX
19248 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2013-05-30 11:44 | 2013-05-30 14:15 | 1 | 151 | 4198271 | 151 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED WENT BAD . ONLY ONE CUST. HAD PART POWER METER # 533968614// VER/DBM IDC XXXX
19249 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2018-05-11 19:17 | 2018-05-11 21:48 | 1 | 151 | 4338421 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | pole39831147D30676, bad 7200, 25 kva. trk to pole at end of ferguson dr. off thompson rd in belhaven. Released by crew 078S07//NEED TRANS BAG//arrived RM power on @21:48 please close tic RM
19250 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2019-07-30 15:24 | 2019-07-30 17:35 | 3 | 131 | 4808331 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Guy wire has sagged down into cutout blowing xfm fuse// will take slack out of guy/// Will have to get ROW crew to cut at get to pole Kudzu vines has taken over lf off @ 1720 on @ 1730 Xfer on @ 1735
19251 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2010-10-27 15:20 | 2010-10-27 17:51 | 1 | 151 | 65843-1 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ENROUTE RELEASED BY CREW 074S02//COD 1// VER/DBM IDCC PN517 XXXX
19252 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-04-05 09:49 | 2021-04-05 12:20 | 1 | 151 | 4418891 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced 6sec burnt up-all good-ds040521
19253 | Hazard | 3309301 | VICCO | REDFOX | 2019-12-19 07:47 | 2019-12-19 10:18 | 1 | 151 | 4168991 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on service pole. made repairs
19254 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-02-02 11:54 | 2018-02-02 14:25 | 1 | 151 | 4795001 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 drop burnt neutral and conductor into...replaced drop with 2/3 service...
19255 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-12-08 12:53 | 2019-12-08 15:24 | 1 | 151 | 4135221 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broken on pole 37830335D00125.will lift hot tap on pole 37830335D00077 and make repairs..cutout broken on pole 335-125.will lift hot tap on pole 37830335D00077 and make repairs..restored.
19256 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-06-13 08:59 | 2018-06-13 11:30 | 1 | 151 | 4595451 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfr cutout replaced complete
19257 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-01-14 19:44 | 2008-01-14 22:15 | 1 | 151 | 56754-1 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 WIRE, 300 FEET 6A SEC. DOWN//34017021//WIRE, 300 FEET 6A SEC. DOWN. COMP..........DAH//VER/CRB IDC XXXX
19258 | South Williamson | 3411401 | DEWEY | INEZ | 2022-04-10 11:44 | 2022-04-10 14:15 | 1 | 151 | 4745071 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tree fell and broke tv line.when tree fell it shook pole 695C-80 breaking cutout.i replace cutout and got transformer fuse back in at 14:15
19259 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-10-01 13:14 | 2013-10-01 15:45 | 1 | 151 | 4902221 | 151 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTIONS THAT WAS HEATING UP AT SEC. AND XFMR POLE// CUST. STATED THAT THEIR PROBLEM SEEMED TO BE CORRECTED VER/CRB L/3 CRB IDC XXXX
19260 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-11-19 15:34 | 2014-11-19 18:05 | 1 | 151 | 4746831 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN INSU-LINK MID SPAN WHICH BURNT NEUT IN TO GOING TO REPLACE WHOLE DROP. CUST STATES BURNT UP STUFF INSIDE WALLS.. WILL TURN IN DROP IN THE MORN. ALL PWR RESTORED PLEASE CLOSE TICKET//MTR # 532943500// SENT TO PEGGY WYSONG VER/CRB
19261 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-11-15 09:24 | 2015-11-15 11:55 | 1 | 151 | 4449261 | 151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST BACK AND THEY SAID THEY CHECEKED BREAKERS & RESET THEM - PER SERVICER ONLY 1 CUSTOMER ON THIS XFMR // XFMR FUSE LINK APPEARS TO HAVE BROKE. RESTORED @ 11:55. SH /// VER/HFP L3/HFP
19262 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-02-22 08:49 | 2009-02-22 11:20 | 1 | 151 | 50246-1 | 151 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD CONNECTION ON CUSTOMERS SEVICE POLE L3/HFP IDCC CCO XXXX
19263 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2008-12-07 15:00 | 2008-12-07 15:30 | 5 | 30 | 55151-1H | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3410601// SECONDARY CONNECTION BURNT OPEN. WILL NEED TO OPEN XFMR TO REPAIR. OPENED AT 15:00. MADE REPAIRS AND CLOSED AT 15:30. SH // OTHER CUSTOMER OUTAGED ON 55151-1 //6 COD// VER/TOM L3/TOM IDC XXXX
19264 | Pikeville | 3421001 | BREAKS | CITY | 2013-05-05 17:30 | 2013-05-05 18:45 | 2 | 75 | 4073961 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP FAILED I REPLACED IT.//COD 2// VER/DBM IDC XXXX
19265 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-11-14 19:30 | 2019-11-14 22:00 | 1 | 150 | 4035291 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1930-2200
19266 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2014-04-16 16:45 | 2014-04-16 19:15 | 1 | 150 | 4613021 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA BETWEEN KENNEDY AND VAN BUREN, CAN USE TRUCK, LINE CREW REQ RELEASED BY CREW 078S06//COD 1//ISO// VER/DBM
19267 | Hazard | 3302704 | HAZARD | KENMONT | 2015-09-04 20:55 | 2015-09-04 22:10 | 2 | 75 | 4203061 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL BROKE..POWER RESTORED. VER/TOM L3/TOM
19268 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2013-05-06 16:50 | 2013-05-06 18:05 | 2 | 75 | 4078181 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE//I REFUSED AND RESTORED AT 1805//COMPLETE//EM ///VER/CRB L/3 CRB IDC XXXX
19269 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-05-25 10:59 | 2014-05-25 12:14 | 2 | 75 | 4929211 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED FUSE DOOR COD-2 ISO TF 38830269A00335 VER/HFP L3/HFP
19270 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-01-07 20:05 | 2014-01-07 21:20 | 2 | 75 | 4255841 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN ON BOTH HOTLEGS, REDONE CONN APR AT 0920 CLOSE TICKET COD-2 ISO SO 38830551000056 VER/HFP L3/HFP
19271 | South Williamson | 3411401 | DEWEY | INEZ | 2012-08-17 12:55 | 2012-08-17 15:25 | 1 | 150 | 4946861 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LUG BROKE ON XFMR AND ONE HOT LEG FELL OUT///GOING TO OPEN XFMR AND CLIMB POLE AND REPAIR LUG//REPAIRS MADE//RESTORED AT1525//COMPLETE//EM VER/KEP IDC XXXX
19272 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-03-01 07:00 | 2020-03-01 08:15 | 2 | 75 | 4441721 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Open wire secondary burnt down opened Xfm @ 07:00 will replace with 1/0twist///Replaced open wire with 1/0 twist and restored service @ 08:15 L3/HFP
19273 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2016-01-28 14:15 | 2016-01-28 15:30 | 2 | 75 | 4656861 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT ON POLE 425-51, WILL HAVE TO OPEN LINE FUSE ON THAT POLE TO REPLACE IT ..OPENED LINE FUSE AT 15:21 REPLACED CUTOUT RESTORED POWER AT 15:30.. VER/KEP
19274 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2018-05-11 12:19 | 2018-05-11 14:49 | 1 | 150 | 4336611 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Replaced one bad conn at weatherhead, apr at 1449, alos advised customer to upgrade service close ticket/ ISO 38830310C10102/ COD 1
19275 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-02-25 10:00 | 2020-02-25 12:30 | 1 | 150 | 4430401 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | will need to replace cutout and arrestor, T Smith crew to replace, they start at 1000 hrs Released by crew 077S02 power restored at 12:30 L3/HFP
19276 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-08-15 21:20 | 2020-08-15 22:35 | 2 | 75 | 4333301 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | red-red pulled apart on xfmr lead, I replaced it
19277 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2017-08-07 17:10 | 2017-08-07 18:00 | 3 | 50 | 4236031 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS BROKE REFUSED XMF APR AT 1800 CLOSE TICKET/ ISO 38830478A31028/ COD 3/ VER/BOW
19278 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2014-08-01 13:50 | 2014-08-01 16:20 | 1 | 150 | 4317391 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANFORMER FUSE BLOWN WILL REFUSE/// BAD 50 KVA TALKED TO TIM MCCOY HE HAS CREW ENROUTE/// CAN GO BACK WITH 25 KVA JUST FEEDS ONE HOUSE/// MAY BE ABLE TO USE TRUCK//// REPLACED BAD TRANSFORMER, CUT OUT AND BRACKET /// RESTORED SERVICE @ 16 :20. VER/CRB
19279 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2021-11-09 13:43 | 2021-11-09 14:58 | 2 | 75 | 4070701 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
19280 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-05-13 21:43 | 2017-05-13 22:58 | 2 | 75 | 4796721 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE PULLED INTO @115-16, REFUSED @2258.
19281 | Hazard | 3303903 | LESLIE | HALSFORK | 2021-06-08 20:10 | 2021-06-08 22:40 | 1 | 150 | 4692451 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke line fuse cutout
19282 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2009-06-17 17:30 | 2009-06-17 18:45 | 2 | 75 | 64804-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//VER/CRB IDC XXXX
19283 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-06-21 10:01 | 2022-06-21 12:31 | 1 | 150 | 4267931 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 771-79//repairs made//restored at 12:31//complete//em
19284 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-10-14 22:00 | 2014-10-15 00:30 | 1 | 150 | 4628961 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WAS BROKE//// CHANGED BAD CUTOUT/// CLOSED TRANSFORMER BACK IN @ 12:30 RELEASED BY CREW 074H17 VER/CRB
19285 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2020-06-23 14:45 | 2020-06-23 15:35 | 3 | 50 | 4064201 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lifted hot tap on broken transformer cutout on pole 38830162C00271, closed Line fuse on 162-251 @ 15:35. Crew required at later date. Transformer just feeds one street light. Please send copy to vernon mullins
19286 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2019-11-27 06:27 | 2019-11-27 08:57 | 1 | 150 | 4071951 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad c/o--replaced-ds112719
19287 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-08-15 20:45 | 2020-08-15 22:00 | 2 | 75 | 4333181 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Restored @ 2200
19288 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-03-18 17:05 | 2009-03-18 18:20 | 2 | 75 | 59913-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP RELATED TO ORDER 59830-1 CREW HAD TO OPEN TRANSFORMER TO MAKE REPAIRS TO CONDUCTOR ON THAT ORDER L3/HFP IDC XXXX
19289 | Hazard | 3420001 | SOFT SHELL | VEST | 2020-02-21 22:30 | 2020-02-21 23:45 | 2 | 75 | 4423501 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad secondary connection on pole 132-8. Power restored at 23:45/ ISO 37830132000008/ COD 2 L3/HFP
19290 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-12-21 12:20 | 2012-12-21 14:50 | 1 | 150 | 4500591 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE IN SERVICE NEUTRAL PULLED OUT ONLY ONE CUSTOMER AFFECTED, REPAIRED NEUTRAL RESTORED POWER AT 14:50 ////VER/CRB L/3 CRB
19291 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-05-03 16:48 | 2021-05-03 19:18 | 1 | 150 | 4518071 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 19:18. sh
19292 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-04-04 14:30 | 2008-04-04 17:00 | 1 | 150 | 63917-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401801//BAD CUTOUT HAS 678-253 BURNED HALFWAY INTO..CALLED CREW,,BB RELEASED BY CREW 076S01// ????? VER/HFP IDC CHANGED START TIME FROM 1258, CHANGED FAULT POLE FROM 678, CHANGE CLEARING POLE FROM 11, EST TIME OFF XXXX
19293 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-12-02 16:00 | 2014-12-02 18:30 | 1 | 150 | 4827151 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CONTACT BROKE ON XFMR CUTOUT CAUSING A SINGLE PHASE CONDITION. REPLACING CUTOUT. OOONLY ONE CUSTOMER AFFECTEDOO REPLACED CUTOUT AND RESTORED @ 18:30. SH VER/CRB
19294 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-12-28 06:50 | 2022-12-28 09:20 | 1 | 150 | 4369051 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 19.9 50kva transformer on pole37830375A32784 right in front of Moutain truck parts in isom. Truck access. Need linecrew.Bad 19.9 50kva transformer on pole 375-2784 right in front of Moutain truck parts in isom. Truck access. Need linecrew. Made repairs. Restored at 09:20.
19295 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-06-17 21:25 | 2017-06-17 22:40 | 2 | 75 | 4989481 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | POLE 140-469 1.6 19.9 FUSE PULLED LOOSE//COD 2
19296 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-05-31 17:45 | 2014-05-31 20:15 | 1 | 150 | 4957441 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OPENED TRANS 17:45 LINE BROKE ON HOT TAP RELEASED BY CREW 078S08/FETR 21:30/ REPAIRS COMPLETE POWER REST.@ 20:15/ JEH CLOSE TICKET PLEASE VER/CRB
19297 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-06-16 12:35 | 2013-06-16 13:50 | 2 | 75 | 4348221 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS IN #4 SERVICE FEEDING 200 AMP ENTRANCE HAVE BEEN HOT MELTING INSULATION OFF HOT CONDUCTORS. OPENED XFMR ON 737-92 @ 12:35, REPLACED SERVICE AND CLOSED XFMR @ 13:50. SH//CO D2// VER/DBM IDCC FEC44 XXXX
19298 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-08-05 20:35 | 2018-08-05 21:50 | 2 | 75 | 4911791 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1148-62 bad 556 basket, needs replaced. temp fix
19299 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-03-12 11:05 | 2012-03-12 11:35 | 5 | 30 | 4571211 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT CUST. POLE., REMADE CONNECTIONS.--- OPENED TRANSFORMER AT 11:05, CLOSED AT 11:35. /// COD-5 ISO TF 37830246D00453 VER/HFP L3/HFP IDC XXXX
19300 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-09-29 16:57 | 2011-09-29 19:27 | 1 | 150 | 4932521 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CANT FIND A SERVICER TO GO, ATTEMPTED TO CONTACT DUTY SUPERVISOR @ 1730 // ATTEMPTED BACKUP DUTY @ 1734 // NO RESPONSE // REPAIRED COND ALL POWER RESTORED AT 1927 CLOSE TICKET//FARM SERVICE NEED TECH TO CHECK IF THE CONDUCTOR IN QUESTION FROM MTR BASE TO HOUSE IS OURS OR CUST ///VER/CRB IDC XXXX
19301 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-03-16 11:12 | 2015-03-16 13:42 | 1 | 150 | 4199091 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | FOUND INSULINK CONNECTION HEATING UP ON XFMR POLE. REWORKED CONNECTIONS. SH VER/HFP L3/HFP
19302 | Pikeville | 3407101 | TOPMOST | DEMA | 2019-04-24 12:15 | 2019-04-24 13:30 | 2 | 75 | 4153941 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replaced leaking xfmr /// opened at 12:15 on at 13:30
19303 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-06-11 18:25 | 2017-06-11 20:55 | 1 | 150 | 4931661 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON PRIMARY METERING CHANGING./ ISO 38830805000042/ COD 1
19304 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-07-31 21:15 | 2009-07-31 21:45 | 5 | 30 | 54092-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 494-79 HAVE TO OPEN LINE FUSE ON POLE 518-40 TO ISOLATE, OPENED AT 21:15 CLOSED FUSE AT 21:45 RESTORING POWER//COD 5// VER/DBM IDC XXXX
19305 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-05-22 19:10 | 2015-05-22 20:00 | 3 | 50 | 4457821 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 68-1114 6T ME FUSE LINK BROKE INSTALLED 10T 50KVA TRANS.// VER/ ADH
19306 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-02-19 14:45 | 2013-02-19 15:15 | 5 | 30 | 4830901 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED LINE FUSES ON POLE 1145-84 AT 14:45 WE REPLACED BURNT OFF CROSS ARM AT POLE 1145-87. AND CLOSED FUSES BACK IN AT 15:15. BAD CUTOUT BURNT CROSS ARM INTO. ///VER/CRB L/3 CRB IDC XXXX
19307 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-02-18 10:29 | 2013-02-18 11:44 | 2 | 75 | 4826591 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 380-329,REPLACED CUTOUT RESTORED POWER AT 11:44 ///VER/CRB L/3 CRB IDCC CDC83 XXXX
19308 | Paintsville | 3401802 | INDEX | HOSPITAL | 2011-08-25 07:40 | 2011-08-25 10:10 | 1 | 150 | 4754041 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY RISER BURNT OFF AT HOT-LINE-CLAMP CONNECTION. REPLACED CLAMP AND RESTORED @ 10:10. SH 38830654A00187 VER/KEP IDC XXXX
19309 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-05-12 14:30 | 2009-05-12 15:20 | 3 | 50 | 65006-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT AT POLE 353-239. IT HAS ALSO BURNED LOOP APART GOING TO NEXT POLE. CECIL SEXTON IS ENROUTE TO HELP ME ON THIS//VER/CRB IDC CHANGED START TIME FROM 1305 AND COUNT FROM 1 XXXX
19310 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-09-27 16:04 | 2008-09-27 16:54 | 3 | 50 | 51450-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP ARRESTOR BAD ON POLE 38821063B00083 COD-3 BAD ARRESTRE AT POLE# 1063-B-83, CLEARED ARRESTER, MAKING LINE HOT IDC XXXX
19311 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2017-12-17 13:45 | 2017-12-17 16:15 | 1 | 150 | 4654611 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Per PR #4 svc drop down feeding tan trailer up on hill, #2 service drop burndt into in 2 different locations, will have to replace, pole is manual will have to open trans. on 49-76, will keep track of times. 1 customer out originally service outage/ Opened trans. @1536, put back on @1615 1 additional customer, all power restored./ ISO 37820049000076/ COD 2
19312 | Hazard | 3309301 | VICCO | REDFOX | 2021-04-05 15:15 | 2021-04-05 15:45 | 5 | 30 | 4419431 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced service drop, checked all connections opened xfmr at 15:15, closed at 15:45
19313 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2019-05-29 12:08 | 2019-05-29 14:38 | 1 | 150 | 4360371 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Customer is mapped wrong, they are on the load side of recloser pole 37820011D00514 at pole 37820011D00001. Apco had a rotten pole to fall.
19314 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-08-10 13:15 | 2009-08-10 14:05 | 3 | 50 | H55008-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP DUPLICATED FOR C PHASE OUTAGE IN ORDER 55008-1 WR # 31155087 //POLE 141-92 19.9 INS. 40T FUSE OUT 141-72POLE 141-92 19.9 INS. 40T FUSE OUT 141-72 SEND TO BILL .POLE 141-92 19.9 INS. 40T FUSE OUT 141-72 SEND TO BILL . RELEASED BY CREW 078S08 ****** TOOK OTHER PHASE OFF @ 1315 L3/HFP IDC XXXX
19315 | Hazard | 3309003 | JEFF | VIPER | 2018-02-10 19:00 | 2018-02-10 21:17 | 2 | 137 | 4824691 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Open transformer on369/196 at 21/04 on at 21/17 power ok bad conn.//cod 1 + 1
19316 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-06-17 09:06 | 2016-06-17 11:36 | 1 | 150 | 4375931 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SERVICE OUTAGE TO REMOVE POWER TEMP AND REPAIR SERVICE/,,,ALL REPAIRS MADE,,REMOVED POWER TEMP,,FOUND 4 SPLICES IN URD,,PLEASE SEND TO TECH TO WRITE JOB TO REPLACE URD/ ISO 38830189000129/ COD 1/ 6414 LAKEVIEW DR, CATLETTSBURG/ VER/BOW
19317 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-12-10 06:40 | 2008-12-10 09:10 | 1 | 150 | 56004-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3301101 -BROKE CUTOUT //VER/GAH L3/KEP IDC XXXX
19318 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2014-08-12 10:55 | 2014-08-12 11:25 | 5 | 30 | 4360171 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING BAD CUTOUT AT POLE 39831123D16042/// ISO TRANS FUSE 39831123D16042/// COD 5---OPENED XFMR @ 10:55---BACK ON @ 11:25---XFMR 1123-6042 HAS 5 CUSTS.---SEC BREAKERS CUT IN SECONDARY AND TRANSFORMER ON PL# 1123-6068 HAS REMAINING 4 CUSTOMERS/// PER RON VIRGIN FIELD// COD 5 CCC*********// VER/BOW
19319 | South Williamson | 3411401 | DEWEY | INEZ | 2009-05-19 12:57 | 2009-05-19 14:12 | 2 | 75 | 65862-1 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3411401// SERV NEUTRAL BROKE VER/TOM L3/TOM
19320 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-03-03 10:00 | 2016-03-03 10:30 | 5 | 30 | 4806101 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT & ARRESTOER ON POLE 770-57, OPENING LINE FUSE FOR 30 MINUTES TO REPLACE/.OPENED 1000 CLOSED 1030/// VER/ ADH
19321 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-03-09 19:25 | 2020-03-09 21:55 | 1 | 150 | 4464151 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke-38830401A10115-replaced-allgood--lat in at 21-55 Released by crew 078S01
19322 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2009-10-21 12:08 | 2009-10-21 14:38 | 1 | 150 | 62970-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT LOOSE ON 3 PHASE BUCK-ARM POLE. DUTY SUPERVISOR ENROUTE TO ASSIST. REPAIRS COMPLETE. SH//COD 1// VER/DBM IDCC PN1005 XXXX
19323 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-03-09 21:55 | 2015-03-09 22:45 | 3 | 50 | 4174151 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA TRANSFORMER IS LEAKING OIL HERE37830139B00175/// NEED 1 MAN AND 25 KVA 7200 XFM //// CAN USE TRUCK/// OPENED XFM @ 21:55//// CHANGED BAD XFM AND CLOSED NEW XFM IN @ 22:45 AND RESTORED SERVICE VER/CRB L3/DKGXXXX
19324 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-09-05 08:21 | 2012-09-05 10:51 | 1 | 150 | 4017121 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTOR ON HOT LEG AT CUST WEATHER HEAD AT SERVICE ENTRANCE CABLE .. REPAIRED AND EVERYTHING CAME BACK ON EXCEPT FOR ONE OF CUST AIR CONDITIONING UNITS .. HE HAS PROBLEMS ON HIS SIDE.. COMPLETE VER/KEP IDCC CDC92, PN332 XXXX
19325 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-05-30 00:50 | 2009-05-30 03:20 | 1 | 150 | 51043-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PLEASE SEND A NOTE TORON RYE IIN PIKEVILLE TO HAVE XFMR CAP INCREASED FUSE BROKE. THANKS G R. VER/PDP IDC XXXX
19326 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-12-12 19:30 | 2012-12-12 20:20 | 3 | 50 | 4465201 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE DROP. VOLTAGE OK.//OPENED TRANS FROM 1930 TO 2020 ///VER/CRB L/3 CRB
19327 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-11-26 10:50 | 2010-11-26 13:20 | 1 | 150 | 59841-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#37889590 19-69 BURNT OFF OPENED REC. ON POLE 19-67 11;30 AM TEP. POLE 40 CLASS 5 BACK ON 13;20//VER/CRB IDC XXXX
19328 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-03-17 13:58 | 2009-03-17 16:28 | 1 | 150 | 59475-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP BAD PLACE IN SERVICE, OPEN TRANSFORMER AT 1608 AND CLOSED AT 1628 COD-2 THIS IS FOR THE SINGLE CUSTOEMR OUTAGE WILL DUPLICATE FOR THE OTHER CUSTOMER (TRANSFORMER) OUTAGE L3/HFP IDC XXXX
19329 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-02-20 13:40 | 2018-02-20 14:55 | 2 | 75 | 4864621 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required broken fuse
19330 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2011-06-14 11:00 | 2011-06-14 11:30 | 5 | 30 | 4316001 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD WESTINGHOUSE ENCLOSED CUTOUT, HAD TO OPEN LINE FUSE ON POLE 878-25 AT 1100, CHANGED CUTOUT AND CLOSED BACK IN LINE FUSE AT 1130, POWER IS RESTORED AND FLICKERING HAS STOPPED COD-5 ISO LF 39830878000025 VER/HFP L3/HFP IDC XXXX
19331 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-03-17 22:30 | 2017-03-17 23:20 | 3 | 50 | H4565831 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV C/O, LA & STANDOFF. NO TRK. CAN CUT LOOP AND INSTALL HOT TAP OR LF @ 43-245. RELEASED BY CREW 078S07 SAME AS 4566321BAD 12 KV C/O, LA & STANDOFF. NO TRK. CAN CUT LOOP AND INSTALL HOT TAP OR LF @ 43-245. RELEASED BY CREW 078S07,CUT LOOP @ 43-245 @ 2230 ALLCUST RESTORED @ 2320 PLEASE CLOSE TICKET THANKS.BT RELEASED BY CREW 078H02 VER/KEP
19332 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-01-09 06:27 | 2015-01-09 06:33 | 25 | 6 | 4922821 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT/CREW ON SITE/APPROX 30 MIN OUTAGE//FETR0700/VEM/OPENED FUSE 91-198 @0627/REPLACED CUTOUT AND POWER RESTORED TO ALL CUST 0633/PLEASE CLOSE TICKET/THANKS/VEM // RELATED TO ORDER 4922841 WHICH WAS MADE A DUP OF THIS ORDER // VER/HFP L3/HFP AJB
19333 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-06-20 22:40 | 2016-06-20 23:30 | 3 | 50 | H4393191-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT, MANUAL, NEED 1 MAN TO ASSIST.... OPENED LOOP ON 248-A-3 @ 22:40, ALL POWER RESTORED @ 23:30 DUPLICATE 37830248A00003 VER/AWD
19334 | Pikeville | 3408103 | SALISBURY | MARTIN | 2013-11-22 19:15 | 2013-11-22 20:05 | 3 | 50 | 4065981 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1099-55 HAS 3 50KVA TRANSFORMERS ON IT HAD TRANSFORMERS OPEN FROM 19:15 TO 20:05 DUE TO BAD CUTOUT REPLACED CUTOUT EVERYTHING OK//COD 3//ISO// VER/DBM
19335 | Whitesburg | 3312901 | JENKINS | KONA | 2012-10-18 14:42 | 2012-10-18 17:12 | 1 | 150 | H4153751 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING.HOT LEG MELTED ON POLE 404-7, WILL HAVE TO OPEN THIS TRANS. TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES.OPENED AT 17.:00, CLOSED BACK AT 17:12. JOB COMPLETE. VER/KEP IDC XXXX
19336 | Hazard | 3309302 | VICCO | JEFF | 2015-01-28 15:05 | 2015-01-28 17:35 | 1 | 150 | 4970751 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 SERV BURN INTO AT WEATHERHEAD === WILL REPLACE SERV === REPLACED SERV WITH 1/0 SERV === POWER OK == NEED TO SEND COPY TO PEGGY YSOME// EMAILED PEGGY/ADH/COD1// VER/ ADH L3/HFP XXX
19337 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-06-25 13:45 | 2020-06-25 14:35 | 3 | 50 | 4073021 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 138830430B00004 span 6A Prim Neut down at Pl# 38830430B00004 --Truck OK--Crew Reqd Released by crew 078H16 Opened xfmr on 430-4 at 13:45 closed at 14:35. Ticket complete. KMG
19338 | Cannonsburg | 3001401 | LOUISA | CITY | 2018-11-13 12:25 | 2018-11-13 12:55 | 5 | 30 | 4394771 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral had broke on servicedrop letting service drop and rub on dripedge of roof, repaires made. Opened txmf at 1225 closed at 1255 apr close ticket
19339 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2020-11-20 09:15 | 2020-11-20 11:45 | 1 | 150 | 4710491 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | Replaceing leaking 500 kva Xfmer.38830954A40952//OFF @ 0915 ON @ 1145
19340 | Hazard | 3308001 | JACKSON | S.JACKSON | 2012-04-16 10:45 | 2012-04-16 11:00 | 10 | 15 | 4675381 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TRANSFORMER OFF 10:45 ON 11:00--NETURAL INTO//COD 10// VER/DBM IDC XXXX
19341 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-10-24 12:30 | 2011-10-24 15:00 | 1 | 150 | 4015151 | 150 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN NEUTRAL IN SERVICE DROP. REPLACED SERVICE DROP. ///VER/CRB IDC XXXX
19342 | Hazard | 3302704 | HAZARD | KENMONT | 2017-12-31 13:00 | 2017-12-31 14:15 | 2 | 75 | 4690161 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
19343 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2012-11-01 10:14 | 2012-11-01 10:44 | 5 | 30 | H4233431 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WE HAVE MIDDLE PHASE OF THREE PHASE OUT AT STEPDOWNS 37830376C00018/// WE HAVE BAD INSULATOR ON POLE 37830376C00052 MIDDLE PHASE. WILL HAVE TO OPEN STEPDOWNS ON POLE 37830376C00018 TO CHANGE. MANUAL UPON HILL ABOVE TRLS. AT MOUTH OF BUZZARD ROCK RD. OPENED "A" AND "B" 1014 CLOSED ALL AT 1044 VER/KEP IDC XXXX
19344 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-09-16 22:45 | 2012-09-17 01:15 | 1 | 150 | 4052041 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE BURNED DOWN GOING TO HOUSE , ONLY ONE CUST. OUT. RED-RED WENT BAD. //VER/GAH IDC XXXX
19345 | South Williamson | 3202201 | LOVELY | LOVELY | 2019-10-12 14:05 | 2019-10-12 15:20 | 2 | 75 | 4134671 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout brokedown and pole on fire at 723-a-207//i opened tap on 723-19 to isolate and fire dept going to put out fire//going to band aid with cross arm and job can be written to replace pole//repairs made//opened line fuse at 14:05,closed at 15:20//please send to bill johnson to get job written//complete//em//NO OUTAGE TILL L/F OPENED ON POLE 38820723A00019//COD 2//SENT TO TECH
19346 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-01-15 16:25 | 2009-01-15 17:15 | 3 | 50 | 55284-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001002// BLOWN XFMR FUSE//MELTED XFMR FUSE//COD 3// VER/DBM L3/KEP
19347 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-04-03 17:50 | 2010-04-03 18:40 | 3 | 50 | 58271-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 67-30A INACTIVE 4/2 D/D WIRE BLEW INTO OPEN WIRE BLEW FUSE ON 67-30 8T ALSO BAD CUTOUT ON POLE CHGED IN. VER/KEP L3/KEP IDC XXXX
19348 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2016-03-06 13:30 | 2016-03-06 14:20 | 3 | 50 | 4821541 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING LINE FUSE TO MAKE REPAIRS TO A CUTOUT ON POLE 37830188B00091 / OPENED POLE 37830188B00091 @ 1330/ CLOSED @1420/ VER/BOW
19349 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-11-17 09:47 | 2013-11-17 11:02 | 2 | 75 | 4045421 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGE CUTOUT COD-2 ISO TF 37830053000080 VER/HFP L3/HFP
19350 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2014-04-25 15:07 | 2014-04-25 15:32 | 6 | 25 | 4634491 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUTOUT @ POLE 254C-314 ALL CUST RESTORED @ 1532 PLEASE CLOSE TICKET THANKS BT//COD 6// VER/DBM
19351 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-07-30 21:10 | 2008-07-30 22:25 | 2 | 75 | 62453-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, CHECKING TROUBLE, CUTOUT DOOR BURNT UP, REPLACED IT, POLE#1036-C-41//3404302/VER/CRB IDC XXXX
19352 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-08-28 10:30 | 2020-08-28 13:00 | 1 | 150 | 4392411 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replaced xfmr
19353 | Hazard | 3303902 | LESLIE | WOOTON | 2009-05-02 21:55 | 2009-05-02 23:10 | 2 | 75 | 63600-1 | 150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE MELTED OUT VER/ARN IDC XXXX
19354 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-12-22 06:16 | 2016-12-22 08:45 | 1 | 149 | 4228231 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT APR AT 0845 CLOSE TICKET VER/EKP
19355 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-06-06 13:36 | 2008-06-06 16:05 | 1 | 149 | 59148-1 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR FUSE BLOWN ON POLE #198-186... BAB ARRESTER.. RESTORED POWER AT 1605 VER/HFP
19356 | Hazard | 3310502 | HADDIX | CANOE | 2017-10-17 06:58 | 2017-10-17 09:27 | 1 | 149 | 4464171 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NO ANSWER @ CALLBACK # & ACCT NUMBER IS NOT IN SERVICE STS HAD BAD CONNECTION ON POLE VER/HFP L3/HFP
19357 | Hazard | 3303902 | LESLIE | WOOTON | 2022-07-22 14:53 | 2022-07-22 17:22 | 1 | 149 | 4549651 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT @ 1722
19358 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2013-01-30 11:26 | 2013-01-30 13:55 | 1 | 149 | 4757731 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP HAD BAD PLACE ON ONE LEG AT TRANSFORMER. ONLY ONE CUSTOMER HAD PART POWER. VER/HFP L3/HFP IDC XXXX
19359 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-04-18 16:56 | 2010-04-18 19:25 | 1 | 149 | 64828-1 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NUETRAL SPICE MID SPAN OF 2/3 SERVICE IS PULLED OUT, GILLEY IS BRINGING ME A LONG LADDER TO FIX IT BACK AT THE WEATHER HEAD. P.HCKS......ALL POWER RESTORED @19:25HRS. P.HICKS//COD 1// VER/DBM IDCC FEC44 XXXX
19360 | Hazard | 3302704 | HAZARD | KENMONT | 2013-10-28 09:43 | 2013-10-28 12:12 | 1 | 149 | 4968991 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE CUTOUT BROKEN IN TRANSFORMER BANK. VER/CRB L/3 CRB
19361 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-09-19 17:31 | 2021-09-19 20:00 | 1 | 149 | 4256541 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke-crew req-ds091921---cked w/ (((((((at 20:00)))))))cust and can work first thing in the morning-- ops order 80525186 //cod 1
19362 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-12-25 11:21 | 2013-12-25 13:50 | 1 | 149 | 4200641 | 149 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD., POWER RESTORED BUT 2/0 3 PHASE SERVICE NEEDS TO BE REPLACED. VER/KEP L3/HFP
19363 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2022-05-20 19:21 | 2022-05-20 21:50 | 1 | 149 | 4919161 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burned down//only one customer out//repairs made//restored at 21:50//complete//em
19364 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2019-03-24 16:40 | 2019-03-24 19:09 | 1 | 149 | 4020201 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole 173-31 has rotted and has laid over the road/// will need 40/4 pole ,8arm .pole top pin ,2 drop in pins, 3- 7200 insulators,and braces. Need line crew and flaggers. Can open 3 switches on pole173-26 when crew gets here to isolate and will only have 1 customer off/// CREW AND FLAGGERS CALLED/OPENDED SWITCHES ON 37820173000026 TO ISO TROUBLE OFF @ 1640 ON @ 1909
19365 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-06-26 17:01 | 2016-06-26 19:30 | 1 | 149 | 4479791 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GATE BURNT OUT VER/CRB
19366 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-10-14 12:56 | 2014-10-14 15:25 | 1 | 149 | 4621161 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN 19.9 CUTOUT, NEED CUTOUT , ARRESTER AND TEE BRACKET AND BIG BUCKET.//COD 1// VER/DBM
19367 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-12-04 11:58 | 2018-12-04 14:27 | 1 | 149 | 4506851 | 149 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broken service neutral and hot leg/servicer to replace drop/vem/repairs made power restored to all cust 1427 /restored 1427/vem L3/HFP
19368 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-04-27 10:26 | 2016-04-27 12:55 | 1 | 149 | 4132001 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE - PHASE A IN BANK. OTHER CUTOUTS ARE CRACKED. REPLACING ALL 3. RESTORED @ 12:55. SH VER/AWD
19369 | South Williamson | 3200302 | BELFRY | TOLER | 2010-12-12 13:22 | 2010-12-12 15:51 | 1 | 149 | 65602-1 | 149 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV SHORTED OUT MIDSPAN,MADE REPAIRS,ALL OK AFTERWARDS.ALSO HAD XFR OPEN FRM ABT 15:21 TO 15:51 COD-3 ISO TF 38821063A00095 DUPLICATE IN HOIS SEE RECORD H65602-1 VER/HFP L3/HFP IDC XXXX
19370 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-09-21 15:31 | 2022-09-21 18:00 | 1 | 149 | 4905791 | 149 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | Replaced lug inside meterbase, also had to replace meter, due to back melted. apr at 1800 close ticket.
19371 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-07-26 14:31 | 2011-07-26 17:00 | 1 | 149 | 4625421 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT GOING TO TRY FUSE, BAD TRANSFORMER NEED 15 KVA 19.9 TRANSFORMER AND BUCKET THE REAL POLE # IS 29-273 RELEASED BY CREW 077S05 VER/KEP IDC XXXX
19372 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2020-07-17 13:01 | 2020-07-17 15:30 | 1 | 149 | 4174961 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken c/o, lifted htsp on pole 1072-161, grd and tg to myself chged c/o and remove lotsa of vines off transformer, power is restored at this loc at 1530
19373 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-07-28 12:42 | 2013-07-28 15:11 | 1 | 149 | 4600621 | 149 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, FOUND BAD CONNECTION ON XFMER POLE//COD 1// VER/DBM IDC XXXX
19374 | Pikeville | 3408401 | KIMPER | LONGFORK | 2008-12-22 07:22 | 2008-12-22 09:51 | 1 | 149 | 62289-1 | 149 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3408401//WILL CHECK FOR PROBLEMSSERV-INS WERE BAD,REPLACED WITH SQUEEZ-ONS,ALL OK AFTERWARDS//VER/CRB L3/KEP IDC XXXX
19375 | Whitesburg | 3409503 | BURDINE | JENKINS | 2008-02-20 10:16 | 2008-02-20 12:45 | 1 | 149 | 65642-1 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409503// #4 SERVICE DROP HAS BURNED DOWN I WILL REPLACE SERVICE AND I WILL NEED FLAGGERS REPLACED SERVICE DROP VER/HFP IDC XXXX
19376 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-08-10 18:31 | 2012-08-10 21:00 | 1 | 149 | 4926221 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SERVE INN VER/KEP IDC XXXX
19377 | Hazard | 3309302 | VICCO | JEFF | 2017-12-23 11:31 | 2017-12-23 14:00 | 1 | 149 | 4667561 | 149 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | neutral burned into in 2/3 service at pole 323-418 need to replace service app 40 truck accessible Released by crew 077E02, made repairs restored power at 14:00, only one customer affected..
19378 | Hazard | 3309301 | VICCO | REDFOX | 2019-07-31 14:01 | 2019-07-31 16:30 | 1 | 149 | 4817871 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr on pole 324-207, not showing xfmr on maps, 25 kva, 7.2 kv, already has new cutout. power restored
19379 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-03-11 20:01 | 2016-03-11 22:30 | 1 | 149 | 4837941 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONN ON SERV BURNT INTO REPAIRS MADE CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/KEP
19380 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-02-10 11:29 | 2022-02-10 13:58 | 1 | 149 | 4464761 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required /service repaired
19381 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-09-05 16:21 | 2014-09-05 18:50 | 1 | 149 | 4469461 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | (OLD CSP XFORM NEEDS TO BE CHANGED OUT 25 KVA NO TRUCK// CUST ALREADY HAS BEEN OUT OF POWER TWICE TODAY// CREW REQUIRED// ISO 38830044B00441// COD 1/ REPAIRS COMP. POWER REST @ 18:50///JEH// VER/BOW
19382 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-12-17 05:10 | 2013-12-17 07:39 | 1 | 149 | 4167081 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | V.MULLINS, L,MCCOY, C.SIMMONS, R.MORGAN TO ASSIST //POLE 92-398 BAD 75. KVA TRANS. OPENED TRANS BANK 5:10 AM TRUCK TO POLE RELEASED BY CREW 078S08/FOREMAN ON SITE/CREW SPLITTING CAN/FETR0745/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0739/PLEASE CLOSE TICKET/THANKS/VEM//COD 1 VER/HFP L3/HFP
19383 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2021-10-26 08:13 | 2021-10-26 10:42 | 1 | 149 | 4016211 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required bad line fuse door/15t
19384 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-05-03 09:31 | 2009-05-03 12:00 | 1 | 149 | 63902-1 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT BROKEN... REPLACED CUTOUT, ALL WORK COMPLETE / GXJ COD-1 ENTERED MD TO HAVE MAP CORRECTED...HFP L3/HFP IDC XXXX
19385 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-09-13 07:31 | 2013-09-13 10:00 | 1 | 149 | 4849481 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1147-734 BAD CUTOUT NEED TO COME TO 1423 CLEARWATER ST. BAD DOGS RELEASED BY CREW 078S08 VER/SEF
19386 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-02-13 15:56 | 2011-02-13 18:25 | 1 | 149 | 56587-1 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT, ALL WORK COMPLETE / GXJ VER/KEP IDC XXXX
19387 | South Williamson | 3200302 | BELFRY | TOLER | 2014-12-17 19:21 | 2014-12-17 21:50 | 1 | 149 | 4867641 | 149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND OFF OF POLE 38821015A00204. UNDERGROUND CABLE RUNS UNDER A BLACKTOP STREET AND A SIX FOOT CONCRETE SLAB, CUSTOMER IS NOT SURE IF CABLE IS IN CONDUIT ALL THE WAY. I INSTALLED A TEMPORARY OVERHEAD SERVICE DROP FOR NOW. TIM HALL IS GOING TO CHECK IN THE MORNING ABOUT EITHER HAVING A CONTRACTOR INSTALL A NEW METERBASE WITH A WEATHERHEAD OR SETTING A SECONDARY POLE NEXT TO THE CUSTOMERS FENCE FOR UNDERGROUND SERVICE. VER/CRB
19388 | Hazard | 3311101 | STINNETT | REDBIRD | 2013-11-24 10:32 | 2013-11-24 13:00 | 1 | 148 | 4069771 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV END BURN OUT === REPAIRED ==== POWER OK VER/CRB
19389 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-01-25 13:46 | 2013-01-25 15:00 | 2 | 74 | 4740501 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER ,SECONDARY LEAD BURNT INTO, ONLY 2 CUSTOMERS AFFECTED MADE REPAIRS RESTORED POWER AT 1500 PER SERVICER ONLY 2 CUSTOMERS AFFECTED /// CCC COD-2 ISO TF 37830381D30170 VER/HFP L3/HFP IDC XXXX
19390 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2018-09-12 13:55 | 2018-09-12 15:09 | 2 | 74 | 4088161 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Crew required, no truck. One conductor of 6A open wire has pulled out of a sleeve is down. I opened the transformer at 13:55. Two customers are off. Released by crew 079S02// Made repairs and restored power at 15:09 Tim McCoy
19391 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-10-06 07:26 | 2013-10-06 08:40 | 2 | 74 | 4913951 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR & FUSE VER/SEF IDC XXXX
19392 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2022-11-19 09:30 | 2022-11-19 11:58 | 1 | 148 | 4161591 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | cust has a hot lead burn into at a squeeze on transformer pole 963D-70.i made repairs.secondary span from pole 963D-70 to 963D-227 needs some ROW work..span has pressure on it from tree limbs..really needs cleared up before the snow starts falling..please send copy to ROW
19393 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2018-08-27 15:35 | 2018-08-27 18:03 | 1 | 148 | 4005151 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SENT TO TECHS//secondary pole 254-127 broke ,,nothing feeding off pole,, cleaned pole and all open wire up and re squeezed xfr connections ,,complete
19394 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-05-14 18:51 | 2012-05-14 20:05 | 2 | 74 | 4793971 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT /// GOING TO REFUSE /// FUSE BROKE, RESTORED @ 20:05///VER/CRB L/3 CRB IDC XXXX
19395 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2013-03-19 14:50 | 2013-03-19 17:18 | 1 | 148 | 4920651 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED HOT TAP LEAD REFUSED TRANSFORMER (ZERO CUSTOMERS PER POWERON - GOING WITH ONE) COD-1 ISO TF 38830045C35173 VER/HFP L3/HFP IDC XXXX
19396 | Whitesburg | 3312902 | JENKINS | JENKINS | 2021-02-03 14:02 | 2021-02-03 16:30 | 1 | 148 | 4934471 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | gold - gold squeeze on frooze apart we replaced it
19397 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-08-22 20:56 | 2013-08-22 22:10 | 2 | 74 | 4697821 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT. COD-2 ISO TF 38820989D00032 VER/HFP L3/HFP
19398 | South Williamson | 3411401 | DEWEY | INEZ | 2022-12-30 07:42 | 2022-12-30 10:10 | 1 | 148 | 4377301 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 745D4-333.ill be making repairs .i got cutout replaced and fuse on pole745D4-333 back in at 10:10
19399 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-08-07 20:51 | 2013-08-07 22:05 | 2 | 74 | 4633911 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED TRANSFORMER CUTOUT. I REPLACED IT.//COD 2// VER/DBM
19400 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-07-12 09:42 | 2011-07-12 12:10 | 1 | 148 | 4528411 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED CONNECTION.//VER/CRB
19401 | South Williamson | 3200302 | BELFRY | TOLER | 2009-07-01 14:24 | 2009-07-01 16:52 | 1 | 148 | 58680-1 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP UNABLE TO CONTACT CUSTOMER ( PHONE BUSY) WILL SEND BOB WHEN HE IS AVAILABLE. CONTACTED CUSTOMER AT 1505 , REVIEWED PROBLEM ADIVSED CUST IT WOULD BE AFTER 1700 BEFORE SERVICER COULD BE THERE. PHONE CALL WAS DIS, ON C. AT THIS POINT. @ 1514 GAVE BOB THIS INFORMATION AND SENT HIM THE ORDER., ON SITE, CHECKING TROUBLE L3/HFP IDCC CNT4 XXXX
19402 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-01-27 10:02 | 2012-01-27 12:30 | 1 | 148 | 4298471 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON U.G. SERVICE. THE RIGHT LEG AT METER BASE BAD. VER/KEP IDCC CNT2, MCCDL XXXX
19403 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-09-06 11:56 | 2008-09-06 14:24 | 1 | 148 | 59909-1 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3003701//WR#26138858// BROKEN 6T FUSE//VER/CRB IDC XXXX
19404 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-06-11 20:58 | 2010-06-11 21:35 | 4 | 37 | 60456-1 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35538120 // POLE 92-206 CUTOUT FELL APART COD-4 VER/HFP L3/HFP
19405 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-08-28 12:35 | 2014-08-28 15:03 | 1 | 148 | 4433201 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 1 OF 3 XFR BANK FUSES OUT,WILL RE-FUSE///////REPLACED 1 BAD CUTOUT,RE-FUSED AND RESTORED,ALL OK AFTERWARDS COD-1 ISO TF 38821083B12031 VER/HFP L3/HFP
19406 | South Williamson | 3200301 | BELFRY | BELFRY | 2021-02-23 11:16 | 2021-02-23 12:30 | 2 | 74 | 4229491 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED OPEN BELOW OUR TROUBLE LOCATION IN HEAD OF THE HOLLOW.WILL MAKE NECESSARY REPAIRS.OPENED RECLRS@12:05,CLOSED@12:30
19407 | South Williamson | 3411401 | DEWEY | INEZ | 2011-06-21 13:12 | 2011-06-21 15:40 | 1 | 148 | 4363171 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. REPLACED AND RESTORED @ 15:40. SH//VER/CRB IDC XXXX
19408 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-07-26 10:50 | 2014-07-26 13:18 | 1 | 148 | 4289881 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON XMF, CLOSE TICKET VER/HFP L3/HFP
19409 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-07-21 14:07 | 2020-07-21 16:35 | 1 | 148 | 4195351 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout Gilley getting help send to T.Smith Released by crew 077S03 power restored at 16:35
19410 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-11-08 12:32 | 2012-11-08 15:00 | 1 | 148 | 4374351 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE BURNT INTO REPAIRED SEND ORDER TO VERNON WILL FIX SEC FRIDAY VER/HFP L3/HFP
19411 | Hazard | 3308002 | JACKSON | PANBOWL | 2022-06-09 16:17 | 2022-06-09 18:45 | 1 | 148 | 4050431 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad underground service on 38831059D00113. Will wait till 6-10-22 to make repairs per duty. Customer is aware. Please forward to Glen Combs and Rob Pigman////emailed Glen Combs and Rob Pigman foir follow up
19412 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-05-10 08:15 | 2017-05-10 10:43 | 1 | 148 | 4775121 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG UG SERVICE, POWER TEMP INSTALLED. AED MADE VER/CRB
19413 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-06-06 15:32 | 2018-06-06 16:46 | 2 | 74 | 4562801 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I remade splice between xfmr lead and service conductor
19414 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-01-07 11:47 | 2020-01-07 14:15 | 1 | 148 | 4220451 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced tran c/o-allgood-in at 14:15--ds010720 L3/HFP
19415 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-06-15 18:02 | 2015-06-15 20:30 | 1 | 148 | 4575871 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN ON XFMER POLE WENT BAD AND BLEW XFMER FUSE ON POLE 875-76///MADE REPAIRS AND REFUSED XFMER AT 20:30////COMPLETE BR/ ISO 38830875D00076/ COD 1/ VER/BOW
19416 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-08-22 09:02 | 2021-08-22 11:30 | 1 | 148 | 4134621 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad 4/0 underground hot leg feeding diamond links clubhouse Released by crew 078S12,install power temp all cust restored @1130 please close ticket thanks.bt
19417 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-06-04 23:56 | 2008-06-05 01:10 | 2 | 74 | 57729-1 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3401801//...FUSE BROKEN REPLACED WITH 20T MD FILED COD-2 VER/KEP
19418 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-03-10 12:30 | 2021-03-10 14:58 | 1 | 148 | 4322561 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1230 / Opened Fuses at 37830198C00042 (1 CC) to allow crews to splice conductor Closed at 1458
19419 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2012-02-17 11:07 | 2012-02-17 13:35 | 1 | 148 | 4355111 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUTS/ARRESTORS //COD 1// VER/DBM IDC XXXX
19420 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-03-08 10:02 | 2011-03-08 10:39 | 4 | 37 | 51627-1 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE #404-164 OPENED FUSE ON POLE 404-54 AT 1002; RETIED PRIMARY ON POLE 404-164; CLOSED 30T FUSE ON POLE 404-54 AT 1039 ALL POWER RESTORED CLOSE TICKET//VER/CRB IDCC TOF0914, TON1038 XXXX
19421 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2013-10-31 14:52 | 2013-10-31 17:20 | 1 | 148 | 4978821 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2 AA PRIMARY BROKE A COUPLE OF FEET FROM TAKEOFF POLE ON ONE POLE LATTERAL TO 728-78. CREW ENROUTE TO ASSIST. REPAIRS COMPLETE. RESTORED @ 17:20. SH ***CHANGE ISO POLE TO 728-12
19422 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-02-18 11:13 | 2008-02-18 13:41 | 1 | 148 | 64769-1 | 148 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3402001//HOT TAP BURN-INTO CENTER PHASE FUSE//COD 1// VER/DBM IDC XXXX
19423 | Hazard | 3309003 | JEFF | VIPER | 2016-10-30 14:47 | 2016-10-30 17:15 | 1 | 148 | 4063711 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY RISER BROKEN AT HOT LINE CLAMP AT POLE 37830417000125..POWER RESTORED @ 17:15 VER/CRB L3/HFP XXXHFP
19424 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-06-28 18:47 | 2021-06-28 21:15 | 1 | 148 | 4818241 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | raplaced broke cutout/ ISO 38830258000059/ COD 1
19425 | Pikeville | 3421001 | BREAKS | CITY | 2022-02-04 11:47 | 2022-02-04 13:30 | 4 | 103 | 4440721 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection almost burnt into @ xfm ////Opened xfm @ 13:15 replaced bad connection closed xfm back in @ 13:30 and restored service
19426 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-01-24 07:49 | 2012-01-24 10:17 | 1 | 148 | 4288391 | 148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT STS FUSE PULL INTO//COD 1//ISO 37830172B00144 // IDCC PN141, CNT3 XXXX
19427 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2017-03-07 08:33 | 2017-03-07 11:00 | 1 | 147 | 4528331 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT 37820056B00517 VER/AWD
19428 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-04-16 13:15 | 2014-04-16 15:42 | 1 | 147 | 4612321 | 147 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE END.RE SQUEEZED SERVICE DROP VER/HFP L3/HFP
19429 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-04-14 13:23 | 2008-04-14 15:50 | 1 | 147 | 51034-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP HAS CAME LOOSE AND FELL OFF STIRRUP//3308402//VER/CRB AJBC CDC88
19430 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-10-13 09:39 | 2016-10-13 12:06 | 1 | 147 | 4990051 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL SEE IF I CAN SAFELY REPLACE IT///////REPLACED AND RESTORED,ALL OK AFTERWARDS VER/CRB L3/HFP XXXHFP
19431 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-01-07 13:34 | 2011-01-07 16:01 | 1 | 147 | 59468-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 10TH ST WEST CENTRAL/--BROKEN SECONDARY POLE--J HEMLEPP TO GET TECH--CANNOT ACESS AT THIS TIME GATES ARE LOCKED--CALLED CITY TO GET GATES UNLOCKED RELEASED BY CREW 078S07/OPENED XFMR BANK 21-3768 AT 1334/BACK ON AT 1601/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
19432 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-10-31 15:27 | 2020-10-31 17:54 | 1 | 147 | 4610151 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on crossarm // truck access crew required//arrived RM power on @17:54 please close tic RM
19433 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2021-06-12 19:43 | 2021-06-12 21:30 | 2 | 107 | 4726721 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt down . repaired..xfmer off 20:50 0n 21:30
19434 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-05-20 12:48 | 2008-05-20 15:15 | 1 | 147 | 66420-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA XFMR. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. RELEASED BY CREW 076S02/ VER/TOM IDC XXXX
19435 | South Williamson | 3411401 | DEWEY | INEZ | 2020-12-31 08:58 | 2020-12-31 11:25 | 1 | 147 | 4838061 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced and restored @ 11:25. sh
19436 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-01-13 10:03 | 2015-01-13 12:30 | 1 | 147 | 4932731 | 147 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I REMADE SPLICE ON SERVICE DROP 37830182C00135 VER/CRB
19437 | Whitesburg | 3409503 | BURDINE | JENKINS | 2009-09-29 19:14 | 2009-09-29 20:03 | 3 | 49 | 56840-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED FUSE LINK
19438 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-06-16 20:01 | 2009-06-16 20:50 | 3 | 49 | 62621-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BAD.
19439 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-04-11 10:03 | 2020-04-11 12:30 | 1 | 147 | 4620781 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink failed and burnt service in two. Repaired and restored @ 12:30. sh
19440 | Whitesburg | 3314401 | MAYKING | ERMINE | 2010-10-18 10:53 | 2010-10-18 13:20 | 1 | 147 | 60600-1 | 147 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION PULLED OUT AT XFMR PART POWER.. MADE REPAIRS RESTORED POWER AT 13:20 VER/KEP L3/KEP IDC XXXX
19441 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-06-28 01:58 | 2010-06-28 04:25 | 1 | 147 | 58664-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER PER PHIL TOLLIVER // FEEDS TRAFFIC LIGHT //WR# 35753531 //REPLACED 50KVA VOLTAGE CHECKED GOOD ALL CUST. RESTORED P R TOLLIVER//THIS FEED TRAFFIC SIGNALS AND STREET LIGHTS/// VER/LDA IDC XXXX
19442 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-10-15 16:00 | 2009-10-15 18:27 | 1 | 147 | 66420-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE #176 / 24 , THIS WAS THE CAUSE THAT WAS OPERATING THE LINE. CUTOUT FINALLY BROKE APART AND CLEARED ITSELF , ONE CUSTOMER OUT OF POWER. REPLACED CUTOUT AND RESTORED POWER TO METER # 533751545 AT 1827 EVERYTHING CHECKS TO BE OK JKC IDCC PN78, TOF1524 ESTIMATED TIME OFF XXXX
19443 | South Williamson | 3411401 | DEWEY | INEZ | 2015-09-13 20:21 | 2015-09-13 21:10 | 3 | 49 | 4235111 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE///REPLACED CUTOUT//RESTORED AT 21:10//COMPLETE//EM VER/SEF
19444 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-02-01 18:52 | 2017-02-01 21:19 | 1 | 147 | 4353301 | 147 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE LEG ON SEC //CONNECTION FAILED//CUST HAS CLAIMS //SENT TO PEGGY WYSONG VER/CRB L3/HFP XXXHFP
19445 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-09-06 07:26 | 2009-09-06 08:15 | 3 | 49 | 50721-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008003// BAD CUTOUT //VER/GAH IDC XXXX
19446 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-04-29 16:33 | 2009-04-29 19:00 | 1 | 147 | 58914-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801//REPLACING CUTOUT DOOR/NO CREW REQUIRED COD-1 VER/KEP L3/KEP IDC XXXX
19447 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-06-14 21:38 | 2019-06-15 00:05 | 1 | 147 | 4508781 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Called customer: No reading on meter//cutout door burnt up in xfmr cutout//customer als showed me connection that had melted on service pole//going to rework connections then try xfmr fuse//repaired connections and refused//restored at 00:05//complete//em/ ISO 38830763000001/ COD 2
19448 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-02-27 08:28 | 2017-02-27 10:55 | 1 | 147 | 4425131 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONTACT AARON WILLIAMSON 606-465-9878 ONCE WE KNOW THE PROBLEM//--BAD CON AT POTHEAD--REPAIRED--ALLGOOD--DS022717 VER/CRB L3/HFP XXXHFP
19449 | Paintsville | 3409302 | KENWOOD | AUXIER | 2019-10-19 09:53 | 2019-10-19 12:20 | 1 | 147 | 4168521 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hot legs on service drop burnt into at xfmr//making repairs//repairs made//restored at 12:20//
19450 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-04-03 12:48 | 2015-04-03 13:09 | 7 | 21 | 4264461 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4262531// OPENING LINE FUSE 38821138C00127 TO SAFELY CHANGE CUTOUT 38821138C00132 L3/DKGXXX
19451 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-08-18 12:48 | 2017-08-18 15:15 | 1 | 147 | 4275761 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 423-254 , I ISOLATED THE TROUBLE BY LIFTING A TAP ON POLE 423-210. STILL ONLY ONE CUSTOMER OUT. GEORGE WHITAKER COMMING WITH BIG BUCKET TO MAKE REPAIRS. RELEASED BY CREW 077S12 POWER RESTORED AT 15:15 37830423C00254 VER/AWD
19452 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2008-10-16 22:48 | 2008-10-17 01:15 | 1 | 147 | 56382-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED CUT OUT AND REFUSED LINE VER/ARN IDC XXXX
19453 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-10-25 11:57 | 2008-10-25 14:24 | 1 | 147 | 58951-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP RELATED TO ORDER 58966-1 (CREW OPENED RECL TO ISOLATE TROUBLE IN THIS ORDER) BURNT OFF POLE 309-84/HOTTAP LIFTED 309-84B/CREW ON SITE/ONE CUST OUT/FETR 1500/VEM/REPAIRS MADE/PLEASE CLOSE TICKET THANKS/VEM IDC XXXX
19454 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2019-11-17 14:18 | 2019-11-17 16:45 | 1 | 147 | 4042431 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on weatherhead. Reworked connections and restored @ 16:45. sh
19455 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2012-04-26 15:48 | 2012-04-26 18:15 | 1 | 147 | 4714291 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED, BAD 25KVA 7200 XFMR. L MCCARTY ON SITE, XFMR CHANGED, ALL POWER RESTORED///VER/CRB L/3 CRB IDC XXXX
19456 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-01-25 11:15 | 2010-01-25 13:42 | 1 | 147 | 59423-1 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED BROKEN NEUTRAL AND RESTORED POWER. TIM MCCOY//VER/CRB IDC XXXX
19457 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2011-08-24 18:25 | 2011-08-24 19:14 | 3 | 49 | 4753071 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 3// VER/DBM IDC XXXX
19458 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-06-17 15:53 | 2012-06-17 18:20 | 1 | 147 | 4923341 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSF CUTOUT == REPLACED CUTOUT AND T BRACKET == POWER OK //COD 1// VER/DBM IDC XXXX
19459 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-10-21 06:13 | 2016-10-21 08:40 | 1 | 147 | 4035901 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL WORK AT START TIME 10/21/16//// RISER IN THE BOTTOM OF CUTOUT HAD PULLED LOOSE, APR AT 0840 CLOSE TICKET. D WEST COD-1 ISO PO @ 38830550000112 VER/HFP L3/HFP
19460 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-06-24 13:30 | 2016-06-24 13:51 | 7 | 21 | 4458391 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN XFR TO REPAIR SERVICE CONNECTIONS.OFF 1:30,ON 1:51/////SERVE-IN CONNECTIONS HEATING UP CAUSING 1 LEG TO OPEN UP OCCASSIONALY VER/CRB
19461 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-02-10 17:11 | 2014-02-10 18:00 | 3 | 49 | 4371681 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SERVE END ON TRANSFORMER POLE RESQUEEZE EVERTHING IS FINE AT THIS LOC NOW
19462 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-01-27 08:03 | 2012-01-27 10:30 | 1 | 147 | 4297841 | 147 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | INSULINK CONNECTOR FAILED ON 1 HOT LEG OF SERVICE ON XFMR POLE..1 CUST ONLY.REPLACED INSULINKS WITH PROPER SQUEEZE-ON CONNECTORS...JRV..01/27/12// VER/DBM IDC XXXX
19463 | Hazard | 3310502 | HADDIX | CANOE | 2022-02-16 17:53 | 2022-02-16 20:20 | 1 | 147 | 4489291 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | riser came out of xfmr
19464 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2021-08-24 09:42 | 2021-08-24 12:02 | 2 | 140 | 4143131 | 147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad squeeze-on at pole 1148-232. opened tranformer on 1148-232 @ 11:55 back on @ 12:02.complete
19465 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-01-21 13:54 | 2012-01-21 16:20 | 1 | 146 | 4280841 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA TRANSFORMER--- POWER RESTORED.1620 ///VER/CRB IDC XXXX
19466 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-06-12 21:17 | 2011-06-12 22:30 | 2 | 73 | 4307501 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE BURNT DOWN AT SPLICE. REPLACED WITH 2/3 SERVICE. OPENED TRANSFORMER AT 2200, CLOSED AT 2230=== POWER RESTORED. //VER/GAH IDC XXXX
19467 | Pikeville | 3421001 | BREAKS | CITY | 2011-02-14 08:09 | 2011-02-14 10:35 | 1 | 146 | 56657-1 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER//VER/CRB IDC XXXX
19468 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-06-26 13:44 | 2009-06-26 16:10 | 1 | 146 | 62904-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411901// TREES HAVE GROWN UP INTO TRANS. AND BLEW FUSE. I AM GOING TO REFUSE TRANS. TRANS. FUSE IS BLOWN ON POLE 96-392 AND LINE FUSE IS ALSO BLOWN ON POLE 96-140. WE HAVE A BAD 25 KVA {19.9} TRANS ON POLE 96-392. I AM CALLING FOR HELP NOW. I AM SHOWING THIS AS EQUIP. FAILURE BUT TREES ARE WHAT BURNED TRANS. UP. THEY KEEP GROWING UP INTO IT BLOWING FUSES. IT HAS BEEN TURNED IN MANY TIMES. WE CHANGED TRANS. WE CLOSED IT IN AT 16:10.
19469 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2020-10-07 13:28 | 2020-10-07 14:41 | 2 | 73 | 4534261 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | thousands & thousands of birds everywhere. they must all use this pole as a perch. also bad current limiting fuse. power restored @ 14:41. pls close. tre
19470 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2017-10-05 18:29 | 2017-10-05 20:55 | 1 | 146 | 4413731 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER, BAD CUTOUT GATE BURNT INTO , REPLACED GATE RESTORED POWER AT 20:55/// VER/DKM L3/HFP XXXHFP
19471 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-11-03 14:17 | 2015-11-03 15:30 | 2 | 73 | 4406631 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD 7200 CUTOUT. VER/CRB
19472 | South Williamson | 3411401 | DEWEY | INEZ | 2016-10-24 10:04 | 2016-10-24 12:30 | 1 | 146 | 4048061 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 19.9 XFMR//CREW ENROUTE//REPAIRS MADE//RESTORED AT 12:30//COMPLETE//EM VER/AWD
19473 | Paintsville | 3401101 | FALCON | FALC-OILS | 2020-08-04 15:47 | 2020-08-04 18:13 | 1 | 146 | 4286501 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 10 KVA transformer in difficult location. Talked with customer and she is ok with waiting until tomorrow morning for crews to start on this. Empty house. work order created for crew to work off of //Released by crew 076S02
19474 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-12-15 20:47 | 2009-12-15 22:00 | 2 | 73 | 63830-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE//COD 2// VER/DBM
19475 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2019-06-05 10:22 | 2019-06-05 12:48 | 1 | 146 | 4429941 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door is burned in two. will make repairs
19476 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2016-01-14 21:40 | 2016-01-14 22:53 | 2 | 73 | 4621081 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I REPLACED A FAILED TRANSFORMER CUTOUT/ ISO 37820147C00134/ COD 2/ VER/BOW
19477 | Hazard | 3310502 | HADDIX | CANOE | 2018-02-19 09:25 | 2018-02-19 11:51 | 1 | 146 | 4860001 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on transformer
19478 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-11-12 09:02 | 2008-11-12 10:15 | 2 | 73 | 64110-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3409303//HOT LINE CLAMP BURNT OFF. WILL REPLACE. REPAIRS COMPLETE. SH IDC XXXX
19479 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2012-05-14 10:34 | 2012-05-14 13:00 | 1 | 146 | 4791091 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | THE CONNECTION ON THE SERVICE NEUTRAL BURNED APART, CAUSING AN OPEN NEUTRAL CONDITION ON THIS SERVICE. I REPLACED THE FAILED CONNECTION. THE CUSTOMER IS COMPLAINING OF DAMAGED APPLIANCES. ONLY ONE CUSTOMER AFFECTED. VER/KEP IDC XXXX
19480 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-01-04 01:14 | 2012-01-04 03:40 | 1 | 146 | 4231321 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPLICE IN SERVICE HAS BURNT INTO ONLY ONE CUSTOMER AFFECTED.REPAIRED WIRE RESTORED POWER AT 03:40,WILL FOLLOW UP TOMORROW TO CHANGE 2/3 SERVICE OUT WITH 1/0 VER/ARN IDCC MCCNI XXXX
19481 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2011-03-03 16:24 | 2011-03-03 18:50 | 1 | 146 | 66252-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR....POLE 965-B-210 ....NEED CREW....CALLED JOEY REED....NEED 15KVA 7.2KV XFMR....ON HILLSIDE....NO TRUCK ACCESS....CREW ENROUTE....//.....REPLACED BAD XFMR....POWER ON NOW....JRV.....03/03/11//VER/CRB IDC XXXX
19482 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-05-23 14:52 | 2011-05-23 16:05 | 2 | 73 | 4145971 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD PULLED LOOSE. REFUSED TRANSFORMER ALL POWER RESTORED AT 1605 CLOSE TICKET // COD-2 ISO TF 38830501C31463 VER/HFP L3/HFP
19483 | Whitesburg | 3401301 | FLEMING | NEON | 2017-12-09 19:04 | 2017-12-09 21:30 | 1 | 146 | 4636581 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | two red-red serve-ins were burned up . I replaced them
19484 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2012-12-07 09:17 | 2012-12-07 10:30 | 2 | 73 | 4448911 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURN UP, REPLACED DOOR, ALL POWER RESTORED//COD 2// VER/DBM IDCC FEC49 XXXX
19485 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2013-07-29 21:12 | 2013-07-29 22:25 | 2 | 73 | 4605361 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BAD..CAN REPLACE SAFELY WITH TRUCK..//.REPLACED BROKEN CUTOUT..FUSE WAS NOT BLOWN..RE-ENERGIZED XFMR..JRV.07/29/13 VER/KEP IDC XXXX
19486 | South Williamson | 3202201 | LOVELY | LOVELY | 2013-11-26 11:09 | 2013-11-26 13:35 | 1 | 146 | 4075071 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CONNECTION ON ONE HOT LEG BROKE AT XFMR POLE//GOING TO REPAIR//REPAIRS MADE//RESTORED AT 13:35//COMPLETE//EM// VER/DBM
19487 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-03-27 15:26 | 2017-03-27 16:39 | 2 | 73 | 4589171 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 16:39 VER/CRB L3/HFP XXXHFP
19488 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-12-14 11:34 | 2009-12-14 14:00 | 1 | 146 | 56052-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O
19489 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2018-02-21 22:07 | 2018-02-21 23:20 | 2 | 73 | 4870541 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired connections
19490 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-11-27 00:03 | 2021-11-27 01:16 | 2 | 73 | 4127471 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1102-A3-143, checking. Trans. fuse melted into, refused @0116.
19491 | Pikeville | 3402002 | KEYSER | STONECOAL | 2013-11-25 19:35 | 2013-11-25 20:48 | 2 | 73 | 4073851 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN // WILL REFUSE// FUSE LINK BROKE// POWER IS RESTORED VER/SEF
19492 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-11-08 08:22 | 2016-11-08 09:35 | 2 | 73 | 4083631 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKE. RESTORED @ 9:35. SH/ ISO 38830786B20741/ COD 2/ VER/BOW
19493 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-12-22 12:57 | 2019-12-22 14:10 | 2 | 73 | 4176221 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broke cutout on 38830235000185. apr at 1410 close ticket dwest
19494 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-12-13 09:09 | 2015-12-13 10:22 | 2 | 73 | 4528581 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD CUTOUT ON 37820049000017 // POWER RESTORED @ 10:22 COD-2 ISO TF 37820049000017 VER/HFP L3/HFP
19495 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-09-29 13:29 | 2008-09-29 15:55 | 1 | 146 | 51890-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S02,,,,BROKE CUTOUT REPLACED WITH POLY CUTOUT HAD TO CLIMB//3007904//VER/CRB IDC XXXX
19496 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2018-06-26 19:19 | 2018-06-26 21:45 | 1 | 146 | 4674441 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | Had t replace guts out in meterbase and replace meter, all repaires made close ticket
19497 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2014-10-31 09:35 | 2014-10-31 10:48 | 2 | 73 | 4676421 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ISO POLE 37830443000057TRANSFORMER FUSE BROKE, DID NOT BLOW. ONLY 2 CUST. OUT. POWER RESTORED.// MADE MAP DISCREPANCY TO SHOW 2 CUSTOMERS ON TRANSFORMER 57//VER/ ADH
19498 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-05-07 11:15 | 2009-05-07 13:41 | 1 | 146 | 64560-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP REPLACING CUTOUT DOOR COD-1 ISO POLE 38830173000054 L3/HFP IDC XXXX
19499 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-01-09 12:04 | 2013-01-09 14:30 | 1 | 146 | 4581071 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HAD A BAD CUTOUT ON POLE 448-632, I ISOLATED IT AND REFUSED THE TAP AT 12:55 ON POLE 448-118. CREW IS GOING TO CHANGE OUT CUTOUT RELEASED BY CREW 077S12 // COD-1 ISO LF 37830448A00118 VER/HFP L3/HFP IDC XXXX
19500 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-04-10 23:31 | 2009-04-11 01:57 | 1 | 146 | 51288-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL 2331 OPENED TRANSFORMER 1147-985 COD-1SEND TO V MULLINS RELEASED BY CREW 078S07/BAD XFMR CUTOUT 1147-985//FETR 0230//04-11-09/VEMSEND TO V MULLINS RELEASED BY CREW 078S07/RESTORED 0157/NEVER HAD 41 OUT/PLEASE CLOSE TICKET/THANKS/VEM VER/LDA IDCC PN985 XXXX IDC XXXX
19501 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-06-20 16:14 | 2018-06-20 18:40 | 1 | 146 | 4629831 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 120/208 transformer bank on 833-579 is not on map. Serves meter 428783776. Three 50 kvas. Please make map correction. Phase B cutout is broke. Need big bucket to replace.//MADE MD TO SHOW TRANSFORMERS ON ABOVE POLE//120/208 transformer bank on 833-579 is not on map. Serves meter 428783776. Three 50 kvas. Please make map correction. Phase B cutout is broke. Need big bucket to replace. Replaced all three cutouts and restored @ 18:40. sh
19502 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-06-04 15:06 | 2018-06-04 17:32 | 1 | 146 | 4555221 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | leaking oil from busted fuse handle
19503 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-03-21 15:02 | 2019-03-21 16:15 | 2 | 73 | 4006771 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | no crew required replace arrestor
19504 | Hazard | 3302703 | HAZARD | HAZARD | 2018-10-29 22:52 | 2018-10-30 00:05 | 2 | 73 | 4341181 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke L3/HFP
19505 | Whitesburg | 3401301 | FLEMING | NEON | 2010-12-22 23:32 | 2010-12-23 00:45 | 2 | 73 | 55203-1 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED FROOZE OUT M.D.I. VER/ARN IDC XXXX
19506 | Hazard | 3303902 | LESLIE | WOOTON | 2012-10-18 16:44 | 2012-10-18 19:10 | 1 | 146 | 4154641 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 512-59 , BAB CUTOUT ON POLE 512-66//COD 1// VER/DBM IDCC CNT11 XXXX
19507 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-12-07 14:22 | 2011-12-07 15:35 | 2 | 73 | 4147641 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BREAKING DOWN ON 845-251// I OPENED LINE FUSE ON POLE 845-165//GOING TO PUT FIRE OUT AND CHANGE CUTOUT//REPAIRS MADE//RESTORED AT 15:35//COMPLETE//EM COD-2 ISO LF 38820845A00165 VER/HFP L3/HFP IDC XXXX
19508 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-03-06 11:37 | 2010-03-06 12:50 | 2 | 73 | 63354-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPAIRED SURGE PROTECTOR VER/KEP L3/KEP IDC XXXX
19509 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-08-16 18:53 | 2008-08-16 20:06 | 2 | 73 | 52622-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3201001//, ON SITE, CUTOUT BAD, REPLACING IT // VER/TOM IDC XXXX
19510 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2013-11-23 21:02 | 2013-11-23 22:15 | 2 | 73 | 4068071 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10T FUSE OUT LOOKS LIKE FUSE BROKE. FUSED UP EVERYTHING OK VER/TOM L3/TOM
19511 | Hazard | 3303902 | LESLIE | WOOTON | 2011-08-24 08:50 | 2011-08-24 11:16 | 1 | 146 | 4750151 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION VER/KEP IDC XXXX
19512 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-12-14 19:34 | 2012-12-14 22:00 | 1 | 146 | 4470641 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S01 REPLACEING BAD CUTOUT, APR AT 2200 CLOSE TICKET DWEST. ///VER/CRB L/3 CRB
19513 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-08-27 08:37 | 2008-08-27 09:50 | 2 | 73 | 55887-1 | 146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3402001//OPEN CUTOUT ON POLE 1127-622 TO TAKE LOAD OFF AT 09:15//COD 2// POLE AT FAULT 1127-621, OPEN HOT TAPS ON POLE 1127-531. ALSO REPLACE INSULATOR. POLE FIRE//ISO 38831127B00531// VER/DBM
19514 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-01-20 14:47 | 2016-01-20 16:00 | 2 | 73 | 4636951 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN @ XFMR REPAIRS MADE PLEASE CLOSE TICKET THANKS.BT// VER/ ADH
19515 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-06-27 17:59 | 2010-06-27 20:25 | 1 | 146 | 58365-1 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL WAS BROKEN IN THIS SERVICE DROP 10 FEET FROM THE POLE. I REPAIRED THE NEUTRAL. NO OTHER CUSTOMERS AFFECTED. VER/LDA
19516 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2017-06-07 10:19 | 2017-06-07 11:32 | 2 | 73 | 4919401 | 146 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SQUEEZE ON @ XFR COMPLETE 38830230000130 VER/AWD
19517 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-11-21 11:05 | 2015-11-21 13:30 | 1 | 145 | 4476041 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, CHGING/ ISO 38830834A10912/ COD 1/ VER/BOW
19518 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-07-26 18:35 | 2014-07-26 21:00 | 1 | 145 | 4290851 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHANGING..M#533774698 VER/ARN
19519 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-06-04 12:50 | 2008-06-04 15:15 | 1 | 145 | 56133-1 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SECONDARY POLE HAS FALLEN WILL NEED A CREW TO REMOVE POLE AND WIRE BEFORE REFUSING TRANSFORMER RELEASED BY CREW 074S07//COD 1 // POLE ROTTED OFF AT THE BOTTOM VER/JHM
19520 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-01-15 21:10 | 2013-01-15 23:35 | 1 | 145 | 4608501 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE CHANGED XFMR CUTOUT AND REFUSED IT // COD-1 ISO PO @ 37830378C00270 VER/HFP L3/HFP IDC XXXX
19521 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-03-07 16:10 | 2022-03-07 18:35 | 1 | 145 | 4583121 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broken// repaired power restored 18:35
19522 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-08-08 19:30 | 2022-08-08 21:55 | 1 | 145 | 4706691 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection in service burnt out. made repaires
19523 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-08-29 11:45 | 2008-08-29 14:10 | 1 | 145 | 57295-1 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3301402//FOUND BAD CONNECTION ON LASH IN MID SPAN.HAVE CREW GETTING MATERIAL TOGETHER.WILL HAVE TO OPEN UP POWER TO SCHOOL TO FIX.WORKING WITH PRINCIPAL TO COORDINATE. OPENED @ 1350 AND CLOSED @ 1410 VER/TOM IDCC TOF1310 HAD PART POWER TO BEGIN WITH, PN310 XXXX
19524 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2019-10-16 15:58 | 2019-10-16 18:23 | 1 | 145 | 4150111 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad con--replaced--allgood-ds101619
19525 | South Williamson | 3200301 | BELFRY | BELFRY | 2015-10-19 16:11 | 2015-10-19 18:36 | 1 | 145 | 4361701 | 145 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BURNT UP LINKET ON TRANS POLE NTA REMOVED SERVICE FROM 38821014C10352 TO TRK APPROACH SECONDARY POLE 38821014C10408 RESTORED POWER AT 18:36/ ISO 38821014C10352/ COD 1/ VER/BOW
19526 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-04-27 06:51 | 2012-04-27 07:20 | 5 | 29 | 4716171 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUTOUT DOOR COD-5 ISO TF 39831148A00241 VER/HFP L3/HFP IDC XXXX
19527 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-07-08 18:00 | 2008-07-08 20:25 | 1 | 145 | 64585-1 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3402802//BROKE SEC. POLE #738-277 30/6 DE-ENERGIZED TO MAKE SAFE AT 18:00//// POLE REPLACED AND SERVICE RESTORED AT 20:25//// TR0UBLE WORK ORDER. W.R.#24381447// VER/TOM IDC XXXX
19528 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2020-05-04 14:07 | 2020-05-04 16:32 | 1 | 145 | 4797661 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | loop burnt in two on pole 282-25. Needs a big bucket to reach it. Power restored at 16:32
19529 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-05-11 09:35 | 2011-05-11 12:00 | 1 | 145 | 4055201 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE HENDRICK BURNT INTO ALSO HOT TAP BROKE NEED TO OPEN ON 45-4150 TO N/O POINT POLE 45-4105 NEED CREW TRUCKS OK NEED A PIECE OF 556 PRI. WIRE RELEASED BY CREW 078S08 OFF AT 23:15 ON AT 12::00 MIDNIGHT ALL POWER RESTORED COMP. //VER/GAH
19530 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-06-12 17:45 | 2017-06-12 18:14 | 5 | 29 | 4953911 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT CUTOUT ON POLE MAKING NOISE, GOING TO CHANGE LINE FUSE AND TRANSFORMER FUSE NO POWER OFF UNTIL WE OPEN THEM// 1745-1814. 38831108B00114 VER/AWD
19531 | Pikeville | 3120102 | STANVILLE | TRAM | 2019-10-26 17:12 | 2019-10-26 19:37 | 1 | 145 | 4199831 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | x fmr fuse out will refuse. fuse link was broke. not blown.
19532 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-04-10 18:30 | 2009-04-10 20:55 | 1 | 145 | 51174-1 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLOWN ON XFMR POLE. WILL CUT IN CLEAR. CLEARED PROBLEM ARRESTER AND RE-FUSED LINE CUTOUT AT 20:55. SH COD-1 VER/KEP L3/KEP
19533 | South Williamson | 3411401 | DEWEY | INEZ | 2008-07-12 22:20 | 2008-07-13 00:45 | 1 | 145 | 51747-1 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JRV ON SITE @ 00:15 ON 07/13/08.....BROKEN CUTOUT...ON POLE 696-C-19....WHICH IS XFRMR POLE FOR THIS MTR #....OUR RECORDS LIST POLE 696-C-17, WHICH IS WRONG...CAN REPLACE CUTOUT......//....COUTOUT REPLACED....POWER RESTORED....JRV...07/13/08//VER/CRB IDC XXXX
19534 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-01-06 12:35 | 2008-01-06 15:00 | 1 | 145 | 54168-1 | 145 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411801//WILL CHECK INSTALLATION OUT FOR PROBLEMSSD NUETRAL BURNED INTO WHERE IT WAS TAPED TO HOT CONDS,TAPE APPARANTLY WAS TOO TIGHT AND A POOR CONNECTION HEATED HOT LEADS UP LEADING TO INSULATION FAILURE AT TAPE LOCATION.MADE NECESSARY REPAIRS,POSSIBLE DAMAGES HERE(MAYBE)// VER/TOM
19535 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-07-21 13:00 | 2011-07-21 15:25 | 1 | 145 | 4574081 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA NEED TO GO BACK WITH A 25 KVA 7200. TRUCKS TO POLE. RELEASED BY CREW 078S01/ XFMER LOADED CREW IN ROUTE/078H05/ XFMER REPLACED POWER REST. @ 15:25 J. HEMLEPP ( 1 CUST. AFFECTED)//VER/CRB
19536 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-01-04 08:00 | 2019-01-04 10:25 | 1 | 145 | 4627171 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | refused transformer. fuse pull into//MADE MD TO SHOW TRANS ON POLE 37830265000030 //COD 1//
19537 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2015-04-10 20:50 | 2015-04-10 23:15 | 1 | 145 | 4306761 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/KEP
19538 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2020-02-04 20:41 | 2020-02-04 23:06 | 1 | 145 | 4362681 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | trans aresstor failed on 1017-A2-425 blowing line fuse on 1017-A2-329.replaced arrestor,restored power at 23:06./ ISO 38821017A20329/ COD 1
19539 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-02-19 16:25 | 2014-02-19 18:50 | 1 | 145 | 4403271 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION AT THE WEATHERHEAD. VER/SEF
19540 | South Williamson | 3411401 | DEWEY | INEZ | 2008-07-28 12:30 | 2008-07-28 14:55 | 1 | 145 | 61093-1 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411401//SLEEVE PULLED OUT ON 4/3 SERV DROP IDC XXXX
19541 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-05-05 10:55 | 2015-05-05 13:20 | 1 | 145 | 4392001 | 145 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION// VER/ ADH
19542 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-04-02 20:45 | 2022-04-02 23:10 | 1 | 145 | 4716791 | 145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | customer states only one leg of power/no crew required bad connection/ 38830225000073
19543 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2014-07-14 12:48 | 2014-07-14 14:00 | 2 | 72 | 4240771 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ POLE 255-81,LINE FUSE IN @ 1400 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT COD 2// VER/ADH
19544 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-06-28 19:44 | 2011-06-28 22:08 | 1 | 144 | 4433101 | 144 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEND TO ENG. DEPT.- 110 #4 SERVICE DROP SHORTED OUT AT HOUSE KNOB AT HOUSE AND BURNED NEUTRAL INTO LETTING IT GET AGAINST METAL ROOF AND BURNED 3 HOLES IN ROOF. I SPLICED IT BACK,BUT DROP IS STILL LYING ON METAL ROOF. I PUT GUARD ON DROP. WE NEED TO CHANGE POLE 286-54 AND MAYBE 286-55 AND SET SET SEC. POLE BEHIND HOUSE. CUSTOMER HAS DAMAGES. I TOLD HIM TO CALL IN DAMAGE COMPLAINT. 2ND TIME THIS HAS HAPPENED. WE NEED TO DO AWAY WITH OPEN SECONDARY. TELL MIKE TO CALL ME VER/KEP IDC XXXX
19545 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-11-07 11:08 | 2010-11-07 12:20 | 2 | 72 | 53685-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BURNED UP WILL CHANGE IT. CHANGED CUTOUT/VER/CRB IDC XXXX
19546 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-07-03 16:42 | 2009-07-03 17:30 | 3 | 48 | 63901-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, HAVE REPLACED AND POWER IS RESTORED TO ALL CUST AT THIS LOC//COD 3// VER/DBM IDC XXXX
19547 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2013-01-23 20:59 | 2013-01-23 23:23 | 1 | 144 | 4735281 | 144 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER SERVICE DROP BURNT INTO ONE HOT LEG HOLDING WIRE UP. OPENED XFMR AT 23:11 MADE REPAIRS RESTORED POWER AT 23:23 VER/KEP IDC XXXX
19548 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-03-05 21:13 | 2013-03-05 22:25 | 2 | 72 | 4874491 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ///VER/CRB L/3 CRB IDC XXXX
19549 | Hazard | 3301101 | CHAVIES | CHAVIES | 2009-02-25 16:28 | 2009-02-25 17:40 | 2 | 72 | 51505-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3301101// BAD CUTOUT PUT OUT FIRE AND REPLACED CUTOUT WILL SEND JOB TO TECH. // VER/TOM L3/TOM IDCC TOF1628, PN11, CNT37, MCCDIS XXXX
19550 | Hazard | 3303902 | LESLIE | WOOTON | 2013-11-06 14:00 | 2013-11-06 16:24 | 1 | 144 | 4015611 | 144 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVEND BAD , 1/0 - #2 @ XFMR. VER/CRB
19551 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2016-02-03 11:55 | 2016-02-03 14:19 | 1 | 144 | 4672161 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT HAS BURNED THE CROSS ARM OFF. NO OUTAGE YET. LINE CREW IS EN-ROUTE TO MAKE REPAIRS. I WILL BE LIFTING HOT TAPS ON POLE 38820942B10996 WHEN LINE CREW GETS HERE//.BAD TRANSFORMER CUTOUT HAS BURNED THE CROSS ARM OFF. NO OUTAGE YET. LINE CREW IS EN-ROUTE TO MAKE REPAIRS. I WILL BE LIFTING HOT TAPS ON POLE 38820942B10996 WHEN LINE CREW GETS HERE. HOT TAPS LIFTED AT 13:23.BAD TRANSFORMER CUTOUT HAS BURNED THE CROSS ARM OFF. NO OUTAGE YET. CLOSED LOOPS @ 1419//IT FORCE CL
19552 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-09-10 11:48 | 2011-09-10 13:00 | 2 | 72 | 4854741 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN//FUSE APPEARED TO HAVE BROKEN//REFUSED//POWER IS RESTORED COD=2 ISO TF 37820075000208 VER/HFP L3/HFP IDC XXXX
19553 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-04-17 21:41 | 2008-04-18 00:05 | 1 | 144 | 51974-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOYD N CREW TO HELP/ REPLACED BAD CUTOUT IDC XXXX
19554 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-02-22 23:08 | 2017-02-23 00:20 | 2 | 72 | 4415321 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//NO ANSWER//FAILED CUTOUT RESTORED AT 0020 VER/KEP L3/HFP XXXHFP
19555 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-12-23 08:38 | 2022-12-23 11:02 | 1 | 144 | 4306541 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp burnt up replaced power restored at 11:02
19556 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-01-03 11:22 | 2020-01-03 12:10 | 3 | 48 | 4204111 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 kva 7200 CSP trans leaking.can wait until tomorrow to replace it.trk app.will need cutout and bracket as well.hold till the morning and then send over to Rick Ray. Released by crew 079H03/// OFF@11:22 // ON @ 12:10 COMPLETED
19557 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-09-16 10:51 | 2014-09-16 13:15 | 1 | 144 | 4503121 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 KV, 25KVA TRANSFORMER IN 120/208 BANK..POWER RESTORED. VER/CRB
19558 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-04-09 08:24 | 2012-04-09 09:00 | 4 | 36 | 4656181 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SPLICES. OPENED XFORMER AT 08:45 TO 09:00. ///VER/CRB IDC XXXX
19559 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-10-30 11:31 | 2011-10-30 11:55 | 6 | 24 | 4036991 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT / OPEN REC. @21-B4-8244 ///4 MIN OUTAGE TO SAFELY CLEAR CUTOUT. ///XFMER@ 44-5010 OFF @ 11:31 ON @ 11:55 REPAIRS COMPLETE J. HEMLEPP 078H05///VER/CRB IDC XXXX
19560 | Whitesburg | 3401301 | FLEMING | NEON | 2008-11-21 23:25 | 2008-11-21 23:37 | 12 | 12 | 50843-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3401301// SECONDARY CONNECTION BURNED OFF AT TRANSFORMER. I HAD TO OPEN TRANSFORMER AT 1125 AND CLOSE BACK AT 1137 TO MAKE REPAIRS// PLUS ONE CUSTOMER DUE TO MAPPING - ISSUED MAP DISC VER/TOM IDC XXXX
19561 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2021-09-06 10:08 | 2021-09-06 11:20 | 2 | 72 | 4213751 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A broken hot line clamp on the source side riser of a line fuse on pole 273-B-276 had the primary open in the clear. Repairs made and power restored at 11:20.
19562 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-08-24 20:50 | 2013-08-24 22:02 | 2 | 72 | 4704471 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BURNED UP CUTOUT DOOR. VER/ARN L3/HFP IDC XXXX
19563 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-12-18 19:42 | 2018-12-18 21:30 | 3 | 108 | 4578251 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | span of secondary down in road,,opened xfr 1023-35 @ 21:12 closed @ 21:30,,repairs made complete///performed map discrepancy L3/HFP
19564 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-10-30 13:18 | 2009-10-30 14:30 | 2 | 72 | 52896-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN. FUSE LINK BROKE. RE-FUSED. SH COD-2 ADDED MISMAPPED CUSTOMER VER/KEP L3/KEP IDC XXXX
19565 | Whitesburg | 3314401 | MAYKING | ERMINE | 2016-05-24 09:26 | 2016-05-24 11:50 | 1 | 144 | 4254181 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING TRANSFORMER 37830497000044/ ISO 37830497000044/ COD 1 REPLACED XFM POWER RESTORED AT 11:50/ VER/BOW
19566 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-01-29 10:09 | 2020-01-29 11:21 | 2 | 72 | 4346291 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on pole 216-11..will make repairs...restored
19567 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-06-17 18:56 | 2018-06-17 21:20 | 1 | 144 | 4612041 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9 CUTOUT//cod 1
19568 | South Williamson | 3200302 | BELFRY | TOLER | 2014-01-24 08:01 | 2014-01-24 10:25 | 1 | 144 | 4306781 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | MADE REPAIRS TO SERVICE. VER/HFP L3/HFP
19569 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-23 17:03 | 2008-07-23 18:15 | 2 | 72 | 59266-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T TRANS FUSE BROKE//3008701//VER/CRB IDC XXXX
19570 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-01-26 12:16 | 2021-01-26 14:40 | 1 | 144 | 4895011 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse is blown will refuse.bad cutout . no truck approach . have called for help.replaced cutout.power is restored.
19571 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2015-03-04 08:03 | 2015-03-04 09:15 | 2 | 72 | 4096581 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED 911 WITH AN ETA OF 0745// BAD CO38830045D16146 LIFT HT @8:03, CREW REQD. RELEASED BY CREW 078S07---CHANGED BAD CUTOUT---PWR BACK ON @ 09:15---TBL TKT COMP VER/CRB L3/DKGXXXX
19572 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-03-05 13:18 | 2018-03-05 14:30 | 2 | 72 | 4967411 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BAD --- COD 2 ISO TF 37830140D00331. 1.6t fuse out. repairs made everything ok closed fuse back in at
19573 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-09-08 13:13 | 2015-09-08 14:25 | 2 | 72 | 4213941 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER IS MIS-MAPPED. PLEASE ENTER TRANSFORMER POLE AS 38830784D00097 ON THIS ACCOUNT. CUTOUT DOOR BURNT UP ON XFMR 784-97.// VER/ ADH
19574 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-10-06 19:51 | 2012-10-06 22:15 | 1 | 144 | 4120201 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THE SECONDARY WAS OPEN AT THE TRANSFORMER. ONLY ONE CUSTOMER AFFECTED. VER/ARN IDC XXXX
19575 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-12-05 15:39 | 2021-12-05 18:03 | 1 | 144 | 4149851 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole 102C/261 power on
19576 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-06-22 18:21 | 2010-06-22 20:45 | 1 | 144 | 54912-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT == REPLACED CUTOUT AND CUT TREES FROM AROUND TRANSF POLE == POWER OK //VER/GAH IDC XXXX
19577 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-09-24 10:06 | 2010-09-24 12:30 | 1 | 144 | 53060-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANS NEEDS CUTOUT BAD 25KVA TRUCK ACCESIBLE//CREW ON SITE//REPLACED XFORMER INSTALLED NEW CUTOUT ALL POWER RESTORED @ 12:30 P R TOLLIVER VER/KEP L3/KEP IDC XXXX
19578 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2019-02-05 09:51 | 2019-02-05 10:27 | 4 | 36 | 4755211 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | opening xfmer to make repairs, hot leg burnt up. all repairs made, voltage good. opened can @ 09:51 back in @ 10:27
19579 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-03-28 11:08 | 2009-03-28 12:20 | 2 | 72 | 62390-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-2 BROKE XFMR CUTOUT ON AT 12:20 L3/HFP IDC XXXX
19580 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-11-01 17:43 | 2015-11-01 18:55 | 2 | 72 | 4401561 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CUTOUT RISER BURNED INTO . REPAIRED RISER . POWER BACK ON @ 18:55/ ISO 38831059D00146/ COD 2/ VER/BOW
19581 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2017-05-11 17:55 | 2017-05-11 20:19 | 1 | 144 | 4781001 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE LEANING CREW REQUIRED BOUT 6 TO 7 FT OUT AT TOP NEEDS RELOCATED TO OTHER SIDE OF DRIVEWAY RELEASED BY CREW 078S03//NO OUTAGE TILL CREW ARRIVES//CREW ON SITE/FETR 2100/VEM/LIFTED HOTTAP AT 1755/RELOCATED POLE AND XFMR POWER RESTORED 2019/PLEASE CLOSE TICKET/THANKS/VEM//ISO 38830227000022//COD 1// VER/DBM
19582 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-04-09 14:12 | 2022-04-09 16:36 | 1 | 144 | 4743601 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout. changing.
19583 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2021-07-14 20:58 | 2021-07-14 22:10 | 2 | 72 | 4913911 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Correct xfmr pole is 38830808000007. Transformer fuse link appears to have broke. Restored @ 22:10. sh
19584 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-04-27 08:19 | 2016-04-27 08:55 | 4 | 36 | 4130911 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR, HAVE REPLACED POWER IS RESTORED AT THIS LOC AT 0855 BY TONY GEORGE VER/AWD
19585 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-06-14 09:48 | 2017-06-14 11:00 | 2 | 72 | 4966331 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNDT UP ON POLE 1128-82, CHANGED OUT AND REFUSED @1100./ ISO 38831128000082/ COD 2 MD DONE/ VER/BOW
19586 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2012-10-11 15:39 | 2012-10-11 18:03 | 1 | 144 | 4132981 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | READ 124/248 AT XFMR AND AT METER BASE READ 124/20.. BAD HOT LEG UNDERGROUND.. NEED LINE CREW AND POWER TEMP.. DISCONNECTED BAD LEG AT XFMR AND IN MTR BASE RELEASED BY CREW 078H22/CRE ON SITE/ FETR1830/ VEM/ TEMP XFMR INSTALLED/FULL POWER AT1803/BAD 1/0 UG SERV/PLEASE COPY RAYBURN/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB L/3 CRB IDC XXXX
19587 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2015-12-22 19:37 | 2015-12-22 20:25 | 3 | 48 | 4551161 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP WILL REPLACE/// REPLACED BURNT UP DOOR AND RESTORED SERVICE @ 20:25/ ISO 37820172000061/ COD 3/ VER/BOW
19588 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-06 07:36 | 2008-03-06 10:00 | 1 | 144 | 54200-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3308401// BAD UNDERGROUND WIRE, GOING TO GO OVERHEAD, CALLING FOR HELP RELEASED BY CREW 077S02 IDC XXXX
19589 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-01-16 14:42 | 2020-01-16 15:30 | 3 | 48 | 4312991 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OUTAGE NECESSARY TO ALLOW CREW TO REPLACE ARRESTOR ¦¦ COD-3 ISO LF 38820818A00027 OFF@ ON@OUTAGE NECESSARY TO ALLOW CREW TO REPLACE ARRESTOR ¦¦ COD-3 ISO LF 38820818A00027 OFF@ ON@//opened at 14:55//restored at 15:30//complete//em
19590 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-07-08 21:58 | 2011-07-08 22:46 | 3 | 48 | 4493701 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 93-189 6T CHANCE FUSE BROKE//VER/CRB IDC XXXX
19591 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-11-16 13:56 | 2010-11-16 16:20 | 1 | 144 | 56280-1 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37783674 // COD-1 VER/HFP L3/HFP IDC XXXX
19592 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2020-01-20 09:28 | 2020-01-20 10:40 | 2 | 72 | 4322441 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke at pole 38830070B43612 L3/HFP
19593 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-01-29 08:33 | 2018-01-29 10:57 | 1 | 144 | 4780781 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout has failed will try to get big bucket & change all 3 while coustomer is out. coustomer is on generator power at this time.
19594 | Cannonsburg | 3001401 | LOUISA | CITY | 2016-03-09 10:35 | 2016-03-09 11:23 | 3 | 48 | 4829991 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OPENING XFMR TO SAFELY REPLACE CROSSARM/APROX ONE HOUR OUTAGE/VEM/OPEN FUSE AT 1035/VEM/ALL CUST RESTORED 1123/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830454A41559 COD 3/ VER/BOW
19595 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-12-01 20:59 | 2014-12-01 22:11 | 2 | 72 | 4823701 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN WILL REFUSE//// CUTOUT WAS BROKE/// CHANGED BAD CUTOUT AND REFUSED TRANSFORMER @22:11 AND RESTORED SERVICE COD-2 ISO TF 37830190C00317 VER/HFP L3/HFP
19596 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2009-12-11 07:32 | 2009-12-11 09:56 | 1 | 144 | 60383-1 | 144 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP FOUND SERVE END HAD COME LOSE, HAVE THIS RESQUEEZED AND EVERYTHING IS OK AT TH IS LOC L3/HFP
19597 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-12-03 08:31 | 2020-12-03 10:55 | 1 | 144 | 4741091 | 144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | bad current limiting fuse-crew req-ds120320 Released by crew 078S01
19598 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-10-15 13:16 | 2014-10-15 15:39 | 1 | 143 | 4633721 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 37830416000088 IS XFMR WE HAVE BLOWN//// REPLACED XFMR FUSE, POWER RESTORED// COD 1// VER/ ADH
19599 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-11-19 16:52 | 2008-11-19 19:15 | 1 | 143 | 50069-1 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411801//WILL CHECK FOR PROBLEMS IF ANYPOOR SPLICE IN SERV DROP HEATED UP BURNING 1 HOT LEG INTO.REPLACED SERVICE DROP.ALL OK AFTERWARDS// VER/TOM IDC XXXX
19600 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-04-05 14:40 | 2017-04-05 17:03 | 1 | 143 | 4617141 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O BURNED THROUGH XARM ON POLE 38831101D30363. OPENED LINE FUSE (ORDER 4617441) TO ISOLATE FOR MAKING REPAIRS.TRANS. OPENED 2 L/F ON POLE1101-D3-365 TO MAKE REPAIRS. OPENED THE 2 L/FS @1536, MADE REPAIRS AND CLOSED BACK IN @1703. RELEASED BY CREW VER/AWD L3/HFP XXXHFP
19601 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2020-11-07 16:16 | 2020-11-07 17:39 | 6 | 83 | 4651501 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | opened xfmer @ 17:27 & back in @ 17:39. hot leg burnt up at insulinks. repairs made. pls close. tre
19602 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-07-21 16:08 | 2013-07-21 18:31 | 1 | 143 | 4571181 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED 1-4/3 SERVICE WITH 2/3 REPAIRED 1-4/3 SERVICE VER/CRB L/3 CRB
19603 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-06-24 13:47 | 2010-06-24 16:10 | 1 | 143 | 56508-1 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUT OUT ON POLE 188-141.//COD 1// VER/DBM IDC XXXX
19604 | Hazard | 3310502 | HADDIX | CANOE | 2020-11-06 13:10 | 2020-11-06 15:33 | 1 | 143 | 4648571 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
19605 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-03-06 17:32 | 2012-03-06 19:55 | 1 | 143 | 4557881 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON SECONDARY POLE HAS ALMOST BURNED INTO. LOOSE CONNECTION ON #4 OPEN SEC. CONDUCTOR. I RESQUEEZED CONNECTIONS. CUSTOMER SAID SHE HAD DAMAGES, ROUTER AND COMPUTER. I TOLD HER TO CALL PEGGY TOMORROW. VER/HFP L3/HFP IDC XXXX
19606 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-01-22 14:57 | 2013-01-22 17:20 | 1 | 143 | 4729281 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHANGED OUT SERV AND TRANSFORMER LEADS // COD-1 PER FRANK // ISO TF 37830221000009 VER/HFP L3/HFP IDC XXXX
19607 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2018-12-25 17:22 | 2018-12-25 19:45 | 1 | 143 | 4598041 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad neutral and connections in service drop. replacing service drop/ ISO 38831121D10418/ COD 1/ due to part power bright and dim i opened transformer at 18:30 and closed transformer back in at 19:45 after i changed service drop out. serve end heated up and burnt neutral into on 4/3 service drop i changed to a 2/3 drop cust said everything was ok. due to open neutral send copy to peggy in damage claims cust could possible call in L3/HFP
19608 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-08-24 19:02 | 2017-08-24 21:25 | 1 | 143 | 4297331 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER NO ANSWER.BAD 12 KV C/O. BIG BKT SHOULD REACH. RESTORED @ 21:25/ ISO 38830115C00232/ COD 1/ VER/BOW
19609 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2018-04-16 10:37 | 2018-04-16 13:00 | 1 | 143 | 4238651 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | 4/0 sleeve pulled out of srv drp, no trucks to pole, have repairs made at this time at this loc at 1300 by amg L3/HFP
19610 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-12-07 17:52 | 2012-12-07 20:15 | 1 | 143 | 4450371 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. REPLACED CUTOUT AND CLOSED LINE FUSE @ 20:15. SH COD-1 ISO TF 38830760D00247 VER/HFP L3/HFP IDCC PN247 XXXX
19611 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-02-15 14:24 | 2009-02-15 16:47 | 1 | 143 | 62115-1 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE //VER/GAH
19612 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-02-02 15:57 | 2009-02-02 18:20 | 1 | 143 | 54810-1 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD SERVIN MADE 3 NEW CONNECTIONS L3/HFP
19613 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-12-09 11:22 | 2021-12-09 13:45 | 1 | 143 | 4165021 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPENING XFMR 38830224000038 ON OLIVE HILL GLOBE CIRCUITopened xfmr at 1315 to repair secondery connections closed xfmr at 1345
19614 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-04-22 15:41 | 2018-04-22 18:04 | 1 | 143 | 4262891 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | customer had neutral and one leg burnt into in service drop.replaced drop..restored.../ ISO 37830284000027/ COD 1
19615 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2017-03-20 08:57 | 2017-03-20 11:20 | 1 | 143 | 4571471 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE GOING TO 139 BURNDT INTO, HAD TO OPEN THE TRANS. ON 24-B4-230 TO MAKE REPAIRS, OPENED @1040, BUT BACK ON @1120. VER/HFP L3/HFP
19616 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2019-12-27 12:28 | 2019-12-27 14:51 | 1 | 143 | 4185441 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout failed on 965C239,replaced cutout,restored power at 14:51.
19617 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-10-16 20:52 | 2022-10-16 23:15 | 1 | 143 | 4033901 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 c/o replaced and repaired // COMPLETE @ 23:15
19618 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-08-25 19:43 | 2019-08-25 22:06 | 1 | 143 | 4944691 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Pole # 202/119 transformer fuse out transformer fuse broke//cod 1
19619 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-09-27 20:02 | 2014-09-27 22:25 | 1 | 143 | 4533291 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, NEED 1 MAN AND 7200 CUTOUT AND ARRESTER....POWER RESTORED. VER/KEP
19620 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2021-05-09 09:55 | 2021-05-09 12:18 | 1 | 143 | 4552821 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | At sometime cust. made home made splice on neutral repaired service voltage good send to tech. pole 490/39 this service is laying on phone cable cust.said we can set pole in yard to fix this
19621 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-12-06 07:37 | 2018-12-06 10:00 | 1 | 143 | 4511441 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | insta link/ serve end melted under load burning neutral in service drop and 1 hot phase into.. service drop is #2-3 triplex the correct size for this 200 amp account,,,cust may have damage. L3/HFP
19622 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-01-28 21:22 | 2014-01-28 23:45 | 1 | 143 | 4320681 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | JUST ARRIVED REPAIRED SEC,CONDUCTOR CHECK VOLATE GOOD PLEASE CLOSE TIC RM VER/KEP
19623 | Whitesburg | 3401301 | FLEMING | NEON | 2016-12-20 07:07 | 2016-12-20 09:30 | 1 | 143 | 4222451 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE IS BURNED UP, CREW IS GOING TO PUT UP PLEASE SEND TO JEFF BAKER RELEASED BY CREW 077S12 REPLACED 2/3 SERVICE DROP EVERYTHING CHECKS OK VER/HFP L3/HFP
19624 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-02-08 01:17 | 2020-02-08 03:40 | 1 | 143 | 4383141 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Hot leg burndt into on customers service, will have to open trans. to make repairs, will keep track of times. Opened trans. @0315 the only feeds the one customer that had part power originally, made repairs and closed it back in @0340./ 38831126B10463 cod 1
19625 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-05-20 15:12 | 2017-05-20 17:35 | 1 | 143 | 4828441 | 143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRANSFORMER ON 906-120. CREW ENROUTE TO REPLACE. REPLACED AND RESTORED @ 17:35. SH/ISO 38830906000120/ COD 2/ VER/BOW
19626 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-03-30 09:42 | 2018-03-30 12:05 | 1 | 143 | 4154721 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | secondary connection burned into on xfmr pole///i repaired connection///restored at 12:05//complete//em/ ISO 38820866B00022/ COD 1
19627 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-02-27 17:37 | 2017-02-27 20:00 | 1 | 143 | 4426811 | 143 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY NUETRAL PULLED LOOSE BETWEEN CUSTOMERS HOUSE AND POLE 194A153 I WILL HAVE TO CLIMB POLE AND MAKE REPAIRS REPLACED 6 FEET OF SECONDARY CONDUCTOR AT POLE 194A153 AND REPAIRED BROKEN NUETRAL CUSTOMERS EQUIPMENT CHECKED OK EXCEPT FOR BLOWN LIGHT BULBS AND I HELPED HER CHANGE THEM PLEASE SEND COPY TO PEGGY WYNSONG IN CASE CUSTOMER CALLS INRESTORED AT 20:00 37820194A00035/SENT TO PEGGY/AWD VER/AWD L3/HFP HFPC CDC89 FP37820194A00035
19628 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-05-22 21:38 | 2014-05-22 22:49 | 2 | 71 | 4743251 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN // WILL REFUSE///FUSE BROKE// POWER RESTORED @ 22:49 VER/SEF
19629 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-02-11 13:41 | 2013-02-11 16:03 | 1 | 142 | 4809871 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | #4 SLEEVE PULLED LOOSE ON NEUTRAL-MADE REPAIRS ///VER/CRB L/3 CRB IDC XXXX
19630 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2013-12-04 08:23 | 2013-12-04 09:34 | 2 | 71 | 4097491 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER CUTOUT FAILED GOING TO CHANGE .CUTOUT CHANGED BACK TO NORMAL//COD 2// VER/DBM L3/HFP
19631 | Pikeville | 3421001 | BREAKS | CITY | 2012-03-21 10:08 | 2012-03-21 12:30 | 1 | 142 | 4602141 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP HAS BURNED INTO AT CONNECTION ON TRANS. POLE. I AM GOING TO SPLICE DROP. 1 CUSTOMER AFFECTED. VER/KEP IDC XXXX
19632 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-04-09 07:18 | 2018-04-09 09:40 | 1 | 142 | 4202311 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection at xfmr pole heated up and burnt service in two. One customer affected. Reworked xfmr connections and restored affected customer @ 9:40. sh
19633 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-11-15 16:14 | 2011-11-15 17:25 | 2 | 71 | 4079821 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACE BAD TRANSFORMER 25 KVA 7200. POWER ON AT 17:25 RELEASED BY CREW 074S05//COD 2// VER/DBM IDC XXXX
19634 | Hazard | 3303902 | LESLIE | WOOTON | 2015-08-25 09:24 | 2015-08-25 10:35 | 2 | 71 | 4170341 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE OR KMATE/ ISO 37830486000025/ COD 2
19635 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-10-31 08:18 | 2011-10-31 10:40 | 1 | 142 | 4038391 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SERVICE DROP ,PART POWER ONLY ONE CUSTOMER AFFECTED, OPENED XFMR AT 10:12 (SEE H4038391) MADE REPAIRS RESTORED POWER AT 10:40//COD 1 // VER/DBM IDC XXXX
19636 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2015-10-02 09:38 | 2015-10-02 12:00 | 1 | 142 | 4301971 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SQUEEZON ON SECONDARY SIDE OF TRANSFORMER, HAVE REPAIRED AND CUST HAS GOOD VOLTAGE AT METER TOP AND BOTTOM// VER/ ADH L3/HFP XXXHFP
19637 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-09-13 13:17 | 2013-09-13 14:28 | 2 | 71 | 4851361 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER VER/SEF
19638 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2022-01-02 22:19 | 2022-01-02 23:30 | 2 | 71 | 4262811 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse melted out on transformer. Power restored at 23:30.
19639 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-06-14 14:58 | 2013-06-14 16:09 | 2 | 71 | 4335211 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK ON TRANSFORMER LOOKED TO HAVE PULLED INTO .//COD 2// VER/DBM IDC XXXX
19640 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-06-16 21:13 | 2013-06-16 23:35 | 1 | 142 | 4351091 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALL A LINEMAN AN BIGGER BUCKET VER/KEP IDC XXXX
19641 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2015-07-17 18:59 | 2015-07-17 20:10 | 2 | 71 | 4904081 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-426 BAD CUTOUT REPLACED/ ISO 38830092A00426/ COD 2
19642 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-12-15 12:28 | 2016-12-15 14:50 | 1 | 142 | 4196691 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830185A20916--CUTOUT WAS BROKEN- CHANGED CUTOUT AND POWER RESTORED AT 14:50--CUSTOMER WAS NOT HOME,CHECKED METER AND LIGHTS WERE ON INSIDE --PLEASE CLOSE TICKET THANKS T. CANTRELL VER/CRB L3/HFP XXXHFP
19643 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2021-04-29 09:42 | 2021-04-29 12:04 | 1 | 142 | 4493361 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 10 kva 7200 trans., will be changing. Changed 10 kva to 15 kva, restored power @1204.
19644 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-03-13 09:17 | 2010-03-13 11:39 | 1 | 142 | 66300-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER BURNT OFF C/O//// REPLACED C/O RISER POWER RESTORED//VER/CRB IDCC PN228 XXXX
19645 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2014-03-20 19:58 | 2014-03-20 22:20 | 1 | 142 | 4514401 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT COD-1 ISO LF 39831099B43635 VER/HFP L3/HFP
19646 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-11-05 14:58 | 2014-11-05 17:20 | 1 | 142 | 4702461 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED AND BURNT NEUTRAL IN TWO. DIFFICULT LOCATION. REPAIRED SERVICE AND RESTORED @ 17:20. SH VER/HFP L3/HFP
19647 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-01-17 19:42 | 2020-01-17 20:53 | 2 | 71 | 4317011 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout changing..
19648 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-07-06 15:08 | 2009-07-06 17:30 | 1 | 142 | 53846-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP REPLACED BAD CUTOUT AND CUT TREES OUT OF VPRIMARY. COD-1 ISO TF 38830473000126 L3/HFP IDC XXXX
19649 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2017-05-05 14:07 | 2017-05-05 15:18 | 2 | 71 | H4754081 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | PADMOUNT TRANS. FUSE OUT @38831152B20218, CHECKING. BAD 50 KVA 7200 PADMOUNT. TIM HALL GETTING A CREW TO HELP CHANGE. HAD TO OPEN THE URD @ JUNCTION BOX 1152-214, OPENED @1407 PUT BACK ON @1518, ALL POWER RESTORED. RELEASED BY CREW 074S05 VER/CRB
19650 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-01-07 15:09 | 2016-01-07 16:20 | 2 | 71 | 4593211 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 426-724, WILL REPLACE . REPLACED CUTOUT AND RESTORED POWER AT 1620./ ISO 37830426C20724/ COD 2/ VER/BOW
19651 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-04-12 19:38 | 2019-04-12 22:00 | 1 | 142 | 4087671 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | at pole 140-D-416 riser from top side of the cutout come out of the hot line clamp. made repairs replaced hot line clamp everything ok
19652 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-02-23 06:53 | 2020-02-23 09:15 | 1 | 142 | 4425311 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Secondary splice failed between trans pole 1036-C-133 and secpole 1036-C-280.Repaired splice restored power at 09:15. send copy to damage claims customer may have damages. L3/HFP
19653 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-03-21 10:38 | 2019-03-21 13:00 | 1 | 142 | 4005601 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | customer had connection pulled out of splice..repairs made.
19654 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-02-15 11:55 | 2010-02-15 14:17 | 1 | 142 | 57893-1 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION// VER/DBM IDCC MCCNI XXXX
19655 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-06-08 18:09 | 2009-06-08 19:20 | 2 | 71 | 57788-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#30191831// CUTOUT DOOR BURNT UP 6T TRANS FUSE//VER/CRB IDC XXXX
19656 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2022-09-15 11:35 | 2022-09-15 12:46 | 2 | 71 | 4885791 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Blown XFMR fuse on pole 152-25, power restored at 12:46 then I re-sagged this customers service drop.
19657 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2008-01-10 20:53 | 2008-01-10 23:15 | 1 | 142 | 55644-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED VER/KEP IDC XXXX
19658 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2015-03-28 20:59 | 2015-03-28 22:10 | 2 | 71 | 4239661 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLKACED BAD 7200 CUTOUT. VER/SEF
19659 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-08-31 18:35 | 2020-08-31 20:57 | 1 | 142 | 4409491 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT/////////////REPLACED XFR CUTOUT&RESTORED POWER,ALL OK AFTERWARDS//cod 1
19660 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-09-24 14:34 | 2011-09-24 15:45 | 2 | 71 | 4912281 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR NO CREW REQUIRED//COD 2// VER/DBM IDCC FEC49 XXXX
19661 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2008-01-25 09:08 | 2008-01-25 11:30 | 1 | 142 | 59736-1 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE IN TROUBLE I REPLACED #4 SERVICE WITH #2 SERVICE.//3403701//ONLY EFFECTED SERVICE DROP//VER/CRB IDC XXXX
19662 | Hazard | 3309301 | VICCO | REDFOX | 2008-05-29 14:32 | 2008-05-29 15:43 | 2 | 71 | 52630-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING XFMR//3309301 VER/HFP IDC XXXX
19663 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-10-29 15:13 | 2009-10-29 17:35 | 1 | 142 | 50981-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD XFMR. DUTY SUP NOTIFIED - CREW ENROUTE TO REPLACE. COMPLETE. RESTORED SERVICE AT 17:35. SH COD-1 ISO TF 38830857000101 L3/HFP IDC XXXX
19664 | Whitesburg | 3312901 | JENKINS | KONA | 2021-01-16 11:02 | 2021-01-16 13:24 | 1 | 142 | 4872761 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service probly 115 ft. long , service neutral broke and service fell. please send to Rob Pigman to send tec. to see about setting pole in service // restored @1324 one customer out
19665 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-04-03 11:18 | 2009-04-03 13:40 | 1 | 142 | 64620-1 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT INTO AT WEATHER HEAD.// VER/DBM IDC XXXX
19666 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-01-10 07:28 | 2010-01-10 09:50 | 1 | 142 | 51612-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/0 SERVICE DROP IS BURNED INTO WILL NEED 20 FT OF WIRE AND ONE MAN TO HELP REPLACED CONDUCTOR VER/KEP L3/KEP IDC XXXX
19667 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-04-23 19:56 | 2020-04-23 21:07 | 2 | 71 | 4743021 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | On pole 336-97 had a broke cutout on this XFM,Made repairs and restored service at 21:07.
19668 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-11-24 12:53 | 2008-11-24 15:15 | 1 | 142 | 51619-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT. CREW EN-ROUTE TO CHANGE IT AND TWO OTHER SILVER TOP CUTOUTS IN XFMR BANK. REPAIRS COMPLETE. SH//3402801 //VER/CRB IDC XXXX
19669 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-02-19 21:28 | 2015-02-19 23:50 | 1 | 142 | 4045061 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SERVE END.PARTIAL POWER 38830834B00351 VER/CRB L3/HFP XXX
19670 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-04-27 09:49 | 2014-04-27 11:00 | 2 | 71 | 4638741 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 116-353 1.6 19.9 TRANS. FUSE OUT UNKNOWN SEND NOTE TO RAYBURN BAD LA AND NO CL FUSE ON TRANS TRANS NEEDS CHGED TO SMALL VER/KEP
19671 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-01-06 13:53 | 2009-01-06 16:15 | 1 | 142 | 51960-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-1 3411802/BAD 277/480 XFR,REPLACEMENT IS ENROUTE WITH CREW(PAUL LAYNE) RELEASED BY CREW 074S06 XFMR CHANGED OUT VOLTGE CK OK L3/HFP IDC XXXX
19672 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-06-19 16:03 | 2008-06-19 18:25 | 1 | 142 | 50893-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3308502// 6/19/08 COMP. XFMR FUSE ROTTEN//COD 1// VER/DBM
19673 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-09-25 23:28 | 2009-09-26 01:50 | 1 | 142 | 63404-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/ARN IDC XXXX
19674 | Pikeville | 3401001 | ELWOOD | DORTON | 2019-03-17 07:38 | 2019-03-17 10:00 | 1 | 142 | 4994471 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | customer had neutral and conductor in service drop burn into..made repairs.restored..
19675 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-08-25 11:28 | 2017-08-25 13:50 | 1 | 142 | 4298681 | 142 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF SERVICE AT THE TRANSFORMER SECONDARY RISER.38821014D00151 VER/AWD
19676 | Hazard | 3302704 | HAZARD | KENMONT | 2008-12-19 20:19 | 2008-12-19 21:30 | 2 | 71 | 61033-1 | 142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3302704// BAD CUTOUT GATE == REPLACED == REFUSED == POWER OK == ISO POLE 320-260 COD-2 VER/KEP L3/KEP IDC XXXX
19677 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-02-20 13:29 | 2015-02-20 15:50 | 1 | 141 | 4056581 | 141 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | LEADS BURNT ON XFMR ONE ABOUT INTO, NEED ONE MAN TO HELP ME.//// LEFT XFMR OPEN HAD HOT WIRE BURNT INTO IN BASE. CUSTOMER WILL NEED TO FIX BEFORE POWER CAN BE RESTORED. I TALKED TO CUST. VER/HFP L3/HFP
19678 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-05-26 06:33 | 2011-05-26 08:54 | 1 | 141 | 4171131 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACE BAD ARRESTER //VER/GAH
19679 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-01-06 13:32 | 2010-01-06 15:53 | 1 | 141 | 63755-1 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 33336418 BAD CUTOUT AND LA 1-CUST OUT RELEASED BY CREW 078S08. COMP 16:00, MP CCC-1 VER/HFP L3/HFP IDC XXXX
19680 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-10-14 07:27 | 2008-10-14 09:48 | 1 | 141 | 55579-1 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411801//TRANSFORMER FUSE OUT, REPLACE BAD CUTOUT//COD 1// VER/DBM IDC XXXX
19681 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-01-09 08:09 | 2012-01-09 10:30 | 1 | 141 | 4241711 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 SERVICE BURNT DOWN, NEED TO REPLACE WITH 4/0 SERVICE.-- B LINDON NOTIFIED. VER/KEP IDC XXXX
19682 | Pikeville | 3401001 | ELWOOD | DORTON | 2020-10-16 12:14 | 2020-10-16 14:35 | 1 | 141 | 4562001 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Customer has splice in service drop that has insulinks in it,going to open Trans on 286-47 to replace splice will keep up with time,Opened at 13:50 made repairs and restored at 14:35,Also replaced cutout on pole 286-47..
19683 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2020-04-25 12:28 | 2020-04-25 13:15 | 3 | 47 | 4747891 | 141 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | xfmr leads need to be changed out. I opened the xfmr at 12:28 and closed back in at 13:15
19684 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-06-20 15:08 | 2021-06-20 17:29 | 1 | 141 | 4775241 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | cutout door on pole 32D-103.was burned into..replaced door and fuse.got cutout on pole 32D-103 back in at 17:29
19685 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-10-05 07:00 | 2014-10-05 09:21 | 1 | 141 | 4554641 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACE CONNECTIONS AND WIRE VER/SEF
19686 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-02-02 12:09 | 2019-02-02 14:30 | 1 | 141 | 4748621 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout,,, changing
19687 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-04-03 17:09 | 2015-04-03 19:30 | 1 | 141 | 4266171 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..CHANGING. VER/KEP L3/DKGXXX
19688 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-11-14 07:14 | 2014-11-14 09:35 | 1 | 141 | 4726701 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND NEED TEP. INSTALLED UNDER GROUND BAD TEN YEARS AGO MIT WANT TO REPLACE TRUCKS TO POLE SEND NOTE TO BOB R. RELEASED BY CREW 078S08 VER/CRB
19689 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2014-02-05 22:49 | 2014-02-06 01:10 | 1 | 141 | 4361061 | 141 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF THE SERVICE AT THE TRANSFORMER POLE. VER/ARN
19690 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-03-08 10:01 | 2016-03-08 10:48 | 3 | 47 | 4824971 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS ON POLE 56-A-4 LEAKING SOME FROM SECONDARY BUSHING TIM HALL IS GOING TO SEND CREW IN MORNING TO REPLACE IT RELEASED BY CREW 079H03 OPEN 10:01 CLOSED 10:48 COMPETED 3/08/16 TOM MCCOWN COD-3 ISO TF 37820056A00004 VER/HFP L3/HFP
19691 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-10-22 11:25 | 2011-10-22 12:12 | 3 | 47 | H4009771 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL CHECK FOR PROBLEMS////4/3 SERV HAD BURNED INTO,MADE NECESSARY REPAIRS,ALL OK AFTERWARDS TR OFF FROM 1125 TO 1212 FOR 3 CUST.... DUP IN HOIS ... COD-4 ISO TF 38831056C00053 FROM 4009771 VER/HFP L3/HFP IDC XXXX
19692 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-12-01 19:12 | 2021-12-01 21:33 | 1 | 141 | 4139661 | 141 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot leg Burned Into at secondary pole 143-C2-396 pulled to make repairs will keep up with time..Pulled Meter at 20:53 made repairs and resored at 21:33.Please send copy to Forestry about cutting secondary out.
19693 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2014-07-02 09:55 | 2014-07-02 12:16 | 1 | 141 | 4182701 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 25T FUSE OUT ON POLE 66-15. I HAVE LINE ISO AND GROUND PLACED AT POLE 66-15 AND TAGED FOR MYSELF. CREW HAS ARRIVED. INSULATOR AT POLE 66-172 PULLED LOOSE FORM PIN AND PRIMARY FELL BELOW NEUTRAL//COD 1// VER/DBM
19694 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-04-07 21:33 | 2015-04-07 23:54 | 1 | 141 | 4286001 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 34.5 CUTOUT BROKE ON POLE # 26-111 NEED 1 MAN AND BIG BUCKET///OPENED LINE FUSE @ 22:40 AND MADE REPAIRS AND CLOSED LINE FUSE IN @ 23:54 AND RESTORED SERVICE// NO ADDITIONAL CUSTOMERS AFFECTED - FUSED CUTOUT ON SINGLE PHASE - 1 POLE TAP// VER/TOM L3/TOM
19695 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-12-12 05:25 | 2013-12-12 07:46 | 1 | 141 | 4155391 | 141 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS ON TRANSFORMER VER/SEF L3/HFP HFPC MCCDL
19696 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2022-04-22 16:39 | 2022-04-22 19:00 | 1 | 141 | 4790771 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | no crew required replaced arrestor and cutout restored at 1900
19697 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-07-11 17:44 | 2017-07-11 20:05 | 1 | 141 | 4107231 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DOOR BROKE ON 199-49, CUTOUT CHANGED AND POWER RESTORED AT 20:05/ ISO 38830199000049/ COD 1/ VER/BOW
19698 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-10-13 19:44 | 2011-10-13 22:05 | 1 | 141 | 4976261 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED--BAD CUTOUT--TRUCK OK RELEASED BY CREW 078S07 COD-1 ISO PO 39831123C45547 VER/HFP L3/HFP IDC XXXX
19699 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-15 20:29 | 2008-03-15 22:50 | 1 | 141 | 57572-1 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401 BAD CU TOUT ON XFMR POLE# 182/133 REPLACED CUTOUT& ARRESTER RESTORED POWER AT 22;50 VER/JHM IDC XXXX
19700 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-07-01 00:59 | 2011-07-01 03:20 | 1 | 141 | 4444311 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL SPLICE PULL LOOSE. REPLACE SERVICE DROP IDC XXXX
19701 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-05-07 12:21 | 2021-05-07 14:42 | 1 | 141 | 4547981 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on secondary pole all restored @1442
19702 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-03 22:24 | 2014-01-04 00:45 | 1 | 141 | 4226531 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR FAILED AND BURNT SERVICE IN TWO. REPLACED 4/3 SERVICE WITH 2/3. RESTORED @ 00:45. SH VER/PDP IDCC CNT7 XXXX
19703 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2010-11-07 15:06 | 2010-11-07 15:53 | 3 | 47 | 53721-1 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE/VER/CRB IDC XXXX
19704 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-01-28 14:49 | 2008-01-28 17:10 | 1 | 141 | 60468-1 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3008702//BAD 19.9 CUTOUT // SERVICER OPENED LATERAL ON 117-299 IN ORDER TO KILL LINE AND MAKE SAFE TO CHANGE FAILED TRANSFORMER CUTOUT//NO ADDITIONAL CUSTOMERS OUTAGED//COD 1//ISO// VER/DBM IDC XXXX
19705 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-01-13 15:43 | 2009-01-13 16:30 | 3 | 47 | 54748-1 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE.....DAH COD-3 VER/KEP L3/KEP IDC XXXX
19706 | Pikeville | 3421001 | BREAKS | CITY | 2013-10-24 14:08 | 2013-10-24 14:55 | 3 | 47 | 4960361 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED CUTOUT.//COD 3// VER/DBM
19707 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2021-02-01 19:39 | 2021-02-01 22:00 | 1 | 141 | 4927211 | 141 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad customer service//replaced and restored @ 2200 //
19708 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2022-08-29 14:26 | 2022-08-29 16:47 | 1 | 141 | 4808921 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | transformer on 38830092A00296 off from 16:27 to 16:47//OUT SINCE BEGGINNING SD WAS BURNT DOWN
19709 | Hazard | 3303902 | LESLIE | WOOTON | 2014-10-08 10:48 | 2014-10-08 11:35 | 3 | 47 | 4566271 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK AM// XFMR BEEN OUT FOR WEEKS// NO ONE LIVES HERE SHOULD BE OK TO DO THIS TOMORROW //SERVICER OPENING LINE FUSE .51-63 TO MAKE REPAIRS//WORK AM// XFMR BEEN OUT FOR WEEKS// NO ONE LIVES HERE SHOULD BE OK TO DO THIS TOMORROW . BROKEN CUTOUT ON POLE 510-70 NEED TO STEP BACK TO POLE 510-63 AND OPEN LINE FUSE TO DO SAFELY , MANUEL POLE OPENED AT 10:48 CLOSED AT 11:35 VER/CRB
19710 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2020-11-11 15:06 | 2020-11-11 17:27 | 1 | 141 | 4663271 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 38830068B00381 broke 12kv c/o. single phase tap. crew reqd. trk to pole Released by crew 078S07---replaced cutout--all repairs made--pwr restored @ 17:27---tbl tkt comp.rmv
19711 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-06-16 12:34 | 2020-06-16 14:55 | 1 | 141 | 4027531 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout no crew required
19712 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-08-23 15:08 | 2018-08-23 15:55 | 3 | 47 | 4993941 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door was burnt up..replaced.. L3/HFP
19713 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2010-11-15 10:21 | 2010-11-15 12:42 | 1 | 141 | 55721-1 | 141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SERVE END ON XFORMER. VER/HFP L3/HFP IDC XXXX
19714 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-02-12 07:04 | 2022-02-12 09:25 | 1 | 141 | 4476211 | 141 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | made repairs to secondery connection
19715 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-01-22 17:30 | 2021-01-22 19:50 | 1 | 140 | 4885761 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | On secondary pole 263-C-459,We have a melted squeeze on,Will have to pull Meter and climb pole to make repairs..Resqueezed it all up and checked voltage and it was good.
19716 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-09-10 07:50 | 2018-09-10 10:10 | 1 | 140 | 4073261 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open on 38830020C45681, Broken cutout on same pole. Cutout changed, line fuse back in at 10:10
19717 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-12-13 08:40 | 2017-12-13 09:00 | 7 | 20 | 4644521 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | reaired burnt hot leg connections,open xfmer @ 08:40, closed @ 09:00
19718 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-11-25 11:00 | 2009-11-25 13:20 | 1 | 140 | 65455-1 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END HAD BURNED LOOSE ON TRANS. POLE. I RESQUEEZED CONNECTIONS.//COD 1 IDCC CNT2 XXXX
19719 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-05-10 10:59 | 2015-05-10 12:09 | 2 | 70 | 4407941 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON P 247 SERVICER TO CHANGE LRM/COD 2// VER/ ADH
19720 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-03-31 15:25 | 2015-03-31 16:35 | 2 | 70 | 4249091 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT APR AT 1635 CLOSE TICKET/ ISO 38830380D40429/ COD 2/ VER/BOW
19721 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-01-22 21:59 | 2020-01-23 00:19 | 1 | 140 | 4330471 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3110903/gaj/2200/all out 3389 T George service drop burnt up, on site making repairs FETR 01003110903/gaj/2200/all out 3389 T George one cust not 7, had 4/3 srv drp burnted up rep with 2/3, all good at this loc comp by amg
19722 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-01-19 09:35 | 2016-01-19 11:55 | 1 | 140 | 4631781 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED UP AT WEATHERHEAD//MELTED MOST OF SERVICE DROP//I REPLACED SERVICE DROP//COMPLETE//EM/ ISO 38820866B00022/ COD 1/ VER/AWD
19723 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-06-20 21:40 | 2014-06-20 22:50 | 2 | 70 | 4126171 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 15 NEED RISERS ALSO TRUCKS OK RELEASED BY CREW 078S03; CORRECT POLE # IS 225/27; BEGINNING REPAIRS; OPENED XFMR AT 2140HRS; 25KVA XFMR REPLACED AND ENERGIZED AT 1050HRS; CLOSE TICKET//COD 2// VER/DBM
19724 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2012-09-28 23:30 | 2012-09-29 00:40 | 2 | 70 | 4097551 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BREAKING DOWN PER GREG AND PAULA BELL//NEEDS REPLACED//PRT ON SITE. VER/SDB IDCC TOF2109 XXXX
19725 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-10-31 10:12 | 2011-10-31 10:40 | 5 | 28 | H4038391 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART OF 4038391//BAD CONNECTION IN SERVICE DROP ,PART POWER ONLY ONE CUSTOMER AFFECTED, OPENED XFMR AT 10:12 MADE REPAIRS RESTORED POWER AT 10:40//COD 5// VER/DBM IDC XXXX
19726 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-01-25 16:50 | 2016-01-25 17:25 | 4 | 35 | H4649721 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FAILED CONNECTION ON XFMR RISER TO 1/0 SECONDARY. THREE CUSTOMERS AFFECTED - PART OUT. OPENED XFMR 882-149 @ 16:50, REWORKED CONNECTIONS AND CLOSED @ 17:25 RESTORING ALL OUTAGED CUSTOMERS. SH RELEASED BY CREW 076S02// VER/ ADH
19727 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-12-06 14:42 | 2022-12-06 17:02 | 1 | 140 | 4234741 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 19.9kv arrestor on pole 501-163. repairs made. complete
19728 | Hazard | 3302704 | HAZARD | KENMONT | 2008-03-21 14:55 | 2008-03-21 16:05 | 2 | 70 | 59776-1 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3302704// LEAD ON TRANSF BURNED OFF == LUG ON SECONDARY SIDE BURN OFF == REPAIRED == NEED TO CHANGE TRANSF OUT LATER// VER/DBM IDCC CNT1 XXXX
19729 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-08-31 19:20 | 2012-08-31 21:40 | 1 | 140 | 4990151 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE OPEN WIRE SECONDARY & NUETRAL BURNT DOWN DUE TO BAD CONNECTION..ONLY ONE CUST AFFECTED BY PART POWER. ///VER/CRB L/3 CRB IDC XXXX
19730 | Hazard | 3303901 | LESLIE | HYDEN | 2009-07-27 15:10 | 2009-07-27 16:20 | 2 | 70 | 64504-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A //COD 2// VER/DBM IDC XXXX
19731 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-08-19 11:05 | 2022-08-19 13:25 | 1 | 140 | 4761941 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole 359-22 is laid over almost into house,Will have to jack back up and add anchor,Crew Required.. Released by crew 074S01///NO OUTAGE till TR was opened at 1105 -- restored at XXXXPole 359-22 is laid over almost into house,Will have to jack back up and add anchor,Crew Required.. Released by crew 074S01/// power restored @ 13:25
19732 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-01-10 10:15 | 2016-01-10 12:35 | 1 | 140 | 4598931 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA 120/240 7.2 KV, TRUCK ACCESS . OPENED TRANSFORMER AT 10:15 ( NO OUTAGE TILL THAT TIME ) . REPLACED 10 KVA TRANSFORMER WITH 15 KVA TRANSFORMER, ALL WORK COMPLETE / GXJ VER/CRB
19733 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-12-10 18:55 | 2012-12-10 21:15 | 1 | 140 | 4458671 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S02 CUTOUT FAILED, BURNING THIS POLE ABOUT HALF THE DIAMETER THRU. WE WILL NEED TO WRITE A WORK ORDER TO REPLACE THIS POLE. ///VER/CRB L/3 CRB
19734 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-02-14 22:19 | 2011-02-15 00:39 | 1 | 140 | 57642-1 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL NEED TO REPLACE SERVICE DROP VER/KEP IDC XXXX
19735 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-03-06 13:30 | 2012-03-06 14:05 | 4 | 35 | 4556871 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED. TRUCK ACCESS. BRING 1/0 LEADS. 25 KVA { 19.9 } TRANS. IS PUTTING OUT LOW VOLTAGE ON POLE 96-21. WE NEED TO CHANGE TO A 50 KVA. THIS IS TRUCK ACCESSIBLE. RELEASED BY CREW 074S01 CHANGED TIME OFF TO TIME CREW ARRIVED TO REPLACE TRANSFORMER VER/HFP L3/HFP IDC XXXX
19736 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-06-09 08:35 | 2020-06-09 10:55 | 1 | 140 | 4982871 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Broken service neutral, repaired
19737 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2011-11-29 15:55 | 2011-11-29 16:30 | 4 | 35 | 4127471 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OFF AT 15:55 . REPLACED TRANSFORMER CUTOUT, ALL WORK COMPLETE / GXJ COD-4 ISO TF 37830211C00285 VER/HFP L3/HFP IDCC TOF1502 XXXX
19738 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-06-25 20:40 | 2014-06-25 21:50 | 2 | 70 | 4156901 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED POWER RESTORED AT 21 50 VER/KEP
19739 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2010-08-02 11:00 | 2010-08-02 11:35 | 4 | 35 | 60409-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | CREWS OPENED FUSE IN ORDER TO REPLACE PADMOUNT ON 1123-8034//COD 4//SEE ORDER 60290-1// VER/DBM IDCC CDC83 XXXX
19740 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2017-11-29 19:26 | 2017-11-29 20:36 | 2 | 70 | 4610601 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse broken on 966A1128 re-fused cutout restored power at 20:36
19741 | Whitesburg | 3312901 | JENKINS | KONA | 2014-01-31 12:05 | 2014-01-31 14:25 | 1 | 140 | 4332901 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANS. AT POLE 404-66, GEORGE WHITAKER ENROUTE TO HELP CHANGE OUT. RELEASED BY CREW 075H01//COD 1// VER/DBM
19742 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-09-08 08:35 | 2011-09-08 09:10 | 4 | 35 | 4847221 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT DOOR BROKEN //VER/CRB IDCC FEC49 XXXX
19743 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-06-16 12:25 | 2015-06-16 14:45 | 1 | 140 | 4579111 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED NEUTRAL CONNECTION/TIGHTENED ALL CONNECTIONS IN METERBASE ALSO// VER/ ADH
19744 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2013-09-20 17:47 | 2013-09-20 20:07 | 1 | 140 | 4871611 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY NEUTRAL CONNECTION FAILED ON TWO BUSHING XFMR. REPLACED LUG AND CLEANED BUSHING. RESTORED @ 20:07. SH//COD 1// VER/DBM
19745 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-04-27 20:20 | 2015-04-27 21:30 | 2 | 70 | 4371061 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SEC. NEUT BROKE 1 HOT LEG. CREW REGD. TRK OK RELEASED BY CREW 078S07----- XFORMER OFF @ 20:20-- ON @ 21:30/COD 2// VER/ ADH
19746 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-04-05 23:05 | 2018-04-05 23:40 | 4 | 35 | 4193871 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | changing xfmer now repairs made off 23:05 back on 23:40 // customer had a bright dim condition until the xfer fuse was opened @ 2305
19747 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-01-04 18:25 | 2013-01-04 19:00 | 4 | 35 | 4569341 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SLEEVE PULLED OUT AT POLE 423-96 ON A HOT LEG OF OPEN WIRE SEC. WILL HAVE TO OPEN THIS TRANS TO MAKE REPAIRS. WILL NEED A PIECE O 6ACW AND SLEEVES.ALSO NEED 1 MAN TO HELP WITH REPAIRS. ////AMBURGEY, ROGERSLEEVE PULLED OUT AT POLE 423-96 ON A HOT LEG OF OPEN WIRE SEC. WILL HAVE TO OPEN THIS TRANS TO MAKE REPAIRS. WILL NEED A PIECE O 6ACW AND SLEEVES.ALSO NEED 1 MAN TO HELP WITH REPAIRS.OPENED THIS TRANS. AT 18:25, MADE REPAIRS, CLOSED BACK IN AT 19:00. ///VER/CRB L/3 CRB IDC XXXX
19748 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2016-05-01 21:20 | 2016-05-01 23:40 | 1 | 140 | 4154481 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED CUTOUT// VER/ ADH
19749 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-09-03 11:53 | 2012-09-03 12:28 | 4 | 35 | 4999611 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | <<ONLY 4 CUSTOMERS AFFECTED>> XFMR FUSE LINK BROKE ON 38830834A00125.//MADE MDC<<ONLY 4 CUSTOMERS AFFECTED>> XFMR FUSE LINK BROKE ON 38830834A00125. RE-FUSED @ 12:28. SH ///VER/CRB L/3 CRB IDC XXXX
19750 | Pikeville | 3407101 | TOPMOST | DEMA | 2014-04-01 17:20 | 2014-04-01 18:30 | 2 | 70 | 4553261 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED TRANSFORMER CUTOUT , COMPLETE / GXJ//COD 2
19751 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-02-09 14:47 | 2010-02-09 17:07 | 1 | 140 | 54492-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 7200. RELEASED BY CREW 078S01//VER/CRB IDC XXXX
19752 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2022-07-15 16:35 | 2022-07-15 17:45 | 2 | 70 | 4495911 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 7200 15 leaking from secondary bushing on pole 351-174, will need replaced, truck accessible, crew required Released by crew 078H13 crew on site FETR 17:45 LRM all pwr restored 17:30 LRM Released by crew 078H06
19753 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-01-05 11:26 | 2013-01-05 11:40 | 10 | 14 | 4571491 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO 4570311 ---- RISER BURNT INTO ON L/F AT POLE 426-258, PATROLLED REST OF LINE, NO TROUBLE, WILL BE MAKING REPAIRS. OPENED THE TRANS ON THIS POLE AT 11:26, CLOSED IT AND THE L/F AT 11:40. COD-10 ISO TF 37830426B00258 VER/HFP L3/HFP IDCC TON1240 XXXX
19754 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-07-16 09:46 | 2008-07-16 10:56 | 2 | 70 | 53175-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN 6T FUSE//3001002//VER/CRB IDC XXXX
19755 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2015-10-21 13:10 | 2015-10-21 15:30 | 1 | 140 | 4366701 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGED OUT BAD ARRESTOR COMPLETE VER/CRB
19756 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2011-03-28 08:40 | 2011-03-28 09:50 | 2 | 70 | 59791-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT & ARRESTERS ON POLE 449-720 WILL NEED BIG BUCKET TO REPLACE /ORIGINAL ORDER 59778-1OPENED TRANSFORMER AT 840 CLOSED IT AT 950//VER/CRB IDC XXXX
19757 | Whitesburg | 3409503 | BURDINE | JENKINS | 2015-02-02 23:12 | 2015-02-02 23:40 | 5 | 28 | H4987091 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S11 BAD CONNECTIONS BURNT SECONDARY LEAD INTO AT POLE 382-143, WILL OPEN XFMR ON POLE 382-144 TO ISOLATE, OPENED AT 23:12 MADE REPAIRS RESTORED POWER AT 23:40. VER/KEP L3/HFP XXX AJB
19758 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2010-01-12 10:40 | 2010-01-12 13:00 | 1 | 140 | 53052-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33407027 //... BAD TRANSFORMER WILL BE CHANGED BY CREW IDC XXXX
19759 | Whitesburg | 3312901 | JENKINS | KONA | 2011-03-04 15:00 | 2011-03-04 15:20 | 7 | 20 | 66544-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PRIMARY CONDUCTOR CAME OFF INSULATORON POLE NO.403-86 I AM GOING TO OPEN LINE ON POLE NO. 403-60 OPENED AT 15:00 CLOSED AT 15:20 VER/HFP L3/HFP IDC XXXX
19760 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2022-07-20 14:35 | 2022-07-20 16:55 | 1 | 140 | 4530541 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 1109C-11.made repairs and ot transformer fuse on pole 1109C-11 back in at 16:55
19761 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-09-11 20:20 | 2013-09-11 21:30 | 2 | 70 | 4840171 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 118-62 BAD CUTOUT AND LA CHGED VER/CRB L/3 CRB
19762 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2013-03-10 16:05 | 2013-03-10 17:15 | 2 | 70 | 4895311 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE , VOLTAGE & CONNECTIONS CHECKED GOOD, DID FIND BAD CUTOUT WITH CRACKS IN IT THAT HAS BEEN TRACKING OVER TO POLE GROUND, OPENED XFMR AT 16:05 REPLACED CUTOUT RESTORED POWER AT 17:15. CUSTOMER SAID THAT IT DAMAGED COMPUTER. CCC COD-2 ISO TF 37830328B00143 VER/HFP L3/HFP IDC XXXX
19763 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-12-29 14:37 | 2019-12-29 16:57 | 1 | 140 | 4189911 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required
19764 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2009-06-03 08:55 | 2009-06-03 11:15 | 1 | 140 | 64640-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT MANUAL JOB GOT HELP ENROUTE REPLACED CUTOUT POWER RESTORED IDC XXXX
19765 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-10-25 08:38 | 2010-10-25 09:48 | 2 | 70 | 62691-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN INTO,WILL REPLACE IT///////REPLACED BAD CUTOUT AND RESTORED,ALL OK AFTERWARDS VER/KEP L3/KEP IDC XXXX
19766 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-11-08 09:25 | 2020-11-08 09:35 | 14 | 10 | 4652011 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK COMPLAINT/////////XFR CUTOUT WAS BROKEN,JUST SITTING ON TOP OF ITSELF.NOT DETERMINABLE UNTIL I GOT IT OFFLINE////////REPLACED IT WITH POLYMER TYPE.OFF@9:25,ON@9:35
19767 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-08-21 20:10 | 2010-08-21 20:30 | 7 | 20 | 59095-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER GOING TO OPEN TRANSFORMER TO MAKE REPAIRS OPENED TRANSFORMER AT 2010 CLOSED IT AT 2030 VER/ARN IDC XXXX
19768 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-11-12 15:12 | 2009-11-12 15:47 | 4 | 35 | 51821-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CREW OPENED TRANSFORMER TO REPLACE CONNECTIONS FROM ORDER 65721-1 COD-4 L3/HFP IDC XXXX
19769 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-09-03 13:30 | 2015-09-03 14:40 | 2 | 70 | 4194841 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XFR BANK 182-227 @ 13:30 REPLACED BURNT UP500 XFR RISER COMPLETE AND POWER RESTORED @ 14:40 VER/ARN L3/DKG
19770 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2022-09-27 11:20 | 2022-09-27 13:40 | 1 | 140 | 4929531 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers 1/0 secondary has a broke neutral and is laying on her gazebo, will have 1 customer out while making repairs. Took customer off @1120, made repairs and restored @1340
19771 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2015-06-23 12:05 | 2015-06-23 12:40 | 4 | 35 | 4644061 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFRM-- TIME OFF 12:05--- TIME ON 12:40/ ISO 38830092A00457/ COD 4 VER/CRB
19772 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-06-10 14:07 | 2010-06-10 14:35 | 5 | 28 | 59789-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10T ME FUSE LINK BROKE VER/KEP L3/KEP
19773 | Cannonsburg | 3000101 | ASHLAND | 25-25STREET | 2019-08-07 10:29 | 2019-08-07 12:49 | 1 | 140 | 4852671 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | C phase san fuse blown on pole 45-C4-5942-going to have to open all 3 fuses here and replace that fuse as well as a ct on the primary meteringBad PTs on primary metering & blown sand fuse. working on replacing PT & CT on C phase. fetr 12:49
19774 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2018-04-09 15:10 | 2018-04-09 15:30 | 7 | 20 | 4204041 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad 12kv c/o & l/a.arrived RM repacing broken cutout power on @ 15:30 please close tic RM off 1510
19775 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2017-08-17 19:00 | 2017-08-17 19:35 | 4 | 35 | H4272861 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, BAD CUTOUT, OPENED LINE FUSE AT 19:00, CHANGED CUTOUT AND ARRESTER, ALL POWER RESTORED AT 19:35 37830230A00124 37830230A00123 VER/AWD
19776 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2017-09-15 11:00 | 2017-09-15 13:20 | 1 | 140 | 4364551 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN AT POLE 38821111B00094. TRANSFORMER CUTOUT FAILED AT PRIMARY DEAD END POLE 38821111B40318. POLE IS BURNED OFF BELOW THE NEUTRAL AND TRANSFORMER IS ON THE GROUND. POSSIBLY CAN USE A SMALL LINE TRUCK AND BUCKET TO REPLACE THE POLE. FOREMAN SHOULD GO LOOK AT THIS FIRST TO BE SURE THAT ITS TRUCK ACCESS. THIS SERVES A CABIN THAT LOOKS LIKE IT HASNT BEEN USED FOR A WHILE NOW, MIGHT CHECK FIRST. SEND TO TIM HALL TO LOOK AT NEXT WEEK. VER/AWD
19777 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-05-05 17:30 | 2009-05-05 19:50 | 1 | 140 | 57067-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410502//VER/CRB IDC XXXX
19778 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-10-25 08:10 | 2008-10-25 08:30 | 7 | 20 | 58844-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003701 - REPLACED BAD CUTOUT. //VER/GAH IDC CHANGED TIME OFF FROM 0716 ESTIMATED IDC XXXX
19779 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-09-22 20:23 | 2020-09-22 21:33 | 2 | 70 | 4487741 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | hot line clamp failed on trans cutout on 1137-A-638,replaced clamp,restored power at 21:33.
19780 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-02-28 08:43 | 2019-02-28 11:03 | 1 | 140 | 4936051 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neut broke. making repairs. service drop burnt up, replaced service, all repairs made. pls close. tre
19781 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-12-26 07:15 | 2016-12-26 09:35 | 1 | 140 | 4237341 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | METER # 533968505 POLE # 38831077D00550, REPLACED TRANSFORMER CUTOUT AND ARRESTER, ALL WORK COMPLETE / GXJ VER/CRB
19782 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-06-10 18:40 | 2008-06-10 21:00 | 1 | 140 | 62032-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008701// BAD CURRENT FUSE // VER/TOM IDC XXXX
19783 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-29 04:10 | 2014-01-29 04:45 | 4 | 35 | H4321051 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | AFFECTS 5 CUSTOMERS SECONDARY CONNECTION FAILED ON XFMR POLE. REPAIRED AND RESTORED @ 4:45. HAD XFMR OPEN FROM 4:10 TO 4:45. SH 3 ON SEC VER/KEP
19784 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-12-11 16:00 | 2013-12-11 17:10 | 2 | 70 | 4150971 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TRANSFORMER LEADS BURNT AT POLE 37830272A41203, POWER OK, --- OPENED TRANSFORMERS AT 16:00, REPLACED LEADS AND CUTOUTS, POWER RESTORED AT 17:10//ISO//COD 2// VER/DBM L3/HFP
19785 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-03-12 10:23 | 2011-03-12 11:33 | 2 | 70 | 53710-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND TRANSFORMER FUSE HAD ROTTED AND BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC.//VER/CRB IDC XXXX
19786 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-05-31 10:55 | 2017-05-31 13:15 | 1 | 140 | 4885641 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | B PHASE L/F OUT @ 1101-D3-33, CHECKING. BAD LIGHTNING ARRESTOR @ 1101-D3-187, MADE REPAIRS AND CLOSED L/F BACK IN @1315. ONLY 1 CUSTOMER WAS AFFECTED ON THE OUTAGE./ ISO 38831101D30033/ COD 1/ VER/BOW
19787 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-09-26 11:10 | 2022-09-26 13:30 | 1 | 140 | 4924881 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | Bad connection at weather head aal repaires made. apr at 1330 close ticket
19788 | Hazard | 3420001 | SOFT SHELL | VEST | 2018-07-13 15:40 | 2018-07-13 16:50 | 2 | 70 | 4770741 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
19789 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2017-01-05 19:44 | 2017-01-05 22:04 | 1 | 140 | 4272411 | 140 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | **SEE H4272411*** PART POWER,OPENED XFMR AT 21:46 (1 ADD CUST) REPAIRED SPLICE RESTORED POWER AT 22:04 (2 CUST REST)../ ISO 37830449C20150 / COD 2/ VER/BOW L3/HFP XXXHFP
19790 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-05-07 04:45 | 2010-05-07 05:55 | 2 | 70 | 56774-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/KEP L3/KEP IDC XXXX
19791 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-11-28 14:40 | 2019-11-28 17:00 | 1 | 140 | 4100461 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout , replaced cutout restored power at 17:00
19792 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-12-13 20:05 | 2019-12-13 20:33 | 5 | 28 | 4151671 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 39831147C35072 cut out tracking opened at 20:05 back in at 20:33
19793 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-02-06 11:05 | 2020-02-06 12:15 | 2 | 70 | 4369621 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | open 30t fuse on 37830030000019 to repair cutout on 37830030000245
19794 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2008-01-05 21:18 | 2008-01-05 22:28 | 2 | 70 | 54095-1 | 140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000601///BROKEN LINK VER/ARN IDCC CNT1 XXXX
19795 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-10-12 23:26 | 2019-10-13 01:45 | 1 | 139 | 4135561 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | replaced secondary connections ,,,complete
19796 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-06-28 14:06 | 2015-06-28 16:25 | 1 | 139 | 4687391 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUSTOMER AFFECTED FOUND TWO BAD CONNECTIONS ON 277/480 XFMR BANK POLE CAUSING LOW VOLTAGE ON ONE LEG OF SERVICE. REPAIRED. CLOSED BANK BACK IN AT 16:25. SH/ ISO 38830930D00287/ COD 1/ VER/BOW
19797 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-12-09 16:50 | 2017-12-09 19:09 | 1 | 139 | 4636161 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRF IS OUT,WILL RE-FUSE//////////////FUSE DETERIORATED AND PULLED INTO///////RE-FUSED&RESTORED
19798 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2012-11-06 08:26 | 2012-11-06 10:45 | 1 | 139 | 4365971 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE IN SERVICE WIRE FAILED AND BURNT NEUTRAL APART. REPLACED 2/3 SERVICE WITH 1/0. SH ///VER/CRB L/3 CRB IDC XXXX
19799 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-10-02 10:31 | 2018-10-02 12:50 | 1 | 139 | 4189361 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 746-8//cutout broke on pole 746-320//repairs made//restored at 12:50//complete//em
19800 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-12-23 08:11 | 2013-12-23 10:30 | 1 | 139 | 4195241 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 3 PHASE BANK ON POLE 37830248C01027, NOTIFIED B.LINDON. -- REPLACED 3 CUTOUTS AND ARRESTORS, POWER RESTORED. VER/SEF L3/HFP
19801 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-10-18 10:37 | 2015-10-18 12:56 | 1 | 139 | 4358371 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE BURNED DOWN , REPLACED SERVICE . SEND TO DOUG C. TO GET XFMR & CUTOUT-TBRACKET REPLACED . CAN GET TRUCK TO POLE .//SENT TO MR CHRISTIAN VER/CRB
19802 | Pikeville | 3413401 | GARRETT | GARRETT | 2019-02-09 18:05 | 2019-02-09 20:24 | 1 | 139 | 4774121 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open on XFMR lead in difficult location I made repairs customer now has full power
19803 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-07-11 17:07 | 2022-07-11 19:26 | 1 | 139 | 4462051 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 255-238, opened line fuse on 255-41 @ 19:01, restored power at 19:26
19804 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-03-09 09:11 | 2013-03-09 11:30 | 1 | 139 | 4892871 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL BE DISPATCHED AFTER 1000./// LEAD BURNT OFF XFMR ON POLE 37830296A31569//// 1/0 TO 1/0 CONNECTIONS.///// MELTED OUT///// SEND TO DOUG CHRISTIAN MAY NEED REBUILD. COD-1 ISO TF 37830296A31569 VER/HFP L3/HFP IDCC CCO XXXX
19805 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-06-12 18:21 | 2019-06-12 20:40 | 1 | 139 | 4489921 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION
19806 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-06-17 10:31 | 2011-06-17 12:50 | 1 | 139 | 4333321 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO REPLACE TRANSFORMER 480 BANK RELEASED BY CREW 074S05 COD-1 ISO TF 38831151C00573 VER/HFP L3/HFP
19807 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-12-01 12:41 | 2022-12-01 15:00 | 1 | 139 | 4217591 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection pulled loose in underground service about 2 down in conduit///Was able to repair connection and restore full service @ 15:00///Customer does have damages
19808 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2019-01-30 16:20 | 2019-01-30 18:39 | 1 | 139 | 4739321 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired broken service nuetral.customer may have damages.send copy to Peggy Wynsong ¦¦ L3/HFP
19809 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-11-15 14:55 | 2019-11-15 17:14 | 1 | 139 | 4038131 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | hot tap has burnt off cutout on pole 207-274, tv booster only thing out, repaired cutout
19810 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-07-16 10:55 | 2009-07-16 13:14 | 1 | 139 | 65229-1 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 30766851 // CUTOUT HAS BROKE, CALLING FOR HELP COD-1 ISO TF 37830275000192 IDC XXXX
19811 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-03-29 15:43 | 2008-03-29 18:02 | 1 | 139 | 61987-1 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308502//THIS IS LOWER HOSPITAL PUMP STATION - FOUND BAD CONNECTION ON POLE // VER/TOM IDC XXXX
19812 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2019-01-31 14:51 | 2019-01-31 17:10 | 1 | 139 | 4744491 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6t fuse out due to bad transformer 25kva crew on the way
19813 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-03-02 21:51 | 2020-03-03 00:10 | 1 | 139 | 4445681 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | attempt to call customer failed, no answer// Cutout bad on xfm pole 37830069B30330. Opened tap @ pole 37830069000219 @ 23.40. Made repairs and energized at 00:10 //
19814 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-12-14 09:26 | 2020-12-14 11:45 | 1 | 139 | 4766531 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 318-128, replaced cutout restored power at 11:45.
19815 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-06-03 08:22 | 2009-06-03 10:41 | 1 | 139 | 64343-1 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308503// STS CUTOUT GATE BURNED UP GOING TO REPLACE IT IDC XXXX
19816 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2021-01-23 12:41 | 2021-01-23 15:00 | 1 | 139 | 4886971 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service neutral broke @ trans. pole 172-63, will have to open trans. to make repairs, will keep track of times. Opened trans. @1420 made repairs and closed back in @1500.//PART POWER FROM THE START
19817 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2017-01-16 14:56 | 2017-01-16 17:15 | 1 | 139 | 4303121 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | CUSTOMER HAD BAD SECONDARY CONNECTION AT SERVICE POLE OPENED SECONDARY AT 15;00 RECONNECTED CUSTOMER AT 15:15 REPLACED ALL THREE CONNECTIONS AT SERVICE POLE VER/CRB
19818 | South Williamson | 3202201 | LOVELY | LOVELY | 2012-10-02 07:54 | 2012-10-02 10:13 | 1 | 139 | 4106361 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE ON 771-276//CHANGING NOW//REPLCED CUTOUT//RESTORED AT 10:13//COMPLETE EM//COD 1// VER/DBM IDC XXXX
19819 | South Williamson | 3411401 | DEWEY | INEZ | 2010-12-22 15:48 | 2010-12-22 18:07 | 1 | 139 | 55124-1 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END CAME LOOSE CAUSING PARTIAL POWER...RE SPLICED AND CHECKED VOLTAGE..NOONE HOME.. VER/HFP L3/HFP IDC XXXX
19820 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-05-20 17:26 | 2022-05-20 19:45 | 1 | 139 | 4918821 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I repaired a bad connection in a span of 1/0 lash at pole 303-4.
19821 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-03-10 09:29 | 2015-03-10 11:48 | 1 | 139 | 4175781 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT // ORIGINALLY RELATED TO 4176221 //CHANGED CUTOUT, ARRESTOR,&BRACKET----PWR RESTORED @ 11:48///TBL TKT COMP/ LIFTED HOTTAP AT TRANSFORMER/ COD-1 ISO 38830044C35151 VER/HFP L3/HFP
19822 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-11-28 11:31 | 2012-11-28 13:50 | 1 | 139 | 4428131 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7200 CUTOUT. COD-1 ISO TF 38830380000142 VER/HFP L3/HFP IDC XXXX
19823 | Pikeville | 3421001 | BREAKS | CITY | 2011-04-13 11:16 | 2011-04-13 13:35 | 1 | 139 | 56288-1 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN 1/0 SERVICE.
19824 | South Williamson | 3411401 | DEWEY | INEZ | 2020-04-02 11:56 | 2020-04-02 14:15 | 1 | 139 | 4555151 | 139 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Splice pulled apart on one leg of service drop. I made repairs and restored to full power @ 14:15
19825 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2017-12-07 09:07 | 2017-12-07 11:26 | 1 | 139 | 4627811 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG conductor is in trouble between lot # 2 & lot #3. spoke with Tim hall in pikeville & he said that sense please send this to Tim hall .no one is occupying this mobile home at the time he will have crew make repairs 1st thing in the morning. UG is in trouble between lot 2&3 Released by crew 074S04//OPS # 034597614
19826 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-06-07 16:01 | 2018-06-07 18:20 | 1 | 139 | 4566621 | 139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
19827 | Hazard | 3303902 | LESLIE | WOOTON | 2009-12-07 22:50 | 2009-12-08 01:08 | 1 | 138 | 53423-1 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN 6-T FUSE IDCC CCO XXXX
19828 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2018-09-10 20:32 | 2018-09-10 20:55 | 6 | 23 | 4079581 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | conductor off of insulator on pole#79-210//// opened recloser on pole# 79-180 @ 20:32 to make repairs/// Repairs made closed recloser back in @ 20:55 Released by crew 074S02
19829 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-12-03 18:31 | 2010-12-03 19:40 | 2 | 69 | 62851-1 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 37986614 ///BAD CONNECTION ON XFMR POLE COD-2 ISO SO 37830004D00247 VER/HFP L3/HFP IDC XXXX
19830 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-08-15 14:22 | 2019-08-15 16:40 | 1 | 138 | 4892071 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on bank pole 359-A1-112..will make repairs.restored L3/HFP
19831 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-05-18 21:52 | 2022-05-19 00:10 | 1 | 138 | 4908671 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout. power restored 00:10
19832 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-12-02 14:03 | 2021-12-02 14:49 | 3 | 46 | 4141441 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a Hot Leg into in service drop,Going to open Trans and pull in new service will keep up with Time..Opened Trans at 14:03 replaced service wire and restored at 14:49..
19833 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-03-31 17:59 | 2015-03-31 18:45 | 3 | 46 | 4252181 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR F IS OUT,WILL RE-FUSE/////////FUSE OUT,DOOR DIDNT DROP,TRYING TO TRACK AND WAS BUZZING PER CUST//////////RE-FUSED AND RESTORED,ALL OK AFTERWARDS COD-3 ISO TF 38821107000015 VER/HFP L3/HFP
19834 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-04-18 15:26 | 2016-04-18 15:32 | 23 | 6 | 4100651 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | NO OUTAGE TILL STEP-DOWN 37830310A10183 WAS OPENED @ PRIMARY OFF INSUL. AT POLE 286-84 OPENED STEPDOWN AT POLE 310-183 AT 1526 CLOSED AT 1532//BAD INSULATER ON POLE 37830286000084 VER/CRB AJB
19835 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-06-05 01:58 | 2010-06-05 03:07 | 2 | 69 | 57044-1 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR FUSE IS OUT,WILL RE-FUSE//////////RE-FUSED AND RESTORED,APPEARED FUSE MAY HAVE JUST ROTTED INTO VER/PDP IDC XXXX
19836 | Hazard | 3303901 | LESLIE | HYDEN | 2011-05-23 15:48 | 2011-05-23 18:06 | 1 | 138 | 4146811 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT AND RESTORED POWER AT 1806 JKC VER/KEP
19837 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-01-19 10:02 | 2009-01-19 12:20 | 1 | 138 | 58229-1 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3402001// CUTOUT BROKE-INTO. ALSO HAD TO REPLACE CROSS ARM. TIME OFF 11:54//ISO 38831127B00461//COD 3// VER/DBM L3/KEP
19838 | Whitesburg | 3314401 | MAYKING | ERMINE | 2017-06-16 07:07 | 2017-06-16 09:25 | 1 | 138 | 4979871 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD, MADE REPAIRS RESTORED POWER AT 09:25.. 37830473000114 VER/AWD
19839 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-11-30 10:52 | 2013-11-30 11:15 | 6 | 23 | H4088951 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 4088951//SERV DROP TO REPAIR/////MADE REPAIRS,SERVE-IN CONNECTIONS HEATED UP AND BURNED SERV INTO.OFF AT 10:52,ON AT 11:15//COD 6// VER/DBM
19840 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2017-03-29 11:01 | 2017-03-29 12:10 | 2 | 69 | 4594391 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGED XFMR COD-2 ISO TF37820126000193. VER/HFP L3/HFP
19841 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-02-10 13:30 | 2008-02-10 15:48 | 1 | 138 | 54362-1 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409301// XFMR PRIMARY RISER IS BROKEN AT BUSHING. CREW ENROUTE TO ASSIST. RELEASED BY CREW 076S02 REPLACED RISER// ON AT 15:48// VER/DBM IDC XXXX
19842 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-02-07 16:46 | 2009-02-07 17:55 | 2 | 69 | 56583-1 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED IN HALF// VER/TOM L3/TOM IDCC CNT1 XXXX
19843 | Hazard | 3303902 | LESLIE | WOOTON | 2019-03-31 19:52 | 2019-03-31 22:10 | 1 | 138 | 4046021 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Lead from cutout had came out of transformer repaired power ok
19844 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2016-01-10 15:42 | 2016-01-10 18:00 | 1 | 138 | 4603121 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION.WATER GOT IN CONNECTION AND FROZE OPEN THE CONNECTION..REPLACING.. VER/CRB
19845 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2013-12-23 17:57 | 2013-12-23 20:15 | 1 | 138 | 4197811 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SEC. RISER LOOSE FROM XFMR// WILL REPAIR // REPAIRS MADE // POWER IS RESTORED//POLE 48 HAS A NEW TRANSFORMER ON IT LESS THAN 1 WEEK 1 COD VER/CRB
19846 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-05-11 14:07 | 2011-05-11 16:25 | 1 | 138 | 4061341 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BURN-INTO DOING STORM// VER/DBM
19847 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-08-31 08:41 | 2014-08-31 09:50 | 2 | 69 | 4440291 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 115-592 BAD CUTOUT CHGED//COD 2// VER/DBM
19848 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2013-07-10 17:35 | 2013-07-10 18:44 | 2 | 69 | 4499651 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT THAT PROTECTED SIDE TAP.//COD 2// VER/DBM IDCC PN389 XXXX
19849 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-03-09 12:12 | 2011-03-09 14:30 | 1 | 138 | 52133-1 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEND TO P TOLLIVER RELEASED BY CREW 078S07REPLACED CUT-OUT ALL POWER RESTORED AT 14:30 P R TOLLIVER VER/KEP IDC XXXX
19850 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-08-29 11:22 | 2013-08-29 13:40 | 1 | 138 | 4718931 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFORM FUSE OUT REFUSE ,CHANGE CUTOUT REMOVED BAD ARR. POWER RESTORED 13:40 VER/SEF IDC XXXX
19851 | Hazard | 3302704 | HAZARD | KENMONT | 2013-04-14 14:05 | 2013-04-14 14:28 | 6 | 23 | 4008311 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SERVICER OPENED STEPDOWN IN ORDER TO MAKE REPAIRS RELATED TO ORDER 4008101//COD 6// VER/DBM IDC XXXX
19852 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-06-14 20:12 | 2015-06-14 21:21 | 2 | 69 | 4571091 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK//COD 2// VER/DBM
19853 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-08-26 13:10 | 2021-08-26 13:56 | 3 | 46 | 4157381 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester went bad on XFM, cut arrester in the clear, refused and restored
19854 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-07-04 11:12 | 2009-07-04 13:30 | 1 | 138 | 64565-1 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT AND ARRESTOR ON POLE 903-26, HAVE CUTOUT CHANGED, BUT DID NOT CHANGE ARRESTOR, DID NOT HAVE ANY ON THE TRUCK, SEND TO RAYBURN TO HAVE CREWS TO COME AND CHANGE THIS, PLEASE, POWER IS RESTORED AT THIS LOC, ALSO CHANGED LINE FUSE FROM A 12T TO A 8T, DID TALK TO GREG BELL ABOUT THIS//COD 1// VER/DBM IDC XXXX
19855 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-01-10 16:36 | 2018-01-10 17:45 | 2 | 69 | 4727931 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv door, replaced, restored/ ISO 38830069D16065/ COD 2
19856 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-05-14 14:05 | 2009-05-14 16:23 | 1 | 138 | 55341-1 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE CORRECT POLE NUMBER IS 1038-11, NEED 19.9 CUTOUT AND ARRESTOR AND NEED TO STRAIGHTEN POLE, NOONE LIVING IN HOME BUT TOLD NEIGHBOR WE WOULD FIX FRIDAY RELEASED BY CREW 077S05 COD-1// VER/KEP L3/KEP IDC XXXX
19857 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2012-02-13 12:42 | 2012-02-13 15:00 | 1 | 138 | 4345301 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT CONDUCTOR BURNT INTO ON 4/3 SERVICE DROP. DROP ALSO HAD SPLICE IN IT THIS IS 200AMP. I CHANGED DROP TO A 2/3 DROP REPAIRS MADE EVERYTHING OK. VER/HFP L3/HFP IDC XXXX
19858 | Paintsville | 3409302 | KENWOOD | AUXIER | 2019-06-12 16:12 | 2019-06-12 18:30 | 1 | 138 | 4489361 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connector failed mid-span of 3 phase service. Reworked connections in mid-span splice and restored @ 18:30. sh
19859 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-02-05 07:32 | 2021-02-05 09:50 | 1 | 138 | 4938881 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Crew required, need power temp installed @ 7213 hickory hills dr. Bad UG hot leg. Leg isolated, meter blanked, ug direct bury. Transformer on 92-648 off from 08:55 back on @ 09:00 Released by crew . 078S02. installed power temp 2/5/21 restored 950//DAE MADE
19860 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2019-03-05 20:17 | 2019-03-05 22:35 | 1 | 138 | 4954761 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open @ xfm and weatherhead/// Replaced bad connections and restored service @ 22:35/// only 1 customer affected L3/HFP
19861 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2017-12-06 11:04 | 2017-12-06 11:50 | 3 | 46 | 4625681 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACING BAD OVERHEAD SECONDARY// open at 11:04 closed at 11:50
19862 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-12-28 10:12 | 2020-12-28 11:21 | 2 | 69 | 4829951 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced fuse door
19863 | Whitesburg | 3401301 | FLEMING | NEON | 2022-07-22 18:06 | 2022-07-22 19:15 | 2 | 69 | 4550391 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT RESTORED POWER @ 19:15
19864 | South Williamson | 3200302 | BELFRY | TOLER | 2017-06-14 13:02 | 2017-06-14 15:20 | 1 | 138 | 4967541 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY CONNECTION AT THE TRANSFORMER./ ISO 38821063C00085/ COD 1/ VER/BOW
19865 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-08-30 15:24 | 2021-08-30 17:42 | 1 | 138 | 4178541 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke in customers service drop, made repairs and restored the one customer
19866 | Whitesburg | 3314401 | MAYKING | ERMINE | 2014-12-23 18:27 | 2014-12-23 19:36 | 2 | 69 | 4877761 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POWER RESTORED AT 19:36 12/23/2014. LIFTED CLAMP ON CSP X-FMR ON POLE 473-80. X-FMR MUST HAVE BEEN BAD.// COD 2// VER/ ADH
19867 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-10-07 13:57 | 2014-10-07 16:15 | 1 | 138 | 4565401 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEND TO PEGGY WYSONG. CUSTOMER SAID THEY HAD DAMAGES TO MICROWAVE AND SECURITY SYSTEM FOR SURE. THEY ARE GOING TO CHECK EVERYTHING ELSE. I TOLD THEM TO CALL 1-800 NUMBER AND REPORT IT. NEUTRAL IS BROKEN IN SERVICE DROP AT SECONDARY POLE. IT BROKE WHERE IT WAS SERVED AT CLEVIS ON POLE. I AM GOING TO SPLICE SERVICE NEUTRAL. I SPLICED NEUTRAL IN SERVICE DROP. // SENT TO PEGGY WYSONG VER/HFP L3/HFP
19868 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-07-24 16:11 | 2010-07-24 17:20 | 2 | 69 | 56429-1 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD NETURAL CONNECTION ON TRANSFORMER VER/KEP L3/KEP IDC XXXX
19869 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-06-01 21:51 | 2019-06-01 23:00 | 2 | 69 | 4409121 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at transformer full power restored at 2300/ ISO 38830188C00322/ COD 2
19870 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-12-07 23:35 | 2019-12-08 00:44 | 2 | 69 | 4134381 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @95-124, cheking. Fuse had melted into , refused @0044.
19871 | Hazard | 3303901 | LESLIE | HYDEN | 2014-03-04 10:42 | 2014-03-04 13:00 | 1 | 138 | 4450451 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPLACED BAD SERVEIN. VER/CRB
19872 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2017-12-13 09:08 | 2017-12-13 10:17 | 2 | 69 | 4645141 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse out @47-D-31, checking. Fuse melted out closed back in @ 1017.
19873 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-05-31 20:57 | 2016-05-31 23:15 | 1 | 138 | 4277191 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 65-D-574 REPLACED CUTOUT RESTORED POWER AT 23:15 VER/AWD
19874 | Hazard | 3303902 | LESLIE | WOOTON | 2016-02-02 16:56 | 2016-02-02 18:05 | 2 | 69 | 4667991 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830437D30150 , REPLACED CUTOUT ./ ISO 37830437D30150/ COD 2/ VER/BOW
19875 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2022-03-01 19:47 | 2022-03-01 22:05 | 1 | 138 | 4558181 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Customer had one leg out at meter base when I arrived. Reworked xfmr and weatherhead connections and seems to have fixed the problem. Restored @ 22:05. sh
19876 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-03-04 12:54 | 2014-03-04 15:12 | 1 | 138 | 4450971 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BAD REPAIRES MADE 15:12 XFMR BACK ON T.R. VER/CRB IDC XXXX
19877 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-05-24 07:27 | 2016-05-24 09:45 | 1 | 138 | 4253571 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE REPLACED FUSE EVERYTHING OK/ ISO 37830068000129/ COD 1/ VER/BOW
19878 | South Williamson | 3411401 | DEWEY | INEZ | 2013-06-25 15:00 | 2013-06-25 17:18 | 1 | 138 | 4397721 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 672-183//GOING TO OPEN FUSE ON 672-21 AND GROUND TAP TO CLIMB AND CHANGE CUTOUT//MADE MDC//COD 1CUTOUT BROKE ON POLE 672-183//GOING TO OPEN FUSE ON 672-21 AND GROUND TAP TO CLIMB AND CHANGE CUTOUT//REPAIRS MADE//RESTORED AT 17:18//COMPLETE//EM VER/CRB L/3 CRB IDCC CDC92 XXXX
19879 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2014-10-10 12:35 | 2014-10-10 13:21 | 3 | 46 | 4602511 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRING CONNECTION ON TRANSFORMER// COD 3// VER/ ADH
19880 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2022-09-18 16:12 | 2022-09-18 18:30 | 1 | 138 | 4893501 | 138 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg burnt into at transformer got repairs made at 18:30
19881 | South Williamson | 3411401 | DEWEY | INEZ | 2014-10-19 00:06 | 2014-10-19 01:15 | 2 | 69 | 4643491 | 138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 673-57//CAN CHANGE WITH TRUCK//RPAIRS MADE//CRESTORED AT 1:15//COMPLETE//EM VER/SEF
19882 | Whitesburg | 3312902 | JENKINS | JENKINS | 2015-04-27 11:21 | 2015-04-27 13:38 | 1 | 137 | 4369541 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO OUTAGE NEUTRAL BROKE AT SPLICE IN SERVICE DROP , REPLACED WITH # 2 SERVICE WIRE .ONLY ONE CUSTOMER AFFECTED VER/CRB
19883 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2017-01-05 13:54 | 2017-01-05 16:11 | 1 | 137 | 4271681 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TWO MEN AND BUCKET TO REPLACE BAD TRANSFORMER CUTOUT. CUTOUT IS BETWEEN TWO PRIMARY PHASES. CAN MOVE CUTOUT FROM THE ARM TO A STAND OFF BRACKET. RELEASED BY CREW 079S02// REPLACED DAMAGED CUTOUT AND RESTORED POWER AT 16:11 TIM MCCOY RELEASED BY CREW 074H10 VER/CRB
19884 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-03-31 10:39 | 2022-03-31 12:56 | 1 | 137 | 4701571 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1103-96, checking. Trans. fuse had melted, refused @1256.
19885 | Hazard | 3303901 | LESLIE | HYDEN | 2019-11-01 18:33 | 2019-11-01 20:50 | 1 | 137 | 4280431 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | secondary connection burnt in two
19886 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-10-14 17:58 | 2014-10-14 20:15 | 1 | 137 | 4626001 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 494-32 , OPENED RECLOSER ON POLE 494-139 AT 19:32 TO ISOLATE(SEE 4627261), REPLACED CUTOUT RESTORED POWER AT 20:15.//COD 1// VER/DBM L3/HFP
19887 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-04-24 15:43 | 2020-04-24 18:00 | 1 | 137 | 4747071 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutout broke into, I have to go to the office to get one. changed out
19888 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2008-12-04 22:19 | 2008-12-05 00:36 | 1 | 137 | 54587-1 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3400302//SERVICE DROP BURNT OPEN ONE SIDE AT WEATHER HEAD. PART POWER. MADE REPAIRES EVERYTHING OK. 27560169 VER/JHM L3/KEP IDC XXXX
19889 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2017-01-24 10:28 | 2017-01-24 12:45 | 1 | 137 | 4326081 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED SERVE END BAD . REPLACED CONN .ONLY 1 CUST. WITH PART POWER . 37830248A00163 VER/AWD // VER PER VOICE REC = L3/HFP HFPC CDC92 LCD FP37830248A00163
19890 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2019-02-13 10:28 | 2019-02-13 12:45 | 1 | 137 | 4789111 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burned up, and bad neutral connection on pole. Repairs made, all power restored at 12:45
19891 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2018-06-01 08:13 | 2018-06-01 10:30 | 1 | 137 | 4537881 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | part power , bad primary metering on Cphase , bypassed metering for now ,so crew can replace later date.restored power at 10:30..
19892 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-08-13 11:43 | 2019-08-13 14:00 | 1 | 137 | 4879131 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke
19893 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2015-09-22 09:23 | 2015-09-22 11:40 | 1 | 137 | 4259361 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED NEUTRAL IN SERVICE DROP. ONE CUSTOMER AFFECTED VER/HFP L3/HFP
19894 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2009-08-09 14:13 | 2009-08-09 16:30 | 1 | 137 | 50164-1 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUST HAS DAMAGE TO EQUIPMENT ON INSIDE OF STORE DUE TO 1/0 NEUTRAL BURNT INTO ON SERVICE DROP. ONE SIDE OF HOT CONDUCTOR WAS BURNT ALSO. DROP IS ABOUT 12 FOOT LONG AND WAS BURNT INTO ABOUT 2 FOOT FROM BUILDING. THIS BUILDING HAS TWO 200 AMP METERS ON IT. LOAD ON THE DEMAND METER WAS 26.1 KW. CUST SAID NOT MUCH LOAD ON THE OTHER 200AMP METER. SEND COPY TO RON RYE ENG PIKEVILLE. TO CHECK PAST LOAD AND SEE IF THIS SEC AND DROP MAY NEED TO BE UPGRADED. METER NBR ON BUILDING// VER/DBM IDC XXXX
19895 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-09-02 11:43 | 2020-09-02 14:00 | 1 | 137 | 4419331 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BLOWED APART@POLE 291,HAVE TO REPLACE IT.ALSO TOOK LINEF@290 OUT,WILL RE-FUSE THERE WHEN REPAIRS ARE COMPLETED@291///////REPLACED CUTOUT,RE-FUSED&RESTORED
19896 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-06-11 07:43 | 2008-06-11 10:00 | 1 | 137 | 62428-1 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3103101//REPAIRING CONNECTIONS 38830149000022 VER/HFP IDC XXXX
19897 | Pikeville | 3402003 | KEYSER | MULLINS | 2013-09-20 19:41 | 2013-09-20 21:58 | 1 | 137 | 4871831 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT INTO ON TRANSFORMER POLE ON HOT LEG.REPAIRED CONDUCTOR.SERVICE RESTORED.// VER/DBM
19898 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2017-01-09 13:25 | 2017-01-09 15:42 | 1 | 137 | 4280961 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | INSULINK CONNECTOR GOT HOT AND BURNED SERVICE NEUTRAL IN TWO. REPAIRED. SH/ 38830858C00012 L3/HFP
19899 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2011-01-25 21:38 | 2011-01-25 23:55 | 1 | 137 | 64305-1 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT.--- POWER RESTORED VER/TOM IDC XXXX
19900 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-10-27 10:28 | 2008-10-27 12:45 | 1 | 137 | 59477-1 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308002// CONNECTION BAD ON XFMR POLE/// REDONE CONNECTION ON POLE. FULL POWER NOW. VER/KEP IDC XXXX
19901 | Pikeville | 3414901 | FISHTRAP | DISTRIBUTION | 2008-08-20 12:28 | 2008-08-20 14:45 | 1 | 137 | 53452-1 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT-TAP BURNED OFF AT P-53-313,WILL TRY TO REPAIR WITHOUT ANY FURTHER OUTAGE.LEAD HAS FALLEN ACROSS ANOTHER PHASE WIRE AT POLE 53-313REPLACED HOT-TAP AT POLE 53-313,RE-TAPPED ONTO MAIN LINE AT THAT POINT.ALL OK AFTERWARDS PER MINE ALTHO NOBODY WAS AROUND//3414901//VER/CRB IDC XXXX
19902 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2011-08-16 15:13 | 2011-08-16 17:30 | 1 | 137 | 4717611 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PRI BUSHING ON XFMR IS BURNED & BROKEN .HAVE CREW ON WAY TO CHG PLEASE SEND A NOTE TO R/W TO CUT HERE // SENT EMAIL AS REQUESTED...HFP // COD-1 ISO TF 38830954A30787 VER/HFP L3/HFP IDCC TOF1413, ESTIMATED TIME OFF XXXX
19903 | Hazard | 3302704 | HAZARD | KENMONT | 2009-05-02 09:12 | 2009-05-02 11:29 | 1 | 137 | 62982-1 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP CREW HAS JOB TO CHANGE TRANSFORMER MONDAY MORNING AND CUSTOMER HAS AGREED TO WAIT. ONLY SERVES A TOOL SHED L3/HFP IDC XXXX
19904 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-09-20 15:31 | 2016-09-20 17:48 | 1 | 137 | 4912831 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | METER BLANK/HEARD POPPING SOUND BEFORE ALL OUT. TRANS CUTOUT DOOR FAILED REPLACED CUTOUT AND ARRESTOR RESTORED POWER AT 17:48 VER/AWD
19905 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2011-02-09 18:48 | 2011-02-09 21:05 | 1 | 137 | 55753-1 | 137 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUST S/D HAS ONE WIRE BURNED INTO ------SPLICED SER. BACK.//VER/CRB IDC XXXX
19906 | Pikeville | 3413402 | GARRETT | LACKEY | 2022-12-15 09:33 | 2022-12-15 11:50 | 1 | 137 | 4263261 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke @ 37830159000523.//Replaced7200 cutout and bracket.//Restored @ 11:50
19907 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2011-04-29 11:23 | 2011-04-29 13:40 | 1 | 137 | 52274-1 | 137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLEW AND RESULTING ARC TOOK OUT XFMR FUSE. WILL NEED TO REPLACE CUTOUT AND ARRESTER. WORK COMPLETE. RESTORED XFMR @ 13:40. SH//COD 1// VER/DBM
19908 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-05-25 17:52 | 2011-05-25 19:00 | 2 | 68 | 4169051 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. FUSE LINK IS BROKEN. I REFUSED TRANS. AND IT STAYED. VER/KEP
19909 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-06-13 18:19 | 2011-06-13 20:35 | 1 | 136 | 4313971 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN SERVICE DROP BROKE AT TRANS. POLE WHERE IT WAS SERVED AROUND ITSELF. I AM GOING TO SPLICE NEUTRAL. I SPLICED NEUTRAL//VER/CRB
19910 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-10-25 12:17 | 2018-10-25 14:33 | 1 | 136 | 4321701 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link appears to have broke. Restored @ 14:33. sh L3/HFP
19911 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-04-21 18:19 | 2012-04-21 19:27 | 2 | 68 | 4693251 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD BROKEN OUT OF CUTOUT,WILL REPAIR///////MADE NECESSARY REPAIRS AND RESTORED,MUST HAVE BROKEN WHILE WE WERE PUTTING WIRE UP AND WAS SWINGING BACK AND FORTH//COD 2// VER/DBM L/3 CRB IDC XXXX
19912 | Whitesburg | 3312901 | JENKINS | KONA | 2014-04-07 10:23 | 2014-04-07 12:39 | 1 | 136 | 4581191 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 403-91 RELEASED BY CREW 077S11 REMOVED TAP ON POLE403-27 AT 1150 PUT IT ON AT 1230 -- SEE 4581541 // COD-1 ISO TF 37830403A00091 VER/HFP L3/HFP
19913 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-12-26 12:11 | 2019-12-26 12:28 | 8 | 17 | 4183001 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | while repairing cutout on pole 261-129.noticed cutout broken as well on pole 261-118..repairs made and restored..
19914 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2016-04-02 09:37 | 2016-04-02 10:45 | 2 | 68 | 4017981 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHGING CUTOUT VER/CRB
19915 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-02-26 13:57 | 2022-02-26 15:05 | 2 | 68 | 4548731 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
19916 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-01-29 16:34 | 2012-01-29 18:50 | 1 | 136 | 4302971 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD 19.9 CURENT LIMERTER FUSE--CREW ASISTED IN MAKING REPAIRS //VER/GAH IDC XXXX
19917 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-06-28 11:39 | 2022-06-28 13:55 | 1 | 136 | 4340091 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutout broke on 216-16 will change///Changed broken cutout and restored service @ 13:55
19918 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-11-16 22:17 | 2019-11-16 23:25 | 2 | 68 | 4041151 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer: can see fuse tail hanging down. cutout broke. repairs made. pls close. tre/ ISO 38830116B00760/ COD 2
19919 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-06-08 18:34 | 2015-06-08 20:50 | 1 | 136 | 4535001 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT UP ON SIDE OF HILL WILL NEED CUTOUT 7200 FUSE SIZE UNKNOWN NOT ON MAPS THIS IS WHERE FLAGGER JAMES DEATON LIVES AT RELEASED BY CREW 077H14// VER/ ADH
19920 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-03-03 08:04 | 2015-03-03 10:20 | 1 | 136 | 4093351 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNT DOWN/CONNECTION HEATED UP AND BURNT SERVICE DOWN.CONNECTION HEATED UP AND BURNT SERVICE DOWN. REPLACED SERVICE AND RESTORED @ 10:20. SH// VER/ ADH L3/HFP XXX
19921 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2011-01-05 09:29 | 2011-01-05 11:45 | 1 | 136 | 58856-1 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUSTOMER AFFECTED. THE SERVICE DROP NEUTRAL BURNED APART NEAR A SPLICE. THE SPLICE HAD TAPE APPLIED ON EACH SIDE OF THE SPLICE,HOLDING THE THREE CONDUCTORS TIGHTLY TOGETHER. THE FAULT WAS UNDERNEATH THE TAPE. THIS CUSTOMER IS COMPLAINING OF DAMAGED APPLIANCES. VER/KEP L3/KEP IDC XXXX
19922 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2020-07-30 15:04 | 2020-07-30 16:30 | 6 | 86 | 4256271 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | conductor burnedin two at 2 bolt clamp.opened@ 16:20 closed in @ 16:30
19923 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-06-26 14:23 | 2014-06-26 16:39 | 1 | 136 | 4159681 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN WILL RE-FUSE/// CUT OUT BROKE WHEN I CLOSED DOOR IN WILL REPLACE///REPLACED BROKEN CUT OUT RESTORED SERVICE @ 16:39 VER/CRB
19924 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-04-29 10:19 | 2020-04-29 12:35 | 1 | 136 | 4765551 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 53-148. will make repaires. restored 12:35
19925 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2019-01-21 09:31 | 2019-01-21 11:47 | 1 | 136 | 4699281 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | no crew required repaired neutral
19926 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-08-18 15:44 | 2013-08-18 18:00 | 1 | 136 | H4676871 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 117-45 NUMBER 4 ACSR BURNT DOWN ACROSS SHOPS CK. NEED 4-MAN CREW AND FLAGGERS POLE 117-45 40T OPENED TRANS ON POLE 117-45 1 CUST. OUT RELEASED BY CREW 078S08//COD 1// VER/DBM IDC XXXX
19927 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-03-24 14:09 | 2019-03-24 16:25 | 1 | 136 | 4020471 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout and bracket. Restored @ 16:25. sh
19928 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-05-10 10:29 | 2021-05-10 12:45 | 1 | 136 | 4570121 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | repalced broke cutout
19929 | Hazard | 3309302 | VICCO | JEFF | 2009-06-24 12:55 | 2009-06-24 15:11 | 1 | 136 | 55926-1 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD CONNECTION ON TOP OF TRL POLE == REPAIRED CONNECTION == L3/HFP IDCC CNT9 XXXX
19930 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-12-03 15:26 | 2020-12-03 16:00 | 4 | 34 | 4742721 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | strands in the primary broke, I opened up to make repairs
19931 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-01-28 13:38 | 2020-01-28 13:46 | 17 | 8 | 4344581 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened recloser on pole 385-20 to change broke cut-out on pole 385-116//OFF @ 1338 ON @ 1346 L3/HFP
19932 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-11-06 11:01 | 2019-11-06 13:17 | 1 | 136 | 4002751 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | changed insulinks out that were getting hot, also meter base lug changed for cust. all repairs made. pls close. tre
19933 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-06-20 07:54 | 2017-06-20 08:28 | 4 | 34 | 4005531 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR & FUSE/// VER/DKM
19934 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-08-03 21:24 | 2012-08-03 23:40 | 1 | 136 | 4892931 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE RM /XFM LUG BROKE ON SEC.SIDE POWER RESTORED AT 23:40 PLEASE CLOSE TIC RM COD-1 ISO TF 38830548000041 VER/HFP L3/HFP IDC XXXX
19935 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-02-10 19:10 | 2022-02-10 21:26 | 1 | 136 | 4466651 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required
19936 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-10-10 08:57 | 2016-10-10 11:13 | 1 | 136 | 4981821 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE BURNT INTO AT POLE 351-110/OPENED L/F ON 4982181C PHASE BURNT INTO AT POLE 351-110, OPENED LINE FUSES ON POLE 351-2 AT 10:25 TO ISOLATE , MADE REPAIRS RESTORED POWER AT 11:13 RELEASED BY CREW 077S11 VER/AWD // SEE 4982181 FOR FUSE OUTAGE L3/HFP XXXHFP
19937 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-01-05 12:14 | 2011-01-05 14:30 | 1 | 136 | 58937-1 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER VER/KEP L3/KEP IDC XXXX
19938 | Hazard | 3302703 | HAZARD | HAZARD | 2013-03-04 05:52 | 2013-03-04 07:00 | 2 | 68 | 4868401 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | MIKE HOLLIFIELD CALLED AND REPORTED HIS POWER IS OFF. HE REPORTS CUTOUT IS OPEN FOR TRANSFORMER.----TRANSFORMER FUSE BLOWN,----- LOOKED LIKE FUSE JUST BROKE. COD-2 ISO TF 37830272D20989 VER/HFP L3/HFP IDC XXXX
19939 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2016-01-17 18:43 | 2016-01-17 19:51 | 2 | 68 | 4627301 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED THE TRANSFORMER FUSE THAT HAD BROKE. VER/KEP
19940 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-01-02 20:29 | 2021-01-02 22:45 | 1 | 136 | 4844521 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | One of Hot Legs is melted at Trans, Will have to Climb pole and Resqueeze service and make new connection..Also had to repair bushing on transformer/ Opened Trans at 22:03 and Restored at 22:45./ Customer had part power originally no one else affected when opening transformer
19941 | Hazard | 3309003 | JEFF | VIPER | 2019-09-22 18:40 | 2019-09-22 20:56 | 1 | 136 | 4047421 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout manuel cust said ok to wait till daylight OPS # 037974741 Released by crew 077H14/ customer is out of town and relative taking care of the home said it would be fine to leave out until tomorrow./ ISO 37830417000037/ COD 1
19942 | Whitesburg | 3409503 | BURDINE | JENKINS | 2014-11-24 15:57 | 2014-11-24 17:05 | 2 | 68 | 4774171 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD BURNED OUT OF CUTOUT, REPLACED LEAD AND RESTORED POWER AT 1705 VER/HFP L3/HFP
19943 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-07-15 12:45 | 2008-07-15 15:01 | 1 | 136 | 52903-1 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303903//BAD 25KVA CSP RELEASED BY CREW 077S01 // VER/TOM IDC XXXX
19944 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2019-11-22 09:37 | 2019-11-22 10:45 | 2 | 68 | 4055841 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout
19945 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-06-13 16:47 | 2021-06-13 17:55 | 2 | 68 | 4729891 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
19946 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-01-06 04:37 | 2010-01-06 05:45 | 2 | 68 | 63033-1 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACING CUTOUT FUSE IDCC PN9 XXXX
19947 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-11-05 06:50 | 2012-11-05 09:06 | 1 | 136 | 4360001 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BLOWN.---- LOOKS LIKE NEW FUSE BROKE FOR NO REASON,--- POWER RESTORED. ///VER/CRB L/3 CRB IDC XXXX
19948 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2014-12-01 09:12 | 2014-12-01 11:28 | 1 | 136 | 4820411 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | FUSE ON BANK C -PH BLOWN, FUSE WAS ROTTON AND BROKE INTO POWER RESTORED VER/CRB
19949 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-02-20 18:21 | 2017-02-20 20:37 | 1 | 136 | 4410371 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | AT FRALEY FIELD POLE 92-4121 PUT AEP LOCK ON RED GATE BAD CLFUSE TRUCK TO POLE SEND TO BOBBY RELEASED BY CREW 078S08 VER/CRB L3/HFP HFPC LCD38830092B04121
19950 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2019-09-13 10:19 | 2019-09-13 11:25 | 8 | 66 | 4013091 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power bad connection at xfmr , opened xfmr at 11:15 to make repairs restored power at 11:25 L3/HFP
19951 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-06-08 12:00 | 2011-06-08 12:34 | 4 | 34 | H4267621 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED FUSE AT 1220HOT LINE CLAMP HAS PULL OFF TOP OF CUTOUT ON LINE FUSE, GOING TO OPEN OTHER LINE FUSE TO MAKE REPAIRS//VER/CRB IDC DUP TO OPEN OTHER FUSE XXXX
19952 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-10-31 20:44 | 2014-10-31 23:00 | 1 | 136 | 4678291 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL PULLED APART AT TRANSFOMER WILL RE-SPLICE NEUTRAL AND HOT LEGS IN SECONDARY//// RESPLICED NEUTRAL AND RE-DONE OLD SPLICE IN SECONDARY ///CHECKED VOLTAGE 120/120/240 EVERTHING IS GOOD NOW VER/HFP L3/HFP
19953 | Whitesburg | 3401301 | FLEMING | NEON | 2014-12-24 07:14 | 2014-12-24 09:30 | 1 | 136 | 4878671 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I CHANGED OUT SPLICE ON SERVICE MAST/ ISO 37830307000042// VER/BOW VER/DKG L3/DKGXXXX
19954 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-05-10 15:52 | 2013-05-10 17:00 | 2 | 68 | 4097031 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED 6T BROKEN LINK COD-2 ISO TF 38830222B00032 VER/HFP L3/HFP IDCC PN32 XXXX
19955 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-02-21 15:44 | 2019-02-21 18:00 | 1 | 136 | 4839011 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | C PHASE STEP DOWN OPEN ON POLE 37830164C40460//COD 1//C phase line side fuse failed on step down trans on 164-C-460.patrolled line,saw no hazards.restored power at 18:00.
19956 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-05-25 08:53 | 2013-05-25 11:09 | 1 | 136 | 4183251 | 136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNED DOWN DUE TO A FAILED SPLICE.// VER/DBM IDCC PN NULL XXXX
19957 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-10-23 07:24 | 2018-10-23 09:40 | 1 | 136 | 4313151 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection in service drop/// replaced bad connection and restored service 124/124/248/// only 1 customer affected L3/HFP
19958 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-07-23 13:14 | 2017-07-23 15:30 | 1 | 136 | 4164761 | 136 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR//I REPARED CONNECTION//RESTORED AT 15:30//COMPLETE//EM/ ISO 38820770B00073/ COD 1/ VER/BOW
19959 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-10-25 12:15 | 2008-10-25 14:30 | 1 | 135 | 58960-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD TRANSFORMER POLE 955C43. I HAVE CREW ON THE WAY. POLE 955C473 HAS TRANSFORMER ON IT THAT SERVES ANOTHER CUST. WE CAN SERVE CUST WITH SPAN OF 2-3 DROP FROM THAT POLE. SEND COPY OF THIS TO RON RYE PIKEVILLE. OLD TRANSFORMER WILL NEED TO BE REMOVED AND OLD SEC DROP. ANCHOR AND GUY WIRE MAY NEED TO BE INSTALLED ON SEC POLE 955C459. SENT EMAIL TO RON RYE & ENTERED MD..HFP IDC XXXX
19960 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2022-05-06 17:30 | 2022-05-06 19:45 | 1 | 135 | 4849451 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Nuetral burnt into in service drop///Repaired broken neutral and restored full power @ 19:45
19961 | Hazard | 3309302 | VICCO | JEFF | 2014-06-27 12:30 | 2014-06-27 14:45 | 1 | 135 | 4162461 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === REPLACED CUTOUT === POWER OK//COD 1// VER/DBM
19962 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2012-11-18 20:40 | 2012-11-18 22:55 | 1 | 135 | 4407121 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | NEED CREW TO INSTALL POWER TEMP--BAD NEUTRAL--PULLED METER TILL TEMP CAN BE INSTALLED RELEASED BY CREW 078S07 LARGE ALL ELECTRIC HOME./INSTALLED TEMP XFMR/PLEASE E-MAIL VEMULLINS A COPY OF TICKET/PLEASE CLOSE /THANKS/VEM VER/DKG IDCC TOF2001, ESTIMATED TIME OFF XXXX
19963 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-09-18 15:35 | 2014-09-18 17:50 | 1 | 135 | 4509521 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | CHECKED OPEN-WIRE SECONDARY AND FOUND NO PROBLEMS WITH IT. GUY WRAP RUSTED IN TWO AND ALLOWED GUY TO FALL INTO XFMR RISER. SECURED GUY WIRE AND RESTORED XFMR @ 17:50. SH VER/CRB
19964 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2017-08-03 16:55 | 2017-08-03 19:10 | 1 | 135 | 4221751 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | SOURCE SIDE PRIMARY METERING FUSE IS BLOWN WILL RE-FUSE/// BAD PRIMARY METERING /// TALKED TO CUSTOMER SAID WE CAN WORK TOMORROW 8/4/17/// TIM HALL SAID WOULD SEND CREW TOMORRW// CREATED IW #031427602/ ISO 37820219A30195/ COD 1/ VER/BOW
19965 | Pikeville | 3407103 | TOPMOST | KITE | 2022-09-12 11:05 | 2022-09-12 13:20 | 1 | 135 | 4870061 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Bad splice in service drop.// Repaired and restored @ 13:20
19966 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2019-01-02 15:00 | 2019-01-02 15:45 | 3 | 45 | 4623071 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT OPENED LINE @ 487-144 @ 1500 AND CLOSED @1545
19967 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-12-08 00:45 | 2008-12-08 01:00 | 9 | 15 | H55291-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3110903/// FOUND 1/0 SECONDARY LASH, BURNTED INTO, HAD TO OPEN TRANSFORMER ON POLE 1098-286, TO MAKE REPAIRS, ALL REPAIRS ARE MADE, AND EVERYTHING IS FINE AT THIS LOCATION VER/JHM L3/KEP IDCC DUP TO OPEN TRANSFORMER XXXX
19968 | Hazard | 3303901 | LESLIE | HYDEN | 2010-09-29 15:45 | 2010-09-29 18:00 | 1 | 135 | 55146-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA IS LEAKING NO OUTAGE AT THIS TIME RELEASED BY CREW 077S01 CSP TRANSFORMER REPLACED AND INSTALLED CUTOUT AND DUG UP THE SPILL JKC VER/KEP L3/KEP IDCC PN NULL XXXX
19969 | South Williamson | 3200301 | BELFRY | BELFRY | 2019-02-07 14:27 | 2019-02-07 16:42 | 1 | 135 | 4764051 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | replaced a bad secondary connection on 1014-B4-132.restored at 16;42.
19970 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-01-24 22:15 | 2013-01-24 23:00 | 3 | 45 | H4738501 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | XFMR RISER AND CONNECTIONS ARE MELTED //REWIRED XFMR// POWER IS RESTORED/// OFF 22:15 ON 23:00 ///VER/CRB L/3 CRB IDCC DUP TO OPEN TRANSFORMER XXXX
19971 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-03-08 11:00 | 2015-03-08 13:15 | 1 | 135 | 4166671 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS////////SERVE-IN SPLICE HAD 1 LEG BURNED INTO,MADE NECESSARY REPAIRS AND RESTORED.ALL OK PER CUST VER/KEP
19972 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-10-05 13:00 | 2010-10-05 13:27 | 5 | 27 | 57042-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PULLED XFMR OFF AT 13:00 HRS, PUT BACK ON AT 13:27//COD 5// VER/DBM IDC XXXX
19973 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-02-23 15:05 | 2019-02-23 17:20 | 1 | 135 | 4849861 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at an. no outage
19974 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-01-01 05:05 | 2008-01-01 07:20 | 1 | 135 | 52308-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402801// REPAIRED SERVICE DROP. SH VER/KEP IDC XXXX
19975 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-02-09 11:29 | 2022-02-09 12:14 | 3 | 45 | 4460721 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutral broke at pole 1126-A-351, will have to open XFM on pole 1126-A-77 to make repairs will keep up with times// pole 1126-A-351 rotted at ground level and needs changed out, and ROW needs cut// XFM on 1126-A-77 off @ 11:29 on @ 12:14// email sent to bill johnson ond corey farmer
19976 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2020-04-16 18:45 | 2020-04-16 19:30 | 3 | 45 | 4707091 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SAME AS 4668741--cc3--1845-1930--xfmr open to repair secondary pole
19977 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-12-29 13:00 | 2020-12-29 13:45 | 3 | 45 | 4832511 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | arrived on power quality, ch voltage and lugs at mtr base at time of arrival, voltage was 123 phase to grd, ph to ph, was 249. ch with beast cust srv drp showed to be good, then neighbor came out saying he had problems, recheck volt was 127 ph to grd, and 256 ph to ph, when and rework sec, still had same volt at transformer, crew req 25 kva 7200 120/240 can use truck Neighbor is fillind damage claims, Released by crew 078S06//NO OUTAGE TILL TRANS OPENED 1300
19978 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-08-16 22:43 | 2019-08-17 00:58 | 1 | 135 | 4898801 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | fuse out on 37830482A20497 restored @ 0058
19979 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2016-12-19 15:20 | 2016-12-19 16:05 | 3 | 45 | 4221371 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE, POWER RESTORED. VER/CRB
19980 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-05-11 17:15 | 2016-05-11 18:00 | 3 | 45 | H4201171 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION MID-SPAN IN LASH SECONDARY, T MORRIS AND CREW COMING TO HELP. ONLY 1 CUST WITH PART POWER, OPENED TRANSFORMER @ 17:15, CLOSED @ 18:00, POWER RESTORED./ ISO 37830223B00042/ COD 1/ VER/BOW
19981 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-07-27 19:45 | 2010-07-27 22:00 | 1 | 135 | 58187-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | APPEARS TO BE A BAD CUTOUT WILL CHANGE--POLE IS BURNED ABOUT 3/4 INTO CALLED FOR 1 MAN AND CROSSARM TO REPAIR//COD 1// VER/DBM IDCC PN79, ESTIMATED TIME OFF CHANGED FROM 1905 XXXX
19982 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-01-28 20:52 | 2015-01-28 23:07 | 1 | 135 | 4971411 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MD TO SHOW CUTOUT ON POLE 38830283D20064 HAS FAILED NOT POLE 3883283000064//INCORRECT CUST PREMISE// MADE MDC TO SHOW L/F ON POLE 38830283000090 OPEN LINE FUSE 283-90 REPLACE CUTOUT ,POWER RESTORED VER/CRB
19983 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-09-18 18:00 | 2019-09-18 20:15 | 1 | 135 | 4034471 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 srv drp burnted into at the weather head made repairs a this loc all is good at this time, time on 2015 by amg
19984 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-09-04 11:30 | 2012-09-04 12:15 | 3 | 45 | 4003911 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFOREMER FUSE WAS ROTEEN AND BROKEN, REFUSED AND POWER IS RESTORED AT THIS LOC AT 1215 ///VER/CRB L/3 CRB IDC XXXX
19985 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-02-13 02:45 | 2011-02-13 03:30 | 3 | 45 | 56485-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. REPLACED FUSE //VER/GAH IDC XXXX
19986 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-09-02 13:00 | 2022-09-02 15:15 | 1 | 135 | 4830791 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke 7.2 Cutout on pole 255-334 ///Truck Access Released by crew 077H12 replaed cutout power restored at 15:15
19987 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-05-20 16:45 | 2018-05-20 19:00 | 1 | 135 | 4383101 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired bad connection//COD 1
19988 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-03-20 16:45 | 2015-03-20 17:30 | 3 | 45 | 4213901 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CHECKING TAKEOFF POLE///SOMETHING IS ARCING ON POLE///FOUND BAD DEADEND INSULATOR BREAKING DOWN///MADE REPAIRS///COMPLETE BR COD-3 ISO LF 38830834C00001 VER/HFP L3/HFP
19989 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2022-01-18 17:30 | 2022-01-18 19:45 | 1 | 135 | 4383291 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke tran c/o--replaced tran c/o--allgood-in at 19:45--ds011822
19990 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-06-26 15:28 | 2008-06-26 17:43 | 1 | 135 | 54903-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHG CUTOUT VER/HFP IDC XXXX
19991 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2010-10-17 11:50 | 2010-10-17 12:35 | 3 | 45 | H60400-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN-WIRE-SECONDARY DOWN. CUSTOMERS SERVED FR XFMR 785-554 WERE NOT AFFECTED UNTIL I OPENED XFMR @ 11:50 TO MAKE REPAIRS. TWO CUSTOMERS HAD PART POWER AND THREE HAD FULL POWER. REPAIR UNDERWAY. ONE HOT CONDUCTOR PULLED OUT OF SLEEVE AT XFMR POLE. REPAIRED AND RE-SQUEEZED SECONDARY RISER CONNECTIONS. RESTORED @ 12:35. SH//VER/CRB IDC XXXX
19992 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2009-10-13 19:45 | 2009-10-13 20:30 | 3 | 45 | 61420-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL INVESTIGATE COMPLAINT/NUETRAL INTO ON ONE SERV DROP,HAVE TO OPEN XFR TO REPAIR/NEUTRAL OF SD RUBBED INTO ON HOT CON.MADE REPAIRS.ALL OK AFTERWARDS PER CUST//VER/CRB IDCC TOF1820 XXXX
19993 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2008-06-03 09:05 | 2008-06-03 11:20 | 1 | 135 | 54818-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3001402//, WE HAVE A BAD UNDERGROUND BETWEEN TRANSFORMER POLE AND METERBASE NEED UNDERGROUND CREW TO LOCATE AND SPLICE WIRE ,,,,CABLE IS ABOUT 160 FT. AND IS 4/0 RELEASED BY CREW 078S02 VER/HFP
19994 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2018-01-13 08:25 | 2018-01-13 10:40 | 1 | 135 | 4742731 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUST//CKD BREAKERS// bad connection at xfmr , made repairs restored power at 10:40..
19995 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-11-26 17:15 | 2012-11-26 18:00 | 3 | 45 | 4422311 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NO OUTAGE TRANSFORMER LEAKING OIL. I WILL KEEP UP WITH OFF ON TIMES WHEN CHANGING TRANSFORMER. OPENED TRANSFORMER UP AT 17:15 BACK ON AT 18:00 ///VER/CRB L/3 CRB IDC XXXX
19996 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-04-18 08:56 | 2018-04-18 11:11 | 1 | 135 | 4249321 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replacing fuse COD-1 ISO TF 38830182A00160
19997 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-09-19 20:03 | 2011-09-19 20:30 | 5 | 27 | 4885781 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD ROTTEN AND BROKEN I HAVE REPLACED AND POWER IS RESTORED AT THIS LOC COD-5 ISO TF 39831024A00102 VER/HFP L3/HFP IDC XXXX
19998 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-11-13 15:05 | 2016-11-13 17:20 | 1 | 135 | 4098131 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK REPAIRED/ ISO 38830147000056/ COD 1/ VER/BOW
19999 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-01-26 00:05 | 2010-01-26 02:20 | 1 | 135 | H1131441-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ABOUT 2-3 FOOT OF POLE BURNT OFF DUE TO BAD CUTOUT. I HAVE HOT LINE CLAMP OFF LINE AT POLE 180-63.. WE HAVE REPAIRS MADE EVERYTHING OK. //VER/GAH IDCC PN76 XXXX
20000 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-07-08 16:49 | 2015-07-08 19:04 | 1 | 135 | 4747071 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SECONDARY SLEEVE///REPAIRED SPLICE COMPLETE/ ISO 38830159000029/ COD 1/ VER/BOW
20001 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-03-08 08:45 | 2014-03-08 11:00 | 1 | 135 | 4460951 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE DROP HAS BURNED INTO AT SPLICE . WILL REPLACE SERVICE. VER/CRB
20002 | South Williamson | 3411401 | DEWEY | INEZ | 2013-11-13 09:00 | 2013-11-13 11:15 | 1 | 135 | 4034551 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE DROP VER/HFP L3/HFP
20003 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2011-06-23 09:46 | 2011-06-23 12:01 | 1 | 135 | 4398571 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONE OF 3 LATERAL FUSES BLOWN ON 941-B-75 (FUSES NOT ON MAP).BAD CUTOUT ON XFMR BANK POLE 941B510..SO WMSN LINE CREW NEARBY..WILL GET THEM TO REPLACE ALL 3 CUTOUTS ON POLE 941B510..// ENTERED MD...HFP AND INSTALLED FUSE ON MAP COD - 1 ISO LF 38820941B00075 VER/HFP L3/HFP IDC XXXX
20004 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-06-17 05:22 | 2008-06-17 05:49 | 5 | 27 | H66069-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OFF ON POLE 223-33, WILL HAVE TO OPEN LINE FUSE TO PUT LOOP BACK ON.MADE LOOP UP POWER RESTORED POLE 33 BETWEEN POLE 223-32 & 223-101 28 CUST OUT DUPLICATED THIS RECORD FOR LINE FUSE OUTAGE & CORRECTED CUSTOMER COUNTS. VER/HFP IDC XXXX
20005 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2015-12-29 10:48 | 2015-12-29 11:33 | 3 | 45 | 4572931 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPED FUSE TO SAFELY REPLACE CUTOUT POLE 46-2137 AND 2139 2- BAD CUTOUTS REPLACED VER/KEP
20006 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-10-22 07:15 | 2009-10-22 09:30 | 1 | 135 | 64144-1 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | FOUND BAD 110 CONNECTION ON X-FMR POLE 223-119. ALL POWER RESTORED AT 9:30. TIM SMITH // VER/DBM IDC XXXX
20007 | Whitesburg | 3401301 | FLEMING | NEON | 2016-05-19 12:25 | 2016-05-19 14:40 | 1 | 135 | 4235421 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED-RED BARREL SPLICE WAS BAD ON XFMR POLE. I REPLACED IT VER/CRB
20008 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-09-26 10:16 | 2018-09-26 10:31 | 9 | 15 | 4160361 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Lifted Hot tap to repair connection on pole 37830024D10527 Opened @ 1016 Closed @ 1031
20009 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-03-31 22:00 | 2015-03-31 22:45 | 3 | 45 | 4253301 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THE NEUTRAL IN XFMER BUSHING HAD BURNED INTO DUE TO LOOSE CONNECTION///OPENED XFMER ON POLE 809-14 @ 22:00 AND CLOSED @ 22:45///MADE REPAIRS///COMPLETE BR // COD-3 ISO TF 38830809A30014 VER/HFP L3/HFP
20010 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-10-19 10:00 | 2022-10-19 10:45 | 3 | 45 | 4042491 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Open XFMR to replace service drop (3COD) off at xxxx on at xxxxoff at 10am back on at 10:45.. replaced s/d.
20011 | Pikeville | 3402003 | KEYSER | MULLINS | 2019-10-18 09:00 | 2019-10-18 11:15 | 1 | 135 | 4165191 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot leg burndt into on customers service drop, spliced in new piece @1115.
20012 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-10-05 08:08 | 2016-10-05 10:23 | 1 | 135 | 4960771 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SINGLE ALL OUT BROKEN FUSE LINK REPLACED 6-T POWER IS ON KWB COD-1 IOS TF 38830198000163 VER/HFP L3/HFP
20013 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-12-27 16:09 | 2010-12-27 16:54 | 3 | 45 | 56300-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK COD-3 ISO TF 38830019B00017 VER/HFP L3/HFP IDC XXXX
20014 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2017-02-11 22:50 | 2017-02-12 01:05 | 1 | 135 | 4387031 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40T FUSE BAD CUTOUT POLE 67-A-464 . CHANGED ALL 3 CUTOUTS CLOSED IN FUSES EVERYTHING OK/// VER/DKM L3/HFP XXXHFP
20015 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-01-04 09:00 | 2009-01-04 11:15 | 1 | 135 | 51218-1 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3408303//, LINE FUSE STILL IN, GOING TO TOP OF MOUNTAIN TO CHECK XFORMER FUSE, XFORMER FUSE BLOWN, REFUSING IT, FUSE BROKE VER/TOM L3/TOM IDC XXXX
20016 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2016-05-15 19:15 | 2016-05-15 21:30 | 1 | 135 | 4221071 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTIONS AT THE TRANSFORMER ONE CUSTOMER AFFECTED. VER/TOM L3/TOM
20017 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2013-11-26 19:24 | 2013-11-26 21:39 | 1 | 135 | 4078051 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD NEUTRAL CONNECTION IN SERVICE DROP AT TRL POLE, REPAIRED CONNECTION. VER/SEF
20018 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2018-05-06 18:30 | 2018-05-06 20:45 | 1 | 135 | 4317661 | 135 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | called customer: no answer///connection bad on pole, repaired and all power restored at 20:45
20019 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2022-07-22 10:06 | 2022-07-22 12:21 | 1 | 135 | 4548011 | 135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. cutout busted @147-C-419, will be changing. 1221
20020 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2020-05-06 14:25 | 2020-05-06 16:39 | 1 | 134 | 4806691 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse open on 1016-c-98.no hazards seen.fuse failed.restored at 16;39.
20021 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2008-10-06 12:31 | 2008-10-06 14:45 | 1 | 134 | 53615-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP 3410601// 26633724 954-713410601// HOT TAP BURNT OFF ON POLE 954-71 MAKING REPAIRS NOW IDCC PN707 XXXX
20022 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-12-22 16:22 | 2008-12-22 18:36 | 1 | 134 | 62721-1 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411902// S/DROP HAS SHORTED OUT IN SPLICE. I AM GOING TO RESPLICE DROP. I SPLICED S/DROP.//COD 1// VER/DBM L3/KEP IDC XXXX
20023 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-05-19 06:16 | 2010-05-19 08:30 | 1 | 134 | 64922-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 15T FUSE BROKE. POLE 67A411. FUSED UP EVERYTHING OK.//VER/CRB IDC XXXX
20024 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2010-08-06 17:15 | 2010-08-06 18:22 | 2 | 67 | 50741-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP ON LATERAL FUSE ON POLE 1015C97....WILL REPLACE......//...REPLACED DOOR...RE-FUSED...POWER ON....JRV...08/06/10 COD-2 VER/HFP L3/HFP
20025 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-08-14 20:21 | 2010-08-14 22:35 | 1 | 134 | 54850-1 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST. SER. NEUT. HAS BURNED OPEN IN MIDSPAN SPLICE VER/KEP L3/KEP
20026 | Pikeville | 3413401 | GARRETT | GARRETT | 2014-04-07 11:16 | 2014-04-07 13:30 | 1 | 134 | 4581421 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT LOOKS LIKE FUSE BROKE. FUSED UP EVERYTHING OK. COD-1 ISO TF 37830041B00038 VER/HFP L3/HFP IDC XXXX
20027 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-11-10 09:01 | 2015-11-10 11:15 | 1 | 134 | 4423991 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR WAS BROKE ON CENTER PHASE OF THE PRIMARY METERING.. CHANGED DOOR AND RESTORED POWER AT 11:15.. COMPLETE RN VER/ARN
20028 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-02-07 20:58 | 2019-02-07 22:05 | 2 | 67 | 4765981 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad door on cutout, power restored at 22:05
20029 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2021-05-28 18:38 | 2021-05-28 19:45 | 2 | 67 | 4639931 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Repaired broken cutout
20030 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-08-06 15:46 | 2013-08-06 18:00 | 1 | 134 | 4628891 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE.REPLACED CUTOUT AND ARRESTOR.SERVICE RESTORED. VER/CRB L/3 CRB
20031 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-11-02 14:28 | 2018-11-02 15:35 | 2 | 67 | 4357241 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | secondary connection @ xfmer urnt off, replacedrepaired/ ISO 38830092A01016/ COD 2 L3/HFP
20032 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2013-07-12 12:07 | 2013-07-12 14:21 | 1 | 134 | 4513181 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLING BROKEN FUSE LINK POWER RESTORED 6-T KWB /// COD-1 ISO TF 39830902C00476 VER/HFP L3/HFP IDC XXXX
20033 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-03-31 09:01 | 2020-03-31 11:15 | 1 | 134 | 4547771 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connectionin service drop at trans 1132-172.replaced conection,restored power at 11:15
20034 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-09-20 08:06 | 2013-09-20 10:20 | 1 | 134 | 4869311 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT POLE 188/215 CREW ON WAY. MP COMP MP VER/CRB L/3 CRB
20035 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-09-06 11:16 | 2021-09-06 13:30 | 1 | 134 | 4213941 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT.////////REPLACED BROKEN PORCELIN CUTOUT WITH POLYMER TYPE
20036 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-10-07 15:31 | 2008-10-07 17:45 | 1 | 134 | 53933-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000201// REPLACED DEFECTIVE 15 KVA TRANSFORMER W / A NEW 25KVA TRANSFORMER // NO FETR PROVIDED IDC XXXX
20037 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2021-02-05 11:18 | 2021-02-05 13:32 | 1 | 134 | 4939531 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | making repairs to bad UG service///opened @ 11:18 Closed@13:32///only 1 cust was out for this at house 301///repairs made complete BR
20038 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-03-27 13:18 | 2018-03-27 14:25 | 2 | 67 | 4128271 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole failed @ pole 38830809A30838/ opened xfmr 38830809A30027 @ 1318 Closed @ 1425/ ISO 38830809A30027/ COD 2open transformer fuse on pole 38830809A30027 at 13:18. secondary pole 38830809A30838. is broke. looking over now. they are a new pole setting here already. going to try to transfer everything over./ MD DONE
20039 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-02-25 10:54 | 2008-02-25 12:01 | 2 | 67 | 50172-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3310501// STS TRANSFORMER OUT GOING TO REFUSED, FUSE BROKE// COD 2 - ISO/FLT 3783002900176// VER/TOM IDC XXXX
20040 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-11-12 09:21 | 2014-11-12 11:35 | 1 | 134 | 4721901 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200, 120/240, 25 KVA RELEASED BY CREW 078H12/ ISO 38830139C00005/ COD 1// VER/BOW L3/HFP
20041 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-07-26 09:46 | 2011-07-26 12:00 | 1 | 134 | 4623731 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | MADE REPAIRS TO SERVICE NEUTRAL PULL LOOSE VER/KEP IDCC CNT4 XXXX
20042 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2020-12-02 07:41 | 2020-12-02 09:55 | 1 | 134 | 4737921 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service nuetral and hot leg burnt into. One customer out. Made repairs and restored @ 9:55
20043 | Hazard | 3308002 | JACKSON | PANBOWL | 2018-01-24 09:44 | 2018-01-24 10:51 | 2 | 67 | 4769981 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called customer: no answer fuse pull into
20044 | Pikeville | 3402002 | KEYSER | STONECOAL | 2018-12-25 19:36 | 2018-12-25 21:50 | 1 | 134 | 4598101 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer: customer saw his service drop arc smells smoke. Hot leg connection burndt into on a splice and burndt customers service down, made repairs @2150. L3/HFP
20045 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-07-08 14:58 | 2015-07-08 17:12 | 1 | 134 | 4746501 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIR HOT LEG IN SD VER/CRB
20046 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2019-03-11 07:31 | 2019-03-11 09:45 | 1 | 134 | 4969661 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | customer has connections burnt into on sec. pole 147-222..will make repairs..restored
20047 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-01-24 14:01 | 2012-01-24 16:15 | 1 | 134 | 4289991 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION IN SERVICE APPEARS TO BE BAD. WILL RE-WORK. REPLACED 40 FT SERVICE THAT WAS DAMAGED. SH VER/HFP L3/HFP IDC XXXX
20048 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-09-21 07:51 | 2011-09-21 10:05 | 1 | 134 | 4891551 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | AWP WORK ZONE SET UP //// 078H05 REPLACING XFMER./POWER RESTORED @ 10:05 J. HEMLEPP VER/KEP IDC XXXX
20049 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-09-19 08:18 | 2008-09-19 09:25 | 2 | 67 | 65405-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3010602// 1 FUSE OUT IN TRANSFORMER BANK//REPLACED BAD ARRESTOR//COD 2// VER/DBM IDC XXXX
20050 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-02-14 12:56 | 2018-02-14 15:10 | 1 | 134 | 4840491 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmer hanging by primary riser going to secure and change out xfmer. xfmer chaged and back to normal
20051 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-07-09 15:13 | 2021-07-09 17:27 | 1 | 134 | 4879501 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE IT///////////REPLACED&RESTORED POWER
20052 | Pikeville | 3402003 | KEYSER | MULLINS | 2016-05-18 12:17 | 2016-05-18 13:24 | 2 | 67 | 4230091 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT WILL CLIMB POLE AND CHANGE CUTOUT R RAY/// REPAIRS MADE POWER RESTORED AT 13:24 VER/CRB
20053 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-04-05 16:46 | 2015-04-05 19:00 | 1 | 134 | 4278321 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV IN @ CUSTOMER ENTRANCE CABLE. MADE NEW CONNECTIONS. ELEC TO CHECK BKR BOX FOR CUST EQUIPMENT/ ISO 38830118D16048/ COD 1
20054 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-04-25 18:46 | 2014-04-25 21:00 | 1 | 134 | 4635501 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT NO TRUCK RELEASED BY CREW 078S08///CHANGED CUTOUT,ARRESTOR & BRACKET///PWR ON @ 21:00///TBL TKT COMP. COD-1 ISO TF 38830115C00193 VER/HFP L3/HFP
20055 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-11-11 08:18 | 2015-11-11 09:25 | 2 | 67 | 4427121 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE LINK APPEARS TO HAVE BROKEN. RESTORED @ 9:25. SH VER/CRB
20056 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2022-06-01 12:15 | 2022-06-01 13:22 | 2 | 67 | 4992931 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | had a fire here monday. when they made the line back hot this transformer on pole 402-B-340 did not come back on. CSP transformer is bad.. talked to customer and they are ok with us waiting until tomorrow morning to replace transformer Released by crew 077S11
20057 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-03-17 16:14 | 2016-03-17 17:21 | 2 | 67 | 4859861 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE ISO 38830248000049 CCC *** 2 VER/AWD
20058 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-12-11 19:33 | 2009-12-11 20:40 | 2 | 67 | 57855-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T XFMR FUSE RELEASED BY CREW 078H12//COD 2// VER/DBM
20059 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-10-08 14:25 | 2017-10-08 16:39 | 1 | 134 | 4422151 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECLOSER OPEN ON POLE 306-211, BAD ARRESTERS ON POLE 306-242 TOOK LINE OUT, CUT ARRESTERS IN CLEAR RESTORED POWER AT 16:39./ ISO 37830306000211/ COD 1/ VER/BOW L3/HFP XXXHFP
20060 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-01-08 08:07 | 2015-01-08 10:21 | 1 | 134 | 4918481 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD CONNECTION IN SERVICE REPLACING BOTH SERVE ENDS/ONLY 1 CUSTOMER// VER/ ADH
20061 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-04-24 10:34 | 2009-04-24 12:48 | 1 | 134 | 56220-1 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WIRE PULLED OUT OF SERVE-END AT TRANS. POLE. I AM GOING TO REWORK LEADS. I REWORKED CONNECTION.//3411801//VER/CRB IDC XXXX
20062 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2017-07-27 22:14 | 2017-07-28 00:28 | 1 | 134 | 4191131 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 445-130,WILL HAVE TO OPEN LINE FUSE ON POLE 445-50 TO ISOLATE. OPENED AT 23:53 MADE REPAIRS RESTORED POWER AT 00:28.. 37830445000130 VER/AWD
20063 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2009-04-12 09:06 | 2009-04-12 11:20 | 1 | 134 | 51597-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | , ON SITE, NEUTRAL BROKE IN SERVICE DROP, MAKING REPAIRS, SEND A COPY OF THIS TO R RYE IN PIKEVILLE ENG DEPT, CUST HAS 3 HEAT PUMPS, HAS TWO SPANS OF 2/3 SECONDARY AND A SERVICE DROP AWAY FROM XFORMER//3404301//VER/CRB IDC XXXX
20064 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-01-29 17:18 | 2008-01-29 18:25 | 2 | 67 | 60764-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3407401// FUSE OUT ON TRANS POLE 6T. WILL BE CHECKING. LOOKS LIKE FUSE BROKE. ISO/FLT - 38831098C00737 COD 2// VER/TOM IDC XXXX
20065 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-06-09 21:58 | 2021-06-10 00:12 | 1 | 134 | 4699681 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad XCO on pole 1149-109, made repairs and restored
20066 | Pikeville | 3408101 | SALISBURY | PRINTER | 2008-08-30 20:26 | 2008-08-30 22:40 | 1 | 134 | 57900-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 26039958. POLE IS LOCATED ON SIDE OF HILL. I WILL BE REPLACING CUTOUT. CHANGED CUTOUT EVERYTHANG OK. SEND COPY OF THIS TO ENG PIKEVILLE RON RYE. CROSS ARM IS BURNT ABOUT HALF WAY INTO. NEEDS TO BE CHANGED. VER/PDP IDC XXXX
20067 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-10-08 16:27 | 2011-10-08 17:34 | 2 | 67 | 4958361 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR FUSE BLOWN//// XFMR LEAD LAYING ON BOLT, WENT TO GROUND BLOWING FUSE, REPOSITIONED LEADS, POWER RESTORED. ///VER/CRB IDC XXXX
20068 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-01-14 14:23 | 2009-01-14 15:30 | 2 | 67 | 54993-1 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3401702// HOT TAP FAILED.//COD 2// VER/DBM L3/KEP
20069 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2013-08-25 13:05 | 2013-08-25 14:12 | 2 | 67 | 4705381 | 134 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPEN WIRE SECONDARY DOWN--OPENED TRANSFORMER AT 13:32--CALLED L MCCOY TO ASSIST--BAD CONECTION AT TRANSFORMER #4 CU OPENWIRE DOWN VER/SEF IDCC TOF1332, CNT8, MCCDL XXXX
20070 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-06-09 10:41 | 2011-06-09 12:55 | 1 | 134 | 4274491 | 134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#40319748//15KVA 7200 NEED MAT HANDLER AND PICK-UP//CLOSE GATE BECAUSE OF GOATS//VER/CRB IDC XXXX
20071 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-08-04 13:49 | 2012-08-04 16:02 | 1 | 133 | 4896371 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED APART, REFUSED TRANS. AT 16:02.//COD 1// VER/DBM IDC XXXX
20072 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-09-01 16:07 | 2011-09-01 18:20 | 1 | 133 | 4781511 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTIONS IN THE UNDERGROUND PEDESTAL VER/KEP IDC XXXX
20073 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-11-03 07:02 | 2014-11-03 09:15 | 1 | 133 | 4694791 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SERVICE DROP, ONLY ONE CUSTOMER AFFECTED./ ISO 37820265B00026/ COD 1 CCC*****// VER/BOW
20074 | Whitesburg | 3401301 | FLEMING | NEON | 2016-06-15 08:20 | 2016-06-15 10:33 | 1 | 133 | 4348991 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE NEUTRAL BROKE AT THE SECONDARY POLE, I REPAIRED IT VER/HFP L3/HFP
20075 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-09-04 12:07 | 2017-09-04 14:20 | 1 | 133 | 4328551 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY BROKE ON 223-11 TAKING XFMER OUT 38830223000011GUY BROKE ON 223-11 TAKING XFMER OUT/ REPAIRED GUY XFMER BACK IN ON 223-11 @ 1420/ PLEASE CLOSE TICKET/MLH VER/AWD
20076 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2016-08-02 10:47 | 2016-08-02 13:00 | 1 | 133 | 4723091 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED-RED SPLICE BURNED UP , I REPLACED IT VER/HFP L3/HFP
20077 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-11-05 18:17 | 2013-11-05 20:30 | 1 | 133 | 4013091 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE DROP BURNED INTO AT A SPLICE. I AM GOING TO REPLACE DROP. I REPLACED SERVICE DROP. VER/HFP L3/HFP
20078 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2019-11-19 14:37 | 2019-11-19 16:50 | 1 | 133 | 4048141 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced 3 serve ends, all good
20079 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2011-10-20 16:20 | 2011-10-20 18:33 | 1 | 133 | 4005021 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND SEND TO BILL FRALEY RELEASED BY CREW 078S08--BAD NEUTRAL----//EMAILED TO B REYNOLDS IDCC CNT4 XXXX
20080 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-03-27 16:28 | 2016-03-27 18:41 | 1 | 133 | 4885351 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 420-528 , WILL NEED 4 WHEELER TO GET TO CABIN, CUSTOMER SAID IT WAS OK TO LEAVE IT FOR NOW. 7200 CUTOUT.. CREATED OPS # 035904996 RELEASED BY CREW 077S11/ ISO 37830420C40528/ COD 1/ VER/BOW
20081 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-10-10 14:19 | 2020-10-10 16:32 | 1 | 133 | 4542391 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 1057-D-310,Causing line fuse to blow on 81-301,Will make repairs and restore service.Restored at 16:32...
20082 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-02-22 12:54 | 2019-02-22 15:07 | 1 | 133 | 4844061 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 93-15/ No trucks to pole in field. GH/// Send to Ron Virgin Released by crew 078H04--crew on site---changed out bad cutout--tbl tkt comp---rmv
20083 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-07-20 18:06 | 2011-07-20 20:19 | 1 | 133 | 4569191 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE BURNT UP CHGED TO 2/3 VER/HFP L3/HFP
20084 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-09-23 07:12 | 2014-09-23 09:25 | 1 | 133 | 4521241 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RESTORED @ 9:25. SH/// ISO 38830875A00221/// COD 1// VER/BOW
20085 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-09-15 17:17 | 2020-09-15 19:30 | 1 | 133 | 4466811 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20t fuse out pole 1097-d-372 cutout broken guywire broken. cable company been work in here also may have cut a tree on the line. also looks like mowing machine cut guy wire into. i replaced cutout repaired guywire closed line fuse back in @ 19:30
20086 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-02-25 08:52 | 2015-02-25 11:05 | 1 | 133 | 4079661 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE IN SERV ==== REPAIRED SPLICE === POWER OK/ VER/BOW
20087 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-06-22 08:57 | 2015-06-22 11:10 | 1 | 133 | 4637191 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CURTOUT DOOR BURNED OUT ON POLE 37820073A00556 BACK ON HILL // WILL REPLACE// CUTOUT BAD ALSO // REPLACED // POWER RESTORED @ 11:10/ ISO 37820073A00556/ COD 1/ VER/BOW
20088 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-05-28 22:55 | 2009-05-29 01:08 | 1 | 133 | 62583-1 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/YHFP BAD CUTOUT L3/HFP IDC XXXX
20089 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-10-07 07:12 | 2019-10-07 09:25 | 1 | 133 | 4106431 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM is blown will refuse and try to close.Cutout is broke we will change..Changed bad cutout and refused XFM at 09:25 and restored service.
20090 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2008-03-24 13:09 | 2008-03-24 15:22 | 1 | 133 | 60289-1 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308601//SERVICE CONNECTION IS BURNED OFF AT TRANSFORMER.// VER/TOM IDC XXXX
20091 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2015-03-03 20:47 | 2015-03-03 23:00 | 1 | 133 | 4095531 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON UG, 80 VOLTS. CREW REQD. RELEASED BY CREW 078S07..CUST PROBLEMS.WILL RE-CHECK WITH CUST AND ELECTRICIAN IN THE MORNING//BAD UG//ALSO BAD BREAKER VER/CRB L3/HFP XXX
20092 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-12-27 17:25 | 2010-12-27 19:38 | 1 | 133 | 56321-1 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN FAILED BURNING ALL THREE CONDUCTORS APART AT ENTRANCE ( 2/3 ALUM ) RELEASED BY CREW 074S03 VER/HFP L3/HFP IDC XXXX
20093 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2009-02-14 16:17 | 2009-02-14 18:30 | 1 | 133 | 61621-1 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | VER/HFP BAD CURRENT LIMETER FUSE L3/HFP
20094 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2015-07-02 15:32 | 2015-07-02 17:45 | 1 | 133 | 4710821 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SERVICE DROP///REPAIRS MADE///COMPLETE BR// VER/ ADH
20095 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-07-08 06:17 | 2010-07-08 08:30 | 1 | 133 | 63237-1 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE MELTED OUT AGAIN..PRIMARY BUSHING ON XFMR IS CRACKED..NEED TO WRITE UP JOB TO CHG XFMR CUTOUT AND ARRESTOR..BB//VER/CRB IDC CHANGED CAUSE FROM OTHER XXXX
20096 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-01-03 12:38 | 2017-01-03 14:51 | 1 | 133 | 4264901 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRF IS OUT,WILL RE-FUSE///////19.9 CUTOUT BROKEN,WILL REPLACE IT//////////REPLACED BROKEN CUTOUT&RESTORED 37820026000020 VER/AWD L3/HFP XXXHFP
20097 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-03-25 12:02 | 2009-03-25 14:15 | 1 | 133 | 61392-1 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401703// THE ARRESTER WAS BLOWN ON THIS POLE.//COD 1// VER/DBM IDC XXXX
20098 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-11-17 13:51 | 2008-11-17 16:04 | 1 | 133 | 65997-1 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP OLD CUTOUT BROKE WILL REPLACE RELEASED BY CREW 078S02 IDC XXXX
20099 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-02-21 21:27 | 2016-02-21 23:40 | 1 | 133 | 4745371 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED 40 T LINE CUTOUT AT POLE 38831123A00036 ( NOT SHOWN ON MAP ) ISOLATING XFMF POLE 36 ALSO AT 22:50 AND CLOSED AT 23:40 , ALL WORK COMPLETE / GXJ
20100 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-11-28 12:37 | 2019-11-28 14:50 | 1 | 133 | 4099891 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out door bad, replace all three cut out doors,
20101 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-06-12 12:35 | 2011-06-12 14:48 | 1 | 133 | 4301611 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 44-206 4/3 SERVICE BURNT DOWN OVERLOAD 300A SERVICE ON 4/3 SERVICE DROP// VER/DBM IDC XXXX
20102 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2020-01-06 11:12 | 2020-01-06 13:25 | 1 | 133 | 4217131 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced xfr connections
20103 | South Williamson | 3411401 | DEWEY | INEZ | 2021-02-05 19:27 | 2021-02-05 21:40 | 1 | 133 | 4940911 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burned down//making repairs//repairs made//restored at 21:40//complete//em
20104 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-03-08 11:00 | 2008-03-08 11:07 | 19 | 7 | 54915-1 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400303//SERVICER ENROUTE// BURN UP CUTOUT DOOR 19.9, OPEN DISC TO REPLACE CUTOUT DOOR. OFF AT 11:00 ON AT11:07//COD 19// VER/DBM IDCC CDC92 XXXX
20105 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-01-13 15:17 | 2016-01-13 17:30 | 1 | 133 | 4617931 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE. REPLACED AND RESTORED @ 17:30. SH VER/CRB
20106 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-11-29 15:07 | 2009-11-29 17:20 | 1 | 133 | 50664-1 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP SERVE-END SHORTED OUT IN MID SPAN AND BURNED NEUTRAL IN SERVICE DROP INTO. I AM GOING TO REPLACE DROP. I CHANGED DROP FROM A 4/3 TO A 2/3 DROP. CUSTOMER SAID MICROWAVE OVEN WAS DAMAGED. I TOLD THEM TO CALL IN TOMORROW AND REPORT IT. L3/HFP IDC XXXX
20107 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-01-17 13:32 | 2008-01-17 15:45 | 1 | 133 | 57394-1 | 133 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3403003//NEED TO REPLACE SERVICE DROP/VER/CRB IDC XXXX
20108 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-08-20 11:05 | 2013-08-20 13:18 | 1 | 133 | 4682451 | 133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE, REFUSED XMF APR AT 1318 CLOSE TICKET COD-1 ISO TF 38830600000112 VER/HFP L3/HFP IDC XXXX
20109 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-12-07 13:49 | 2008-12-07 14:55 | 2 | 66 | 55164-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308603// SERV-IN CONNECTION IS BURNED OFF AT TRANSFORMER - . VER/TOM L3/TOM IDC XXXX
20110 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-06-02 18:48 | 2009-06-02 21:00 | 1 | 132 | 61302-1 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE, CUSTOMER HAS DAMAGE EQUIPMENT VER/KEP L3/KEP
20111 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-05-25 20:03 | 2012-05-25 22:15 | 1 | 132 | 4831931 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, NEED ONE MAN BIG BUCKET, AND 25KVA 19.9 XFMR, RESTORED POWER AT 2215//COD 1// VER/DBM IDC XXXX
20112 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2013-06-07 10:28 | 2013-06-07 12:40 | 1 | 132 | 4235391 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON BANK POLE 809 907// CREW ON THERE WAY// CHANGED CUTOUT RISERS FIXED // POWER RESTORED COMPLETE TT VER/KEP IDC XXXX
20113 | Hazard | 3303901 | LESLIE | HYDEN | 2010-08-27 16:46 | 2010-08-27 18:58 | 1 | 132 | 61300-1 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | PARTIAL POWER ON 305 MORGAN LN MTR#533760519 PER JAMES AMBURGY LEAD OUT OF XFMR REPAIRED// VER/DBM IDC XXXX
20114 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2011-06-29 09:19 | 2011-06-29 10:25 | 2 | 66 | 4435931 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | //VER/CRB IDCC FP NULL XXXX
20115 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-04-11 15:03 | 2009-04-11 17:15 | 1 | 132 | 51524-1 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED INTO AT WEATHERHEAD,WILL REPAIR.REPAIRED CONNECTION,ALL OK AFTERWARDS//3411801//VER/CRB IDC XXXX
20116 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-03-30 17:58 | 2015-03-30 20:10 | 1 | 132 | 4244771 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD A LOOSE CONNECTION @ POLE 38830834D00237 BETWEEN SEC. AND SERVICE////MADE REPAIRS///COMPLETE BR VER/HFP L3/HFP
20117 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-01-09 12:03 | 2019-01-09 14:15 | 1 | 132 | 4650851 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Jim Holliday reports primary meter fuse is open and cannot get reading on meter due to fuse being open,. arrestor bad, changed cutout and arrestor, complted AS BUILT. all power restored @ 14:15
20118 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2020-04-30 13:03 | 2020-04-30 15:15 | 1 | 132 | 4781341 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | have a bad c/o on 901-4637, can get truck to pole, i lifted htsp on 901-4636, de engerizing pri, just single pole tap, no grd or tgs placed, send to Brain Ramey CREW REQ Released by crew 078S06///complete BR
20119 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-01-22 10:34 | 2010-01-22 11:40 | 2 | 66 | 57959-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY ONE CUSTOMER ON TRANSFORMER--REPLACED CUTOUT//VER/CRB IDCC CNT1, FEC49 XXXX
20120 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-12-18 21:44 | 2013-12-18 22:50 | 2 | 66 | 4174691 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-517 BAD CUTOUT VER/SEF L3/HFP
20121 | Whitesburg | 3312902 | JENKINS | JENKINS | 2020-02-10 08:04 | 2020-02-10 09:10 | 2 | 66 | 4386951 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power clamp burnt off , made repairs restored power at 09:10. L3/HFP
20122 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2021-05-19 13:12 | 2021-05-19 13:23 | 12 | 11 | 4599961 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Crews opened TR to make repairs to broken neutral Off at 1312 On at 1323
20123 | Hazard | 3420001 | SOFT SHELL | VEST | 2016-09-18 12:14 | 2016-09-18 13:20 | 2 | 66 | 4903581 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT . CLOSED XFMR BACK @ 13:20 VER/KEP
20124 | Pikeville | 3410602 | E.PRESTON | LANCER | 2009-08-19 10:18 | 2009-08-19 12:30 | 1 | 132 | 50080-1 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | VER/HFP REPLACED CUTOUT DOOR COD-1 ISO LF 38830980000113 L3/HFP IDC XXXX
20125 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-10-06 09:03 | 2008-10-06 11:15 | 1 | 132 | 53539-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308402// PART POWER, SPLICE BAD IN SERVICE DROP VER/TOM IDC XXXX
20126 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-01-04 11:08 | 2012-01-04 13:20 | 1 | 132 | 4232661 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE HAS SHORTED OUT IN MID SPAN AND BURNED ONE HOT LEG INTO. I AM GOING TO REPLACE SERVICE DROP. I REPLACED SERVICE DROP. FAULT HAD ALSO BURNED NEUTRAL IN SERVICE DROP INTO, BUT CUSTOMER SAID HE DIDNT SEEM TO HAVE ANY DAMAGES. VER/KEP IDC XXXX
20127 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-07-24 19:05 | 2014-07-24 21:17 | 1 | 132 | 4285571 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE WILL REPLACE VER/CRB
20128 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-12-08 13:10 | 2014-12-08 13:54 | 3 | 44 | 4846841 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SERVICER OPENING LINE FUSE 248-229 TO REPAIR BROKEN CROSSARM//COD 3// OPENED 13:10, CLOSED 13:54// VER/ ADH
20129 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-08-05 13:02 | 2013-08-05 15:14 | 1 | 132 | 4624221 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 120240,7.2, FUSE BLEW WITH ARRESTER AND RISER IN ,CLEARED ARRESTER DROPED RISERS STAYED IN, PUT RISERS BACK IN FUSE STAYED BUT HAVE 70/ 140 AT METERBASE, TRUCK OK, METER PULLED RELEASED BY CREW 078H08//CUST AGREED TO WORK ON OPS VER/CRB L/3 CRB
20130 | Pikeville | 3407103 | TOPMOST | KITE | 2019-12-06 14:07 | 2019-12-06 14:51 | 3 | 44 | 4131561 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | looks like 6t fuse broke fused up everything ok
20131 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-01-26 09:35 | 2011-01-26 10:08 | 4 | 33 | 64457-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT, UP ON HILL, GOING TO TRY FUSE, LOOK LIKE FUSE PULL IN TWO IDC XXXX
20132 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-06-05 16:01 | 2016-06-05 18:13 | 1 | 132 | 4310091 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT ON POLE 1039-17 , FUSE WAS BROKE . CLOSED XFMR BACK @ 18:13 VER/CRB
20133 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-01-24 09:50 | 2012-01-24 10:12 | 6 | 22 | 4288871 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4287031 // OPENED FUSE IN ORDER TO MAKE REPAIRS TO FAILED CUTOUT // COD 6// VER/DBM IDC XXXX
20134 | Hazard | 3310502 | HADDIX | CANOE | 2013-12-17 06:06 | 2013-12-17 06:28 | 6 | 22 | H4167061 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BROKE ON POLE 169-C-66 AND IS DOWN IN LASH // OPENED LINE FUSE AT POLE 169-C-276 AT 0606, MADE REPAIRS AND CLOSED AT 0628 BAD LINE FUSE CUTOUT ON POLE 37830169C00066 OPEN LINE FUSE ON POLE 169-276 AT 0606 AND CLOSED AT 0628 DUP OF 4167061 VER/HFP L3/HFP IDC XXXX
20135 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-10-30 16:34 | 2013-10-30 18:46 | 1 | 132 | 4976511 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR POPPED OFF POLE TOP PIN LETTING CONDUCTOR FLOAT ON POLE 28-135..REPLACED INSULATOR, TIED CONDUCTOR BACK AND RE-FUSED WITH 30T..SERVICE RESTORED//COD 1// VER/DBM
20136 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-12-06 08:24 | 2012-12-06 09:30 | 2 | 66 | 4446291 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT. CLOSE TICKET PER FIELD//MDH VER/KEP IDC XXXX
20137 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2021-07-08 12:16 | 2021-07-08 13:22 | 2 | 66 | 4873181 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cut out on pole 1017A-372.made repairs and back in at 13:22
20138 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-03-12 14:18 | 2014-03-12 16:30 | 1 | 132 | 4473361 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ POLE 278-51 NEED LINE CREW TO REPLACE TRUCK OK,REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TTICKET THANKS.BT COD-1 ISO TF 38830278000051 VER/HFP L3/HFP
20139 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-07-25 19:08 | 2012-07-25 21:20 | 1 | 132 | 4828921 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 19.9 REPLACED XMF, APR AT 2120 CLOSE TICKET. DWEST VER/ARN
20140 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2019-08-30 20:34 | 2019-08-30 22:46 | 1 | 132 | 4966931 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Pole # 513B/158 lighting arrester went bad send to tech. to change cut in clear power ok now
20141 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-04-19 11:26 | 2011-04-19 12:10 | 3 | 44 | 60574-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORM. FUSE 8T BROKE LOOKS LIKE IT WAS OLD AND BROKE POWER RESTORED 12:10 VER/KEP IDC XXXX
20142 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2009-04-03 20:28 | 2009-04-03 22:40 | 1 | 132 | 64944-1 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3001102// STS WR 29234660 BAD UNDER GROUND CALLED LLOYD M. RELEASED BY CREW 078S08/PUT POWER TEMP ON TIL NEXT WEEK SEND INFO TO DAN HUFF// 22:40 VER/TOM L3/TOM IDC XXXX
20143 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2021-02-27 12:24 | 2021-02-27 13:30 | 2 | 66 | 4262201 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broken neutral in service drop and melted hot connection//made repaired voltage good//restored @ 1330 ticket complete
20144 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-01-12 15:28 | 2014-01-12 17:40 | 1 | 132 | 4275481 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED ON XFMR POLE. REWORKED ALL XFMR CONNECTIONS AND RESTORED @ 17:40. SH// VER/DBM L3/HFP
20145 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2019-07-17 16:33 | 2019-07-17 18:45 | 1 | 132 | 4723451 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad 12kv c/o
20146 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-07-09 05:58 | 2017-07-09 08:10 | 1 | 132 | 4098641 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE ON POLE 279-27 OPEN, CLOSED BACK IN AND POWER RESTORED AT 8:10. FUSE BROKE VER/KEP
20147 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-06-28 11:58 | 2013-06-28 14:10 | 1 | 132 | 4421111 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACING #4 SERVICE WITH #2 SERVICE. ONLY THIS CUSTOMER AFFECTED. VER/CRB L/3 CRB
20148 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-05-18 07:00 | 2020-05-18 09:12 | 1 | 132 | 4847351 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse link broken. changing
20149 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-07-09 12:24 | 2011-07-09 13:30 | 2 | 66 | 4496811 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON TRANSFORMER BANK, REPLACED CUTOUT COD-2 ISO TF 38830182D06052 VER/HFP L3/HFP IDC XXXX
20150 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-02-17 14:15 | 2010-02-17 14:48 | 4 | 33 | H58637-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | I HAVE A TRANSFORMER LEAD BURNT INTO ON POLE 37830072B00072 I WILL REPLACE BOTH LEADS, BAD TRANSFORMER CREW ENROUTE TO REPLACE/// I RESTORED POWER AT 12:40 I WILL HAVE TO DE-ENERGIZE AGAIN WHEN CREW ARRIVES TO CHANGE TRANSFORMER OUT./// PULLED OFF AT 14:15 BACK ON AT 14:48 TIM MCCOY RELEASED BY CREW 074H10 VER/KEP L3/KEP IDC XXXX
20151 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-05-07 10:54 | 2011-05-07 12:00 | 2 | 66 | 4016611 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | STS WR # 39868149 CHANGED BAD C/O. COD-2 ISO TF 37830272B11303 VER/HFP L3/HFP IDC XXXX
20152 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-03-06 08:53 | 2010-03-06 11:05 | 1 | 132 | 63314-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE HAD FROOZEN OUT OF SERVE-END ON TRANS. POLE. I RESPLICED WIRE. VER/KEP L3/KEP IDC XXXX
20153 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2008-10-20 09:43 | 2008-10-20 10:05 | 6 | 22 | 57237-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP RELATED TO ORDER 57179-1 ...OUTAGE TO MAKE REPAIRS FOR THAT ORDER. CREW OPENED TRANSFORMER FUSE TO ALLOW THEM TO REPAIR SECONDARY. IDC XXXX
20154 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-11-02 14:54 | 2015-11-02 17:06 | 1 | 132 | 4403891 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD NEUTRAL CONNECTIONS @ XFM//// RESQEEZED CONNECTIONS AND FIXED CUSTOMERS PROBLEM////120/120/240 VER/CRB
20155 | Whitesburg | 3312901 | JENKINS | KONA | 2020-12-11 14:48 | 2020-12-11 17:00 | 1 | 132 | 4762021 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | we changed xfmr
20156 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2020-05-26 17:00 | 2020-05-26 19:12 | 1 | 132 | 4908631 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | customer still has full power ,,,,30-6 windstream pole 230-154 broke in the ground ,,,aep has open wire and a service and duplex and guy wire coming off pole ,,,no trucks ,,CREW REQUIRED Released by crew 078S05 crew on site FETR 19:00 opened xfmr @ 17:00 on @ 19:12 please close ticket LRM
20157 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2009-02-02 13:33 | 2009-02-02 15:45 | 1 | 132 | 54695-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN ALL REPAIRS MADE POWER BACK ON AJB
20158 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-11-24 08:34 | 2011-11-24 09:40 | 2 | 66 | 4112471 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN, NOT BLOWN. --- POWER RESTORED.///VER/CRB IDC XXXX
20159 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2015-09-13 09:12 | 2015-09-13 11:24 | 1 | 132 | 4234081 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE @ 271-194 .OPENED LINE FUSE @ 272-73 @ 10:20///REPAIRS MADE LINE FUSE 272-73 IN @ 11:24// VER/ ADH
20160 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-07-23 14:18 | 2008-07-23 15:24 | 2 | 66 | 58952-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN CREW 077H01 7200 CUTOUT AND ARRESTOR CHANGED OUT IDCC CNT1 XXXX
20161 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-03-05 09:20 | 2013-03-05 09:32 | 11 | 12 | 4871131 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED RECLOSER TO ALLOW THEM TO SAFELY REPLACE BURNT OFF BASKET ON RECLOSER POLE 190-146 // COD-27 ISO OCR38830190000146 // OPENED AT 0920 AND CLOSED AT 0932// V ER/TOM L3/TOM IDC XXXX
20162 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-01-18 11:26 | 2022-01-18 13:38 | 1 | 132 | 4380761 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | service neutral pulled loose ,,repairs made complete
20163 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2009-06-04 14:27 | 2009-06-04 16:39 | 1 | 132 | 59474-1 | 132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | SERVICE NEUTRAL BURN INTO AT POLE NUMBER 916-B-104. CALLED FOR CREW.BAD CONNECTION ON SECONDARY POLE .// VER/DBM
20164 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2020-12-23 15:28 | 2020-12-23 17:40 | 1 | 132 | 4797961 | 132 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broken neut in sd repairs made
20165 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2021-11-24 09:46 | 2021-11-24 11:57 | 1 | 131 | 4121351 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout on 38830091C46100 broke, Lifted ht @ pole 38830091C00209 @ 11:30, tagged to Gh Restored @11:57 Please add cutout on 91-c4-6100 to mapping, 10T//MDR complete
20166 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-11-05 16:09 | 2010-11-05 18:20 | 1 | 131 | 53289-1 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE NEUTRAL AND RESET CSP//VER/CRB IDC XXXX
20167 | South Williamson | 3411401 | DEWEY | INEZ | 2022-08-07 16:37 | 2022-08-07 18:48 | 1 | 131 | 4699781 | 131 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection bad on xfmr pole 696-72//one hot leg almost burned into//repairs made//restored at 18:48//complete//em
20168 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2015-10-25 01:09 | 2015-10-25 03:20 | 1 | 131 | 4374121 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BROKE GROWING THRU TREE POWER RESTORED KWB RESTORED 0320 CUSTOMER MISMAPPED MD FILED VER/KEP
20169 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-06-08 17:24 | 2014-06-08 19:35 | 1 | 131 | 4995901 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN WILL RE-FUSE.///// CUTOUT IS BROKE WILL CHANGE/// CHANGED BROKEN CUTOUT AND RESTORED SERVICE @ 19:35//COD 1// VER/DBM
20170 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-07-06 14:10 | 2019-07-06 16:21 | 1 | 131 | 4666651 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Current limiting fuse burndt into @140-C-349, got replaced @1621.
20171 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-07-08 07:39 | 2012-07-08 09:50 | 1 | 131 | 4590461 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT DOOR ,BURNT IN HALF REPLACED AND POWER RESTORED KWB//COD 1
20172 | Hazard | 3420001 | SOFT SHELL | VEST | 2014-08-28 12:04 | 2014-08-28 14:15 | 1 | 131 | 4433071 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKEN WILL HAVE TO OPEN AND ISOLATE AND CHANGE./// OPENED AT 13:45 CLOSED AT 14:15. POWER RESTORED COD-1 ISO TF 37830133000133 VER/HFP L3/HFP
20173 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-07-17 17:29 | 2012-07-17 19:40 | 1 | 131 | 4751311 | 131 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND SPLIT BOLTS ON TRANSFORMER NEUTRAL, POLE GROUND, CASE GROUNDED AND ALSO FOUND CRACK CUTOUT, I HAVE ALL REPAIRS MADE AND EVERYTHING IS OK AT THIS LOC, AT 1940 TIME
20174 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-03-08 15:09 | 2022-03-08 17:20 | 1 | 131 | 4590271 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 255-46... Power restored at 17:20
20175 | Hazard | 3420001 | SOFT SHELL | VEST | 2014-04-30 20:49 | 2014-04-30 23:00 | 1 | 131 | 4653511 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 133-144, CALLING FOR HELP VER/CRB
20176 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-06-10 08:59 | 2020-06-10 11:10 | 1 | 131 | 4989581 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed midspan in service. Made repairs and restored @ 11:10. sh
20177 | Hazard | 3309302 | VICCO | JEFF | 2020-10-29 11:09 | 2020-10-29 13:20 | 1 | 131 | 4596431 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Send to R.Maggard need 7200V cutout and T/bracket will need to block road Released by crew 077S03
20178 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-10-05 17:55 | 2010-10-05 20:06 | 1 | 131 | 57174-1 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGED XFMR ///VER/CRB IDC XXXX
20179 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-07-09 17:57 | 2015-07-09 20:08 | 1 | 131 | 4757141 | 131 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE IN @ POLE ON HT LEG/ ISO 38830044D16054/ COD 1
20180 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-08-08 06:19 | 2011-08-08 08:30 | 1 | 131 | 4677501 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1.6T FUSE BAD CUTOUT DOOR BURNT INTO. REPLACED DOOR FUSED UP EVERYTHING OK//COD 1// VER/DBM IDC XXXX
20181 | Hazard | 3303901 | LESLIE | HYDEN | 2019-01-27 08:02 | 2019-01-27 10:13 | 1 | 131 | 4725611 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPLACED SPLICES ON 1/0 SERVICE
20182 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-01-19 19:40 | 2009-01-19 21:51 | 1 | 131 | 58425-1 | 131 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL DETERMINE PROBLEMSERVE-IN CONNECTOR HAD FROZEN OUT ON POLE,MADE REPAIRS,ALL OK AFTERWARDS//3411801//VER/CRB L3/KEP
20183 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-08-11 14:39 | 2008-08-11 16:50 | 1 | 131 | 50998-1 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD FUSE BROKEN - AND CHANGED METER VER/TOM IDC XXXX
20184 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-03-31 09:16 | 2022-03-31 11:27 | 1 | 131 | 4700301 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 19.9 cutout, manual. I have help on the way. This pole isnt on the maps, it is a one pole tap that appears to come from pole 37830154000149.
20185 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-08-26 21:04 | 2019-08-26 23:15 | 1 | 131 | 4949371 | 131 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 19.9 xfm. cutout broke on bank pole 190-360.have one other that is cracked and needs replaced.please send copy to PR and tech to have job written up to replace.
20186 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-07-07 16:52 | 2011-07-07 19:03 | 1 | 131 | 4482951 | 131 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE CONNECTED WITH SPLIT BOLTS. SPLIT BOLTS RUSTED AND SERVICE LEG BECAME HOT AND BURNT INN-TO. MADE REPAIRS TO BOTH HOT LEGS AT MAST. CUSTOMER VOLTAGE IS 246, 123, AND 123. POWER RESTORED 19:03. 7/07/2011. J.S.B.//VER/CRB IDC XXXX
20187 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-02-06 07:34 | 2009-02-06 09:45 | 1 | 131 | 56084-1 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3001201// SERVICE DROP BAD AT SPLICE VER/KEP L3/KEP IDC XXXX
20188 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-06-18 13:10 | 2018-06-18 15:21 | 1 | 131 | 4616521 | 131 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad squeeze on. all good now. pls close. tre/ ISO 38830140B00469/ COD 1
20189 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-05-09 07:59 | 2015-05-09 10:10 | 1 | 131 | 4405541 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE IN @1010// VER/ ADH
20190 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2020-04-27 08:44 | 2020-04-27 10:55 | 1 | 131 | 4756131 | 131 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at pole, repaired
20191 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-07-09 09:22 | 2013-07-09 11:33 | 1 | 131 | 4491121 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFR TO RE-FUSE,POSSIBLY BAD SURGE ARRESTOR,WILL RE-FUSE///////SURGE ARRESTOR FAILED,REMD IT AND RE-FUSED,ALL OK AFTERWARDS COD-1 ISO TF 38821034000006 VER/HFP L3/HFP IDC XXXX
20192 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-12-15 09:26 | 2018-12-15 11:37 | 1 | 131 | 4567711 | 131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout, chging.. L3/HFP
20193 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2010-06-03 17:43 | 2010-06-03 19:53 | 1 | 130 | 56061-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFRMER CUTOUT...CAN REPLACE, WITH TRUCK....//....REPLACED CUTOUT...POWER RESTORED.....JRV....06/03/10//COD 1// VER/DBM IDC XXXX
20194 | Hazard | 3309302 | VICCO | JEFF | 2019-01-24 08:05 | 2019-01-24 10:15 | 1 | 130 | 4715651 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service was burnt into, made repairs
20195 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-04-19 07:15 | 2014-04-19 09:25 | 1 | 130 | 4617931 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNED DN IN SPLICE ONLY ONE CUSTOMER AFFECTED VER/CRB
20196 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2014-08-14 14:08 | 2014-08-14 14:18 | 13 | 10 | 4369441 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY LEAD BURNT INTO IN CONNECTION AT MASK WILL HAVE TO OPEN BANK OF XFMRS ON POLE 449-678 TO ISOLATE .. OPENED XFMR AT 14:08 MADE REPAIRS RESTORED POWER AT 14:18// COD 13// VER/ ADH
20197 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-10-06 17:00 | 2008-10-06 19:10 | 1 | 130 | 53638-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308402//XFMR LEAKING BAD, CREW TO REPLACE LEAKING XFMR. CREW WILL CALL FOR TICKET// FETR 2000//COD 1//OPENED XFRMR @ 1700//BACK ON @ 1910// VER/DBM IDC XXXX
20198 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-10-16 09:15 | 2011-10-16 11:25 | 1 | 130 | 4987281 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN THE SERVICE DROP// VER/DBM IDC XXXX
20199 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-11-19 13:50 | 2014-11-19 14:55 | 2 | 65 | 4746491 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 38830070B43617 BAD LA/ CUTOUT CHGED POLE 38830070B43612 30T 2-CUSTS VER/CRB
20200 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-02-08 13:07 | 2011-02-08 13:20 | 10 | 13 | 55313-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW OPENED LINE FUSE TO ALLOW THEM TO SAFELY REPLACE INSULATORS THEY FOUND BROKEN /// COD-10 ISO LF 37830098D00634 // VER/HFP L3/HFP IDC XXXX
20201 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-07-07 12:10 | 2012-07-07 14:20 | 1 | 130 | 4572941 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR BAD, FUSE BLOWN ON POLE 102-27, REPLACED XFMR & REFUSED TAP RESTORED POWER
20202 | Hazard | 3301101 | CHAVIES | CHAVIES | 2020-02-06 16:15 | 2020-02-06 17:20 | 2 | 65 | 4371621 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 146-8. restored power at 17:2037830071C20029
20203 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-03-07 14:25 | 2009-03-07 15:30 | 2 | 65 | 56036-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT.//3000201//VER/CRB IDC XXXX
20204 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-12-30 07:30 | 2009-12-30 09:40 | 1 | 130 | 65774-1 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END FROOZE OUT. I RESQUEEZED CONNECTIONS. ONLY 1 CUSTOMER WAS AFFECTED. IDCC CNT3 XXXX
20205 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-05-18 14:45 | 2010-05-18 16:55 | 1 | 130 | 64763-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35173793 // BAD XFMR RELEASED BY CREW 077S01 COD-3 VER/HFP L3/HFP IDCC PN4, CNT3 XXXX
20206 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2019-09-13 08:05 | 2019-09-13 09:10 | 2 | 65 | 4012461 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | xfmer restored in bank.
20207 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-02-23 08:15 | 2017-02-23 09:20 | 2 | 65 | 4415591 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O DOOR BAD--REPLACED-ALLGOOD--DS022317 38830162A00114/2 VER/AWD L3/HFP XXXHFP
20208 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2013-04-10 16:05 | 2013-04-10 17:10 | 2 | 65 | 4996021 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-4635 BAD CUTOUT 6T FUSE CHGED CUTOUT COD-2 ISO PO @ 38830044C24635 VER/HFP L3/HFP IDC XXXX
20209 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-02-28 16:20 | 2009-02-28 17:25 | 2 | 65 | 52572-1 | 130 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | CUTOUT | 3308502//REPLACED BAD CUTOUT COD-2 VER/KEP L3/KEP IDC XXXX
20210 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-03-12 19:08 | 2010-03-12 21:18 | 1 | 130 | 65809-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT.//COD 1// VER/DBM IDC XXXX
20211 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-03-11 13:37 | 2022-03-11 14:42 | 2 | 65 | 4600641 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout reported by Kenny Napier change broke cutout
20212 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-07-13 15:10 | 2010-07-13 16:15 | 2 | 65 | 65805-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 35959780 // NO OUTAGE , NEUTRAL CONNECTINS ON XFMR BANK MELTING DOWN, GOING TO SHUT MILL DOWN AT 15:00 TO MAKE REPAIRS.. SEND TO CECIL SEXTON RELEASED BY CREW 077S11 OPENED BANK AT 1510 CLOSED AT 1615 COD-2 VER/HFP L3/HFP IDC XXXX
20213 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-07-20 13:20 | 2015-07-20 15:30 | 1 | 130 | 4917371 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMER FUSE LINK BROKE///REFUSED AT 15:30///COMPLETE BR VER/CRB
20214 | Whitesburg | 3312902 | JENKINS | JENKINS | 2015-06-22 16:55 | 2015-06-22 19:05 | 1 | 130 | 4640661 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR WILL NEED CREW, MAY HAVE TO WAIT UNTIL TOMORROW. CREATED OPS ORDER# 032060404 TO REPLACE BAD XFMR. RELEASED BY CREW 077S11//SERVICER TALKED TO CUST//ONLY 1 CUST //SENT TO G.WHITAKER//B.LNDON AND J. MULLINS VER/CRB
20215 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-05-08 12:10 | 2011-05-08 13:15 | 2 | 65 | 4019661 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR 39869756//NO CREW REQUIRED REPLACED FUSE DOOR COD-2 ISO TF 38830175000099 VER/HFP L3/HFP IDC XXXX
20216 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2010-03-31 13:14 | 2010-03-31 15:24 | 1 | 130 | 56520-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | STS WR # 34477939 //#4 CU SEC DOWN, TRUCK APPROACH, TALKED TO R MARCUM, HECSAID TO SEND THIS TO JOEY REED RELEASED BY CREW 080S01 VER/HFP L3/HFP AJB
20217 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-02-14 14:18 | 2021-02-14 15:23 | 2 | 65 | 4051761 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Xfm riser burnt up///Replaced riser and restored service @ 15:23
20218 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-02-28 08:18 | 2018-02-28 09:23 | 2 | 65 | 4889351 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | COD 2// Replaced the transformer fuse that had broke. Power is restored.
20219 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-01-26 18:09 | 2011-01-26 20:19 | 1 | 130 | 65569-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUDE BLOWN/// FUSE BROKE, REFUSED POWER RESTORED//COD 1 // VER/DBM IDC XXXX
20220 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-09-11 08:55 | 2014-09-11 10:00 | 2 | 65 | 4488271 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1123-7567 6T FUSE BROKE/// ISO 39831123D47567/// COD 2// VER/BOW
20221 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-03-19 15:10 | 2012-03-19 16:15 | 2 | 65 | 4593941 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FETR 1600. LMR. SERVICER OUT OF RANGE. ///VER/CRB IDC CHANGED START TIME FROM 1148 3/19 CHANGED COUNT FROM 1 XXXX
20222 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-03-09 10:51 | 2011-03-09 11:56 | 2 | 65 | 52072-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, HAVE CREW ON THE WAY TO HELP ME TO CHANGE IT, HAVE CUTOUT CHANGED AND POWER IS RESTORED AT THIS LOC VER/KEP IDC XXXX
20223 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2013-11-06 09:30 | 2013-11-06 11:40 | 1 | 130 | 4014191 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE REPAIRED VER/CRB
20224 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-08-13 18:50 | 2010-08-13 21:00 | 1 | 130 | 54463-1 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPLICE BURNED OPEN IN SER. BURNING 1 HOT LEG AND NEUT. INTO I CHANGED OUT S/D.//VER/CRB
20225 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-05-23 10:47 | 2014-05-23 12:57 | 1 | 130 | 4744571 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHECKED VOLTAGE AT CUST METER BASE 150/300.. OTHER XFMRS ON SAME LINE 120/240.. NEED 25KVA 7200 XFMR.. TRUCK CAN POSSIBLE BE BACKED TO POLE THROUGH BARN LOT.. CUST NOT HOME RELEASED BY CREW 078H22/CREW ON SITE/FETR1300/VEM/REPAIRS COMPLETE/POWER RESTORED TO ALL CUST 1257/PLEASE CLOSE TICKET/THANKS/VEM COD-1 ISO TF 38830090000311 VER/HFP L3/HFP
20226 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-05-27 21:25 | 2014-05-27 22:30 | 2 | 65 | 4940781 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | NO CREW REQUIRED REPLACED ARRESTOR AND CUTOUT/ON POLE 102-9001 VER/KEP
20227 | Pikeville | 3407103 | TOPMOST | KITE | 2022-08-17 13:51 | 2022-08-17 14:56 | 2 | 65 | 4756261 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrester will make repairs
20228 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-04-22 08:30 | 2011-04-22 10:40 | 1 | 130 | 61909-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR 39668222// BROKEN XFORMER FUSE. VER/TOM L3/TOM IDC XXXX
20229 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-11-20 08:40 | 2017-11-20 09:45 | 2 | 65 | 4587951 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | Fuse link appears to have broken. Restored @ 9:45. sh
20230 | South Williamson | 3200301 | BELFRY | BELFRY | 2012-01-10 09:00 | 2012-01-10 10:05 | 2 | 65 | 4244291 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ANOTHER BROKEN XFMR CUTOUT..CAN REPLACE.//.REPLACED BROKEN CUTOUT..POWER ON NOW.JRV..01/10/12 VER/KEP IDC XXXX
20231 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-02-18 12:50 | 2022-02-18 15:00 | 1 | 130 | 4511841 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 19.9 xfm cutout on pole 697-97.will need bucket to make repairs.restored.
20232 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-12-16 10:05 | 2011-12-16 12:15 | 1 | 130 | 4182181 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER ON ONE OF THE SERVICE PHASE CONDUCTORS. I REPLACED THE CONNECTION// VER/DBM IDC XXXX
20233 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-02-19 16:00 | 2019-02-19 18:10 | 1 | 130 | 4808121 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TWO BAD CUTOUTS 283-55 AND 283-113, MAKING REPAIRS RESTORED @ 1910bad cutout all pwr restored
20234 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-05-01 18:50 | 2014-05-01 19:55 | 2 | 65 | 4655921 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNT UP WILL REPLACE. REPLACED CURRENT LIMITING FUSE RESTORED SERVICE @19:55 VER/CRB
20235 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2012-10-11 23:00 | 2012-10-12 00:05 | 2 | 65 | 4133781 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. ///VER/CRB L/3 CRB IDC XXXX
20236 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2016-01-09 14:59 | 2016-01-09 15:25 | 5 | 26 | 4597281 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RESTORED VER/CRB
20237 | Paintsville | 3401802 | INDEX | HOSPITAL | 2020-12-08 10:05 | 2020-12-08 12:15 | 1 | 130 | 4753521 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 12:15. sh
20238 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2018-02-06 15:27 | 2018-02-06 17:37 | 1 | 130 | 4809711 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service burned dn
20239 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-05-05 11:35 | 2009-05-05 12:40 | 2 | 65 | 55162-1 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT MADE REPAIRS COD-2 VER/KEP L3/KEP IDC XXXX
20240 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2016-08-21 12:40 | 2016-08-21 13:45 | 2 | 65 | 4821671 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY BUSHING WAS LOOSE CAUSING PART POWER.. CLEANED WIRE AND RE-TIGHTENED BUSHING CUST SAYS EVERYTHING IS OK NOW.. PLEASE CLOSE TICKET CY/ ISO 39831098D00498/ COD 2/ VER/BOW
20241 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-09-13 09:50 | 2011-09-13 12:00 | 1 | 130 | 4863501 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFORMER, TRUCKS TO POLE. RELEASED BY CREW 078S01..POWER BACK ON @ NOON //VER/CRB IDCC TOF0913 ESTIMATED TIME OFF XXXX
20242 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2015-04-28 09:45 | 2015-04-28 11:55 | 1 | 130 | 4372131 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORM FUSE BROKE REFUSE POWER RESTORED VER/CRB
20243 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2013-03-24 23:32 | 2013-03-25 01:42 | 1 | 130 | 4953271 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE //VER/GAH IDC XXXX
20244 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2020-01-09 05:20 | 2020-01-09 06:25 | 2 | 65 | 4226551 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link appears to have broke. Restored @ 6:25. sh
20245 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2016-07-24 16:53 | 2016-07-24 19:03 | 1 | 130 | 4673771 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR F IS OUT,WILL RE-FUSE///////RE-FUSED AND RESTORED,APPEARED FUSE SIMPLY ROTTED INTO VER/AWD
20246 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-01-26 22:25 | 2017-01-26 23:30 | 2 | 65 | 4336101 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT/ CHANGED/ POWER RESTORED 2330/ COD 2 **CCC MD DONE/ VER/BOW L3/HFP XXXHFP
20247 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-02-28 10:05 | 2012-02-28 11:10 | 2 | 65 | 4512831 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED CUTOUT--TRANSFORMER OFF 10:05 ON 11:10 IDC CHANGED ISO POLE FROM 37830173A20233 AND COUNT FROM 3 XXXX
20248 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2018-07-10 11:20 | 2018-07-10 13:30 | 1 | 130 | 4757621 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lifted hot tap at 1120. Need crew-called D Massey/restored 1330
20249 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2013-06-17 11:35 | 2013-06-17 13:45 | 1 | 130 | 4355791 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN SERV TO FIX, REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/HFP L3/HFP
20250 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-02-07 18:32 | 2011-02-07 20:42 | 1 | 130 | 55100-1 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN SERVICE DROP SHORTED OUT WITH HOT CONDUCTOR AND BURNED INTO. I SPLICED WIRE.//VER/CRB IDC XXXX
20251 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-09-01 10:15 | 2021-09-01 12:25 | 1 | 130 | 4193391 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | fixed bad spot in secondery wire. this service needs upgraded. the drop is about 500 ft long and both secondery lift poles are rotten. please send to a tech// email sent to pat thovson
20252 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-01-22 21:55 | 2019-01-23 00:05 | 1 | 130 | 4706091 | 130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Neutral burnt into in service drop will make repairs/// replaced burnt up neutral connection in service drop and everything is ok now 120/120/240/// Send copy to Peggy Wysong/// Only 1 customer affected//emailed to p wysong//cod 1 L3/HFP
20253 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-07-27 09:41 | 2017-07-27 11:51 | 1 | 130 | 4184881 | 130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830523D30371. REPLACING CUTOUT, APR AT 1151 CLOSE TICKET/ ISO 38830523D30371/ COD 1/ VER/BOW
20254 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-03-11 19:21 | 2013-03-11 21:30 | 1 | 129 | 4899151 | 129 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | HOT LEAD ON SERVICE DROP HAD BURNED IN TWO AT TRANSFORMER POLE..D LEWIS 3-11-13 VER/KEP IDC XXXX
20255 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-10-24 08:01 | 2017-10-24 10:10 | 1 | 129 | 4490831 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTIONS BURNED INTO ON POLE 830-162///I REPAIRED CONNECTIONS//RESTORED AT 10:10//COMPLETE/EM VER/AWD L3/HFP XXXHFP
20256 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-06-10 06:31 | 2010-06-10 08:40 | 1 | 129 | 59567-1 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POWER OFF NOW.....CURRENT LIMITING FUSE IS BURNT UP, ON TOP OF XFRMER....WILL REMOVE, AND TRY XFRMER FUSE.....//.....REMOVED BURNT UP CUURENNT LIMITING FUSE....TESTED XRFMR...GOOD.....CLOSED FUSE...POWER ON NOW.....JRV.....06/10/10 VER/KEP L3/KEP
20257 | Whitesburg | 3314401 | MAYKING | ERMINE | 2022-08-06 11:06 | 2022-08-06 13:15 | 1 | 129 | 4691211 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Hot secodnary on ground billy preece made per Mike Hatfield,. Broken C/O on pole 37830426B30794, opened LF on pole 37830426B00612 to climb and make repairs.Hot secodnary on ground billy preece made per Mike Hatfield,. Broken C/O on pole 37830426B00122, opened LF on pole 37830426B00612 to climb and make repairs.. All repairs have been made, replaced C/O, cut down abandonned secondary. COMPLETE.
20258 | Hazard | 3309301 | VICCO | REDFOX | 2015-12-26 12:06 | 2015-12-26 14:15 | 1 | 129 | 4562061 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT, POWER RESTORED// VER/ ADH
20259 | Hazard | 3309302 | VICCO | JEFF | 2011-12-26 10:19 | 2011-12-26 12:28 | 1 | 129 | 4202321 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE HAS BURNT INTO, 4/3 SERVICE BURNT INTO AT SPLICE, REPAIRED //VER/GAH IDCC CNT6, CDC89 XXXX
20260 | Pikeville | 3408101 | SALISBURY | PRINTER | 2015-03-20 15:12 | 2015-03-20 17:21 | 1 | 129 | 4213961 | 129 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BURNT INTO IN SERVICE DROP /// WILL REPAIR//// REPAIRED NEUTRAL IN SERVICE AND RESTORED SERVICE @ 17:21//// EVERYTHING OK NOW 124/124/248//// ONLY 1 CUSTOMER AFFECTED VER/HFP L3/HFP
20261 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-06-29 10:21 | 2009-06-29 12:30 | 1 | 129 | 50680-1 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | THE CURRENT LIMITING FUSE FAILED. VER/KEP L3/KEP
20262 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-01-22 12:26 | 2019-01-22 14:35 | 1 | 129 | 4704411 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 37830409000067 LINE FUSE OUT ON 37830409000021 // ENTERED MD FOR CUST ON WAGONWHEEL L3/HFP
20263 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-05-25 09:48 | 2020-05-25 11:57 | 1 | 129 | 4902841 | 129 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | A phase line fuse open on pole 181-27.. repairs made and restored @ 1157
20264 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2017-11-23 14:11 | 2017-11-23 16:20 | 1 | 129 | 4598181 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfmr cutout, ALL WORK COMPLETE / GXJ
20265 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-09-29 20:51 | 2013-09-29 23:00 | 1 | 129 | 4897451 | 129 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE-IN CONNECTION ON XFR POLE,REPLACD ALL W SQUEEZONS,ALL OK AFTERWARDS VER/CRB L/3 CRB IDC XXXX
20266 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-04-06 11:54 | 2016-04-06 14:03 | 1 | 129 | 4057991 | 129 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | POLE 70-1085 LOOKS LIKE UNDERGROUND BAD DISCONNECTED SERVICE AT METER RELEASED BY CREW 078S08//OPS ORDER BEING MADE VER/CRB
20267 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-04-09 14:53 | 2013-04-09 17:02 | 1 | 129 | 4991541 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SQUEEZE BURNED OPEN ON TRANSFORMER RISER.REPAIRS MADE.D LEWIS 4-9-13.SEND THIS TO TIM HALL.THE RISERS ON THIS XFMR HAS BEEN VERY HOT.MAY NEED TO REPLACE RISERS OR XFMR.//COD 1//EMAILED TO TIM HALL// VER/DBM IDC XXXX
20268 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-11-01 09:54 | 2009-11-01 12:03 | 1 | 129 | 54622-1 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR TO RE-FUSEHAD TO REPLACE BROKEN CUTOUT,ALL OK AFTERWARDS VER/KEP L3/KEP IDC XXXX
20269 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-07-20 08:41 | 2020-07-20 10:50 | 1 | 129 | 4186241 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replaced bad xfmer and closed back in @10:50// complete TG
20270 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2020-04-27 09:36 | 2020-04-27 11:45 | 1 | 129 | 4756621 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burned down . will replace. replaced service that burned down at splice
20271 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-08-10 12:31 | 2010-08-10 14:40 | 1 | 129 | 52017-1 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 75 KVA CUST WILLING TO WAIT TILL WE GET A XFMR AND SEND CREW TO REPLACE VER/HFP L3/HFP IDC XXXX
20272 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-03-31 14:03 | 2015-03-31 16:12 | 1 | 129 | 4248001 | 129 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | INSTA LINK PULLED LOOSE AT XFMR ON SECONDARY NEUTRAL.CONTRACTORS HUNG THIS XFMR YEARS AGO..APPEARS WATER MAY HAVE FROZEN IN CONNECTION DURING WINTER BREAKING OPEN CONN.WIND TODAY PULLED LOOSE. CUST HAD OPEN NEUTRAL..REPLACED 6 INSTA LINKS..(AKA SERVE ENDS..)./ ISO 38830801000098/ COD 1/ VER/BOW
20273 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-11-18 12:51 | 2013-11-18 15:00 | 1 | 129 | 4053411 | 129 | PARTIAL POWER | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE LOOSE CAUSE THIS PROBLEM, WAITING ON CREW TO COME WITH BIG BUCKET TO REMOVE GUY WIRE, IT IS SPATTING AGAINST BPHASE CUTOUT. GUY WIRE HAS BEEN REMOVED AND POWER IS RESTORED AT THIS LOC AT 1500 VER/CRB
20274 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-09-22 14:21 | 2014-09-22 16:30 | 1 | 129 | 4519801 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKEN.RE FUSED VER/CRB
20275 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-03-24 07:46 | 2011-03-24 09:55 | 1 | 129 | 58534-1 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//COD 1// VER/DBM IDC XXXX
20276 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-10-29 23:40 | 2017-10-30 01:49 | 1 | 129 | 4512541 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DISP DUE TO PREDICTED TEMPS CUTOUT GATE BURNED UP/// VER/DKM L3/HFP XXXHFP ACBC FEC49
20277 | South Williamson | 3411401 | DEWEY | INEZ | 2020-03-29 11:01 | 2020-03-29 13:10 | 1 | 129 | 4522911 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken xfmr cutout on pole 38830744B00256 // repairs made and restored @ 1310
20278 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2020-05-26 15:36 | 2020-05-26 17:45 | 1 | 129 | 4909961 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Transformer on pole 380A-14 bad. Replaced transformer and power restored at 17:45
20279 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-06-16 19:35 | 2019-06-16 21:44 | 1 | 129 | 4515431 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer no answerneed 1 a lineman ,material handler 25 kva 7200 to 120/240 & cutout
20280 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-12-07 19:46 | 2008-12-07 21:55 | 1 | 129 | 55228-1 | 129 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3311101// SECONDARY CONNECTION OPENED ... MADE REPAIRS, RESTORED AT 21:55 // VER/TOM L3/TOM IDC XXXX
20281 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2018-10-15 13:32 | 2018-10-15 15:41 | 1 | 129 | 4254931 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o-replaced-in at 15:41-allgood-ds101518 L3/HFP
20282 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-10-21 14:47 | 2020-10-21 15:30 | 3 | 43 | 4574021 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 1515bad 12 kv door. replaced door. restored
20283 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-05-28 20:26 | 2020-05-28 22:35 | 1 | 129 | 4923481 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o pole 20-6044. hot tap lifted @ 20-6012 isolating bad c/o.repairs made all cust restored @ 2235 please close ticket thanks.bt
20284 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-04-02 22:44 | 2015-04-03 00:53 | 1 | 129 | 4261301 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ON SITE/BAD CUTOUT/FETR0115/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0053/PLEASE CLOSE TICKET/THANKS/VEM COD-1 ISO TF 38830351000165 VER/HFP L3/HFP
20285 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-01-26 11:52 | 2021-01-26 12:35 | 3 | 43 | 4894821 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout changed, restored @ 12:35
20286 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-09-25 20:51 | 2017-09-25 23:00 | 1 | 129 | 4389141 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830185000305-BROKE C/O--REPLACED-ALLGOOD-DS092517/// VER/DKM
20287 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-08-26 17:41 | 2014-08-26 19:50 | 1 | 129 | 4426081 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION ON XFMR.TOOK XFMR OFF AT 19..12.BACK ON AT 19.50//COD 1 (+ 6 SEE H4426081) // VER/DBM
20288 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-05-11 09:43 | 2017-05-11 11:52 | 1 | 129 | 4779671 | 129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQD. BAD 15 KVA, NO 6-WHEELER, NO TRUCK RELEASED BY CREW 078S05CREW REQD. BAD 15 KVA, NO 6-WHEELER, NO TRUCK . CREATED OPS ORDER, SENT TO BRENT TACKETT. OPS #:030083222//SENT TO LINE DEPT VER/CRB
20289 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-07-04 23:16 | 2021-07-05 00:20 | 2 | 64 | 4856811 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout. time on 00:20/ 38830163000193/ 2
20290 | Pikeville | 3421001 | BREAKS | CITY | 2022-10-30 09:18 | 2022-10-30 11:26 | 1 | 128 | 4078261 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a hot leg and neutral into in service drop,Will be making repairs..Restored 11:26..
20291 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2021-06-04 08:37 | 2021-06-04 10:45 | 1 | 128 | 4667191 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral was broke in service drop near weather head. Customer stated box truck got caught on tv drop and caused damage. I de-energized service @ 10:10 to repair conductor and restored to full power @10:45. This customer is also mismapped and actually feeds from pole 38830954B40093.
20292 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-04-27 15:32 | 2014-04-27 16:36 | 2 | 64 | 4639451 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , REPLACED CUTOUT APR AT 1636 CLOSE TICKET//COD 2// VER/DBM
20293 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-06-07 16:58 | 2021-06-07 18:02 | 2 | 64 | 4682311 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN,WILL REPLACE IT////////////REPLACED CUTOUT&RESTORED POWER,ALL OK AFTERWARDS
20294 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2009-01-31 16:47 | 2009-01-31 18:55 | 1 | 128 | 53619-1 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED. COD-1
20295 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-12-13 07:12 | 2013-12-13 09:20 | 1 | 128 | 4158461 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 SERVICE BURNT INTO , ONLY 1 CUSTOMER AFFECTED, REPLACED SERVICE DROP WITH #2/3 .RESTORED POWER AT 09:20. VER/CRB L3/HFP
20296 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2008-04-22 15:02 | 2008-04-22 17:10 | 1 | 128 | 53306-1 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3301701/ BAD LUG ON SECONDARY SIDE ON HOT LUG == CHANGED TRANSF == POWER OK// VER/TOM IDC XXXX
20297 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-11-24 15:26 | 2013-11-24 16:30 | 2 | 64 | 4070711 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD LINE FUSE CUTOUT. VER/CRB L3/HFP
20298 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2013-01-14 17:23 | 2013-01-14 19:31 | 1 | 128 | 4603841 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. NU. PULLED LOOSE REPAIRED VER/HFP L3/HFP IDC XXXX
20299 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-09-26 15:48 | 2011-09-26 17:56 | 1 | 128 | 4920271 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CUSTOMER U.G. SERVICE BAD . RAN TEMP OVER HEAD WILL MAKE REPAIRS LATER. CUSTOMER MAY GO WITH OVER SERVICE. VER/HFP L3/HFP IDC XXXX
20300 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-06-28 15:43 | 2018-06-28 17:51 | 1 | 128 | 4685821 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout on 549-12 apr at 1751 close ticket
20301 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-11-16 17:37 | 2012-11-16 19:45 | 1 | 128 | 4403621 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | .BAD XFMR LUG ON SECONDARY, REPLACED BAD LUG, ALL POWER RESTORED COD-1 ISO TF 38830472000068 VER/HFP L3/HFP IDC XXXX
20302 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-11-13 09:55 | 2022-11-13 12:03 | 1 | 128 | 4138051 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER CALLED IN BY KENNY NAPIER /// SQUEEZE ON BURNT UP ON TRANSFORMER POLE /// MADE REPAIRS
20303 | Cannonsburg | 3001401 | LOUISA | CITY | 2015-08-02 21:25 | 2015-08-02 23:33 | 1 | 128 | 4968541 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUST AFFECTED/REWORKED SERVICE DROP AT SECONDARY POLE/BAD SQUEEZE ON/CUST POWER OKAY/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP
20304 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-09-16 11:42 | 2018-09-16 13:50 | 1 | 128 | 4104501 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | had 4/3 serv drp burnted down i made rep all good at this loc at 1350 by amg
20305 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-10-23 09:36 | 2010-10-23 11:44 | 1 | 128 | 62316-1 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED BAD PLACE IN NEUTRAL// VER/DBM IDC XXXX
20306 | Pikeville | 3408101 | SALISBURY | PRINTER | 2015-08-17 21:48 | 2015-08-17 23:56 | 1 | 128 | 4144551 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT LOOKS LIKE FUSE BROKE. FUSED UP EVERYTHING OK/ MD DONE/ ISO 38831123A00012/ COD 1/ VER/BOW
20307 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-01-20 09:17 | 2009-01-20 10:21 | 2 | 64 | 58526-1 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3314402// FUSE LINK HAD BROKE AND I REPLACED FUSE VER/TOM L3/TOM
20308 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-12-16 15:31 | 2021-12-16 17:39 | 1 | 128 | 4202721 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT//////////XFR IS BAD,RICK RAY ENROUTE TO REPLACE XFR/////////REPLACED XR&RESTORED POWER
20309 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2018-01-02 21:49 | 2018-01-02 23:57 | 1 | 128 | 4700441 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | one leg of 4/3 service burnt in two resagged service and replaced 2 feet of 4/3 service drop
20310 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-01-18 18:41 | 2011-01-18 20:49 | 1 | 128 | 62433-1 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | WR#38488214 NEED 19.9 CUTOUT AND LA 3 RELEASED BY CREW 078S08/CREW ON SITE/FETR2115/VEM/CUTOUTS CHANGED AND POWER RESTORED AT 2049/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB. IDC XXXX
20311 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2019-04-07 15:37 | 2019-04-07 17:45 | 1 | 128 | 4066771 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o pole 45-4374. campbell woods parkig lot @ 17 st bldg. crew reqd. Released by crew 078S07//cod 1
20312 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-07-17 21:01 | 2018-07-17 23:09 | 1 | 128 | 4791711 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o-replaced-ds071718 L3/HFP
20313 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2021-03-11 20:37 | 2021-03-11 22:45 | 1 | 128 | 4328401 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required//cod 1
20314 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2010-05-29 09:47 | 2010-05-29 11:55 | 1 | 128 | 53201-1 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HEATED UP AT CUSTOMERS WEATHERHEAD AND CAUSED INSULATION TO MELT OFF WIRES BURNING ONE OPEN. RE-SQUEEZED ALL CONNECTIONS @ WEATHERHEAD AND SECONDARY POLE. SH VER/KEP L3/KEP IDC XXXX
20315 | Hazard | 3310502 | HADDIX | CANOE | 2012-10-16 11:06 | 2012-10-16 13:14 | 1 | 128 | 4145661 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD BAD CONNECTION ON TRAILER POLE, REMADE ALL CONNECTIONS ///VER/CRB L/3 CRB IDC XXXX
20316 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-01-08 12:16 | 2018-01-08 14:24 | 1 | 128 | 4720701 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr ..gave info to Roger Maynard. Released by crew 076S01// crew on site, starting repairs // repairs complete, checked voltage and restored at 14:24
20317 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2015-03-27 19:23 | 2015-03-27 20:27 | 2 | 64 | 4236021 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-178 BAD CUTOUT/ MD DONE/ ISO 38830045A10178/ COD 2/ VER/BOW
20318 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2022-07-16 14:52 | 2022-07-16 17:00 | 1 | 128 | 4499921 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad 7200 cutout
20319 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-01-05 14:28 | 2015-01-05 16:36 | 1 | 128 | 4908261 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD INSULINK IN SERVICE DROP REPLACED BOTH WITH SQUEEZEONS FULLPOWER CLOSE TICKET/ ISO 38830571C20133/ COD 1/ VER/BOW
20320 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-06-26 17:51 | 2009-06-26 19:59 | 1 | 128 | 63680-1 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVEND ON DROP. MADE REPAIRS.// VER/DBM
20321 | South Williamson | 3200302 | BELFRY | TOLER | 2009-08-11 08:56 | 2009-08-11 10:00 | 2 | 64 | 65680-1 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQUEST # 31173864 // CUTOUT DOOR BURNED UP. REPLACED CUTOUT, POWER IS ON. IDC XXXX
20322 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-02-10 03:47 | 2020-02-10 05:55 | 1 | 128 | 4386611 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out, broken fuse, power restored/ ISO 37830251000139/ COD 1
20323 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-03-11 06:41 | 2021-03-11 08:49 | 1 | 128 | 4324731 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | per V Mullins, customer reports loop burnt open on middle phase at pole 38830142C00191//-crew req-ds031121 Released by crew 078S01///making repairs///Complete BR
20324 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2011-12-28 13:42 | 2011-12-28 15:50 | 1 | 128 | 4211381 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTIONS VER/KEP IDC XXXX
20325 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-11-06 09:20 | 2012-11-06 11:28 | 1 | 128 | 4366331 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONDUCTOR BURNT IN TWO MID SPAN, POWER RESTORED. ///VER/CRB L/3 CRB IDC XXXX
20326 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-09-09 15:32 | 2021-09-09 16:36 | 2 | 64 | 4226881 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | CREW REQUIRED 278-93 smoking at tap dead end bells ,,,,,lifted both taps on pole ,,,still smoking ,, Released by crew 078S05,lifted hot tap @ 278-189 @ 1532,repairs made all cust restored @ 1636 please close ticket thanks.bt Released by crew 078H02
20327 | Paintsville | 3410602 | E.PRESTON | LANCER | 2019-06-06 12:42 | 2019-06-06 14:50 | 1 | 128 | 4438061 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse out,,trying fuse,,bad 15kva 120/240 7200 xfmr, change tomorrow per PR reed Released by crew 074H07//OPS # 037486215
20328 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2021-06-13 09:43 | 2021-06-13 10:47 | 2 | 64 | 4728411 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse tail broke, apr at 1047 close ticket
20329 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2010-06-02 13:19 | 2010-06-02 13:51 | 4 | 32 | 55377-1 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 FUSE OUT IN TRANSFORMER BANK-BROKEN FUSE VER/KEP L3/KEP IDC INCORRECT POLE NUMBER CHANGED FROM 38830021B43520 GUESSING POLE NUMBER XXXX
20330 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-06-12 15:07 | 2010-06-12 16:11 | 2 | 64 | 61320-1 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..BROKEN IN HALF.. CHANGED OUT CUTOUT...BB//COD 2// VER/DBM
20331 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-03-05 11:07 | 2014-03-05 13:15 | 1 | 128 | 4453871 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUST APPEARS TO HAVE 1 PHASE OUT // WILL CHECK// WILL CHECK IN THE MORNING VER/HFP L3/HFP
20332 | Pikeville | 3408103 | SALISBURY | MARTIN | 2013-12-18 09:17 | 2013-12-18 11:25 | 1 | 128 | 4172591 | 128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT CONDUCTORS BURNT INTO AT WEATHER HEAD. WILL BE MAKING REPAIRS. REPLACED 4-3 DROP WITH 2-3 DROP EVERYTHING OK. VER/CRB L3/HFP
20333 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-06-13 20:12 | 2008-06-13 22:20 | 1 | 128 | 64249-1 | 128 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE ON POLE VER/PDP IDC XXXX
20334 | Whitesburg | 3312902 | JENKINS | JENKINS | 2008-12-15 20:24 | 2008-12-15 22:31 | 1 | 127 | H58774-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312902//OPENED LINE IN ORDER TO MAKE REPAIRS TO BAD CUTOUT//SEE ORDER 58754-1//COD 2// VER/DBM L3/KEP IDC XXXX
20335 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2017-07-25 11:38 | 2017-07-25 13:45 | 1 | 127 | 4177771 | 127 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED AND BURNT SERVICE NEUTRAL IN TWO. OOONE CUSTOMER AFFETEDOO REPAIRED & RESTORED @ 13:45. SH VER/CRB L3/HFP XXXHFP
20336 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2022-10-24 17:58 | 2022-10-24 20:05 | 1 | 127 | 4061081 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse melted out. changing
20337 | Paintsville | 3401101 | FALCON | FALC-OILS | 2021-03-11 17:48 | 2021-03-11 19:55 | 1 | 127 | 4327981 | 127 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed at weatherhead. One customer affected. Made repairs and restored @ 19:55. sh
20338 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2014-07-30 12:58 | 2014-07-30 15:05 | 1 | 127 | 4310071 | 127 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END BURNED LOOSE ON SERVICE POLE. I AM GOING TO SPLICE WIRE. I RESQUEEZED ALL CONNECTIONS. VER/HFP L3/HFP
20339 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-04-30 09:38 | 2010-04-30 11:45 | 1 | 127 | 53017-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA PER JOE MORELAND // SERVICER CONTACTING CREW //---CREW ON SITE //COD `// VER/DBM IDC XXXX
20340 | Pikeville | 3421001 | BREAKS | CITY | 2012-11-18 16:13 | 2012-11-18 18:20 | 1 | 127 | 4406951 | 127 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVE END AT WEATHER HEAD HAS PULLED APART ON 1 HOT LEG. I AM GOING TO PUT NEW CONNECTIONS ON ALL 3 CONDUCTORS. I RESQUEEZED ALL 3 CONNECTIONS// VER/DBM IDC XXXX
20341 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-09-21 12:38 | 2022-09-21 14:45 | 1 | 127 | 4905051 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout on 499-51 apr at 1445 close ticket. dwest
20342 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2020-11-06 18:53 | 2020-11-06 21:00 | 1 | 127 | 4649791 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection at weatherhead at sewer pump station . Made repairs // cod 1
20343 | Whitesburg | 3309302 | VICCO | JEFF | 2013-11-08 09:03 | 2013-11-08 11:10 | 1 | 127 | 4021361 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY BROKE LETTING PRIMARY INTO TREES === NEED TO INSTALL ANCHOR & GUY === MADE OPS ORDER 038871653 === TALKED TO CUST ABOUT THIS HE OK WITH THIS === GOES TO OIL WELL// VER/DBM L3/HFP
20344 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-05-02 16:17 | 2022-05-02 18:24 | 1 | 127 | 4825261 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans fuse open at 283-12,Had a broke fuse replaced and restored at 18:24.
20345 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2018-03-05 09:08 | 2018-03-05 11:15 | 1 | 127 | 4965471 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | pole 38830021D26636 bad connection on pole. fixed connection. COD-1 ISO TF 38830021D26636
20346 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-12-19 12:58 | 2018-12-19 15:05 | 1 | 127 | 4580201 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout only one customer out L3/HFP
20347 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2019-10-31 11:18 | 2019-10-31 13:25 | 1 | 127 | 4225401 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 247 c 235 will replace power restored at 13:25
20348 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-04-04 08:13 | 2008-04-04 10:20 | 1 | 127 | 63712-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3308503//FUSE LINK ROTTED INTO ON XFMR CUTOUT//COD 1// VER/DBM IDC XXXX
20349 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-11-16 17:45 | 2010-11-16 19:52 | 1 | 127 | 56441-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37786173 ///....LIFTED HOT LINE CLAMP ON BAD CUTOUT (LINE FUSE) @17:45 0N POLE 1113-D-065.....CALLED 911....LOCAL FIRE DEPT ENROUTE...LINE CREW ENROUTE ALSO....//....FIRE DEPT ARRIVED....OPENED CUTOUT ON 1113-C-30 TO DE-ENERGIZE ALL CONDUCTRS ON POLE @ 18:33....FIRE EXTINGUISHED....MAKING POLE REPAIRS.....REPAIRS MADE....CLOSED CUTOUT ON 1113-C-30 @ 19:52....ALL POWER ON.....JRV....11/16/10//VER/CRB IDC XXXX
20350 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-01-20 18:33 | 2008-01-20 20:40 | 1 | 127 | 58081-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED TRANSFORMER VER/ARN IDC XXXX
20351 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-02-04 11:18 | 2014-02-04 13:25 | 1 | 127 | 4347511 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 184-55 ,REPLACED CUTOUT RESTORED POWER AT 13:25 //VER/GAH
20352 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-04-26 15:02 | 2011-04-26 17:09 | 1 | 127 | 65615-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39710549 // COD-1 ISO LF 37830177A00208 VER/HFP L3/HFP IDC XXXX
20353 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-03-30 12:14 | 2009-03-30 14:21 | 1 | 127 | 63077-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACING BROKEN FUSE LINK//COD 1// VER/DBM IDC XXXX
20354 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2016-06-07 21:13 | 2016-06-07 23:20 | 1 | 127 | 4322231 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT SERVICER TO MAKE REPAIRS PWR RESTORED 23:20/ ISO 38830401B10123/ COD 1/ VER/BOW
20355 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-08-03 14:23 | 2022-08-03 16:30 | 1 | 127 | 4669751 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Broken guy wire got up across the pri. & neut. at pole 458-33. Cleared broken guy wire re-fused 15T at pole 458-32 In & holding at 16:30. TJS
20356 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2016-11-12 19:33 | 2016-11-12 21:40 | 1 | 127 | 4096601 | 127 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | /CONNECTION ON CUST TRL POLE BAD === REPAIRED POWER OK/// VER/DKM
20357 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2018-04-05 09:59 | 2018-04-05 12:06 | 1 | 127 | 4190501 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse back in at 12:06 COD-1 ISO TF 39831099B20113
20358 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-11-20 21:31 | 2022-11-20 23:38 | 1 | 127 | 4166901 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | transformer is in, splice in customer service failed // opening xfmr for repairs, no addtl customers affected //cod 1//back in at 2338 //
20359 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-02-05 21:11 | 2010-02-05 23:18 | 1 | 127 | 65427-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN INTO,WILL REPLACE IT///////REPLACED BROKEN CUTOUT AND RESTORED POWER,ALL OK AFTERWARDS //VER/GAH IDC XXXX
20360 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-11-18 19:03 | 2016-11-18 21:10 | 1 | 127 | 4111291 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTION AT SERVICEVER/AWD
20361 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-12-05 11:23 | 2013-12-05 13:30 | 1 | 127 | 4100981 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK//COD 1// VER/DBM L3/HFP
20362 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-12-31 17:58 | 2008-12-31 20:05 | 1 | 127 | 50259-1 | 127 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3008702//CUTOUT DOOR BURNT UP-REPLACED CUTOUT DOOR//COD 1// VER/DBM L3/KEP IDC XXXX
20363 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-03-31 07:08 | 2011-03-31 09:15 | 1 | 127 | 60724-1 | 127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 39380948 // 4/3 SERVICE BURNT LOOSE REPLACED 100FT 4/3 WITH 100 FT. 2/3 VER/HFP L3/HFP IDC XXXX
20364 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-02-11 13:40 | 2010-02-11 13:54 | 9 | 14 | 56869-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED @ 1340 AND CLOSED IN @ 1354 // HAD TO OPEN TO MAKE UP LOOPS AND RESTORE POWER TO LINE// 9 CUSTOMERS WERE OUTAGED//LINE FUSE NOT OUT--HOT TAP LOOP BURNT OPEN ON POLE 38830091C00066--CALLING CREW--SEND TO B FRALEY IDC XXXX
20365 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-05 09:05 | 2011-01-05 09:26 | 6 | 21 | H58797-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | C- PHASE ONLY OUT. I REMOVED 3 100 AMP CES ON POLE 117-41 AND INSTALLED 3- 30T FUSES. SEND COPY TO ENG. ALSO SEND COPY TO ROW PIKEVILLE TREES ARE GETTING UP BETWEEN PHASES NEEDS CUT FROM FUSE POLE ALL THE WAY UP FILED MD TO HAVE SECT REMOVED AND 30T INSTALLED VER/KEP L3/KEP IDC XXXX
20366 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2022-11-19 18:39 | 2022-11-19 20:45 | 1 | 126 | 4163041 | 126 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad squeeze @ xfmr // repaired & complete @ 20:45//cod 1
20367 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2017-11-26 21:48 | 2017-11-26 23:54 | 1 | 126 | 4603201 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad splice in service drop on pole 492-16, made repairs restored power at 23:54, only one customer affected..
20368 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-01-09 10:29 | 2014-01-09 12:35 | 1 | 126 | 4264571 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT. VER/CRB
20369 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-06-13 13:48 | 2022-06-13 14:51 | 2 | 63 | 4065781 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required bad cutout door
20370 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-05-16 10:42 | 2011-05-16 11:45 | 2 | 63 | 4100081 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT TO REPLACE//////REPLACED CUTOUT AND RESTORED//COD 2// VER/DBM
20371 | South Williamson | 3200301 | BELFRY | BELFRY | 2021-09-18 19:33 | 2021-09-18 20:15 | 3 | 42 | 4255261 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse out on 1014C-371 and transformer fuse out on pole 1014-C1-401 ..had arrester on transformer blow.i removed arrester and got the can fuse in dead.picked all cust up with the 40T line fuse on pole 1014C-371 at 20:15 // md filed //cod 3
20372 | Pikeville | 3408101 | SALISBURY | PRINTER | 2019-01-11 17:59 | 2019-01-11 20:05 | 1 | 126 | 4660561 | 126 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | looke like neutral was wore into where it was served around conduit clamp probably happened over a long period of time. replaced drop due to several splices. cust said everythnig was ok. send copy to peggy in damage claims due to open neutral L3/HFP
20373 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-05-10 22:49 | 2016-05-11 00:55 | 1 | 126 | 4195421 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT POLE 92-51 DUE TO BAD CUTOUT. HAD TO OPEN HOT LINE CLAMP POLE 92-51 AT 00:30 CLOSED LOOP AT 00:55 AND TRANFORMER BACK IN ON POLE 92-51 AT 00:55/// VER/ ADH
20374 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-05-30 07:19 | 2008-05-30 09:25 | 1 | 126 | 52755-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3003703//HOTTAP WAS OFF OF BASKET ON POLE `-89//COD 1//0925 RESTORED// VER/DBM IDCC PN90 XXXX
20375 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-05-19 10:03 | 2020-05-19 10:45 | 3 | 42 | 4854651 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | the transformer fuse i had out was 38831040000033 call center pull up wrong acc
20376 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-04-02 23:27 | 2015-04-03 00:30 | 2 | 63 | 4261371 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE & CUTOUT DOOR WAS BURNING. REPLACED DOOR & FUSE COD-2 ISO TF 38831148000199 VER/HFP L3/HFP
20377 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-10-16 19:44 | 2009-10-16 21:50 | 1 | 126 | 52881-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 1 CUSTOMER ONLY, REPLACED 4/3 TO 2/3. CUSTOMER MAY HAVE A TV DAMAGED......DAH//VER/CRB IDC XXXX
20378 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-06-15 20:06 | 2022-06-15 22:12 | 1 | 126 | 4131781 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse in door/restored 2206
20379 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-03-19 22:15 | 2015-03-20 00:21 | 1 | 126 | 4211391 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRYING TO ISOLATE PROBLEM/NO CREW REQUIRED VER/TOM L3/TOM
20380 | Hazard | 3420001 | SOFT SHELL | VEST | 2015-04-22 12:14 | 2015-04-22 14:20 | 1 | 126 | 4352931 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOT TAP HAS BEEN REMOVED OFF XFMR FUSE, BEEN THIS WAY FOR AWHILE, WILL NEED TO REPLACE CUTOUT AND ARRESTOR, G. SHOUSE CREW ON WAY TO HELP// VER/ ADH
20381 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-04-14 19:11 | 2016-04-14 20:14 | 2 | 63 | 4092431 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. REPLACED CUTOUT AND RESTORED @ 20:14. SH VER/CRB
20382 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-03-13 09:29 | 2014-03-13 11:35 | 1 | 126 | 4487981 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD CONNECTION /// COD-1 ISO TF 38830175000032 VER/HFP L3/HFP
20383 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-08-07 10:19 | 2008-08-07 11:22 | 2 | 63 | 66399-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401002// TRANS. FUSE ON BANK OF TRANS. IS OUT. I AM GOING TO REFUSE TRANS. LIGHTENING ARRESTER WAS BAD ON POLE TAKING OUT TRANS. FUSE. I CLEARED ARRESTER AND REFUSED TRANS.//COD 2// VER/DBM IDC XXXX
20384 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-09-10 09:59 | 2013-09-10 12:05 | 1 | 126 | 4833971 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON B PHASE. THIS USE TO BE A BANK, BUT ONLY ONE TRANSFORMER IS IN USE. I MOVED THE SECONDARY TO THE A PHASE TRANSFORMER. POWER IS OK NOW. PLEASE SEND TO CLIFF FREEMAN TO HAVE THE OTHER TWO TRANSFORMERS REMOVED. COD-1 ISO TF 38820964D00035 VER/HFP L3/HFP
20385 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-12-07 07:44 | 2010-12-07 09:50 | 1 | 126 | 63914-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38014969 //REPLACED TRANSFORMER ON POLE 38831151D00096 AND RESTORED AT 950 COD-1 ISO TF 38831151D00096 VER/HFP L3/HFP IDC XXXX
20386 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-06-02 10:57 | 2018-06-02 12:00 | 2 | 63 | 4546121 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 10t fuse
20387 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-10-25 09:47 | 2017-10-25 11:53 | 1 | 126 | 4496661 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER NO READING ON METER REPLACED THE TRANSFORMER FUSE THAT BROKE. COD=1 ISO TF 38821014B20594 VER/HFP L3/HFP
20388 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-12-03 12:54 | 2020-12-03 15:00 | 1 | 126 | 4742181 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DAE#1000053687// 1 customer out going to try to find and fix bad ug LRM repairs made pwr temp removed please close ticket LRM
20389 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-08-25 14:12 | 2022-08-25 16:18 | 1 | 126 | 4794091 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Repaired service drop,slice had burnt up. apr at 1618 close ticket. dwest
20390 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2022-12-20 15:04 | 2022-12-20 17:10 | 1 | 126 | 4281291 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed in service. Replacing service. Restored at 17:10. sh
20391 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-10-12 08:54 | 2022-10-12 11:00 | 1 | 126 | 4018051 | 126 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connectoin failed on one leg of the service/ repaired @1100
20392 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-11-01 05:32 | 2009-11-01 06:35 | 2 | 63 | 54441-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000303// NEW 6T TRANS FUSE BROKE //VER/GAH IDC XXXX
20393 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2019-01-10 10:07 | 2019-01-10 12:13 | 1 | 126 | 4655691 | 126 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug service/will need power temp/vem/FETR 1330/vem/power temp installed power restored 1213/please close ticket/thanks/vem//AED MADE
20394 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-06-22 13:14 | 2010-06-22 15:20 | 1 | 126 | 54595-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CHANGED BAD INSULATOR ON HI SIDE RISER, B PHASE XFMR OUT VER/ARN IDC XXXX
20395 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2013-12-06 14:18 | 2013-12-06 15:00 | 3 | 42 | 4108021 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER OUT OF CUTOUT HAS COME OUT , CREW IS COMMING TO FIX , MANUAL POLE PROBLEY WILL HAVE TO KILL PHASE TO CLEAR UP. "B" PHASE COD-27 OPEN FUSE ON POLE 376-18 AT 14:18 CLOSED AT 15:00 POWER RESTORED /// RELATED TO 4107091 WHICH WAS MISS MAPPED THIS IS ACTUALLY C PHASE 5 CUST VER/SEF L3/HFP
20396 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-04-30 10:54 | 2020-04-30 13:00 | 1 | 126 | 4780341 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole122-313 will make repairs/// Replaced bad cutout and restored service @ 13:00
20397 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-11-24 11:41 | 2013-11-24 12:44 | 2 | 63 | 4069951 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING FAILED CUTOUT. VER/CRB
20398 | South Williamson | 3411401 | DEWEY | INEZ | 2020-04-24 13:12 | 2020-04-24 14:15 | 2 | 63 | 4746221 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfmr cutout//i replaced cutout and arrestor//restored at 14:15//complete//em
20399 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-11-15 09:10 | 2013-11-15 11:16 | 1 | 126 | 4040581 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SERVICE BAD CONNECTION MIDSPAN COD-1 ISO TF 38830173000023 VER/HFP L3/HFP
20400 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-06-27 16:03 | 2015-06-27 18:09 | 1 | 126 | 4680271 | 126 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION POWER RESTORED KWB/. ISO 39831072000022/ COD 1/ VER/BOW
20401 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-12-13 15:32 | 2017-12-13 16:14 | 3 | 42 | 4646601 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 37840384000036 service neutral burnt into service 4/3 service will change service to a 2/3 drop 1532-1614service neutral burnt into service 4/3 service will change service to a 2/3 drop opened xfmr at 15:32 closed at 16:14
20402 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-07-07 14:53 | 2011-07-07 16:59 | 1 | 126 | 4482121 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25KVA 7200 XFMR BAD PER GREG FUGATE// CREW REQ///CREWW ON SITE CHANGING TRANSFORMER//COD 1// VER/DMB IDC XXXX
20403 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2014-05-22 07:32 | 2014-05-22 09:38 | 1 | 126 | 4737291 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED ARRESTER AND REFUSED TRANSFORMER, ALL WORK COMPLETE / GXJ//COD 1// VER/DBM
20404 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2017-07-03 18:23 | 2017-07-03 18:41 | 7 | 18 | 4069991 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | B PHASE XFMER PRI RISER BURNT OFF @ BOTTOM OF C/O RELEASED BY CREW 078S07/CREW ON SITE/WILL NEED TO OUTAGE XFMR BANK FOR REPAIRS/APROX 15 MINUTE OUTAGE/VEM/OPEN XFMRS AT 1823 REPAIRS MADE AND ALL CUST RESTORED 1841/PLEASE CLOSE TICKET/THANKS/VEM 38830021B43569 VER/AWD
20405 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-02-13 13:18 | 2011-02-13 14:21 | 2 | 63 | 56546-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE REPLACED FUSE ALL POWER RESTORED AT 1421 CLOSE TICKET VER/KEP IDCC PN161 XXXX
20406 | Cannonsburg | 3001401 | LOUISA | CITY | 2010-03-13 00:09 | 2010-03-13 00:51 | 3 | 42 | 66043-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT. IDC XXXX
20407 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-11-14 10:17 | 2011-11-14 11:20 | 2 | 63 | 4073971 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT FUSE BROKE INTO ///VER/CRB IDC XXXX
20408 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-12-31 16:38 | 2020-12-31 17:41 | 2 | 63 | 4839481 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
20409 | Hazard | 3309302 | VICCO | JEFF | 2016-01-01 16:57 | 2016-01-01 18:00 | 2 | 63 | 4580341 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAD TO OPEN THIS TRANSFORMER TO CHANGE TRANSFROMER ON POLE 37830322C00059 IN ORDER 4579931/ ISO 37830322C00059/ COD 2/ 1657-1800/ VER/BOW
20410 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-05-16 19:32 | 2020-05-16 21:38 | 1 | 126 | 4843901 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Changed blown lighting arrester./ ISO 37830110B20074/ COD 1
20411 | Hazard | 3302704 | HAZARD | KENMONT | 2011-02-21 22:43 | 2011-02-21 23:25 | 3 | 42 | 59989-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BOTTOM OF ARRESTTER BLOW OFF == REFUSED TRANSF ==POWER OK DIDNT REPLACE ARRESTTER // SENT EMAIL TO BRUCE LINDON & GLEN COMBS TO HAVE ARRESTOR REPLACED/// COD-3 ISO TF 37830321C00351 VER/HFP L3/HFP IDC XXXX
20412 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-10-21 19:08 | 2021-10-21 19:50 | 3 | 42 | 4373651 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout. Changed out power restored at 19:50.
20413 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-12-06 08:59 | 2012-12-06 11:05 | 1 | 126 | 4446451 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON SERVICE AT XFMR POLE. RE-WORKED CONNECTIONS ON XFMR POLE AND RESTORED AT 11:05. <<ONLY ONE CUSTOMER AFFECTED>> SH VER/KEP IDC XXXX
20414 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-10-28 11:42 | 2022-10-28 12:45 | 2 | 63 | 4074451 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse melted out, changing
20415 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-05-18 18:16 | 2011-05-18 18:58 | 3 | 42 | 4111281 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD PULLED LOOSE ON TRANSFORMER APR AT 1858 CLOSE TICKET // COD-3 ISO TF 38830668000012 VER/HFP L3/HFP IDC XXXX
20416 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2019-04-07 19:37 | 2019-04-07 19:55 | 7 | 18 | 4067471 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | replaced pole top pin @ 280-60..opened line fuse 280-55 @ 19:37 closed @ 19:55 complete /// L3/HFP
20417 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-09-10 09:22 | 2019-09-10 10:25 | 2 | 63 | 4999001 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | per Travis Burton Xfmer Fuse is blown to concession stand. restored
20418 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-11-23 10:18 | 2015-11-23 12:24 | 1 | 126 | 4479781 | 126 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE-IN CONNECTION 6 POLES AND NUMEROUS SPLICES AWAY FRM MTR.REPLACED AND RESTORED TO NORMAL,ALL OK AFTERWARDS.TOOK A WHILE TO FIND VER/CRB
20419 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-09-15 10:14 | 2015-09-15 12:20 | 1 | 126 | 4239501 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK HAD MELTED AND BURNED NEUTRAL INTO IN SERVICE DROP///CUST.STATED FIRE SHOT OUT FROM TV AND SHOWED ME THE CABLE THAT HAD BURNED INSIDE TE HOUSE///I SPLICED SERVICE ,DID NOT HAVE ENOUGH 2/3 WITH ME,I TOLD CUSTOMER I WOULD COME BACK TOMORROW AND RUN NEW SERVICE DROP TO GET RID OF SPLICES//PLEASE SEND TO PEGGY WYSONG,SAID HE WOULD CALL DAMGE CLAIM IF TV DOESNT WORK AFTER CABLE CO. RUNS NEW CABLE//COMPLETE//EM/ ISO 38820842B00028/ COD 1/ VER/BOW
20420 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2021-09-21 09:44 | 2021-09-21 11:50 | 1 | 126 | 4262491 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral burnt in two in service drop, repaired
20421 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-04-09 17:32 | 2015-04-09 18:35 | 2 | 63 | 4298331 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD 7200 CUTOUT./COD 2// VER/ ADH
20422 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-02-25 09:55 | 2019-02-25 12:01 | 1 | 126 | 4909601 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
20423 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-04-08 11:09 | 2021-04-08 13:15 | 1 | 126 | 4430021 | 126 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole, replaced all connections
20424 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-12-23 11:08 | 2012-12-23 11:26 | 7 | 18 | 4510871 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SECONDARY RISERS MELTED GOING TO OPEN TRANSFORMER ON POLE 147-2 TOMAKE REPAIRS. REPLACED BAD SPLICES ON SEC. RISERS . OPENED TRANSFORMER UP @ 11:08 CLOSED BACK IN @ 11:26 RESTORED SERVICE ///VER/CRB L/3 CRB
20425 | Hazard | 3303902 | LESLIE | WOOTON | 2010-04-08 17:24 | 2010-04-08 19:30 | 1 | 126 | 61175-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT//COD 1// VER/DBM IDC XXXX
20426 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-02-07 12:34 | 2010-02-07 14:40 | 1 | 126 | 51763-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED CONNECTION IN BASE REPLACE METER ALSO BURNT UP COD-1 VER/KEP L3/KEP IDC XXXX
20427 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-03-03 11:39 | 2014-03-03 13:45 | 1 | 126 | 4447181 | 126 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN, ON TRL POLE VER/SEF IDCC CNT2 XXXX
20428 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2010-01-17 22:13 | 2010-01-17 23:16 | 2 | 63 | 55674-1 | 126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401002// ARRESTER WENT BAD AND BLEW TRANS. FUSE. I AM GOING TO CLEAR ARRESTER AND REFUSE TRANS. I CLOSED TRANS. FUSE IN AND IT STAYED. IDC XXXX
20429 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-03-03 12:15 | 2008-03-03 14:20 | 1 | 125 | 52026-1 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3410602//THERE ARE 2 XFMRS ON POLE 955-339 THAT ARE LEAKING OIL. ONE IS SMOKING AT SECONDARY BUSHING & THE OTHER HAS SECONDARY RISER ALMOST BURNED IT TWO.//CREW REQUIRED//NO OUTAGE YET BUT WILL REQUIRE ONE TO REPAIR// ROBBY WORRIX TRUCK # 3145 - NO RADIO // TOOK POWER OFF @ 1215 AND ON @ 1420//COD 1//ISO 38830955D00339// VER/DBM IDC XXXX
20430 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-12-20 18:30 | 2020-12-20 18:55 | 5 | 25 | 4789271 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | one hot leg and neutral burnt into mid span// will have to open XFM up to make repairs// XFM off at 18:30 on at 18:55// customer is restored
20431 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-11-17 13:25 | 2016-11-17 15:30 | 1 | 125 | 4108361 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR.CHANGING/ ISO 38830852000034/ COD 1/ VER/BOW
20432 | Whitesburg | 3401301 | FLEMING | NEON | 2008-01-02 09:25 | 2008-01-02 09:50 | 5 | 25 | 52610-1 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO POWER IS OFF AT THIS TIME CUTOUT IS BAD AND I WILL CALL WHEN READY TO TAKE POWER OFFTOOK POWER OFF AT 0925 AND RESTORED AT 0950//3401301.//VER/CRB IDC XXXX
20433 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-08-20 12:15 | 2010-08-20 14:20 | 1 | 125 | 58677-1 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUT LUGS ON TRANSF WENT BAD == REPLACED LUGS == POWER OK// VER/DBM IDC XXXX
20434 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-02-04 04:25 | 2013-02-04 06:30 | 1 | 125 | 4789021 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE MELTED INTO AT XFMR POLE, ONLY ONE CUSTOMER WAS AFFECTED , REPAIRED SERVICE DROP RESTORED POWER AT 06:30 //VER/GAH IDC XXXX
20435 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2020-07-14 19:05 | 2020-07-14 21:10 | 1 | 125 | 4165011 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | secondery hot leg was laying against the pole ground and burnt in to. repairs made, power restored at 2110
20436 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-03-05 13:35 | 2014-03-05 14:00 | 5 | 25 | 4454321 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4453951 // CREW OPENED RECLOSER TO ALLOW THEM TO SAFELY REPLACE BAD CUTOUT ON STEPDOWN POLE 37830246D00458 // COD-5 // OFF 1335 ON 1400 VER/HFP L3/HFP
20437 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-06-19 19:19 | 2016-06-19 21:24 | 1 | 125 | 4389151 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFORM CUTOUT BROKE REPLACE POWER RESTORED/ ISO 38830186B10320/ COD 1/ VER/BOW
20438 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2019-05-03 21:10 | 2019-05-03 23:15 | 1 | 125 | 4214381 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 38830183D00235//crew replaced xfr cutout,,,complete//cod 1//iso
20439 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-07-01 09:55 | 2013-07-01 12:00 | 1 | 125 | 4435871 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT //VER/GAH
20440 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2018-01-15 21:52 | 2018-01-15 23:57 | 1 | 125 | 4750331 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | called customer and customer stated blue flames shoot out from the transformer secondary conductor burnt in two replaced 6 ft of service conductor restored power at 23:57
20441 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-12-08 13:31 | 2016-12-08 15:36 | 1 | 125 | 4177811 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | TWO HOT CONDUCTORS STILL TOGEATHER LOOK LIKE NEUTRAL PULLED OUT OF A TENSION SLEVE NOT SURE IF A TREE LIMB HAD HIT IT OR NOT MADE REPAIRS EVERYTHING OK NO ONE AT HOME HOUSE LOOKS TO BE EMPTY. SEND COPY TO PEGGY IN DAMAGE CLAIMS DUE TO OPEN NEUTRAL CUST COULD CALL IN. ALSO SEEN COPY TO ENG PIKEVILLE MAY NEED TO SET ANOTHER SEC POLE DUE TO LOW CLEARANCE OVER ROOF//SENT NOTE TO WYSONG/AWD VER/AWD VER/HFP L3/HFP
20442 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-10-19 20:35 | 2015-10-19 22:40 | 1 | 125 | 4362501 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 162-4030 6T FUSE BROKE REPLACED/ ISO38830162C14030/ CPD 1/ VER/BOW
20443 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-03-20 17:10 | 2017-03-20 17:35 | 5 | 25 | 4573091 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON 38830141C00064 BAD 19.9 CUTOUT OPENED LINE FUSE 17:10 TO 17:35 POLE 141-190 VER/AWD
20444 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2012-10-01 15:19 | 2012-10-01 17:24 | 1 | 125 | 4103601 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT TO REPLACE/////REPLACED CUTOUT AND RESTORED COD-1 ISO TF 38821060B00184 VER/HFP L3/HFP IDC XXXX
20445 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-11-04 09:15 | 2012-11-04 09:40 | 5 | 25 | H4354551 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY BURNED INTO..BAD CONNECTION.TOOK XFMR OFF AT 9.15.BACK ON 9.40.. COD-6 ISO TF 38830851B00083 DUP OF 4354551 VER/HFP L3/HFP IDC XXXX
20446 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-01-05 08:10 | 2021-01-05 10:15 | 1 | 125 | 4848531 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service has burnt into//service has burnt into, repaired service drop, one cust affected
20447 | Hazard | 3303902 | LESLIE | WOOTON | 2011-12-17 15:22 | 2011-12-17 17:27 | 1 | 125 | 4185571 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR C/O ON XFMR POLE 37830535000054//////// REPLACED XFMR C/O POWER RESTORED //COD 1// VER/DBM IDC XXXX
20448 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-11-02 18:19 | 2019-11-02 20:24 | 1 | 125 | 4285621 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ooCorrect xfmr is 38830805000209oo Xfmr fuse link appears to have broke. One customer affected. Restored @ 20:12. sh
20449 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-09-08 08:50 | 2011-09-08 10:55 | 1 | 125 | 4846821 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED -BAD CUTOUT NEEDS REPLACED--TRUCK TO POLE RELEASED BY CREW 078S07//CHANGED CUTOUT 1 CUST //VER/CRB IDCC TOF648 ESTIMATED TIME OFF XXXX
20450 | Hazard | 3310502 | HADDIX | CANOE | 2022-02-25 10:55 | 2022-02-25 13:00 | 1 | 125 | 4545191 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout made per james gilley// restored at 1300bad cutout made per james gilley.. restored power at 13:00
20451 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-11-19 10:07 | 2019-11-19 12:12 | 1 | 125 | 4046931 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced 6 connections .serve ends,,, voltage good now..
20452 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-09-07 08:40 | 2012-09-07 10:45 | 1 | 125 | 4025981 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAD PART POWER- FOUND CONNECTION AT TRANSFORMER WAS BURNT IN-TO CAUSING PART POWER RE-SQUEEZED SECONDRY AND RESTORED FULL POWER AT 10:45 //VER/CRB L/3 CRB IDC XXXX
20453 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-04-14 21:25 | 2009-04-14 23:30 | 1 | 125 | 52309-1 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3000801//BAD CONNECTION ON POLE IN BACK YARD NO CREW REQUIRED//COD 1//ISO 38830268D00183// VER/DBM IDC XXXX
20454 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2013-11-24 13:45 | 2013-11-24 14:10 | 5 | 25 | 4069921 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAD OPEN WIRE SECONDARY, THAT WAS TOGETHER, HAD TO OPEN TRANSFORMER, THE TIME OFF WAS 1345 TIME ON WAS 1410, RESAGGED OPEN WIRE, TO RESOLVE THIS PROBLEM VER/CRB
20455 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2014-09-18 12:19 | 2014-09-18 14:24 | 1 | 125 | 4508871 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION @ WEATHERHEAD// WILL REPAIR// REPLACED BAD SPLITBOLT// POWER RESTORED/// ISO 37830072C00351/// COD 1 CCC*******// VER/BOW
20456 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2021-08-17 11:35 | 2021-08-17 13:40 | 1 | 125 | 4085111 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Changing out transformer Off @ 1135 ON @ 1340//1 COD
20457 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-07-27 23:25 | 2014-07-27 23:50 | 5 | 25 | 4297921 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4297281//SERVICER OPENED FUSE TO REPLACE FAILED CUTOUT//COD 5// VER/DBM
20458 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-06-21 17:43 | 2021-06-21 19:48 | 1 | 125 | 4784301 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans cutout is broke at 168-106,Going to make repairs and restore service..Restored at 19:48..
20459 | Hazard | 3309302 | VICCO | JEFF | 2019-02-08 04:51 | 2019-02-08 06:56 | 1 | 125 | 4767871 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN SERVICE BROKEN
20460 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2017-08-04 07:59 | 2017-08-04 10:04 | 1 | 125 | 4223181 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BURNT UP 2ND CONNECTION.38830334B00040 VER/AWD
20461 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-06-15 09:10 | 2022-06-15 11:15 | 1 | 125 | 4122371 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | cutout door burnt up, restored
20462 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-12-13 09:45 | 2017-12-13 11:50 | 1 | 125 | 4645271 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broken in xfmr cutout.changing.
20463 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2020-08-26 10:56 | 2020-08-26 13:01 | 1 | 125 | 4382681 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | secondary riser fell out of bushing on xfmer. repairs made. pls close. tre
20464 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2011-09-04 19:55 | 2011-09-04 22:00 | 1 | 125 | 4811171 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION ON SERVICE DROP, HAVE REPAIRS MADE AND POWER IS RESTORED TO THIS CABLE BOX// VER/DBM IDC XXXX
20465 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-02-24 15:28 | 2011-02-24 17:33 | 1 | 125 | 60804-1 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BROKEN DOWN CUTOUT////////REPLACED CUTOUT AND RESTORED//VER/CRB IDC XXXX
20466 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-09-12 22:10 | 2013-09-13 00:15 | 1 | 125 | 4848601 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE DROP, RELEASED BY CREW 078S01 VER/CRB L/3 CRB
20467 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-01-08 07:38 | 2015-01-08 08:03 | 5 | 25 | H4917141 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRS MADE, POWER RESTORED. ORGINAL 2 OFF, OPENED THE OTHER 5 LATER/ OPENED TRANSFORMER AT 07:38.CLOSED AT 08:03/COD2+5// VER/ ADH
20468 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2013-08-23 17:15 | 2013-08-23 19:20 | 1 | 125 | 4701101 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORM FUSE LINK BROKE CHECK,REFUSE 6T POWER RESTORED .POLE329-116 NEEDS PRI. DOWN GUY INSTALLED POLE PULLED OVER NEEDS STRAIGHTENED TR. TO POLE IF DRY SEND COPY TO RAYBURN SENT EMAIL AS REQUESTED...HFP COD-1 ISO TF 38830329000116 VER/HFP L3/HFP IDC XXXX
20469 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2014-05-06 17:35 | 2014-05-06 19:40 | 1 | 125 | 4668901 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL WAS BROKEN, I REPAIRED IT//COD 1// VER/DBM
20470 | South Williamson | 3411401 | DEWEY | INEZ | 2016-01-14 21:58 | 2016-01-15 00:03 | 1 | 125 | 4621091 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN REFUSED CUTOUT RESTORED POWER AT 12:03 VER/KEP
20471 | Whitesburg | 3312902 | JENKINS | JENKINS | 2012-11-26 09:05 | 2012-11-26 11:10 | 1 | 125 | 4420761 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER ONLY ONE CUSTOMER AFFECTED, BAD SPLICE IN SERVICE MADE REPAIRS RESTORED POWER AT 11:10///VER/CRB L/3 CRB IDC XXXX
20472 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-12-31 16:45 | 2008-12-31 17:10 | 5 | 25 | 50092-1 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308002// RELEASED BY CREW 077S05 LEAD BURNED INTO//OPENED TRANSFORMER FOR REPAIRS @ 1645//COD 5//RESTORED 1710// VER/DBM L3/KEP IDC XXXX
20473 | Whitesburg | 3314401 | MAYKING | ERMINE | 2020-12-30 09:20 | 2020-12-30 11:25 | 1 | 125 | 4835161 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service conductor burnt in two and neutral as well on pole 449-201. cutting service down to make repairs. customer also has to make repairs to service mast
20474 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2015-10-05 11:30 | 2015-10-05 11:55 | 5 | 25 | 4318141 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | COMPL. TICKET OFF @ 1130 OPENED TR TO REPAIR BROKEN NEUTAL COD-5 ISO TF 37830019B00048 VER/HFP L3/HFP
20475 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-03-02 17:05 | 2008-03-02 19:10 | 1 | 125 | 51982-1 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3408303//, ON SITE, CHECKING TROUBLE RELEASED BY CREW 080S01// BOB SPOKE WITH RANDALL MARCUM AND CUSTOMER WAS AGREEABLE TO HAVING ONLY 110 FOR THE NIGHT - THIS IS UG AND THEY WILL NEED TO GET THE THUMPER TO FIND THE FAULT// IDC XXXX
20476 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-12-26 13:20 | 2008-12-26 15:25 | 1 | 125 | 64104-1 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON WEATHERHEAD BAD == REPAIRED == POWER OK//3308503//VER/CRB L3/KEP IDC XXXX
20477 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-12-27 15:25 | 2015-12-27 15:50 | 5 | 25 | H4564791 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1147-4124 REPAIRED #2 AL. HOT LEG OPEN WIRE SEC. RESTORED XFMER OFF @ 15:25, ON @ 15:50/COD 10// VER/ ADH
20478 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-04-22 07:40 | 2017-04-22 09:45 | 1 | 125 | 4666671 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE C/O--REPLACED-ALLGOOD-DS042217 38830260000107 VER/AWD L3/HFP XXXHFP
20479 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-05-08 21:55 | 2019-05-08 22:20 | 5 | 25 | 4242221 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout on pole 335-101 cracked and is arcing. will make repairs. repairs made.. // servicer did not provide exact outage times, states had 25 min outage to replace cutout//cod 5
20480 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-06-05 08:30 | 2016-06-05 10:35 | 1 | 125 | 4306081 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED CUTOUT APR AT 1035 CLOSE TICKET VER/CRB
20481 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2022-05-12 09:05 | 2022-05-12 11:10 | 1 | 125 | 4880421 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN 7200 C/O///REPAIRS MADE///RESTORED @ 11:10
20482 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-04-20 17:30 | 2009-04-20 19:35 | 1 | 125 | 61761-1 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD CONNECTION ON TRANSF == REPAIRED CONNECTION == L3/HFP AJBC CNT2
20483 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-02-12 06:55 | 2020-02-12 09:00 | 1 | 125 | 4395071 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ooOne customer affectedoo Insulink connection failed at weatherhead. Made repairs and restored @ 9:00. sh
20484 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2022-06-10 09:05 | 2022-06-10 09:30 | 5 | 25 | 4052011 | 125 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | xfmer off @ 09:05, restored @ 09:30. replaced bad connections on pole
20485 | Pikeville | 3402002 | KEYSER | STONECOAL | 2019-03-13 14:20 | 2019-03-13 16:25 | 1 | 125 | 4977791 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Customer had both hot legs burndt into @ trans. pole1128-48, made repairs @1625.
20486 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2009-12-13 14:15 | 2009-12-13 16:20 | 1 | 125 | 52050-1 | 125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. CUTOUT IS BROKEN INTO I AM GOING TO HAVE TO CHANGE CUTOUT. DALE IS BRINGING ME ONE. I CHANGED CUTOUT. VER/KEP L3/KEP
20487 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-01-06 22:38 | 2020-01-06 23:40 | 2 | 62 | 4219131 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Both 187 & 217 are served from this xfmr. Restored @ 23:40. sh
20488 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-05-02 14:58 | 2008-05-02 16:00 | 2 | 62 | 56386-1 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3410502// VER/HFP IDC XXXX
20489 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-09-12 11:30 | 2016-09-12 13:34 | 1 | 124 | 4887691 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF THE SERVICE DROP AT THE TRANSFORMER. VER/CRB
20490 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2019-11-03 09:32 | 2019-11-03 11:36 | 1 | 124 | 4286761 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced connections at mast
20491 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-08-08 13:38 | 2011-08-08 15:42 | 1 | 124 | 4679901 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED BAD ARRESTER//COD 4// VER/DBM IDCC PN9, CNT4 XXXX
20492 | Pikeville | 3413401 | GARRETT | GARRETT | 2012-02-07 22:03 | 2012-02-07 23:05 | 2 | 62 | 4327231 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN, REPLACED FUSE. ALL WORK COMPLETE / GXJ IDC XXXX
20493 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-07-20 21:18 | 2017-07-20 22:20 | 2 | 62 | 4148411 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE OUT ON 38820771B30061 RESTORED POWER AT 22:20 VER/CRB
20494 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2011-05-09 11:46 | 2011-05-09 13:50 | 1 | 124 | 4022331 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN.--- BAD CUTOUT.---- POWER RESTORED.//VER/CRB IDC XXXX
20495 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-06-28 17:01 | 2019-06-28 19:05 | 1 | 124 | 4614391 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout all pwr restored @ 19:05 please close ticket LRM
20496 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2015-12-15 17:45 | 2015-12-15 18:47 | 2 | 62 | 4535811 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD 2 ON ORIGINAL OUTAGE//HAD TO OPEN L/F ON POLE 39831098B33048 TO SAFELEY CHANGE CUTOUT ON FAUT POLE 39831098B33143// HAVE BAD CUTOUT CHG. ON POLE 1098-3143, OPENN L/F AT 1815, CLOSED BACK IN AT 1847, POWER RESTORED TO ALL CUST// VER/ ADH
20497 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-12-05 12:09 | 2015-12-05 13:11 | 2 | 62 | 4512151 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT INTO REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT// VER/ ADH
20498 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-12-13 09:32 | 2008-12-13 11:36 | 1 | 124 | 57933-1 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3409003// SERVICE WIRE BURNT DOWN. REPAIRED. SH// VER/DBM L3/KEP IDC XXXX
20499 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2017-12-27 05:06 | 2017-12-27 07:10 | 1 | 124 | 4680721 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | burnt up connections
20500 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2014-04-04 21:54 | 2014-04-04 23:58 | 1 | 124 | 4576521 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN AT TRANSFORMER LOOSE, REPLACED SERV-INS WITH SQUEEZONS, CUSTOMER ALSO HAS BAD CONNECTIONS ON NEUTRAL IN METER SOCKET . LEFT 200A MTR SOCKET ON SITE, CUSTOMER WILL CALL AT LATER DATE FOR DISCONNECT , ALL WORK COMPLETE / GXJ VER/KEP
20501 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-09-01 12:41 | 2015-09-01 14:45 | 1 | 124 | 4187881 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENING FUSE TO SAFELY REPAIR TRANSFORMER @38830020A41564/VERY DIFFICULT LOCATION/APPROX TWO HOUR OUTAGE/VEMOPENING FUSE TO SAFELY REPAIR TRANSFORMER @ 20-A4-1564/VERY DIFFICULT LOCATION/APPROX TWO HOUR OUTAGE/VEM XFMR OPEN @ 12:41//IT FORCE CLOSED
20502 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-04-09 18:38 | 2014-04-09 20:42 | 1 | 124 | 4590361 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPLACED CONNECTIONS ON SERVICE POLE AND TRANSFORMER POLE FIXED PROBLEM HJ VER/CRB
20503 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-06-21 12:41 | 2018-06-21 14:45 | 1 | 124 | 4634461 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @48-B4-815, checking. COD-1 IOS TF 37830048B40815 Trans. fuse open @48-B4-815, checking. Fuse pulled into, refused @1445.
20504 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-03-16 13:31 | 2014-03-16 15:35 | 1 | 124 | 4496991 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON 38831101C40084// WILL REPLACE// REPLACED CUTOUT// POWER IS RESTORED @ 15:35// 3-16 //COD 1//ISO// VER/DBM
20505 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-08-15 03:30 | 2010-08-15 04:32 | 2 | 62 | 55473-1 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE AND LAYING ON BRACKET..NEED TO OPEN LINE FUSE ON POLE 210-44 LONG ENOUGH TO MAKE REPAIRS.. OPENED FUSE ON POLE 210-44 AT 4:15 CLOSED BACK IN AFTER RELACING CUTOUT AT 4:32.. VER/KEP L3/KEP
20506 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-03-09 06:41 | 2008-03-09 08:45 | 1 | 124 | 55599-1 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 340172// CONNECTION WAS BAD ON HOT LEG OF THE SERVICE DROP. VER/JHM IDC XXXX
20507 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-09-01 18:45 | 2018-09-01 19:47 | 2 | 62 | 4032241 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT LEG BURNED INTO // L3/HFP
20508 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-08-10 07:43 | 2014-08-10 08:45 | 2 | 62 | 4349701 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT. WILL CHANGE//COD 2// VER/DBM
20509 | Hazard | 3309003 | JEFF | VIPER | 2018-06-07 14:43 | 2018-06-07 16:47 | 1 | 124 | 4566271 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Restored @ 1647
20510 | Hazard | 3310502 | HADDIX | CANOE | 2021-03-24 14:26 | 2021-03-24 16:30 | 1 | 124 | 4370111 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse pulled into. restored 16:30
20511 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2010-06-28 10:16 | 2010-06-28 10:47 | 4 | 31 | 58882-1 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND ROTTED FUSE LINK, HAD BROKEN, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC //VER/GAH
20512 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-09-26 17:06 | 2016-09-26 19:10 | 1 | 124 | 4928201 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRIED TO CALL CUST BACK & NO ANSWER..CUTOUT BROKE ON POLE 215-480.WILL REPLACE.RESTORED.. COD-1 ISO LF 37830215C00272 VER/HFP L3/HFP
20513 | Hazard | 3303902 | LESLIE | WOOTON | 2014-12-04 12:06 | 2014-12-04 14:10 | 1 | 124 | 4833191 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT VER/KEP
20514 | South Williamson | 3411401 | DEWEY | INEZ | 2016-10-20 17:43 | 2016-10-20 18:45 | 2 | 62 | 4033151 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANFORMER CUTOUT BROKE//REPAIRS MADE//RESTORED AT 1845//COMPLETE/EM VER/CRB
20515 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-03-20 15:27 | 2008-03-20 17:31 | 1 | 124 | 59535-1 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3410501// LOOSE CONNECTION ON WIRE AT WEATHER HEAD. I TIGHTENED CONNECTION. VER/HFP IDC XXXX
20516 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-03-03 15:06 | 2008-03-03 17:10 | 1 | 124 | 52279-1 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUT OUT ON POLE 834-356. ALSO NEED TO SEND NOTE TO ENG DEPT TO CHANGE THIS POLE IT IS IN A SLIDE & LEANING VERY BAD SENT NOTE TO RON RYE & PERRY FARMER--HFP /// VER/HFP IDC XXXX
20517 | Whitesburg | 3309302 | VICCO | JEFF | 2021-12-08 18:23 | 2021-12-08 19:25 | 2 | 62 | 4163181 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout. Made repairs and power restored 19:25.
20518 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2015-05-01 12:28 | 2015-05-01 14:32 | 1 | 124 | 4381641 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL BROKE AT MAST ///REPAIRED SERVICE NEUTRAL POWER RESTORED. VER/CRB
20519 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2018-04-05 08:46 | 2018-04-05 10:50 | 1 | 124 | 4189991 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Replaced bad connection at the weather head./ ISO 38820966A40616/ COD 1
20520 | Pikeville | 3413402 | GARRETT | LACKEY | 2022-05-16 21:26 | 2022-05-16 23:30 | 1 | 124 | 4900241 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester failed causeing xformer fuse to blown on pole 111-8... got restored at a time of 11:30
20521 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-07-09 19:00 | 2008-07-09 19:31 | 4 | 31 | 66503-1 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3202201//JRV ON SITE @ 18:30....TALKED TO CUST ABOUT WHERE HE SAW FIRE ON OUR POLE...CANT TELL IF TREES GOT INTO LINE HERE OR NOT...MAY HAVE CUTOUT GOING BAD...WILL RAISE UP AND TAKE A CLOSER LOOK...NO OUTAGE, SO FAR...//....FOUND SECONDARY CONNECTIONS GOING COD-4 VER/KEP IDCC TOF1806 XXXX
20522 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-11-03 18:24 | 2008-11-03 19:26 | 2 | 62 | 61929-1 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3311101// XFMR FUSE BLOWN, FUSE BROKE, REFUSED POWER RESTORED//COD 2// VER/DBM IDC XXXX
20523 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-04-16 10:16 | 2012-04-16 12:20 | 1 | 124 | 4675631 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RISER WIRE FROM PRIMARY METERING BURNT INTO//COD 1// VER/DBM IDCC MCCDL XXXX
20524 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-01-09 12:41 | 2022-01-09 13:12 | 4 | 31 | 4328631 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke XCO on pole 1125-C3-599, need one man to help with repairs
20525 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-10-01 07:32 | 2014-10-01 09:36 | 1 | 124 | 4540511 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER CALLING FROM ANOTHER LOCATION - CUSTOMER REPORTING OUTAGE @ POLE 37830398C00374 // BAD CUTOUT ON POLE 398-374, REPLACED CUTOUT RESTORED POWER AT 09:36. ONLY ONE CUSTOMER AFFECTED. // CCC COD-1 ISO TF 37830398C00374 VER/HFP L3/HFP
20526 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2017-12-26 15:34 | 2017-12-26 17:38 | 1 | 124 | 4680021 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | cust had part power, connection bad on xfmr pole, repaired
20527 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-11-11 12:28 | 2018-11-11 14:32 | 1 | 124 | 4389561 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SERVE IN//COD L3/HFP
20528 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2009-12-02 11:36 | 2009-12-02 13:40 | 1 | 124 | 55801-1 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 TWIST HAS A CONDUCTOR BURNT OPEN AT SECONDARY POLE. NOT ACCESSIBLE BY TRUCK - WILL HAVE TO CLIMB POLE AND RE-WORK CONNECTIONS. REPAIRS COMPLETE. SH IDCC MCCDL XXXX
20529 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2016-06-15 19:53 | 2016-06-15 21:57 | 1 | 124 | 4356741 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STINGER GOING INTO PRIMARY BUSHING ON XMF HAD BROKE, ALL REPAIRES MADE AND APR AT 2157 CLOSE TICKET VER/CRB
20530 | Hazard | 3310502 | HADDIX | CANOE | 2019-06-08 10:16 | 2019-06-08 12:20 | 1 | 124 | 4456341 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrestor
20531 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-10-30 10:48 | 2008-10-30 12:52 | 1 | 124 | 60834-1 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3301101// BAD CONNECTION ON TRANSFORMER IDCC MCCDL XXXX
20532 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2020-01-17 16:41 | 2020-01-17 18:45 | 1 | 124 | 4316681 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt into mid span, replaced drop restored power at 18:45, only one customer affected..
20533 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-11-18 13:41 | 2015-11-18 15:45 | 1 | 124 | 4462371 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE RUSTED INTO . REPAIRED . SEND TO TECH TO MAKE JOB TO REPLACE ANCHOR . ATACHED TO PHONE CO. GUY FOR NOW./ ISO 38831084A00297/ COD 1/ EMAIL SENT/ VER/BOW
20534 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-03-30 18:07 | 2019-03-30 19:09 | 2 | 62 | 4039111 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout. making repairs. repairs made. pls close. tre
20535 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2015-02-24 14:33 | 2015-02-24 15:35 | 2 | 62 | 4078651 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT../COD 2// VER/ ADH
20536 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-04-21 09:06 | 2014-04-21 11:10 | 1 | 124 | 4620761 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7200 CUTOUT ON POLE 380-247.//COD 1// VER/DBM
20537 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2018-12-18 17:26 | 2018-12-18 19:30 | 1 | 124 | 4578131 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout NBT L3/HFP
20538 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-01-30 09:46 | 2008-01-30 11:50 | 1 | 124 | 62098-1 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAVE A HOT TAP BURNTED OFF OF UNDERGROUND PRIMARY POLE, THAT FEED VALUE CITY, NEED A CREW TO MAKE REPAIRS RELEASED BY CREW 078S06 VER/ARN IDC XXXX
20539 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2017-01-23 09:04 | 2017-01-23 11:08 | 1 | 124 | 4320991 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED THE BURNED UP CUTOUT DOOR. THERE IS ONLY ONE CUSTOMER ON THIS TRANSFORMER. 38821111D00030 VER/AWD
20540 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-09-18 15:02 | 2016-09-18 16:04 | 2 | 62 | 4904151 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 423-133, REPLACED CUTOUT , RESTORED POWER AT 16:04.. VER/CRB
20541 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2021-01-22 01:01 | 2021-01-22 03:05 | 1 | 124 | 4884211 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer multiple times no answer voicemail full, broken cutout on pole 560-16/ ISO 37830560000016/ COD 1
20542 | Hazard | 3309301 | VICCO | REDFOX | 2018-11-26 18:45 | 2018-11-26 20:49 | 1 | 124 | 4481491 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on cust trl pole, replaced connection/ ISO 37830349000007/ COD 1 L3/HFP
20543 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2022-11-18 22:16 | 2022-11-19 00:20 | 1 | 124 | 4160781 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection at xfm.//Opened xfm from 00:15 to 00:20.//Repairs made.//cod 1
20544 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2018-11-08 12:06 | 2018-11-08 14:10 | 1 | 124 | 4379961 | 124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | xfmr bushing conn broken . replaced broken terminal, ALL WORK COMPLETE / GXJ38830810A00100
20545 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-10-24 16:13 | 2011-10-24 17:15 | 2 | 62 | 4016411 | 124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT..NO TREES...DONT SEE ANY ANIMAL..WILL RE-FUSE.//.OLD CUTOUT DOOR HAD DETERIORATED.FUSE NOT BLOWN.DOOR HAD JUST FALLEN OPEN..//..REPLACED DOOR & RE-FUSED.POWER ON NOW..JRV.10/24/11//COD 2// VER/DBM IDCC FEC49 XXXX
20546 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2011-09-23 09:42 | 2011-09-23 11:45 | 1 | 123 | 4908101 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | NO CREW REQUIRED REPAIRING NEUTRAL LEAD//COD 1// VER/DBM IDC XXXX
20547 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-07-04 16:17 | 2013-07-04 18:20 | 1 | 123 | 4463661 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | 37830168000032. PART OF BUSHING ON TRANSFORMER BROKE. I AM GOING TO REPLACE BUSHING PART. I RESTORED POWER AT 18:20 VER/CRB L/3 CRB
20548 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-01-06 15:00 | 2008-01-06 17:03 | 1 | 123 | 54206-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3312202//PRIMARY BURNED INTO AT CONNECTOR// VER/TOM IDCC PN182 XXXX
20549 | Hazard | 3303902 | LESLIE | WOOTON | 2008-05-20 18:57 | 2008-05-20 21:00 | 1 | 123 | 66568-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303902// REPLACED BAD XFMR G.SHOUSE//OPENED XFRMER @ 1857 AND RESTORED @ 2100//COD 1// VER/DBM IDC XXXX
20550 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2021-01-05 12:22 | 2021-01-05 14:25 | 1 | 123 | 4849691 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | bad 3 phase meter. t. burton changed meters
20551 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-10-02 15:42 | 2021-10-02 17:45 | 1 | 123 | 4310671 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced door
20552 | South Williamson | 3411401 | DEWEY | INEZ | 2010-07-10 23:07 | 2010-07-11 01:10 | 1 | 123 | 64958-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUT BROKE, POLE GROUND HOLDING IT IN AIR, CAUSED FUSE TO BLOW, ALL REPAIRS MADE, POWER BACK ON IDCC CCO, CNT2 XXXX
20553 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-12-02 12:54 | 2019-12-02 13:35 | 3 | 41 | 4115121 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | crew required 40/4 pole inline with open wire 269-94 trucks ok Released by crew 078S03///repairs made///opened xfmer on pole 269-112 @ 12:54 Closed @ 13:35///complete BR
20554 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-10-27 14:02 | 2009-10-27 16:05 | 1 | 123 | 58081-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKEN INTO. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. VER/KEP L3/KEP IDC XXXX
20555 | South Williamson | 3411401 | DEWEY | INEZ | 2014-05-02 08:32 | 2014-05-02 10:35 | 1 | 123 | 4656801 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP HAD BROKE FROM OVERTIGHTENING AND LEAD FELL OUT//I REPLACED HOT TAP//RESTORED AT 10:35//COMPLETE//EM VER/SEF
20556 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-11-09 11:27 | 2019-11-09 13:30 | 1 | 123 | 4014851 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burndt into @the trans. @1083-A-77, got repaired @1330.
20557 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2018-08-09 07:22 | 2018-08-09 09:25 | 1 | 123 | 4931291 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on transformer secondary riser. Replaced connection and restored @ 9:25. sh
20558 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-11-11 08:22 | 2008-11-11 09:03 | 3 | 41 | 63837-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001002// BROKEN XFMR FUSE//VER/CRB IDC XXXX
20559 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2010-02-12 08:05 | 2010-02-12 10:08 | 1 | 123 | 57115-1 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SERVICE DROP, REPAIRED//VER/CRB IDC XXXX
20560 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-08-02 09:42 | 2013-08-02 11:45 | 1 | 123 | 4616391 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIR SER.//REPAIRED SER./// ALSO REPAIRED LOOSE CONNECTION ON THE CUTOUT//POWER IS RESTORED VER/SER
20561 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2017-03-24 08:33 | 2017-03-24 09:14 | 3 | 41 | 4581621 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XMF AT 0833, CLOSED AT 0914, REPLACED NEUTRAL CONN ON XMF, ALSO CHECKED AND TIGHTENED CONN INSIDE METERBASE. CLOSE TICKET COD-3 ISO TF 38830454B43557 VER/HFP L3/HFP
20562 | Hazard | 3310502 | HADDIX | CANOE | 2009-06-22 13:57 | 2009-06-22 16:00 | 1 | 123 | 60982-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | VER/HFP METER WAS BURNED BLACK AND NO POWER WAS GOING THRU, CHANG METER L3/HFP IDCC CNT5 XXXX
20563 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2016-06-08 15:26 | 2016-06-08 17:29 | 1 | 123 | 4325671 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 38830044C35026, BAD 7200, 120-240, 25 KVA. TRK OK RELEASED BY CREW 078S07/CREW ON SITE/FETR 1800/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1729/PLEASE CLOSE TICKET THANKS/VEM VER/CRB
20564 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-11-05 18:24 | 2015-11-05 20:27 | 1 | 123 | 4413391 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL CONNECTION PULLED APART IN SERVICE DROP//// REPAIRED CONNECTION AND RESTORED SERVICE 124/124/248//// ONLY 1 CUSTOMER AFFECTED/// SEND COPY TO CLIFF FREEMAN ABOUT INSTALLING GUY ON POLE # 193-66/EMAILED TECH/ADH// VER/ ADH
20565 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2022-09-09 09:12 | 2022-09-09 11:15 | 1 | 123 | 4858381 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 25KVA xfrm on pole 449A-294. Crew required.//TRANSFORMER NOT ON MAP//Bad 7200 25KVA xfrm on pole 449A-294. Crew required.
20566 | Cannonsburg | 3001401 | LOUISA | CITY | 2020-03-14 15:49 | 2020-03-14 16:30 | 3 | 41 | 4478421 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | Replaced fuse and door. apr at 1630 close ticket
20567 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2012-01-11 07:27 | 2012-01-11 09:30 | 1 | 123 | 4246381 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKING FUSE NOW POSSIBLE BAD TRANSFORMER OUR CURRENT LIMIT FUSE GIVE TICKET TO JIM LINKOUS RELEASED BY CREW 078S09 //REPLACED CURRENT LIMITING FUSE/// VER/KEP IDC XXXX
20568 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-07-12 18:27 | 2008-07-12 19:08 | 3 | 41 | 51724-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 8T ME FUSE BROKE//3001201//VER/CRB IDC XXXX
20569 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2015-04-05 22:10 | 2015-04-06 00:13 | 1 | 123 | 4278701 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LOOKS LIKE A SERV DROP PROBLEM,WILL CHECK/////////SERVE-INS HEATED UP,BURNED INTO ONLY THE HOT LEGS,NOT THE NEUTRAL VER/HFP L3/HFP
20570 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-12-03 13:40 | 2018-12-03 14:21 | 3 | 41 | 4503511 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | transformer lead on secondary was loose and that burned it into, replaced lead open transformer fuse at 1340 and closed at 1421 L3/HFP
20571 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-11-14 06:07 | 2018-11-14 08:10 | 1 | 123 | 4396961 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replacing cutout L3/HFP
20572 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2011-05-02 10:39 | 2011-05-02 11:20 | 3 | 41 | 53480-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN// XFMR IS BAD, CONTACTED TIM H. HE STATED THAT THE CUST. ISNT USING THIS, I WILL REM. THE MTR. AND HAVE A JOB WRITTEN TO HAVE THE XFMR REM. AT A LATER DATE COD-3 ISO TF 38831078000026 VER/HFP L3/HFP IDC XXXX
20573 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2021-12-23 11:10 | 2021-12-23 11:51 | 3 | 41 | 4221251 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | PER DUTY RUSSEL AKEMON HOLD UNTIL MORNING 12/23 AND CALLOUT HIM AND TWO FROM BARREL CREW // Transformer is going bad. Need a 50kva 7200 transformer and cutout and t bracket. Voltage was spiking when I was checking voltage on the secondary bushing its causing flickering lights. Crew is going to change in the morning for safety reasons. Full power here right now. Released by crew 077H15 opened xfmr @ 11:10 closed back @ 11:51. xfmr reading low voltage .
20574 | Pikeville | 3408101 | SALISBURY | PRINTER | 2013-10-10 06:52 | 2013-10-10 08:55 | 1 | 123 | 4926451 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL CHECK AT REGULAR WORKTIME AS PER SET GUIDELINES // FUSE LINK BROKEN . REPLACED FUSE, ALL WORK COMPLETE / GXJ ***CHANGE ISO POLE*** VER/SEF L3/HFP
20575 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-01-18 07:33 | 2016-01-18 09:36 | 1 | 123 | 4627741 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE IN TRANSFORMER CUTOUT/ ISO 38830784C00219/ COD 1// VER/BOW
20576 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-06-28 02:32 | 2019-06-28 04:35 | 1 | 123 | 4610281 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Arrestor on primary riser pole 38830115D06001 failed, One phase out, opening other two phases, grounding and tagging to myself to change arrestor and cutouts. Line fuses back in at 04:35
20577 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-03-08 02:06 | 2018-03-08 04:09 | 1 | 123 | 4977731 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 424-2225, replaced cutout restored power at 04:09..
20578 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-12-31 16:22 | 2014-12-31 18:25 | 1 | 123 | 4895321 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CRACKED CUTOUT ON P 38830379000200 ALL PWR RESTORED AT 18:25 PLEASE CLOSE TICKET THANK YOU VER/CRB
20579 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-03-07 13:27 | 2016-03-07 15:30 | 1 | 123 | 4824211 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON SPLICE IN SERVICE AND AT WEATHERHEAD, ONLY 1 CUST WITH FLICKERING LTS., POWER RESTORED. VER/HFP L3/HFP
20580 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-11-18 07:33 | 2011-11-18 09:36 | 1 | 123 | 4089341 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BURNT DOWN AT WEATHERHEAD// REPAIRING//REPAIRS COMPLETE POWER RESTORED// TT ///VER/CRB IDCC CDC89 XXXX
20581 | Hazard | 3303902 | LESLIE | WOOTON | 2009-06-16 15:07 | 2009-06-16 17:10 | 1 | 123 | 60047-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | BROKEN SERVICE NEUTRAL IDC XXXX
20582 | Hazard | 3303902 | LESLIE | WOOTON | 2020-05-19 12:27 | 2020-05-19 14:30 | 1 | 123 | 4856101 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | anchor pulled out manuel /// Sent email as requested
20583 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-09-11 16:42 | 2022-09-11 18:45 | 1 | 123 | 4866711 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout burned up, vines on pole removing.
20584 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-10-02 19:17 | 2009-10-02 21:20 | 1 | 123 | 65748-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRIED TO CALL 911 BACK - BUSY SIGNAL XFMR BURNT UP WITH MINOR OIL SPILL. XFMR DOES NOT SERVE ANY CUSTOMERS EXCEPT FOR 1 FESTIVAL SERVICE. ALSO SERVES STREET LIGHTS. CREW ENROUTE. REPAIRS COMPLETE. SH VER/TOM IDCC PN66 XXXX
20585 | Pikeville | 3421002 | BREAKS | GRASSY | 2008-01-21 01:09 | 2008-01-21 03:12 | 1 | 123 | 58168-1 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BLOWN TRANF FUSE ON P#222B-198 CC=1 UP ON HILL FETR 03:30// BAD CUTOUT DOOR CHANGED DOOR POWER RESTORED 03:12//***SHOULD BE ELKHORN STA/GRASSY CKT (3400902). VER/CRB IDC XXXX
20586 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-07-08 09:14 | 2019-07-08 11:17 | 1 | 123 | 4677341 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7.2KV CO---replaced---pwr restored @ 11:17---tbl tkt comp---RMV
20587 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-03-24 19:27 | 2018-03-24 21:30 | 1 | 123 | 4057311 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no answerchange cutout
20588 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-10-14 08:17 | 2019-10-14 10:20 | 1 | 123 | 4137471 | 123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 6A open-wire secondary down. Crew enroute to assist.6A open-wire secondary down. Repaired and restored @ 10:20. sh
20589 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-03-01 22:03 | 2009-03-02 00:06 | 1 | 123 | 53272-1 | 123 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308401// D/S WILL TAKE CARE OF THIS TICKET. AND CALL DDC BACK. BAD CONNECTER AT POLE SERVICER OPENED TR AT 00:00 -CLOSED AT 00:06 VER/PDP IDCC MCCDL, TOF 0000 XXXX
20590 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2013-02-09 09:54 | 2013-02-09 10:55 | 2 | 61 | 4804541 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN//WILL REFUSE// FUSE APPEARED TO HAVE BROKE// REFUSED//POWER IR RESTORED // COD 2// VER/DBM IDC XXXX
20591 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2021-05-16 12:19 | 2021-05-16 13:20 | 2 | 61 | 4589981 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1151-C-267, checking. Trans. fuse melted, closed back in @1320.
20592 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2019-07-27 11:22 | 2019-07-27 13:24 | 1 | 122 | 4798511 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOOKS LIKE CUTOUT DOOR BURNED OUT,WILL REPLACE.LOOKS LIKE FUSE MELTED OUT AND DOOR TRACKED BEFORE IT FELL OPEN.I REPLACED IT.ALL OK AFTERWARDS
20593 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-10-10 15:10 | 2020-10-10 16:11 | 2 | 61 | 4542501 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout broke
20594 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-10-10 09:58 | 2022-10-10 12:00 | 1 | 122 | 4010931 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad 7200 cutout
20595 | South Williamson | 3411401 | DEWEY | INEZ | 2022-04-04 10:23 | 2022-04-04 12:25 | 1 | 122 | 4719831 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed mid-span in service drop. Repaired and restored @ 12:25. sh
20596 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2016-01-15 11:18 | 2016-01-15 13:20 | 1 | 122 | 4622171 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE LEG OF THE 2/3 TRIPLEX MUST OFF HAD A BAD SPOT AND HAD BURNT THE SERVICE DROP NEUTRAL INTO. I REPLACED THE SERVICE DROP.// VER/ ADH
20597 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-04-06 11:32 | 2016-04-06 13:34 | 1 | 122 | 4057851 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER VER/CRB
20598 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-05-11 19:23 | 2009-05-11 21:25 | 1 | 122 | 62741-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED SERVICE DROP
20599 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-07-16 12:48 | 2014-07-16 14:50 | 1 | 122 | 4253721 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | S/D BURNED IN TWO // WILL REPAIR // REPLACED S/D // POWER RESTORED @ 14 :50 VER/CRB
20600 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2019-10-10 15:53 | 2019-10-10 16:54 | 2 | 61 | 4129171 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse out on 845A188.no hazards seen.restored power at 16;54
20601 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2010-09-13 17:14 | 2010-09-13 18:15 | 2 | 61 | 66173-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WR# 36858277 // BAD INSULATOR ON 493-123.. REPLACED INSULATOR RESTORED POWER AT 18:15//COD 2// VER/DBM IDC XXXX
20602 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-03-20 21:29 | 2016-03-20 22:30 | 2 | 61 | 4865931 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV C/O.RESTORED VER/TOM L3/TOM
20603 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-11-20 08:28 | 2017-11-20 10:30 | 1 | 122 | 4587841 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | bad cutout on 976-24/ opened bank @ 1000 repairs made and closed bank @1030/ please close ticket/ MLH/ ISO 39830976B20024/ COD 1
20604 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2019-03-30 21:55 | 2019-03-30 23:57 | 1 | 122 | 4039521 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection. repairs made, power restored
20605 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2011-03-09 14:09 | 2011-03-09 15:10 | 2 | 61 | 52227-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 COPPER OPEN-WIRE-SECONDARY DOWN. APPEARS WIRE HAD A BAD SPOT IN IT AND JUST BROKE. REPAIRING. REPLACED ABOUT 100 FT OF WIRE AND RE-SAGGED. RESTORED @ 15:10. SH VER/KEP IDC XXXX
20606 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-01-01 09:13 | 2009-01-01 11:15 | 1 | 122 | 50466-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BROKE AT SPLICE. REPLACED SERVICE. POLE 38830834A00150 HAS A 50 KVA XFMR ON IT. PLEASE SEND TO MAPPING. SH//3409301//MADE A MDC//VER/CRB L3/KEP IDC XXXX
20607 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2014-05-14 18:43 | 2014-05-14 20:45 | 1 | 122 | 4703741 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED FUSE LINK COD-1 ISO TF 38830280000173 VER/HFP L3/HFP
20608 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-11-12 16:09 | 2012-11-12 17:10 | 2 | 61 | 4388771 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. COD-2 ISO TF 38830188C00520 VER/HFP L3/HFP IDCC FP NULL XXXX
20609 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2018-03-19 14:01 | 2018-03-19 16:03 | 1 | 122 | 4027021 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection @ xfm/// Replaced bad connection and fixed problem good voltage now 123/123/246
20610 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2014-01-03 14:13 | 2014-01-03 16:15 | 1 | 122 | 4224931 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD CONN AT THE HOUSE ON ONE OF THE PHASE WIRES, #2 SERVICE.// VER/DBM
20611 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-02-01 21:54 | 2019-02-01 22:55 | 2 | 61 | 4747891 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | restored
20612 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2016-04-13 06:58 | 2016-04-13 09:00 | 1 | 122 | 4086971 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED CUTOUT DOOR// VER/ ADH
20613 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2015-11-18 16:58 | 2015-11-18 19:00 | 1 | 122 | 4464391 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7200 CUTOUT ON POLE 213-908// VER/ ADH
20614 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2015-01-30 18:49 | 2015-01-30 19:50 | 2 | 61 | 4976541 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830068D00757 BAD CUTOUT DOOR 10T TRANS FUSE REPAIRED TWO CUST VER/CRB
20615 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-12-05 12:28 | 2015-12-05 14:30 | 1 | 122 | 4512191 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTIONS ON WEATHERHEAD SERVICE DROP WAS MELTED, HAVE REPAIRS MADED ALL IS FINE AT THIS LOC AT THIS TIME// VER/ ADH
20616 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2021-05-29 14:43 | 2021-05-29 16:45 | 1 | 122 | 4647281 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a broke Neutral on the service drop coming off Trans pole,Pulled Meter to Safely make repairs will restore once Conductor is fixed..Restored service @ 16:45 checked Voltage and its good now.
20617 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2008-12-07 13:28 | 2008-12-07 15:30 | 1 | 122 | 55151-1 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3410601// SECONDARY CONNECTION BURNT OPEN. WILL NEED TO OPEN XFMR TO REPAIR. OPENED AT 15:00. MADE REPAIRS AND CLOSED AT 15:30. SH // OTHER 5 CUSTOMER OUTAGED ON 55151-1H //6 COD// VER/TOM L3/TOM IDC XXXX
20618 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-11-24 16:23 | 2008-11-24 18:25 | 1 | 122 | 51687-1 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3303903// OPEN SECONDARY NEUTRAL.... REPAIRED NEUTRAL , RESTORED POWER AT 18:25// COD 1 // SERVICER STATES THAT CUSTOMER TOUCHED HIS MTR BASE AND GOT A MILD SHOCK... SERVICER CHECK OUT BUT FOUND NO VOLTAGE ON THE MBASE// CUSTOMER SAID HE WAS "ALRIGHT"//LEFT MESSAGE ON BRUCE LINDON`S CELL PHONE TO INFORM HIM OF THE ELECTRICAL CONTACT DBM// VER/DBM IDC XXXX
20619 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-02-06 11:28 | 2014-02-06 13:30 | 1 | 122 | 4362611 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I REPLACED RED TO RED SQUEEZE-ONS ON SECONDARY POLE IDC XXXX
20620 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-12-30 13:22 | 2008-12-30 15:24 | 1 | 122 | 65195-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3410602//BAD CONNECTION INSIDE A 167KVA/277 VOLT TRANSFORMER/// REPLACED TRANSFORMER AND CHECKED VOLTAGE VER/TOM L3/TOM IDC XXXX
20621 | Hazard | 3303902 | LESLIE | WOOTON | 2021-11-03 09:10 | 2021-11-03 11:12 | 1 | 122 | 4052141 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | rotted fuse
20622 | Pikeville | 3413401 | GARRETT | GARRETT | 2014-02-05 11:29 | 2014-02-05 12:30 | 2 | 61 | 4356681 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED UP XFMR ON POLE 40-26 TO REPAIR OPEN NEUTRAL IN LASH CABLE,, POWER BAC ON AT 12:30 VER/TOM L3/TOM
20623 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2013-05-24 08:54 | 2013-05-24 09:55 | 2 | 61 | 4178151 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-589 BAD GE CUTOUT REPLACED 6T TRANS FUSE //COD 2 ISO 38830044D40589 VER/SEF IDC XXXX
20624 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-08-03 10:58 | 2018-08-03 13:00 | 1 | 122 | 4902461 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | made new connction at service mast
20625 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-10-06 10:28 | 2011-10-06 12:30 | 1 | 122 | 4951911 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVICE NEUTRAL NEUTRAL BURNRT-INTO. MADE REPAIRS //VER/GAH IDC XXXX
20626 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-04-29 11:48 | 2022-04-29 13:50 | 1 | 122 | 4814971 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 120-240 7200 at pole 219-86. voltage was 140-140-280. opened transformer at 12:05.. crew required Released by crew 078S05 Closed at 13:50 Voltage checked good. Ticket complete
20627 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-06-10 19:43 | 2013-06-10 21:45 | 1 | 122 | 4255421 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERV-IN CONNECTION BURNED INTO,MADE NECESSARY REPAIRS AND RESTORED,ALL OK AFTERWARDS VER/SEF
20628 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-01-26 10:58 | 2009-01-26 13:00 | 1 | 122 | 59889-1 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309103//CUST REPLACED BREAKER WE ALSO HAD TROUBLE I REPLACED TRANSFORMER LUG//VER/CRB IDC XXXX
20629 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-09-24 13:58 | 2013-09-24 16:00 | 1 | 122 | 4882891 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED XMF ALSO HAD BAD CUTOUT AND ARRESTER, APR AT 1600 CLOSE TICKET.//COD 1// VER/DBM IDCC PN8 XXXX
20630 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-05-21 13:24 | 2020-05-21 14:25 | 2 | 61 | 4880201 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | b phase line fuse is blown on pole 1058-B-14, looked line over no hazards found, will try fuse on pole 1058-B-14. restored at 1425
20631 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-09-29 18:47 | 2016-09-29 19:48 | 2 | 61 | 4945121 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS CUTOUT FAILED ON 1080-70 I REPLACED CUTOUT RESTORED POWER AT 19:48 COD-2 ISO TF 38831080000070 VER/HFP L3/HFP
20632 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-11-12 22:29 | 2011-11-13 00:31 | 1 | 122 | 4070871 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. CC = 1. VER/SDB IDCC CCO XXXX
20633 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-06-08 00:13 | 2008-06-08 02:15 | 1 | 122 | 60010-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT....CANNOT GET TRUCK CLOSE TO POLE...CHG CUTOUT..BB VER/ARN IDC XXXX
20634 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2010-05-21 14:48 | 2010-05-21 15:20 | 11 | 32 | 66053-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35230215 // 7.2 C/O BAD OPENED UP AT 14:48 CLOSED BACK IN ON 3/0 TAP AT 14:57 CLOSED SINGLE PHASE IN AT 15:20 VER/HFP L3/HFP IDC XXXX
20635 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-09-07 21:29 | 2008-09-07 22:30 | 2 | 61 | 60237-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 13001102// WR 26147754 BAD CUTOUT COD-2 VER/LDA IDC XXXX
20636 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2018-07-10 14:43 | 2018-07-10 16:45 | 1 | 122 | 4758501 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke on 835-256. Replaced and restored @ 16:45. sh
20637 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-04-24 07:52 | 2011-04-24 08:53 | 2 | 61 | 63409-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURN UP CHANGE CUTOUT AND DOOR REFUSE 6T OFF 09:30 AM ON 09:40 AM POWER RESTOREDCUTOUT DOOR IS BURN UP CHANGE CUTOUT AND DOOR REFUSE 6T OFF 8:30AM ON 08:40 AM POWER RESTORED RELEASED BY CREW 078S04
20638 | Hazard | 3303901 | LESLIE | HYDEN | 2011-05-04 14:48 | 2011-05-04 16:50 | 1 | 122 | 4008521 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKED LIKE SERV-INS PULL OFF XFMR POLE. GOT FLAGGING CREW COMMING TO ME.//// SERVICE HOT LEADS ON XFMR WERE CUT. CONNECTED BACK. POWER RESTORED.// VER/DBM IDC XXXX
20639 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2010-10-14 13:29 | 2010-10-14 14:30 | 2 | 61 | 59715-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL ROTTEN BROKE REFUSED CUTOUT VER/HFP L3/HFP IDC XXXX
20640 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-09-30 08:58 | 2014-09-30 11:00 | 1 | 122 | 4538241 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR VER/CRB
20641 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-04-14 11:48 | 2019-04-14 13:50 | 1 | 122 | 4091411 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke on 99-103, Cutout changed, all power restored at 13:50
20642 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2021-06-18 16:22 | 2021-06-18 18:24 | 1 | 122 | 4768021 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BURNED UP,WILL REPLACE IT//////////CUTOUT NOT ACTUALLY BURNED UP,ONLY THE DOOR.REPLACED IT&RESTORED POWER////////ALL OK AFTERWARDS
20643 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-02-21 18:58 | 2015-02-21 21:00 | 1 | 122 | 4066531 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 426-176, 1 CUST. OUT, WILL BE CHANGING. LINE FUSE CUTOUT ALSO BAD ON THIS POLE, CHANGED THEM OUT. TOOK THE POWER OFF ON LINE FUSE AT 2027, CLOSED BACK IN AT 2100. BOTH CUSTOMERS RESTORED./ ISO 37830426C00176/ COD 1/ VER/BOW
20644 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2020-09-04 13:22 | 2020-09-04 15:24 | 1 | 122 | 4431341 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad yellow to yellow on pole 371/174 power ok now
20645 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2013-12-13 12:13 | 2013-12-13 14:15 | 1 | 122 | 4159501 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE LEG OF THE 4/3 SERVICE BURNED THE NEUTRAL DOWN. MADE REPAIRS POWER BACK ON. PLEASE SEND TO CLIFF FREEMAN TO UPGRADE SECONDARY EXT. FROM 4/3 TO 1/0. THIS IS A 200 AMP SERVICE ON A BIG HOUSE. VER/CRB L3/HFP
20646 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-12-01 10:08 | 2017-12-01 12:10 | 1 | 122 | 4614451 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING BAD TRANS. cahnged a CSP 25 to a regluar 25 with cutout,and repalced secondary
20647 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2008-09-18 06:18 | 2008-09-18 08:20 | 1 | 122 | 65093-1 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | 3403801// BLOWN ARRESTER ON THE PRIMARY METERING POLE. THE TICKET WAS MAPPED WRONG. I PUT THE CORRECT POLE # IN THE FAULT LOCATION BOX. WAS PART POWER IDC XXXX
20648 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-10-31 17:41 | 2014-10-31 18:42 | 2 | 61 | 4677921 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | X-FMR FUSE IS OPEN ON POLE 519-160. LIGHTENING ARRESTOR BLOWN ON X-FMR. CUT ARRESTOR IN CLEAR. RESTORED POWER AT 18:42. 10/31/2014 // CCC ENTERED MD = COD 2 ISO TF 37830519D00160 VER/HFP L3/HFP
20649 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-11-30 14:43 | 2013-11-30 16:45 | 1 | 122 | 4089591 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS///////FOUND A FROZEN-OUT SERVE-IN ON CONNECTIONS AT XFR,REPLACED BOTH ON HOT LEGS.WAS BARELY MADE UP AND TOGETHER AT SERVE-IN.NOBODY HOME,LEFT NOTE// VER/DBM
20650 | Whitesburg | 3309302 | VICCO | JEFF | 2014-10-17 08:45 | 2014-10-17 10:47 | 1 | 122 | 4639371 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE LEAD BURNT INTO AT XFMR , MADE REPAIRS RESTORED POWER AT 10:47/ ISO 37830396000014/ COD 1// VER/BOW
20651 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-09-29 12:20 | 2011-09-29 13:21 | 2 | 61 | 4931571 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK//COD 2// VER/DBM IDC XXXX
20652 | South Williamson | 3200301 | BELFRY | BELFRY | 2018-12-14 11:33 | 2018-12-14 13:35 | 1 | 122 | 4564601 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | B phase trans fuse blown on 1014-C1-3.closed trans fuse in at 13;35
20653 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-06-17 10:33 | 2019-06-17 12:35 | 1 | 122 | 4523411 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout changed, fuse back in at 12:35
20654 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2021-03-02 12:21 | 2021-03-02 14:23 | 1 | 122 | 4290711 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at pole.. redid connection. voltage check good
20655 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2019-10-25 13:20 | 2019-10-25 15:22 | 1 | 122 | 4196161 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | netural was broke at squeezon . have made repairs . coustomer is complaining of damaged equiptment.
20656 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-09-14 06:58 | 2012-09-14 09:00 | 1 | 122 | 4047341 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | A CONNECTION ON TRANS. POLE TO SERVICE DROP HAD BURNED INTO. I REPLACED CONNECTION. VER/HFP L3/HFP IDC XXXX
20657 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-11-10 08:28 | 2021-11-10 10:30 | 1 | 122 | 4072451 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout on pole 420-527. Made repairs. Power restored at 10:30.
20658 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-02-13 11:21 | 2011-02-13 12:22 | 2 | 61 | 56528-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNED INTO AT HOT TAP; I AM GOING TO REINSTALL HOTTAP. I REPLACED HOT TAP. VER/KEP IDC XXXX
20659 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-01-25 01:42 | 2015-01-25 02:43 | 2 | 61 | H4961601 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ASSOCIATED WITH 4961601 //OPENED RECLOSER ON POLE 8-D-93 AT 01:42. POWER IS BACK ON.////COD 2// VER/DBM L3/HFP XXX
20660 | Hazard | 3309302 | VICCO | JEFF | 2008-05-26 17:34 | 2008-05-26 19:36 | 1 | 122 | 51393-1 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309302//CALLED DUTY SUPERVISOR @ 1748//BAD CONNECTION AT TRANSFORMER// VER/DBM IDC XXXX
20661 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2011-04-19 18:53 | 2011-04-19 20:55 | 1 | 122 | 60823-1 | 122 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION ON ONE LEG . MAKING REPAIRS// VER/DBM IDC XXXX
20662 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2010-07-20 10:33 | 2010-07-20 12:35 | 1 | 122 | 53738-1 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK REQ 36062478 //------- BAD 25KVA IDC XXXX
20663 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-03-26 12:58 | 2022-03-26 15:00 | 1 | 122 | 4677381 | 122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OPEN ON POLE 1081-255////CURRENT LIMITING FUSE BAD////RESTORED AT 15:00
20664 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-07-27 09:19 | 2011-07-27 11:20 | 1 | 121 | 4627881 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON WEATHER HEAD, PART POWER/// RECONNECTED , FULL POWER RESTORED// VER/DBM IDC XXXX
20665 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-07-07 17:44 | 2014-07-07 19:45 | 1 | 121 | 4201761 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON UG SERVICE , NEED POWER TEMP. RELEASED BY CREW 078S01///SPLICED BAD 4/0UG HOT LEG INSIDE MTR BASE///VOLT CK GOOD///SEND B REYNOLDS COPY OF TICKET TO HAVE UG SERV REPLACED////SERV BACK ON 19:45//COD 1//EMAILED TO B REYNOLDS// VER/DBM
20666 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-04-02 22:14 | 2017-04-03 00:15 | 1 | 121 | 4608011 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR..CHANGING/// VER/DKM L3/HFP XXXHFP
20667 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2021-12-12 15:20 | 2021-12-12 17:21 | 1 | 121 | 4188981 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer is mis mapped she feeds off of pole 22-31, will have to open XFM to make repairs, will keep up with times, customer had hot leg and neutral burned in 2// opened XFM on 22-31@17:05 closed @ 17:21
20668 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-11-30 14:52 | 2013-11-30 16:53 | 1 | 121 | 4089601 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BAD . REPLACED CLF , ALL WORK COMPLETE / GXJ//COD 1// VER/DBM
20669 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-08-09 23:20 | 2019-08-10 01:21 | 1 | 121 | 4868131 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired connection 69-5522
20670 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-01-26 13:49 | 2009-01-26 15:50 | 1 | 121 | 59945-1 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRING CONNECTIONS AND REPLACING METER//3000802//VER/CRB IDC XXXX
20671 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-07-02 12:34 | 2009-07-02 14:35 | 1 | 121 | 61822-1 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGED OUT AN OLD (DEFECTIVE) 5 KVA ... REPLACED WITH A 15 KVA ... ALSO CHANGED THE CUTOUT & BRACKET....BLR VER/KEP L3/KEP IDC XXXX
20672 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-07-27 11:14 | 2021-07-27 13:15 | 1 | 121 | 4966161 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout..changing
20673 | Hazard | 3303902 | LESLIE | WOOTON | 2010-11-13 13:14 | 2010-11-13 15:15 | 1 | 121 | 55422-1 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACEING BAD CUTOUT ALL MANUAL WILL BE AWAY FROM TRUCK AWHILE//COD 1 PER SERVICER// VER/DBM IDCC MCCDIS XXXX
20674 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-06-27 21:29 | 2018-06-27 23:30 | 1 | 121 | 4682471 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout .changing.no truck access.
20675 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-03-08 11:49 | 2019-03-08 13:50 | 1 | 121 | 4961921 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT Released by crew 077S01 changed cutout L3/HFP
20676 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-01-09 00:04 | 2020-01-09 02:05 | 1 | 121 | 4226401 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers service wire burnt up at pole, repaired
20677 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-11-06 09:08 | 2019-11-06 11:09 | 1 | 121 | 4002071 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout going bad. changed. pls close. tre
20678 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2016-11-07 14:54 | 2016-11-07 16:55 | 1 | 121 | 4082201 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 304-942-6044 DUANE TECH ON SITE FOUND BAD C/O AT THIS LOC, I HAVE CHANGED POWER IS RESTORED TO THIS CUST AT 1655 BY AMG/ ISO 39830901000407/ COD 1/ VER/BOW
20679 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-04-04 10:04 | 2014-04-04 12:05 | 1 | 121 | 4572561 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1012B418. TRANSFORMER DOES NOT SERVE ANYBODY SO I LEFT IT OFF LINE. LINE FUSE WAS OUT ON POLE 38821012B00401. POWER IS RESTORED. PLEASE SEND TO CLIFF FREEMAN TO HAVE THIS FUSE MOVED OFF THE SIDE OF THE HILL. UNSAFE LOCATION TO REPLACE THE FUSE.//COD 1//EMAILED TO TECH// VER/DBM
20680 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-03-05 08:39 | 2018-03-05 10:40 | 1 | 121 | 4965161 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 785-180// opened the bother two cutouts at 1000 and closed at 1040// complete tt COD-34 ISO TF38830785D20206
20681 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-08-02 14:29 | 2016-08-02 16:30 | 1 | 121 | 4724241 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE LEG OF SERVICE BURNED OFF AT SERVICE MAST. I OPENED XFMR AT 16:10 TO MAKE REPAIRS, CLOSED BACK IN AT 16:30 COD-6 ISO TF 37830426C00437 FIX IN HOIS SEE H4724241 FOR 5 CUST VER/HFP L3/HFP
20682 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-04-19 14:39 | 2015-04-19 16:40 | 1 | 121 | 4334661 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST PART OUT DUE TO BAD CONNECTION AT INSULINK AND HEATED WIRE UP.. I REPLACED ALL CONNECTIONS AT SEC POLE 115-89 EVERYTHING OK NOW/COD 1// VER/ ADH
20683 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2018-03-16 17:17 | 2018-03-16 19:18 | 1 | 121 | 4020801 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | secondary connection failed on 115-159 replaced connection restored power at 19:18
20684 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2018-06-16 21:54 | 2018-06-16 23:55 | 1 | 121 | 4609181 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed and burnt neutral and on hot conductor in two in service. Replaced service and restored @ 23:55. sh//cod 1
20685 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-04-10 16:29 | 2011-04-10 18:30 | 1 | 121 | 54378-1 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CRACKED CUTOUT SAME AS TICKET 54393 AND 54328 CAN CLOSE TICKET MWL//COD 1 IDC XXXX
20686 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-06-26 14:46 | 2019-06-26 16:47 | 1 | 121 | 4601301 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR//COD 1//FUSE OUT ON POLE 38821130C10047//RESTORED 1647
20687 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-09-21 12:59 | 2011-09-21 15:00 | 1 | 121 | 4893041 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JOURNEY OPERATINGCUTOUT BAD ON POLE 37830396000072 == THIS GOES TO A OIL WELL TALKED TO CUST ABOUT REPAIRING AFTER ROADS DRY S UP SO WE CAN GET TRUCK TO POLE == WILL MAKE OPS ORDER TO REPLACE CUTOUT ==CUTOUT BAD ON POLE 37830396000072 == THIS GOES TO A OIL WELL TALKED TO CUST ABOUT REPAIRING AFTER ROADS DRY S UP SO WE CAN GET TRUCK TO POLE == WILL MAKE OPS ORDER TO REPLACE CUTOUT ==OPS ORDER 036163619 VER/KEP IDC XXXX
20688 | South Williamson | 3411401 | DEWEY | INEZ | 2022-10-07 10:24 | 2022-10-07 12:25 | 1 | 121 | 4003551 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | One leg of service burnt open. Repaired and restored @ 12:25. sh
20689 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-10-20 15:14 | 2010-10-20 17:15 | 1 | 121 | 61379-1 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELOCATED TO POLE 450-9 PER GREG BELL TO CHANGE CUTOUT FOUND DEF. BY LEAD EQUIP. 1 CUST AFFECTED XFMER//VER/CRB IDC XXXX
20690 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-12-15 08:32 | 2013-12-15 10:33 | 1 | 121 | 4162771 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE ON POLE 217-303 WHICH BLOWED LINE FUSE ON POLE 217-11 GOING TO CHANGE BAD CUT OUT. CHANGED CUT OUT ON POLE 217-303 AND CLOSED LINE FUSE IN ON POLE 217-11 @10:33 RESTORED SERVICE VER/CRB L3/HFP HFPC CFP303
20691 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-08-28 20:49 | 2012-08-28 22:50 | 1 | 121 | 4981901 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BAD.//..REPLACED & RE-FUSED..JRV..08/28/12 ///VER/CRB L/3 CRB IDC XXXX
20692 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2009-12-12 14:46 | 2009-12-12 16:47 | 1 | 121 | 64234-1 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE ON PRI. METERING HAS BURNED INTO. DALE IS SENDING BIG BUCKET TO REPAIR. RELEASED BY CREW 074S01//DEH REPAIRS MADE ON METERING, CALLED CUSTOMER SO HE COULD PUT LOAD BACK ON. VER/KEP L3/KEP
20693 | Pikeville | 3408103 | SALISBURY | MARTIN | 2013-01-14 20:19 | 2013-01-14 22:20 | 1 | 121 | 4604411 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BE CAREFUL ON THE ROADS THEY MAY BE SLICK DUE TO SOME FREEZING RAIN & SLEET. TRANSFORMER CUTOUT BROKEN . OPENED LINE FUS POLE 357 AT 21:50 AND CLOSED AT 22:20 . REPLACED CUTOUT, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 (ONLY 1 CUSTOMER PER POWERON ) COD-1 ISO LF @ 38831074A00357 VER/HFP L3/HFP IDC XXXX
20694 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-01-24 14:50 | 2015-01-24 16:51 | 1 | 121 | 4960001 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED OFF AT 1630 BACK ON AT 1651 HRS POLE 293-25/ TRANSFORMERS SHOWS 4, JOE SAID ONLY 1 CUSTOMER ON IT// VER/ ADH
20695 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-09-13 13:20 | 2018-09-13 15:21 | 1 | 121 | 4092611 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired ser drop at hs. & pole power restored
20696 | Hazard | 3310502 | HADDIX | CANOE | 2012-09-09 00:01 | 2012-09-09 02:02 | 1 | 121 | 4032861 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER AND THEY REPORT CREW WAS WORKING IN THE AREA FRIDAY AND SAID THEY WOULD CHCEK, STILL OUT. THIS FEEDS A GARAGE AND DEEP FREEZE IS ABOUT THAWED OUT. VER/ARN IDC XXXX
20697 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2011-01-04 13:47 | 2011-01-04 15:48 | 1 | 121 | 58618-1 | 121 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL INVESTIGATE COMPLAINT,BAD CON ON XFR POLE,WILL REPAIR//////RE-WORKED CONNECTIONS,ALL OK AFTERWARDS//VER/CRB IDC XXXX
20698 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2022-08-11 22:54 | 2022-08-12 00:55 | 1 | 121 | 4730931 | 121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfmr cutout // cod 1
20699 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-05 12:19 | 2015-02-05 14:19 | 1 | 120 | 4992801 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, BAD CONNECTION ON XFMR, ALL POWER RESTORED/ ISO 37830256000016/ COD 1/ VER/BOW L3/HFP XXX
20700 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-02-22 21:10 | 2014-02-22 23:10 | 1 | 120 | 4427361 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SER. CONNECTOR ON POLE BAD REPLACED POWER RESTORED //VER/GAH
20701 | South Williamson | 3411401 | DEWEY | INEZ | 2021-11-24 08:20 | 2021-11-24 09:20 | 2 | 60 | 4120761 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | insulink burnt into on xfmr pole//i repaired connections///restored at 9:20//complete//em
20702 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-12-19 23:14 | 2008-12-19 23:38 | 5 | 24 | 61066-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3008001//OPENED TRANSFORMER AT 23:14 TO 23:38 TOREPAIR SECONDARY// 5 COD - VER/TOM L3/TOM IDCC FEC60 XXXX
20703 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-01-08 13:00 | 2016-01-08 14:00 | 2 | 60 | 4595261 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S03 CUTOUT BAD OPENED AT 1300/NO OUTAGE TILL HOT TAP LIFTED AT 1300.RELEASED BY CREW 074S03 CUTOUT BAD OPENED AT 1300 CLOSED IN AT 1400 VER/CRB
20704 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-01-29 19:36 | 2011-01-29 21:36 | 1 | 120 | 52122-1 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP NEUTRAL INTO MIDSPAN,WILL REPAIR////////NEUTRAL INTO MIDSPAN AT SPLICE,MADE NECESSARY REPAIRS.POSSIBILITY OF DAMAGES VER/ARN IDC XXXX
20705 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-05-21 11:00 | 2008-05-21 11:10 | 12 | 10 | 50097-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 3110903/// OPEN TR @ 1100 CLOSED @ 1110 SENT EMAIL TO STEVE MARTIN & BILL FRALEY TO REPLACE/REPAIR ANCHOR & GUY AT LATER DATE VER/HFP IDCC CNT1 XXXX
20706 | Whitesburg | 3312902 | JENKINS | JENKINS | 2010-06-16 10:36 | 2010-06-16 11:00 | 5 | 24 | 66060-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SERVICE DROP OPENED TRANSFORMER AT 1036 AND CLOSED BACK AT 1100
20707 | South Williamson | 3411401 | DEWEY | INEZ | 2014-08-27 12:06 | 2014-08-27 13:06 | 2 | 60 | 4428491 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPENED TO MAKE REPAIRS ON 4427071 VER/KEP
20708 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2016-10-30 12:04 | 2016-10-30 13:04 | 2 | 60 | 4063381 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | I REPLACED THE TRANSFORMER FUSE THAT HAD BROKE. VER/CRB
20709 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-05-11 12:21 | 2019-05-11 14:21 | 1 | 120 | 4252981 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | MADE MD TO SHOW CUST SHOULD BE MAPPED TO TRANSFORMER 37830045A30373//COD 1//Replaced the transformer fuse that broke. Power is restored.
20710 | Pikeville | 3413402 | GARRETT | LACKEY | 2020-04-20 13:05 | 2020-04-20 15:05 | 1 | 120 | 4723401 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t transformer fuse broke. changed fuse closed fuse back in @ 15:05 everything ok
20711 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-12-18 13:00 | 2021-12-18 13:30 | 4 | 30 | 4207721 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BELIEVE CUST IS HEARING NORMAL BUZZING NOISE DUE TO DAMP CONDITIONS.WILL REPLACE XFR CUTOUT ANYWAY SINCE WE ARE@SITE.////////////OPENED XFR13:00,CLOSED 13:30////////ACTUALLY ON POLE 50-110///////XFR CUTOUT WAS CRACKED
20712 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-08-17 13:00 | 2013-08-17 14:00 | 2 | 60 | 4673361 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT//COD 2// VER/DBM IDC XXXX
20713 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-03-13 18:30 | 2009-03-13 19:30 | 2 | 60 | 58232-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401702// POLE SMOKING @ 74-1873401702//FAILED CUTOUT // I CHANGED CUTOUT.//COD 2// VER/DBM IDCC TOF1606 ESTIMATED TIME OFF XXXX
20714 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-04-03 18:40 | 2008-04-03 19:10 | 4 | 30 | 63556-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 402-75 REPLACED CUTOUT VER/HFP IDCC CNT1 XXXX
20715 | Cannonsburg | 3001401 | LOUISA | CITY | 2021-04-09 10:30 | 2021-04-09 11:00 | 4 | 30 | 4433501 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. broke B phase cutout on pole 38830454A41746 by ruck, 411 n clay feeds from this pole opened xfmr @ 1030, made repairs, closed at 1100
20716 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-05-25 11:00 | 2012-05-25 11:20 | 6 | 20 | 4830221 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN NETURAL IN SERV//OPENED TRANS AT 1100 CLOSED AT 1120 ///VER/CRB L/3 CRB IDC XXXX
20717 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-11-16 18:25 | 2015-11-16 20:25 | 1 | 120 | 4452751 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO. TWO TRIPLEX BURNED DOWN AT THE XFMR POLE, THE NEUTRAL AND ONE HOT LEG VER/CRB
20718 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-07-30 10:30 | 2017-07-30 11:30 | 2 | 60 | 4206361 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POWER IS ON UNTIL WE OPEN XFMR TO REPLACE IT. BUSHING IS BUSTED ON CSP XFMR. OPENED XFMR @ 10:30. REPLACED XFMR, INSTALLED NEW CUTOUT AND RESTORED @ 11:30. SH RELEASED BY CREW 076S02 VER/CRB
20719 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-09-30 17:00 | 2012-09-30 18:00 | 2 | 60 | 4100891 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED OUT ///VER/CRB L/3 CRB IDC XXXX
20720 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2012-12-27 10:25 | 2012-12-27 11:25 | 2 | 60 | 4537331 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TR FUSE MELTED OUT // REFUSED AT 1125 //VER/GAH
20721 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-05-15 16:48 | 2017-05-15 18:48 | 1 | 120 | 4801991 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER NO ANSWER TRANS FUSE BROKE RELACED FUSE RESTORED POWER AT 18:48 VER/CRB
20722 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-04-26 10:52 | 2008-04-26 12:52 | 1 | 120 | 54290-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801// FOUND BAD CUTOUT ON FUSE POLE/// BACK ON 1252 // VER/TOM IDC XXXX
20723 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-11-01 14:05 | 2018-11-01 15:05 | 2 | 60 | 4351221 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke when climbing to repair light//going to replace cutout//restored at 15:05//complete//em L3/HFP
20724 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2020-08-28 09:30 | 2020-08-28 10:30 | 2 | 60 | 4392001 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | cross arm split out.. replaceing now .. OpenedL/Fr @ 9:30 closed @10:30 back to normal
20725 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-11-10 12:00 | 2020-11-10 12:40 | 3 | 40 | 4657321 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | crossarm split out on pole 426-C-462. wire was down around communication cable. opened line fuse on 426-C-79 to make repairs.. opened @ 12:00 closed @ 12:40
20726 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-12-28 09:05 | 2021-12-28 10:40 | 2 | 95 | 4231491 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Opened latteral on 833-472 @ 10:15. Replaced cutout and restored latteral and xfmr bank @ 10:40. sh
20727 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-06-29 10:30 | 2008-06-29 11:00 | 4 | 30 | 59077-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 524-145, CHANGED CUTOUT BUT POLE NEEDS CHANGED OUT AS ASAP NEXT WEEK TRUCKS TO POLE OK.POLE IS 40/4 ADDRESS 133 SHIRT TALE FORK. RELEASED BY CREW 078S01 VER/KEP IDC CHANGED START TIME FROM 0701 XXXX
20728 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-08-10 16:00 | 2015-08-10 16:15 | 8 | 15 | 4117831 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. TRANS. OPEN 04:00 TO 04:15 VER/CRB
20729 | Hazard | 3311101 | STINNETT | REDBIRD | 2013-11-30 16:00 | 2013-11-30 17:00 | 2 | 60 | 4089171 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION WENT BAD BURN NEUT INTO ON SECONDARY === REPLACED SECONDARY === POWER OK//COD 2// VER/DBM IDCC TOF1143 ESTIMATED TIME OFF XXXX
20730 | Hazard | 3303902 | LESLIE | WOOTON | 2017-12-26 11:50 | 2017-12-26 13:50 | 1 | 120 | 4679371 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot leg of service pulled out on pole 366-63. restored power at 13:50.
20731 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-02-26 10:30 | 2020-02-26 12:30 | 1 | 120 | 4433021 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | bad CT metering & cutout, opened at 10:30 replaced metering & cutout restored power at 12:30.. L3/HFP
20732 | Hazard | 3302704 | HAZARD | KENMONT | 2018-02-05 08:40 | 2018-02-05 10:40 | 1 | 120 | 4805691 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | got red to red froz out way up on side of mountian got biran clemons coming to help on this
20733 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-06 08:24 | 2018-02-06 10:24 | 1 | 120 | 4808311 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | called customer: no answer//connection failed on secondary pole///repairs made//restored to normal at 10:20//complete/em
20734 | Pikeville | 3402003 | KEYSER | MULLINS | 2016-05-27 12:06 | 2016-05-27 14:06 | 1 | 120 | 4264611 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F IS OUT,WILL RE-FUSE////////XFR IS BAD,WILL REPLACE,STEVE RAY CREW ENROUTE W A 25KVA///////REPLACED XFR AND RESTORED,ALL OK AFTERWARDS/ ISO 38831127D00590/ COD 1/ VER/BOW
20735 | South Williamson | 3411401 | DEWEY | INEZ | 2022-02-15 15:40 | 2022-02-15 17:40 | 1 | 120 | 4484691 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 838-33//repairs made///restored at 17:40//complete//em
20736 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-06-15 09:15 | 2010-06-15 09:55 | 3 | 40 | 64881-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED TR TO MAKE REPAIRS TO CONNECTIONS COD-3 VER/HFP L3/HFP
20737 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-05-31 19:50 | 2008-05-31 20:10 | 6 | 20 | 53552-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3116703// BAD CONN ON POLE//COD 6// VER/DBM IDC XXXX
20738 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-05-07 14:45 | 2012-05-07 15:45 | 2 | 60 | 4755801 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF,,, MAKING REPAIRS,,,,ALL WORK COMPLETE//COD 2// VER/DBM IDCC PN44 XXXX
20739 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-04-13 07:35 | 2021-04-13 09:35 | 1 | 120 | 4446761 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP BURNED INTO AT CUSTS SERVICE POLE.MADE NECESSARY REPAIRS&RESTORED.ALL OK AFTERWARDS///////APPEARED BAD SQUEEZON CONNECTION HEATED UP,MELTED INSULATION,BURNT DROP DOWN
20740 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-03-11 10:00 | 2016-03-11 10:30 | 4 | 30 | 4836711 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGING CUTOUT AND ARRESTER ON POLE 38830044A00162/ OPENED 10:00AM TO 10:30/ ISO 38830044A00162/ COD 4/ VER/BOW
20741 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-05-06 13:20 | 2020-05-06 15:20 | 1 | 120 | 4806331 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad connnection on trans affecting 1 customer.made repairs,restored at 15;12.
20742 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-05-18 08:45 | 2022-05-18 09:15 | 4 | 30 | 4905401 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 215-378( had crack in it--no outage till TR was opened)///Opened xfm @ 08:45 and replaced cutout closed back in @ 09:15 and restored service
20743 | Hazard | 3303902 | LESLIE | WOOTON | 2010-02-22 12:45 | 2010-02-22 13:25 | 3 | 40 | 59776-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33962237 // RELEASED BY CREW 077S01 REPLACED TRANSFORMER CUTOUT AND ARRESTOR OFF 1245 POWER RESTORED AT 1325 CREW 077H01 VER/HFP L3/HFP IDCC TON1332 XXXX
20744 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2014-07-23 08:52 | 2014-07-23 10:52 | 1 | 120 | 4275231 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN//COD 1// VER/DBM
20745 | Hazard | 3311103 | STINNETT | WENDOVER | 2022-04-02 09:38 | 2022-04-02 10:38 | 2 | 60 | 4715371 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE MELTED OUT Power restored @ 10:38
20746 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-01-08 15:15 | 2018-01-08 16:15 | 2 | 60 | 4721651 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Opened txmf at 1515 closed at 1615, found neutral bushing on txmf a little loose apr at 1615 close ticket
20747 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-05-11 20:40 | 2008-05-11 22:40 | 1 | 120 | 62071-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 VOLT CUTOUT BAD ON XFMR COD-1 VER/KEP IDC XXXX
20748 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-07-02 13:05 | 2009-07-02 13:45 | 3 | 40 | 61983-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON B PHASE, HAVE IT CHANGED AND POWER IS RESTORED AT THIS LOC VER/KEP L3/KEP IDC XXXX
20749 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-12-04 09:54 | 2011-12-04 11:54 | 1 | 120 | 4139541 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE BURNED INTO SERVING CHURCH ONLY ONE CUSTOMER AFFECTED, REPLACED SERVICE RESTORED POWER AT 11:45 VER/HFP L3/HFP IDC XXXX
20750 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2017-07-19 20:30 | 2017-07-19 21:30 | 2 | 60 | 4144581 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD L/A ON POLE 42-50, ON INACTIVE TRANSFORMER, HAVE HOT TAP LIFTED ON TRANSFORMER, CLOSED IN L/F AT 2130 RESTORINNG POWER AT THIS LOC BY AMG// MADE AED ON L/A 38830042000050 VER/CRB
20751 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2019-10-14 10:50 | 2019-10-14 12:50 | 1 | 120 | 4138301 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired burn up hot leg and neutral. time restored1250
20752 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-09-10 16:00 | 2018-09-10 18:00 | 1 | 120 | 4078281 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at pole, repaired
20753 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-12-11 09:10 | 2014-12-11 11:10 | 1 | 120 | 4853761 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | HAD SPLICE GO BAD ON 1 PHASE OF URG. CABLE VER/CRB
20754 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2018-11-06 14:50 | 2018-11-06 16:50 | 1 | 120 | 4373141 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad hot leg in URD secondary coming from pedestal 37830024B21869, crew enroute to help with repairs, only 1 customer out at this time. Installed add-a-phase transformer until service can be traced out, got back on @1650.//MADE AED// L3/HFP
20755 | South Williamson | 3411401 | DEWEY | INEZ | 2016-10-24 08:05 | 2016-10-24 10:05 | 1 | 120 | 4047611 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER//CONNECTION BAD ON XFMR POLE//REPAIRED CONNECTION//RESTORED TO NORMAL AT 10:05//COMPLETE//EM COD-1 ISO SO @ 38830743C00014
20756 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2020-10-22 10:30 | 2020-10-22 11:30 | 2 | 60 | 4575591 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse on 21-b1-51 back in @ 11:30
20757 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-12-24 23:10 | 2011-12-25 01:10 | 1 | 120 | 4200671 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUYWIRE RUSTED OFF AT GROUND LEVEL FALL AGAINST XFMR TAKING FUSE OUT, MADE GUYWIRE SAFE RESTORED POWER AT 01:10 VER/TOM L3/TOM IDCC PN34 XXXX
20758 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-03-04 01:51 | 2015-03-04 02:15 | 5 | 24 | H4095751 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A & B PHASE OUT COD-12 2 OF 3 LINE FS OUT,WILL PTRL//////////BROKEN PIN-TYPE INSULATORS ON POLE 1058-81,NEED INSULATORS,2 MEN,BIG BUCKET/////OPND OTHER F AT 01:51,MADE REPAIRS,CLOSED ALL AT 02:15 VER/KEP --- COULD NOT VERIFY VIA SCADA OR VOICE RECORDER (VOICE RECORDER HAS ISSUES) MADE DUP FOR C PHASE OUTAGE L3/HFP HFPC DUP
20759 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-07-20 19:48 | 2012-07-20 19:58 | 12 | 10 | 4788211 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A PHASE FUSE BLOWN ON POLE 37830023000310 DID NOT SEE ANYTHING WRONG CLOSED FUSE @ 17:25 & POWER RESTORED GOING TO RUN LEAD EQUIPMENT AND SNIFFER TO FIND EQUIPMENT THAT IS BLOWING FUSES PIN INSULATOR CRACKED ON POLE 37830047C00532 // CREW REPLACING INSULATOR COD-12 ISO LF 37830023000310 VER/HFP L3/HFP
20760 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-22 23:45 | 2011-01-23 00:45 | 2 | 60 | 63674-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DUE TO BAD CURRENT LIMIT FUSE I OPENED TRANSFORMER 23:45. NOT ABLE TO GET TRUCK TO THIS. WILL BE AWAY FROM TRUCK. I HAVE RPAIRS MADE EVERYTHING OK. SEND COPY OF THIS TO BOB SHURTLEFF PIKEVILLE. AND TOM MAMING ENG PIKEVILLE. TRANSFORMER BACK ON 00:45. VER/PDP IDC XXXX
20761 | Whitesburg | 3312901 | JENKINS | KONA | 2013-02-04 22:51 | 2013-02-04 23:51 | 2 | 60 | 4791601 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED RECLOSER ON POLE 380-121 AT 11:30 TO REPAIR CUTOUT AND CLOSED BACK IN AT 11:54 NEW ORDER CREATED TO SHOW OUTAGE. IDCC TON2330 XXXX
20762 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-05-03 23:40 | 2016-05-04 00:10 | 4 | 30 | 4171971 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4171781 CREW OPENED RECLOSER @ 2340 TO ALLOW THEM TO SAFELY REPLACE BROKEN CUTOUT ON @ 0010// 4 COD - OTHER 63 ACCOUNTED FOR ON DIFFERENT OUTAGE//TOM VER/TOM L3/TOM
20763 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-05-09 19:45 | 2022-05-09 20:45 | 2 | 60 | 4871141 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o. repaired
20764 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-10-11 17:05 | 2011-10-11 19:05 | 1 | 120 | 4966041 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT..CAN REPLACE.//..REPLACED CUTOUT..POWER ON..JRV..10/11/11 COD-1 ISO 38821138C00091 VER/HFP L3/HFP IDC XXXX
20765 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-09-15 17:45 | 2011-09-15 18:45 | 2 | 60 | 4874501 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. THE POLE IS BURNED ABOUT 60%. I EXTINGUISHED THE FIRE AND REPLACED THE CUTOUT.//EMAILED TO C FREEMAN//COD 2 IDC XXXX
20766 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2012-10-11 12:10 | 2012-10-11 12:50 | 3 | 40 | 4130901 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TRANSFORMER AT 12:10 AND CLOSED AT 12:50, ALL WORK COMPLETE / GXJ VER/KEP IDC XXXX
20767 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2017-04-06 06:15 | 2017-04-06 08:15 | 1 | 120 | 4620221 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-641 10T TRANS FUSE CUTOUT DOOR BURNT UP 38830068C00641 VER/AWD L3/HFP XXXHFP
20768 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-05-01 05:30 | 2016-05-01 05:50 | 6 | 20 | H4146761 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT 49-74,WILL HAVE TO OPEN RECLR 49-75,THEN ISOLATE AT 49-73 IN ORDER TO SAFELY REPAIR CUTOUT,NEED 1 MAN,BUCKET TO HOLD OUTAGE TIME TO A MINIMUM////OPND RECLR 05:25,REPLACED CUTOUT,CLOSED RECLR @05:55 RELEASED BY CREW 074S06 VER/AWD /// DUPLICATING AND EST TIMES FOR WHEN HOT TAP WAS LIFTED 6 CUST TO COMP WORK SAFELY /// L3/HFP
20769 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-10-29 05:42 | 2011-10-29 06:42 | 2 | 60 | 4032621 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// FUSE LINK BROKE//REFUSED//POWER IS RESTORED VER/PDP IDC XXXX
20770 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2016-08-08 10:50 | 2016-08-08 12:50 | 1 | 120 | 4749021 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE C/O--REPLACED--ALLGOOD--DS080816 VER/AWD L3/HFP HFPC CDC96
20771 | Hazard | 3303901 | LESLIE | HYDEN | 2009-01-13 22:10 | 2009-01-13 22:50 | 3 | 40 | 54795-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303901// BAD CUTOUT COD 3 VER/TOM L3/TOM IDC CHANGED START TIME FROM 1946 ESTIMATED TIME OFF XXXX
20772 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-12-13 14:15 | 2019-12-13 14:55 | 3 | 40 | 4150121 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout hanging in the air , it goes on the arm between the phases Released by crew 077S12. cutout replaced. open @ 14:15 closed back 14:55
20773 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-01-20 14:45 | 2015-01-20 15:15 | 4 | 30 | 4945881 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR TO RE-FUSE////////CORRECTION,CUTOUT IS BROKEN,WILL REPLACE IT.ROBINETTE ENROUTE TO HELP//////REPLACED AND RESTORED.HAD TO OPEN LINEF HERE,OFF AT 14:45,ON AT 15:15 IN ORDER TO REPLACE XFR CUTOUT/// VER/ ADH
20774 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-04-24 22:15 | 2018-04-24 22:39 | 5 | 24 | 4275421 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT MAKING A LOT OF NOISE,MAY HAVE BEEN BREAKING DOWN.NO OBVIOUS CRACK BUT A LOT OF GLUE COMING OUT OF IT.REPLACED IT,NO NOISE NOW.OFF@22:15,ON@22:39 L3/HFP
20775 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-07-26 16:12 | 2017-07-26 16:42 | 4 | 30 | 4181861 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 120FT. 1/0 SERVICE DROP HAS ALL THE INSULATION MELTED OFF AND WILL NEED CHANGED OUT, TIM HALL GETTING A CREW TO CHANGE OUT. CAN WORK WITH A BIG BUCKET. RELEASED BY CREW 074S05.. OPENED TRANSFORMER AT 16:12 CLOSED IN AT 16:42/ ISO 38831126B00192/ COD 4/ VER/BOW
20776 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-03-07 12:32 | 2015-03-07 14:32 | 1 | 120 | 4158881 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED/RED SERVE END BAD ON SECONDARY POLE . VER/KEP
20777 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-07-30 17:42 | 2009-07-30 18:42 | 2 | 60 | 57184-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER MAY BE BAD WILL HAVE SOMEONE COME AND CHANGE IT OUT TOMORROW//COD 2// VER/DBM IDC XXXX
20778 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-06-09 19:08 | 2009-06-09 21:08 | 1 | 120 | 62547-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST PHONE #298-3500 BAD TRANSF CALLED R MARCUM CHECKING ON TRANSF 277/480 VOLTS RELEASED BY CREW 079S01//VER/CRB IDC XXXX
20779 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-03-05 09:58 | 2011-03-05 11:58 | 1 | 120 | 50022-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 39050642 // SERVICE NEUTRAL AND HOT LEG PULLED APART // NO OBVIOUS SIGNS OF PRIO DAMAGE TO CONDUCTOR / TAKE OFF POLE IS LEANING AND MR. HURT CREATED A JOB TO STRAITEN POLE AND HAVE #4 SERVICE UPGRADED TO #2. LOOKS AS IF CONDUCTOR JUST BROKE/FAILED VER/HFP L3/HFP IDC XXXX
20780 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-02-19 22:10 | 2008-02-19 23:10 | 2 | 60 | 65544-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3117601 CHANCE FUSE BROKE VER/PDP IDC XXXX
20781 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2019-10-16 15:10 | 2019-10-16 15:30 | 6 | 20 | 4147041 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cracked cutout on pole 321B-32//OFF 1510 ON 1530 L3/HFP
20782 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-08-25 13:00 | 2015-08-25 13:30 | 4 | 30 | 4169791 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER TO CHECK AT START TIME//.WILL NEED BIG BUCKET,3 TO 4 FT.PIECE OF 1/0 AUL TO SPLICE AT XFMR ON POLE#37830048D30155. CONNECTION FROM RISER TO 1/0 SECONDARY IS BURNING.T.HALL IS TO HAVE TIM MCCOY DO THIS. RELEASED BY CREW 074S04//IM AT JOB SITE.// MADE REPAIRS AND RESTORED POWER AT 13:30 TIM MCCOY RELEASED BY CREW 074H10 OPENED 1300/ ISO 37830048D30155/ COD 4 VER/CRB
20783 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2017-10-02 09:55 | 2017-10-02 10:15 | 6 | 20 | H4403891 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 1148-186 BAD CONN. ON POLE REPAIRED/ OPENED XFMR 0955-1015/ ISO 39831148A00186/ COD 7/ VER/BOW L3/HFP XXXHFP
20784 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-08-01 14:07 | 2017-08-01 16:07 | 1 | 120 | 4214271 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKE CREW REQ-DS-080117 RELEASED BY CREW 078S01/CREW ON SITE/FETR 1630/VEM/REPAIRS MADE AND ALL CUST RESTORED 1607/PLEASE CLOSE TICKET/THANKS/VEM 38830235000123 VER/AWD
20785 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-05-25 16:35 | 2017-05-25 16:50 | 8 | 15 | 4860101 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER CUTOUT BROKE ON POLE 160-7///CREW ENROUTE TO HELP WITH REPAIRS///OPENED LINE FUSE ON POLE 160-5 @ 16:35///CLOSED @ 16:50///REPAIRS MADE////COMPLETE BR 38830160000005 38830160000007 VER/AWD
20786 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2016-01-10 16:45 | 2016-01-10 18:45 | 1 | 120 | 4603421 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1147-405, BAD 12 KV C/O RELEASED BY CREW 078S07---CREW ON SITE CHANGING BAD CUTOUT---REPAIRED CUTOUT ---PWR RESTORED @ 18:45---ONLY 1 CUST..TBL TKT COMP--RMV VER/CRB
20787 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-11-02 17:00 | 2012-11-02 17:40 | 3 | 40 | 4339081 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACE LEAKING TX ATPOLE 38820818A00134 LAST POLE IN HOLLOWER// OPENED XFMR AT 17:00 TO CHANGE// SERVICE RESTORED AT 17:40 RELEASED BY CREW 076H02 COD-3 ISO TF 38820818A00134 VER/HFP L3/HFP IDC XXXX
20788 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-04-23 09:35 | 2009-04-23 10:05 | 4 | 30 | 52600-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED SECONDARY WIRE IS DOWN WILL NEED A CREW TO PUT THIS BACK UP RELEASED BY CREW 074S07OPENED TRANSFORMER AT 935 CLOSED IT AT 1005//VER/CRB IDC XXXX
20789 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2013-11-22 10:15 | 2013-11-22 10:45 | 4 | 30 | 4064511 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAD TRANSFORMER OPEN FROM 10:15 TO 10: 45 MADE REPAIR TO OVERHEAD CONDUCTOR. VER/CRB
20790 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-07-13 09:45 | 2016-07-13 10:45 | 2 | 60 | 4622341 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKEN.CHGING FUSE.// VER/ ADH
20791 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-07-30 14:30 | 2012-07-30 15:30 | 2 | 60 | 4866151 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK NO CREW REQUIRED//COD 2// VER/DBM
20792 | Hazard | 3310502 | HADDIX | CANOE | 2010-11-16 18:30 | 2010-11-16 20:30 | 1 | 120 | 56656-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | RUSTED GUY WIRE BLOWING INTO ARRESTOR---STAPLED TO POLE----//VER/CRB IDC XXXX
20793 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-02-09 18:00 | 2011-02-09 19:00 | 2 | 60 | 55737-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CLF BAD----REMOVED BAD CLF.//VER/CRB IDC CHANGED TIME OFF FROM 1709 ESTIMATED TIME OFF XXXX
20794 | Pikeville | 3413401 | GARRETT | GARRETT | 2017-09-01 09:10 | 2017-09-01 10:10 | 2 | 60 | 4315691 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT CRACKED ON POLE 17-12 OPENING LINE FUSES ON POLE 17-6 TO SAFELY MAKE REPAIRS.OPENED FUSES @ 9:50 AND CLOSED BACK IN @ 10:10 COD-15 ISO LF @ 37830017000006 VER/HFP L3/HFP
20795 | Whitesburg | 3312902 | JENKINS | JENKINS | 2011-12-03 02:00 | 2011-12-03 02:30 | 4 | 30 | 4137381 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMERS SERVICE BURNED OUT IN SPLICE.OPENED XFMR AT 0200 CLOSED AT 0230 //VER/GAH IDC XXXX
20796 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2019-07-01 12:45 | 2019-07-01 13:25 | 3 | 40 | 4627461 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | due to bad cutout and arrester i opened transformer on ple 211-a-127 at 12:45 made repairs closed transformer back in at 13:25
20797 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-09-13 12:00 | 2018-09-13 14:00 | 1 | 120 | 4092161 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POSSIBLE DAMAGE COMPLAINT
20798 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2021-04-16 08:30 | 2021-04-16 10:30 | 1 | 120 | 4455701 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connections bad on weatherhead, repaired
20799 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-10-28 08:42 | 2019-10-28 10:42 | 1 | 120 | 4208921 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 drop shorted out.need 1 man and material.chg out drop.
20800 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2016-05-20 09:13 | 2016-05-20 10:13 | 2 | 60 | 4236331 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CONTACT KEVIN BROWN IF INFO NEEDED// V. MULLINS AWARE AND WILL FIX IN THE AM/CREW ON SITE/POSSIBLE BAD U/G/VEM/SECONDARY IS DICON IN LIVE FRONT XFMR/WILL NEED TO OUTAGE XFMR 68-834/APROX ONE HOUR OUTAGE/VEM/OPENED XFMR AT1013/CONNECT SECONDARY AND POWER RESTORED TO ALL CUST 1023/PLEASE CLOSE TICKET/THANKS/VEM// VER/ ADH AJBC TOF1013 5/19
20801 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-10-09 09:50 | 2008-10-09 10:50 | 2 | 60 | 54517-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP STS WR# 26698003 RELEASED BY CREW 074S04. CHANGED OUT XFMR AND CUTOUT. COMPLTED BDC. OPEN UP AT 9:50 CLOSED BACK IN AT 10:50. COD-2 IDC XXXX
20802 | Whitesburg | 3312902 | JENKINS | JENKINS | 2016-01-04 07:58 | 2016-01-04 09:58 | 1 | 120 | 4583001 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BURNED INTO, I REPAIRED IT VER/CRB
20803 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-10-31 16:30 | 2008-10-31 17:30 | 2 | 60 | 61144-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3003701//CREW REQUIRED NEED 25KVA TRUCKS OK RELEASED BY CREW 078S03//VER/CRB IDCC TOF1302 ESTIMATED TIME OFF XXXX
20804 | South Williamson | 3411401 | DEWEY | INEZ | 2018-04-06 14:00 | 2018-04-06 16:00 | 1 | 120 | 4196241 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | insulink melted out and burned down service drop///i replaced service drop//restored at 16;00//complete//em/ ISO 38830767B00021/ COD 1
20805 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-08-04 15:45 | 2014-08-04 17:45 | 1 | 120 | 4330491 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 66-17 BAD CUTOUT POLE 66-16 15T LINE FUSE OUT COD 1//VER/ ADH
20806 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-10-27 11:15 | 2014-10-27 11:35 | 6 | 20 | 4663281 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT IN TWO FROM XFMR RISER TO 1/0 LASH SECONDARY. REWORKED CONNECTIONS. HAD XFMR 978-224 OPEN FROM 11:15 TO 11:35. SH// COD 6// VER/ ADH
20807 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-12-24 15:50 | 2014-12-24 16:50 | 2 | 60 | 4879891 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED CUTOUT APR AT 1650 CLOSE TICKET// COD 2// VER/ ADH VER/DKG L3/DKGXXXX
20808 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-03-17 08:05 | 2011-03-17 10:05 | 1 | 120 | 55026-1 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE LEG OF SERVICE DROP IS OPENED. I AM CHECKING NOW. WIRE HAD PULLED OUT OF SERVE END. I RESPLICED WIRE. THIS METER IS ACTUALLY OFF TRANS. POLE 263B-384. ONLY CUSTOMER OFF TRANS. IT IS A 480 TRANS. VER/KEP IDC XXXX
20809 | Pikeville | 3403001 | PIKEVILLE | CITY | 2008-07-15 15:48 | 2008-07-15 17:48 | 1 | 120 | 53011-1 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3403001//WILL CHECK SERV FOR PROBLEMSBAD CONNECTION ON XFR POLE,REPAIRED,ALL OK AFTERWARDS // VER/TOM IDC XXXX
20810 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-05-04 13:45 | 2010-05-04 14:15 | 4 | 30 | 55547-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | THERE ARE NUMEROUS CONNECTIONS ON TRANS. POLE THAT NEEDS REWORKED. I AM GOING TO OPEN TRANS. LONG ENOUGH TO REWORK SECONDARY CONNECTIONS. THIS WILL HAVE 3 OTHER PEOPLE OUT OF SERVICE FOR ABOUT 30 MINUTES. I OPENED TRANS. AT 13:45 AND CLOSED IT IN AT 14:00. I REWORKED ALL CONNECTIONS. EVERYTHING SEEMS TO BE OK NOW. IDC XXXX
20811 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-10-23 09:00 | 2011-10-23 09:30 | 4 | 30 | 4011751 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 374-14, REPLACED CUTOUT RESTORED POWER AT 09:30 COD-4 ISO TF 37830374D00014 VER/HFP L3/HFP IDC FLICKERING LIGHTS CHANGED TIME OFF FROM 810 ESTIMATED TIME OFF XXXX
20812 | Hazard | 3303901 | LESLIE | HYDEN | 2011-02-25 14:15 | 2011-02-25 14:35 | 6 | 20 | 61065-1 | 120 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED OPEN NEUTRAL AND REPLACED SECTION OF SECONDARY//OPENED TRANSFORMER TO REPAIR SERVICE NEUTRAL @ 1415//COD 6// VER/DBM IDC XXXX
20813 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-09-06 19:36 | 2021-09-06 20:16 | 3 | 40 | 4215351 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew on site to upgrade xfmr fetr 20:50 all pwr restored LRM 20:16please close
20814 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-07-16 17:00 | 2019-07-16 19:00 | 1 | 120 | 4717821 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out changed and power restored at19:00
20815 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-01-23 11:10 | 2016-01-23 12:10 | 2 | 60 | H1240105-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | *****SEE 4643191***** NO VOLTAGE @ METER (1 CUST). OTHER METERS CHECK GOOD. RELEASED BY CREW 078S07 OPENED TRANSFORMER 39831147D30806 EFFECTING (2 ADD CUST)// DUPLICATE IN HOIS/ OPENED TRANSFORMER 39831147D30806@ 1110 TO 1210/ ISO 39831147D30806/ COD 3/ VER/BOW
20816 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-07-15 21:40 | 2020-07-15 23:40 | 1 | 120 | 4168941 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Split bolt burndt hot leg into @ secondary pole 24-D2-480, only 1 customer was affected, restored @2340.
20817 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-03-04 01:51 | 2015-03-04 02:15 | 5 | 24 | H4095751 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A & B PHASE OUT COD-12 2 OF 3 LINE FS OUT,WILL PTRL//////////BROKEN PIN-TYPE INSULATORS ON POLE 1058-81,NEED INSULATORS,2 MEN,BIG BUCKET/////OPND OTHER F AT 01:51,MADE REPAIRS,CLOSED ALL AT 02:15 VER/KEP L3/DKGXXXX
20818 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-08-02 12:55 | 2013-08-02 13:07 | 10 | 12 | 4617121 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | ON SITE WORKING OPENED FUSE AT 12:55 CLOSED BACK AT 13:07 REAIRED POLE TOP PEN COD-10 ISO LF 37830126C40252 VER/HFP L3/HFP
20819 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-08-13 10:35 | 2020-08-13 12:35 | 1 | 120 | 4319151 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | looks like 6t transformer fuse broke replaced fuse everything ok
20820 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-09-26 09:30 | 2011-09-26 10:30 | 2 | 60 | 4916811 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED 15 KVA CSP WITH A 25 KVA CONVENTIONAL. OFF @ 09:30 AND BACK 0N @ 10:30 VER/HFP L3/HFP IDCC PN156 XXXX
20821 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-07-09 21:20 | 2010-07-09 21:50 | 4 | 30 | 64430-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER C/O. WILL REPLACE..P.HICKS....REPLACED @ 21:48 HRS. P.HICKS, VER/HFP L3/HFP IDCC TOF1948 XXXX
20822 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2008-02-08 22:30 | 2008-02-08 22:50 | 6 | 20 | 52818-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3403302// HOT LINE CLAMP APPEARS TO BE LOOSE. CLAMP WAS NOT THE PROBLEM. CREW ENROUTE TO CHANGE XFMR.3403302// BAD 50 KVA XFMR. OPENED AT 22:30 TO CHANGE. CLOSED AT 22:50 RESTORING ALL CUSTOMERS. SH / COD-6 / VER/LDA IDCC TOF1744 XXXX
20823 | Pikeville | 3407102 | TOPMOST | CANEY | 2010-02-23 17:15 | 2010-02-23 18:15 | 2 | 60 | 60264-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 68 ROTTED AT GROUND LEVEL AND LEANING, CREW ENROUTE TO STRAIGHTEN ... OPENED AT POLE 37830161D00101 AT 17:15 .. ON AT 18:15, ALL WORK COMPLETE / GXJ CCC - COD-2 VER/HFP L3/HFP IDC XXXX
20824 | Hazard | 3309302 | VICCO | JEFF | 2020-02-20 13:55 | 2020-02-20 14:15 | 6 | 20 | 4421081 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad connections on transformer leads makeing repairs opened at 13:55 closed at 14:15 L3/HFP
20825 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-10-02 13:30 | 2015-10-02 15:30 | 1 | 120 | 4303151 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT HAS BROKE DOWN. WILL NEED 7.2 C/O AND L/A AND BRACKET. MADE REPAIRS AND RESTORED POWER AT 15:30 TIM MCCOY// VER/ ADH L3/HFP XXXHFP
20826 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2008-12-05 18:23 | 2008-12-05 20:23 | 1 | 120 | 54767-1 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3309902//CONNECTOR WENT BAD ON SERVICE REPAIRED CONNECTION P HICKMAN R PIGMAN//COD 1// VER/DBM L3/KEP IDC XXXX
20827 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-09-03 17:55 | 2011-09-03 19:55 | 1 | 120 | 4795281 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WE JUST HAVE 2 PHASES HOT COMING UP HILL TO PRI. METERING ON POLE 238-239. I AM PATROLLING LINE NOW. HOT TAP HAD BURNED OFF CONDUCTOR AT RECLOSER POLE 239-182. I REPLACED HOT TAP AND RESTORED POWER TO MINES.//ISO 37830238000182//COD 1// VER/DBM IDC XXXX
20828 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-04-11 07:55 | 2017-04-11 09:55 | 1 | 120 | 4636261 | 120 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 6T TRANSFORMER FUSE OUT ON TRANSFORMER BANK POLE 1101-513. FUSED UP EVERYTHING OK VER/CRB L3/HFP XXXHFP
20829 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-08-31 03:55 | 2014-08-31 05:55 | 1 | 120 | 4439971 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW RERQUIRED BROKEN FUSE LINK VER/KEP
20830 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2011-10-22 11:15 | 2011-10-22 11:45 | 4 | 30 | 4010121 | 120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NUET AND BOTH HOT LEGS FAULTED, NUET WAS COMPLETLY GONE, CUST TALKED TO THE CREW ABOUT DAMAGES IN THE HOUSE: TIME OFF FOR REPAIRS WAS 11:15, TIME ON WAS 11:45 COD-4 ISO TF 38830020A10429 VER/HFP L3/HFP IDC XXXX
20831 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-03-25 14:38 | 2021-03-25 16:37 | 1 | 119 | 4374001 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 1108-267 blowing the fuse for the one span tap off of pole 38821108000240cutout broke on pole 38821108000267 blowing the fuse for the one span tap off of pole 38821108000240 cleared up cutout on pole 267. it didnt feed anything. rufused cutout on pole 240 and have a on time of 16:37
20832 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-10-25 14:56 | 2019-10-25 16:55 | 1 | 119 | 4196601 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad secondary connections at weatherhead, very difficult location. complted
20833 | Whitesburg | 3312901 | JENKINS | KONA | 2010-05-05 10:32 | 2010-05-05 12:31 | 1 | 119 | 55967-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUST SERVICE DROP BURNED DOWN I REPLACED SERVICE WITH2/3 TRIPLEX VER/HFP L3/HFP IDC XXXX
20834 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-05-11 13:31 | 2009-05-11 15:30 | 1 | 119 | 60629-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON 317-25 VER/KEP L3/KEP
20835 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2014-07-05 16:41 | 2014-07-05 18:40 | 1 | 119 | 4195441 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 281-15 BAD CUTOUT POLE 281-180 6T TRANS FUSE BROKE COD-1 ISO LF 38830281000015 VER/HFP L3/HFP
20836 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-03-14 23:19 | 2020-03-15 01:18 | 1 | 119 | 4478911 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | replaced secondary connections restored at 01:18.
20837 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2012-09-21 14:31 | 2012-09-21 16:30 | 1 | 119 | 4075531 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKEN. COD-1 ISO TF 38830679000107 ///VER/CRB L/3 CRB IDC XXXX
20838 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2020-08-29 02:40 | 2020-08-29 04:39 | 1 | 119 | 4396471 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad squeeze on at transformer
20839 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2021-06-21 18:20 | 2021-06-21 20:19 | 1 | 119 | 4784721 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service down that fed a meter for the rail road..service was hot on the ground.pulled out of squeeze..made repairs
20840 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-11-23 12:21 | 2020-11-23 14:20 | 1 | 119 | 4718151 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt into @ xfm///Replaced bad connection and restored full power @ 14:20/// only 1 customer affected
20841 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-07-01 16:35 | 2009-07-01 18:34 | 1 | 119 | 59500-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP ,,TRANSFORMER BAD ON POLE 427-23 CUSTOMER SAID IT COULD WAIT TILL TOMMOROW,, TRANSFORMER NEEDS TO BE A 25KVA 7200V POLE IS NOT TRUCK ACCESSIBLE // SENT EMAIL TO BOBBY REYNOLDS, LLOYD RAYBURN & LLOYD MCCARTY TO HAVE THIS REPLACED TOMORROW L3/HFP IDCC PN139 XXXX
20842 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2009-04-22 08:59 | 2009-04-22 10:58 | 1 | 119 | 50060-1 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD TWO BOLT CLAMP. REPLACED CLAMP.//3002101/VER/CRB IDC XXXX
20843 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-07-15 18:17 | 2009-07-15 20:16 | 1 | 119 | 63312-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER TOOK LINE FUSE OUT.//COD 1// VER/DBM IDC XXXX
20844 | Hazard | 3310502 | HADDIX | CANOE | 2008-05-25 13:41 | 2008-05-25 15:40 | 1 | 119 | 51172-1 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 3310502// == BAD 15 KVA TRANSF == WILL CHANGE OUT 5-27-08 == CUST SAID WOULD BE OK TO DO THAT == OPS 030059337 TO CHANGE TRANSF == VER/TOM IDC XXXX
20845 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-04-20 22:19 | 2017-04-21 00:18 | 1 | 119 | 4663241 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRIED TO CONTACT CUSTOMER NO ANSWERTRANS FUSE OUT ON 842-37 RE-FUSED CUTOUT RESTORED POWER AT 00:18/// VER/DKM L3/HFP XXXHFP
20846 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-05-03 11:19 | 2008-05-03 13:18 | 1 | 119 | 56611-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202201// CUTOUT BROKE//COD 1// VER/DBM IDC XXXX
20847 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-01-31 18:22 | 2011-01-31 20:21 | 1 | 119 | 52651-1 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WR# 38640445 // BAD PIECE OF WIRE AND CONN. VER/HFP L3/HFP IDC XXXX
20848 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2010-09-23 12:46 | 2010-09-23 14:45 | 1 | 119 | 52808-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 FUSES OUT ON XFRMR BANK....SECONDARY CABLE MELTED & SHORTED OUT NEAR CUSTS ENTRANCE....OPENED 3RD CUTOUT ON BANK....CHECKING TO SEE HOW LONG REPAIRS WILL TAKE.....CUST HAS ADDED LOAD...MAY HAVE OVERLOADED CABLE CAPACITY.....//.....SORTED CABLE....CUT OUT BAD CONNECTIONS AND REPLACED....RE-FUSED XFRMRS....POWER ON....JRV & ED MATNEY....09/23/10 //VER/CRB IDC XXXX
20849 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2019-11-22 09:49 | 2019-11-22 11:48 | 1 | 119 | 4055941 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | transformer cutout hot line clamp broke,
20850 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2014-05-08 13:58 | 2014-05-08 15:57 | 1 | 119 | 4675281 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD PULLED-APART TAPED-UP SERVE IN CONNECTOR.MADE REPAIRS.ALL OK AFTERWARDS///////THOUGHT XFR WAS BAD INITIALLY BUT FURTHER CHECKING FOUND SERVE-IN PROBLEM,XFR IS OK VER/SEF
20851 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-05-25 19:31 | 2008-05-25 21:30 | 1 | 119 | 51218-1 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3408402//WILL CHECK SERV FOR PROBLEMS1 LEG OUT.RE-WORKED CONNECTIONS AND RESTORED TO NORMAL.WAS OK WHEN I LEFT VER/LDA IDC XXXX
20852 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-02-16 11:39 | 2010-02-16 13:38 | 1 | 119 | 58381-1 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, CHECKING TROUBLE, CONNECTOR BURNT UP AT XFORMER POLE WHERE SERVICE MADE UP TO SECONDARY// VER/DBM IDC XXXX
20853 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-02-12 11:36 | 2015-02-12 13:35 | 1 | 119 | 4010321 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER BAD CONNECTION IN SERVICE DROP ONLY ONE CUSTOMER AFFECTED, MADE REPAIRS RESTORED POWER AT 13:35 VER/CRB L3/HFP XXX
20854 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-11-19 11:06 | 2014-11-19 13:05 | 1 | 119 | 4745801 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE38830044D37120 6T BROKE REPLACED FUSE VER/CRB
20855 | Hazard | 3303902 | LESLIE | WOOTON | 2022-03-01 18:26 | 2022-03-01 20:25 | 1 | 119 | 4558001 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
20856 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-12-12 09:38 | 2009-12-12 11:37 | 1 | 119 | 61814-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE FAILED VER/KEP L3/KEP
20857 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-12-03 08:41 | 2008-12-03 10:40 | 1 | 119 | 54141-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP ON SITE, BAD CUTOUT, REPLACING IT COD-1 IDC XXXX
20858 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-02-23 13:04 | 2019-02-23 15:03 | 1 | 119 | 4849171 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection in tree
20859 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2013-12-16 07:01 | 2013-12-16 09:00 | 1 | 119 | 4164661 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT. ALSO REMOVED PRIMARY NEUTRAL THAT IS DOWN BETWEEN POLES 38820892D00059 AND 38820892D00060. NEEDS TO BE PUT IN THE ABNORMAL.//COD 1//AED ENTRY CREATED// VER/DBM L3/HFP
20860 | South Williamson | 3411401 | DEWEY | INEZ | 2019-09-11 08:26 | 2019-09-11 10:25 | 1 | 119 | 4002801 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | hot leg pulled out of splice in service drop///have to get r/w cut to climb pole and let drop down to repair//repairs made//restored at 10:25//complete//em
20861 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-09-26 11:46 | 2022-09-26 13:45 | 1 | 119 | 4925171 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OPEN ON POLE 225-D-281 //// CLOSED LINE FUSE AT 13:45 POWER RESTORED ////
20862 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2018-06-07 18:01 | 2018-06-07 20:00 | 1 | 119 | 4566971 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse link rotten and broke, old c/o, bad loc, had to trim tree from around the pole, and then had to climb to put fuse back in, all power is restored at this loc at 2000 by amg
20863 | Pikeville | 3421001 | BREAKS | CITY | 2014-01-22 13:46 | 2014-01-22 15:45 | 1 | 119 | 4301491 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN THE SERVICE DROP ONLY ONE CUSTOMER AFFECTED VER/HFP L3/HFP
20864 | Hazard | 3310502 | HADDIX | CANOE | 2012-06-28 14:31 | 2012-06-28 16:30 | 1 | 119 | 4971701 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER
20865 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-07-09 19:21 | 2010-07-09 21:20 | 1 | 119 | 64415-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRMER FUSE AND LATERAL FUSE BLOWN ON POLE 794-B-107 (XFRMER NOT MADE UP ON LATERAL).....LINE LOOKS OK....WILL RE-FUSE BOTH.....//XFRMER CUTOUT BROKE ON POLE 794-B-107.....2 CUSTS ON THIS XFRMER....(LATERAL FUSE PREVIOUSLY PULLED OFF....DOESNT SERVE ANY CUSTS NOW)...DID NOT HAVE 19.9 CUTOUT....RIGGED XFMR TEMP UP ON LATERAL CUTOUT.....WILL GENERATE ORDER FOR CREW TO REPLACE.....JRV...07/09/10.... COD-1 VER/HFP L3/HFP IDC XXXX
20866 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2017-02-09 21:46 | 2017-02-09 23:45 | 1 | 119 | 4382041 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT UP C/O DOOR--REPAIRED--ALLGOOD--DS020917 L3/HFP XXXHFP
20867 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2020-07-28 21:45 | 2020-07-28 23:44 | 1 | 119 | 4248041 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | failed 1/0 sec splice,made repairs,restored at 11:30.one customer affected.
20868 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-06-17 17:01 | 2019-06-17 19:00 | 1 | 119 | 4527571 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot leg burndt into @ secondary pole 1126-C-762, only 1 customer was affected, made repairs @1900.
20869 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-12-21 09:51 | 2008-12-21 11:50 | 1 | 119 | 61415-1 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP COD-1 STS WR # 27766034 // FUSE BROKE L3/HFP IDC XXXX
20870 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2017-01-18 11:03 | 2017-01-18 11:20 | 7 | 17 | 4308731 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS A CRACK NEED TO OPEN IT TO CHANGE IT/ ISO 37820026000037/ COD 7/ 1103-1120/ VER/BOW L3/HFP XXXHFP
20871 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-02-03 02:01 | 2015-02-03 04:00 | 1 | 119 | 4987461 | 119 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS/////////SERVE-IN FROZE OUT ON XFR POLE.REPLACED,ALL OK AFTERWARDS VER/KEP L3/HFP XXX
20872 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2019-09-21 08:18 | 2019-09-21 10:17 | 1 | 119 | 4043991 | 119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout replaced cutout
20873 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-03-20 09:54 | 2015-03-20 10:53 | 2 | 59 | 4212711 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT 19.9KV COD-2 ISO TF 37820266000025 VER/HFP L3/HFP
20874 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-09-23 22:27 | 2012-09-24 00:25 | 1 | 118 | 4081171 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | THE SERVICE BURNED DOWN AT A SPLICE. ONLYONE CUSTOMER AFFECTED. I MADE REPAIRS. //VER/GAH IDC XXXX
20875 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-02-28 12:17 | 2018-02-28 14:15 | 1 | 118 | 4890211 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 37830134A40271 Released by crew 077S02BROKEN CUTOUT ON POLE 37830134A40271 power restored
20876 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-07-30 10:26 | 2019-07-30 12:24 | 1 | 118 | 4806711 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRF IS OUT,WILL RE-FUSE/////////RE-FUSED&RESTORED,ALSO REPLACED PORCELIN CUTOUT WITH AN EPOXY TYPE////////FUSE WAS BLOWN BUT NO EVIDENT REASON FOR THAT
20877 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-02-16 08:27 | 2013-02-16 10:25 | 1 | 118 | 4823371 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTIONS AT TRANSFORMER. EVERYTHING OK VER/KEP IDC XXXX
20878 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-09-05 21:43 | 2015-09-05 23:41 | 1 | 118 | 4208561 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED HOT LEGS IN SD VER/TOM L3/TOM
20879 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2009-07-15 15:22 | 2009-07-15 17:20 | 1 | 118 | 62506-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP SERVICE BURNT DOWN. ONLY ONE CUSTOMER OUT. REPLACED SERVICE. RESTORED AT 17:20. SH L3/HFP IDC XXXX
20880 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-08-09 18:55 | 2021-08-09 20:53 | 1 | 118 | 4024761 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Broke Neutral in service drop,Going to pull Meter and Climb pole and make repairs..Everything working Right now.
20881 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-03-19 09:48 | 2018-03-19 11:24 | 2 | 96 | 4026041 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | sercice drop burned down. will make repairs.opened xfmr @ 11:02 closed back in @11:24.only 1 c0ustomer out till I opened xfmr @ 11:02
20882 | Hazard | 3309302 | VICCO | JEFF | 2008-11-07 16:40 | 2008-11-07 18:38 | 1 | 118 | 63087-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 3309302// GUY WIRE BROKE AND FELL ACROSS XFMR RISER REMOVED GUY WIRE P HICKMAN//COD 1// VER/DBM IDC XXXX
20883 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2019-08-18 14:22 | 2019-08-18 16:20 | 1 | 118 | 4902561 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t fuse out due to bad cutout door replaced fuse and door closed fuse in everything ok
20884 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-04-20 20:17 | 2008-04-20 22:15 | 1 | 118 | 52832-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT UP AND FELL OFF STIRRUP. CUSTOMER STATED THEY KNEW POWER WAS OFF FRIDAY BUT DID NOT CALL BECAUSE THEY THOUGHT EVERYONE WAS OFF AND IT WOULD BE FIXED. CUSTOMER WAS OUT OF TOWN. REPLACED PRIMARY RISER AND HOT LINE CLAMP. SH VER/ARN IDC XXXX
20885 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-06-02 13:28 | 2016-06-02 15:26 | 1 | 118 | 4285511 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STURP BURNED OFF PRIMARY METERING === NEED BIG BUCKET === REPAIRED STURP POWER OK/ ISO 37830320C10451/ COD 1/ VER/BOW
20886 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-08-28 15:01 | 2008-08-28 16:00 | 2 | 59 | 57028-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3008702// CUT ARRESTER IN CLEAR.//COD 2// VER/DBM IDC XXXX
20887 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-07-31 04:07 | 2009-07-31 06:05 | 1 | 118 | 60145-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T ME FUSE LINK BROKE VER/KEP L3/KEP IDC XXXX
20888 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-08-07 07:36 | 2020-08-07 08:35 | 2 | 59 | 4297741 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link broke. Restored @ 8:35. sh
20889 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-02-19 16:21 | 2009-02-19 17:20 | 2 | 59 | 65620-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008001// WR# 28600888--BROKEN FUSE LINK//COD 2// VER/DBM IDC XXXX
20890 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-03-21 18:50 | 2020-03-21 19:49 | 2 | 59 | 4500121 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Looked everything over looked good took fuse down and seen it was broke,Refused and restored service at 19:49.
20891 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-05-02 14:06 | 2009-05-02 15:05 | 2 | 59 | 63166-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP ANOTHER CUTOUT FAILED. COD-2 37820194C00086 L3/HFP IDC XXXX
20892 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-02-28 12:16 | 2018-02-28 13:15 | 2 | 59 | 4890201 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | refused xfmr. fuse appeared to have broke.
20893 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-01-08 16:25 | 2019-01-08 18:23 | 1 | 118 | 4641551 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | servicer on site/xfmr fuse open/vem/broken cutout/FETR 1830/vem/repairs made and all cust restored 1823/please close ticket/thanks/vem
20894 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-03-23 13:45 | 2012-03-23 15:43 | 1 | 118 | 4609141 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD ENCLOSED CUTOUT/SERVICER TO CHANGE CUTOUT AND LA WHEN RAIN PASSES /FETR1615/VEM/REPAIRS MADE AND POWER RESTORED 1543/PLEASE CLOSE TICKET/VEM // COD 1// VER/DBM IDC XXXX
20895 | Hazard | 3303901 | LESLIE | HYDEN | 2011-11-25 12:05 | 2011-11-25 14:03 | 1 | 118 | 4113951 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP ON POLE 412-282 BURNT OFF, REPLACED HOT LINE CLAMP AND RESTORED ALL POWER @ 14:03 HRS..P.HICKS//COD 1//ISO// VER/DBM IDC XXXX
20896 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-12-31 09:37 | 2014-12-31 11:35 | 1 | 118 | 4894451 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 4TH OR 5TH TIME XFR HAS BEEN OUT,NEED CREW TO REPLACE IT,NEED 45KVA 19.9.POSSIBLY TRUCK ACCESSABLE RELEASED BY CREW 074S06// VER/CRB
20897 | Pikeville | 3408103 | SALISBURY | MARTIN | 2018-06-25 11:07 | 2018-06-25 13:05 | 1 | 118 | 4661921 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | t6 transformer fuse look like fuse broke put in new fuse everthing ok
20898 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-06-28 10:52 | 2022-06-28 12:50 | 1 | 118 | 4339621 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout on pole 161-143. bak in @ 12:50. complete
20899 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-11-26 17:42 | 2019-11-26 19:40 | 1 | 118 | 4070821 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | attempted to call customer but rings off hook//no response //bad cutout// power restored at 19:40/ ISO 38830236000154/ COD 1
20900 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2021-04-14 11:25 | 2021-04-14 13:23 | 1 | 118 | 4450781 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt up/repairs made. pls close. tre
20901 | Hazard | 3309302 | VICCO | JEFF | 2016-08-13 09:38 | 2016-08-13 11:36 | 1 | 118 | 4769871 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | FUSE BROKE VER/AWD
20902 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-12-04 17:21 | 2010-12-04 18:20 | 2 | 59 | 63054-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN 6T FUSE// COD 2// VER/DBM IDC XXXX
20903 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-04-03 22:31 | 2009-04-03 23:30 | 2 | 59 | 64956-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ANOTHER CUTOUT FAILED. COD 2 - VER/TOM L3/TOM IDC XXXX
20904 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-08-09 19:04 | 2019-08-09 20:03 | 2 | 59 | 4866401 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1126-C-132, checking. Trans. fuse broke, refused @2003.
20905 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-04-03 09:11 | 2021-04-03 11:09 | 1 | 118 | 4415691 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced 2 connections
20906 | Pikeville | 3421001 | BREAKS | CITY | 2008-01-30 11:32 | 2008-01-30 13:30 | 1 | 118 | 62224-1 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PARTIAL POWER COMING TO METER. IM CHECKING IT NOW. SERVE-END BURNED INTO ON A HOT LEG ON S/DROP. I RESQUEZZED CONNECTIONS. VER/HFP IDC XXXX
20907 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2009-02-18 10:39 | 2009-02-18 12:37 | 1 | 118 | 64097-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3400101// RELEASED BY CREW 074S043400101// SECONDARY RISER WIRE BURN-INTO
20908 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-03-08 23:20 | 2009-03-09 01:18 | 1 | 118 | 56393-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28836864// CSP XFMR BAD WILL REQUIRE A CREW WITH A MATERIAL HANDLING JIB CUSTOMER AGREED TO WAIT TILL MORNING// CLOSE TICKET WILL BE WORKED ON WR# 28837593 L3/HFP IDCC CDC96 XXXX
20909 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-09-29 19:17 | 2019-09-29 21:15 | 1 | 118 | 4072351 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout replaced and back in at 21:15
20910 | Hazard | 3309302 | VICCO | JEFF | 2020-07-09 07:45 | 2020-07-09 09:43 | 1 | 118 | 4133741 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken XFMR cutout on pole 346-C-617, replaced and power restored at 9:43.
20911 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-03-15 11:27 | 2013-03-15 13:25 | 1 | 118 | 4907811 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, GOT WALLACE MELTON AND CALVIN WILLIAMS COMMING TO HELP ///VER/CRB L/3 CRB IDC XXXX
20912 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-08-15 15:05 | 2019-08-15 16:04 | 2 | 59 | 4892401 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1,6 amp fuse pull into on pole 38831108C00051//COD 2 L3/HFP
20913 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-05-21 13:49 | 2015-05-21 15:47 | 1 | 118 | 4453541 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER , SERVICE LEAD BURNT INTO DUE TO LOOSE CONNECTION, MADE REPAIRS RESTORED POWER AT 15:47.. VER/HFP L3/HFP
20914 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2022-01-18 10:52 | 2022-01-18 12:50 | 1 | 118 | 4380461 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke on 810-744. Replacing. Replaced and restored @ 12:50. sh
20915 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-10-30 12:42 | 2011-10-30 14:40 | 1 | 118 | 4037341 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR ON OPEN WIRE SECONDARY, MADE REPAIRS RESTORED POWER AT 14:40, ONLY ONE CUSTOMER AFFECTED///VER/CRB IDC XXXX
20916 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-04-28 08:34 | 2011-04-28 10:32 | 1 | 118 | 51065-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED XFMR.....ALL OK NOW//VER/CRB IDC XXXX
20917 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-04-12 07:00 | 2008-04-12 08:58 | 1 | 118 | 50327-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HAD 1 LEG ON XFMR RISE BURNED INTO -REPLACED RISER -CHECKED VOLTAGE ON XMFR -IT IS GOOD -CPR VER/HFP IDC XXXX
20918 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-01-20 15:06 | 2015-01-20 16:05 | 2 | 59 | 4947661 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPAIRED FUSE LINK/COD 2// VER/ ADH
20919 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-03-25 10:56 | 2018-03-25 12:54 | 1 | 118 | 4092651 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke and blowed line fuse on pole 217-163 will make repairs/// Changed bad cutout and restored service @12:54
20920 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-08-05 19:28 | 2015-08-05 20:27 | 2 | 59 | 4101211 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BROKE ON POLE37830328B00031 WILL BE CHANGING. VER/CRB
20921 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-01-08 23:47 | 2008-01-09 01:45 | 1 | 118 | 54884-1 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT VER/KEP IDC XXXX
20922 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-05-17 15:17 | 2013-05-17 17:15 | 1 | 118 | 4127371 | 118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN ON TRANS. POLE 26-191. I AM GOING TO CHANGE CUTOUT.///VER/CRB L/3 CRB IDC XXXX
20923 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-07-02 12:03 | 2009-07-02 14:01 | 1 | 118 | 61703-1 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION ON POLE COD-1 VER/KEP L3/KEP IDC XXXX
20924 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2014-07-14 17:17 | 2014-07-14 19:15 | 1 | 118 | 4243701 | 118 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON XFMR BANK, I CHANGED IT OUT AND REFUSED IT//COD 1// VER/DBM
20925 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-07-22 15:28 | 2015-07-22 17:25 | 1 | 117 | 4932421 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | OPEN SERVICE NEUTRAL WERE IT WAS SPLICED, TENSION SPLICE PULL INTO. RESPLICED POWER RESTORED. SEND TO CLAIMS DEPT. CUSTOMER WILL PROBABLY CALL, SHE SAID HER MICROWAVE WAS BURNT UP./ ISO 37830225D00129/ COD 1/ VER/BOW
20926 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-09-09 16:50 | 2015-09-09 18:47 | 1 | 117 | 4218781 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEC. BURNT OPEN RECONNECTED../ 1 CUSTOMER AFFECTED ONLY/ ISO 37830310000165/ COD 1/ VER/BOW
20927 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2010-02-27 15:48 | 2010-02-27 17:45 | 1 | 117 | 61583-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE WIRE BURNT INTO/// SPLICED AND ADDED SOME SERVICE. POWER RESTORED VER/HFP L3/HFP IDC XXXX
20928 | Hazard | 3310502 | HADDIX | CANOE | 2015-01-03 03:18 | 2015-01-03 05:15 | 1 | 117 | 4899621 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT . FUSE BROKE , CLOSED XFMR BACK @ 05:15 VER/SEF VER/DKG L3/DKGXXXX
20929 | Hazard | 3303901 | LESLIE | HYDEN | 2008-05-04 13:54 | 2008-05-04 15:51 | 1 | 117 | 56960-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3303901//REPAIRED BAD XFMR LUG// COD 1// VER/DBM IDC XXXX
20930 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-03-25 11:12 | 2011-03-25 13:09 | 1 | 117 | 59252-1 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS IF ANY////////SERV-IN HAD COME APART,REPLACED ALL,ALL OK AFTERWARDS VER/KEP IDC XXXX
20931 | Whitesburg | 3314401 | MAYKING | ERMINE | 2010-12-08 12:33 | 2010-12-08 14:30 | 1 | 117 | 64396-1 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED XFMR UP AT 14:05 TO REPAIR CONNECTION CLOSED AT 14:30 M.D.I.//COD 1 (+2 SEE H 64396-1) // VER/DBM IDC XXXX
20932 | Hazard | 3303902 | LESLIE | WOOTON | 2011-12-09 16:53 | 2011-12-09 17:32 | 3 | 39 | 4165881 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ON SITE REPLACING BAD TRANSFORMER ///VER/CRB IDC XXXX
20933 | Hazard | 3309301 | VICCO | REDFOX | 2012-02-24 09:18 | 2012-02-24 11:15 | 1 | 117 | 4492101 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER DOUG CHRISTIAN - TRANSFORMER ON POLE 37830349D10163 IS BAD AND NEEDS CHANGED...XFMER REPLACED @11:15 POWER RESTORED...CPS COD-1 ISO TF 37830349D10163 VER/HFP L3/HFP IDC XXXX
20934 | Pikeville | 3414901 | FISHTRAP | DISTRIBUTION | 2017-03-24 18:08 | 2017-03-24 18:47 | 3 | 39 | 4583341 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SEE DOL 729695//FEEDER OUTAGE TO MAKE SAFE REPAIRS TO REGULATOR BYPASS SWITCHES ON POLE 37820053000311//COD 4//OPENED CB AT 1808// VER/ARN
20935 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-11-24 13:39 | 2012-11-24 15:36 | 1 | 117 | 4417881 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHECKING. CUT- OUT AND ARRESTOR BOTH FAILED AT THIS LOCATION, WILL BE MAKING REPAIRS. CHANGED C/O AND ARRESTOR, CLOSED BACK IN AT 15:36. COD-1 ISO TF 37830446000044 VER/HFP L3/HFP IDC XXXX
20936 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-07-02 14:18 | 2009-07-02 16:15 | 1 | 117 | 62222-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT ON TRANSF == REPLACED CUTOUT == COD-1 ISO TF 37830419B00321 L3/HFP IDC XXXX
20937 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2009-02-26 21:18 | 2009-02-26 23:15 | 1 | 117 | 51925-1 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP SPLICE BURNED INTO,WILL REPAIRSERVE-IN CONNECTIONS HEATED UP,BURNED INSULATION OFF AND SHORTED OUT BURNING NEUTRAL INTO ALSO.POSSIBLE DAMAGES HERE ALTHO CUST SAID ALL APPEARED TO BE OK BEFORE I LEFT AFTER MAKING REPAIRS//VER/CRB IDC XXXX
20938 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-04-29 00:28 | 2009-04-29 02:25 | 1 | 117 | 56680-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701// 29577675 BAD CUTOUT ON POLE 212-205 , CHANGED IT OUT POWER BACK ON. IDC XXXX
20939 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-03-26 21:48 | 2015-03-26 23:45 | 1 | 117 | 4233031 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 352-173, REPLACED CUTOUT RESTORED POWER AT 23:45.//COD 1// VER/DBM
20940 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2014-01-24 09:20 | 2014-01-24 11:17 | 1 | 117 | 4307651 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 4/3 SER. DROP BAD SPLICE REPAIRED POWER RESTORED37/PLEASE CLOSE TICKET/THANKS/VEM
20941 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2020-08-27 20:51 | 2020-08-27 21:30 | 3 | 39 | 4391071 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad c/o door, have door rep all power restored at this loc, at 2130, then i trimmed a lot of limbs so could work from the ground with long stick, at this lol
20942 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2015-09-09 11:13 | 2015-09-09 13:10 | 1 | 117 | 4217061 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT IS BROKE. R. MAYNARD IS COMING TO SERVE AS QUALIFIED OBSERVER WHILE I REPLACE IT. REPLACED CUTOUT AND RESTORED @ 13:10. SH VER/CRB
20943 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2018-02-16 16:33 | 2018-02-16 18:30 | 1 | 117 | 4852391 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 418-132 on fire, extinguished fire and replaced cutout. power to 1 customer restored at 18:30. Send something to Doug Christian about getting this looked at for replacement on monday/ ISO 37830418000132/ COD 1*** per servicer
20944 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-08-08 15:33 | 2022-08-08 17:30 | 1 | 117 | 4705441 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | ryan newsomew reports trans fuse out at this location customer contact 606 496 5038. bad cutoy in bank..opened 2 other cutouts at 16:50.back on at 17:30
20945 | South Williamson | 3411401 | DEWEY | INEZ | 2008-06-13 10:15 | 2008-06-13 12:12 | 1 | 117 | 63794-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411401// LOOSE CONN ON HOT LEAD ON TRANSF POLE// VER/DBM IDC XXXX
20946 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2019-01-27 12:03 | 2019-01-27 14:00 | 1 | 117 | 4725941 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on trl pole affecting one customer, repaired
20947 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-02-08 07:03 | 2017-02-08 09:00 | 1 | 117 | 4370221 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED-RED SQUEEZE-ON PULLED APART , I REPLACED IT/ ISO 37830306000120/ COD 1/ VER/BOW L3/HFP XXXHFP
20948 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-07-11 11:18 | 2008-07-11 13:15 | 1 | 117 | 51159-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401103//...15 KVA BAD...CALLED TIM THOMAS...TO BRING A CREW TO CHG. OUT...BB // COD 1// VER/DBM IDC XXXX
20949 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-12-03 17:06 | 2019-12-03 17:45 | 3 | 39 | 4121071 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer restored//MADE MD COD SHOULD BE 3//ORDER 4121081 IS THE SAME AS THIS ORDER
20950 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2018-09-25 12:03 | 2018-09-25 14:00 | 1 | 117 | 4155361 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | secondary hot leg and netural splice fail,only 1 customer L3/HFP
20951 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-05-03 12:12 | 2016-05-03 12:51 | 3 | 39 | 4169551 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ON SITE---FOUND BAD CUTOUT ON XFMR POLE 116-694---WHILE MAKING REPAIRS TO SERVICE DROP---CREW MAKING REPAIRS--CHANGED CUTOUT AND SERVICE---TBL TKT COMP/ ISO 38830116A00694/ COD 3/ VER/BOW
20952 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2017-10-08 17:48 | 2017-10-08 19:45 | 1 | 117 | 4423001 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER METER BLANK BAD C/O ON POLE 879-184, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC BY AMG AT 1945/ ISO 39830879D00184/ COD 1/ VER/BOW L3/HFP XXXHFP
20953 | Paintsville | 3401102 | FALCON | SALYERSVI | 2021-11-26 23:48 | 2021-11-27 01:45 | 1 | 117 | 4127461 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | kearney serve end froze open.replaced 3 serve ends..
20954 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2011-12-24 12:33 | 2011-12-24 14:30 | 1 | 117 | 4200201 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-1 ISO PO 37830187A00279 VER/HFP L3/HFP IDC XXXX
20955 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-12-06 16:03 | 2016-12-06 18:00 | 1 | 117 | 4171841 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 290-276BAD CUTOUT ON POLE 29-276 . REPLACED CUTOUT . VER/CRB L3/HFP XXXHFP
20956 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-10-29 22:38 | 2011-10-30 00:35 | 1 | 117 | 4036261 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SOMEONE HAS USED WRONG CONNECTIONS ON SERVICE DROP AT WEATHER HEAD. THEY GOT HOT AND SERVICE DROP SHORTED OUT. I AM GOING TO REPLACE DROP. I REPLACED #4/3 DROP WITH A 2/3. - AFFECTING 1 CUSTOMER ONLY IDCC PN61, CNT11 XXXX
20957 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2021-11-04 11:09 | 2021-11-04 13:06 | 1 | 117 | 4056761 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse out on pole 1084A-7.cutout door had burned into.relpaced door and got fuse back in at 13:06
20958 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-12-18 06:51 | 2013-12-18 07:30 | 3 | 39 | 4172171 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 12KV CUTOUT VER/CRB VER/HFP L3/HFP
20959 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-03-29 09:14 | 2013-03-29 11:11 | 1 | 117 | 4966091 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL IN SERVICE DROP HAD PULLED OUT OF SLEEVE. I AM GOING TO SPLICE NEUTRAL. ONLY SERVES CAMPER. I SPLICED NEUTRAL. VER/HFP L3/HFP IDC XXXX
20960 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2010-09-06 09:30 | 2010-09-06 11:27 | 1 | 117 | 63953-1 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKE AT MAST. NO VISIBLE CAUSES, CHANGED SERVICE DROP. POSSIBLE DAMAGE COMPLAINT, CUSTOMER STATING SEVERAL THINGS IN HOUSE NOT WORKING. VER/HFP L3/HFP IDC XXXX
20961 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-01-06 14:53 | 2014-01-06 16:50 | 1 | 117 | 4238431 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | A SPLICE IN THE SERVICE NEUTRAL PULLED OUT VER/HFP L3/HFP
20962 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-03-19 17:48 | 2008-03-19 19:45 | 1 | 117 | 58860-1H | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3311101// CREW OPENING UP RECLOSER TO REPLACE BROKEN INSULATOR AND RETIE PHASE WIRE/// RELATED TO ORDER 58814-1// VER/KEP IDCC 1 CUSTOMER OUT AT 1748, DUP CREATED DUPLICATE FOR SINGLE CUSTOMER XXXX
20963 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2012-03-24 15:36 | 2012-03-24 16:15 | 3 | 39 | 4612851 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE //VER/CRB IDC XXXX
20964 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2008-10-08 11:16 | 2008-10-08 11:55 | 3 | 39 | 54269-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT FAILED ON POLE #78 & TOOK OUT LINE FUSE ON POLE#38831003D00091 ISOLATED BAD CUT OUT & RESTORED POWER . WILL NOW REPLACE BAD CUTOUT. IDCC CNT1 XXXX
20965 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2008-11-05 11:03 | 2008-11-05 13:00 | 1 | 117 | 62372-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007905//REPLACED BAD CUTOUT.//VER/CRB IDC XXXX
20966 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-07-20 08:33 | 2021-07-20 10:30 | 1 | 117 | 4937191 | 117 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | service connection burnt out. made repaires
20967 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-11-08 13:02 | 2009-11-08 13:41 | 3 | 39 | 50985-1 | 117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WORK REQ # 32579949 //REPLACED BAD CUTOUT DOOR NO CREW REQUIRED COD-3 ISO TF 38830269A00186 L3/HFP IDC XXXX
20968 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-09-05 21:09 | 2008-09-05 22:07 | 2 | 58 | 59774-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401001//BAD CUTOUT. REPLACED......DAH COD-2 VER/LDA IDC XXXX
20969 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2022-07-24 18:34 | 2022-07-24 20:30 | 1 | 116 | 4569391 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Neutral connection broke on customers service drop, made repairs @2030. Only 1 customer was affected.
20970 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2010-12-14 21:34 | 2010-12-14 23:30 | 1 | 116 | 50315-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | INSULINK SPLICE MELTED OUT & BURNT CUSTS SERVICE NEUTRAL & ONE HOT LEG IN TWO....WILL REPLACE...//...REPLACED SERVICE DROP....JRV....12/14/10// VER/DBM IDC XXXX
20971 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2021-10-25 09:02 | 2021-10-25 10:00 | 2 | 58 | 4009111 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | Burnt up cutout gate. Power restored at 10:00.
20972 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-03-18 15:19 | 2014-03-18 17:15 | 1 | 116 | 4506081 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 076S02 TRANSFORMER FUSE BROKEN ON 808-8.TV BOOSTER OUT.. COD 1 ****CHANGE ISO POLE****** VER/SEFDC XXXX
20973 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-12-01 16:19 | 2011-12-01 17:17 | 2 | 58 | 4134281 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMER FUSE OPEN CHECKING NOW . FUSE BROKE//COD 2// VER/DBM IDCC CCU XXXX
20974 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2014-10-20 20:04 | 2014-10-20 22:00 | 1 | 116 | 4647711 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOURT BROKE WILL CHANGE///// CHANGED BROKEN CUTOUT AND RESTORED SERVICE @ 22:00// COD 1//VER/ ADH
20975 | Hazard | 3311103 | STINNETT | WENDOVER | 2017-10-28 14:50 | 2017-10-28 15:48 | 2 | 58 | 4505121 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT RELEASED BY CREW 077H14BAD CUTOUT OPENED AT 14:50 CLOSED BACK AT 15:48 VER/AWD L3/HFP XXXHFP
20976 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2012-07-16 11:05 | 2012-07-16 13:01 | 1 | 116 | 4737741 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-3060 BAD CUTOUT REPLACED CCC ENTERED MD COD-1 ISO TF 38830045B33060 VER/HFP L3/HFP
20977 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-03-28 19:29 | 2019-03-28 21:25 | 1 | 116 | 4034011 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | called customer - no answer//bad connection on pole//
20978 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-05-16 08:14 | 2008-05-16 10:10 | 1 | 116 | 64586-1 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3404302//, ON SITE, CONNECTION BURNT OFF AT WEATHERHEAD, MAKING REPAIRS VER/HFP IDC XXXX
20979 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2022-06-22 16:31 | 2022-06-22 17:00 | 4 | 29 | 4277081 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrestor/// power restored 17:00
20980 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2010-11-27 15:54 | 2010-11-27 16:52 | 2 | 58 | 60067-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WR#37892219 POLE 68-6055 BROKE NEED 35 CLASS 5 TRUCK TO POLES RELEASED BY CREW 078S08/TECH TO WRITE JOB/CREW ON SITE REPLACING POLE/NO OUTAGE/POLE CHANGED//TWO SERV DROP OUTAGED ABOUT AN HOUR/PLEASE CLOSE TICKET //THANKS/VEMVEM/VER/CRB IDC XXXX
20981 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2016-02-21 13:35 | 2016-02-21 15:31 | 1 | 116 | 4743701 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 190-59 PER TOM CANTRELL // ONE CUSTOMER OUT AT THIS TIME, OFF TIME 1335 RELEASED BY CREW 078S11/CREW ON SITE/WILL NEED TO OPEN FUSE 190-19 FOR REPAIRS/APROX ONE HOUR OUTAGE/VEM/OPEN LINE FUSE AT 1447/REPAIRS MADE AND ALL CUST RESTORED 1531/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
20982 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-12-25 12:47 | 2017-12-25 13:45 | 2 | 58 | 4677441 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout door burnt up will replace//// Replaced cutout and restored service @13:45
20983 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-06-04 09:40 | 2015-06-04 11:36 | 1 | 116 | 4509961 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION AT WEATHER HEAD APR AT 11 36 CLOSE TICKET// VER/ ADH
20984 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-01-05 07:34 | 2016-01-05 09:30 | 1 | 116 | 4585791 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 37820001000253 // REPLACED // POWER RESTORED @ 09:30 // ONLY 1 CUST OUT VER/CRB
20985 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2022-07-07 08:24 | 2022-07-07 10:20 | 1 | 116 | 4416941 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 2 fuses blown on xfm bank 79-216 will refuse///B phase cutout broke//changed bad cutout and refused xfms @ 10:20 and restored full power
20986 | Hazard | 3302703 | HAZARD | HAZARD | 2016-08-12 19:02 | 2016-08-12 19:31 | 4 | 29 | 4768641 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE/ ISO 37830272D20436/ COD 4/ VER/BOW
20987 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-08-18 12:30 | 2015-08-18 12:59 | 4 | 29 | 4147711 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078H06///PRIM NEUT BURNT DOWN IN SQUEEZE ON ALUM/CU.---OPENED XFMR ON PL#181 TO MAKE REPAIRS///XFMR OPENEED @ 12:30----BACK IN@ 12:59///TBL TKT COMP
20988 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-03-29 18:45 | 2012-03-29 20:41 | 1 | 116 | 4632651 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VOLTAGE CHECKS SHOW AN OPEN NEUTRAL.GOING TO TROUBLESHOOT.REPLACED CONNECTIONS ON HOUSE AND SECONDARY POLE.FOUND BROKEN NEUTRAL ON XFMR POLE 37830068000019.VOLTAGE CHECKS GOOD NOW.CUSTOMER SAYS EVEYTHING BACK TO NORMAL BUT STATED THEY HAD ALOT OF DAMAGES.SAID THEY CALLED THIS PROBLEM IN A WHILE BACK.PLEASE SEND TO PEGGY /// COD-1 ISO TF 37830068000019 VER/HFP L3/HFP IDCC TOF1602 ESTIMATED TIME OFF FOR REPAIR XXXX
20989 | Pikeville | 3413401 | GARRETT | GARRETT | 2021-10-17 13:20 | 2021-10-17 14:18 | 2 | 58 | 4359411 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Nuetral broke in secondary @ 37830041A10267.// Will open xfm @ 37830041A10161 to make repairs.//Xfm off @ 13:20//Repaired and restored @ 14:18
20990 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-12-31 12:04 | 2018-12-31 14:00 | 1 | 116 | 4615571 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout changing
20991 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2010-07-16 12:04 | 2010-07-16 14:00 | 1 | 116 | 50896-1 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR WENT BAD IN SPLICE// CALLED CREW TO HELP CHANGE DROP VER/HFP L3/HFP IDC XXXX
20992 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2021-08-08 17:04 | 2021-08-08 19:00 | 1 | 116 | 4019041 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | sd neutral
20993 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-05-20 12:32 | 2010-05-20 13:30 | 2 | 58 | 65599-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CREW OPENED TR TO REPLACE ARRESTER.;//VER/CRB IDC XXXX
20994 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-10-23 11:34 | 2015-10-23 13:30 | 1 | 116 | 4371311 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A, TANK MOUNT KIT OR MOUNT ON STANDOFF.. TRUCK ACCESSABLE, COPY TO L RAYBURN/AED CREATED/EMAILED LLYOD/ VER/KEP
20995 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-08-16 17:15 | 2013-08-16 19:11 | 1 | 116 | 4671681 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | OPENED XFMR FOR REPAIRS/RESAG OPEN WIRE SECONDARY/ ANCHOR RUSTED OUT/PLEASE COPY TICKET TO VERNON MULLINS FOR ANCHOR INSTALL/SHOULD HAVE XFMR BACK IN 1900/VEM/REPAIRS MADE AND POWER RESTORED TO PUMP HOUSE AT 1911/PLEASE CLOSE TICKET/THANKS/VEM VER/SEF IDCC PN122 XXXX
20996 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-11-24 10:12 | 2010-11-24 11:10 | 2 | 58 | 59279-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37879651 // POLE 92-384 CHGED BAD CUTOUT AND LA COD-2 VER/HFP L3/HFP IDC XXXX
20997 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-05-11 19:59 | 2014-05-11 21:55 | 1 | 116 | 4686631 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED TRANSFORMER CUTOUT, ALL WORK COMPLETE / GXJ VER/ARN
20998 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2020-07-11 14:04 | 2020-07-11 16:00 | 1 | 116 | 4152551 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | old c/o door did not drop when fuse blow, causing the fiberglass door to get hot and smoke, chged c/o all good at this loc at this time time on 1600
20999 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2017-02-06 15:17 | 2017-02-06 17:13 | 1 | 116 | 4361951 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE VER/CRB L3/HFP XXXHFP
21000 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-10-24 13:29 | 2022-10-24 15:25 | 1 | 116 | 4060061 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse // RESTORED @ 15:25
21001 | Hazard | 3310502 | HADDIX | CANOE | 2018-08-06 22:13 | 2018-08-07 00:09 | 1 | 116 | 4916061 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | attempted to call customer//no answer// change cutout//cod 1
21002 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-04-04 08:04 | 2008-04-04 10:00 | 1 | 116 | 63709-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3408402// RELEASED BY CREW 074S053408402// CSP TRANSFORMER BAD ON POLE 54-55 REM HOT TAP OFF LINE//COD 1// VER/DBM IDC XXXX
21003 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-09-06 06:57 | 2015-09-06 07:55 | 2 | 58 | 4208901 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINKE BROKE VER/SEF
21004 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-11-18 07:04 | 2011-11-18 09:00 | 1 | 116 | 4089241 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REMADE CONNECTION ON XFMR POLE ///VER/CRB IDC XXXX
21005 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2008-02-07 15:04 | 2008-02-07 17:00 | 1 | 116 | 52468-1 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 30000802//CHANGED SER WIRE AND RESQUEEZED ALL CONNECTIONS, ONLY HAD HALF POWER, COULD NOT FIND VISIBLE FAULT VER/HFP IDC XXXX
21006 | Paintsville | 3401101 | FALCON | FALC-OILS | 2016-04-12 16:19 | 2016-04-12 18:15 | 1 | 116 | 4086061 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED 6 SERVE ENDS.SPLICED S/D. VER/CRB
21007 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-03-03 12:02 | 2010-03-03 13:58 | 1 | 116 | 62490-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | I SPOKE WITH THE CUSTOMER AND THIS WILL TAKE A 4-WHEELER TO GET TO THIS SITE THEY SAID IT WOULD BE O.K. TO WAIT TILL MORNING TO CHECK THIS OUT. THEY ALSO SAID THAT THEY HAD NO POWER AND THEY SAW THE NEUTRAL BROKEN AT THE WEATHER HEAD. SEND A NOTE TO TIM HALL TO REMIND HIM OF THIS FOR IN THE MORNING. TIM MCCOY RELEASED BY CREW 074H10 VER/HFP L3/HFP IDCC MCCDIS, CCO XXXX
21008 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2018-06-13 08:49 | 2018-06-13 10:45 | 1 | 116 | 4595351 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral wire broke in service drop . made repairs restored power at 10:45
21009 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-11-27 09:34 | 2017-11-27 11:30 | 1 | 116 | 4603841 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customers neutral in service drop broke mid span, replaced service drop restored power at 11:30..only one customer affected..
21010 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-09-30 21:52 | 2009-09-30 22:50 | 2 | 58 | 60422-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD FUSE LINK.
21011 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-12-04 10:43 | 2015-12-04 11:41 | 2 | 58 | 4509741 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | XFMR BANK FUSE MELTED OUT , RESTORED POWER AT 11:41.// VER/ ADH
21012 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-03-27 13:04 | 2019-03-27 15:00 | 1 | 116 | 4030411 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF XFMRHot tap burn off will repair/// replaced hot tap and cutout //restored @ 15:00
21013 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-03-21 18:26 | 2011-03-21 20:22 | 1 | 116 | 56490-1 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION//VER/CRB IDCC MCCDL XXXX
21014 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-01-22 17:29 | 2012-01-22 19:25 | 1 | 116 | 4282721 | 116 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD CONN. ON POLE REPAIRED ///VER/CRB IDC XXXX
21015 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-07-12 22:35 | 2010-07-12 23:33 | 2 | 58 | 65766-1 | 116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE ON POLE 38830206C02301, CORRECT TRANSFORMER OUT IS 38830206C02301, 664 EASTVIEW IS MISMAP COD-2 MD FILED VER/KEP L3/KEP IDC XXXX
21016 | Hazard | 3309302 | VICCO | JEFF | 2008-11-08 06:41 | 2008-11-08 08:36 | 1 | 115 | 63201-1 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED D/S FOR CREW. FUSE PULLED INTO REFUSED XFMR P HICKMAN VER/PDP IDC XXXX
21017 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-01-06 16:58 | 2020-01-06 18:53 | 1 | 115 | 4218611 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer neutral broke @ xfm. pole..made repairs.restored..customer said that they might have appliances burnt up.please send copy to damage complaint.
21018 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2013-12-05 15:53 | 2013-12-05 17:48 | 1 | 115 | 4102281 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 517-15, OPENED LINE FUSE ON POLE 517-14 AT 17:05 TO ISOLATE , MADE REPAIRS RESTORED POWER AT 17:48. VER/CRB L3/HFP
21019 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-10-02 15:59 | 2010-10-02 17:54 | 1 | 115 | 56296-1 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BAD//////REPLACED BAD C/O. POWER RESTORED//COD 1// VER/DBM IDCC PN487 XXXX
21020 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-02-10 14:20 | 2015-02-10 16:15 | 1 | 115 | 4006041 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT ON POLE 186-178, NEED LINE CREW ONLY PICKUP TRUCK , BLACK TOP DRIVE WAY, NO TRUCKS TO POLE. RELEASED BY CREW 078S01 REPLACED CUTOUT RESTORED POWER AT 16:15 PLEASE CLOSE TICKET THANKS DWW/COD1// VER/ ADH L3/HFP XXX
21021 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-07-07 17:49 | 2018-07-07 19:44 | 1 | 115 | 4749421 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | melted connectionsm repaired, restored
21022 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-09-22 13:23 | 2017-09-22 15:18 | 1 | 115 | 4382371 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD PHASE CONNECTION 37830047D00029 VER/AWD VER/ALB
21023 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2022-03-14 14:35 | 2022-03-14 16:30 | 1 | 115 | 4624341 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connections melted out. Repaired
21024 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2018-04-16 21:23 | 2018-04-16 23:18 | 1 | 115 | 4242731 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse was broken on xform. refuse, power restored/ ISO 38830018000052/ COD 1
21025 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-08-09 13:35 | 2013-08-09 15:30 | 1 | 115 | 4640261 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD FEEDING 3 PHASE PRIMARY UNDERGROUND LATERAL . REPLACED ALL THREE CUOUTS AND ARRESTERS, ALL WORK COMPLETE / GXJ//MADE MDC VER/CRB L/3 CRB
21026 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-03-16 20:09 | 2020-03-16 22:04 | 1 | 115 | 4483911 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | On pole 335-C-141 had a XFM cut out broke made repairs and restored service at 22:04.//cod 1
21027 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2010-08-12 11:20 | 2010-08-12 13:15 | 1 | 115 | 53480-1 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NOW AN OUTAGE....BAD CUT OUT & POLE TOP FIRE POLE 966-A1-701....LIFTED HOT LINE CLAMP @ 11:20...FIRE DEPT HERE....FIRE PUT OUT...POLE NEEDS REPAIRED....CALLING CREW....SEND TO JOEY REED...THANKS....JRV...08/12/10 RELEASED BY CREW 079H08 VER/KEP L3/KEP
21028 | Hazard | 3303902 | LESLIE | WOOTON | 2011-04-28 11:20 | 2011-04-28 13:15 | 1 | 115 | 51347-1 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION//VER/CRB IDCC PN41 XXXX
21029 | South Williamson | 3411401 | DEWEY | INEZ | 2016-11-12 10:35 | 2016-11-12 12:30 | 1 | 115 | 4095711 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 75+ KVA 19.9. THIS IS THE HIGH LEG TRANSFORMER THAT IS NOT BEING USED. I ISOLATED THAT TRANSFORMER TILL IT CAN BE REPLACED.
21030 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-10-18 06:33 | 2022-10-18 08:28 | 1 | 115 | 4038561 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse broke. Restored @ 8:28. sh
21031 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-07 20:15 | 2011-01-07 22:10 | 1 | 115 | 59667-1 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | I OPENED 1.6T FUSE DUE TO BAD CURRENT LIMIT FUSE. I WILL BE MAKING REPAIRS. I HAVE REPAIRS MADE EVERYTHING OK. SEND COPY OF THIS TO PEGGY WYSONG. CUST SAID HE SMELLED SMOKE IN ONE OF THE BED ROOMS. HE SAID LIGHTS GOT REAL DIM SEVERAL TIMES BEFORE POWER WENT OUT. SEND COPY TO BOB SHURTLEFF PIKEVILLE AND TOM MAMING PIKEVILLE.//EMAILED TO APPROPRIATE PERSONNEL//COD 1// VER/DBM IDC TOF1959 CALL WAS DIM ESTIMATED TIME OFF XXXX
21032 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-03-25 12:27 | 2014-03-25 12:50 | 5 | 23 | 4524091 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED TRANS TO MAKE REPAIRS ON ARRESTEROPENED TRANSFORMER AT 12:27 REPLACED CUTOUT AND ARRESTOR, POWER RESTORED AT 12:50 VER/CRB
21033 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2009-03-20 10:26 | 2009-03-20 12:21 | 1 | 115 | 60323-1 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3403701//WILL DETERMINE AND REPAIR IF POSSIBLE#4 SERV BURNED INTO(NEUTRAL),REPLACED WITH #2 DROP// VER/DBM IDC XXXX
21034 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-08-07 09:44 | 2017-08-07 11:39 | 1 | 115 | 4233451 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT AND GOT FIRE PUT OUT COMPLETE VER/HFP L3/HFP
21035 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-11-27 16:50 | 2019-11-27 18:45 | 1 | 115 | 4092261 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke //repaired//restored at1845//complete/ ISO 38820818D00095/ COD 1
21036 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-02-23 17:15 | 2014-02-23 19:10 | 1 | 115 | 4428921 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | #2 SERVE END BAD @ XFMR. REPLACED BOTH CONN. ONLY 1 CUST. OUT.//COD 1// VER/DBM
21037 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2019-10-22 13:36 | 2019-10-22 15:31 | 1 | 115 | 4182151 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | current limiting fuse bad, riser burnt up also. repairs made. pls close. tre
21038 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-11-20 11:47 | 2009-11-20 13:42 | 1 | 115 | 59080-1 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LEAD HAS FALLEN OUT OF HOT-TAP,WILL MAKE REPAIR//MADE REPAIRS AND RESTORED,NEW MINE INSTALLATION HERE VER/KEP L3/KEP IDC XXXX
21039 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-01-27 07:25 | 2011-01-27 09:20 | 1 | 115 | 66134-1 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT //// COD-1 ISO TF 37830178B00225 VER/HFP L3/HFP IDC XXXX
21040 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-02-24 15:55 | 2021-02-24 17:50 | 1 | 115 | 4244321 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken manual cutout on pole 318-C-19, Tim Smith is on his way to help me make repairs. Power restored at 18:03
21041 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-06-05 16:25 | 2018-06-05 18:20 | 1 | 115 | 4558961 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Secondary pole 38830810A40191 broke and on the ground. Power is on but will be opening xfmr 38830810A00101 when crew arrives to replace pole. Emergency dig # 1806051533. Opened xfmr @ 16:25.//COD 1//Secondary pole 38830810A40191 broke and on the ground. Power is on but will be opening xfmr 38830810A00101 when crew arrives to replace pole. Emergency dig # 1806051533. Opened xfmr @ 16:25. Replaced downed pole and restored @ 18:20. sh
21042 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-12-27 14:55 | 2021-12-27 16:50 | 1 | 115 | 4230301 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans cutout broke at pole 261-A1-125,Will be making repairs.Restored at 16:50.
21043 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-06-28 10:20 | 2020-06-28 12:15 | 1 | 115 | 4083271 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Have a broke XFM cutout on 170-33,Will make repairs and restore service..Restored at 12:15..
21044 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-03-27 08:55 | 2011-03-27 10:50 | 1 | 115 | 59646-1 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 39319391 // FOUND BAD SERVE ENDS ON SERVICE DROP ON HOUSE SIDE, HAVE ALL REPLACED AND EVERYTHING IS OK AT THIS LOC VER/HFP L3/HFP IDC XXXX
21045 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2012-01-02 14:05 | 2012-01-02 16:00 | 1 | 115 | 4225581 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER BAD SPLICE IN SERVICE ONLY ONE CUSTOMER AFFECTED, MADE REPAIRS RESTORED POWER AT 1600// VER/DBM IDC XXXX
21046 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-01-21 09:05 | 2010-01-21 11:00 | 1 | 115 | 57115-1 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN..6 T FUSE//VER/CRB IDC XXXX
21047 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2020-04-08 18:00 | 2020-04-08 19:55 | 1 | 115 | 4582641 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 125-118 will make repairs/// Changed bad cutout and restored service @ 19:55
21048 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-05-17 08:00 | 2010-05-17 09:55 | 1 | 115 | 63659-1 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN FAILED AT ENTRANCE, ONLY 1 CUSTOMER AFFECTED, REPLACED ALL CONNECTIONS AT ENTRANCE WITH SQUEEZONS ... ALL WORK COMPLETE / GXJ VER/HFP L3/HFP IDC XXXX
21049 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-11-16 11:20 | 2015-11-16 13:15 | 1 | 115 | 4451361 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 116-54 6T TRANS FUSE BROKE VER/KEP
21050 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-01-02 16:40 | 2020-01-02 18:35 | 1 | 115 | 4204841 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer has broke neutral,will make repairs.Fixed broke neutral checked voltage and it was correct..
21051 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-03-18 21:30 | 2021-03-18 23:25 | 1 | 115 | 4350971 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke trans cutout on 237-B-94,Going to get it changed and restore service.Restored at 23:25./ ISO 37830237B00094/ COD 1
21052 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-11-26 22:20 | 2018-11-27 00:15 | 1 | 115 | 4482221 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SQUEEZON CONNECTION ON 1 HOT LEG AT THE SERVICE TO RISER CONNECTIONS.MADE NECESSARY REPAIRS,ALL OK AFTERWARDS//iso// cod 1// L3/HFP
21053 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-06-07 16:37 | 2016-06-07 18:32 | 1 | 115 | 4321221 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE BETWEEN SERVICE AND ENTRANCE CABLE/ ISO 37830351D00083/ COD 1/ VER/BOW
21054 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2022-08-25 15:00 | 2022-08-25 16:55 | 1 | 115 | 4794441 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer was opened up during flood. Cutout was broke on pole 444-128. Made repairs and restored at 16:55.
21055 | Hazard | 3303902 | LESLIE | WOOTON | 2021-02-23 01:41 | 2021-02-23 03:36 | 1 | 115 | 4226881 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at weather head/ repaired/ customer had part power/ 37830510C40221/ COD 1
21056 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2021-12-02 21:15 | 2021-12-02 23:10 | 1 | 115 | 4143161 | 115 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | had burnt connection. customer was only getting 120.. redid all connections,voltage checks good.
21057 | Hazard | 3310502 | HADDIX | CANOE | 2020-07-22 21:27 | 2020-07-22 23:22 | 1 | 115 | 4210461 | 115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced blown arrester and cutout. at 37830051D20157 (1 CC) Power restored @ 23:22
21058 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2011-05-24 17:03 | 2011-05-24 18:00 | 2 | 57 | 4162081 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | /25 T FUSE ON 38830808000095 APPEARS TO HAVE BROKEN.
21059 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-11-25 07:53 | 2008-11-25 09:47 | 1 | 114 | 52025-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOKS LIKE TRANSFORMER RISER WIRE ON SEC SIDE IS BURNT INTO. I WILL BE OUT OF TRUCK POLE IS BACK ON SIDE OF HILL.//3400301. I HAVE MADE REPAIR ON WIRE EVERYTHING OK.//VER/CRB IDC XXXX
21060 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-09-30 21:24 | 2009-09-30 22:21 | 2 | 57 | 60360-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T BAD CUTOUT DOOR
21061 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-04-28 10:06 | 2015-04-28 12:00 | 1 | 114 | 4372221 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SERVICE DROP CONNECTION AT XFMR VER/CRB
21062 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2022-07-25 09:46 | 2022-07-25 11:40 | 1 | 114 | 4572431 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BROKE MID SPAN
21063 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-05-26 22:07 | 2013-05-26 22:45 | 3 | 38 | H4186551C | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN, 1 CUST HAD PART POWER. TR OUTAGED AT THE FOLLOWING TIMES... 1752-1805 1958-2007 2207-2245. CC 4. ORIGINAL OUTAGE 4186551. DUPLICATE OUTAGES H1181075-1, H1181076-1 & H1181077-1. VER/SDB IDCC CNT1 XXXX
21064 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-05-14 21:14 | 2015-05-14 21:52 | 3 | 38 | 4431201 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED LOOSE APR AT 2152 CLOSE TICKET VER/CRB
21065 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-03-07 02:23 | 2008-03-07 03:20 | 2 | 57 | 54450-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008701// BROKEN FUSE LINK VER/LDA IDCC CNT1 XXXX
21066 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-10-04 08:36 | 2013-10-04 10:30 | 1 | 114 | 4909381 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT SERV TO TRY,CUTOUT BROKE SERV TO CHANGE,REPAIRS MADE ALL CUST RESTORED @1030 PLEASE CLOSE TICKET THANKS.BT VER/SEF L3/HFP IDC XXXX
21067 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-04-08 20:47 | 2010-04-08 22:41 | 1 | 114 | 61371-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT CUTOUT BROKE AND POLE IS ROTTEN, GOING TO TRY GET TRUCK INTO POLE AND CHANGE CUTOUT//COD 1// VER/DBM IDC XXXX
21068 | Whitesburg | 3312901 | JENKINS | KONA | 2019-11-25 16:48 | 2019-11-25 18:42 | 1 | 114 | 4067171 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral wire broke in service drop serving storage building, made repairs restored power at 18:42.
21069 | Paintsville | 3401802 | INDEX | HOSPITAL | 2013-11-26 19:51 | 2013-11-26 21:45 | 1 | 114 | 4078291 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A NEUTRAL BROKE IN SERVICE DROP.. WILL BE MAKING REPAIRS.. REPAIRED NUETRAL BACK TO NORMAL SERVICE AT 21:45.. COMPLETE RN VER/SEF
21070 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2019-01-12 21:58 | 2019-01-12 22:55 | 2 | 57 | 4662511 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE REPLACED IT//cod 2 L3/HFP
21071 | Hazard | 3310502 | HADDIX | CANOE | 2021-09-07 15:06 | 2021-09-07 17:00 | 1 | 114 | 4218191 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse pulled into. restored 17:00
21072 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-07-14 21:23 | 2017-07-14 22:20 | 2 | 57 | 4125221 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 68-1350 6T FUSE BROKE INSTALLED 8T/ ISO 38830068A01350/ COD 2/ VER/BOW
21073 | South Williamson | 3200302 | BELFRY | TOLER | 2009-10-19 08:28 | 2009-10-19 10:22 | 1 | 114 | 56621-1 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP ON SITE, BAD CONNECTION IN 2/3 TRIPLEX SECONDARY, MAKING REPAIRS NEEDS SECONDARY UPGRADED. SENT EMIAL TO RON RYE...HFP L3/HFP IDCC CCO XXXX
21074 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-06-30 19:28 | 2008-06-30 21:22 | 1 | 114 | 60599-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | JRV ON SITE @ 20:30....FOUND BAD HOT CONNECTION ON SECONDARY POLE....WILL REPAIR....//...CONNECTION REPLACED...CUST HAS FULL POWER....JRV ...06/30/08 // VER/TOM IDC XXXX
21075 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-06-17 15:35 | 2020-06-17 17:29 | 1 | 114 | 4035941 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout
21076 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2012-04-02 11:46 | 2012-04-02 13:40 | 1 | 114 | 4639941 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | PRIMARY METERING FUSE BLOWN ON C PHASE, METER IS BURNT ON SIDE OF TANK WILL BYPASS FOR NOW. RESTORED POWER AT 13:40. VER/HFP L3/HFP IDC XXXX
21077 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2017-01-04 15:01 | 2017-01-04 16:55 | 1 | 114 | 4269381 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | MID SPAN SERVICE SPLICE SEEMS TO BE MELTED. POWER RESTORED AT 16:55 VER/CRB L3/HFP HFPC FEC46
21078 | Whitesburg | 3314401 | MAYKING | ERMINE | 2012-12-27 10:03 | 2012-12-27 11:00 | 2 | 57 | 4537081 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE MELTED OUT ON XFMR BANK ON POLE 449-844, RESTORED POWER AT 11:00 //VER/GAH
21079 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-04-09 07:46 | 2010-04-09 09:40 | 1 | 114 | 61448-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 4/3 SERVICE DROP BURNT INTO IN A SPLICE ABOUT MID SPAN. NEUTRAL AND HOT CONDUCTORS BURNT INTO. I CHANGED 4/3 DROP TO 2/3 DROP. RECONNECT CUST. HE SAID EVERYTHING WAS OK. DUE TO NEUTRAL BEING BURNT INTO CUST COULD HAVE DAMAGE.//VER/CRB IDC XXXX
21080 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-08-31 15:26 | 2008-08-31 17:20 | 1 | 114 | 58031-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP STS WORK REQUEST # 26040827 // 1.6T TRANSFORMER FUSE BROKE. FUSED UP EVERYTHANG OK. IDC XXXX
21081 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-04-28 15:47 | 2010-04-28 16:25 | 3 | 38 | 52522-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED SECONDARY//COD 3// VER/DBM IDC XXXX
21082 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-04-20 15:09 | 2022-04-20 17:03 | 1 | 114 | 4783931 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER DOUG HALL PLEASE REFUSE TRANSFORMER AND REPAIR GROUND//Have a Broke cutout 193-D-390,Will be making repairs./Have a Broke cutout 193-D-390,Will be making repairs.Restored Trans fuse at 17:03,and Replaced Pole Ground down pole.
21083 | South Williamson | 3200302 | BELFRY | TOLER | 2022-04-07 18:12 | 2022-04-07 20:06 | 1 | 114 | 4738641 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | transformer fuse out on pole38820990C40462.service wire down..i will be making repairs.got transformer fuse on pole 38820990C40462 back in at 20:06
21084 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-05-19 20:24 | 2017-05-19 22:18 | 1 | 114 | 4822101 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPS 038993098. BAD 10 KVA 19.9, NO TRUCK ACCESS. CAN BLOCK FROM POLE WITH A LINE TRUCK, LEVEL GROUND ACROSS CREEK. CAN ALSO OPEN THE TAP, ONLY ONE MORE CUSTOMER ON THE TAP. CUTOUT AND BRACKET NEEDS REPLACED. SENT TO TIM HALL VER/CRB
21085 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2022-02-18 10:53 | 2022-02-18 12:47 | 1 | 114 | 4510571 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Service red to red connection failed. Gonna have to open up Xfrm on pole 419-D-45 to make repairs. Opened xfrm at 12:42 closed back at 12:47.
21086 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2014-03-18 12:46 | 2014-03-18 14:40 | 1 | 114 | 4505451 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD INSULINK AT WEATHER HEAD. REPLACED ALL CONNECTIONS EVERYTHING OK. HOT CONDUCTOR WAS APART AT WEATHER HEAD. VER/SEF
21087 | Paintsville | 3410602 | E.PRESTON | LANCER | 2022-03-08 14:55 | 2022-03-08 15:52 | 2 | 57 | 4590221 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @979-C-17, checking. Trans. fuse pulled into, refused @1552.
21088 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-01-22 14:43 | 2020-01-22 15:40 | 2 | 57 | 4329661 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout is broke I will replace// Replaced cutout and restored power @ 15:40 L3/HFP
21089 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-04-24 17:01 | 2017-04-24 18:55 | 1 | 114 | 4677981 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER BAD SPLICE IN SERVICE DROP, MADE REPAIRS RESTORED POWER AT 18:55.. VER/CRB L3/HFP HFPC FEC66
21090 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-11-18 16:26 | 2014-11-18 18:20 | 1 | 114 | 4743051 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN WILL REFUSE/// REFUSED TRANSFORMER AND CUTOUT IS BROKE WILL CHANGE//// CHANGED BAD CUTOUT AND RESTORED SERVICE @ 18:20 COD-1 ISO TF 38831099B20027 VER/HFP L3/HFP
21091 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-06-15 09:56 | 2009-06-15 11:50 | 1 | 114 | 65546-1 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 6T XFORMER FUSE BROKE. NO CAUSE//VER/CRB IDC XXXX
21092 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-12-12 20:17 | 2008-12-12 22:11 | 1 | 114 | 57854-1 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP 4/3 DROP BURNED NEUTRAL INTO...100 AMP SERVICE...ALL CONNECTIONS WERE GOOD...LINE HAD RUB MARKS ON TRIPLEX MAYBE SOMTHING HAD HIT EARLIER..INSTALLED 2/3 TRIPLEX DROP...BB L3/KEP IDC XXXX
21093 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2018-01-13 00:21 | 2018-01-13 02:15 | 1 | 114 | 4741051 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | called customer they have part power///// Replaced bad conn at weather head apr at 0215 close ticket
21094 | Hazard | 3301401 | COMBS | COMBS | 2018-11-29 14:52 | 2018-11-29 15:30 | 3 | 38 | 4491361 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout 72kv,replace cutout L3/HFP
21095 | South Williamson | 3411401 | DEWEY | INEZ | 2015-04-20 18:56 | 2015-04-20 20:50 | 1 | 114 | 4344241 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 38830767B30209//CANNOT ACCESS WITH TRUCK DUE TO DRIVEWAY BROKE OFF//GOING TO OPEN LINE FUSE ON POLE 38830767A40201// SO WE CAN CLIMB AND CHANGE CUTOUT//STILL ONLY AFFECTS THE ONE CUSTMER///BRYAN RAMEY ENROUTT HELP//CUTOUT BROKE ON POLE 767-209//CANNOT ACCESS WITH TRUCK DUE TO DRIVEWAY BROKE OFF//GOING TO OPEN LINE FUSE ON /RESTORED AT 20:50//COMPLETE// VER/CRB
21096 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-09-01 17:06 | 2008-09-01 19:00 | 1 | 114 | 58334-1 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEND COPY OF TICKET TO PEGGY WYNNSONG, CUST STATES THAT THERE ARE DAMAGES, NETUTRAL HAD RUBBED INTO HOTLEG AND BURNED THE NETURAL INTOAT THE LOOPS ON SEC POLE TBURTON//3001401//VER/CRB IDC XXXX
21097 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-02-28 14:24 | 2008-02-28 16:18 | 1 | 114 | 51284-1 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308503//BAD CONNECTION ON XFMR POLE// VER/DBM IDC XXXX
21098 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2018-05-18 22:18 | 2018-05-18 23:15 | 2 | 57 | 4374341 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse
21099 | Pikeville | 3403001 | PIKEVILLE | CITY | 2021-08-02 14:10 | 2021-08-02 16:04 | 1 | 114 | 4994191 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers service drop neutral broke into, will be making repairs. Got service sliced and power restored @1604. Only 1 cust. had part power.
21100 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2020-08-31 19:25 | 2020-08-31 21:19 | 1 | 114 | 4409611 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral burnt into @ xfmr///Repaired broken neutral and restored @ 21:19 124/124/248///Only 1 customer was affected
21101 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-10-27 19:33 | 2009-10-27 20:30 | 2 | 57 | 59262-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED CUTOUT INACTIVE TRANSFORMER 40T LINE FUSE/LINE 248-26 IDCC PN218 XXXX
21102 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-06-07 18:09 | 2018-06-07 20:03 | 1 | 114 | 4567001 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 144A309 patrolled line saw no hazards.line fuse door was open but not blown.i replaced cutout due to spring being weak nd allowing door to drop open.restored power at 20;03.
21103 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-01-08 11:42 | 2014-01-08 12:20 | 3 | 38 | 4259891 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORM FUSE ON 94-56 BROKE REFUSE POWER RESTORED 12:20 VER/CRB IDC XXXX
21104 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-07-12 12:37 | 2016-07-12 13:34 | 2 | 57 | 4615201 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SINGLE ALL OUT BROKEN FUSE LINK, 12-T REPLACED POWER RESTORED KWB// VER/ ADH
21105 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-04-23 20:31 | 2020-04-23 22:25 | 1 | 114 | 4743201 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer cutout on pole 93-67 broke. will replace. power restored at 2225
21106 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-01-24 07:36 | 2008-01-24 09:30 | 1 | 114 | 59348-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411801//SD BURNED INTO,WILL REPLACE ITPOOR SERVE-IN CONNECTION HEATED UP AT SPLICE,INSULATION FAILURE THERE BURNED NEUTRAL INTO.REPLACED WITH NEW DROP.MOST LIKELY DAMAGES HERE VER/KEP IDC XXXX
21107 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2018-09-27 11:21 | 2018-09-27 13:15 | 1 | 114 | 4166491 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutral broke at the pole, I replaced it
21108 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-10-23 14:37 | 2014-10-23 15:15 | 3 | 38 | 4656581 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEVERAL BAD CONNECTIONS AT XFMR POLE .WILL PULL OFF & REWORK CONNECTIONS. PULLED OFF 2 14:37 BACK ON @ 15:15/ ISO 38831125C30239/ COD 3// VER/BOW
21109 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2008-08-04 09:53 | 2008-08-04 10:50 | 2 | 57 | 64917-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001402// BAD CUTOUT DOOR, REPLACED VOLTAGE OK.//VER/CRB IDC XXXX
21110 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-10-05 16:21 | 2015-10-05 18:15 | 1 | 114 | 4319511 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVCE DROP BROKEN NEUTRAL. VER/CRB L3/HFP XXXHFP
21111 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-12-16 13:00 | 2014-12-16 14:54 | 1 | 114 | 4864681 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED OPEN NUETRAL VER/HFP L3/HFP
21112 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-04-18 17:42 | 2018-04-18 19:36 | 1 | 114 | 4252161 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer: no answer replaced broken19.9 cutout on 793-D-61 restored power at 19:36
21113 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-08-04 15:15 | 2009-08-04 15:53 | 3 | 38 | 56552-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED AT POLE 38831074A00366 AT 15:15... REPLACED CUTOUT AND RE-ENERGIZED TAP , ALL WORK COMPLETE / GXJ//COD 3// VER/DBM IDCC TOF1459 XXXX
21114 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2016-12-09 13:06 | 2016-12-09 14:03 | 2 | 57 | 4180961 | 114 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS ON POLE 449-367..REPLACED XFMR LEADS & CONNECTIONS, OPENED AT 13:41 & CLOSED XFMR AT 14:03.//PART POWER FROM BEGINNING VER/CRB L3/HFP HFPC MCCDL
21115 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-10-31 09:51 | 2009-10-31 11:45 | 1 | 114 | 53498-1 | 114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR C/O BROKEN AND FELL OFF POLE 37830230A00035, WILL PROBABLY OPEN LINE C/O ON TAP ,OFF THIS POLE TO BE SAFE./////// DIDNT OPEN TAP, CHANGED XFMR C/O, POWER RESTORED VER/KEP L3/KEP IDCC PN36, CNT4 XXXX
21116 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-02-10 15:10 | 2022-02-10 17:03 | 1 | 113 | 4465961 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse open at 121-28,Fuse is broke going to Refuse and restore service..Restored at 17:03.
21117 | Hazard | 3309302 | VICCO | JEFF | 2014-03-24 07:49 | 2014-03-24 09:42 | 1 | 113 | 4520951 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD, MISMAPPED, FED FROM POLE 37830322C00118 -- ONLY 1 CUST. WITH PART POWER. MADE MDC VER/CRB
21118 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-02-22 14:05 | 2021-02-22 15:58 | 1 | 113 | 4220201 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 3-PHASE TRANSFORMER BANK, CHANGED ALL 3 CUTOUTS WHILE POWER WAS OUT; SERVICE RESTORED AT 15:58
21119 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-06-17 10:57 | 2010-06-17 12:50 | 1 | 113 | 50449-1 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE BURNT OFF @ CUSTOMER`S STATION NEAR PIKEVILLE AIRPORT..//THIS IS ON AEP`S SIDE//RELEASED BY CREW 074H14 LEAD OFF PRI. MTR WILL TRY TO REPAIRRELEASED BY CREW 074H14 LEAD OFF PRI. MTR WILL TRY TO REPAIR ----I HAD A HOT TAP BURNED OFF PRI MTR. REPLACED HOT TAP// VER/DBM
21120 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-01-04 09:27 | 2010-01-04 11:20 | 1 | 113 | 59680-1 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN ON XFMR POLE. RE-SQUEEZED ALL SECONDARY CONNECTIONS AND CHANGED OLD CUTOUT AND ARRESTER. RESTORED @ 11:20. SH VER/KEP L3/KEP IDC XXXX
21121 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2013-01-23 06:57 | 2013-01-23 08:50 | 1 | 113 | 4731681 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | APPROX SERVICER ETA 0750 // ONE HOT CONDUCTOR AND NEUTRAL BURNT INTO DUE TO INSULINK HEATING UP AND BREAKING DOWN. I HAVE REPAIRS MADE EVERYTHING OK. CUST SAID EVERYTHING OK. SEND COPY TO PEGGY IN DAMAGE CLAIMS. CUST COULD POSIBLY CALL IN. CONDUCTOR BURNT INTO ABOUT 3 FOOT FROM WEATHER HEAD.//EMAILED TO P WYSONG// VER/DBM IDC XXXX
21122 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-03-04 08:42 | 2019-03-04 10:35 | 1 | 113 | 4949131 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Insulink connection failed at weatherhead. Replaced weatherhead connections and restored @ 10:35. sh
21123 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-02-27 20:32 | 2012-02-27 22:25 | 1 | 113 | 4512641 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PRIMARY OPEN DUE TO BAD CURRENT LIMIT FUSE. I WILL BE MAKING REPAIRS. SEND COPY OF THIS TO ENG PIKEVILLE TOM MAMING. I HAD ONE BAD LAST NIGHT ON POLE 37830117000288 AND THIS ONE TONIGHT ON POLE 37830139C00217. THESE SEEM TO FAIL MORE IN THE WINTER TIME. NOT SURE OF THE NUMBER I HAVE HAD MAYBE 15 TO 25 OTHERS HAVE HAD SEVERAL ALSO. NOT SURE OF THE NUMBER OF THESE ON THE BEAVERCREEK LIGON 800 TO 1000- MORE OR LESS. THESE WILL CONTINUE TO BE A PROBLEM UNTIL CHANGED.//EMAILED TO ENGINEERING// VER/DBM IDC XXXX
21124 | Pikeville | 3402003 | KEYSER | MULLINS | 2018-11-27 12:24 | 2018-11-27 14:17 | 1 | 113 | 4484001 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | arm mounted cutout failed.have called for cover up. complted . power is restored
21125 | Hazard | 3310502 | HADDIX | CANOE | 2021-12-30 09:37 | 2021-12-30 11:30 | 1 | 113 | 4238411 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout at 75-60. replaced
21126 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-10-30 17:38 | 2016-10-30 19:31 | 1 | 113 | 4063941 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON SECONDARY VER/CRB L3/HFP XXXHFP
21127 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2014-11-18 16:07 | 2014-11-18 18:00 | 1 | 113 | 4742961 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 2-BAD CONN. ON HOUSE REPAIRED
21128 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-02-05 20:29 | 2014-02-05 22:22 | 1 | 113 | 4360711 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | MADE MDC LF ON POLE 37830045000012 COD 1 VER/CRB
21129 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-10-04 00:12 | 2010-10-04 02:05 | 1 | 113 | 56518-1 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 0012 - OPENED TR DUE TO FAULTY CUTOUT AND ARRESTER WHICH WAS REPORTED ON TROUBLE ORDER 56512-1. RESTORED 0205 //VER/GAH IDC XXXX
21130 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-03-05 09:52 | 2018-03-05 11:45 | 1 | 113 | 4965781 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout COD-1 ISO TF 38831088000022
21131 | Pikeville | 3409502 | BURDINE | LEVISA | 2009-12-07 22:57 | 2009-12-08 00:50 | 1 | 113 | 53452-1 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE HOT LEGS ON THIS CUSTOMERS SERVICE DROP. ONLY ONE CUSTOMER AFFECTED. IDCC CNT3 XXXX
21132 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-10-12 16:52 | 2018-10-12 18:45 | 1 | 113 | 4244151 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad cutout, apr at 1845 close ticket dwest L3/HFP
21133 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-08-08 17:25 | 2014-08-08 19:18 | 1 | 113 | 4343741 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BREAKING DOWN/// PUT FIRE OUT AND REPLACED CUTOUT. POLE OK COD-1 ISO TF 3783102000210 VER/HFP L3/HFP
21134 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-06-27 06:45 | 2022-06-27 08:38 | 1 | 113 | 4329281 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout, restored @ 08:38
21135 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-09-10 06:17 | 2015-09-10 08:10 | 1 | 113 | 4221641 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR VER/CRB
21136 | Whitesburg | 3309302 | VICCO | JEFF | 2015-01-21 19:07 | 2015-01-21 21:00 | 1 | 113 | 4950401 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT GATE IS BURNT UP ON POLE 373-92. CHANGED CUT-OUT AND RESTORED POWER AT 21:00. 1.21.2015/ ISO 37830373000092/ COD 1/ VER/BOW
21137 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-05-09 11:47 | 2010-05-09 13:40 | 1 | 113 | 58645-1 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN ON HILLSIDE-- BAD TRANSFORMER-MANNUAL--REPLACE 5-10-10//VER/CRB IDC XXXX
21138 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-05-12 14:19 | 2016-05-12 16:12 | 1 | 113 | 4206741 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE HOT PHASE BAD ON CUSTOMERS SERVICE, INSTALLED POWERTEMP UNTILL JOB CAN BE WRITTEN TO REPLACE OR REPAIRE BAD UNDERGROUND PLEASE CLOSE TICKET. DEW APR AT 1612 CLOSE TICKET// VER/ ADH
21139 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-04-05 14:11 | 2019-04-05 16:04 | 1 | 113 | 4061341 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUTbroke cutout on pole 174-437 L3/HFP
21140 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-01-01 15:07 | 2008-01-01 17:00 | 1 | 113 | 52494-1 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401001//1 HOT LEG BURNED INTO AT SPLICE IN SERVICE. DROP. I AM GOING TO SPLICE CONDUCTOR. I SPLICED S/DROP. IDC XXXX
21141 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-12-11 18:52 | 2019-12-11 20:45 | 1 | 113 | 4146141 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced c/o--allgood--in at 20:45--ds121119
21142 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-01-14 17:37 | 2021-01-14 19:30 | 1 | 113 | 4869851 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broken neut and hot leg in tree. repairs made, restored
21143 | Hazard | 3302703 | HAZARD | HAZARD | 2018-11-12 12:42 | 2018-11-12 14:35 | 1 | 113 | 4391871 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | found netural sleeve connection failed,pull apart,customer states he has some equiment damage. L3/HFP
21144 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2019-06-09 21:07 | 2019-06-09 23:00 | 1 | 113 | 4470801 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed on secondary pole. Repaired and restored @ 23:00. sh
21145 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-01-19 12:57 | 2015-01-19 14:50 | 1 | 113 | 4944661 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, BAD CONNECTION AT XFMR ,MADE REPAIRS RESTORED POWER AT 14;50.ONLY ONE CUSTOMER AFFECTED// VER/ ADH
21146 | Pikeville | 3407101 | TOPMOST | DEMA | 2018-02-22 20:43 | 2018-02-22 22:36 | 1 | 113 | 4874191 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout
21147 | Hazard | 3310502 | HADDIX | CANOE | 2009-03-01 10:00 | 2009-03-01 11:53 | 1 | 113 | 52709-1 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3310502// REPLACED A LOOSE CONNECTION ON XFMR SECONDARY RISER VER/KEP L3/KEP IDC XXXX
21148 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-03-26 00:07 | 2019-03-26 02:00 | 1 | 113 | 4025081 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout arcing on 834-733. 38830834A40733Cutout arcing on 834-733. Replaced cutout and restored @ 2:00. sh
21149 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-10-27 15:32 | 2015-10-27 17:25 | 1 | 113 | 4381061 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGED OUT BAD ARRESTOR.POWER RESTORED COMPLETE/ ISO 38830292C00282/ COD 1/ VER/BOW
21150 | Hazard | 3420001 | SOFT SHELL | VEST | 2019-01-17 09:52 | 2019-01-17 11:45 | 1 | 113 | 4680731 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | found bad secondary connection, repaired
21151 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2010-01-18 08:07 | 2010-01-18 10:00 | 1 | 113 | 55738-1 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT IN TWO REPAIRED SERVICE// VER/DBM IDC XXXX
21152 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-04-01 09:28 | 2020-04-01 11:21 | 1 | 113 | 4551341 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew require 6t fuse broke
21153 | Hazard | 3309301 | VICCO | REDFOX | 2013-03-31 07:04 | 2013-03-31 08:57 | 1 | 113 | 4968931 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 326-89, BAD CUTOUT ON POLE 326-129, REPLACED CUTOUT RESTORED POWER AT 08:57 COD-1 ISO LF 37830326D00089 VER/HFP L3/HFP IDC XXXX
21154 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-06-12 21:52 | 2010-06-12 23:45 | 1 | 113 | 61943-1 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BURNT UP CUTOUT DOOR VER/KEP L3/KEP
21155 | Hazard | 3311103 | STINNETT | WENDOVER | 2022-10-31 16:42 | 2022-10-31 18:35 | 1 | 113 | 4083331 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cut out, replaced. Power restored.
21156 | Hazard | 3303902 | LESLIE | WOOTON | 2016-06-10 15:22 | 2016-06-10 17:15 | 1 | 113 | 4333301 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT LEG CONNECTION AND NETURAL CONNECTION, MADE UP WITH SPLIT BOLTS,MADE ALL NEW CONNECTION,ALL GOOD NOW/ ISO 37830437000076/ COD 1/ VER/BOW
21157 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2021-05-14 13:13 | 2021-05-14 15:06 | 1 | 113 | 4586501 | 113 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Opened transformer at 14:38 closed at 15:06 bad conn. at transformer LR- The 1st part out call came in at 13:13
21158 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2018-01-06 01:29 | 2018-01-06 03:22 | 1 | 113 | 4711071 | 113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 65t line fuse out. look defective may have broken this is 1 span tap out to pole 42-c-348. looked everything over fused up everything good. just had 1 cust out
21159 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-08-26 18:58 | 2017-08-26 20:50 | 1 | 112 | 4301591 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CALLED CUSTOMER: NO ANSWER RELEASED BY CREW 076S01//XFMR RISER HAD COME LOOSE FROM BOTTOM OF CUTOUT///I PUT RISER BACK IN AND RESTORED AT 20:50//COMPLETE//EM //COD 1
21160 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-05-28 10:44 | 2013-05-28 11:40 | 2 | 56 | 4190311 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BAD ON POLE 167-162 AND BLEW TRANS. FUSE. I AM GOING TO REFUSE TRANS. COD 2 //ISO 167A-162 VER/SEF IDC XXXX
21161 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2018-01-25 15:28 | 2018-01-25 17:20 | 1 | 112 | 4773511 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 17:20. sh
21162 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2022-08-23 14:08 | 2022-08-23 16:00 | 1 | 112 | 4785331 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral in service drop had broken///Repaired broken neutral and restored full power///124/124/248///There was no electrical contact on our side///Only 1 customer was affected
21163 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-10-04 07:43 | 2022-10-04 09:35 | 1 | 112 | 4973581 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer had neutral and one hot leg burnt off in service drop going to house///// spliced service drop out and got power restored ata time of 9:35
21164 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-05-23 15:00 | 2017-05-23 15:56 | 2 | 56 | 4843341 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CRE W REQUIRED/REPLACED CUTOUT VER/CRB
21165 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2017-05-22 11:20 | 2017-05-22 11:48 | 4 | 28 | H4837791 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 0NE LINE FUSE OUT ON POLE 159-9, BROKEN CUTOUT ON XFMR ON POLE 159-10//COD 5 FROM THE BEGINNING OF OUTAGE//0NE LINE FUSE OUT ON POLE 159-9, BROKEN CUTOUT ON XFMR ON POLE 159-10, ALL POWER RESTORED//OPENED A&C @ 1120/ DUPLICATE OUTAGE OF 4837791// VER/CRB
21166 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-06-04 09:26 | 2015-06-04 11:18 | 1 | 112 | 4509891 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 11:18.// VER/ ADH
21167 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-03-30 15:32 | 2020-03-30 16:00 | 4 | 28 | 4545001 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Secondary riser connection going bad on 1/0 secondary to pole 810-341. No interruption until I open xfmr to make repairs. Opened xfmr 810-212 @ 15:32, replaced xfmr connections and restored @ 16:00. sh
21168 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-12-28 20:03 | 2008-12-28 21:55 | 1 | 112 | 64779-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | GOT BAD CONNECTION ON SERVICE REPAIR CONNECTION OPEN TRANSF FUSE AT 2134, RESTORED ALL CUSTOMERS AT 2155 //VER/GAH L3/KEP IDC XXXX
21169 | South Williamson | 3411401 | DEWEY | INEZ | 2014-02-12 09:24 | 2014-02-12 10:20 | 2 | 56 | 4375251 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN//REFUSED AND CAME ON FEW MINUITES LATER///POWER IS ON NOW//RESTORED AT 10:20///CREW GOING TO CHANGE XFMR THIS AFTERNOON///COMPLETE//EM VER/SEF
21170 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2008-12-23 10:20 | 2008-12-23 10:48 | 4 | 28 | 62960-1 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3200201//SERV DROP SHORTED OUT,WILL OPEN XFR TO REPAIRBAD SERVE-IN CONNECTION HEATED UP AND SHORTED OUT BURNING SERV NEUTRAL INTO,MADE NECESSARY REPAIRS.POSSIBLE DAMAGES HERE,PROBABLY WILL BE CONTACTED//VER/CRB L3/KEP IDCC CNT1, CHANGED START TIME FROM 0801 XXXX
21171 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2019-06-03 09:08 | 2019-06-03 11:00 | 1 | 112 | 4419171 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout complete
21172 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2020-07-12 20:03 | 2020-07-12 21:55 | 1 | 112 | 4155991 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required need to send a copy to tech to have a transformer installed closer to house 271-104
21173 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2020-03-26 15:28 | 2020-03-26 17:20 | 1 | 112 | 4513451 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM FUSE BLOWN WILL REFUSE/// BAD 15KVA XFM WILL NEED 1 MAN/// CHANGED BAD XFM AND RESTORED @ 17:20
21174 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-01-28 09:59 | 2010-01-28 10:55 | 2 | 56 | 60617-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL HANGING DOWN GOING TO TRY CLOSEING BACK IN.REFUSED DOOR EVERY THING BACK TO NORMAL/VER/CRB IDC XXXX
21175 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2020-08-19 15:29 | 2020-08-19 17:21 | 1 | 112 | 4347991 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced door
21176 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-06-29 21:04 | 2011-06-29 22:00 | 2 | 56 | 4439851 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LOOKED LIKE IT WAS PULLED LOOSE, REFUSED TRANSFORMER ALL POWER RESTORED CLOSE TICKET VER/KEP IDC CHANGED CAUSE FROM OTHER XXXX
21177 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-01-04 16:29 | 2014-01-04 18:21 | 1 | 112 | 4228981 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL IN SERVICE DROP IS BURNED INTO. I AM GOING TO SPLICE WIRE. I RESQUEEZED ALL CONNECTIONS ON SECONDARY POLE. SEND TO PEGGY. CUSTOMER SAID HE MAY HAVE DAMAGES. I TOLD HIM TO CALL IN IF HE DID. VER/CRB
21178 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-12-29 11:53 | 2012-12-29 13:45 | 1 | 112 | 4550191 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL PULLED OUT OF SLEEVE WITH NO VISIBLE CAUSE, SLEEVE WAS CORRECT SIZE, NOT SURE WHAT WAS USED TO MAKE SQUEEZES, THIS IS ON METER 533519359, 88 SYCAMORE, NOT 88A AS TICKET SAYS. MAY BE DAMAGE CLAIM, ONLY 1 CUSTOMER//EMAILED TO P WYSONG// VER/DBM
21179 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2020-01-20 10:08 | 2020-01-20 12:00 | 1 | 112 | 4322621 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection in secondary L3/HFP
21180 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-06-06 22:39 | 2013-06-06 23:35 | 2 | 56 | 4233321 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP. -- POWER RESTORED.//COD 2// VER/DBM
21181 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-06-10 12:03 | 2013-06-10 12:59 | 2 | 56 | 4251761 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON XFMR POLE 28-56.CAN REPLACE..//.REPLACED BROKEN CUTOUT.CLOSED FUSE.POWER ON.JRV..06/10/13 // COD 2// VER/DBM IDC XXXX
21182 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2010-06-02 09:30 | 2010-06-02 11:22 | 1 | 112 | 55231-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE ON 325-366 BAD CUTOUT OPENED LINE FUSE ON POLE 425-96 TO ISOLATE..REPLACED CUTOUT & REPAIRED POLE RESTORED POWER AT 11:22, ONLY ONE CUSTOMER AFFECTED VER/HFP L3/HFP IDCC TOF0904 XXXX
21183 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-01-29 19:01 | 2008-01-29 19:57 | 2 | 56 | 60779-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202202// CUTOUT DOOR BURNED UP//COD 2// VER/DBM IDC XXXX
21184 | Pikeville | 3413401 | GARRETT | GARRETT | 2014-03-02 16:20 | 2014-03-02 18:12 | 1 | 112 | 4444311 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN, NO TRUCK ACCESS . REPLACED CUTOUT AND ARRESTER , ALL WORK COMPLETE / GXJ//COD 1// VER/DBM
21185 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2022-07-15 10:14 | 2022-07-15 11:10 | 2 | 56 | 4493821 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | servicer found broke cutout repairs made
21186 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-05-01 16:44 | 2011-05-01 17:40 | 2 | 56 | 53275-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O ON POLE 377-249, WILL BE CHANGING.... MADE REPAIRS RESTORED POWER AT17:40//COD 2//ISO 37830377B00249// VER/DBM IDC CHANGED TIME OFF FROM 1622 PER TICKETS XXXX
21187 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-06-04 01:15 | 2009-06-04 03:07 | 1 | 112 | 56189-1 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION VER/LDA IDC XXXX
21188 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2022-12-07 13:05 | 2022-12-07 13:21 | 7 | 16 | 4238751 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | Trans fuse open on Trans Bank at 72-D-632,Will be trying to get it back in.Arrester was Bad at Trans Cleared it up and Restored at 13:21.
21189 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-11-23 11:38 | 2019-11-23 13:30 | 1 | 112 | 4059081 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | red-red splice pulled apart. I replaced it
21190 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2021-06-05 22:48 | 2021-06-06 00:40 | 1 | 112 | 4673341 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1.6 xfmr fuse, broke
21191 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-04-10 06:10 | 2016-04-10 06:26 | 7 | 16 | H4076981 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY BROKE IN THE CLEAR @ POLE #38831078000037 COD-7 WILL ISOLATE @ 38831078000033 NEED #4 C0PPER SLEVES ,MATERIAL HANDLER & 2 MENPRIMARY BROKE @ POLE #38831078000037 WILL ISOLATE @ 38831078000033 NEED #4 C0PPER SLEVES ,MATERIAL HANDLER & 2 MEN OPCLOSED BACK IN @06:10ENED @ 33 @06:26 VER/KEP
21192 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-07-22 18:53 | 2020-07-22 20:45 | 1 | 112 | 4207741 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will be replacing/// Replaced bad cutout and refused xfm @ 20:45 and restored service
21193 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-01-17 18:53 | 2009-01-17 20:45 | 1 | 112 | 57811-1 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP NEUTRAL AND 1 HOT LEG IN SECONDARY CONDUCTOR HAS SHORTED OUT. I AM GOING TO SPLICE CONDUCTORS. SECONDARY CONDUCTOR { 2/3 } FAILED AT A SPLICE IN MID SPAN AND SHORTED OUT, BURNING NEUTRAL AND ONE HOT CONDUCTOR INTO. CUSTOMER SAID HE MAY HAVE DAMAGES. I TOLD HIM TO CALL IN A DAMAGE COMPLAINT IF HE DID. L3/HFP
21194 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-01-17 14:43 | 2009-01-17 16:35 | 1 | 112 | 57646-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP REPLACED BAD CONNECTIONS ON SERVICE DROP L3/HFP
21195 | Paintsville | 3409302 | KENWOOD | AUXIER | 2011-01-29 01:15 | 2011-01-29 03:07 | 1 | 112 | 51694-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL PULLED OUT OF SPLICE COMPROMISING INSULATION ON HOT CONDUCTOR IN SERVICE WIRE. WILL HAVE TO REPLACE SERVICE. DIFFICULT LOCATION. #4 SERVICE REPLACED WITH #2. CLOSER INSPECTION OF WIRE SHOWS SLEEVE DIDNT PULL OUT - NEUTRAL WAS BURNT IN TWO ABOVE SPLICE DUE TO CONNECTION HEATING UP AND MELTING INSULATION. SH VER/ARN IDCC TOF2350, CNT3, ESTIMATED TIME OFF XXXX
21196 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-06-24 13:48 | 2012-06-24 15:40 | 1 | 112 | 4957041 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE DROP BURNTED INTO, HAVE REPAIRS MADE AND NO MORE DIM LIGHTS AT THIS LOC VER/HFP L3/HFP AJB
21197 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-01-07 18:23 | 2022-01-07 19:19 | 2 | 56 | 4322031 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfr fuse melted out complete
21198 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-03-28 08:54 | 2008-03-28 09:50 | 2 | 56 | 61497-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3007904//,,,,FOUND BLOWN ARRESTER ,, CLEARED IT UP,,// COD 2// ISO/FLT 38830478D10266// VER/TOM IDC XXXX
21199 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2018-03-11 16:22 | 2018-03-11 16:50 | 4 | 28 | 4984961 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Side tap fuse had broke at pole 38820991D20101, replaced the fuse and power is restored./ ISO 38820991D20101/ COD 4****XFMR IS ON LOAD SIDE SIDE
21200 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-10-16 09:51 | 2008-10-16 11:43 | 1 | 112 | 56107-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE REPLACED FUSE//3410602//VER/CRB IDC XXXX
21201 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-03-07 21:22 | 2013-03-07 22:18 | 2 | 56 | 4888961 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN THE SECONDARY FAILED ///VER/CRB L/3 CRB IDC XXXX
21202 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-12-22 09:51 | 2012-12-22 11:43 | 1 | 112 | 4507171 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP MELTED TOGETHER AND SHORTED OUT AT THE ENTRANCE CABLE, I REPAIRED SERVICE. CUSTOMER STATED THAT THEY ADDED SOME KIND OF ELECTRIC FURNACE. ////VER/CRB L/3 CRB
21203 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-12-07 10:21 | 2010-12-07 12:13 | 1 | 112 | 64013-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE AT HOT LINE CLAMP BROKE COD-1 ISO PO 37830056000040 VER/HFP L3/HFP IDC XXXX
21204 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-03-21 20:01 | 2019-03-21 21:53 | 1 | 112 | 4008521 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired connection
21205 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-11-16 09:38 | 2015-11-16 11:30 | 1 | 112 | 4450851 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION ON TRANSFORMER BUSHING.LOOSE HOT TAP CLAMP..REPLACED CLAMP..TIGHTENED SECONDARY BUSHING.SPLICED S/D./ ISO38830875C00644 / COD 1/ VER/BOW
21206 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-10-05 11:53 | 2010-10-05 13:45 | 1 | 112 | 57012-1 | 112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED APART ON SECONDARY POLE// VER/DBM IDC XXXX
21207 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-11-01 07:38 | 2009-11-01 09:30 | 1 | 112 | 54509-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3417602// SERVICE BURN DOWN AT POLE 965-D-29. MAKING REPAIRS. OPENED TRANSFORMER AT 09:10 CLOSED IN AT 09:30 //VER/GAH IDC XXXX
21208 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-02-28 15:53 | 2014-02-28 17:45 | 1 | 112 | 4440941 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TAKEN @ 1539 // DONALD HICKMAN @ 344 GARDEN BRANCH RD, LOUISA, KY /// CALLER BETTY HICKMAN @ 606-673-3648 // DOG //BAD FUSE VER/CRB L3/GSL
21209 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2016-10-26 13:03 | 2016-10-26 14:55 | 1 | 112 | 4055161 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE 858-425 BLOWN. TRANSFORMER FUSE LINK APPEARS TO HAVE BROKE. REPLACED AND RESTORED @ 14:55. SH/ ISO 38830858A20425/ COD 1/ MD DONE/ VER/BOW L3/HFP XXXHFP
21210 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-02-28 13:44 | 2014-02-28 14:12 | 4 | 28 | 4440561 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 7905 RT 168 NO POWER, BARBARA WICOX 606-739-6660/ FUSE LINK BROKE ALSO NEEDS SOME ROW CLEARED VER/KEP
21211 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-05-08 06:48 | 2013-05-08 08:40 | 1 | 112 | 4084941 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP GOING TO CHANGE IT//CHANGED CUTOUT // POWER RESTORED COMPLETE TT//COD 1// VER/DBM IDC XXXX
21212 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2010-09-04 08:49 | 2010-09-04 09:45 | 2 | 56 | 63521-1 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 114-154 1.2 FUSE BAD 19.9 CUTOUT DOOR BURNT UP//COD 2// VER/DBM IDC XXXX
21213 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2019-07-27 23:06 | 2019-07-28 00:58 | 1 | 112 | 4799501 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no answer//Xfmr cutout has failed and broke on pole 801-153.I can access with truck and will be making repairs//Replaced cutout and restored power @ 00:58/ ISO 38830801000153/ COD 1
21214 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-07-09 05:53 | 2014-07-09 06:07 | 8 | 14 | H4216141 | 112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PATROLLING LINE/VEM/LOOP BURNT OPEN 162-66/WILL NEED TO OPEN FUSE ON 162-28 FOR REPAIRS/APPROX 30 MINUTE OUTAGE/VEMOPEN FUSE @0553/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0607/NOT TO MAPPING CUST OFF OF FUSE 162-C-28 ARE ON A PHASE/PLEASE CLOSE TICKET/THANKS/VEM *****DUPLICATE TICKET FOR OTHER 8 CUSTOMERS FROM 0553 TILL 0607***** VER/SEF
21215 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2013-04-23 16:12 | 2013-04-23 16:49 | 3 | 37 | 4039901 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN // WILL REFUSE// FUSE LINK APPEARED TO HAVE BROKEN// REFUSED// POWER IS RESTORED ///VER/CRB L/3 CRB IDC XXXX
21216 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-07-27 19:29 | 2013-07-27 21:20 | 1 | 111 | 4598671 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4/3 SERVICE DROP BURNED DOWN. I AM GOING TO CHANGE TO A 2/3 SERVICE DROP. I CHANGED DROP. VER/ARN IDCC CDC89, CNT3 XXXX
21217 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-02-23 13:39 | 2015-02-23 15:30 | 1 | 111 | 4075481 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT & ICE CAME OFF HOUSE AND BROKE SERVICE WIRE . VER/CRB L3/HFP XXX
21218 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-09-28 08:44 | 2022-09-28 10:35 | 1 | 111 | 4932071 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase riser cutout failed on 1127-A-544, will have to open A and C phase to safely make repairs/ opened A and C phase @ 10:21
21219 | Hazard | 3309301 | VICCO | REDFOX | 2016-12-18 17:21 | 2016-12-18 19:12 | 1 | 111 | 4217711 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR , RESTORED POWER AT 07:12..37830326D00330 VER/AWD
21220 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-01-08 19:57 | 2022-01-08 21:48 | 1 | 111 | 4325941 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Secondary connection burnt open on pole 289-A-64 replaced bad connection and restored full power @ 21:48///Only 1 customer was affected
21221 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-01-02 08:59 | 2008-01-02 10:50 | 1 | 111 | 52639-1 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN S/DROP AND 1 HOT LEG IS BURNED INTO.I AM GOING TO REPLACE DROP. IT LOOKED LIKE SOMETHING HAD CAUGHT S/DROP AND BROKE S/DROP DOWN ONCE I HAD IT ON GROUND. I REPLACED DROP.//3401702.//VER/CRB IDC XXXX
21222 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2008-07-19 10:38 | 2008-07-19 11:15 | 3 | 37 | 54129-1 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3403302//FUSE BLOWN CHECKING NOW FUSE BROKE REPLACED USE BACK TO NORMAL T GOBLE // VER/TOM IDC XXXX
21223 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-11-10 20:43 | 2011-11-10 21:20 | 3 | 37 | 4066571 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR. ///VER/CRB IDC XXXX
21224 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-12-24 21:59 | 2014-12-24 23:50 | 1 | 111 | 4883001 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SEC. RISER CAME LOOSE WILL HAVE TO CLIMB AND REPAIR////REPAIRED SEC RISER..
21225 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2014-08-24 17:36 | 2014-08-24 19:27 | 1 | 111 | 4419291 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | ETA 1815 ONE FUSE IS BLOWN ON PRIMARY METERING ON POLE 941-D-503. HOSPITAL PERSONEL SAY THAT THEY HAVE A BURNT SMELL IN THE HOSPITAL AND THAT ONE OF THEIR TRANSFORMERS WAS SPARKING. RUDY VASS HAS BEEN CALLED OUT. SPOKE WITH RUDY IS EN ROUTE AND THE FIRE ALARM HAS NOW WENT OFF IN THE HOSPITAL. IM GOING TO WAIT TILL WE SEE WHAT IS GOING ON IN THE HOSPITAL BEFORE POWER IS TUNED BACK ON. THE SPARKING IS KUDZU ALL OVER ONE OF THEIR POLES. BAD CT BYPASSED THE METERING. VER/CRB
21226 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-09-29 11:43 | 2008-09-29 12:20 | 3 | 37 | 51850-1 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3301402// XFMR FUSE OUT.// FUSE ROTTED INTO//COD 3// VER/DBM IDC XXXX
21227 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-09-11 19:18 | 2013-09-11 19:55 | 3 | 37 | 4839981 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 43-5 6T FUSE LINK BROKE VER/CRB L/3 CRB
21228 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-12-04 09:39 | 2020-12-04 11:30 | 1 | 111 | 4744211 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout /no crew
21229 | Paintsville | 3401102 | FALCON | SALYERSVI | 2011-12-24 11:57 | 2011-12-24 13:48 | 1 | 111 | 4200141 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | S/D BURNED INTO.SERVE END HEATED UP.POLE HAD BEEN CHG OUT YEARS AGO AND CONTRACTOR SPLICED WIRE.CUST HAD DAMAGE TO HOOD OF CAR.///. OPENED TR @ 1250 TO REPAIR/REPLACE SERVICE DROP /// COD-4 ISO TF 38830875A00150 DUP IN HOIS IS H1163170-1 VER/HFP L3/HFP IDC XXXX
21230 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-01-29 14:49 | 2009-01-29 16:40 | 1 | 111 | 51272-1 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR
21231 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-09-27 11:10 | 2021-09-27 13:01 | 1 | 111 | 4294691 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad con replaced-(trlr pole rotted of at ground .advised cust needed replaced.)allgood-ds092721
21232 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-02-06 12:49 | 2015-02-06 14:40 | 1 | 111 | 4996801 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE BURNT INTO IN SERVICE WILL REPAIR///// OLD SERVICE DROP HAD SPLICE THAT HAD BURNT ONE HOT LEG AND NEUTRAL INTO IN SPLICE//// REPLACED SERVICE DROP AND RESTORED SERVICE @ 14:40 122/123/245//// SEND COPY TO PEGGY WYSON/// ONLY 1 CUSTOMER AFFECTED VER/CRB L3/HFP XXX
21233 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-10-29 20:39 | 2015-10-29 22:30 | 1 | 111 | 4395611 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, CUSTOMER IS OK WITH WAITING TILL MORNING. 15 KVA CSP XFMR 7200 THERE NOW WE NEED 15KVA CUTOUT AND BRACKET.JOB FOR TOMMOROW OPS 030776986, WR 59727568 RELEASED BY CREW 077S12//STOP TIME @ 2230 ON 10-29-2015// COD 1// VER/CRB
21234 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-04-20 01:59 | 2011-04-20 03:50 | 1 | 111 | 60885-1 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | FUSE MELTED OUT IDC XXXX
21235 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-02-08 08:36 | 2010-02-08 10:27 | 1 | 111 | 52981-1 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FROM THE GROUND LOOKS LIKE A CONNECTOR HAS BRUNT OPEN WILL CLIMB POLE TO INVESTAGATE./// REPAIRED LOOSE CONNECTION ON POLE AND RESTORED POWER. 2/8/10 TIM MCCOY IDC XXXX
21236 | South Williamson | 3202201 | LOVELY | LOVELY | 2012-11-17 13:39 | 2012-11-17 15:30 | 1 | 111 | 4405301 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 DROP HAS HOT LEG AND PART OF NEUTRAL BURNT INTO//I REPLACED WITH 2/3 DROP//BACK ON AT 1530//COMPLETE//EM// VER/DBM IDC XXXX
21237 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-04-11 11:44 | 2012-04-11 13:35 | 1 | 111 | 4666081 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT COD-1 ISO TF 37830554000119 VER/HFP L3/HFP OOO
21238 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-01-08 13:39 | 2018-01-08 15:30 | 1 | 111 | 4721231 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//CKD BREAKERS cutout is bad .this is up on hill have called for help to change out
21239 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-02-26 17:24 | 2012-02-26 19:15 | 1 | 111 | 4509201 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TENSION SPLICE IN 2/3 TRIPLEX NEUTRAL PULLED FREE. REPLACED POWER RESTORED. OPENED TRANSFORMER AT 1829 CLOSED AT 1914 COD-3 ISO TF 37830202000040 SEE DUP H4509201 FOR 2 VER/HFP L3/HFP IDC XXXX
21240 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-01-26 11:52 | 2015-01-26 13:43 | 1 | 111 | 4964871 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION @ POLE. RESTORED/ ISO 38830045D26725/ COD 1/ VER/BOW
21241 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-07-24 13:29 | 2017-07-24 15:20 | 1 | 111 | 4173351 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/CRB L3/HFP XXXHFP
21242 | Cannonsburg | 3001401 | LOUISA | CITY | 2017-05-05 08:39 | 2017-05-05 10:30 | 1 | 111 | 4753861 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BROKEN NEUTRAL IN SERVICE, REPAIRS MADE, VOLTAGE GOOD, TICKET COMPLETE VER/CRB
21243 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-01-20 10:12 | 2020-01-20 12:03 | 1 | 111 | 4322641 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service pulled apart at the weatherhead from pole 199C-112 L3/HFP
21244 | Pikeville | 3409502 | BURDINE | LEVISA | 2014-03-30 09:04 | 2014-03-30 10:55 | 1 | 111 | 4540191 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION MID SPAN IN THE SERVICE DROP ONLY ONE CUSTOMER AFFECTED VER/CRB
21245 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-08 15:39 | 2011-06-08 17:30 | 1 | 111 | 4270561 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WR#40307202 POLE 116-64 TREE ON POLE CUT TREE DOWN CHGED BAD 19.9 LA AND 1.6 FUSE//VER/CRB IDC XXXX
21246 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-03-14 23:24 | 2020-03-15 01:15 | 1 | 111 | 4478921 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replace cutout
21247 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2008-11-20 08:34 | 2008-11-20 10:25 | 1 | 111 | 50167-1 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3409401// SERVICE DROP SHORTED OUT IN A SPLICE AND BURNED NEUTRAL AND ONE HOT LEG INTO. I AM GOING TO RESPLICE DROP. I SPLICED DROP. VER/KEP IDC XXXX
21248 | South Williamson | 3411401 | DEWEY | INEZ | 2017-06-06 09:42 | 2017-06-06 11:33 | 1 | 111 | 4915041 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | APT. BUILDING HAVING PARTIAL OUTAGE PERIODICALLY AT THE ELEVATOR AND OFFICE//FOUND A BURNED CONNECTION ON XFMR POLE//I REPAIRED CONNECTION//RESTORED TO NORMAL//COMPLETE//EM/ ISO 38830743C30200/ COD 1/ VER/BOW
21249 | Pikeville | 3413401 | GARRETT | GARRETT | 2017-05-11 15:47 | 2017-05-11 17:38 | 1 | 111 | 4781701 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE NEUTRAL CONNECTION ON SECONDARY POLE , REPAIRS COMPLETE / GXJ VER/CRB
21250 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-02-28 11:19 | 2011-02-28 13:10 | 1 | 111 | 64445-1 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR SECONDARY RISER, REPAIRED SECONDARY, ONLY 1 CUSTOMER VER/ARN IDC XXXX
21251 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-02-04 15:09 | 2009-02-04 17:00 | 1 | 111 | 55615-1 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000202 - CUT TREE OFF SEC, REPAIRED SEC. NEUTRAL. //VER/GAH
21252 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2018-02-25 15:54 | 2018-02-25 17:45 | 1 | 111 | 4882181 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CALLED 911 W/ETA OF 1645//. look like serv end connection heated up one of the hot wires melted into the neutral and burnt neutral into and hot wire just about into. replaced connections everything ok. send copy to peggy in damage claims cust could possibly call in. old 60amp meter base cust said had 100 amp breaker box.//SENT TO CLAIMS
21253 | Whitesburg | 3314401 | MAYKING | ERMINE | 2016-01-08 10:48 | 2016-01-08 12:39 | 1 | 111 | 4594901 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY AND NEUTRAL IN 1/0 TWIST BURNED INTO AT POLE 449-891 . I REPAIRED IT VER/CRB
21254 | Hazard | 3303902 | LESLIE | WOOTON | 2019-08-16 22:04 | 2019-08-16 23:55 | 1 | 111 | 4898771 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | had fuse bad
21255 | Hazard | 3310502 | HADDIX | CANOE | 2011-05-14 11:21 | 2011-05-14 13:12 | 1 | 111 | 4090331 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 169-169. CHECKING LINE. 37830169C00200 FOUND BAD ARRESTOR ON CSP XFMR. REMOVED ARRESTOR. POWER RESTORED.
21256 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-07-13 10:24 | 2010-07-13 12:15 | 1 | 111 | 65904-1 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED HOT TAP TO REPLACE DEFECTIVE CUTOUT IN ORDER 65838-1 /// VER/HFP L3/HFP IDCC CNT3, PN240, TOF901 XXXX
21257 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2018-10-10 11:45 | 2018-10-10 13:36 | 1 | 111 | 4215201 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse had broke. Power restored. L3/HFP
21258 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2013-12-18 23:34 | 2013-12-19 01:25 | 1 | 111 | 4174761 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER POLE MELTED THE INSULATION OFF OF ONE LEG OF THE SERVICE DROP AND BURNED THE NEUTRAL INTO. THE CUSTOMER SAYS THAT HE HAS DAMAGES. // SENT COPY TO PEGGY WYSONG // VER//GAH L3/HFP
21259 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2020-01-02 12:14 | 2020-01-02 14:05 | 1 | 111 | 4203991 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t tansformer fuse looks like fuse broke. fused up everything ok
21260 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-10-08 21:27 | 2009-10-08 23:18 | 1 | 111 | 66106-1 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN - DIFFICULT LOCATION. SECONDARY LOOKS OK. WILL TRY TO RE-FUSE. FUSE LINK BROKE. RE-FUSED. SH VER/KEP L3/KEP IDC XXXX
21261 | South Williamson | 3411401 | DEWEY | INEZ | 2014-01-01 10:29 | 2014-01-01 12:20 | 1 | 111 | 4216801 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 792-161//OPENED TAP AT POLE 816-64 AND GROUNDED TO MAKE REPAIRS//OPENED AT11:25//CUTOUT REPLACED//RESTORED AT 12:20//COMPLETE//EM VER/SEF
21262 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-08-21 10:09 | 2014-08-21 12:00 | 1 | 111 | 4394031 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CUSTOMER MAIN BREAKER/// TEMP DISCONECT/// ACTUALLY FOUND OUT THIS WAS AEP PROBLEM WITH CONNECTIONS AT THE WEATHER HEAD NOT CUSTOMERS EQUIPMENTBAD CUSTOMER MAIN BREAKER/// CUST HAD PART POWER DUE TO BAD CONNECTION AT WEATHER HEAD. BREAKER WAS OK// VER/BOW
21263 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-03-12 07:23 | 2009-03-12 09:14 | 1 | 111 | 57451-1 | 111 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | VER/HFP WRCLOSED IT AT # 28897245 //BAD ARESTER ON PRIMARY METERING GOING TO OPEN METERING TO REPAIR OPENED METERING AT 0900 CLOSED AT 0914 COD-1 L3/HFP IDCC TOF0900 XXXX
21264 | Hazard | 3303901 | LESLIE | HYDEN | 2013-03-05 12:04 | 2013-03-05 13:55 | 1 | 111 | 4871581 | 111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-1 ISO LF @ 37830364000064 4871751 RELATED TO THIS SEE NOTE IN THAT ORDER CHANGED REST TIME IN THIS ORDER TO TIME OF THAT ORDER DUE TO 2 PROBLEMS ON THIS LINE AND CUST ONLY BEING RESTORED FOR 18 MIN VER/HFP L3/HFP VER/HFP L3/HFP IDC XXXX
21265 | South Williamson | 3411401 | DEWEY | INEZ | 2022-07-31 09:20 | 2022-07-31 11:10 | 1 | 110 | 4641611 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced cutout and restored @ 11:10. sh
21266 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-04-04 17:45 | 2013-04-04 19:35 | 1 | 110 | 4979591 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP AND STIRRUP BURNED OFF ON RECLOSER POLE.REPAIRS MADE AND POWER RESTORED..4-4-13.19:35.SEND TICKET TO TIM HALL TO HAVE CREW REPLACE THESES STIRRUPS AND HOT TAPS AND ONE ARRESTOR.//COD 1// VER/DBM IDCC TON1930 XXXX
21267 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-12-19 19:20 | 2008-12-19 21:10 | 1 | 110 | 61010-1 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3003701// RESQUEZED SERVICE VER/KEP L3/KEP IDC XXXX
21268 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-09-10 13:25 | 2015-09-10 15:15 | 1 | 110 | 4224321 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE WIRE BURNT INTO, WILL HAVE TO REPLACE WITH 1/0 SERVICE TWIST, COMPLTED VER/CRB
21269 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-08-03 10:52 | 2017-08-03 11:47 | 2 | 55 | 4220181 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSED BROKE ON TRANS POLE 1129-A4-452, REFUSED @1147./ VER/HFP L3/HFP
21270 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2021-12-01 19:15 | 2021-12-01 21:05 | 1 | 110 | 4139671 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed at xfmr and burnt service in two. Made repairs and restored xfmr @ 21:05. sh
21271 | Pikeville | 3407101 | TOPMOST | DEMA | 2019-07-26 13:55 | 2019-07-26 15:45 | 1 | 110 | 4796191 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout///replaced cutout//restored at 15:45//complete//em
21272 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-02-01 23:10 | 2013-02-02 01:00 | 1 | 110 | 4784401 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 15 KVA { 34.5 } TRANS. IS BAD. WE NEED TO BRING A 25KVA BACK. CUSTOMER SAID WE COULD WAIT UNTIL TOMORROW TO CHANGE IT. OPS. ORDER#-037494365. I TRANSFERED OPS. ORDER TO DENNIS. YOU CAN CLOSE THIS TICKET. RELEASED BY CREW 074S01 VER/KEP IDC XXXX
21273 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-08-01 16:35 | 2011-08-01 17:30 | 2 | 55 | 4652521 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 1147-865 BAD LA REPLACED POLE 1147-239 30T LINE FUSE//VER/CRB IDC XXXX
21274 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-10-19 20:30 | 2011-10-19 22:20 | 1 | 110 | 4001201 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN 6T FUSE, ALL POWER RESTORED ///VER/CRB IDC XXXX
21275 | South Williamson | 3411401 | DEWEY | INEZ | 2014-01-01 11:25 | 2014-01-01 12:20 | 2 | 55 | H4216801 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 792-161//OPENED TAP AT POLE 816-64 AND GROUNDED TO MAKE REPAIRS//OPENED AT11:25//CUTOUT REPLACED//RESTORED AT 12:20//COMPLETE//EM VER/SEF
21276 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-04-09 12:00 | 2015-04-09 12:22 | 5 | 22 | 4295291 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TIM OPENING LINE TO REPLACE NBAD INSULATOR/// JOB IS COMPLTED 4/9/15 PULLED OFF AT 12:00 BACK ON AT 12:22 TIM MCCOY RELEASED BY CREW 074H10/ ISO 37830215A00046/ COD 5// VER/BOW L3/DKGXXX
21277 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-01-09 08:40 | 2020-01-09 10:30 | 1 | 110 | 4226911 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad A phase cutout @37830024D20462, will have to open other 2 cutouts on bank to make repairs. Will keep track of times. Opened B and C phase @0945, had to change all 3 cutouts, closed all 3 back in @1030. L3/HFP
21278 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-04-09 15:08 | 2012-04-09 15:30 | 5 | 22 | 4657731 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT ///VER/CRB IDC XXXX
21279 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-08-19 06:15 | 2011-08-19 08:05 | 1 | 110 | 4728531 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT ON POLE 188-44. ENTERED MD // COD-2 ISO LF 38830188B00044 VER/HFP L3/HFP IDCC PN472 XXXX
21280 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-08-05 02:35 | 2008-08-05 04:25 | 1 | 110 | 65192-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400301// CUTOUT DOOR BURNT OUT. I WILL BE MAKING REPAIRES. REPLACED CUOUT DOOR 1.6T FUSE. EVERYTHANG OK. SEND COPY OF THIS TO ROW PIKEVILLE POLE NEEDS CUT AROUND. JASON BRAD. VER/KEP IDC XXXX
21281 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-07-13 16:10 | 2009-07-13 18:00 | 1 | 110 | 52366-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400301//TOP OF POLE BURNT OFF, TRANSFORMER LAYING IN TREES//DALE HAMILTON HAS BEEN NOTIFIED//CREW REQUIRED//WR# 30712798// T HALL WILL SEND CREW07-14 09 WILL OPEN LINE AND CUT TREES WHILE CHANGING POLE R RAY RELEASED BY CREW 074H12/COD 1// VER/DBM IDC XXXX
21282 | Pikeville | 3402003 | KEYSER | MULLINS | 2017-02-15 09:25 | 2017-02-15 11:15 | 1 | 110 | 4398931 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL CONNECTION BROKE INTO AT TRANS. POLE, MADE REPAIRS. VER/CRB L3/HFP XXXHFP
21283 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-01-05 16:25 | 2015-01-05 18:15 | 1 | 110 | 4908661 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 SERVICE BURNT, REPLACED SERVICE. 37830246D00462 VER/CRB
21284 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-08-23 06:45 | 2014-08-23 08:35 | 1 | 110 | 4411211 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CLF WAS BAD ON HIGH SIDE OF TRANS. ALL PWR RESTORED PLEASE CLOSE TICKET THANK YOU LRM VER/KEP
21285 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-01-09 16:56 | 2014-01-09 17:51 | 2 | 55 | 4266481 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK VER/CRB IDC XXXX
21286 | South Williamson | 3200301 | BELFRY | BELFRY | 2010-07-08 13:30 | 2010-07-08 14:25 | 2 | 55 | 63445-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRMR FUSE OUT.....NO TREES....CAN NOT SEE ANY CAUSE....WILL RE-FUSE...//...FUSE WAS JUST BROKE AT BASE OF DOOR....RE-FUSED....JRV....07/08/10//VER/CRB IDC XXXX
21287 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-10-22 07:08 | 2008-10-22 07:30 | 5 | 22 | 57780-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307301//OPENED LINE FUSE ON POLE 130-36 AT 0708, CUTOUT FIRE VER/TOM IDCC TOF623, TON0700 XXXX
21288 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-02-26 20:20 | 2012-02-26 21:15 | 2 | 55 | 4509481 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMIT FUSE BURNING. ON POLE 117-228. WILL BE MAKING REPAIRS. TRANSFORMER OFF FROM 20:20 TO 21:15 I HAVE REPAIRS MADE EVERYTHING OK. //R/GAH IDC XXXX
21289 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2022-08-16 13:06 | 2022-08-16 14:56 | 1 | 110 | 4751071 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Ph B fuse blown onprimary metering. Found cracked cutouts on inspection. Replacing all three cutouts and arresters so we can troubleshoot. Opened hot line clamps on 38830809C30107 @ 14:00, replaced cutouts and restored @ 14:56. sh
21290 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-01-18 11:00 | 2012-01-18 12:50 | 1 | 110 | 4272651 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL COND PULLED APART IN PRESSED SLEEVE, REPAIRED COND. APR CLOSE TICKET VER/KEP IDC XXXX
21291 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-09-02 15:25 | 2015-09-02 16:20 | 2 | 55 | 4192041 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD 7200 CUTOUT,/ ISO 38830282000110/ COD 2/ VER/BOW
21292 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-01-29 01:40 | 2014-01-29 02:35 | 2 | 55 | 4320701 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | COD 2 CHANGE ISO POLE TO 151D3-327 15 KVA 7200 TRANSFORMER BAD, NEED 25 KVA, MATERIAL HANDLER AND 2 MEN.15 KVA 7200 TRANSFORMER BAD, NEED 25 KVA, MATERIAL HANDLER AND 2 MEN. OPENED @ 01:40 RELEASED BY CREW 077S04 TRANSFORMER REPLACED POWER RESTORED AT 02:35 MD FILED VER/KEP IDCC TOF1/28 XXXX
21293 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-01-04 10:24 | 2011-01-04 12:14 | 1 | 110 | 58533-1 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN SERVICE, MADE REPAIRS RESTORED POWER AT 12:14//VER/CRB IDC XXXX
21294 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-06-21 17:10 | 2011-06-21 17:20 | 11 | 10 | H4363521 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN ON 446-263, WIRE OFF INSULATOR AT POLE 446-22 BURNING CROSSARM, LIFTED CLAMP ON 446-90 TO ISOLATE .. CLOSED RECLOSER AT 15:15 RELEASED BY CREW 077S11 OPENED RECLOSER AT 1710 CLOSED IT AT 1720//COD 29// VER/DBM IDC XXXX
21295 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2021-05-26 10:29 | 2021-05-26 12:19 | 1 | 110 | 4624391 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | bad meter--Mtr number 190824006 was blank---changed meter---pwr restored @ 12:19---tbl tkt comp--rmv
21296 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-11-17 15:14 | 2015-11-17 15:25 | 10 | 11 | 4455211 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE ROTTED OFF AND LAID OVER INTO THE TREES// TIED OFF POLE /// OPENED L/F @ 15:14 // CLOSED @ 15:25/ ISO 37830024D10527/ COD 10/ VER/BOW
21297 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-02-17 10:35 | 2017-02-17 12:25 | 1 | 110 | 4404251 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ROTTEN FUSE 37830205C00486 1 VER/AWD L3/HFP XXXHFP
21298 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-02-23 14:45 | 2012-02-23 16:35 | 1 | 110 | 4487781 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | METERING FUSE BLOWN ON POLE 37830237A40305.GOING TO REFUSE.LOOKS LIKE FUSE BROKE.POWER RESTORED @ 16:35 VER/HFP L3/HFP AJB
21299 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2010-12-12 17:05 | 2010-12-12 18:00 | 2 | 55 | 65670-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW OPENED TRANSFORMER TO ALLOW THEM TO SAFELY CLEAR UP STREE LIGHT WIRE THAT IS DOWN AND TANGLED UP WITH SECONDARY - FROM ORDER 65645-1 05;05 TO 05;12 // COD-2 ISO TF 39831098C00429 VER/HFP L3/HFP IDC XXXX
21300 | South Williamson | 3200301 | BELFRY | BELFRY | 2021-07-14 15:20 | 2021-07-14 16:15 | 2 | 55 | 4911911 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | cust had an open neutral at pole 1014D-141.. i opend the transformer on pole 1014D-140 @15:20 to climb and fix the prb on pole 141..i got the fuse on pole 1014D-140 back in @16:15
21301 | Hazard | 3303902 | LESLIE | WOOTON | 2022-04-07 07:25 | 2022-04-07 09:15 | 1 | 110 | 4734561 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Repaced broke cut-out. Power restored @ 09:15///customer fed from pole 37830486000184
21302 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-09-27 17:50 | 2009-09-27 18:00 | 11 | 10 | H65661-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY DAMAGED-CALLED B REYNOLDS TO HELP REPAIR--OPENED TRANSFORMER AT 17:50 BACK IN AT 18:00 VER/KEP L3/KEP IDC XXXX
21303 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-12-31 11:20 | 2016-12-31 13:10 | 1 | 110 | 4258651 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE IN SERVICE FAILED AND BURNT SERVICE DOWN. REPAIRED AND RESTORED @ 13:10. SH VER/CRB
21304 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-12-29 10:04 | 2008-12-29 10:59 | 2 | 55 | 64881-1 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3002001// HAD A BAD CUTOUT ON A PHASE, HAVE IT REPLACED AND EVERYTHING SHOULD BE OK, AT THIS LOC. // COD 2// VER/TOM L3/TOM IDC XXXX
21305 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-02-02 18:40 | 2018-02-02 20:30 | 1 | 110 | 4796461 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced bad serve in.
21306 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-02-25 11:50 | 2011-02-25 12:45 | 2 | 55 | 61974-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | MADE REPAIRS TO CUST SERVICE DROP.//COD 2// VER/DBM IDC XXXX
21307 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-01-23 07:25 | 2022-01-23 09:15 | 1 | 110 | 4397711 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 10 mckenzie ave, auxier // part power // no customer phone number provided //insulink had melted out and burned neutrl and one hot leg into//repairs made//restored at 9:15//complete//em
21308 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-12-29 20:24 | 2012-12-29 20:35 | 10 | 11 | 4553401 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY LEAD GOT INTO SIDE OF TRANSFORMER AND WAS ARCHING GOING TO MAKE REPAIRS//COD 10// MADE REPAIRS ON SECONDARY RISERS RESTORED SERVICE OPENED TRANSFORMER UP @20:24 CLOSED BACK IN @ 20:35//COD 10// VER/DBM
21309 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-05-16 23:37 | 2018-05-16 23:59 | 5 | 22 | 4363231 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | open transformer at 2337 and closed at 2359
21310 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-02-15 16:05 | 2010-02-15 17:00 | 2 | 55 | 58069-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 33877971 // POLE 93-393 BURNT OFF POLE 93-4 20T SEND NOTE TO RAYBURN FOR TEC. TO RIGHT UP TEMP. POLE FOR NOW CANGET TO POLE AFTER WINTER//COD 1 MD FILED VER/KEP L3/KEP IDC XXXX
21311 | Hazard | 3311103 | STINNETT | WENDOVER | 2010-12-12 19:26 | 2010-12-12 21:16 | 1 | 110 | 65697-1 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38078204 //..BAD CONNECTION ON TRANSFORMER POLE... ALL POWER RESTORED @21:16 COD-1 ISO TF 37830435000254 VER/HFP L3/HFP IDC XXXX
21312 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-09-05 18:59 | 2016-09-05 20:49 | 1 | 110 | 4869921 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKEN ON 4/3 SERVICE DROP AND HOT LEGS MELTED TOGETHER, HAVE REPAIRS MADED AT THIS LOC BY AMG, SEND COPY TO PEGGY W. MAY BE DAMAGE CLAIM FOR THIS NOT SURE/ 39831070000005/ VER/BOW L3/HFP HFPC MCCNI CCPQ CDC85 FEC57 CNT6
21313 | Whitesburg | 3312901 | JENKINS | KONA | 2009-03-05 09:47 | 2009-03-05 11:37 | 1 | 110 | 55174-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3312901// PLEASE CANCEL THIS WILL TAKE CONST TO GET POWER BACK ON WE WILL REPAIR THIS LATER I TALKED TO GLENN COMBS ABOUT THIS RELEASED BY CREW 074S07//NOT CALLED IN BY CUSTOMER//SEASONAL USE ONLY//THIS WAS CALLED IN BY AEP METER READER// CLOSING ORDER// VER/DBM IDC XXXX
21314 | Pikeville | 3421001 | BREAKS | CITY | 2022-11-05 18:05 | 2022-11-05 19:55 | 1 | 110 | 4103451 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral burnt into in service drop///Repairs made everything is ok now 123/123/246///Restored full power @ 19:55// 1 customer was affected
21315 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-10-01 22:25 | 2009-10-02 00:15 | 1 | 110 | 63725-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400303//CUTOUT DOOR BAD 6T FUSE NEED TO CUT TREES. SEND TO R/W.......DAH VER/LDA IDC XXXX
21316 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-11-24 16:21 | 2014-11-24 18:11 | 1 | 110 | 4774661 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BAD WILL CALL FOR HELP/// REPLACED DEFECTIVE CUTOUT AND RESTORED POWER AT 18:11. TIM MCCOY RELEASED BY CREW 074H10 VER/HFP L3/HFP
21317 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-08-08 14:00 | 2010-08-08 15:50 | 1 | 110 | 51322-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR 36344935 //SERVICE DROP BURNT DOWN //OPENED TRAN. 15;30 TO 15;50//COD 10// VER/DBM IDC XXXX
21318 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2017-11-06 20:30 | 2017-11-06 22:20 | 1 | 110 | 4536921 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called cust/ trans cutout door burnt up will replace door replaced door restored power at 22:20
21319 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-06-05 08:34 | 2020-06-05 10:24 | 1 | 110 | 4961431 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad c/o on pole 48-C1-799, will be changing out. Got cutout replaced and closed back in @1024.
21320 | Pikeville | 3407101 | TOPMOST | DEMA | 2019-10-20 07:40 | 2019-10-20 09:30 | 1 | 110 | 4171181 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 6t fuse out du to tail of guy wire hit transformer riser. looks like fastener holding guywire poped out. repositioned guywire fused up everything ok/ ISO 37830162000010/ COD 1
21321 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-06-22 20:05 | 2011-06-22 21:00 | 2 | 55 | 4396751 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 118-4065 6T FUSE BROKE INSTALLED 10T 50KVA//COD 2// VER/DBM
21322 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-11-16 18:09 | 2009-11-16 18:31 | 5 | 22 | 62262-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CHG CUTOUT...BAD CUTOUT..BB COD-5 L3/HFP IDC XXXX
21323 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2017-01-10 08:58 | 2017-01-10 09:20 | 5 | 22 | 4282091 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ASSIGN TO TIM MCCOY TO BE WORKED DURING REGULAR HOURS TUESDAY A.M., , NEED TO REPLACE ALL SECONDARY CONNECTIONS AT TRANSFORMER, MAY BE ABLE TO REACH POLE WITH BIG BUCKET// REPLACED A BAD CONNECTION ON THE SECONDARY SIDE. MADE SECONDARY UP TO TRANSFORMER RISERS. OFF AT 8:58 BACK ON AT 9:20 TIM MCCOY/ SEND TO TECH NEEDS BIGGER TRANSFORMER INSTALLED FOR THE LOAD ISO 37830092000007/COD 5/ VER/BOW L3/HFP XXXHFP
21324 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-06-13 17:55 | 2010-06-13 18:50 | 2 | 55 | 63034-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURN IN HALF, REPLACED DOOR//COD 2// VER/DBM
21325 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2017-05-19 13:43 | 2017-05-19 15:33 | 1 | 110 | 4819431 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED SD VER/HFP L3/HFP
21326 | Hazard | 3309302 | VICCO | JEFF | 2016-03-03 12:05 | 2016-03-03 13:00 | 2 | 55 | 4806921 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGE LIGHTENING ARRESTOR.REPLACED ARR.P.HICKS..OPEN XFMR @12:05, AND CLOSED BACK IN AT 13:00// VER/ ADH
21327 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2018-11-07 10:33 | 2018-11-07 12:23 | 1 | 110 | 4375931 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad Leg in 350MCM UG service feeding RWHS ball field lights---company crew replacing UG Conductor--opened xfmr 1099B26998 @ 10:33---Out for most of the day---replaced 350mcm UG 135--pwr restored at 12:23---volt ck good 122/122/244---tbl tkt comp--rmv
21328 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2017-02-05 20:43 | 2017-02-05 22:33 | 1 | 110 | 4360071 | 110 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BOB SHURTLEFF REPORTS LIFT STATION OUT OF POWER MOUTH OF FIELDS WAY POSSIBLY POLE 37830048A11182. SECONDARY HOT LEG CONNECTION BURNDT INTO ON A 3 PHASE SERVICE OFF OF POLE 37830048A11182, WILL HAVE TO OPEN BANK TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED TRANS. BANK @2200, MADE REPAIRS AND CLOSED BACK IN @2233./// VER/DKM L3/HFP XXXHFP
21329 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-06-28 14:10 | 2018-06-28 16:00 | 1 | 110 | 4685441 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Replacing blown arrester and bad cutout so I can fuse transformer up to see if it is bad. Replaced cutout & arrester and restored @ 16:00. sh
21330 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-08-26 20:10 | 2008-08-26 20:21 | 10 | 11 | 55290-1 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3201001// BAD CUTOUT / WILL HAVE TO CHANGE OUT // POLE HAS BEEN ON FIRE, PROBABLY A BAD CUTOUT, PULLED WILLIAMS BRANCH OFF AT 2010 AND BACK ON AT 2021//COD 10//VER/CRB
21331 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-06-18 07:35 | 2017-06-18 09:25 | 1 | 110 | 4990191 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR ON POLE 204-13 CLOSED AT 9:25, POWER RESTORED. VER/CRB
21332 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2020-08-28 10:25 | 2020-08-28 11:20 | 2 | 55 | 4392141 | 110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | had a weak connection on pole 381-C-535. redid all connections.. open @ 10:25 closed @ 11:20
21333 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-04-13 14:34 | 2018-04-13 16:23 | 1 | 109 | 4221191 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Power restored, insalink came loose
21334 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2016-11-26 18:01 | 2016-11-26 19:50 | 1 | 109 | 4130841 | 109 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG BURNDT INTO ARCING AGAINST TRANS. MADE REPAIRS @1950. 37820025B00234 VER/AWD
21335 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2019-05-15 11:26 | 2019-05-15 13:15 | 1 | 109 | 4272481 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Risers out of transformer, repairs made and power restored at 13:15//COD 1 PER SERVICER//
21336 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-02-06 19:11 | 2010-02-06 21:00 | 1 | 109 | 51055-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SERVE ENDS ON SERVICE DROP AND REMOVED AND SQUEEZED UP GOOD EVERYTHING IS OK HERE AT THIS LOC VER/KEP L3/KEP IDC XXXX
21337 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-01-15 11:43 | 2015-01-15 13:32 | 1 | 109 | 4937311 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNT UP WILL REPLACE/// REPLACED BAD CURRENT LIMITING FUSE AND RESTORED SERICE @13:32/ ISO 37830117000021/ COD 1/ VER/BOW L3/HFP
21338 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-01-08 16:06 | 2012-01-08 17:55 | 1 | 109 | 4241411 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR FUSE BLOWN ON POLE 376-323, CONNECTION BURNT INTO AT XFMR.. MADE REPAIRS RESTORED POWER AT 17:55//COD 1 IDC XXXX
21339 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-01-09 22:26 | 2014-01-10 00:15 | 1 | 109 | 4267391 | 109 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED CONNECTION ON POLE COD-1 VER/KEP
21340 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-11-30 09:26 | 2013-11-30 11:15 | 1 | 109 | 4088951 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP TO REPAIR/////MADE REPAIRS,SERVE-IN CONNECTIONS HEATED UP AND BURNED SERV INTO.OFF AT 10:52,ON AT 11:15//COD 1 (+ 6 SEE H4088951)// VER/DBM
21341 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2012-11-21 12:25 | 2012-11-21 14:14 | 1 | 109 | 4413351 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER BAD ON THIS POLE FEEDS BARN AND CORN CRIB // CUSTOMER SAID IT CAN WAIT TILL MONDAY TO FIX// RELEASED BY CREW 076H04 // SENT TO MILLER HE IS AWARE AND WILL TAKE CARE OF // VER/DKG VER/TOM L3/TOM IDCC FEC57 XXXX
21342 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-09-11 09:31 | 2016-09-11 11:20 | 1 | 109 | 4884981 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE TOP IS BURNED OFF AT 38821107000078 AND BLOWED TAP FUSE. THIS DOES NOT SERVE ANYTHING, SO I MADE IT SAFE. I CLOSED TAP FUSE ON POLE 38821107000010 BACK IN AT 11:20./ ISO 38821107000010/ COD 1/ VER/BOW
21343 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-12-09 18:26 | 2017-12-09 20:15 | 1 | 109 | 4636351 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
21344 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-01-09 12:16 | 2017-01-09 14:05 | 1 | 109 | 4280611 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEC. LEAD BURNT INTO ON XFM WILL MAKE REPAIRS..REPAIRS MADE.RESTORED/ ISO 37830263B00256/ COD 1/ VER/BOW L3/HFP HFP
21345 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-03-06 14:02 | 2013-03-06 15:51 | 1 | 109 | 4883331 | 109 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER CHECKING FIXED BAD CONNECTION ON POLE POWER RESTORED KWB ///VER/CRB L/3 CRB IDC XXXX
21346 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-12-26 11:18 | 2012-12-26 13:07 | 1 | 109 | 4526061 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD DOOR IN CUTOUT, APR CLOSE TICKET. DWEST ///VER/CRB L/3 CRB
21347 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-01-06 10:06 | 2016-01-06 11:55 | 1 | 109 | 4589541 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2 SERVICE BURNT IN TWO NEAR WEATHERHEAD. REPAIRED AND RESTORED @ 11:55. SH/ ISO 38830954A10384/ COD 1/ VER/BOW
21348 | Hazard | 3303902 | LESLIE | WOOTON | 2019-08-14 12:35 | 2019-08-14 14:24 | 1 | 109 | 4886801 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout L3/HFP
21349 | Paintsville | 3401101 | FALCON | FALC-OILS | 2013-10-19 08:41 | 2013-10-19 10:30 | 1 | 109 | 4947781 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVE ENDS HEATED UP BURNING DOWN SERVICE DROP.2-3 TRIPLEX DROP.200 AMP SERVICE.CHG DROP..CONTRACTORS BUILT THIS LINE TO THIS RELOCATED TRAILOR SEVERAL YEARS AGO.PUT IN NEW DROP.//COD 1// VER/DBM
21350 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-12-11 16:55 | 2011-12-11 18:44 | 1 | 109 | 4169301 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BUT DOES NEED SENT TO ENGINEERING TO UPGRSDE ALL THIS SECONDARY RELEASED BY CREW 078S03//UPGRADE TRANSFORMER ///VER/CRB IDC XXXX
21351 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-07-20 20:05 | 2015-07-20 21:54 | 1 | 109 | 4920391 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET BURNT INTO, REPLACED WITH SREW ON BASKET, HT STILL ON BROKEN BASKET PLEASE SEND COPY TO LOYD R TO HAVE CREW REPLACE CUTOUT AND BASKET. APR AT 2154 CLOSE TICKET VER/HFP L3/HFP
21352 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-04-19 08:41 | 2021-04-19 10:30 | 1 | 109 | 4460331 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changed bad C/O 19.9//repairs made power restored 10:30
21353 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-05-30 14:21 | 2012-05-30 16:10 | 1 | 109 | 4849941 | 109 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE PHASE WIRES IN THE SERVICE AT THE TRANSFORMER. ONLY ONE CUSTOMER AFFECTED. ///VER/CRB L/3 CRB IDC XXXX
21354 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-01-09 01:20 | 2008-01-09 03:09 | 1 | 109 | 54894-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON 197-44 20T LINE FUSE ON 197-39 NEEDS CREW TO REPAIR BAD INSULATOR IN DAYLIGHT GOES OUT WHEN DAMP/BACK ON AT 0309/EXPLAINED WILL TAKE BACK OFF TO MAKE REPAIRS LATER RELEASED BY CREW 078S03 VER/KEP IDC XXXX
21355 | Paintsville | 3401102 | FALCON | SALYERSVI | 2011-12-12 17:41 | 2011-12-12 19:30 | 1 | 109 | 4172761 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD SECONDARY CONNECTION ON XFMR POLE. <<ONLY ONE CUSTOMER AFFECTED>> REPAIRED CONNECTION AND RESTORED @ 19:30. SH CCC = 1 ISO SO @ 38830850000104 VER/HFP L3/HFP IDC XXXX
21356 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-06-03 12:03 | 2014-06-03 13:52 | 1 | 109 | 4965451 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830248A00294, K. CAMPBELL ENROUTE TO ASSIST.//COD 1// VER/DBM
21357 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-04-11 03:53 | 2009-04-11 05:42 | 1 | 109 | 51350-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BELIEVE SURGE ARRESTOR HAS FAILED BUT IS FEEDING THRU ANYWAY,WILL REPLACE ITREPLACED SURGE ARRESTOR AND ALSO XFR CUTOUT THAT HAD A BAD CHIP IN IT COD-1 VER/LDA IDC XXXX
21358 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2020-10-17 09:05 | 2020-10-17 10:54 | 1 | 109 | 4563861 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRF IS OUT,WILL RE-FUSE///////////RE-FUSED&RESTORED.FUSE APPEARED TO HAVE JUST ROTTED INTO
21359 | South Williamson | 3200301 | BELFRY | BELFRY | 2011-02-28 20:14 | 2011-02-28 22:03 | 1 | 109 | 65163-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT CREW BRINGING ONE // RESTORED @ 2203 //VER/GAH IDC XXXX
21360 | Hazard | 3310502 | HADDIX | CANOE | 2011-01-19 07:11 | 2011-01-19 09:00 | 1 | 109 | 62560-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP ON TRANSFORMER COME LOOSE AND OFF LINE//COD 1// VER/DBM IDC XXXX
21361 | South Williamson | 3200302 | BELFRY | TOLER | 2008-10-09 21:18 | 2008-10-09 23:07 | 1 | 109 | 54753-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3200302//ON SITE, NEUTRAL BROKE IN SERVICE DROP, STUCK UP, TRYING TO GET OUT OF DITCH TO MAKE REPAIRS, NEUTRAL PULLED OUT OF SPLICE, POLE# 1040-181// VER/DBM IDC XXXX
21362 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-06-01 13:11 | 2011-06-01 15:00 | 1 | 109 | 4219101 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WIRE CUSTOMER WAS REPORTING LOW WAS CABLE. OUTAGE ON GARAGE IS BAD 19.9 25KVA TRANSFORMER. 501-404 CREW REQUIRED. CUSTOMER SAID IT COULD WAIT. NOONE OUT GARAGE ONLY RELEASED BY CREW 078S11 COD-1 ISO TF 38830501000404 VER/HFP L3/HFP IDC XXXX
21363 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-03-23 20:54 | 2009-03-23 22:43 | 1 | 109 | 61006-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6-T FUSE LINK BROKE RE PLACED 6-T FUSE//3007905/VER/CRB IDC XXXX
21364 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-08-17 12:41 | 2009-08-17 14:30 | 1 | 109 | 61263-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 37830507000050 WE HAVE SERVICE NEUTRAL BROKE. SERVICE NEUTRAL TENSION CONNECTOR PULLED OUT ON XFMR POLE. CUST. SAID EVERYTHING WAS WORKING EXCEPT HIS WINDOW AIR CONDITIONER. POWER RESTORED VER/KEP L3/KEP IDC XXXX
21365 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-01-05 19:26 | 2012-01-05 21:15 | 1 | 109 | 4236261 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HEATED UP AND BURNT BOTH HOT CONDUCTORS OPEN ON SECONDARY POLE. REPLACING SERVICE. REPLACED 2/3 SERVICE AND RESTORED @ 21:15. SH COD-1 ISO SO @ 38830834D00260 VER/HFP L3/HFP IDC XXXX
21366 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-07-07 15:19 | 2010-07-07 17:08 | 1 | 109 | 63105-1 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED 4/3 SERVICE BURNT DOWN VER/HFP L3/HFP IDCC PN NULL, FP NONE XXXX
21367 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-06-04 11:49 | 2014-06-04 13:38 | 1 | 109 | 4972421 | 109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON 526-18 BIG BUCKET MAY REACH POLE, LINECREW REQUIRED. DENSIL W WORKING TICKET RELEASED BY CREW 078S11 VER/SEF
21368 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-04-28 14:26 | 2011-04-28 15:20 | 2 | 54 | 51632-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE DROPED OPEN.//VER/CRB IDC XXXX
21369 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2009-07-26 09:09 | 2009-07-26 09:18 | 12 | 9 | H61601-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN POLE #102-80 #4 SOLID COPPER PRIMARY & NUT RELEASED BY CREW 077S10// BROKE IN THE CLEAR - LINE IS ENERGIZED UP TO POLE 102-80// IS SAFE// TRIED TO CALL FAA TO ADVISE WOULD BE OUT UNTIL MORNING NO ANSWER. OPENED RECLOSER 0909 CLOSED 0918 VER/KEP L3/KEP IDC XXXX
21370 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-10-16 09:32 | 2010-10-16 11:20 | 1 | 108 | 60252-1 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT INTO AT CUST SERVICE POLE . I HAVE REPAIRES MADE EVERYTHING OK//VER/CRB IDC XXXX
21371 | Pikeville | 3413401 | GARRETT | GARRETT | 2011-04-27 12:28 | 2011-04-27 12:40 | 9 | 12 | 65923-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER AT POLE 83 AT 12:28 AND CLOSED AT 12:40, FOUND NEUTRAL BUSHING LOOSE ON TRANSFORMER , ALL WORK COMPLETE / GXJ//VER/CRB IDC XXXX
21372 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-02-05 15:42 | 2015-02-05 17:30 | 1 | 108 | 4993591 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O, WILL HAVE TO CHANGE//// CHANGED OUT 19.9 C/O, POWER RESTORED/ ISO 37830178B30609/ COD 1/ VER/BOW L3/DKGXXXX
21373 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2020-09-22 14:23 | 2020-09-22 16:11 | 1 | 108 | 4486911 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout. repairs made. pls close. tre
21374 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2019-06-24 12:09 | 2019-06-24 13:57 | 1 | 108 | 4573951 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | cust had 4/3 srv drp, was burnted up from pole to house, i rem 40ft of 4/3 srv drp and installed 40 ft of 2/3 srv drp solving this problem at this loc, comp by amg
21375 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2017-07-19 11:12 | 2017-07-19 13:00 | 1 | 108 | 4142491 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGE XFMR OUT VER/CRB
21376 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-12-16 12:09 | 2015-12-16 13:57 | 1 | 108 | 4537411 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR & FUSE VER/CRB
21377 | Pikeville | 3413402 | GARRETT | LACKEY | 2012-05-22 13:41 | 2012-05-22 15:29 | 1 | 108 | 4818471 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION AT TRANSFORMER, REPLACED SQUEEZON, ALL WORK COMPLETE / GXJ ///VER/CRB L/3 CRB IDC XXXX
21378 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2020-07-09 19:20 | 2020-07-09 21:08 | 1 | 108 | 4137321 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad splice burnt service drop down. only one customer. made repairs and restored at 2108.
21379 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-07-06 17:57 | 2013-07-06 19:45 | 1 | 108 | 4475891 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE///////////RE-FUSED AND RESTORED,BELIEVE FUSE JUST BROKE,THIS IS A NEW INSTALLATION,ONLY BEEN IN ABT 4 DAYS//COD 1// VER/DBM IDC XXXX
21380 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-08-23 22:14 | 2018-08-23 22:50 | 3 | 36 | 4994961 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke, transformer back in at 22:50---TR pole 38830044A00179
21381 | Hazard | 3302703 | HAZARD | HAZARD | 2015-02-02 15:30 | 2015-02-02 15:48 | 6 | 18 | 4985261 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL DETERIORATED AND BROKE, POWER RESTORED. 37830296C10415 VER/CRB L3/HFP XXX
21382 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2009-04-06 18:52 | 2009-04-06 20:40 | 1 | 108 | 50010-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29258491 COD-1WR # 29258491BAD CUTOUT.WR # 29258491BAD CUTOUT.POLE NEEDS REPLACED SEND COPY TO RON RYE IN PIKEVIL L3/HFP IDC XXXX
21383 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2022-09-15 13:47 | 2022-09-15 15:35 | 1 | 108 | 4886461 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 103-38 will be making repairs///Replaced bad cutout and restored service 15:35
21384 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-08-29 12:37 | 2017-08-29 14:25 | 1 | 108 | 4307791 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE WIRE BURNT INTO AT WEATHER HEAD GETTING WIRE TO FIX NOW/ ISO 38830737000289/ COD 1/ VER/BOW L3/HFP XXXHFP
21385 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-11-02 14:57 | 2018-11-02 16:45 | 1 | 108 | 4357521 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced 2 connections on pole/ ISO 38830219000130/ cOD 1/ L3/HFP
21386 | Pikeville | 3421001 | BREAKS | CITY | 2010-08-12 10:36 | 2010-08-12 11:30 | 2 | 54 | 53506-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | COMPETED 081210 REPLACE BAD TRANFORMER TOM MCCOWN //VER/GAH
21387 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-04-28 23:30 | 2009-04-29 00:24 | 2 | 54 | 56669-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3002107 BROKEN FUSE LINK IDC XXXX
21388 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2017-07-30 08:17 | 2017-07-30 10:05 | 1 | 108 | 4206391 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | B PHASE METERING OUT ON POLE 38831151D30966, TAGGED B PHASE TO TIM HALL, CLOSED BYPASS ON B PHASE @1005. PLEASE SEND A COPY OF THIS TO DEWAYNE THACKER AND TIM HALL.//TAGGED TO TIM HALL//SENT TO MMETER ELECTRICIAN AND LINE// VER/CRB
21389 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-07-10 10:21 | 2020-07-10 10:48 | 4 | 27 | 4139791 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | open transformer at 1021 and closed at 1048
21390 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-02-09 10:57 | 2008-02-09 12:45 | 1 | 108 | 52895-1 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3400301//BAD SERVE-IN CONNECTIONS BURNED INTO,MADE NECESSARY REPAIRS AND RESTORED.ALL OK AFTERWARDS// VER/DBM IDC XXXX
21391 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2015-06-04 17:53 | 2015-06-04 18:47 | 2 | 54 | 4512411 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN DUE TO AGE REPLACED FUSE POWER RESTORED AT 18:47 VER/CRB
21392 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-06-28 11:00 | 2018-06-28 12:48 | 1 | 108 | 4684411 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | broken guy wire need guys repaired manuel pole // SENT EMAIL AS REQUESTED TO G COMBS COD-1 ISO TF 37830199C00084
21393 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-12-23 12:02 | 2021-12-23 13:50 | 1 | 108 | 4222141 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced brke cutout. power restored
21394 | South Williamson | 3411401 | DEWEY | INEZ | 2008-11-01 09:14 | 2008-11-01 09:32 | 6 | 18 | 61351-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411401//BURNT STIRRUP//VER/CRB IDCC TON946 XXXX
21395 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-07-13 09:45 | 2011-07-13 10:12 | 4 | 27 | 4534351 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WHITE HOUSE # 182 & BROWN TRL BEHIND HAVING PART POWER SOMETIMES. OFF POLE 37830214C00149. WILL NEED TO CHECK CONNECTIONS ON POLE. NO TRUCK. BJ RELEASED BY CREW 074E04 ALL CUSTOMERS HAD FULL POWER, HOWEVER I DID REPAIR A BAD CONNECTION WHERE THE TRANSFORMER WAS MADE UP TO THE #4 CU OPEN WIRE SECONDARY. COD-4 ISO TF 37830214C00130 VER/HFP L3/HFP IDC CHANGED TIME OFF FROM 1518 7/12 XXXX
21396 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-04-16 10:30 | 2014-04-16 10:57 | 4 | 27 | 4611661 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL PULL XFMR ON POLE #38821105C00166 OFF TO REPAIR SECONDARY CONNECTIONS. OPENED AT 1030 CLOSED @ 1057 COD-4 ISO TF 38821105C00166 VER/HFP L3/HFP
21397 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-06-15 15:32 | 2011-06-15 17:20 | 1 | 108 | 4323001 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | XFORM CUTOUT LUG ON TOP SIDE BROKE ALLOW PRI RISER TO BE LOOSE IN CUTOUT POWER RESTORED AT 17:20//COD 1// VER/DBM
21398 | Paintsville | 3401802 | INDEX | HOSPITAL | 2013-10-27 12:21 | 2013-10-27 13:15 | 2 | 54 | 4967301 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1300 - CHECKING TR TO DETERMINE CAUSE //BROKEN TRANSFORMER FUSEBROKEN TRANSFORMER FUSE..RE FUSED XFMR. COD-2 ISO TF 38830654D00273 VER/HFP L3/HFP
21399 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-10-24 21:27 | 2014-10-24 22:03 | 3 | 36 | H4660251 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 SERVICE BURNT DOWN BETWEEN 37830247D00769 AND 37830247D00869, OPENED TRANSFORMER ON 37830247D00769 AT 21:27, CLOSED AT 22:03...NO OBVIOUS REASON FOR WIRE TO BE BURNT DOWN. VER/KEP L3/HFP
21400 | South Williamson | 3200302 | BELFRY | TOLER | 2009-04-10 07:00 | 2009-04-10 07:36 | 3 | 36 | 50922-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE, XFORMER FUSE BLOWN, REFUSING IT, FUSE BROKE VER/PDP IDC XXXX
21401 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2011-12-19 08:12 | 2011-12-19 10:00 | 1 | 108 | 4187421 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER BAD SPLICE IN SERVICE, MADE REPAIRS RESTORED POWER AT 10:00, ONLY ONE CUSTOMER AFFECTED VER/HFP L3/HFP IDC XXXX
21402 | Pikeville | 3403001 | PIKEVILLE | CITY | 2009-06-17 12:41 | 2009-06-17 13:35 | 2 | 54 | 60265-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUT-OUT DOOR HAS BURNED INTO WILL REPLACE DOOR FAIL AS I ARRIVED WILL TALK TO CUST R RAY L3/HFP
21403 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2010-02-23 18:10 | 2010-02-23 18:28 | 6 | 18 | 60368-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, CHECKING TROUBLE/CRACKED CUTOUT NO OUTAGE CREW TO REPLACE ON SITE, CHECKING TROUBLE, XFORMER OFF AT 1810, BACK ON AT 1828 VER/KEP L3/KEP IDC XXXX
21404 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2008-12-26 12:37 | 2008-12-26 14:25 | 1 | 108 | 64083-1 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | JRV ON SITE @ 14:50......BAD UG SERVICE.....ONE HOT LEG GOING BAD.......TALKED TO R MARCUM....CAN PUT TEMP OVERHEAD IN UNTIL UG CAN BE TESTED & REPAIRED LATER ON....//..TEMP OVRHD SERVC INSTALLED....TOLD CUST THAT CO WILL CONTACT THEM NEXT WEEK TOARRANGE REPAIRS.....JRV..12/26/08//2150501//VER/CRB L3/KEP IDC XXXX
21405 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2022-02-27 16:27 | 2022-02-27 18:15 | 1 | 108 | 4550291 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse broken, changing
21406 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2022-05-19 09:29 | 2022-05-19 10:05 | 3 | 36 | 4910311 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened LF 38830183B00038 (3 COD) to put out pole fire at 138-2003---open 09:29---closed 10:05
21407 | Hazard | 3303902 | LESLIE | WOOTON | 2009-03-27 21:37 | 2009-03-27 22:31 | 2 | 54 | 62213-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//3303902...WILL HAVE TO LIFT CLAMP ON POLE 342-51 TO MAKE REPAIRS THIS WILL HAVE TO CUSTOMERS OFF *** @ 2010 WALLACE MELTON ENROUTE TO HELP RICK....LIFTED CLAMP AT 21:37, RESTORED POWER AT 22:31//3303902 IDCC TOF1945, TON2239, PN70 XXXX
21408 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-12-11 19:53 | 2018-12-11 21:41 | 1 | 108 | 4555481 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced xfr connections complete L3/HFP
21409 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-10-26 17:30 | 2020-10-26 18:06 | 3 | 36 | 4587291 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOING TO REPLACE LOUD BUZZING CUTOUT,MAY BE BREAKING DOWN ALTHO IT APPEARS OK////////REPLACED CUTOUT,HAD A SMALL CRACK IN IT.SEEMED TO STOP BUZZING NOISE.OFF@1730 BACK ON@18:06
21410 | Whitesburg | 3312902 | JENKINS | JENKINS | 2022-01-09 20:52 | 2022-01-09 22:40 | 1 | 108 | 4330811 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customers service had burnt down. service was undersized. ran new 2/3 service for customer. checked voltage, restored power
21411 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2009-11-13 10:27 | 2009-11-13 12:15 | 1 | 108 | 54584-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WR#32670109///REPLACE SEC. POLE AND SECONDARY COMPLTED AT 12:15 P R TOLLIVER VER/KEP L3/KEP IDC XXXX
21412 | Hazard | 3301401 | COMBS | COMBS | 2009-07-01 16:03 | 2009-07-01 16:30 | 4 | 27 | 58760-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NETURAL SPLICE HAS PULLED OUT WAITING ON CREW W.MELTON TOOK POWER OFF 16;03 ON16;30 COMP. W.MELTON VER/KEP L3/KEP IDC XXXX
21413 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2015-02-26 12:45 | 2015-02-26 13:39 | 2 | 54 | 4083751 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERV DROP BURNED INTO,WILL MAKE REPAIRS////////MADE REPAIRS AND RESTORED,NOBODY HOME,BUT SHOULD BE OK NOW///////SERVE-INS HEATED UP AND SHORTED SERV INTO/ DID NOT DUPLICATE BECAUSE THEY WERENT PART OUT AND BOTH CUSTOMER HAD SAME TIME OFF AND ON/ 12:45 1339/ ISO 37820054000026/ COD 2/ VER/BOW
21414 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-06-12 22:05 | 2019-06-12 23:53 | 1 | 108 | 4490571 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open @ xfm on service drop /// replaced bad connection and restored service @ 23:53
21415 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-11-16 10:54 | 2015-11-16 12:42 | 1 | 108 | 4451251 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV DROP BURNED INTO,WILL REPAIR//////POOR SERV-IN CONNECTIONS HEATED UP,BURNED NEUTRAL IN SERV DROP INTO.THERE ARE SOME DAMAGES HERE.MADE REPAIRS./ ISO 38821082000159/ COD 1/ VER/BOW
21416 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-11-26 11:15 | 2010-11-26 12:09 | 2 | 54 | 59829-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 400-314 HAS POLE ON FIRE. GOING TO EXTINGUISH FIRE AND REPLACE CUTOUT. PUT FIRE OUT AND REPLACED CUTOUT. OPENED X-FMR AT 11:15 AND RESTORED POWER AT 12:09. ONLY ONE SERVICE OFF OF POLE 400-314 SERVING AN OLD SHED. NO HOURS ON METER. 11/26/10. J. BAKER//VER/CRB IDCC PN292 XXXX
21417 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-05-04 14:15 | 2018-05-04 15:09 | 2 | 54 | 4306481 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse blown on high side of step-down due to cutout door bad..had to replace cutout on step-down pole 96D-390 ( high side )..opened xfm. @ 14:15 made repairs and closed back in @ 15:09...please send copy to Mike Hatfeild to have job written up to replace cutouts on both highside and load side of step-downs (old equip.) and to change out one 333 step-down xfm. noticed cracking around highside bushing...
21418 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2008-05-03 18:12 | 2008-05-03 20:00 | 1 | 108 | 56808-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000903// 6T ME FUSE BROKE//COD 1// VER/DBM IDC XXXX
21419 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-07-07 09:02 | 2012-07-07 10:50 | 1 | 108 | 4567191 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK WAS BROKE NOT BLOWN
21420 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2021-11-04 09:42 | 2021-11-04 11:30 | 1 | 108 | 4056251 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired service connection complete
21421 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-04-29 07:37 | 2009-04-29 08:13 | 3 | 36 | 56960-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000802//NO CREW REQUIRED REPLACED CUTOUT DOOR//COD 3//ISO 38830270D00025//NO CREW REQUIRED REPLACED CUTOUT DOOR/25 T LINE FUSE// VER/DBM IDC XXXX
21422 | Pikeville | 3410602 | E.PRESTON | LANCER | 2009-01-07 13:45 | 2009-01-07 14:39 | 2 | 54 | 52713-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED AT 13:45 /// CHANGED OUT CUTOUT AND ARRESTER // ON AT 14:39/ PRIMARY OPEN ON SOURCE SIDE OF POLE 48 ONLY 2 CUSTOMER OUT VER/KEP L3/KEP IDCC CNT1 XXXX
21423 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-02-01 22:24 | 2015-02-01 22:33 | 12 | 9 | H4979171 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRI. CONDUCTOR AT POLE 358-439 BURNED INTO UNDER TIE WIRE. IT OPENED RECLOSER AT POLE 359-113. I CUT A LOOP AT DOUBLE DEADEND POLE 359-34. I CLOSED RECLOSER AT 359-113 IN AT 18:55. HELP IS ON THE WAY. I OPENED RECLOSER AT 22:24 SO WE COULD PUT HOT TAP BACK ON LINE AT 359-34. WE CLOSED RECLOSER AT 22:33 / ISO 37830359A10113/ COD 55 AJB SEE 4979171
21424 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2010-02-18 21:36 | 2010-02-18 22:30 | 2 | 54 | 59048-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN 6T FUSE, REPLACED FUSE VER/HFP L3/HFP IDC XXXX
21425 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-12-30 12:39 | 2012-12-30 14:27 | 1 | 108 | 4556881 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED . REPLACED CUR LIM FUSE, ALL WORK COMPLETE / GXJ// COD 1// VER/DBM
21426 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-03-26 10:45 | 2011-03-26 11:12 | 4 | 27 | 59455-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 59431-1 NOTES FROM THAT ORDER " 248-626 WE HAVE A BAD XFMR C/O, WILL HAVE TO OPEN TAP OFF POLE 626 TO BE ABLE TO CHANGE C/O. TAP OFF FROM 10:45 TO 11:12. C/O CHANGED OUT POWER RESTORED." // SERVICER LIFTED HOT TAP ON POLE 37830248A00626 TO REPLACE CUTOUT ON POLE 37830248A00626 COD-4 ISO PO 37830248A00626 VER/HFP L3/HFP IDC XXXX
21427 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2013-09-10 11:07 | 2013-09-10 12:55 | 1 | 108 | 4834341 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT. LOOKS LIKE 6T FUSE BROKE. FUSED UP EVERYTHING OK COD-1 ISO TF 37830188C00264 VER/HFP L3/HFP
21428 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-06-04 09:00 | 2009-06-04 10:48 | 1 | 108 | 57162-1 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409301// XFMR CUTOUT BROKE. REPLACED AND RESTORED AT 10:48. SH//VER/CRB
21429 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2012-04-02 10:57 | 2012-04-02 12:45 | 1 | 108 | 4639711 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE PHASE WIRES IN THE SERVICE DROP VER/HFP L3/HFP IDC XXXX
21430 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-01-29 23:37 | 2010-01-30 01:25 | 1 | 108 | 61274-1 | 108 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUS.SER.SHORTED TOGETHER---REPAIRED SER. VER/LDA IDC CREATED DUPLICATE TO OPEN TRANSFORMER XXXX
21431 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-09-01 14:46 | 2022-09-01 15:40 | 2 | 54 | 4827011 | 108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse link broke
21432 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2018-02-04 12:33 | 2018-02-04 14:20 | 1 | 107 | 4800461 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | red to red pulled apart
21433 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-03-30 18:13 | 2015-03-30 20:00 | 1 | 107 | 4244811 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , REPLACED COD-1 ISO TF 37830295B30323 VER/HFP L3/HFP
21434 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-04-29 18:13 | 2017-04-29 20:00 | 1 | 107 | 4695861 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT/ ISO 38830174000104/ COD 1/ VER/BOW L3/HFP XXXHFP
21435 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2018-05-18 08:31 | 2018-05-18 10:18 | 1 | 107 | 4369271 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Wire came out of hot line clamp 1 phase out called for help//MADE MD TO SHOW 3-L/F 65T ON POLE 37830296C21621//Wire came out of hot line clamp 1 phase out called for help hot line broke 3 65t
21436 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-12-30 20:59 | 2020-12-30 22:46 | 1 | 107 | 4837091 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 12KV cutout on pole 246-C-507, manual, behind a house. Close spacing. Crew required. Released by crew 077H20 power restored at 10: 46
21437 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2011-05-31 11:23 | 2011-05-31 13:10 | 1 | 107 | 4213451 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION FAILED. INSPECTED SERVICE WIRE AND 1/0 SECONDARY AND THEY APPEAR TO BE OKAY. WILL HAVE TO ADD WIRE AND RE-WORK CONNECTIONS ON SEC POLE. REPAIRS COMPLETE. SH//VER/CRB IDC XXXX
21438 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-07-05 19:23 | 2015-07-05 21:10 | 1 | 107 | 4725591 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT , FUSE IS BROKE . CLOSED XFMR BACK @ 21:10 . VER/KEP
21439 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2022-03-08 16:03 | 2022-03-08 17:50 | 1 | 107 | 4590541 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse burnt into// repaired and power restored 17:50
21440 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-12-18 23:14 | 2015-12-19 01:01 | 1 | 107 | 4543891 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE TAIL VER/TOM L3/TOM
21441 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2008-06-11 07:23 | 2008-06-11 09:10 | 1 | 107 | 62412-1 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400101//CUT OUT FAILED . I WILL REPLACE REPLACED XFMR CUTOUT VER/HFP IDC XXXX
21442 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2013-05-09 21:43 | 2013-05-09 23:30 | 1 | 107 | 4092001 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COTOUT GATE FELL OPEN DIDNT BLOW FUSE CLOSED BACK POWER RESTORED ///VER/CRB L/3 CRB IDC XXXX
21443 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-06-13 14:34 | 2018-06-13 16:21 | 1 | 107 | 4597601 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT,WILL REPLACE IT///////////REPLACED CUTOUT&RESTORED////////ALL OK AFTERWARDS
21444 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2013-07-22 19:52 | 2013-07-22 21:39 | 1 | 107 | 4578141 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CALL DRT TO ASSIST--REPAIRED SERVICE COD 1 VER/SEF IDC XXXX
21445 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-07-30 12:43 | 2013-07-30 14:30 | 1 | 107 | 4607211 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED BROKEN NEUTRAL VER/HFP L3/HFP IDC XXXX
21446 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2016-11-30 15:43 | 2016-11-30 17:30 | 1 | 107 | 4151251 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON 795-19//CUTOUT BROKE ON POLE 795-84//MAKING REPAIRS//REPAIRS MADE//RESTORED AT 17:30//COMPLETE//EM
21447 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-06-17 09:24 | 2008-06-17 11:11 | 1 | 107 | 66502-1 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOTLEG AT SERVICE POLE BURNT INTO REPAIRED RELEASED BY CREW 078S11 VER/HFP
21448 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-05-04 09:43 | 2008-05-04 11:30 | 1 | 107 | 56929-1 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308402//SERVICE HEATED UP AND BURNT IN TWO//SERVICER REPLACED AND POWER RESTORED @ 1130// VER/DBM IDC XXXX
21449 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-01-29 09:43 | 2008-01-29 11:30 | 1 | 107 | 60593-1 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3308401// BAD UNDERGROUND AND BAD JUNCTION BOX ON OUR POLE, CUST TO GO OVERHEAD VER/KEP IDC XXXX
21450 | Hazard | 3303901 | LESLIE | HYDEN | 2015-04-03 10:46 | 2015-04-03 12:33 | 1 | 107 | 4263791 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 7200 CUTOUT//ISO//COD 1// VER/DBM
21451 | South Williamson | 3411401 | DEWEY | INEZ | 2010-08-06 10:33 | 2010-08-06 12:20 | 1 | 107 | 50268-1 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SQUEZZ ON BURNT OFF AT XFMER REPLACED CONNECTION
21452 | Hazard | 3303902 | LESLIE | WOOTON | 2010-12-30 13:28 | 2010-12-30 15:15 | 1 | 107 | 57072-1 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN THE SECONDARY OVER HEAD. YELLOW/YELLOW 1/0 SPLICE. ONLY 1 CUSTOMER HAVING TROUBLE ON THIS TRANSFORMER. VER/KEP L3/KEP IDC XXXX
21453 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-09-28 11:13 | 2017-09-28 13:00 | 1 | 107 | 4396711 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER/ METER IS BLANK/NO CREW REQUIRED REPLACED FUSE/ ISO 38830197000129/ COD 1/ VER/BOW
21454 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-09-25 08:23 | 2018-09-25 10:10 | 1 | 107 | 4154091 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole38830021B12051, opened line fuses on pole 38830021B12050 to safely change cutout. Cutout changed, line fuse open from 09:55 to10:10. All power restored ???????? HFP
21455 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-10-17 17:31 | 2011-10-17 19:18 | 1 | 107 | 4992371 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN . REPLACED FUSE, ALL WORK COMPLETE / GXJ ///VER/CRB IDC XXXX
21456 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-09-02 18:01 | 2011-09-02 19:48 | 1 | 107 | 4787831 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | # 2-3 DROP..POLE HAS BEEN CHG OUT SEVERAL YEARS AGO CREW USED SERVE ENDS TO SPLICE S/D..SERVE END HEATED UP BURNING S/D NEUTRAL IN TWO..REPLACED S/D.. VER/KEP IDC XXXX
21457 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-04-21 19:08 | 2015-04-21 20:55 | 1 | 107 | 4350501 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKE CUTOUT APR AT 2055 CLOSE TICKET VER/CRB
21458 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-05-29 11:08 | 2020-05-29 12:55 | 1 | 107 | 4927761 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole, opened xfmr at 12:25 closed at 12:55
21459 | Whitesburg | 3401301 | FLEMING | NEON | 2020-03-01 14:23 | 2020-03-01 15:40 | 4 | 77 | 4442491 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad connection on the xfmr lead , I changed it out. I opened the xfmr at 15:30
21460 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-08-31 17:13 | 2008-08-31 19:00 | 1 | 107 | 58068-1 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WILL NEED TO REPLACE TRANSFOMER AND CUTOUT COD 1 IDC XXXX
21461 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2022-03-31 10:22 | 2022-03-31 12:09 | 1 | 107 | 4701311 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | xfmer restored. tre
21462 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-07-25 08:13 | 2012-07-25 10:00 | 1 | 107 | 4822281 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT, BROKE CUTOUT ON POLE 110-28, POWER RESTORED// VER/DBM
21463 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-07-15 11:28 | 2008-07-15 13:15 | 1 | 107 | 52864-1 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3401702// WE HAD A BAD CONNECTION AT THE TRANSFORMER ON ONE OF THE HOT LEGS. // VER/TOM IDC XXXX
21464 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2012-10-31 18:43 | 2012-10-31 20:30 | 1 | 107 | 4305501 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION ON THE MAST I HAVE RESQUEEZED AND EVERYTHING IS BACK TO NORMAL AT THIS LOC AT 2030 ///VER/CRB L/3 CRB IDC XXXX
21465 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2016-12-22 11:21 | 2016-12-22 13:08 | 1 | 107 | 4228841 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT APR AT 1308 CLOSE TICKET VER/CRB
21466 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-03-17 09:53 | 2017-03-17 11:40 | 1 | 107 | 4564221 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, BROKE CUTOUT ON POLE 157-229, REPLACED CUTOUT, POWER RESTORED TO TV POWER SUPPLY- CAN CLOSE MAY NEED TO CORRECT MODELING TICKET WAS CLOSED ON THE WRONG TRANSFORMER MWL/ ISO 37830157000229/ COD 1 CODC***PER FEILD/ VER/BOW
21467 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2022-12-28 08:21 | 2022-12-28 10:08 | 1 | 107 | 4369341 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad insulink in drop/repairs made/also meter base had bad lug/electician working now & will call when ready for reconnect. tre
21468 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2009-03-17 18:14 | 2009-03-17 20:01 | 1 | 107 | 59570-1 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP ON SITE, CHECKING TROUBLE, METER THAT WAS IN TROUBLE WAS #533594564, LOOSE CONNECTION AT XFORMER POLE , NEUTRAL CONNECTION, COMP OF DAMAGES L3/HFP IDC XXXX
21469 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-01-29 09:46 | 2014-01-29 11:33 | 1 | 107 | 4323211 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER , BAD CONNECTION IN SERVICE DROP, MADE REPAIRS RESTORED POWER AT 11:33 VER/HFP L3/HFP
21470 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-05-25 20:13 | 2021-05-25 22:00 | 1 | 107 | 4622081 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout was bad and broke. Replaced and restored @22:00//cod 1
21471 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-07-09 13:35 | 2017-07-09 15:22 | 1 | 107 | 4099361 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF SERVICE DROP AT THE TRANSFORMER. VER/CRB
21472 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2020-05-06 12:13 | 2020-05-06 14:00 | 1 | 107 | 4806091 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service nuetral broken t pole.repaiired broken service nuetral
21473 | Pikeville | 3403001 | PIKEVILLE | CITY | 2014-05-15 14:48 | 2014-05-15 16:35 | 1 | 107 | 4710031 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON CROSSARM // CREW ENROUTE TO REPLACE /// REPAIRS MADE /// POWER RESTORED @ 16:35 // 5-15-14 COD-1 ISO TF 37820025A00385 VER/HFP L3/HFP
21474 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-01-01 06:18 | 2015-01-01 08:05 | 1 | 107 | 4896021 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 25T UG RISER FUSE APPEARS TO HAVE BROKE. RESTORED @ 8:05. SH VER/KEP VER/DKG L3/DKGXXXX
21475 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-06-02 01:07 | 2010-06-02 02:54 | 1 | 107 | 55141-1 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR--NEED TREE TICKET MADE--TREE AROUND POLE NEEDS REMOVED-- VER/ARN IDC XXXX
21476 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-01-04 11:23 | 2014-01-04 13:10 | 1 | 107 | 4228131 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 139-284 BAD CURRECT LIMMING FUSE MELTED DOWN REPLACED VER/CRB IDC XXXX
21477 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-02-19 11:28 | 2009-02-19 13:15 | 1 | 107 | 65267-1 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER LOOSE CONNECTION AT SEC POLE 211B411. I MADE REPAIRS EVERYTHING OK.// VER/DBM IDC XXXX
21478 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2022-01-13 09:08 | 2022-01-13 10:55 | 1 | 107 | 4342591 | 107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | both service leads were brunt at service pole and customer was getting part power, made new squeezes on service leads and restored power
21479 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2020-06-16 12:13 | 2020-06-16 14:00 | 1 | 107 | 4027411 | 107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 39831148D26543, fuse broke. resored at 14:00
21480 | Hazard | 3309302 | VICCO | JEFF | 2020-05-01 12:38 | 2020-05-01 14:24 | 1 | 106 | 4785201 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Secondary riser came out of transformer made reairs power ok
21481 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-05-29 12:44 | 2021-05-29 14:30 | 1 | 106 | 4646781 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse pulled into. restored 14:30
21482 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-03-19 13:29 | 2015-03-19 15:15 | 1 | 106 | 4209981 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT 19.9KV/ ISO 37820194C00054/ COD 1/ VER/BOW
21483 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-12-18 11:54 | 2018-12-18 13:40 | 1 | 106 | 4577151 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connection L3/HFP
21484 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2017-06-07 07:04 | 2017-06-07 08:50 | 1 | 106 | 4918361 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON WEATHER HEAD === REPAIRED === POWER OK 37830248B00390 VER/AWD
21485 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-02-05 15:14 | 2011-02-05 17:00 | 1 | 106 | 54414-1 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONNECTION IN SERVICE DROP FAILED AND BURNED NEUTRAL IN SERVICE DROP INTO. I SPLICED SERVICE DROP. CUSTOMER DID NOT KNOW FOR SURE IF ANY DAMAGES OR NOT.// VER/DBM IDC XXXX
21486 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-07-26 13:42 | 2010-07-26 14:35 | 2 | 53 | 57446-1 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | ON SITE P R TOLLIVER// FOUND BAD CURRENT LIMITING FUSE REPLACED AND CHECKED VOLTAGE POWER RESTORED AT 14:35 P R TOLLIVER VER/HFP L3/HFP IDCC PN84 XXXX
21487 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-02-08 09:44 | 2018-02-08 11:30 | 1 | 106 | 4816521 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | found connection burnt into on sec. side of xfm. on pole 265-232/////will make reapirs..restored//INSULINK
21488 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-09-05 15:49 | 2011-09-05 17:35 | 1 | 106 | 4821341 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 37830023000173 // FUSE OUT ON POLE 37830023000168 PER BOB SHURTLEFF. CALL BOB IF MORE INFO NEED WE ISOLATED THE TRANSFORMER BANK ON POLE 23-173 AS PER BOB SHURTLEFF. LINE FUSE BACK IN AT 1735. COD-1 ISO LF 37830023000168 VER/HFP L3/HFP IDC XXXX
21489 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2019-05-26 13:14 | 2019-05-26 15:00 | 1 | 106 | 4336651 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broke fuse
21490 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-06-16 13:07 | 2015-06-16 14:00 | 2 | 53 | 4579491 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC AT 1400// VER/ ADH
21491 | Hazard | 3420001 | SOFT SHELL | VEST | 2009-01-13 12:39 | 2009-01-13 14:25 | 1 | 106 | 54700-1 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, BAD CONNECTION ON POLE//3420001//VER/CRB L3/KEP IDC XXXX
21492 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-12-24 17:59 | 2015-12-24 19:45 | 1 | 106 | 4557871 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED 2/3 SER. NEUT & HOT LEG VER/CRB
21493 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-08-07 13:45 | 2012-08-07 15:31 | 1 | 106 | 4908071 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE COD-1 ISO TF 38830092B00481 VER/HFP L3/HFP IDC XXXX
21494 | Pikeville | 3413402 | GARRETT | LACKEY | 2012-11-13 18:28 | 2012-11-13 19:21 | 2 | 53 | 4395221 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN COD-2 ISO TF 37830064000078 VER/HFP L3/HFP IDC XXXX
21495 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-05-13 20:04 | 2011-05-13 21:50 | 1 | 106 | 4087881 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CUSTOMER HAS ONE LEG OPEN ON SERVICE DROP. WILL TRY TO CORRECT WITHOUT OPENING TRANSF.///////CUSTOMER HAD PARTIAL POWER. REPAIRED FAILED CONNECTOR, AND RESTORED TO FULL POWER AT 21:40. RELEASED BY CREW 074H03 VER/HFP L3/HFP
21496 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-02-16 21:44 | 2010-02-16 23:30 | 1 | 106 | 58524-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 33902235 /BAD CUTOUT /CHANGED OUT BAD 7200 CUTOUT. VER/LDA IDC XXXX
21497 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-06-20 18:29 | 2011-06-20 20:15 | 1 | 106 | 4358251 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON TRANSFORMER POLE, HAVE CHANGED AND CUST HAS POWER AT THIS LOC//COD 1// VER/DBM IDC XXXX
21498 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-12-16 17:49 | 2008-12-16 19:35 | 1 | 106 | 59159-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE. REMOVED HOT LINE CLAMP ON POLE 38830811B00004 TO ISOLATE TROUBLE. OPENED TAP AT 19:05 TAKING XFMR ON POLE 811- 4 OFFLINE ALSO 2 CUSTOMERS . REPAIR IN PROGRESS. REPLACED CUTOUT AND ENERGIZED TAP AT 19:35 RESTORING BOTH CUSTOMERS. SH VER/KEP L3/KEP IDC XXXX
21499 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-12-19 18:24 | 2008-12-19 20:10 | 1 | 106 | 60981-1 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3008702//BAD CONNECTION AT TRANSFORMER COD-1 VER/KEP L3/KEP IDC XXXX
21500 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-10-15 16:37 | 2010-10-15 18:23 | 1 | 106 | 60118-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN...RE FUSED TRANSFORMER 6 T FUSE..BB//COD 1// VER/DBM IDC XXXX
21501 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-02-16 07:42 | 2019-02-16 08:35 | 2 | 53 | 4799091 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer fuse, restored
21502 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-02-01 11:14 | 2011-02-01 13:00 | 1 | 106 | 52755-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR HAD BEEN OPEN FOR ABOUT TWO YEARS ,JUST INSTALLED SERVICE YESTERDAY I BELEAVE BAD FUSE//COD 1// VER/DBM IDC CHANGED FROM OTHER XXXX
21503 | South Williamson | 3202201 | LOVELY | LOVELY | 2016-05-05 23:59 | 2016-05-06 01:45 | 1 | 106 | 4180101 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38820746D10326TRANSFORMER CUTOUT DOOR BURNT UP ON 746-B-326 REMOVED DEFECTIVE DOOR AT 01:30 AND RESTORED POWER AT 01:45 ARRESTOR IS BROKEN OFF OF STANDOFF NEED BIG BUCKET TO REPLACE IT PLEASE SEND COPY TO TECH TO MAKE JOB TO REPLACE ARRESTOR VER/KEP
21504 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2015-09-14 08:21 | 2015-09-14 09:14 | 2 | 53 | 4235911 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE .ON POLE#38831003D00245 WILL REPLACE./ ISO 38831003D00245/ COD 2/ VER/BOW
21505 | Hazard | 3308001 | JACKSON | S.JACKSON | 2018-06-13 12:55 | 2018-06-13 14:41 | 1 | 106 | 4597001 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had broke cutout on pole 1083-1185
21506 | South Williamson | 3411401 | DEWEY | INEZ | 2017-04-18 16:45 | 2017-04-18 17:38 | 2 | 53 | 4655481 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER/ BAD CUTOUT CREW CHANGING 38820745B00044 VER/AWD L3/HFP XXXHFP
21507 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-07-28 12:09 | 2014-07-28 13:55 | 1 | 106 | 4301081 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT VER/CRB
21508 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-05-06 18:41 | 2015-05-06 20:27 | 1 | 106 | 4397871 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR C/O,/// CHANGED OUT BAD C/O , POWER RESTORED/ ISO 38831038000022/ COD 1/ VER/BOW
21509 | Hazard | 3309301 | VICCO | REDFOX | 2017-05-10 08:43 | 2017-05-10 10:29 | 1 | 106 | 4775291 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S02, SECONDARY LEAD BURNT OFF AT XFMR BUSHING , MADE REPAIRS RESTORED POWER AT 10:29.. VER/CRB
21510 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-01-10 13:34 | 2022-01-10 15:20 | 1 | 106 | 4333471 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up on secondary pole repairs made and restored @1520
21511 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-04-20 14:50 | 2010-04-20 15:43 | 2 | 53 | 65463-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34750426 // PLEASE HAVE SERV CK FOR HIGH VOLTAGE COMPLAINT.- GREG HEDRICK , COMM. ON SITE AN MEASURING 138 VOLTS TO GROUND AND 267 PH TO PH. NEED 12 KV 25KVA SINGLE BUSHING 120/240 ; CHECKED VOLTAGES ON TRANSFORMER LUGS--139/139/275 VOLTS; CHECKED TRANSFORMER DOWNSTREAM C PHASE--READS NORMAL; NEED 25KVA 7200 TRANSFORMER; TRUCK ACCESSABLE; RELEASE TO LINE CREW // COD-2 VER/HFP L3/HFP IDC XXXX
21512 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-05-09 13:40 | 2014-05-09 15:26 | 1 | 106 | 4677851 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACE BAD XFORMER VER/CRB
21513 | Hazard | 3310502 | HADDIX | CANOE | 2017-03-06 20:44 | 2017-03-06 22:30 | 1 | 106 | 4527941 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT ON POLE 97-32 , FUSE WAS BROKE . CLOSED XFMR BACK AT 22:30/ 37830097000032/ VER/BOW
21514 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-02-07 21:39 | 2014-02-07 23:25 | 1 | 106 | 4367361 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPEN NETURAL. REPAIRED SERVICE DROP.CONNECTION HEATED UP WHERE SERVICE HAD BEEN SPLICED & BURNED NETURAL IN TWO. VER/CRB
21515 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-06-03 12:06 | 2009-06-03 12:59 | 2 | 53 | 66140-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TIME OFF 1249 RELEASED BY CREW 078S11TIME OFF 1249 REPLACED CUTOUT DOOR //VER/GAH IDC XXXX
21516 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-04-07 22:30 | 2017-04-08 00:16 | 1 | 106 | 4629801 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM. CUTOUT BROKEN ON POLE 214C-120////WILL MAKE REPAIRS...//COD 1// VER/DBM L3/HFP XXXHFP
21517 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2015-09-14 08:21 | 2015-09-14 09:14 | 2 | 53 | 4235911 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE .ON POLE#38831003D00245 WILL REPLACE./ ISO 38831003D00245/ COD 2/ VER/BOW
21518 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-05-25 23:03 | 2011-05-25 23:56 | 2 | 53 | 4170151 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 20TFUSE HERE ALSO NO MD VER/KEP
21519 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2022-05-01 09:42 | 2022-05-01 11:28 | 1 | 106 | 4820231 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open at 241-C-114,InactiveTrans cutout on this pole broke causing line fuse to blow,No service Drops off this Trans isolated it and restored Line fuse at 11:28.
21520 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-04-12 16:59 | 2017-04-12 18:45 | 1 | 106 | 4641441 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4641541*** BROKE CUTOUT ON POLE 387C-240 ./ ISO 37830387C00240/ COD 1BROKE CUTOUT ON POLE 387C-240 . OPENED XFMR ON POLE 387C-240 @ 18:15 CLOSED BACK @ 18:45 . VER/AWD L3/HFP XXXHFP
21521 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-05-04 04:14 | 2009-05-04 06:00 | 1 | 106 | 64911-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT I WILL REPLACE,,,,I REPLACED CUTOUT. CUSTOMER BACK ON VER/ARN IDC XXXX
21522 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-01-28 16:04 | 2014-01-28 17:50 | 1 | 106 | 4320141 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 075H04 RED/RED SERVE END BAD @ XFMR//COD 1
21523 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-07-07 09:32 | 2017-07-07 11:18 | 1 | 106 | 4087301 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | A PHASE FUSE BROKE ON UNDER GROUND FEED TO PAD MOUNT TRANSFORMER VER/CRB
21524 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-10-11 15:19 | 2018-10-11 17:05 | 1 | 106 | 4228431 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t L3/HFP
21525 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2008-03-19 13:04 | 2008-03-19 14:50 | 1 | 106 | 58584-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401703// ANOTHER CUTOUT FAILED - COD 1.// VER/TOM IDC XXXX
21526 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-02-27 19:35 | 2014-02-27 21:21 | 1 | 106 | 4439451 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED BAD SERVIE END VER/CRB
21527 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2013-02-21 22:14 | 2013-02-22 | 1 | 106 | 4838781 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SERV ENDS IN SERVICE NO CREW REQUIRED// VER/DBM IDCC PN104 XXXX
21528 | Pikeville | 3410602 | E.PRESTON | LANCER | 2015-02-05 18:23 | 2015-02-05 20:09 | 1 | 106 | 4994101 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN IN SERVICE DROP //// WILL MAKE REPAIRS//// RESQUEEZED CONNECTIONS ON SERVICE DROP/// 123/123/246 EVERYTHING OK NOW//// ONLY 1 CUSTOMER AFFECTED// VER/ ADH L3/DKGXXXX
21529 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-06-27 19:14 | 2013-06-27 21:00 | 1 | 106 | 4418231 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SUDDENLINK POWER SUPPLY, BAD CONNECTION ON THE POLE. POLE 217-50. NO OTHER CUSTOMERS AFFECTED.// VER/DBM
21530 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-05-11 19:29 | 2012-05-11 21:15 | 1 | 106 | 4783401 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKEN IN SERVICE DROP /// GOING TO REPAIR /// POWER RESTORED @ 21:15 /// LONG DROP & NOT MUCH CLEARANCE OVER TRAILER, PLEASE SEND TO ENGINEERING TO SET SECONDARY POLE VER/KEP IDC XXXX
21531 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-01-08 07:44 | 2018-01-08 09:30 | 1 | 106 | 4719881 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//UNABLE TO CHECK BREAKERS//..fuse broken.re fusing
21532 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-09-08 17:08 | 2020-09-08 18:01 | 2 | 53 | 4442831 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Fuse door had burnt up apr at 1801 close ticket
21533 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2012-11-06 15:54 | 2012-11-06 17:40 | 1 | 106 | 4368561 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OLD TYPE CLAMP CONNECTION HAD BURNT OPEN. RE-WORKED ALL WEATHERHEAD CONNECTIONS AND RESTORED @ 17:40. SH COD-1 VER/KEP IDC XXXX
21534 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-05-09 11:49 | 2016-05-09 13:35 | 1 | 106 | 4189571 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER. DUE TO BROKEN NEUTRAL. NEUTRAL BROKE AT THE POINT WHERE IT WAS SERVED THROUGH THE CLEVIS. REPAIRED NEUTRAL EVERYTHING OK. METER# 533731225. SEND COPY TO PEGGY IN DAMAGE CLAIMS CUST COULD POSSIBLY CALL IN.//SENT TO CLAIMS VER/CRB
21535 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-07-31 11:47 | 2022-07-31 13:33 | 1 | 106 | 4642341 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew reqd truck ok/cutout looks ok/xfmer blown 2 times this morning/25kva. tre Released by crew 078S04///Repairs made ///Complete BR
21536 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2012-01-23 07:04 | 2012-01-23 08:50 | 1 | 106 | 4283741 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 3 CUTOUTS ON XFMR BANK.BANK IS NOT SHOWN ON MAP. 1 CUTOUT WAS BAD//ISO//COD 1// MD FILED VER/KEP IDC XXXX
21537 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-03-09 09:39 | 2020-03-09 11:25 | 1 | 106 | 4462221 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replaced xfmr and restored power @ 1125
21538 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2021-12-12 10:44 | 2021-12-12 12:30 | 1 | 106 | 4187761 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connections
21539 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-10-24 10:54 | 2010-10-24 12:40 | 1 | 106 | 62502-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ONLY 1 CUST ON THIS XFMR FUSED ROTTED OUT//COD 1 PER SERVICER// VER/DBM IDC XXXX
21540 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-07-19 20:22 | 2010-07-19 21:15 | 2 | 53 | 53513-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED FUSE DOOR//VER/CRB IDCC FEC49 XXXX
21541 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-03-06 08:09 | 2016-03-06 09:55 | 1 | 106 | 4820911 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR./ ISO 38830308000017/ COD 1/ VER/BOW
21542 | Hazard | 3311103 | STINNETT | WENDOVER | 2020-02-27 10:46 | 2020-02-27 12:17 | 2 | 91 | 4436471 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | checked voltage at meter and top of breaker, bad connection on pole, opened xfmr at 12:02 closed at 12:17 L3/HFP
21543 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-05-09 21:54 | 2016-05-09 23:40 | 1 | 106 | 4191251 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RESET BREAKERS. METER BLANK. BAD CUTOUT , REPLACED CUTOUT , POWER BACK ON @ 23:40 .//COD 1// VER/DBM
21544 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-01-27 12:24 | 2020-01-27 14:10 | 1 | 106 | 4342071 | 106 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | secondary splice failed on38821138C00158.replaced splice re-energized at 14:00//COD 1
21545 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-04-03 08:16 | 2008-04-03 10:02 | 1 | 106 | 63320-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3300601//7200 VOLT CUTOUT BAD ON PRIMARY UG TO PADMOUNT ON POLE 37830272C10538 // VER/TOM IDCC PN1436 XXXX
21546 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-05-08 21:14 | 2010-05-08 23:00 | 1 | 106 | 58519-1 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GOINGTO CHANGE.CHANGED CUTOUT BACK TO NORMAL//VER/CRB IDC XXXX
21547 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-10-02 13:09 | 2014-10-02 14:55 | 1 | 106 | 4544901 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER MIS-MAPPED.CORRECT XFMR FOR THIS METER IS 38830905000051...ONLY ONE CUST AFFECTED INSULINK CONNECTION BURNT UP ON XFMR POLE. HAD TO REPLACE SECONDARY RISERS. REPAIRS COMPLETE - RESTORED @ 15:55. SH COD-1 ISO SO @ 38830905000051 VER/HFP L3/HFP
21548 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-02-03 14:17 | 2014-02-03 16:03 | 1 | 106 | 4344841 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED SERVIVE DROP VER/SEF
21549 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2017-01-14 12:32 | 2017-01-14 13:25 | 2 | 53 | 4297591 | 106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TR// CREW REPLACING. REPLACED XFMR AND RESTORED @ 13:25. HAD LINE FUSE 810-52 OPEN FROM 13:10 TO 13:25. SH RELEASED BY CREW 076S02/ ISO 38830810D00074/COD 2/ VER/BOW // RELATED TO 4297631 - FUSE OUTAGE = L3/HFP HFP
21550 | South Williamson | 3411401 | DEWEY | INEZ | 2019-04-24 15:03 | 2019-04-24 16:48 | 1 | 105 | 4154811 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 743-148 where u/g comes back to overhead//i opened line fuse on 743-29 to isolate//same customer count///cutout replaced//cutout on 743-29 also broke//replaced both cutouts//restored at 16:48//complete//em
21551 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-13 08:45 | 2015-02-13 10:30 | 1 | 105 | 4012811 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK PULLED APART AT WEATHERHEAD//I REWORKED CONNECTIONS///RESTORED AT 10:30//COMPLETE//EM// VER/ ADH L3/HFP XXX
21552 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-02-24 19:00 | 2011-02-24 19:35 | 3 | 35 | 60882-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38938274 ///ON SITE BAD CUTOUTPUT OUT FIRE,POLE WILL NEED TO REPLACE 1ST THING FRIDAY ,SEND TO DOUG AND GLEN...40 FT POLE CUT OUT ARR. COMPLETE. COD-3 ISO TF 38831060B00022 VER/HFP L3/HFP IDC CHANGED START TIME FROM 1757 XXXX
21553 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-01-01 01:25 | 2008-01-01 03:10 | 1 | 105 | 52242-1 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRING CONNECTION ON POLE VER/KEP IDC XXXX
21554 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-12-18 12:15 | 2020-12-18 14:00 | 1 | 105 | 4784501 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 20t lf restored @ 13:25, current limiting replaced @ xfmer & restored @ 14:00 LR-The 1st CC was 12:15 on 12/18/20
21555 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-04-06 13:40 | 2022-04-06 15:25 | 1 | 105 | 4730581 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced and restored @ 15:25. sh
21556 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2019-10-11 11:00 | 2019-10-11 11:21 | 5 | 21 | 4131091 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connection off at 11 back on at 1121
21557 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2017-12-05 13:18 | 2017-12-05 13:25 | 15 | 7 | 4622551 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Crews opened recloser on 38830114000251 to make emergency repairs. open recloser @ 1318 OPENED 1318-1325 /// PER VOICE RECORDER STRAND BROKEN IN PRIMARY IN FRONT OF 2216 W COBB FORK @ 38830114000068
21558 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-06-08 13:45 | 2011-06-08 14:20 | 3 | 35 | 4268621 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL PULLED OUT OF SPLICE MIDSPAN VER/DKG L3/DKG IDCC TOF1202 ESTIMATED TIME OFF FOR REPAIR XXXX
21559 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-12-11 06:30 | 2017-12-11 08:15 | 1 | 105 | 4638191 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg burnt into.opened xfmr to make repaires at 8:02 restored power at 8:15/ 1 customer part out originally/ when opened 2 add cust/ ISO 37830205D00107/ COD 3
21560 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-12-14 12:00 | 2014-12-14 13:45 | 1 | 105 | 4859781 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP HAD OLD SPLIT BOLT CONNECTORS //ONE LEG BURNED COMPLETELY INTO AND THE OTHER ALMOST INTO///I REWORKED ALL CONNECTIONS//RWSTORED BACK TO NORMAL AT 13:45//COMPLETE//EM// COD 1// VER/ ADH
21561 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-08-09 12:00 | 2022-08-09 13:45 | 1 | 105 | 4709371 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke power restored at 13:45
21562 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-12-07 11:50 | 2015-12-07 12:25 | 3 | 35 | 4515771 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD FUSE LINK, ROTTEN AND BROKE, REPLACED POWER RESTORED AT THIS LOC AT 1225 COD-3 ISO TF 39831123B00553 VER/HFP L3/HFP
21563 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-02-03 17:38 | 2010-02-03 19:23 | 1 | 105 | 62791-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SECONDARY// VER/DBM IDC XXXX
21564 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-01-24 22:00 | 2012-01-24 22:35 | 3 | 35 | H4290771 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CUSTOMER IS ONLY GETTING 120V IN METER BASE.VOLTAGE ON POLE CHECKED GOOD, 4/0 UNDERGROUND SERVICE MUST HAVE A CONDUCTOR OPEN.WILL NEED A 3MAN CREW //DALE HAMILTON & PAUL LAYNE & TOM MCCOWN // OPENED XFMR @ 22:00 ON @ 22:35.TEMPORARY REPAIRS MADE (AUTO TRANSFORMER), WILL HAVE TO WORK IN THE MORNING COD-4 ISO TF 38831126A00461 DUP FROM 4290771 FOR 3 CUST VER/HFP L3/HFP IDC XXXX
21565 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2022-02-19 15:10 | 2022-02-19 16:55 | 1 | 105 | 4518101 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | secondary lead burnt into, made repairs restored @ 16:55
21566 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-02-12 08:10 | 2011-02-12 09:55 | 1 | 105 | 56342-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT AT POLE 472-43, REPLACED CUTOUT, BAD CUTOUT WAS INSTALLED NEW IN 2005. VER/KEP IDC XXXX
21567 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-08-03 11:48 | 2011-08-03 13:33 | 1 | 105 | 4659211 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED BROKEN CUTOUT ON RT 1947 BEFORE S AND S READY MIX TRUCK OK NEED TO FLAG TRAFFIC RELEASED BY CREW 078S03 VER/KEP IDC XXXX
21568 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-06-07 09:25 | 2018-06-07 09:40 | 7 | 15 | 4565041 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fuse door burnt into
21569 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-07-23 09:08 | 2010-07-23 10:53 | 1 | 105 | 55856-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WORK REQ - 36118011 // SERV DROP BURNT DOWN/// REPAIRED #4 AND #2 TRIPLEX//// CONNECTION WENT BAD AND BURNT CONDUCTOR ON SEC POLE//// PWR CK OK... VER/KEP L3/KEP IDC XXXX
21570 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-01-08 17:35 | 2013-01-08 19:20 | 1 | 105 | 4579241 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD DOOR IN CUTOUT.//COD 1 //ISO 38830308000017//MD FILED// VER/DBM IDC XXXX
21571 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-09-18 12:30 | 2009-09-18 13:05 | 3 | 35 | 51505-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CHANGED CUTOUT & XFORMER & RESAGED PRIMARY WIRE L3/HFP IDC XXXX
21572 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-12-29 11:40 | 2010-12-29 13:25 | 1 | 105 | 56728-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED/REPLACED FUSE DOOR //COD 5// ISO 38830223000040 // IDCC FEC49 XXXX
21573 | Hazard | 3302704 | HAZARD | KENMONT | 2016-03-14 15:45 | 2016-03-14 16:00 | 7 | 15 | 4843821 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON SECONDARY BAD REPAIRED POWER OK OPEN TRANSF 15:45 CLOSED AT 16:00 POWER OK/ ISO 37830320C00239/ COD 7/ VER/BOW
21574 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2017-10-01 21:30 | 2017-10-01 21:45 | 7 | 15 | 4403571 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUSTOMER-NO ANSWER OPEN XFMER @ 21:30, RESTORED 21:45--REPAIRED FAILED SECONDARY CONNECTION/// VER/DKM L3/HFP XXXHFP
21575 | Pikeville | 3413401 | GARRETT | GARRETT | 2021-11-30 16:10 | 2021-11-30 16:45 | 3 | 35 | 4134891 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary down from 37830016D00058 to 37830016D00168.//Wire burnt in clear at stirrup.// No customer out.// Crew required Released by crew 074S11//opened L/F on pole 16-54 @ 16:10 closed at 16:45 Released by crew 074H07
21576 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-11-12 17:45 | 2018-11-12 19:30 | 1 | 105 | 4392891 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replACED FUSE L3/HFP
21577 | Hazard | 3309002 | JEFF | JEFF | 2018-04-16 09:03 | 2018-04-16 10:48 | 1 | 105 | 4237591 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Middle phase riser has brunt out and neutral 321D/416 cod 1 iso 37830321D00416 // restored @ 1048 L3/HFP
21578 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-06-21 16:53 | 2012-06-21 18:38 | 1 | 105 | 4941251 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKING.TRANS. FUSE PULLED APART, REFUSED AT 18:38.//COD 1// VER/DBM
21579 | Hazard | 3309302 | VICCO | JEFF | 2021-02-20 18:55 | 2021-02-20 20:40 | 1 | 105 | 4198751 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout on pole 323C123 Power restored at 20:40
21580 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2020-10-16 14:45 | 2020-10-16 15:20 | 3 | 35 | 4562321 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANS FORMER @ 1445 CLOSED @ 1520 TO MAKE CONNECTIONS
21581 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-11-14 12:20 | 2015-11-14 12:35 | 7 | 15 | 4447761 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMER OFF @ 12:20 ON @ 12:35// VER/ ADH
21582 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-07-10 18:15 | 2010-07-10 20:00 | 1 | 105 | 64925-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLEW ON POLE 357-68, ALSO NEED NEW ANCHOR INSTALLED. NO TRUCKS TO POLE.//AED CREATED AND EMAILED TO TECH//COD 1// VER/DBM IDC XXXX
21583 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2017-03-30 21:00 | 2017-03-30 21:15 | 7 | 15 | 4599381 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE AND HOT LEGS BURNTED INTO ON4/3 SERV DRP, REPAIRS MADED ALL GOOD AT THIS LOC, BY AMG, OPEN TRANSFORMER AT 2100, CLOSED BACK IN AT 2115 BY AMG// VER/ ADH
21584 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2010-10-08 14:13 | 2010-10-08 14:48 | 3 | 35 | 58111-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OUTAGE FROM/RELATED TO 58016-1 VER/HFP L3/HFP IDC XXXX
21585 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-03-20 11:15 | 2018-03-20 13:00 | 1 | 105 | 4030521 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse out on pole 38830875B10987fuse out on pole 875-987// looks like 20t fuse broke refused it held // they checked there equipment it good // complete tt
21586 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-06-04 14:51 | 2008-06-04 16:36 | 1 | 105 | 56326-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3411802//TREE TO CUT AWAY FRM XFR,XFR TO RE-FUSECUT TREE AWAY,ALSO HAD TO REPLACE CURRENT LIMITING FUSE.RE-FUSED XFR,ALL OK AFTERWARDS//COD 1// VER/DBM
21587 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-07-19 15:30 | 2014-07-19 16:05 | 3 | 35 | 4264071 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-858 BAD CUTOUT AND LA REPLACED//COD 3// VER/DBM
21588 | Hazard | 3302703 | HAZARD | HAZARD | 2012-07-23 15:15 | 2012-07-23 15:50 | 3 | 35 | 4799471 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830272D10978 --- OPENED TRANSFORMER AT 15:15, CLOSED AT 15:50 VER/KEP
21589 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-01-11 18:15 | 2013-01-11 20:00 | 1 | 105 | 4596991 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830303000222, REPLACED CUTOUT, ALL POWER RESTORED//COD 1// VER/DBM IDC XXXX
21590 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-07-13 12:04 | 2012-07-13 13:49 | 1 | 105 | 4712371 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BAD ------ CHANGED CUTOUT ----- POWER RESTORED @ 13:40//COD 1
21591 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2014-03-04 14:27 | 2014-03-04 16:12 | 1 | 105 | 4451311 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF THE SERVICE AT THE WEATHER HEAD. ONLY ONE CUSTOMER WAS OFF. VER/CRB
21592 | Hazard | 3310502 | HADDIX | CANOE | 2018-12-06 13:57 | 2018-12-06 15:42 | 1 | 105 | 4513011 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout L3/HFP
21593 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-07-16 20:30 | 2013-07-16 22:15 | 1 | 105 | 4533691 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE NETURAL. PULLED XFMR OFF ON POLE#38831101C40077 @ 10:00 BACK ON @10:15//COD 1 (+ 1, SEE H4533691)// VER/DBM IDC XXXX
21594 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-12-29 11:35 | 2016-12-29 13:20 | 1 | 105 | 4248501 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | K-MATE CURRENT LIMITING DEVICE ON TRANSFORMER HAS GONE BAD, WILL REPLACE AND TRY TRANSFORMER..P.HICKS.ALL POWER RESTORED @ 13:20 HRS.P.HICKS// VER/ ADH
21595 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2020-03-20 12:45 | 2020-03-20 14:30 | 1 | 105 | 4495701 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken 12kv c/o. trk to pole. to b.reynolds
21596 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2019-01-23 16:50 | 2019-01-23 18:35 | 1 | 105 | 4711391 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | serve-in pulled apart , I replaced it L3/HFP
21597 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-12-15 20:55 | 2010-12-15 21:30 | 3 | 35 | 50837-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED.//COD 3// VER/DBM IDCC TOF1931 XXXX
21598 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2011-08-22 10:30 | 2011-08-22 11:05 | 3 | 35 | 4741641 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WILL OPEN XFMR TO CHECK CUTOUT /CONNECTIONS//XFMR SEC. RISER WAS IN BAD CONDITION// REPLACED RISER //VER/CRB IDCC TOF0911 ESTIMATED TIME OFF XXXX
21599 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-11-22 20:05 | 2021-11-22 21:50 | 1 | 105 | 4117201 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing..changed xfmr cutout.. back on 21:50//cod 1
21600 | Pikeville | 3421001 | BREAKS | CITY | 2016-10-12 08:58 | 2016-10-12 10:43 | 1 | 105 | 4987371 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SERVICE DROP, ONE CUSTOMER AFFECTED VER/CRB L3/HFP XXXHFP
21601 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2012-01-13 09:56 | 2012-01-13 11:41 | 1 | 105 | 4257091 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHANGED OUT 4-3 DROP TO 2-3 DROP.CUST HAD SERVE END BAD. VER/KEP IDCC CNT2 XXXX
21602 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2010-02-27 18:20 | 2010-02-27 20:05 | 1 | 105 | 61607-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 34050381 // NO CREW REQUIRED REPAIRED CONNECTION VER/HFP L3/HFP IDC XXXX
21603 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-09-26 12:54 | 2016-09-26 14:39 | 1 | 105 | 4927011 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP ==== REPLACED GATE ==== POWER OK/ ISO 37830491000140/ COD 1/ VER/BOW L3/HFP XXXHFP
21604 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2020-04-30 13:00 | 2020-04-30 14:45 | 1 | 105 | 4781331 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o-replaced- tran in at 14:45-allgood-ds043020
21605 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2022-09-26 14:05 | 2022-09-26 14:20 | 7 | 15 | 4926321 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole is old and leaning allowing open wire secondary to sag down and get together in trees. Opened xfmr at 14:05 to resag secondary. Closed xfmr @ 14:20. I will send a job to eng to replace pole. sh
21606 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-11-01 14:45 | 2019-11-01 15:20 | 3 | 35 | 4275541 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr. send ticket to George Whitaker Released by crew 077S12 1445 to 1520
21607 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-08-08 02:00 | 2021-08-08 02:35 | 3 | 35 | 4017741 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 75-208 and covered in vines///Opened xfm @ 02:00 removed vines and changed bad cutout///Restored @ 02:35//cod 3
21608 | Hazard | 3303901 | LESLIE | HYDEN | 2010-05-02 11:30 | 2010-05-02 13:15 | 1 | 105 | 53786-1 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED XFMR CUTOUT AND REFUSED LINE//VER/CRB IDCC PN169, CNT1 XXXX
21609 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-05-26 21:41 | 2013-05-26 23:26 | 1 | 105 | 4187151 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT///NEED 1 MAN AND BUCKET TO CHANGE///CHANGED CO///PWR CK OK. CC 1. VER / SDB IDC XXXX
21610 | Hazard | 3310502 | HADDIX | CANOE | 2016-03-14 21:55 | 2016-03-14 22:30 | 3 | 35 | 4848111 | 105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT ON POLE 37830025000009/ HAVE TO OPEN TRANSFORMER ON POLE 37830025000009 TO CHANGE/ ISO 37830025000009/ COD 3/ OPEN TRANSFORMER AT 2155 AND CLOSED AT 2230/ VER/BOW
21611 | Hazard | 3302703 | HAZARD | HAZARD | 2015-02-25 09:45 | 2015-02-25 11:30 | 1 | 105 | 4080051 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 PART OUT ORIGINALLY/ BAD CONNECTION AT SPLICE IN SERVICE. OPENED TRANSFORMER AT 10:59, REPAIRED SERVICE, CLOSED TRANSFORMER AT 11:30/ ISO 37830272B40320/ COD 8/ DUPLICATE IN HOIS SEE H4080051/ VER/BOW
21612 | Whitesburg | 3401301 | FLEMING | NEON | 2013-03-04 06:35 | 2013-03-04 08:20 | 1 | 105 | 4868441 | 105 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK AT REGULAR WORK TIME // RED - RED SQUEEZEON FROOZE OUT. I REPLACED IT VER/HFP L3/HFP IDC XXXX
21613 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-04-25 23:36 | 2010-04-26 01:20 | 1 | 104 | 51171-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3401702// NON TENSION SLEEVE IN THE NEUTRAL PULLED OUT. THIS CUSTOMER STATED THAT A CREW FROM MICHIGAN REPAIRED THIS DURING THE 12/09 SNOW STORM. CUSTOMER COMPLAINING OF APPLIANCES DAMAGED. #2 SERVICE. VER/DKG L3/DKG CHANGED MCC FROM PART POWER TO DL IN ORDER TO DOCUMENT OH SPLICE AS FAILED EQUIPMENT/ORIGINAL CALL WAS PART POWER IDC XXXX
21614 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2009-03-30 14:33 | 2009-03-30 16:17 | 1 | 104 | 63113-1 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SEC BURNT UP RELEASED BY CREW 078S08---CREW WILL REMOVE AND INSTALL TWO SPANS OF 1/0 SEC // VER/TOM L3/TOM IDCC MCCNI XXXX
21615 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-04-03 22:11 | 2014-04-03 23:55 | 1 | 104 | 4570661 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT. COD-1 ISO TF 38821062C00278 VER/HFP L3/HFP
21616 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-07-21 07:10 | 2021-07-21 08:54 | 1 | 104 | 4940741 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRF IS OUT,WILL RE-FUSE/////////REPLACED PORCELIN CUTOUT WHILE@SITE,RE-FUSED&RESTORED POWER.NOTHING VISIBLY WRONG WITH CUTOUT BUT REPLACED IT ANYWAY
21617 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2017-08-26 15:13 | 2017-08-26 16:57 | 1 | 104 | 4301261 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON SECONDARY , MADE REPAIRS RESTORED POWER AT 16:57..ONLY ONE CUSTOMER AFFECTED. VER/AWD
21618 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2008-12-07 16:37 | 2008-12-07 18:21 | 1 | 104 | 55183-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3400302//REPLACEDN4/3 SERVICE WITH 2/3 - OPENED TRANSFORMER @ 1815 AND CLOSED BACK IN @ 1821 RESTORING ALL CUSTOMERS 5 TOTAL - 1 ACCOUNTED FOR IN THIS OUTAGE OTHER 4 IN 55183-1H// VER/TOM L3/TOM IDC XXXX
21619 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-03-26 14:12 | 2009-03-26 15:56 | 1 | 104 | 61796-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SDRAY CHANGING XFMR OUT FBLANKENSHIP BRINGING XFMR//COD 1// VER/DBM IDC XXXX
21620 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2009-11-17 15:57 | 2009-11-17 17:41 | 1 | 104 | 65822-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP 10T LINE FUSE4 OUT ON POLE 39831122C0002312T LINE FUSE OUT ON POLE 39831122C00023// ENTERED MD ...HFP L3/HFP IDC XXXX
21621 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2022-03-21 07:23 | 2022-03-21 08:15 | 2 | 52 | 4651751 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase cutout pulled apart at pole 45-C3-4//Single phasing Mansbach Recycling,open a&c @ 0759 restored @ 0815 please close ticket thanks.bt
21622 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-11-17 11:57 | 2013-11-17 13:41 | 1 | 104 | 4045751 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVEND BAD ON XFMR POLE 134B-200 , ONLY 1 CUST. ON THIS POLE. ENTERED MD COD-1 ISO TF 37830134B00200 VER/HFP L3/HFP
21623 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-03-20 01:26 | 2008-03-20 02:18 | 2 | 52 | 59203-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3411801// *** UPSET CUSTOMERSXFR TO RE-FUSERE-FUSED XFR,ALL OK AFTERWARDS VER/PDP IDCC CNT1 XXXX
21624 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-10-14 17:46 | 2009-10-14 19:30 | 1 | 104 | 63373-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE NEUTRAL. IDC XXXX
21625 | Hazard | 3309301 | VICCO | REDFOX | 2022-08-31 20:40 | 2022-08-31 21:32 | 2 | 52 | 4824301 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored at 21:32 //cod 2
21626 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-03-19 11:01 | 2017-03-19 12:45 | 1 | 104 | 4570211 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMMITING FUSE, XMF BANK OFF AT 1233, TIME ON APR AT 1245 CLOSE TICKET. DWEST/ ISO 38830454A27701/ COD 1/ VER/BOW
21627 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-02-04 09:26 | 2015-02-04 11:10 | 1 | 104 | 4989801 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | HAVE C PHASE OF UNDER GROUD PRIMARY OUT . FUSE GOT OLD & BROKE . CLOSED FUSE BACK @ 11:10/ ISO 37830269C00171/ COD 1 VER/HFP L3/HFP
21628 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-01 15:05 | 2012-02-01 15:18 | 8 | 13 | 4313311 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED FUSE TO SAFELY MAKE REPAIRS ON 4312721 VER/KEP IDCC CNT18 XXXX
21629 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-02-06 12:53 | 2020-02-06 14:37 | 1 | 104 | 4370311 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | On pole number 190-124 had a broke cutout,Made my repairs and restored service at 14:37..
21630 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-03-05 19:31 | 2022-03-05 21:15 | 1 | 104 | 4570061 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUSTOMER STATES NO RDG ON METER// removed bad arrester on pole 117-569 lf back in @ 21:15 on pole 117-49
21631 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-03-18 12:44 | 2019-03-18 14:28 | 1 | 104 | 4997131 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout complete
21632 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-12-15 17:06 | 2008-12-15 18:50 | 1 | 104 | 58713-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT 7200.//COD 1// VER/DBM L3/KEP IDC XXXX
21633 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-03-04 15:08 | 2011-03-04 16:00 | 2 | 52 | 66563-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39046036 // POLE 90-191 BAD CUTOUT // COD-2 ISO TF 38830090000191 VER/HFP L3/HFP IDC XXXX
21634 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2022-08-09 19:32 | 2022-08-09 20:53 | 2 | 81 | 4712181 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Service neutral pulled out of a splice at pole 273-B-73 and allowed the hot secondary leads to make contact with the XFMR case ground, burning it apart. Repairs made and power restored at 20:53. XFMR open from 20:30 to 20:53.
21635 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-07-17 17:10 | 2015-07-17 18:02 | 2 | 52 | 4903301 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING XFMR AND CUTOUT/ ISO 38830094A20156/ COD 2///CREW ON SITE///OPENED @ 17:10///CLOSED @ 18:02///TBL TKT COMP// VER/ ADH
21636 | Hazard | 3308001 | JACKSON | S.JACKSON | 2018-09-21 20:02 | 2018-09-21 20:54 | 2 | 52 | 4139901 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout//cod 2
21637 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-03-14 11:11 | 2014-03-14 12:55 | 1 | 104 | 4491971 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HEATED UP AND BURNT NEUTRAL IN TWO AT WEATHERHEAD. IS A 1/0 DROP TO TWO 200 AMP SERVICES. ADDING 2/3 TO PICK ONE OF THEM UP TO LIGHTEN LOAD ON CONNECTIONS. REPLACED 1/0 SVC WITH 4/0 AND RESTORED @ 12:55. SH// VER/DBM
21638 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-09-05 10:16 | 2021-09-05 12:00 | 1 | 104 | 4211051 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | t fuse back in at 12:00
21639 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-07-30 16:30 | 2018-07-30 17:22 | 2 | 52 | 4873191 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole#169-40 which blew line fuse on pole#169-39/// will change cutout//MADE MD TO SHOW TRANS ON LOAD SIDE OF L/F//COD 2//Cutout broke on pole#169-40 which blew line fuse on pole#169-39/// will change cutout// Changed bad cutout and refused line fuse @ 17:22 and restored service
21640 | Hazard | 3309301 | VICCO | REDFOX | 2008-02-13 09:08 | 2008-02-13 10:00 | 2 | 52 | 62225-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309301// NO POWER OUT, BAD C/O ON POLE 326-244, WILL OPEN XFMR TO CHANGE IT OUT. POWER RESTORED//COD 2//ISO37830326B00244// VER/DBM IDC XXXX
21641 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-12-14 19:26 | 2010-12-14 21:10 | 1 | 104 | 50197-1 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION// VER/DBM IDC XXXX
21642 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-02-06 12:16 | 2017-02-06 14:00 | 1 | 104 | 4361361 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | SWITCH, OH | FOUND SOLID BLADE SWITCH BROKE ON POLE 358D-290..WILL MAKE REPAIRS..REPAIRS MADE.. VER/CRB L3/HFP XXXHFP
21643 | Whitesburg | 3312902 | JENKINS | JENKINS | 2008-12-25 17:02 | 2008-12-25 17:28 | 4 | 26 | 63928-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP 4/3 SERVICE DROP HAS BURNED UP I WILL BE REPLACING IT REPLACED SERVICE DROP OPENED TR @ 1702 CCC L3/HFP IDC XXXX
21644 | South Williamson | 3202201 | LOVELY | LOVELY | 2016-02-21 10:41 | 2016-02-21 12:25 | 1 | 104 | 4743261 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 698-D-154//CUTOUT BROKE ON POLE 698-154////REPLACED CUTOUT//RESTORED AT 12:25//COMPLETE//EM VER/CRB
21645 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2021-05-26 17:01 | 2021-05-26 18:45 | 1 | 104 | 4628221 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection at house, repaired
21646 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-05-09 12:38 | 2022-05-09 13:30 | 2 | 52 | 4869371 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hottap had broken replaced H.T. apr at 1330 close ticket
21647 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-06-23 20:16 | 2012-06-23 22:00 | 1 | 104 | 4955861 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BURNT DOWN. REPAIRS COMPLETED AT 2200. NEED BIG BUCKET TO REPLACE CUT OUT & ARRESTER ON REGULAR WORK SCHEDULE. SENT TO LLOYD RAYBURN. CC = 1. VER/SDB
21648 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2016-11-28 08:06 | 2016-11-28 09:50 | 1 | 104 | 4132021 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BAD.CHANGING/ ISO 38830703000055/ COD 1/ VER/BOW
21649 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2019-11-09 09:27 | 2019-11-09 11:11 | 1 | 104 | 4014511 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | neutral burned into in service, several splices ,I replaced service
21650 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-10-13 13:31 | 2011-10-13 15:15 | 1 | 104 | 4974471 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA ///VER/CRB IDC XXXX
21651 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2019-05-22 13:31 | 2019-05-22 15:15 | 1 | 104 | 4315611 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | The bushing on phase B switch to capacitor bank has faulted and blown the fuse.
21652 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2017-06-09 11:31 | 2017-06-09 12:23 | 2 | 52 | 4926551 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE
21653 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-02-03 10:11 | 2010-02-03 11:03 | 2 | 52 | 62547-1 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR BURNED OFF SECONDARY RISER ON XFMR OPENED XFMR AT 10:50 AND CLOSED AT 11:03//VER/CRB IDC XXXX
21654 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-05-12 12:06 | 2013-05-12 13:50 | 1 | 104 | 4107121 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER , BAD CONNECTION AT XFMR, MADE REPAIRS RESTORED POWER AT 13:50 VER/HFP L3/HFP IDC XXXX
21655 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-08-03 20:01 | 2008-08-03 21:45 | 1 | 104 | 64740-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANSF == REPLACED == RESTORED POWER TO A TV BOOSTER ONLY THING ON IT VER/ARN IDCC PN143 XXXX
21656 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2019-07-14 18:01 | 2019-07-14 19:45 | 1 | 104 | 4707681 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE OPEN//37830379C00318
21657 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-11-26 10:31 | 2011-11-26 12:15 | 1 | 104 | 4115551 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY OPEN AT THE TRANSFORMER // REPAIRING//COMPLETE TT// VER/DBM IDC XXXX
21658 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2013-12-15 19:43 | 2013-12-15 20:35 | 2 | 52 | 4164051 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-4126 10T FUSE AND CUTOUT DOOR BAD REPAIRED VER/HFP L3/HFP
21659 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-03-24 10:31 | 2011-03-24 12:15 | 1 | 104 | 58708-1 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR ON ONE HOT LEG OF SERVICE DROP PULLED LOOSE....WILL REPLACE WITH BETTER CONNECTOR....//....REPLACED BAD CONNECTION....JUST ONE CUST AFFECTED....SERVICE LEVEL PART POWER OUTAGE....JRV....03/24/11// VER/DBM IDC XXXX
21660 | Pikeville | 3451201 | BEEFHIDE | BEEFHIDE | 2008-08-06 17:01 | 2008-08-06 18:45 | 1 | 104 | 66134-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED STATION & CIRCUIT NUMBER PLEASE..THANKS. CUTOUT DOOR SERVING PRI. METERING IS BURNED UP. I AM GOING TO CHANGE DOOR. I CHANGED CUTOUT DOOR AT POLE 334-114. COD-1 VER/HFP IDC XXXX
21661 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-06-20 12:56 | 2008-06-20 14:40 | 1 | 104 | 51134-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3401102//SERVE IN CAME LOOSE ON POLE// COMPLETE TT // VER/TOM
21662 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-03-08 10:31 | 2015-03-08 12:15 | 1 | 104 | 4166281 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SQUEEZON ON MAST AND FOUND ONE ON THE POLE ON 480V BANK REPAIRED AND I AM WAITING ON CUST TO CHECK THINGS OUT VER/KEP
21663 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-04-30 11:47 | 2013-04-30 13:31 | 1 | 104 | 4059291 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP SERVE-IN COME APART,WILL REPAIR//////SERVE-IN BAD,DAMAGED DROP.REPLACED W NEW ONE,ALL OK AFTERWARDS// VER/DBM IDC XXXX
21664 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-12-26 20:36 | 2015-12-26 22:20 | 1 | 104 | 4563061 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 25T FUSE ON 783-217 PH B APPEARS TO HAVE BROKEN. RESTORED @ 22:20. SH
21665 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2010-11-11 21:01 | 2010-11-11 21:27 | 4 | 26 | 55026-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 37732015 //--BROKEN FUSE ISO TF 38830092C00244 COD-4 VER/HFP L3/HFP IDCC CCO XXXX
21666 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-09-12 09:31 | 2019-09-12 11:15 | 1 | 104 | 4008531 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required
21667 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-06-09 14:10 | 2018-06-09 15:54 | 1 | 104 | 4572151 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout complete
21668 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-01-17 13:02 | 2010-01-17 13:54 | 2 | 52 | 55449-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPAIRED VER/TOM IDC XXXX
21669 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-08-06 12:33 | 2021-08-06 13:25 | 2 | 52 | 4012191 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout complete
21670 | Whitesburg | 3312901 | JENKINS | KONA | 2022-11-23 14:38 | 2022-11-23 15:30 | 2 | 52 | 4176931 | 104 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Transformer lug burnt up. Made repairs.
21671 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-11-15 21:53 | 2008-11-15 22:45 | 2 | 52 | 65541-1 | 104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR 27305092 NO CREW REQUIRED REPLACING CUTOUT DOOR VER/PDP IDC XXXX
21672 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-01-08 14:33 | 2022-01-08 16:16 | 1 | 103 | 4325301 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken xfmr cutout changing ..
21673 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-10-17 17:49 | 2016-10-17 19:32 | 1 | 103 | 4023611 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP NEUTRAL IN SERV TO ANOTHER HSE HAD BROKEN,LET DROP COME DOWN ONTO CUSTS ROOF.MADE NECESSARY REPAIRS.ALL OK AFTERWARDS.APPARANTLY CUST DIDNT NOTICE ANY PROBLEM THIS COULD HAVE CAUSED. VER/CRB L3/HFP HFPC FEC46
21674 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-03-11 11:17 | 2021-03-11 13:00 | 1 | 103 | 4325981 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burndt into @1124-A-178, only 1 customer having part power. Will be making repairs. Replaced all trans. connections @1300.
21675 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2008-03-08 21:52 | 2008-03-08 23:35 | 1 | 103 | 55546-1 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3004301// BAD SERVE ENDS ON THE HOUSE SIDE, HAVE REPAIRS MADE AND EVERYTHING IS FINE AT THIS LOCATION VER/LDA IDC XXXX
21676 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2022-10-01 23:53 | 2022-10-02 01:36 | 1 | 103 | 4963961 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Squeeze on burnt into made repairs and restored customer
21677 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-04-16 23:30 | 2010-04-17 01:13 | 1 | 103 | 64177-1 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34715350REPLACED CUTOUT AND BRACKET RESTORED POWER AT 0113 CREW 077H01 VER/LDA IDCC TOF2212 ASSUMED TIME OFF XXXX
21678 | Hazard | 3309302 | VICCO | JEFF | 2008-08-26 16:47 | 2008-08-26 18:30 | 1 | 103 | 55222-1 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 347-395 WE HAVE BAD C/O CAUGHT POLE ON FIRE//3309302347-395 WE HAVE BAD C/O CAUGHT POLE ON FIRE./// REPLACED BRACKET AND C/O, POWER BACK ON//VER/CRB IDC XXXX
21679 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2021-09-04 18:41 | 2021-09-04 20:24 | 1 | 103 | 4210261 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTIONS@XFR ABT 150FT FRM HOUSE UP ON HILL///////REPLACED THEM,ALL OK AFTERWARDS
21680 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-12-10 22:12 | 2018-12-10 23:55 | 1 | 103 | 4549771 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | serve end was burnt up..repaired connection..
21681 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-03-01 16:05 | 2018-03-01 17:48 | 1 | 103 | 4894291 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | called customer number is no good span open wire was wraped with neutral caused CSP xfmr to open
21682 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2013-11-19 10:04 | 2013-11-19 11:47 | 1 | 103 | 4056031 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE BURNT OPEN ON HOUSE REPAIRED VER/CRB
21683 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-05-15 16:22 | 2016-05-15 18:05 | 1 | 103 | 4220711 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT .FUSE OLD & BROKE . REFUSED XFMR POWER BACK ON @ 18:05 . VER/CRB
21684 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-10-23 13:47 | 2012-10-23 15:30 | 1 | 103 | 4166291 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN//// FUSE BROKE, REFUSED, POWER RESTORED.//COD 1// VER/DBM IDC XXXX
21685 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-12-12 09:17 | 2011-12-12 11:00 | 1 | 103 | 4170621 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | OUTAGE DUE TO BAD CURRENT LIMIT FUSE I HAVE REPAIRS MADE EVERYTHING OK//COD 1//NO WIRE DOWN PER SERVICER// VER/DBM IDC XXXX
21686 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-11-28 12:26 | 2018-11-28 14:09 | 1 | 103 | 4487451 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Busted cutout on pole 24-D3-130, will be changing. Got changed out and closed back in @1409.
21687 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-02-11 20:07 | 2011-02-11 21:50 | 1 | 103 | 56308-1 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSF POLE REPAIRED == POWER OK//VER/CRB IDC XXXX
21688 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-03-02 16:02 | 2014-03-02 17:45 | 1 | 103 | 4444291 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT . POWER BACK ON @ 17:45 , REPLACED CUTOUT.. VER/CRB
21689 | Whitesburg | 3401301 | FLEMING | NEON | 2018-12-18 13:41 | 2018-12-18 15:24 | 1 | 103 | 4577521 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service outage, service drop burnt into mid span , restored power at 15:24 only one customer affected.. L3/HFP
21690 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-07-06 17:42 | 2019-07-06 19:25 | 1 | 103 | 4668681 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Broken neutral in service drop, transformer on 1099-a4-57 open from 19:20 to 19:25, repairs made, power restored
21691 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-04-29 10:38 | 2015-04-29 12:21 | 1 | 103 | 4375431 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHGING/ ISO 38830834C00194/ COD 1/ VER/BOW
21692 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-06-20 12:17 | 2015-06-20 14:00 | 1 | 103 | 4616681 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S08 BAD CONN. ON SEC./CLOSED 1400// VER/ ADH
21693 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-09-05 20:12 | 2009-09-05 21:55 | 1 | 103 | 50380-1 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD ARRESTOR AND CHANGED CUTOUT ALSO // VER/LDA IDC XXXX
21694 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-11-22 17:34 | 2015-11-22 19:17 | 1 | 103 | 4478701 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED/RED SERVEND MELTED OUT . ONLY 1 CUST. WITH PART POWER ./ ISO 37840384000001/ COD 1/ VER/BOW
21695 | Pikeville | 3402002 | KEYSER | STONECOAL | 2018-01-15 12:00 | 2018-01-15 13:43 | 1 | 103 | 4748921 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad c/o on trans. pole 1129-A4-451, changed out @1343.
21696 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-10-15 20:17 | 2017-10-15 22:00 | 1 | 103 | 4459691 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 38831065D10126. MAKING REPAIRS.CHANGE CUTOUT VER/AWD L3/HFP XXXHFP
21697 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2018-06-16 14:51 | 2018-06-16 16:34 | 1 | 103 | 4608361 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | the service burned down #2-4con . we put wire back up. this needs to be sent to technicians to work a job to set a pole in this service
21698 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-06-16 18:17 | 2021-06-16 20:00 | 1 | 103 | 4760851 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
21699 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2013-04-18 11:50 | 2013-04-18 13:33 | 1 | 103 | 4021841 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT..OLD FUSE LINK JUST PULLED APART.WILL RE-FUSE.//.RE-FUSED ..POWER ON.JRV.04/18/13 //VER/GAH IDC XXXX
21700 | Hazard | 3310502 | HADDIX | CANOE | 2009-04-29 10:36 | 2009-04-29 12:19 | 1 | 103 | 57460-1 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3310502//VER/CRB IDC XXXX AJBC FEC57
21701 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-11-06 08:07 | 2011-11-06 09:50 | 1 | 103 | 4054791 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SERVICE// VER/DBM IDC XXXX
21702 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-02-01 20:42 | 2011-02-01 22:25 | 1 | 103 | 52913-1 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN SERVICE AT XFMR POLE 496-46... MADE REPAIRS RESTORED POWER AT 22:25, ONLY ONE CUSTOMER AFFECTED COD-1 ISO TF 37830496000046 VER/HFP L3/HFP IDC XXXX
21703 | Hazard | 3310502 | HADDIX | CANOE | 2016-02-15 14:07 | 2016-02-15 15:50 | 1 | 103 | 4697581 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN. OVERHEAD @ WEATHER HEAD BAD . REPLACED . VER/CRB L/3 CRB
21704 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2019-02-25 10:52 | 2019-02-25 12:35 | 1 | 103 | 4911121 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral was broke in secondary I made repairs voltage is good
21705 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-01-12 18:42 | 2012-01-12 20:25 | 1 | 103 | 4253051 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERV-END (RED TO RED) BURNT UP.. PART POWER RESTORED 20:25 //VER/CRB IDC XXXX
21706 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-02-27 11:37 | 2015-02-27 13:20 | 1 | 103 | 4085591 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL BURNT INTO IN SERVICE DROP @ SPLICE //// WILL REPLACE/// REPLACED BAD SPLICES IN SERVICE DROP@ POLE37820126000071/// RESTORED SERVICE @ 13:20/// ONLY 1 CUSTOMER AFFECTED VER/CRB
21707 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-11-17 14:27 | 2019-11-17 16:10 | 1 | 103 | 4042441 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfmr cut out on 1048-239/ xfmr back on @ 1610/ please close ticket/MLH
21708 | South Williamson | 3411401 | DEWEY | INEZ | 2008-01-28 11:01 | 2008-01-28 12:44 | 1 | 103 | 60403-1 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3411401// TRANSF FUSE BROKE COD-1 VER/KEP IDC XXXX
21709 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-02-26 23:42 | 2014-02-27 01:25 | 1 | 103 | 4436831 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SPLICE IN ONE LEG OF THE SERVICE DROP AT THE TRANSFORMER POLE. VER/KEP
21710 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-01-29 01:02 | 2012-01-29 02:45 | 1 | 103 | 4301321 | 103 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD, REPLACED CONN. APR AT 0245 CLOSE TICKET //VER/GAH IDC XXXX
21711 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2016-05-03 13:34 | 2016-05-03 15:17 | 1 | 103 | 4170071 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT .ON POLE# 954-928 WILL REPLACE.CUTOUT IS REPLACED &POWER RESTORED/ ISO 38830954B40928/ COD 1/ VER/BOW
21712 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-11-14 16:37 | 2021-11-14 18:20 | 1 | 103 | 4091161 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout was bad here, was able to access and replace. Restored @ 18:20
21713 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-07-04 11:41 | 2021-07-04 13:24 | 1 | 103 | 4855771 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | xfmr fuse blown, case ground is off xfmr causing fuse to blow
21714 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-06-26 06:47 | 2014-06-26 08:30 | 1 | 103 | 4157491 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED FUSE NO CREW VER/CRB
21715 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-07-25 17:47 | 2009-07-25 19:30 | 1 | 103 | 58036-1 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 1// VER/DBM IDC XXXX
21716 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-01-04 21:50 | 2019-01-04 23:33 | 1 | 103 | 4629661 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on pole 119-143.non-truck access..will make repairs..restored
21717 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-05-20 19:08 | 2014-05-20 20:51 | 1 | 103 | 4727981 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACING BAD CONNECTIONS VER/SEF
21718 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2022-10-01 09:02 | 2022-10-01 10:45 | 1 | 103 | 4954861 | 103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 10:45. sh
21719 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-08-16 15:36 | 2011-08-16 17:18 | 1 | 102 | 4717931 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY WIRE CAME OUT OF BUSHING == LUG BROKE REPAIRED LUG == POWER OK AND REPLACED POLE GROUND AND GROUND ROD//VER/CRB IDC XXXX
21720 | Whitesburg | 3312901 | JENKINS | KONA | 2020-12-28 12:48 | 2020-12-28 14:30 | 1 | 102 | 4830731 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad connection on conduit mast at house. repaired and restored power at 1430
21721 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-04-22 07:56 | 2014-04-22 08:30 | 3 | 34 | 4623901 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-258 BAD CUTOUT DOOR REPAIRED//COD 3// VER/DBM
21722 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2019-05-28 16:51 | 2019-05-28 18:33 | 1 | 102 | 4356461 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on 992D58.replaced cutout.restored power at 18:33.
21723 | Pikeville | 3421001 | BREAKS | CITY | 2016-01-05 08:53 | 2016-01-05 10:35 | 1 | 102 | 4586091 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE FAILED AT THE POLE, BURNING THE NEUTRAL APART DUE TO ALL 3 CONDUCTORS BEING TAPED TOGETHER.//PEGGY POSSIBLE CLAIM//SENT TO CLAIMS// VER/CRB
21724 | South Williamson | 3200301 | BELFRY | BELFRY | 2020-11-11 20:16 | 2020-11-11 21:58 | 1 | 102 | 4665471 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad splice at weatherhead will be making repairs// opened 480 bank to make repairs, off at 21:10 on at 21:58. LR- The service went down at 20:16 on 11/11/20
21725 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-11-20 20:42 | 2019-11-20 21:33 | 2 | 51 | 4052551 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @47-B-13, checking. Fuse had melted, refused @2133./ ISO 37830047B00013/ COD 2
21726 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-05-05 11:54 | 2016-05-05 12:45 | 2 | 51 | 4177541 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PLE 140-186 6T TRANS FUSE BROKE REPLACED FUSE VER/AWD
21727 | Cannonsburg | 3001401 | LOUISA | CITY | 2018-06-27 09:23 | 2018-06-27 11:05 | 1 | 102 | 4676951 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout on 38830454A10221, apr at 1105 close ticket
21728 | Pikeville | 3409502 | BURDINE | LEVISA | 2018-06-09 16:12 | 2018-06-09 17:54 | 1 | 102 | 4572581 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on pole 358-411.will have to lift hot tap on pole 358-406 to make repairs safely..//MADE MD TO SHOW MIS-MAPPED CUST PREMISE//COD 1//
21729 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-07-08 11:53 | 2015-07-08 13:35 | 1 | 102 | 4745491 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 13:35.. VER/CRB
21730 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2008-10-30 09:24 | 2008-10-30 11:06 | 1 | 102 | 60799-1 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP PARTIAL POWER LOOSE CONNECTION...RESQUEEZED CONNECTION...BB IDC XXXX
21731 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-04-03 13:00 | 2010-04-03 14:42 | 1 | 102 | 57932-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED ON SERVIVE AND MELTED SECONDARY, REPAIRED AND REPLACED DROP VER/KEP IDC XXXX
21732 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-02-13 17:54 | 2011-02-13 18:45 | 2 | 51 | 56601-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BELIEVE ARRESTOR HAS BROKEN DOWN,OPENED XFR TO REPAIR//////SURGE ARRESTOR HAD BROKEN DOWN,REMD FROM XFR RISER TAP COD-2 93-29 VER/KEP IDCC TOF1713 XXXX
21733 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-01-06 14:48 | 2019-01-06 16:30 | 1 | 102 | 4635251 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A
21734 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-07-12 11:48 | 2022-07-12 13:30 | 1 | 102 | 4465801 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke in secondary.// Made repairs and restored @ 13:30.//Only one customer affected
21735 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2020-12-28 14:38 | 2020-12-28 15:12 | 3 | 34 | 4831281 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | secondary splice into ;;made repairs and restored power at 15:12
21736 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-04-20 16:38 | 2018-04-20 18:20 | 1 | 102 | 4259561 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | customerhad partial power.replaced secondary connection at weather head.customer not home./ ISO 38820818C00140/ COD 1
21737 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2011-01-03 10:53 | 2011-01-03 12:35 | 1 | 102 | 58179-1 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON 3 PHASE PUMP SERVICE RESTORED 1235 VER/KEP L3/KEP IDC XXXX
21738 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-10-25 09:40 | 2022-10-25 11:22 | 1 | 102 | 4062541 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired connectionsand service
21739 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-06-23 15:59 | 2012-06-23 16:50 | 2 | 51 | 4955351 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | UG PADMOUNT XFMR FUSE MELTED OUT. MAY HAVE BEEN A WEAK FUSE THAT MELTED OUT UNDER LOAD. ADVISED CUSTOMER TO CALL IF IT GOES BACK OUT BUT IT HAS BEEN ON FOR OVER 10 MINUTES NOW. SH COD-2 ISO TF 38830784C21518 VER/HFP L3/HFP
21740 | Hazard | 3309302 | VICCO | JEFF | 2010-08-23 12:39 | 2010-08-23 13:30 | 2 | 51 | 59595-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER WENT BAD == REFUSED TRANSF == DIDNT REPLACE ARRRESTER == POWER OK COD-2 VER/HFP L3/HFP IDC XXXX
21741 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-12-19 10:07 | 2014-12-19 11:49 | 1 | 102 | 4870431 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING BROKEN CUTOUT/ ISO 38830182A00101/ COD 1/ VER/BOW
21742 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2015-11-18 17:18 | 2015-11-18 19:00 | 1 | 102 | 4464641 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT/ ISO 38830249000196/ COD 1/ VER/BOW
21743 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-03-15 13:38 | 2012-03-15 15:20 | 1 | 102 | 4583151 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD CUTOUT//COD 1// VER/DBM IDC XXXX
21744 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-01-05 12:53 | 2021-01-05 14:35 | 1 | 102 | 4849761 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 794-a-96//repairs made//restored at 14:35//complete//em
21745 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-06-20 20:25 | 2015-06-20 22:07 | 1 | 102 | 4623521 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED 40FT, 4/3 SERVICE WITH 40 FT. 2/3 SERVICE VER/HFP L3/HFP
21746 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-08-05 18:57 | 2021-08-05 20:39 | 1 | 102 | 4009841 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken c/o--in at 20:39--allgood-ds080521
21747 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-05-31 20:03 | 2012-05-31 21:45 | 1 | 102 | 4856581 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SMALL LIMB GOT ON PRI. COND. AT POLE 166-159 AND BLEW LINE FUSE ON 166-109. I AM GOING TO REMOVE LIMB AND REFUSE LINE FUSE.TRANS. CUTOUT IS BROKEN ON POLE 166-159 AND BLEW LINE FUSE ON POLE 166-109. I AM GOING TO CHANGE CUTOUT. // COD-1 ISO LF 37830166000109 VER/HFP L3/HFP IDC XXXX
21748 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-02-15 10:58 | 2016-02-15 12:40 | 1 | 102 | 4697151 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 165-261.WILL CHANGE OUT/////CHANGED OUT CUTOUT AND CLOSED BACK IN @ 12:40.. VER/CRB L/3 CRB
21749 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-06-09 19:08 | 2010-06-09 20:50 | 1 | 102 | 59465-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT. COD-1 VER/HFP L3/HFP
21750 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-04-28 10:43 | 2019-04-28 12:25 | 1 | 102 | 4181311 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open @ xfm/// Replaced bad connection and restored service @ 12:25 L3/HFP
21751 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-12-04 15:15 | 2020-12-04 16:57 | 1 | 102 | 4745281 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | no crew required repaired service
21752 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-06-08 20:43 | 2022-06-08 22:25 | 1 | 102 | 4041911 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed and burnt service neutral in two. Replaced #4 service with #2 and restored @ 22:25. sh
21753 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-01-11 17:44 | 2008-01-11 18:18 | 3 | 34 | 56073-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3409302//POLE #905-43 ROTTED OFF. WILL PULL BACK UP STRAIGHT FOR THE WEEKEND. OPENED LINE FUSE ON POLE 905-42 TO MAKE REPAIRS.OFF AT 17:44. ON AT 18:18//ISO 38830905000042//SENT REPORT TO MAPPING ON MISSING FUSE//COD 3// VER/DBM IDC XXXX
21754 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-01-29 16:06 | 2008-01-29 16:57 | 2 | 51 | 60726-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3400301// LOOKS LIKE TRANSFORMER FUSE BROKE. 6TFUSE OUT//COD 2// VER/DBM IDC XXXX
21755 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-03-06 12:31 | 2009-03-06 13:22 | 2 | 51 | 55687-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411802 - XFMR BAD CHANGED OUT TO 25 KVA //VER/GAH IDC XXXX
21756 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-05-19 15:08 | 2019-05-19 16:50 | 1 | 102 | 4299031 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 19-4, broken 12 kv c/o.
21757 | Hazard | 3309003 | JEFF | VIPER | 2015-03-06 14:43 | 2015-03-06 16:25 | 1 | 102 | 4147981 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE === REFUSED TRANSF POWER OK VER/SEF
21758 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-06-09 13:53 | 2013-06-09 15:35 | 1 | 102 | 4242111 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON 4/3 DROP ON 200A SERVICE BURNT OFF REPLACED 60 FT. 4/3 SERVICE WITH 60FT. 2/3 SERVICE DROP VER/KEP
21759 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2014-03-14 22:08 | 2014-03-14 23:50 | 1 | 102 | 4494101 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF THE SERVICE AT THE TRANSFORMER. ONLY ONE CUSTOMER OUT. VER/ARN
21760 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-06-14 22:23 | 2013-06-15 00:05 | 1 | 102 | 4339511 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE PHASE WIRES AT THE WEATHERHEAD. I MADE REPAIRS. VER/PDP IDCC CNT3 XXXX
21761 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2008-01-29 22:11 | 2008-01-29 22:45 | 3 | 34 | 60816-1 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 3002106//PART POWER// 1 FUSE OUT IN BANK/BROKEN FUSE LINK//COD 3//ISO 38830021B435419// VER/DBM IDC XXXX
21762 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-07-23 15:18 | 2010-07-23 17:00 | 1 | 102 | 56046-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP...OLD TYPE CUTOUT....WILL REPLACE WITH NEW CUTOUT....//....REPLACED CUTOUT...POWER ON....JRV....07/23/10 VER/KEP L3/KEP IDC XXXX
21763 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-02-20 15:06 | 2011-02-20 16:48 | 1 | 102 | 59493-1 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT HSE//VER/CRB IDC XXXX
21764 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-06-11 07:58 | 2009-06-11 09:40 | 1 | 102 | 57142-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10T FUSELINK BROKE. POWER OK. IDC XXXX
21765 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-11-04 10:19 | 2011-11-04 11:10 | 2 | 51 | 4050451 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 OF 3 FUSES OUT AT 3P XFR BANK,WILL RE-FUSE//////////FUSE HAD ROTTED INTO,REPLACED,RE-FUSED AND RESTORED//COD 2// VER/DBM IDCC PN5 XXXX
21766 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-02-14 19:30 | 2012-02-14 21:12 | 1 | 102 | 4348811 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE CUTOUT BAD SET POLE ON FIRE. ///// PUT FIRE OUT, CHANGED CUTOUT, POWER RESTORED. VER/HFP L3/HFP IDCC TOF1830 ESTIMATED TIME OFF XXXX
21767 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-07-29 20:08 | 2009-07-29 21:50 | 1 | 102 | 66562-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308001//CUTOUT ON POLE 1108-645 ON FIRE//JIM MULLINS OPENED FUSE ON POLE 1108-302 TO ISOLATE//NEED 1 MAN, A 7200 CUTOUT AND "T" BRACKETT//COD 1//STS WR# 30979918// C/O CHANGED, POWER RESTORED//COD 1// VER/DBM IDC XXXX
21768 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2019-04-29 08:14 | 2019-04-29 09:56 | 1 | 102 | 4183501 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Replaced 5ft of secondary. Connection at the entrance cable failed. Customer has a 100 amp meterbase with a 200 amp switchbox. Im not sure if the connections failed due to load, because it has been that way for a long time. L3/HFP
21769 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-07-30 09:48 | 2008-07-30 11:30 | 1 | 102 | 62044-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308502//RISER CAME LOOSE FROM HOT LINE CLAMP. REPLACED HOT LINE CLAMP, POWER RESTORED IDC XXXX
21770 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-04-14 16:24 | 2021-04-14 18:06 | 1 | 102 | 4451671 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS////////FOUND A BAD SQUEEZON CONNECTION AT THE XFR//////REPLACED BOTH SEC CONNECTIONS,ALL SEEMED OK AFTERWARDS,POWER WAS COMING&GOING AT TIMES DUE TO THIS BAD CONNECTION
21771 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-04-04 23:38 | 2015-04-05 01:20 | 1 | 102 | 4276471 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE DROP ONLY CUSTOMER AFFECTED, MADE REPAIRS RESTORED POWER AT 01:20. VER/ARN
21772 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-01-18 16:13 | 2018-01-18 17:55 | 1 | 102 | 4755881 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | service drop neutral into replaced service
21773 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-09-24 14:08 | 2010-09-24 15:50 | 1 | 102 | 53211-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#37036455 BAD X-FRMER CREW TO REPLACE.....PLEASE SEND TO TIM SMITH CREW TO CHANGE XFMER....XFMR IS LOCATED ON VISTA DR. AT THE GATE TO DR. ACE CHANEYS HSE... FUSE IS STILL IN BUT NO VOLTAGE OUTPUT. P.HICKS RELEASED BY CREW 077H01 VER/KEP L3/KEP IDC XXXX
21774 | Hazard | 3303902 | LESLIE | WOOTON | 2021-07-07 21:38 | 2021-07-07 23:20 | 1 | 102 | 4869981 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | loose guy wire made contact with xfmr riser, tightened guy and refused xfmr, power restored/ ISO 37830487000032/ COD 1
21775 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-12-12 18:47 | 2010-12-12 19:38 | 2 | 51 | 65692-1 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BLOWN ON TRNSFORMER. TRANSFORMER ON POLE 1084-43 FUSE PULL INTO, THIS IS TWICE THAT THIS HAS HAPPEN, (BROKE A WEILD BETWEEN CAP & FUSE CORD) COD-2 (1 ON TR PLUS THIS CUST) ENTERED MD NOT POLE 1083-189 VER/HFP L3/HFP IDC XXXX
21776 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-01-20 17:44 | 2015-01-20 18:35 | 2 | 51 | 4948021 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED CUTOUT APR AT 1835 CLOSE TICKET/ ISO 38830501000339/ COD 2/ VER/BOW
21777 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2019-01-04 13:52 | 2019-01-04 15:03 | 2 | 71 | 4628301 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Service drop is made up on a mid span open wire. Connection on one leg of the service drop had burned down one of the open wire secondary. Repairs are made, power restored. Send to Bill Johnson to have the open wire removed and a secondary pole set. I have made several trips here, and the #4 copper open wire is burned up in several places. Part power till I opened the transformer at 14:32, closed in at 15:03. Two customers were off.
21778 | Whitesburg | 3308402 | BECKHAM | CARR CREEK | 2008-12-14 11:18 | 2008-12-14 13:00 | 1 | 102 | 58188-1 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308402//WIRE DOWN ACROSS ROAD AT THIS LOCATION VER/PDP L3/KEP IDC XXXX
21779 | Hazard | 3309302 | VICCO | JEFF | 2010-02-24 11:45 | 2010-02-24 13:27 | 1 | 102 | 60562-1 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE CUSTOMER WAS ALL THAT WAS AFFECTED. SERV-IN MELTED, REPLACED WITH SQUEEZ-ONS, POWER RESTORED. IDC XXXX
21780 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-01-07 15:20 | 2014-01-07 17:02 | 1 | 102 | 4253441 | 102 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVEND CONNECTION POLE 117-150 REPAIR MADE EVERYTHING OK VER/HFP L3/HFP IDCC CNT5 FEC57 XXXX
21781 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-03-31 12:40 | 2020-03-31 14:22 | 1 | 102 | 4548821 | 102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, power restored
21782 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-09-04 08:40 | 2019-09-04 10:21 | 1 | 101 | 4977971 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad insulink. replaced. pls close. tre
21783 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-03-18 21:19 | 2011-03-18 23:00 | 1 | 101 | 55676-1 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN IN TWO. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. COD-1 ISO TF 38831104000041 VER/HFP L3/HFP IDC XXXX
21784 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-04-18 16:08 | 2015-04-18 17:49 | 1 | 101 | 4332721 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE // POWER RESTORED @ 17:49// VER/ ADH
21785 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-08-06 14:23 | 2009-08-06 16:04 | 1 | 101 | 54661-1 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP NETURAL WAS BROKE IN SECONDARY. IT HAD PULLED OUT OF SLEEVE. WIRE WAS ORIGINALLY BROKE DUE TO COUSTOMER CUTTING TREE. L3/HFP IDC XXXX
21786 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-01-09 20:06 | 2008-01-09 21:47 | 1 | 101 | 55363-1 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTIONS AT WEATHERHEAD BURNT CUSTOMERS DROP DOWN. REPAIRED. SH IDC XXXX
21787 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-05-27 16:49 | 2019-05-27 18:30 | 1 | 101 | 4350711 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connections
21788 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-01-02 13:44 | 2019-01-02 15:25 | 1 | 101 | 4623301 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | i think current limit fuse is bad on the high side of the transformer will be checking. had bad arrester and current limit fuse made repairs everything ok
21789 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-10-04 16:53 | 2014-10-04 18:34 | 1 | 101 | 4553571 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN // WILL REFUSE// BAD C/L FUSE // POWER RESTORED VER/CRB
21790 | South Williamson | 3411401 | DEWEY | INEZ | 2014-04-19 10:34 | 2014-04-19 12:15 | 1 | 101 | 4618241 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SERVE END  MAKING REPAIRS  REPAIRS COMPLETE, CUSTOMER SAID EVERYTHING APPEARS BACK TO NORMAL VER/CRB
21791 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-03-16 18:01 | 2016-03-16 19:42 | 1 | 101 | 4857011 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | THREE NEW CONNECTIONS @ ENTRANCE/ ISO 38830070B43504/ COD 1/ VER/BOW
21792 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-02-19 03:48 | 2022-02-19 05:29 | 1 | 101 | 4514931 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse appears to have broke. Restored @ 5:29. sh
21793 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-07-02 08:19 | 2021-07-02 10:00 | 1 | 101 | 4846171 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
21794 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-07-11 15:37 | 2012-07-11 17:18 | 1 | 101 | 4687561 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1.6T FUSE OUT DUE TO BAD CURRENT LIMITE FUSE WILL BE MAKING REPAIRS. I HAVE REPAIRS MAID FUSED UP EVERYTHING OK
21795 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2013-07-18 07:04 | 2013-07-18 08:45 | 1 | 101 | 4546051 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 91-17 BAD HOT TAP VER/SEF IDC XXXX
21796 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-03-01 14:34 | 2013-03-01 16:15 | 1 | 101 | 4865331 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED SERVLINK BAD. COD-1 ISO TF 37830134B00140 VER/HFP L3/HFP IDC XXXX
21797 | South Williamson | 3411401 | DEWEY | INEZ | 2008-02-28 19:25 | 2008-02-28 21:06 | 1 | 101 | 51338-1 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411401// REWORKED CONN. ON TRANSF POLE AND INSIDE METER BASE// VER/DBM IDC XXXX
21798 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-08-24 09:19 | 2020-08-24 11:00 | 1 | 101 | 4363301 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Tie wire was broken on the neutral spool at pole 387-134 and broke all of the ground connections to a XFMR. Only one customer off of this XFMR and no one was home so I opened the XFMR and made repairs. Cannot check voltage at the meter base, customer has 2 bull dogs at this location.
21799 | Hazard | 3310502 | HADDIX | CANOE | 2021-03-26 08:04 | 2021-03-26 09:45 | 1 | 101 | 4377591 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | red to red burnt out. made repaires
21800 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2018-07-07 18:59 | 2018-07-07 20:40 | 1 | 101 | 4749581 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed in 1/0 service to resturaunt. Burnt one hot leg and service neutral in two. Made repairs and restored @ 20:40. sh
21801 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-09-25 07:31 | 2019-09-25 09:12 | 1 | 101 | 4055691 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burndt into @95-86, will have to open this trans. to make repairs, will keep track of times. Opened @0903, made repairs and closed back in @0912.
21802 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2019-05-04 07:01 | 2019-05-04 08:42 | 1 | 101 | 4216041 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer/ sounds like service drop is down to a barn (green/cream colored Barn),,,,repaired cutout complete/ ISO 38830350000116/ COD 1
21803 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2015-10-16 11:22 | 2015-10-16 13:03 | 1 | 101 | 4353631 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR F IS OUT,WILL RE-FUSE/////////RE-FUSED AND RESTORED,FUSE HAD ROTTED INTO VER/CRB
21804 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-05-04 15:54 | 2019-05-04 17:35 | 1 | 101 | 4218161 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced c/o and arr.
21805 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-03-17 19:53 | 2015-03-17 21:34 | 1 | 101 | 4205401 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION @ ENTRANCE VER/SEF
21806 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2021-10-12 15:49 | 2021-10-12 17:30 | 1 | 101 | 4344391 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required fuse door
21807 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-01-05 20:04 | 2012-01-05 21:45 | 1 | 101 | 4236301 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A SPLICE FAILED AT THE SERVICE POLE, BURNING THE SERVICE DROP DOWN. I REPLACED THE SERVICE DROP. VER/HFP L3/HFP IDC XXXX
21808 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-10-09 08:04 | 2020-10-09 09:45 | 1 | 101 | 4538761 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired connection on secondary
21809 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2018-12-10 18:42 | 2018-12-10 20:23 | 1 | 101 | 4548501 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout
21810 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-08-14 09:11 | 2014-08-14 10:52 | 1 | 101 | 4368471 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 469-25, REPLACED CUTOUT RESTORED POWER AT 10:52.// COD 1// VER/ ADH
21811 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-06-06 06:44 | 2009-06-06 08:25 | 1 | 101 | 50242-1 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE IS BURNED APART. I AM GOING TO REPLACE CUTOUT VER/LDA IDC XXXX
21812 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-06-08 09:59 | 2017-06-08 11:40 | 1 | 101 | 4922861 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHER HEAD,, REPLACED CONN, COMPLETE38830182B30250 VER/AWD
21813 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2013-10-16 13:49 | 2013-10-16 15:30 | 1 | 101 | 4940611 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAD 4/3 SERVICE DROP THAT HAD MANY SPLICE IN IT, I I REMOVED IT AND INSTALLED 2/3 SERVICE DROP, PROBLEM IS SOLVE AT THIS LOC VER/CRB L/3 CRB
21814 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-03-28 22:51 | 2010-03-29 00:32 | 1 | 101 | 55383-1 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BARREL CONNECTER AT XFMR WAS BAD, PART POWER, REPAIRED VER/LDA IDC XXXX
21815 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-12-19 18:29 | 2011-12-19 20:10 | 1 | 101 | 4189731 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END HAS FROZEN OUT ON ONE HOT LEG AT ENTRANCE. I AM GOING TO RESQUEEZE CONNECTION. I RESQUEEZED CONNECTION. //VER/CRB IDC XXXX
21816 | Hazard | 3308002 | JACKSON | PANBOWL | 2022-05-10 18:19 | 2022-05-10 20:00 | 1 | 101 | 4874841 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Ligting arrester went bad blowing transformer power send to tech. to replace lighting arr.
21817 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-08-09 03:04 | 2016-08-09 04:45 | 1 | 101 | 4752121 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | HOMER JUSTICE WAS OVER THERE EARLIER AND REMOVED SOME VINES.HOMER JUSTICE WAS OVER THERE EARLIER AND REMOVED SOME VINES BAD CURRENT LIMITING FUSE VER/ARN
21818 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-06-09 17:34 | 2014-06-09 19:15 | 1 | 101 | 4999861 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK. VER/CRB
21819 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-09-15 08:40 | 2020-09-15 10:21 | 1 | 101 | 4464501 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | notified customers/ Opened XFMR fuse/ Crew replacing underground conductor/ ISO 38831052D00262/ COD 1/ OFF 8:40 ; ON 10:21
21820 | Hazard | 3307301 | BULAN | ARY-HEINE | 2018-03-04 12:40 | 2018-03-04 14:21 | 1 | 101 | 4960781 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad serve end connection in midspan,made repaires
21821 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-07-10 13:17 | 2012-07-10 14:58 | 1 | 101 | 4669841 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED CONNECTOR AT HSE,AND WEATHER HEAD POWER RESTORED KWB IDC XXXX
21822 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-06-16 19:56 | 2011-06-16 21:37 | 1 | 101 | 4329771 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE CKING TROUBLE//CUST HAS BURNT APPLIANCES//VER/CRB
21823 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2018-06-25 11:24 | 2018-06-25 13:05 | 1 | 101 | 4662071 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ser drop neu broke cust gr. wire loose on gr. rod
21824 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-03-18 08:46 | 2008-03-18 10:27 | 1 | 101 | 58103-1 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3409003// SECONDARY CONNECTIONS BURNT OPEN. RE-SQUEEZED SECONDARY CONNECTIONS. SH//VER/CRB IDC XXXX
21825 | Hazard | 3309301 | VICCO | REDFOX | 2014-06-09 15:02 | 2014-06-09 16:43 | 1 | 101 | 4999271 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 300-140, WILL NEED 15 KVA, 19.9 KV, BAD MANUEL, WILL ALSO NEED 4-WHEEL DR TRUCK. CUST OK WITH WAITING UNTILL TOMORROW. OPS # 038798981 RELEASED BY CREW 077S02 VER/HFP L3/HFP
21826 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2018-05-02 13:37 | 2018-05-02 15:18 | 1 | 101 | 4298431 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xform cutout broke ,replace power restored
21827 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-01-21 13:54 | 2011-01-21 15:35 | 1 | 101 | 63384-1 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38530891 // SERVE-END FROZE OUT...REPLACED AND EVERYTHING OK VER/HFP L3/HFP IDC XXXX
21828 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-08-12 18:09 | 2011-08-12 19:50 | 1 | 101 | 4700941 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTOR ON CONNECTOR AT XFMR, FIXED, POWER RESTORED. VER/HFP L3/HFP IDC XXXX
21829 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-07-10 08:49 | 2022-07-10 10:30 | 1 | 101 | 4451341 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew requird replacced cutout
21830 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-10-28 22:12 | 2012-10-28 23:53 | 1 | 101 | 4179901 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE # 1139-C-175 CAUSING POLE FIRE. OPENED LINE AT POLE # 1115-C-8 AT 23:13. CLOSED BACK IN AT 23:53. RECLOSER OUTAGE ON ORDER 4180041. CC 1. VER/SDB IDC XXXX
21831 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-04-21 20:49 | 2008-04-21 22:30 | 1 | 101 | 53174-1 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308502 SPLICE WENT BAD ON CUST POLE == REPAIRED ==ON HOT LEG == VER/GAH IDC XXXX
21832 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-07-06 19:56 | 2020-07-06 21:37 | 1 | 101 | 4119881 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | New home sevice was just installed today. no one living here customer said it would be fine to replace txmf tommorrow. Bad 25kva. 7200. Please send copy to Vernon mullins Released by crew 078S11
21833 | Hazard | 3301101 | CHAVIES | CHAVIES | 2009-08-22 09:34 | 2009-08-22 11:15 | 1 | 101 | 60487-1 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURNT UP ON SEC VER/KEP L3/KEP IDC XXXX
21834 | Paintsville | 3410602 | E.PRESTON | LANCER | 2022-06-27 20:29 | 2022-06-27 22:10 | 1 | 101 | 4337201 | 101 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke in service drop.//Repairs made 22:10
21835 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2022-11-10 22:07 | 2022-11-10 23:48 | 1 | 101 | 4123841 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
21836 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-05-16 19:44 | 2009-05-16 21:25 | 1 | 101 | 59321-1 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP REPLACED BAD CUTOUT. L3/HFP IDC XXXX
21837 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2014-03-10 12:34 | 2014-03-10 14:15 | 1 | 101 | 4464901 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 352-338, REPLACED CUTOUT RESTORED POWER AT 14:15 ONLY ONE CUSTOMER AFFECTED//COD 1//ISO// VER/DBM
21838 | Pikeville | 3402002 | KEYSER | STONECOAL | 2015-07-30 18:31 | 2015-07-30 20:12 | 1 | 101 | 4961661 | 101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE//////////RE-FUSED AND RESTORED,FUSE APPEARED TO HAVE ROTTED INTO ALTHO THERE LIMBS ALL AROUND POLE AND XFR/ ISO 38821129B30459/ COD 1/ VER/BOW
21839 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-02-24 09:40 | 2015-02-24 10:30 | 2 | 50 | 4077841 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING CUTOUT---1 CUST--CUST AWARE OF OUTAGE----XFMR OFF @ 09:40//XFMR IN AT 10:30 ALL PWR RESTORED PLEASE CLOSE TICKET//COD 2// VER/DBM
21840 | Hazard | 3309302 | VICCO | JEFF | 2012-07-27 13:05 | 2012-07-27 14:45 | 1 | 100 | 4845401 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT == REPLACED == REFUSED POWER OK VER/KEP
21841 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-06-03 16:35 | 2018-06-03 17:00 | 4 | 25 | 4550831 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop fell, arcing in backyard. opened transformer at 16:35, back in around 17:00. Service drop put back up, all power restored
21842 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-11-27 07:20 | 2016-11-27 07:45 | 4 | 25 | 4131131 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELATED TO 4131061// WIRE PULLED OUT OF SLEEVE ON POLE 37830122000023//LIFTED CLAMP ON POLE 37830146000014//TO MAKE SAFE REPAIRS//OPENED @ 0720//CLOSED @ 0745//COD 4 VER/TOM L3/TOM HFPC LCDTEMPORARY OPEN
21843 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-05-16 08:15 | 2012-05-16 09:55 | 1 | 100 | 4799691 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE , RESTORED POWER AT 09:55//COD 1// VER/DBM IDC XXXX
21844 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-05-02 13:06 | 2015-05-02 14:46 | 1 | 100 | 4384021 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE HAS GONE BAD IN THE SERVICE DROP. I OPENED THE TRANSFORMER AT 14:11 TO MAKE REPAIRS, ONLY ONE CUSTOMER IS OFF. POWER IS BACK ON AT 14:46. VER/CRB
21845 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-03-26 15:30 | 2009-03-26 16:20 | 2 | 50 | 61829-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED UP 3 PHASE TAP AT 1530 ON POLE 496-26 TO PUT OUT POLE FIRE ON POLE 26 AND REPLACE BAD CUTOUT//ISO//COD 2// VER/DBM IDC XXXX
21846 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-06-29 13:48 | 2020-06-29 14:08 | 5 | 20 | 4089451 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broke service neutral on pole 446-199.. repaired service neutral. open @ 13:48 closed @ 14:08
21847 | Hazard | 3309302 | VICCO | JEFF | 2015-03-13 14:25 | 2015-03-13 16:05 | 1 | 100 | 4190751 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED AT CUST MAST, REPAIRED // VER/DBM
21848 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2015-11-22 16:30 | 2015-11-22 18:10 | 1 | 100 | 4478241 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE ROTTED OFF UNDERGROUND ONLY THING HOLDING IT UP,,ROTTED POLE # 38830069B48031,,COULD NOT CONTACT WINDSTREAM,,DID NOT ANSWER PHONE,,WE WILL SET POLE/ HAD SERVICE OUT ON POLE 38830069B48031 ONLY 1630-1810/ ISO 38830069B48031/ COD 1 RELEASED BY CREW 078H03/ VER/BOW
21849 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2022-10-10 10:15 | 2022-10-10 11:55 | 1 | 100 | 4011011 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Replacing rotted off pole
21850 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-03-31 18:25 | 2020-03-31 19:15 | 2 | 50 | 4550231 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000901/gaj/1829/all out disp 3317 G Hicks. Power on at 19:15
21851 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-01-08 17:15 | 2014-01-08 18:05 | 2 | 50 | 4262271 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. FUSE IS BLOWN ON POLE 143-196. I AM GOING TO REFUSE TRANS. CUTOUT WAS ACTUALLY BROKEN. I CHANGED CUTOUT. VER/CRB
21852 | Whitesburg | 3409503 | BURDINE | JENKINS | 2015-08-29 23:11 | 2015-08-30 00:51 | 1 | 100 | 4182921 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GOING BAD ON POLE 358-91, WILL HAVE TO OPEN 3 LINE FUSES ON POLE 382-162, WILL KEEP TRACK OF TIMES. I OPENED THOSE L/FS AT 0007, MADE REPAIRS AND CLOSED THEM BACK IN AT 0051. VER/KEP
21853 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-08-02 16:10 | 2016-08-02 16:30 | 5 | 20 | H4724241 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ONE LEG OF SERVICE BURNED OFF AT SERVICE MAST. I OPENED XFMR AT 16:10 TO MAKE REPAIRS, CLOSED BACK IN AT 16:30 COD-6 ISO TF 37830426C00437 FIX IN HOIS DUP OF 4724241 VER/HFP L3/HFP
21854 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-06-05 19:10 | 2008-06-05 20:50 | 1 | 100 | 58605-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GATE ON POLE #270-331..... REPLACED CUTOUT... RESTORED POWER AT 2050//3308503//VER/CRB
21855 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-05-30 10:00 | 2016-05-30 11:40 | 1 | 100 | 4271951 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR OPEN ON POLE 1036-27 , BROKE CUTOUT . REPLACED CUTOUT & CLOSED XFMR BACK @ 11:40 VER/CRB
21856 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-11-13 08:30 | 2016-11-13 08:55 | 4 | 25 | 4096571 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POWER CHECK OK AT THIS TIME === WILL CHECK THIS IN AM BAD SECONDARY CONNECTION ON TRANSF === REPAIEREED === OPEN TRANSF AT 8:30 TO 8:55 === POWER OK/ ISO 37830318D00046/ COD 4/ VER/BOW
21857 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-10-15 13:57 | 2018-10-15 15:37 | 1 | 100 | 4255141 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repair connection L3/HFP
21858 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-06-17 14:05 | 2019-06-17 15:45 | 1 | 100 | 4525631 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad conn on sec repairs made please close ticket thanks.bt
21859 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2011-05-23 09:20 | 2011-05-23 09:45 | 4 | 25 | 4123731 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST HAS PART POWER AGREED TO WAIT TIL 2MORROW NEED BIG BUCKET AND 80 FEET OF NO 2 SERVICE CREW 077H01 RELEASED BY CREW 077H01 --- CHANGED SERVICE -- OPENED TRANSFORMER AT 0920 -- CLOSED AT 0945 -- POWER RESTORED. //VER/GAH
21860 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2010-03-17 13:30 | 2010-03-17 14:20 | 2 | 50 | 51130-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND BAD TRANSFORMER DURING CONVERSION JOB CREW ENROUTE TO REPLACE VER/KEP L3/KEP IDC XXXX
21861 | Pikeville | 3408101 | SALISBURY | PRINTER | 2018-05-28 17:08 | 2018-05-28 18:48 | 1 | 100 | 4510951 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t broken. replace fuse closed in everything ok.
21862 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-04-11 20:50 | 2021-04-11 22:30 | 1 | 100 | 4443071 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm cutout gate burnt up. replaced and restored power at 22:30
21863 | Pikeville | 3421001 | BREAKS | CITY | 2009-09-04 11:19 | 2009-09-04 12:59 | 1 | 100 | 64960-1 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3400901// HOT TAP HAS BURNED OFF BELL AT PRI. METERING AT POLE 244-109. I AM GOING TO OPEN CUTOUTS AND REPLACE HOT TAP. BACK ON @ 1248 IDC XXXX
21864 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2022-09-23 17:10 | 2022-09-23 18:00 | 2 | 50 | 4914711 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bright dim call made per tyler evans/bad 25kva along rt 23/flaggers reqd/send to L. Mccoy. tre Released by crew 078S04crewon site FETR 18:30LRMoponed17:10 in at 18:00 LRM
21865 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-09-15 16:05 | 2009-09-15 16:25 | 5 | 20 | H59722-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP # 6 COPPER SECONDARY BROKEN AT DEADEND MAKING REPAIRS /// OPENED TRANSFORMER @ 1605 CLOSED @ 1625 # 6 COPPER SECONDARY BROKEN AT DEADEND MAKING REPAIRS//REPAIRS COMPLETE PLEASE SEND COPY TO DOUG CHRISTIAN FOR REBUILD ON # 6 SECONDARY THIS IS FOR THE 5 CUST OUTAGE L3/HFP IDC XXXX
21866 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-01-30 17:20 | 2008-01-30 19:00 | 1 | 100 | 62504-1 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | 3310501//LEAD FELL OUT OF SECONDARY BUSH// VER/DBM IDC XXXX
21867 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2014-09-18 10:00 | 2014-09-18 10:25 | 4 | 25 | 4508101 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | I OPENED XFMR AT 10:00 AND CHANGED LEAD OUT AND CLOSED BACK AT 10:25 VER/CRB
21868 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-02-22 15:35 | 2014-02-22 16:00 | 4 | 25 | 4426381 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL PULLED OUT OF SPLICE ON SERVICE, WILL OPEN UP XFMR 0N POLE 531-31//// OPENED XFMR 15:35 BACK ON 16:00, RESAGED SERVICE POWER RESTORED.//COD 4// VER/DBM
21869 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-04-27 16:35 | 2015-04-27 17:00 | 4 | 25 | 4370551 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OFF AT TRANSFORMER, CREW COMING TO HELP. NO OUTAGE UNTILL OPENED TRANSFORMERS TO MAKE REPAIRS AT 16:35, CLOSED AT 17:00, ELECTRIC MOTOR REPAIR SHOP TESTING 300 HP MOTOR, BURNT CONNECTIONS AT TRANSFORMER, PLEASE SEND TO D. CHRISTIAN. VER/CRB
21870 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-05-24 21:15 | 2018-05-24 21:35 | 5 | 20 | 4409141 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer lights are dim throughout whole house/ ISO 38830069A10213/ COD 5/ 2115-2135
21871 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2010-09-04 18:30 | 2010-09-04 20:10 | 1 | 100 | 63692-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR# 36752335 //NEU WIRE BROKE AT POLE// VER/DBM IDC XXXX
21872 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-05-27 10:00 | 2021-05-27 10:50 | 2 | 50 | 4631021 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replacing bad transformer (2COD)// Opening to replace bad xfmr//OFF@10:00// Replaced xfmr and cutout and restored @ 10:50
21873 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-11-25 15:41 | 2017-11-25 16:31 | 2 | 50 | 4601811 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse broke/ ISO 38830269A00335/ COD 2
21874 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2017-04-07 10:34 | 2017-04-07 10:54 | 5 | 20 | 4627171 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE AT 1034. CLOSED AT 1054 REPLACED CUTOUT THE POLE IS BURNED ABOUT HALFWAY THRU. 45-5 THREE PHASE DOUBLE ARMS WITH A FUSED SINGLE PHASE LATERAL. WE SHOULD REPLACE IT, BUT IT WILL STAND UNTIL WE CAN DO IT./ XFMR ON POLE 125-8 IS ON LOAD SIDE OF FUSE/ ISO 37820125000008/ COD 5/ VER/BOW L3/HFP XXXHFP
21875 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-08-21 11:02 | 2009-08-21 11:22 | 5 | 20 | 58781-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE TO SAFELY REPLACE CUTOUT ON ORDER 58060-1 VER/KEP L3/KEP IDC XXXX
21876 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2018-04-15 11:35 | 2018-04-15 13:15 | 1 | 100 | 4227021 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 13:15. sh
21877 | Hazard | 3309003 | JEFF | VIPER | 2016-03-02 09:05 | 2016-03-02 10:45 | 1 | 100 | 4800691 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | K-MAYET BAD ON TRANSF === REM REFUSED POWER OK// VER/ ADH
21878 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-05-08 14:20 | 2011-05-08 16:00 | 1 | 100 | 4019791 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39869803 // BAD CUTOUT ON 352-344 ONLY ONE CUSTOMER AFFECTED // OPENED LINE FUSE ON 352-170 @ 1526 TO TRANSFER PRIMARY STS WR # 39869803 // BAD CUTOUT ON 352-344 ONLY ONE CUSTOMER AFFECTED... OPENED LINE FUSE ON 352-170 AT 15:35 MADE REPAIRS RESTORED POWER AT 1600 SEE H4019791 FOR FUSE VER/HFP L3/HFP IDCC PN367 DCMT XXXX
21879 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-08-09 10:17 | 2019-08-09 11:57 | 1 | 100 | 4863371 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on Pl# 138B450---replaced and Restored Pwr @ 11:57---tbl tkt comp---rmv
21880 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-05-09 22:39 | 2015-05-10 00:19 | 1 | 100 | 4407221 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN ON POLE VER/KEP
21881 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-11-04 10:20 | 2018-11-04 12:00 | 1 | 100 | 4361611 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | customer had connection heating up and burnt conductors into.repairs made.restored.. L3/HFP
21882 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-03-31 10:33 | 2015-03-31 12:13 | 1 | 100 | 4246451 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PER GREG FUGATE, METER 190314536 IS PART POWER// CONNECTOR BAD ON SERVICE, POWER RESTORED./ ISO 37830248A00885/ COD 1/ VER/BOW
21883 | Cannonsburg | 3113601 | WORTHINGTON | CSX WELD SHOP | 2015-02-23 18:14 | 2015-02-23 19:54 | 1 | 100 | 4076331 | 100 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | BELLEFONTE 69KV CB A AT RACELAND OPENED AT 1814 CLOSED AT 1954 // VERIFIED TIMES WITH DDC & TDC LOG & SCADA VER/HFP L3/HFP
21884 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2008-08-25 16:30 | 2008-08-25 16:55 | 4 | 25 | 54777-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP XFMR ON POLE 1101-498 IS LEAKING OIL. NEEDS TO BE CHANGED. G.R. TIM HALL TO SEND CREW OUT OF PIKEVILLE TO CHANGE THIS.THEY ALREADY HAVE THE INFO. RELEASED BY CREW 074S04 ----STS WR# 25937222 ---- NEED TIME OFF 1630 & TIME ON 1655 THANKS...HFP IDC XXXX
21885 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-02-03 | 2019-02-03 01:40 | 1 | 100 | 4749601 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | tried to call customer--no answer///LINEF ON 1SPAN SIDETAP IS OUT,WILL CHECK//////////NOTHING EVIDENT,RE-FUSED&RESTORED///////NO IDEA WHY FUSE WAS BLOWN Released by crew 074S06
21886 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-02-23 22:10 | 2015-02-23 23:00 | 2 | 50 | 4076591 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE/SERVICER OPENING TRANSFORMER 771-B-547 TO MAKE REPAIRS/BAD CURRENT LIMITING FUSE. POWER IS ON NOW, BUT I WILL NEED TO OPEN THE TRANSFORMER TO MAKE REPAIRS. REPAIRS MADE, I OPENED THE TRANSFORMER AT 22:10, AND CLOSED AT 23:00./COD 2// VER/ ADH
21887 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-10-04 13:10 | 2009-10-04 14:50 | 1 | 100 | 50963-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPLACED BAD SPLICE IN SERVICE DROP.//VER/CRB IDCC MCCDL XXXX
21888 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-08-07 12:30 | 2015-08-07 12:55 | 4 | 25 | 4108671 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY NEUTRAL LUG AND THE TANK GROUND LUG ON THE TRANSFORMER WAS VERY LOOSE CAUSING HIGH VOLTAGE ON THE CUSTOMERS. I MADE REPAIRS AND THE VOLTAGE IS GOOD NOW. I OPENED THE TRANSFORMER AT 12:30, AND CLOSED IT BACK IN AT 12:55./ ISO 38821058D00036/ COD 4/ VER/BOW
21889 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-04-22 19:05 | 2017-04-22 20:45 | 1 | 100 | 4669421 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830478B40298 BROKE C/O--REPLACED--( D WEST BROUGHT ME A 19.9 C/O) IN AT 20:45--ALLGOOD--DS042217 1 CUSTOMER OUT AT 38830478B40298 VER/AWD L3/HFP XXXHFP
21890 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-01-03 19:45 | 2008-01-03 21:25 | 1 | 100 | 53356-1 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308602// REPLACED CONNECTION ON TRANSFORMER POLE// VER/DBM IDC XXXX
21891 | Whitesburg | 3409503 | BURDINE | JENKINS | 2009-01-16 23:55 | 2009-01-17 01:35 | 1 | 100 | 56513-1 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTOR BURNED OFF AT TRANSFORMER VER/LDA L3/KEP
21892 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2011-11-22 14:15 | 2011-11-22 14:35 | 5 | 20 | 4100851 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED THE POLE IS BURNED 2/3 THRU. I REPLACED THE FAILED CUTOUT. OFF AT 1415 ON AT 1435//COD 5//ISO 37820147A20507//FEEDER # 3400702 //EMAILED TO LINE CREW AND TECH// VER/DBM IDC XXXX
21893 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2010-09-21 15:50 | 2010-09-21 17:30 | 1 | 100 | 51955-1 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LEG OF SERVICE DROP WAS BURNTED INTO, HAVE REPAIRS MADE AND EVERYTHING IS FINE HERE AT THIS LOC// VER/DBM IDCC MCCNI XXXX
21894 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-10-31 22:20 | 2013-10-31 23:10 | 2 | 50 | H4980541 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 4980541// 4/3 SERVICE BURNT DOWN IN TREE REPAIRED OPENED TRANS. 10 ;20 TO 11: 10//COD 2// VER/DBM
21895 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-08-21 11:05 | 2011-08-21 12:45 | 1 | 100 | 4735201 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF OF ONE PHASE OF PRIMARY METERING POLE 819-175// MADE REPAIRS ON OUR EQUIPMENT/// OPEN 3 CUTOUTS ON CUST. SIDE OF METERING BEFORE PUTTING HOT TAP BACK ON// CANT SEE THEIR LINE TO MAKE SURE ITS ALL CLEAR// PRETTY SURE THIS DOESNT SERVE ANYTHING// METER IS STILL ACTIVE// COMPLETE//EM COD-1 ISO PO 38820819A30175 VER/HFP L3/HFP IDC XXXX
21896 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-01-24 21:20 | 2017-01-24 23:00 | 1 | 100 | 4328531 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT ===CHANGED CUTOUT POWER OK/ ISO 37830270D00254/ COD 1/ VER/BOW L3/HFP XXXHFP
21897 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-01-29 10:30 | 2015-01-29 10:55 | 4 | 25 | 4972121 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED ON SECONDARY XFMR RISER, 954-1145. OPENED XFMR @ 10:30, REPAIRED AND CLOSED XFMR @ 10:55. SH//COD 4// VER/ ADH
21898 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-09-17 18:50 | 2015-09-17 20:30 | 1 | 100 | 4247391 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 HOT WIRE IN #4 SERVICE DROP WAS BURNED INTO///INSTALLED NEW #2 DROP///CUST BACK ON AT 2030///ONLY 1 CUST WAS OUT///COMPLETE BR VER/CRB
21899 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-02-25 14:14 | 2015-02-25 14:39 | 4 | 25 | 4081161 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE CURRENT LIMITING FUSE FAILED BY BURNING UP. THE TRANSFORMER FUSE WAS NOT BLOWN.//COD 4// VER/DBM
21900 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-11-13 18:10 | 2011-11-13 18:35 | 4 | 25 | 4072381 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | CHECKING.GUY WIRE BROKE LAYING ON OPEN WIRE SECONDARY, WILL HAVE TO GET GUY WIRE AND BREAKER AND REINSTALL. WILL BE OPENING TRANS. ON POLE 497-31 TO MAKE REPAIRS WILL KEEP TRACK OF TIMES.OPENED TRANS. AT 18:10 CLOSED BACK IN AT 18:35, MADE REPAIRS TO GUY WIRE. ///VER/CRB IDC XXXX
21901 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-03-24 13:20 | 2020-03-24 13:30 | 10 | 10 | 4505451 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Primary is intact but has come loose from primary pole top pin. ¦¦ 1320 TO 1330
21902 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2011-04-12 17:31 | 2011-04-12 19:11 | 1 | 100 | 56020-1 | 100 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | 2153502//CC=446//HI SIDE SW BURNING///NOTE: THIS STATION IS FED FROM THE LOVELY/WOLF CTREEK CKT. VER/MF
21903 | Paintsville | 3401802 | INDEX | HOSPITAL | 2021-07-03 19:55 | 2021-07-03 20:45 | 2 | 50 | 4854751 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken xfmr fuse changing/ ISO 38830654D00152/ COD 2
21904 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-02-09 16:15 | 2015-02-09 17:55 | 1 | 100 | 4003671 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN. @ XFMR BAD , REDONE CONN. FULL POWER @ METER . ONLY 1 CUST.// VER/ ADH L3/HFP
21905 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2018-02-03 19:51 | 2018-02-03 20:41 | 2 | 50 | 4798501 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | fire around down guy, grass was on fire Released by crew 078S07/no cust out at this time/will need to open line fuse for repairs/aprox one hour outage/cust is aware/vem/opened 1951 closed 2043fire around down guy, grass was on fire Released by crew 078S07/no cust out at this time/will need to open line fuse for repairs/aprox one hour outage/cust is aware/vem/open line at1951/repaired service /all cust restored 2041/please close ticket/thanks/vem
21906 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-05-30 12:50 | 2017-05-30 13:10 | 5 | 20 | 4881521 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION BROKE ON CUSTOMERS NEUTRAL IN SERVICE DROP, WILL HAVE TO OPEN UP THE TRANS. ON POLE 1102-184 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED THAT TRANS. @1250 AND MADE REPAIRS, CLOSED BACK IN @1310. 38831102000184 VER/AWD
21907 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-12-26 16:50 | 2012-12-26 18:30 | 1 | 100 | 4530771 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND MISER NUTS ON SERVICE DROP, I CUT THEM OUT AND RESQUEEZED EVERYTHING, IS FINE AT THIS LOC AT 1830 TIME VER/KEP
21908 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-11-04 14:25 | 2014-11-04 14:35 | 10 | 10 | 4698411 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD U/G GETTING PARTIAL POWER.SINGLE PHASE.CALLED TIM MILLER. RELEASED BY CREW 076S01// CREW ON SITE TCM/ INSTALLED AUTO TRANSFORMER , OPENED POT ON 834-427 AT 14:25 CLOSED BACK AT 14:35 ALL BACK ON , PLEASE SEND COPY TO BILL JOHNSON FOR FAULT LOCATION, TCM// ISO 38830834B00427/ COD/ VER/BOW
21909 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-05-07 20:26 | 2017-05-07 22:06 | 1 | 100 | 4766111 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BROKE NETURAL ON POLE37830157000093, CAUSING HIGH VOLTAGE ON 1 LEG OF SERVICE(238 VOLTS)..REPAIRED NETURAL ,,CUSTOMER STATED HEAT PUMP NOT WORKING AT THIS TIME,,//EMAILED TO P WYSONG// VER/DBM
21910 | Hazard | 3303901 | LESLIE | HYDEN | 2022-11-24 14:20 | 2022-11-24 16:00 | 1 | 100 | 4178381 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cleared blown lighting arrester on transformer. Power restored @ 16:00
21911 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-09-06 15:10 | 2021-09-06 16:00 | 2 | 50 | 4214851 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | cut bad arrester in the clear. power restored at 1600
21912 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2016-05-14 20:50 | 2016-05-14 22:30 | 1 | 100 | 4218461 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE. I CHANGED CUTOUT DOOR FUSED UP EVERYTHING OK VER/TOM L3/TOM
21913 | Cannonsburg | 3001401 | LOUISA | CITY | 2016-02-15 21:05 | 2016-02-15 21:15 | 10 | 10 | H4698421 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XMF CUTOUT BROKE HANGING IN THE CLEAR, CUTOUT ON ARM AND IS LINECREW REQUIRED RELEASED BY CREW 078S11--SECOND BAD CUTOUT FEEDING SIDETAP TOWARD POLE 454-1801--OPENED AT 21:05---BOTH 30T LF AND XFMR FUSES-BACK IN AT 21:15---TBL TKT COMP RELEASED BY CREW 078H16// VER/ ADH
21914 | Hazard | 3301401 | COMBS | COMBS | 2014-12-31 14:25 | 2014-12-31 16:05 | 1 | 100 | 4895141 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 37830271A00035 SERVICE BURNT DOWN, PRIMARY DEADEND INS BROKEN ON TWO PHASES, J COMBS AND CREW ENROUTE TO HELP, WILL NEED TO OPEN REC ON POLE 37830271C11075 TO MAKE REPAIRS. RELEASED BY CREW 077S04//MADE TICKET 4895311 FOR RECLOSER OUTAGE//CLOSED @ 1751//IT FORCE CLOSED
21915 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-03-17 11:54 | 2014-03-17 12:19 | 4 | 25 | 4498151 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | NO CUSTOMER OUT AT THIS TIME - CUSTOMERS SEEING MULTIPLE OPERATIONS - CREW PATROLLING CKT TO SEE IF THEY CAN DETERMINE CAUSE OF FLICKERIN LIGHTS. //PATROLLED LINE FOUND NOTHING /NEEDS TO BE LOOKED AT IN DAYLIGHT/VEM CREW REQUIRED X-ARM BRACES BROKEN 268-60 ALSO TREE CREW ON 268-53 RELEASED BY CREW 078S03/OPEN FUSE ON 268-60@1154 FOR REPAIRS/REPAIRS MADE AND FUSE BACK IN @1219/PLEASE CLOSE TICKET/THANKS/VEM 15T FUSE DID MD VER/SEF
21916 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-05-08 15:35 | 2011-05-08 16:00 | 4 | 25 | 4019791 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39869803 // BAD CUTOUT ON 352-344 ONLY ONE CUSTOMER AFFECTED // OPENED LINE FUSE ON 352-170 @ 1526 TO TRANSFER PRIMARY STS WR # 39869803 // BAD CUTOUT ON 352-344 ONLY ONE CUSTOMER AFFECTED... OPENED LINE FUSE ON 352-170 AT 15:35 MADE REPAIRS RESTORED POWER AT 1600 FROM 4019791 VER/HFP L3/HFP IDCC PN367, CDC92 XXXX
21917 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-11-29 15:50 | 2015-11-29 16:40 | 2 | 50 | 4492421 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOUNDS LIKE CUTOUT BREAKING DOWN WILL HAVE TO OPEN XFM. BANK AND CLIMB POLE 37830143A00149 TO CHANGE OUT CUTOUT.ONLY ONE CUSTOMER HERE.FEEDS CHURCH.SOUNDS LIKE CUTOUT BREAKING DOWN WILL HAVE TO OPEN XFM. BANK AND CLIMB POLE 143A-149 TO CHANGE OUT CUTOUT.ONLY ONE CUSTOMER HERE.FEEDS CHURCH.OPENED BANK @ 15:50 CLOSED BACK @ 16:40.. VER/CRB
21918 | Pikeville | 3407101 | TOPMOST | DEMA | 2009-03-26 16:15 | 2009-03-26 17:05 | 2 | 50 | 61840-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3407101// BAD CUTOUT ON POLE 114-92. I HAVE FIRE OUT AND WILL BE REPLACING CUTOUT. I INSTALLED NEW FIBERGLASS BRACKET. CUTOUT AND ARRESTER. POLE HAS SMALL HOLE BURNT OUT IN IT SEND COPY OF THIS TO RON RYE ENG PIKEVILLE.//ISO 37830114D00092//COD 2// VER/DBM IDC XXXX
21919 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-07-16 15:00 | 2013-07-16 15:20 | 5 | 20 | H4528621 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FAULT INDICATOR SHOW BAD CABLE BETWEEN PAD MOUNT TRANSFORMER 1073-3616 TO 1073-3614, THINK YOU CAN ISOLATED THIS SECTION OF CABLE BUT HAD NO FEED THRU, AND PARKING STANDS IN TRANSFORMER RELEASED BY CREW 078S06 RELEASED BY CREW 078H07 VER/CRB L/3 CRB IDC DUP TO OPEN OTHER TAP XXXX
21920 | Pikeville | 3421001 | BREAKS | CITY | 2013-09-12 14:40 | 2013-09-12 15:00 | 5 | 20 | H4842431 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED INTO AT POLE 220-332. I AM GOING TO OPEN LINE FUSE ON POLE 220-389 LONG ENOUGH TO REPAIR LOOP. I OPENED LINE FUSE ON POLE 220-389 AT 14:40, (5 CUSTOMERS) REPAIRED LOOP, AND CLOSED LINE FUSE IN AT 15:00 COD-28 ISO PO @ 37820220D10332 DUP OF 4842431 FOR 5 CUST // VER/HFP L3/HFP IDC XXXX
21921 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-10-19 08:20 | 2018-10-19 10:00 | 1 | 100 | 4269191 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ROUSEAU SCHOOL/ops 035574855-talked to owner ok/ need by NOV 6 ELECTION---JIM 1 PHASE OUT /TAGGED FOR DDC
21922 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-03-26 12:20 | 2009-03-26 14:00 | 1 | 100 | 61720-1 | 100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOOK CUTOUT OFF LINE NEED BIG BUCKET TO CHG...CALLED MILLER RELEASED BY CREW 076S01//COD 1// VER/DBM IDC XXXX
21923 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-12-11 17:45 | 2013-12-11 19:25 | 1 | 100 | 4154471 | 100 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | ONE LEG ON SECONDARY BURNT OPEN AT SPLICE WILL REPAIR. REPAIRED SECONDARY RESTORED SERVICE @ 19:25 GOOD VOLTAGE 119/119/238//COD 1// VER/DBM L3/HFP
21924 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2019-11-26 13:04 | 2019-11-26 14:43 | 1 | 99 | 4069471 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | quicksleeve in neut not making good connection, jumpered sleeve, voltage good. pls close. tre
21925 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2016-02-13 05:01 | 2016-02-13 06:40 | 1 | 99 | 4692461 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED. REPLACED CONNECTION AND RESTORED @ 6:40. SH VER/TOM L3/TOM
21926 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-06-04 16:18 | 2015-06-04 17:57 | 1 | 99 | 4512151 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BURNT INTO ON SECONDARY WILL REPAIR/// REPAIRED NEUTRAL IN SECONDARY 124/124/248 EVERYTHING OK NOW VER/CRB
21927 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2008-10-28 19:16 | 2008-10-28 20:55 | 1 | 99 | 60346-1 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 2150502//, ON SITE, CHECKING TROUBLE, BAD CONNECTION ON NEUTRAL ON XFORMER POLE// VER/DBM IDC XXXX
21928 | South Williamson | 3200302 | BELFRY | TOLER | 2008-04-03 15:45 | 2008-04-03 17:24 | 1 | 99 | 63443-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200302//, ON SITE, POLETOP ON FIRE, CALLING R MARCUM FOR HELP VER/HFP IDC ORIGINAL CALL WAS FULL POWER ESTIMATED TIME OFF AND CHANGED FROM 1451 XXXX
21929 | Whitesburg | 3314401 | MAYKING | ERMINE | 2010-08-19 19:21 | 2010-08-19 21:00 | 1 | 99 | 58437-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 449-1037 , OPENED LINE FUSE ON 449-560 AT 20:36 TO ISOLATE.. MADE REPAIRS RESTORED POWER AT 2100 MADE DUP OUTAGE FOR LINE FUSE VER/KEP L3/KEP IDC XXXX
21930 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-03-29 20:51 | 2009-03-29 22:30 | 1 | 99 | 62835-1 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONN ON TRANS ONE CUSTOMER ON TR. VER/PDP IDCC MCCDL XXXX
21931 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-01-16 09:35 | 2018-01-16 10:08 | 3 | 33 | 4750371 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | changed all the connections at xfm and weatherhead// customer is still getting flicker problem /// will have to get help in the A.M. to upgrade service Released by crew 074S02 off 0935-1008. send copy to mike hatfield to replace tfo.changed all the connections at xfm and weatherhead// customer is still getting flicker problem /// will have to get help in the A.M. to upgrade service /// Changed service helped flicker some///Secondary Bushing is loose on xfm/// Send copy to Mike hatfield to write
21932 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-06-25 14:32 | 2008-06-25 16:11 | 1 | 99 | 53924-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401101//BAD XFMR. CREW ENROUTE. RELEASED BY CREW 076S02//CHANGED OUT 15 KVA TRANSFORMER BACK ON AT 16:11 TC MILLER // VER/TOM IDC XXXX
21933 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2009-03-11 16:15 | 2009-03-11 16:48 | 3 | 33 | 57287-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 28887228 //APPEARS XFR CUTOUT HAS BROKEN DOWN,WILL REPLACE ITAPPEARS XFR CUTOUT HAS BROKEN DOWN,REPLACED IT AND RESTORED.ALL OK AFTERWARDS.OFF AT 16:15 ON AT 16:48 COD-3 L3/HFP IDC XXXX
21934 | South Williamson | 3411401 | DEWEY | INEZ | 2018-09-26 19:44 | 2018-09-26 21:23 | 1 | 99 | 4163231 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse out on 766-126.saw no hazards. restored power at 21;23 // cod 1
21935 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-05-21 19:03 | 2019-05-21 20:42 | 1 | 99 | 4312611 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout failed on 818-D3-337.replaced cutout.restored power at 20:42
21936 | Hazard | 3311103 | STINNETT | WENDOVER | 2016-01-11 21:14 | 2016-01-11 22:53 | 1 | 99 | 4608201 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION/ BAD SERV END/ ISO 37830435000062/ COD 1/ VER/BOW
21937 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-07-21 08:54 | 2010-07-21 10:33 | 1 | 99 | 54854-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT//COD 1// VER/DBM IDC XXXX
21938 | Hazard | 3420001 | SOFT SHELL | VEST | 2016-01-03 12:06 | 2016-01-03 13:45 | 1 | 99 | 4582461 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 157-107 , REPLACED CUTOUT , CLOSED XFMR BACK @ 13:45/ ISO 37830157000107/ COD 1/ VER/BOW
21939 | South Williamson | 3411401 | DEWEY | INEZ | 2022-03-23 14:12 | 2022-03-23 14:45 | 3 | 33 | 4662131 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | oPEN PADMOUNT tr 38830885000008 (3 COD) to repair underground secondary to a pedestal///Off at 1412 -- On at 1445 replace damaged pedestal
21940 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-06-09 19:51 | 2010-06-09 21:30 | 1 | 99 | 59480-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT DOOR. COD-1 VER/HFP L3/HFP
21941 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-08-01 16:11 | 2011-08-01 16:44 | 3 | 33 | 4650701 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TRANS AT 1611//NU. BURNT INTO WIRE MELTED REPAIRED//VER/CRB IDC XXXX
21942 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-09-17 14:12 | 2021-09-17 14:45 | 3 | 33 | 4252211 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connections
21943 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-09-09 09:33 | 2020-09-09 11:12 | 1 | 99 | 4444481 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | changing out 4-3 triplex drop to a 2-3 triplex service drop.
21944 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-01-17 13:21 | 2019-01-17 15:00 | 1 | 99 | 4681651 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection L3/HFP
21945 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-11-28 20:21 | 2015-11-28 22:00 | 1 | 99 | 4490281 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE DOOR BURNT UP. REPLACED AND RESTORED @ 22:00. SH VER/TOM L3/TOM
21946 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2018-06-19 12:36 | 2018-06-19 14:15 | 1 | 99 | 4621391 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken xfmr cutout,,replaced cutout,,all power restored/ ISO 38830453A20411/ COD 1
21947 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-03-11 20:21 | 2014-03-11 22:00 | 1 | 99 | 4469501 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD HOT TAP ALSO REPLACED FUSE VER/SEF
21948 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-07-30 14:22 | 2018-07-30 14:55 | 3 | 33 | 4870651 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED: seondary pole 38831076000174 down, 30 - 6 pole , 50 ft 2/3 triplex, line truck, big bucket . 811 called - # 1807301036 . opened XFMR pole 1076-127 @ 14:22 and closed @ 14:55 / ALL WORK COMPLETE / GXJ Released by crew 074S03
21949 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-07-26 13:00 | 2012-07-26 14:39 | 1 | 99 | 4832581 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED LOOSE//REFUSED//COD 1// VER/DBM
21950 | Hazard | 3309302 | VICCO | JEFF | 2009-01-21 21:36 | 2009-01-21 23:15 | 1 | 99 | 58951-1 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3309302// UNDERGROUND GOING TO METERBASE CONNECTION BAD == REPAIRED FOR NOW == WILL REWORK 1-22-09//VER/CRB L3/KEP
21951 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2014-05-21 19:51 | 2014-05-21 21:30 | 1 | 99 | 4731001 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER MIKE PHELPS, BAD CUTOUT VER/SEF
21952 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-08-15 15:21 | 2009-08-15 17:00 | 1 | 99 | 58968-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP #4 SERVICE SHORTED OUT,WILL TRY TO REPAIRREPAIRED 4/3 SERVICE DROP,BELIVE BAD SERVE-IN CONNECTION OVERHEATED,MELTED INSUL AND BURNED DROP DOWN,WAS 100AMP SERVICE INSTALLATION L3/HFP IDC XXXX
21953 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2019-08-19 09:04 | 2019-08-19 09:15 | 9 | 11 | 4905521 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 40t lf open @ 1123-5077, bad xfmer @39831123C35051. bad xfmer took out lf. restored @ 09:15 L3/HFP
21954 | Paintsville | 3401802 | INDEX | HOSPITAL | 2020-04-23 13:21 | 2020-04-23 15:00 | 1 | 99 | 4740511 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broken, changing..
21955 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-02-12 17:54 | 2018-02-12 19:33 | 1 | 99 | 4835791 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfr fuse complete/ ISO 38830472000071/ COD 1
21956 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-07-21 18:57 | 2015-07-21 20:36 | 1 | 99 | 4928621 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION AT ENTERANCE WAS HEATING UP // REWORKED ENTERANCE VER/HFP L3/HFP
21957 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-11-15 19:40 | 2011-11-15 21:19 | 1 | 99 | 4080261 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHECKING. BAD C/O AT POLE 353-58, WILL BE MAKING REPAIRS. MADE REPAIRS, CLOSED BACK IN AT 21:19.//COD 1// VER/DBM IDC XXXX
21958 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2014-11-19 08:03 | 2014-11-19 09:42 | 1 | 99 | 4744791 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR.REPLACING..38830678C00230 VER/CRB
21959 | Hazard | 3303902 | LESLIE | WOOTON | 2014-06-20 14:36 | 2014-06-20 16:15 | 1 | 99 | 4123351 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9 KV CUTOUT VER/CRB
21960 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-03-24 09:16 | 2012-03-24 10:55 | 1 | 99 | 4611221 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT..CAN REPLACE..1 CUST..//..REPLACED CUTOUT..POWER ON ..JRV..03/24/12 ///VER/CRB IDC XXXX
21961 | Hazard | 3303902 | LESLIE | WOOTON | 2022-01-20 12:33 | 2022-01-20 13:06 | 3 | 33 | 4390311 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | opened xfmr from 12:33 to 12:45///was no outage until TR was opened to make repairs
21962 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-06-22 09:52 | 2020-06-22 10:25 | 3 | 33 | 4058281 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced hot line clamp,,opened line fuses @ 09:55 closed @ 10:25,,complete // cod 3
21963 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2013-04-06 15:11 | 2013-04-06 16:50 | 1 | 99 | 4984081 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT SERV. TO CHANGE. REPAIRS MADE ALL CUST REST@1650 ///VER/CRB /L/3 CRB IDC XXXX
21964 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-08-10 18:06 | 2013-08-10 18:39 | 3 | 33 | 4645651 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED HELP,XFR CUTOUT BROKEN,IS UP IN PRIM TAPS THAT GO 3 WAYS OFF POLE.///OPENED LINE F 1013-247 TO REPLACE CUTOUT @18:06////REPLACED AND RESTORED AT 18:39 VER/CRB L/3 CRB
21965 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-06-02 20:16 | 2010-06-02 21:55 | 1 | 99 | 55589-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PRIMARY METERING BAD ON C PHASE.//AED CREATED // VER/DBM IDCC PN404 XXXX
21966 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-10-05 12:36 | 2014-10-05 14:15 | 1 | 99 | 4555411 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BURNED INTO AT TRANSFORMER. I AM GOING TO REPLACE DROP TO A BIGGER SIZE WIRE. I CHANGED SERVICE DROP TO A 2/3 SERVICE. VER/CRB VER/DKG L3/DKGXXXX
21967 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-04-06 14:12 | 2015-04-06 15:51 | 1 | 99 | 4281161 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE REPAIRED VER/CRB
21968 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2018-07-05 14:36 | 2018-07-05 16:15 | 1 | 99 | 4729331 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | MARSHALL RECOMMENDS S/D BE REPLACED TOMORROW JULY 6TH//JOB HAS BEEN WRITTEN//IN THE AM//HAS BURNT HOLE IN CUSTOMERS ROOF.MEXICAN RESTURANT//SENT TO LINE DEPT
21969 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-09-24 10:43 | 2013-09-24 12:22 | 1 | 99 | 4882091 | 99 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE BAD HOTLEG ON GARAGE SERVICE, UNABLE TO ISOLATE AT THIS TIME. CONTACT # FOR CUSTOMER 606-483-2810 BESURE AND CONTACT CUSTOMER BEFORE ENTERING ON PROPERTY 3 AGGRESSIVE DOGS. WILL BE WORKED ON OPS ORDER 032028777 PLEASE CLOSE TICKET//COD 1// VER/DBM IDCC PN NULL, MCCDL XXXX
21970 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-01-30 10:26 | 2021-01-30 12:05 | 1 | 99 | 4920181 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout and restored @ 12:05. sh
21971 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-09-24 08:58 | 2019-09-24 10:37 | 1 | 99 | 4052871 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout going bad. all power restored. pls close. tre
21972 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-09-03 20:16 | 2009-09-03 21:55 | 1 | 99 | 64321-1 | 99 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT .. CHG CUTOUT...BB//COD 1// VER/DBM IDC XXXX
21973 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2018-04-16 12:52 | 2018-04-16 14:30 | 1 | 98 | 4239861 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 14:30. sh cod 1 iso 38831027A00571
21974 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2008-10-09 18:22 | 2008-10-09 20:00 | 1 | 98 | 54719-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3001001//BLOWN XFMR FUSE// 6A COPPER NEUTRAL DOWN FROM POLE 329-37 TO POLE 38830329000029, WIRE HANGING FROM POLE GOT INTO OPEN WIRE SEC GOING TO HOUSE, CLEARED UP ON POLE, NEED TO PUT IN ABNORMAL TO REPLACE NETRAL, APPEARS TO HAVE BEEN DOWN FOR A WHILE.//COD 1//MADE ADE// VER/DBM IDC XXXX
21975 | Pikeville | 3421001 | BREAKS | CITY | 2022-12-08 07:22 | 2022-12-08 09:00 | 1 | 98 | 4241061 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop caught on fire and burnt into @ xfm Repairs made restored @ 09:00////Only 1 customer affected
21976 | Paintsville | 3410602 | E.PRESTON | LANCER | 2021-06-16 23:07 | 2021-06-16 23:56 | 2 | 49 | 4761321 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse was open on 979-C-15 due to fuse pulling apart inside cutout door. I refused and restore @ 23:56
21977 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-07-22 03:12 | 2014-07-22 03:26 | 7 | 14 | H4269471 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | BAD UG CABLE BETWEEN 115-489 AND 115-477/ BAD FEED THRU AT JUNTION 115-468/RELEASED BY CREW 078H12 RELEASED BY CREW 078H03..DKG/PER LOG AND SWITCH COORDINATOR/5 CUST REST AT 2000,7 CUST AT 2225,1 CUST AT 0328. VER/DKG/ L3/DKG THIS OUTAGE FOR INTERRUPTING 7 CUST THAT WAS RESTORED ON 4269471 IDCC TOF3012 7/21 XXXX
21978 | Pikeville | 3421001 | BREAKS | CITY | 2012-09-12 10:34 | 2012-09-12 11:23 | 2 | 49 | 4042081 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | THE RECLOSER HANDLE WAS RELUCTANT TO STAY UP, BUT I WAS ABLE TO GET IT TO STAY CLOSED. ///VER/CRB L/3 CRB IDC XXXX
21979 | Hazard | 3302704 | HAZARD | KENMONT | 2022-03-02 10:11 | 2022-03-02 11:00 | 2 | 49 | 4559381 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | bad current limiting fuse bad on pole 296 c2 958// MDR submitted
21980 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2011-10-20 20:41 | 2011-10-20 21:30 | 2 | 49 | 4006211 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK ROTTEN AND BROKEN, POWER IS RESTORED AT THIS LOC//MADE A MDC//COD 2 ///VER/CRB IDC XXXX
21981 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2013-06-07 11:56 | 2013-06-07 12:45 | 2 | 49 | 4235971 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | I CHECKED AND REFUSED XFMR FUSE BROKE VER/KEP IDC XXXX
21982 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-03 08:37 | 2011-01-03 10:15 | 1 | 98 | 58119-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMT FUSE I WILL BE CHANGING OUT. WE HAVE REPLACED BAD EQUIPMENT EVERYTHING OK VER/KEP L3/KEP IDC XXXX
21983 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2020-05-16 17:40 | 2020-05-16 19:18 | 1 | 98 | 4843411 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout complete
21984 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-10-30 11:33 | 2019-10-30 13:11 | 1 | 98 | 4219381 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on pole 1124B2026. repairs made. pls close. tre
21985 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2022-03-28 13:45 | 2022-03-28 14:34 | 2 | 49 | 4683251 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | City of Paintsville reports dim light issue Bad 10 kva transformer in bank. Opened latteral off 810-156 @ 13:45, replaced xfmr and closed latteral and xfmr bank @ 14:25. sh
21986 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2018-11-17 01:37 | 2018-11-17 03:15 | 1 | 98 | 4446961 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | attempted to call customer, no response//low ambient temps //SERVICE DROP BURNT DOWN WILL MAKE REPAIRS// PUT SERVICE DROP BACK UP AND RESTORED SERVICE @ 03:15// ONLY 1 CUSTOMER AFFECTED L3/HFP
21987 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2009-07-03 11:00 | 2009-07-03 11:49 | 2 | 49 | 63471-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 2// VER/DBM IDC XXXX
21988 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2010-11-17 17:30 | 2010-11-17 19:08 | 1 | 98 | 57668-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE DROP SHORTED OUT AT A SPLICE IN MIDSPAN AND BURNED DROP DOWN. I AM GOING TO REPAIR DROP. I REPAIRED SERVICE DROP AND RESTORED POWER.//VER/CRB IDC XXXX
21989 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2020-05-14 11:52 | 2020-05-14 13:30 | 1 | 98 | 4835081 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse door had burnt up, replaced fuse and door apr at 1330 close ticket.
21990 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-01-04 21:11 | 2015-01-04 22:00 | 2 | 49 | 4905531 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 91-173 6T FUSE BROKE REPLACED VER/SEF
21991 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2018-03-19 14:41 | 2018-03-19 15:30 | 2 | 49 | 4027201 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | riser burnt into on xfmr cutout, will need flaggers.replaced cutout restored power at 15:30..
21992 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-08-10 12:56 | 2008-08-10 14:34 | 1 | 98 | 50691-1 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308603// NO TROUBLE VISIBLE. I AM GOING TO CHECK VOLTAGE AND CONNECTIONS. FOUND SERVICE CONNECTOR BURNED OFF AT TRANSFORMER//VER/CRB IDC XXXX
21993 | Whitesburg | 3312902 | JENKINS | JENKINS | 2008-12-15 21:42 | 2008-12-15 22:31 | 2 | 49 | 58774-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312902//OPENED LINE IN ORDER TO MAKE REPAIRS TO BAD CUTOUT//SEE ORDER 58754-1//COD 2// VER/DBM L3/KEP IDC XXXX
21994 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-12-15 19:52 | 2011-12-15 21:30 | 1 | 98 | 4181161 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REMADE CONNECTIONS AT WEATHERHEAD, APR CLOSE TICKET VER/HFP L3/HFP IDC XXXX
21995 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-11-10 19:15 | 2008-11-10 20:53 | 1 | 98 | 63742-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP NO CREW REQUIRED REPLACED EVERY CONNECTION IDC XXXX
21996 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-02-14 22:52 | 2009-02-15 00:30 | 1 | 98 | 61837-1 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP REPLACED CONNECTIONS ON POLE L3/HFP
21997 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-05-12 16:52 | 2015-05-12 18:30 | 1 | 98 | 4422521 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE A CONNECTION HAS BURNED INTO AT TRANSFORMER ON SERVICE DROP. I AM GOING TO FIX PROBLEM. I RESQUEEZED ALL CONNECTIONS ON TRANSFORMER POLE./ ISO 37830215C00265/ COD 1
21998 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-07-01 11:56 | 2010-07-01 12:45 | 2 | 49 | 61253-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT OFF... REPLACED CLAMP RESTORED POWER AT 12:45 VER/KEP L3/KEP IDC XXXX
21999 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-09-29 11:07 | 2009-09-29 12:45 | 1 | 98 | 54601-1 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE AT TRANSFORMER POLE CAN USE TRUCK SEND TO S HAMMONDS RELEASED BY CREW 078H03,,,,BACK ON POWER RESTORED//VER/CRB
22000 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-01-10 08:51 | 2018-01-10 09:40 | 2 | 49 | 4725941 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50 KVA transformer on 785-1114. Crew enroute to replace. Replaced and restored @ 9:40. sh/ ISO 38830785D41114/ COD 2
22001 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-12-17 15:17 | 2008-12-17 16:55 | 1 | 98 | 59632-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008702// BAD FUSE.//COD 1// VER/DBM L3/KEP IDC XXXX
22002 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2020-06-25 12:37 | 2020-06-25 14:15 | 1 | 98 | 4073331 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse had broke inside cutout door. I refused and restored @ 14:15
22003 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-04-17 11:28 | 2017-04-17 13:06 | 1 | 98 | 4651871 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED-RED PULLED APART ON SERVICE AT THEIR TRL. POLE. I REPLACED IT 37830353C00069 VER/AWD L3/HFP XXXHFP
22004 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-01-26 17:34 | 2017-01-26 19:12 | 1 | 98 | 4335671 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE ON @ 1912/ VER/BOW L3/HFP XXXHFP
22005 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2015-09-10 11:37 | 2015-09-10 13:15 | 1 | 98 | 4223691 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT VER/CRB
22006 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-07-22 12:56 | 2014-07-22 13:45 | 2 | 49 | 4272881 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED UP.CHANGING.BACK ON AT 13:45 COD 2// VER/ ADH
22007 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-11-07 15:28 | 2017-11-07 17:06 | 1 | 98 | 4539381 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 338-84 replaced cutout and 338-85 repaired lead burnt into will need to come back and replace span 4/2 to pole 338-69
22008 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-01-17 03:37 | 2009-01-17 05:15 | 1 | 98 | 56662-1 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3409301// NEUTRAL PULLED OUT OF SLEEVE. REPAIRED NEUTRAL AND ADDED WIRE TO MAKE SLACK IN HOT CONDUCTORS ALSO. CUSTOMER REPORTS ALL OK NOW. SH VER/KEP L3/KEP
22009 | Paintsville | 3409302 | KENWOOD | AUXIER | 2010-01-31 10:18 | 2010-01-31 11:56 | 1 | 98 | 61664-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 33667915. CHECKING NOW SERVICE DROP BURNT IN TWO BACK TO NORMAL VER/HFP L3/HFP IDC XXXX
22010 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-05-25 10:52 | 2021-05-25 12:30 | 1 | 98 | 4619801 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse on pole 295-344 still in. xfm cutout broke on pole 295-265. restored 12:30 Released by crew 077S10
22011 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2017-09-24 10:17 | 2017-09-24 11:55 | 1 | 98 | 4385611 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CHURCH HAVING HOMECOMING SERVICE AT NOON REPLACED BAD SECONDARY CONNECTION AT THE TRANSFORMER./ ISO 38821138C00142/ COD 1/ VER/BOW VER/ALB
22012 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-09-24 19:21 | 2009-09-24 20:10 | 2 | 49 | 61699-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT.//VER/CRB IDC XXXX
22013 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-06-10 12:35 | 2016-06-10 14:13 | 1 | 98 | 4332381 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUT SPLICE WAS PULLED APART. CUST STATES HAS BEEN FOR FEW DAYS. ALL PWR RESTORED PLEASE CLOSE TICKET DID NOT HAVE XFMR OFF LINE JUST PULLED MTR.. VER/HFP L3/HFP
22014 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-07-10 12:22 | 2017-07-10 14:00 | 1 | 98 | 4101751 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 135-14; CUTOUT BENT, AND DOOR BURNT UP. CUTOUT CHANGED, AND POWER RESTORED AT 14:00.38830195000014 VER/AWD
22015 | South Williamson | 3411401 | DEWEY | INEZ | 2011-02-24 11:16 | 2011-02-24 12:05 | 2 | 49 | 60705-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN ON POLE 743-93//CUTOUT BAD//RESTORED AT 12:05//COMPLETE//EM//VER/CRB IDC LOOKS LIKE THIS SHOULD BE 2 CUSTOMERS, CHANGED FROM 6 XXXX
22016 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2015-02-19 11:42 | 2015-02-19 13:20 | 1 | 98 | 4042921 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNT INTO @ SECONDARY POLE/// WILL REPAIR REPAIRED SERVICE DROP AND RESTORED SERVICE @ 13:20/// ONLY 1 CUSTOMER AFFECTED VER/HFP L3/HFP
22017 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-05-10 17:31 | 2015-05-10 19:09 | 1 | 98 | 4408521 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLEW ON POLE 376-328, MADE AED/ADH/ ON @ 1909// VER/ ADH
22018 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-04-06 08:47 | 2012-04-06 10:25 | 1 | 98 | 4651731 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKE. RE-FUSED @ 10:25. SH COD-1 ISO TF 38830834B00392 VER/HFP L3/HFP OOO IDC XXXX
22019 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-06-11 13:28 | 2015-06-11 14:17 | 2 | 49 | 4555141 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON XFMR BANK POLE 401-121, REPLACED CUTOUT RESTORED POWER AT 14:18./ ISO 37830401B00121/ COD 2/ VER/BOW
22020 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-03-22 05:52 | 2013-03-22 07:30 | 1 | 98 | 4946861 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9 KV CUTOUT//COD 1// VER/DBM IDC XXXX
22021 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2018-09-03 18:57 | 2018-09-03 20:35 | 1 | 98 | 4039421 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole #126-240 which blew line fuse on pole#126-146/// will change cutout /// Changed bad cutout and refused line fuse @ 20:35 and restored service
22022 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-11-11 07:17 | 2013-11-11 08:55 | 1 | 98 | 4027011 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON POLE 11-D-516. VER/SEF
22023 | Hazard | 3303902 | LESLIE | WOOTON | 2020-06-29 14:56 | 2020-06-29 15:45 | 2 | 49 | 4090011 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Replaced blown lightning arrester. Power restored @ 15:45
22024 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-05-18 15:02 | 2021-05-18 15:51 | 2 | 49 | 4596771 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRF IS OUT,WILL RE-FUSE/////////ACTUALLY,XFR CUTOUT WAS BROKEN.I REPLACED IT
22025 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-01-04 11:00 | 2014-01-04 12:38 | 1 | 98 | 4228081 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTIONS OVER HEATING// WILL REPAIR// REPLACED S/D// ALL REPAIRS MADE VER/CRB
22026 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-04-03 19:42 | 2014-04-03 21:20 | 1 | 98 | 4569041 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER POLE VER/CRB
22027 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-01-13 12:09 | 2009-01-13 13:47 | 1 | 98 | 54693-1 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3411902//SERVICER IS INSTALLING AN OVER-HEAD UNTIL TOMORROW WHEN THE UNDERGROUND WILL BE WORKED//SENT TO TIM HALL3411902// WE HAVE AN UNDERGROUND SERVICE AND ONE HOT LEG IS INTO SOMEWHERE FROM TOP OF CONDUIT ON TRANS. POLE TO METER BASE. TIM HALL WANTS ME TO PUT AN OVERHEAD SERVICE IN, AND HE WILL SEND SOME BACK AT A LATER DATE TO FIX PROBLEM. ONE CUSTOMER IS ALL THATS EFFECTED.//VER/CRB L3/KEP IDCC PN436 XXXX
22028 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2009-05-25 21:31 | 2009-05-25 22:20 | 2 | 49 | 65482-1 | 98 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE TRANSFORMER FUSE WAS BROKEN AT THE BOTTOM OF THE CUTOUT DOOR.//VER/CRB IDC XXXX
22029 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-07-30 14:52 | 2018-07-30 16:30 | 1 | 98 | 4872651 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg connection burnt off @ xfm in service drop/// Replaced bad connection and restored service @ 16:30
22030 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2014-01-15 08:22 | 2014-01-15 10:00 | 1 | 98 | 4282871 | 98 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | S/D IS MELTED AT ENTERANCE// WILL MAKE REPAIRS// REPLACED S/D// POWER IS RESTORED/// VER/DBM L3/HFP
22031 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-03-28 14:38 | 2020-03-28 16:15 | 1 | 97 | 4519481 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kva Xfer // replaced and restored @ 1615
22032 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-11-13 17:12 | 2013-11-13 18:49 | 1 | 97 | 4036941 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REWORKED CUST. SER AT HIS SER. ENTERANCE// HE STATED THAT IT SEEMED TO HAVE FIXED HIS PROBLEM VER/CRB
22033 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-12-21 18:26 | 2016-12-21 20:03 | 1 | 97 | 4227881 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN SERVICE WENT BAD , REPLACED SPLICE . ONLY 1 CUST. WITH PART POWER . VER/CRB
22034 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2017-12-28 09:33 | 2017-12-28 11:10 | 1 | 97 | 4684701 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I replaced bad splice at the service mast
22035 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-07-06 11:38 | 2018-07-06 13:15 | 1 | 97 | 4737121 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke. Replaced and restored @ 13:15. sh
22036 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-01-28 18:35 | 2013-01-28 20:12 | 1 | 97 | 4749021 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER , BAD CONNECTION ON POLE 518-41 , REPAIRED CONNECTIONS ON SERVICE RESTORED POWER AT 20:12//COD 1// VER/DBM IDC XXXX
22037 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-05-10 20:53 | 2009-05-10 22:30 | 1 | 97 | 57984-1 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION AT SERVICE DROP ON OPEN WIRE COPPER. ONLY 1 CUSTOMER AFFECTED. VER/KEP L3/KEP
22038 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-05-23 10:53 | 2017-05-23 12:30 | 1 | 97 | 4842161 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | XFMR LEAD FELL OUT OF XFMR . CUST. HAS PART POWER . REPAIRED XFMR . VER/CRB
22039 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2015-12-07 12:08 | 2015-12-07 13:45 | 1 | 97 | 4515851 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED CUTOUT AND REFUSED LINE COD-1 ISO LF 37830330000011 VER/HFP L3/HFP
22040 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-10-20 21:33 | 2014-10-20 23:10 | 1 | 97 | 4647831 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMERS AT 22:42, REMADE CONNECTIONS, CLOSED AT 23:10, NO WIRE DOWN, BAD CONNECTION AT TRANSFORMER. TRANSFORMER LEAKING OIL, NEEDS TO BE REPLACED, CAN WORK WITH TRUCK IF DRY.// EMAILED BRUCE, JIM, AND DOUG///COD 1// ISO37830272B21275// VER/HFP L3/HFP
22041 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-01-10 14:43 | 2010-01-10 16:20 | 1 | 97 | 51751-1 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT WILL TRY IT TO SEE WHAT HAPPENS//// FUSE TAIL BROKE REPLACED FUSE AND RESTORED POWER. TIM MCCOY VER/KEP L3/KEP IDC XXXX
22042 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-02-18 08:37 | 2008-02-18 10:14 | 1 | 97 | 64666-1 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE DROP, MAKING REPAIRS//3404302//VER/CRB IDC XXXX
22043 | South Williamson | 3411401 | DEWEY | INEZ | 2008-08-11 19:08 | 2008-08-11 20:45 | 1 | 97 | 51127-1 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT DOOR FELL OPEN//COD 1// VER/DBM IDC XXXX
22044 | South Williamson | 3411401 | DEWEY | INEZ | 2018-06-18 18:09 | 2018-06-18 19:46 | 1 | 97 | 4617941 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on 766-A-94.replaced cutout .restored power at 19:46
22045 | Paintsville | 3401802 | INDEX | HOSPITAL | 2015-03-22 19:23 | 2015-03-22 21:00 | 1 | 97 | 4217901 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN XFMR FUSE..CHG XFMR FUSE VER/TOM L3/TOM
22046 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2011-12-01 12:23 | 2011-12-01 14:00 | 1 | 97 | 4133231 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE ON WEATHERHEAD WENT BAD == REPLACED == POWER OK /// VER/DBM IDC XXXX
22047 | Whitesburg | 3314401 | MAYKING | ERMINE | 2011-12-10 01:03 | 2011-12-10 02:40 | 1 | 97 | 4166361 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER ,SPLICE BURNED INTO IN SERVICE MADE REPAIRS RESTORED POWER AT 02:40, ONLY ONE CUSTOMER AFFECTED. CC 1. VER/SDB IDC XXXX
22048 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-11-28 19:18 | 2016-11-28 20:55 | 1 | 97 | 4135531 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT. VER/CRB
22049 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-05-22 20:17 | 2010-05-22 21:54 | 1 | 97 | 66420-1 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008003 STS WR # 35236964 IDC XXXX
22050 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-01-11 09:23 | 2022-01-11 11:00 | 1 | 97 | 4335291 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | inulink burned into in secondary//repairs made//restored at 11:00//complete//em
22051 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-09-11 13:38 | 2009-09-11 15:15 | 1 | 97 | 50982-1 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP STS WR# 31680047 // L3/HFP IDC XXXX
22052 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-06-06 14:08 | 2008-06-06 15:45 | 1 | 97 | 59166-1 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT LEG CONNECTION GOT INTO NEUT == BURNED INTO == REPAIRED
22053 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-06-25 13:08 | 2015-06-25 14:45 | 1 | 97 | 4655401 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD CONNECTIONS ON POLE/122-19// VER/ ADH
22054 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-03-08 12:08 | 2021-03-08 13:45 | 1 | 97 | 4314921 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | neutral sleeve pulled apart, repairs made
22055 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-12-23 16:23 | 2022-12-23 18:00 | 1 | 97 | 4328361 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Partial power. Restored at 18:00.
22056 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-12-04 13:23 | 2016-12-04 15:00 | 1 | 97 | 4164111 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 92-474 4/3 SERVICE MELTED ON POLE REPAIRED SERVICE/ ISO 38830092A00474/ COD 1/ VER/BOW
22057 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-03-05 07:58 | 2012-03-05 09:35 | 1 | 97 | 4548701 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | C PHASE XMF FUSE BLOWN, FUSE HAD PULLED LOOSE ON B PHASE XMF APR AT 935 CLOSE TICKET//COD 1// VER/DBM IDC XXXX
22058 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-12-06 22:48 | 2014-12-07 00:25 | 1 | 97 | 4843801 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | GUY/ANCHOR | GUY RUSTED OFF LET POLE LAY OVER & PULL XFMR LEAD INTO TANK AND BURN OFF, ALL REPAIRS MADE AT XFMR, NEED TO SEND NOTE TO ENG. TO REPLACE GUY AT POLR 38831027B00213, OPENED XFMR UP AT 23:55 CLOSED IN AT 00:25 DUPLICATE IN HOIS FOR OTHER 1 CUSTOMER ON XMER FROM 2355 TILL 0025 VER/SEF
22059 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-02-05 07:59 | 2009-02-05 09:36 | 1 | 97 | 55815-1 | 97 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3411801//WILL MAKE REPAIRS IF NECESSARYSERVE-IN HAD FROZEN OUT ON POLE,REPLACED,ALL OK AFTERWARDS//VER/CRB
22060 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-03-14 20:43 | 2019-03-14 22:20 | 1 | 97 | 4985271 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke xfr cutout complete
22061 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-09-17 07:32 | 2008-09-17 09:09 | 1 | 97 | 64749-1 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3116703// PART POWER SERVICE BURNT OF TRANS RISER IDC XXXX
22062 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-02-23 20:32 | 2014-02-23 22:09 | 1 | 97 | 4429201 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE, REPLACED FUSE AND POWER IS BACK ON. //VER/GAH
22063 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-02-22 11:43 | 2018-02-22 13:20 | 1 | 97 | 4872621 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse appeared to have fallen open, fuse not blown. closed fuse and restored power/ ISO 37830473000242/ COD 1
22064 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2020-07-11 16:18 | 2020-07-11 17:55 | 1 | 97 | 4153161 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t fuse out due to bad cutout. changed cutout closed transformer fuse back in @ 17:55 everything ok
22065 | South Williamson | 3411401 | DEWEY | INEZ | 2016-12-18 15:28 | 2016-12-18 17:05 | 1 | 97 | 4216831 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE XFMR CUTOUT//REPAIRS MADE RESTORED AT 17:05//COMPLETE//EM/ ISO 38820721B00006/ COD 1/ VER/BOW
22066 | South Williamson | 3411401 | DEWEY | INEZ | 2008-11-13 16:59 | 2008-11-13 18:36 | 1 | 97 | 64670-1 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP JRV ON SITE @ 17:40......GREEN POLE FIRE FROM BAD CUTOUT..POLE 792D110.....CAN WORK W/ TRUCK...WILL CLEAR BAD CUTOUT, EXTINGUISH FIRE, AND REPLACE CUTOUT IDC XXXX
22067 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-02-11 20:45 | 2008-02-11 22:22 | 1 | 97 | 60513-1 | 97 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3003703//FOUND TRANSFORMER LEG BURNT INTO I REPLACED WITH NEW ONE,,,BACK TO NORMAL AT 22:22// VER/TOM IDC XXXX
22068 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2013-04-05 09:24 | 2013-04-05 11:00 | 1 | 96 | 4981111 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. REPLACING. RESTORED @ 11:00. SH ///VER/CRB L/3 /CRB IDC XXXX
22069 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-01-09 12:24 | 2019-01-09 14:00 | 1 | 96 | 4651041 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection at house, all repairs made power restored//COD 1
22070 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-07-18 09:36 | 2011-07-18 10:08 | 3 | 32 | 4557001 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED XMF AT 0936. TIME ON WAS 0956. RESAGGED TWO SERVICE DROPS CLOSE TICKET//COD 3// VER/DBM
22071 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-06-30 09:12 | 2013-06-30 10:00 | 2 | 48 | 4429771 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 139-224 BAD CUTOUT REPLACED VER/CRB L/3 CRB
22072 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2017-07-25 03:02 | 2017-07-25 03:50 | 2 | 48 | 4176331 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT THREE CUTOUTS (TWO BROKEN) ON THREE PHASE RISER POLE AT PAUL BLAZER HIGH SCHOOL,,BLR VER/ARN L3/HFP HFPC CDC83
22073 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-12-18 14:09 | 2016-12-18 15:45 | 1 | 96 | 4216341 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , I CHANGED IT OUT/ ISO 37830519D00028/ COD 1/ VER/BOW
22074 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2022-05-26 08:25 | 2022-05-26 10:01 | 1 | 96 | 4950771 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 19.9 cutout on pole 272-B2-1285, I isolated the other two cutouts in an attempt to save this pole from burning, opened at 8:25. Calling for a crew to replace these cutouts and T-brackets. Released by crew 077S04.repairs comp
22075 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2009-08-01 21:24 | 2009-08-01 23:00 | 1 | 96 | 58069-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402802/// XFMR CUTOUT DOOR BURNT UP. REPLACED DOOR AND RE-FUSED XFMR. SH IDC XXXX
22076 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-06-06 19:22 | 2008-06-06 20:58 | 1 | 96 | 59382-1 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | I WILL HAVE TO REPLACE SERVICE DROP. 4-3 SERVICE DROP NEUTRAL BURNT INTO CUST SAID HE HAD SOME DAMAGE. MICROWAVE AND GASH REGISTER. METER SHOWS 29.2 KW ON 25 KVA TRANSFORMER. TRANSFORMER ALSO HAS ANOTHER 200AMP ON IT SEND COPY OF THIS TO ENG PIKEVILLE . TRANSFORMER FEELS HOT. I REPLACED 4-3 DROP WITH 2-3 DROP. VER/ARN
22077 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-10-14 14:27 | 2009-10-14 15:15 | 2 | 48 | 62824-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT HAS FAILED // REPLACED BROKEN 7200 VOLT 15 KV XFMR CUTOUT VER/TOM IDC XXXX
22078 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-09-01 19:12 | 2016-09-01 19:44 | 3 | 32 | 4862271 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMER 44-6071 RESTORED. 3 CUSTOMER 504,505,513./ VER/BOW L3/HFP XXXHFP
22079 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-02-14 09:09 | 2011-02-14 10:45 | 1 | 96 | 56681-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CLF BAD---REMOVED BAD CLF//VER/CRB IDC XXXX
22080 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-09-26 12:40 | 2014-09-26 13:12 | 3 | 32 | 4530731 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HANGER LOOSE ON TRANSFORMER/// CHANGING THE TRANSFORMER 37830143C00053 OPENED AT 1240 CLOSED AT 1312// VER/BOW
22081 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-11-20 16:47 | 2010-11-20 17:35 | 2 | 48 | 58383-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 37840541 // OPENED LINE FUSE @ 1720 STS WR# 37840541 // REPLACED BAD CUT OUT DOOR. SEE H58383-1 FOR FUSE OUTAGE OF 5 CUST VER/HFP L3/HFP IDC XXXX
22082 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-07-18 21:24 | 2011-07-18 23:00 | 1 | 96 | 4560301 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 236-109. RELEASED BY CREW 078S01 COD-1 ISO TF 38830236000109 VER/HFP L3/HFP
22083 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2020-12-10 20:12 | 2020-12-10 21:00 | 2 | 48 | 4760131 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on pole
22084 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-09-29 13:24 | 2021-09-29 15:00 | 1 | 96 | 4302861 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | power quality issue// trans putting out too much voltage rick maggard will be coming to replace trans..replaced xfmr restored @ 15:00..
22085 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2014-10-07 14:24 | 2014-10-07 14:48 | 4 | 24 | 4565641 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER CHANGING OUT BAD TRANFORMER ON POLE 68-428//,,CREW ON SITE,,TRANSFORMER REPLACED,,ALL POWER RESTORED// COD 4// VER/ ADH
22086 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2009-03-02 08:39 | 2009-03-02 10:15 | 1 | 96 | 53728-1 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3403801//A CONNECTION FAILED AT THE TRANSFORMER ON ONE OF THE HOT LEGS.//VER/CRB IDC XXXX
22087 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-03-05 20:29 | 2009-03-05 22:05 | 1 | 96 | 55503-1 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD SPLICE ON SEC LASH L3/HFP IDC XXXX
22088 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-05-19 00:01 | 2018-05-19 01:37 | 1 | 96 | 4374591 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, burnt off 9 arm @ 38830020C34588==opened LF on 38830020C45567 @ 00:01--T&G to RMV--replaced arm---closed 3 cutouts 20-5567 @ 01:37---tbl tkt comp.---rmv
22089 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-03-08 20:55 | 2013-03-08 22:31 | 1 | 96 | 4891931 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLIT BOLT CONNECTORS ON SERVICE GOT HOT AND MELTED SERVICE, I HAD TO REPLACE ABOUT TWENTY FEET OF # 2-3 SERVICE WIRE ///VER/CRB L/3 CRB IDC XXXX
22090 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2022-11-30 17:07 | 2022-11-30 17:55 | 2 | 48 | 4214531 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse failed. Power restored at 17:55.
22091 | Pikeville | 3402003 | KEYSER | MULLINS | 2013-07-22 13:49 | 2013-07-22 15:25 | 1 | 96 | 4575921 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A&C FUSES BLOWN ON 38831127A00302// 1 FUSE BLOWN & 1 CUTOUT BROKEN ON 38831127A00450// WILL REPAIR/// REPLACED 3 CUTOUTS// OPENED AT 14:20// CLOSED AT 15:25//? IDCC CNT7 XXXX
22092 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-10-31 21:34 | 2013-10-31 23:10 | 1 | 96 | 4980541 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE BURNT DOWN IN TREE REPAIRED OPENED TRANS. 10 ;20 TO 11: 10//COD 1 (+ 2.. SEE H4980541) // VER/DBM
22093 | Whitesburg | 3314401 | MAYKING | ERMINE | 2011-07-28 16:39 | 2011-07-28 18:15 | 1 | 96 | 4635101 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS.FUSE OUT WILL REFUSE BAD 15 KVA 7200 NEED 1 MAN BIG BUCKET WILL WORK ON OPS ORDER#037194375 W.R.#41026802//COD 1// VER/DBM IDC XXXX
22094 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-06-02 16:34 | 2020-06-02 18:10 | 1 | 96 | 4945761 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR 37830458C40395, 277v/137v at meter, changed xfmr, new one 124v/248v all power restored @ 18:10.p.hicks
22095 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-11-22 15:59 | 2014-11-22 17:35 | 1 | 96 | 4754321 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL PULLED OUT OF SLEEVE. REPAIRED AND RESTORED POWER AT 17:35. 11/22/2014//COD 3// VER/ ADH AJBC CNT3
22096 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2018-02-16 22:58 | 2018-02-16 23:30 | 3 | 32 | 4853521 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
22097 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-12-26 22:27 | 2008-12-26 23:15 | 2 | 48 | 64223-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008702 - WR#27808758 6T ME FUSE LINK BROKE //VER/GAH L3/KEP IDC XXXX
22098 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2015-05-30 08:18 | 2015-05-30 09:54 | 1 | 96 | 4484211 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | APPEARS TO BE A SECONDARY SERVICE POLE CONNECTION GONE BAD,WILL REPAIR/////////MADE NECESSARY REPAIRS AND RESTORED,ALL OK AFTERWARDS/////WAS A 480V SERVICE
22099 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-03-23 16:24 | 2022-03-23 18:00 | 1 | 96 | 4663351 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew reqd/truck ok/no flaggers/cross arm & cutout broken on pole 38830092A00738/send to B. Tackett Released by crew 078S04repairs made all cust restored @1800 please close ticket thanks.bt
22100 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-10-27 12:14 | 2010-10-27 13:50 | 1 | 96 | 65708-1 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST CONDUIT CLAMP WAS BENT PORCELAIN BROKEN. LOOKS LIKE SERVICE DROP MAY HAVE BEEN REAL TIGHT. NEUTRAL BROKEN ABOUT 2 FOOT FROM CONDUIT. THIS IS A 2/3 DROP 200AMP. I CUT SLACK IN NEUTRAL AND CONNECT NETURAL EVERYTHING OK. CUST SAID THEY HAVE BEEN HAVING TROUBLE WITH TV. SEND COPY TO DAMAGE CLAIMS JUST IN CASE THEY CALL IN. VER/KEP L3/KEP IDCC FP0 XXXX
22101 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-12-29 07:54 | 2017-12-29 09:30 | 1 | 96 | 4687041 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o failed--replaced-ds122917
22102 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-03-31 08:39 | 2011-03-31 10:15 | 1 | 96 | 60770-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39381658 // BAD CUTOUT ON POLE 351-408, REPLACED CUTOUT RESTORED POWER AT 10:15 COD-1 ISO TF 37830351C00408 VER/HFP L3/HFP IDC XXXX
22103 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-02-21 10:42 | 2017-02-21 12:18 | 1 | 96 | 4411711 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN,WILL REPLACE IT//////////REPLACED CUTOUT&RESTORED/ ISO 38830984A20187/ COD 1/ VER/BOW L3/HFP XXXHFP
22104 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-01-25 16:14 | 2014-01-25 17:50 | 1 | 96 | 4312721 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGED OUT BAD ARRESTER. COD-1 ISO TF 38830235000166 VER/HFP L3/HFP IDC XXXX
22105 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-01-04 07:36 | 2008-01-04 09:12 | 1 | 96 | 53548-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL PULLED OUT OF SLEEVE ON SERVICE DROP, HAVE REPAIRS MADE AND SERVICE IS RESTORED AT THIS LOCTION// VER/TOM IDC XXXX
22106 | Pikeville | 3407103 | TOPMOST | KITE | 2017-04-26 14:02 | 2017-04-26 15:38 | 1 | 96 | 4684741 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SQUEEZE ON FAILED. MAKING REPAIRS.SQUEEZEON BURNT OPEN ON OPEN WIRE @ POLE 234 -8 I WILL MAKE REPAIRS.PULLED METER TO TAKE LOAD OFF SECONDARY @ 15:19 AND RESTORED @ 15:38 37830234000008 VER/AWD L3/HFP XXXHFP
22107 | South Williamson | 3411401 | DEWEY | INEZ | 2011-08-24 18:17 | 2011-08-24 19:05 | 2 | 48 | 4753011 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED APART IN NEWLY INSTALLED CUTOUT//MUST HAVE BEEN TIGHTENED TO0 TIGHT//REFUSED AT 19:05//COMPLETE//EM//COD 2//ISO 38830815B00142// VER/DBM IDC XXXX
22108 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2022-11-17 15:44 | 2022-11-17 17:20 | 1 | 96 | 4155911 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | Primary neutral tie wire was damaged in a recent storm causing neutral to shift and rub service neutral loop in two over time. Repaired tie wire, reworked all connections on pole 811-144. sh
22109 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-10-07 17:15 | 2012-10-07 18:51 | 1 | 96 | 4121911 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE///////REPLACED CUTOUT AND RESTORED,ALL OK AFTERWARDS//COD 1 IDC XXXX
22110 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-05-15 11:12 | 2012-05-15 12:00 | 2 | 48 | 4797201 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP. I AM GOING TO REPLACE DOOR. I CHANGED DOOR. VER/KEP IDC XXXX
22111 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-05-16 08:55 | 2012-05-16 09:27 | 3 | 32 | 4799881 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICER OPENED FUSE IN ORDER TO RESAG CONDUCTORS SAFELY//OPENED FUSE @ 0855 // COD 3// RESAGGED CONDUCTOR CLOSED FUSE AT 0927 APR CLOSE TICKET// VER/DBM IDC XXXX
22112 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-05-09 18:24 | 2015-05-09 20:00 | 1 | 96 | 4406891 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SLEEVE IN NEUT. HAD FAILED @ POLE // REPAIRED NEUT.// ALL OK// VER/ ADH
22113 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-10-17 22:57 | 2020-10-18 00:33 | 1 | 96 | 4564851 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, made repairs..
22114 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2022-02-20 17:54 | 2022-02-20 19:30 | 1 | 96 | 4521101 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad neutral connection @ xfm///Replaced bad connection///Opened xfm @ 19:15 and closed back in @ 19:30 and restored service///Everything ok now
22115 | Hazard | 3311102 | STINNETT | BEECH FORK | 2018-08-18 12:30 | 2018-08-18 14:06 | 1 | 96 | 4968841 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | PRIMARY METER CAN BLEW UP ON 579-148 OPEN SWITCH's TO Primary Metering AND CLOSED BYPASSES /// VERIFIED TIMES PER SCADA & DOL - L3/HFP
22116 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-01-16 11:37 | 2008-01-16 13:13 | 1 | 96 | 57129-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3404302//MADE NECESSARY REPAIRS TO SERVICE DROP,ALL OK AFTERWARDS// SERVICE OUTAGE// 38821060C00098// COULD NOT ENTER FETR DUE TO ORDER TYPE// VER/TOM IDC XXXX
22117 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-02-28 17:16 | 2008-02-28 18:04 | 2 | 48 | 51318-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BLOWN XFMR FUSEBROKEN FUSE//3116102//VER/CRB IDC XXXX
22118 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-03-25 07:54 | 2014-03-25 09:30 | 1 | 96 | 4523451 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL CHECK FOR PROBLEMS///////////CURRENT LIMITING F HAD BURNED OUT,LET LEAD FALL ONTO LA AND BURNED IT OUT ALSO.WAS MAKING CONTACT INTERMIDATELY AND ARCING.MADE NECESSARY REPAIRS AND RESTORED,ALL OK AFTERWARDS VER/CRB IDC XXXX
22119 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-11-10 13:36 | 2011-11-10 14:00 | 4 | 24 | 4065341 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW FOUND BAD CUTOUT & CHANGED SAME ///VER/CRB IDC XXXX
22120 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-08-11 18:18 | 2010-08-11 18:30 | 8 | 12 | 52869-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SAME AS 52749//VER/CRB IDC THIS WAS NOT A DUPLICATE THIS WAS OPENING LINE FUSE XXXX
22121 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-01-03 11:12 | 2012-01-03 12:00 | 2 | 48 | H4228161 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PART OF 4228161//BAD UNDERGROUND SERVICE RELEASED BY CREW 077S04BAD UNDERGROUND SERVICE ---OPENED TRANSFORMER AT 11:12 CLOSED AT 12:00 -- OPENED AT 14:10, CLOSED AT 14:25 SPLICED WIRE, POWER RESTORED.// + 2 // VER/DBM IDC XXXX
22122 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-01-29 16:39 | 2008-01-29 18:15 | 1 | 96 | 60746-1 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312202// BAD CUTOUT == REPLACED CUTOUT ==//COD 1// VER/DBM IDC XXXX
22123 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2016-07-23 12:37 | 2016-07-23 13:25 | 2 | 48 | 4670501 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACE BAD SERVE IN ON HOT LEGS, RESTORED VER/AWD
22124 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-12-17 14:03 | 2022-12-17 14:35 | 3 | 32 | 4272711 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester was blown on xforner pole 882-C-414 causeing xformer fuse to blow cut arrester loss and got xformer fuse at pole 882-C-414 restored at a time of 14:35
22125 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-04-15 10:36 | 2020-04-15 11:00 | 4 | 24 | 4693101 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | low service nuetral broke xfm off@ 10:36 on @ 11:00. Repairs made
22126 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2013-02-22 10:54 | 2013-02-22 11:42 | 2 | 48 | 4839731 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 FUSE OUT IN BANK--BROKEN FUSE LINK ///VER/CRB L/3 CRB IDCC CCU XXXX
22127 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2021-10-11 12:54 | 2021-10-11 14:30 | 1 | 96 | 4340511 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced cutout door
22128 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-03-05 16:39 | 2013-03-05 18:15 | 1 | 96 | 4872641 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT IS BROKEN INTO ON POLE 167-383. IT IS TOO CLOSE TO CHANGE HOT. DAVE LEWIS IS GOING TO OPEN RECLOSERS ON POLE 144-380 LONG ENOUGH FOR ME TO CHANGE CUTOUT. WE WILL CALL JUST B4 OPENING RECLOSERS. I OPENED RECLOSER AT 18:00, CHANGED CUTOUT, AND CLOSED RECLOSER IN AT 18:15. RELEASED BY CREW 074S01//SEE OTHER TICKET ///VER/CRB L/3 CRB IDC XXXX
22129 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-11-20 15:29 | 2015-11-20 17:05 | 1 | 96 | 4475061 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BAD XFMR CUTOUT. RESTORED @ 17:05. SH VER/CRB
22130 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-06-25 09:36 | 2017-06-25 11:12 | 1 | 96 | 4042841 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED DOOR 38830329000126 VER/AWD
22131 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-12-03 07:21 | 2008-12-03 08:57 | 1 | 96 | 54112-1 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION AT WEATHERHEAD//3001002//VER/CRB L3/KEP IDC XXXX
22132 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-12-21 18:04 | 2011-12-21 19:40 | 1 | 96 | 4194031 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 70-1053 HOT TAP BURNT OFF B PHASE ///VER/CRB IDC XXXX
22133 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-11-09 07:19 | 2012-11-09 08:55 | 1 | 96 | 4375971 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE AND OPENED DOOR.. REFUSED AND CLOSED BACK IN AT 8:55 .. COMPLETE.. ///VER/CRB L/3 CRB IDC XXXX
22134 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2020-05-31 17:55 | 2020-05-31 18:19 | 4 | 24 | 4937371 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad secondary connection on pole 248C-498, XFMR off from 18:13 to 18:19.
22135 | Pikeville | 3401001 | ELWOOD | DORTON | 2019-11-09 10:19 | 2019-11-09 11:55 | 1 | 96 | 4014681 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Serv -end burnt out in service drop/// Replaced bad connection and restored full power @ 11:55
22136 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-02-11 16:09 | 2015-02-11 17:45 | 1 | 96 | 4008821 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN WILL RE-FUSE//// CUTOUT IS BROKE ON POLE #38831101D40620 WILL REPLACE//// REPLACED BAD CUTOUT AND RESTORED SERVICE @ 17:45 VER/CRB L3/HFP XXX
22137 | Hazard | 3309002 | JEFF | JEFF | 2016-04-03 09:17 | 2016-04-03 10:53 | 1 | 96 | 4040711 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HOT LINE CLAMP BURNED OFF ON PRIMARY METERING === REPAIRED AND REFUSED LINE POWER OK VER/CRB
22138 | South Williamson | 3411401 | DEWEY | INEZ | 2015-08-16 14:27 | 2015-08-16 15:15 | 2 | 48 | 4140431 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD BROKE IN CUTOUT DOOR//CUTOUT WAS RECENTLY CHANGED AND FUSE WAS PROBABLY TIGHTENED TO TIGHT// VER/CRB
22139 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-02-23 12:04 | 2014-02-23 13:40 | 1 | 96 | 4428111 | 96 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN, AT SER, LOOP TO WEATHER HEAD// VER/DBM
22140 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-10-16 11:24 | 2021-10-16 13:00 | 1 | 96 | 4356051 | 96 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired connection
22141 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2011-03-31 13:55 | 2011-03-31 15:30 | 1 | 95 | 60905-1 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 10 KVA TRANS. IS BAD. ALL THIS SERVES IS BOOSTER FOR INTERMOUNTAIN CABLE. I CALLED THEM AND THEY SAID NO ONE WAS WITHOUT TV AND WE COULD WAIT UNTIL TOMORROW TO CHANGE IT. I TALKED TO DAVE SAMMONS AND HE SAID HE WOULD SEND A CREW FIRST THING TOMORROW TO CHANGE TRANS. ONLY 1 METER ON THIS TRANS. COD-1 ISO TF 38831078000027 VER/HFP L3/HFP IDCC PN26 XXXX
22142 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-11-04 08:05 | 2012-11-04 09:40 | 1 | 95 | 4354551 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY BURNED INTO..BAD CONNECTION.TOOK XFMR OFF AT 9.15.BACK ON 9.40.. COD-6 ISO TF 38830851B00083 SEE H4354551 FOR 5 CUST /// VER/HFP L3/HFP IDC XXXX
22143 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-09-13 12:15 | 2012-09-13 13:50 | 1 | 95 | 4045761 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD., POWER RESTORED. ///VER/CRB L/3 CRB IDC XXXX
22144 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-03-15 18:52 | 2020-03-15 20:27 | 1 | 95 | 4480541 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr, restored power at 20:27..
22145 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-04-29 08:40 | 2020-04-29 10:15 | 1 | 95 | 4764801 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service neutral broken, repaired
22146 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2019-02-15 11:55 | 2019-02-15 13:30 | 1 | 95 | 4797291 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt open in secondary on pole 171-82 /// will make repairs//only 1 customer affected/// Replaced bad connections in secondary and restored sevice @ 13:30
22147 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2020-09-21 08:35 | 2020-09-21 10:10 | 1 | 95 | 4481441 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on secondary pole. Replaced connection and restored @ 10:10. sh
22148 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-03-01 13:50 | 2009-03-01 15:25 | 1 | 95 | 52781-1 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3110903/RESQUEEZED VER/KEP L3/KEP IDC XXXX
22149 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2010-01-01 18:37 | 2010-01-01 20:12 | 1 | 95 | 56133-1 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ON SITE, CHECKING TROUBLE, BAD SPLICE IN SERVICE DROP VER/HFP L3/HFP IDC XXXX
22150 | Hazard | 3302703 | HAZARD | HAZARD | 2019-05-08 07:24 | 2019-05-08 08:59 | 1 | 95 | 4238411 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer out 37830296A30754 not 37830272B40315,fuse broke
22151 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-04-08 17:40 | 2019-04-08 19:15 | 1 | 95 | 4071891 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | riser is burnt off stirrup, replaced cutout and arrester, power restored
22152 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2009-08-23 15:40 | 2009-08-23 17:15 | 1 | 95 | 61410-1 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT. LOOKS LIKE FUSE MAY HAVE BROKE. FUSED UP EVERYTHING OK. VER/KEP L3/KEP IDC XXXX
22153 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-08-14 13:49 | 2011-08-14 15:24 | 1 | 95 | 4708241 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//COD 1// VER/DBM IDCC FEC49 XXXX
22154 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2012-06-27 20:00 | 2012-06-27 21:35 | 1 | 95 | 4969431 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT //VER/CRB L/3 CRB
22155 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-01-17 05:46 | 2020-01-17 07:21 | 1 | 95 | 4314781 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced bad connections
22156 | Pikeville | 3401001 | ELWOOD | DORTON | 2014-12-06 11:04 | 2014-12-06 12:39 | 1 | 95 | 4840291 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #4 SECONDARY BURNED DOWN DUE TO A CONNECTION HEATING. OPENED TRANSFORMER AT 1229 CLOSED AT 1239//THIS CAUSED 3 OTHERS OUTAGE//ORGINAL WAS 1 VER/CRB
22157 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-01-23 13:38 | 2008-01-23 15:13 | 1 | 95 | 59218-1 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308401// CUST HAS PART POWER, BAD CONNECTION ON XFMR POLE, CUST DIDNT EVEN KNOW IT VER/KEP IDC XXXX
22158 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-08-09 15:39 | 2015-08-09 17:14 | 1 | 95 | 4114001 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG CONNECTION @ WEATHERHEAD/ ISO 38830118B00041/ COD 1/ VER/BOW
22159 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-08-28 12:00 | 2020-08-28 13:35 | 1 | 95 | 4392891 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced a broken cutout on pole 458-41 and power restored at 13:35.
22160 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-06-22 12:25 | 2019-06-22 14:00 | 1 | 95 | 4568091 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 211-198 hot line clamp got loose and fell apart had to install new one. back on at 14:00
22161 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-03-19 12:25 | 2008-03-19 14:00 | 1 | 95 | 58562-1 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FEEDER PLEASE// SERVEN FAILED ON HOT LEG OF SERVICE DROP. WATER WAS ABLE TO ENTER AND CAUSE FREEZE OUT .// VER/TOM IDC XXXX
22162 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-03-11 17:22 | 2010-03-11 18:57 | 1 | 95 | 65205-1 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED NEUTRAL,TENSION SLEEVE HAD PULLED APART,NO OBVIOUS REASON.POSSIBLE DAMAGES HERE,NOBODY HOME.FLAG TICKET FOR PEGGY WYESONG ?//EMAILED TO P WYSONG // VER/DBM IDC XXXX
22163 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-10-20 14:25 | 2014-10-20 16:00 | 1 | 95 | 4646831 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SINGLE ALL OUT BROKEN FUSE LINK REPLACED 6-T POWER ON KWB VER/CRB
22164 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2017-05-23 17:20 | 2017-05-23 18:55 | 1 | 95 | 4844001 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 401-252, REPLACED CUTOUT RESTORED POWER AT 18:55.. 37830401A00252 1 VER/AWD
22165 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2018-12-10 10:25 | 2018-12-10 12:00 | 1 | 95 | 4543111 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed in 1/0 secondary. Restored at 12:00. sh L3/HFP
22166 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2021-09-16 12:40 | 2021-09-16 14:15 | 1 | 95 | 4248181 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced old door
22167 | South Williamson | 3200301 | BELFRY | BELFRY | 2014-12-11 21:31 | 2014-12-11 23:06 | 1 | 95 | 4855511 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK FOR PROBLEM/////////XFR CUTOUT WAS BROKEN,REPLACED IT AND RESTORED POWER VER/ARN
22168 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-02-05 15:25 | 2014-02-05 17:00 | 1 | 95 | 4358791 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TAP CUTOUT ON POLE 38821060A00008. NO TRUCK, I CAN REPLACE IT. REPLACED BAD CUTOUT, POWER IS BACK ON. VER/TOM L3/TOM
22169 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2010-10-04 08:45 | 2010-10-04 10:20 | 1 | 95 | 56566-1 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A SPLICE IN THE SERVICE DROP BURNED APART UNDERNEATH SOME TAPE. ONLY ONE CUSTOMER AFFECTED. VER/KEP L3/KEP IDC XXXX
22170 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2010-06-03 12:05 | 2010-06-03 13:40 | 1 | 95 | 55899-1 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 38830305000016 VER/KEP L3/KEP IDC XXXX
22171 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-11-29 08:40 | 2020-11-29 10:15 | 1 | 95 | 4727741 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 10:15. sh
22172 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-12-12 20:30 | 2013-12-12 22:05 | 1 | 95 | 4157891 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNT UP WILL REPAIR. REPLACED BAD CURRENT LIMITING FUSE RESTORED SERVICE. GOOD VOLTAGE 122/122/244//COD 1 VER/HFP L3/HFP
22173 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-12-25 23:35 | 2010-12-26 01:10 | 1 | 95 | 55728-1 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER BAD SPLICE IN SERVICE , MADE REPAIRS RESTORED POWER AT 01:10 VER/PDP IDC XXXX
22174 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2022-11-18 22:15 | 2022-11-18 23:50 | 1 | 95 | 4160771 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customer service drop burnt up. One customer off. Repaired
22175 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-04-26 15:04 | 2018-04-26 16:39 | 1 | 95 | 4282151 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Old barrel connection going bad at customers weatherhead, will be making repairs. Made repairs @1639. Only 1 cust. was affected./ ISO 38831101D40285/ COD 1 L3/HFP
22176 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2019-07-08 16:11 | 2019-07-08 17:46 | 1 | 95 | 4678531 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | trans is leaking.need crew to replace it.possible trk app but not sure.25 kva 7200. Released by crew 079H03 off @ 1611 on @ 1746
22177 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2018-01-07 17:35 | 2018-01-07 19:10 | 1 | 95 | 4718901 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service drop burnt down,,,replaced complete/ ISO 38830305000085/ COD 1
22178 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-11 11:00 | 2018-02-11 12:35 | 1 | 95 | 4828661 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 791-132//repairs made//restored at 12:35//complete//em
22179 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2020-03-05 17:58 | 2020-03-05 19:33 | 1 | 95 | 4454971 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 38830400000069 35/6 ky pole rotten at the top of ground--has a old 15kva 7200 tran feeding cust..crew req ..by trk--ds030520 Released by crew 078S01//arrived RM open xfm@17:58 closed @ 19:33 WO to be wrote please close tic RM//NO OUTAGE TILL FUSE OPENED
22180 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-11-18 08:10 | 2009-11-18 09:45 | 1 | 95 | 50362-1 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT. IDC XXXX
22181 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2016-01-22 07:42 | 2016-01-22 09:17 | 1 | 95 | 4640291 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 401-252, REPLACED CUTOUT RESTORED POWER AT 09:17../ ISO 37830401A00252/ COD 1/ MD DONE METER #435943974/ VER/BOW
22182 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-10-18 21:26 | 2010-10-18 23:01 | 1 | 95 | 60834-1 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 37379953 // REWORK SER. DROP. M.P RELEASED BY CREW 078H12 VER/HFP L3/HFP IDCC PN4076 FP NULL XXXX
22183 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2022-05-26 21:00 | 2022-05-26 22:35 | 1 | 95 | 4955811 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | cutout broke, wont stay closed at pole 46b2292/crew reqd truck ok/no flaggers needed. Released by crew 078S04,repairs made all cust restored Please close ticket thanks.bt
22184 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-04-15 12:05 | 2021-04-15 13:40 | 1 | 95 | 4453521 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | cust has a prb with UG conductor between home and pole 1008-99..paul lane is coming to help. Released by crew 079S03
22185 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2017-12-07 21:16 | 2017-12-07 22:51 | 1 | 95 | 4629431 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no power in house or outdoor light broke cutout/ ISO 37830032000002/ COD 1
22186 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-11-10 20:00 | 2015-11-10 21:35 | 1 | 95 | 4426561 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION BURNED THE #2 SECONDARY DN. I HAVE COMPLTED REPAIRS. ONE CUSTOMER AFFECTED. VER/KEP
22187 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2022-11-04 12:50 | 2022-11-04 14:25 | 1 | 95 | 4097991 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad secondary connection. Restored at 14:25.
22188 | Hazard | 3311103 | STINNETT | WENDOVER | 2015-07-06 11:40 | 2015-07-06 13:15 | 1 | 95 | 4731091 | 95 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION
22189 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-01-13 01:25 | 2017-01-13 03:00 | 1 | 95 | 4293481 | 95 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD XFM CUTOUT ON POLE 213-178..OPENED LINE FUSE ON POLE 213-175 @ 01:25 MADE REPAIRS AND CLOSED BACK IN @ 03:00.RESTORED. NO OUTAGE TILL FUSE OPEN VER/KEP L3/HFP HFP
22190 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-12-15 10:27 | 2017-12-15 12:01 | 1 | 94 | 4651301 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad splice in service wire made repairs./ ISO 37830353A00126/ COD 1
22191 | Hazard | 3309302 | VICCO | JEFF | 2022-02-24 17:26 | 2022-02-24 19:00 | 1 | 94 | 4541431 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hot leg open in sevice. meter blank,changed meter
22192 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-01-19 12:58 | 2018-01-19 14:32 | 1 | 94 | 4757321 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke-replaced in at 14:32-allgood-ds011918
22193 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-08-10 08:13 | 2012-08-10 09:00 | 2 | 47 | 4922461 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK COD-2 ISO TF 38830245B00193 VER/HFP L3/HFP IDC XXXX
22194 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-01-18 20:43 | 2010-01-18 21:30 | 2 | 47 | 56261-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33487182 // POLE 1123-6065 BAD CUTOUT DOOR AND 6T CHANCE FUSE BROKE VER/HFP L3/HFP IDCC PN60604 XXXX
22195 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-10-18 19:21 | 2014-10-18 20:55 | 1 | 94 | 4643251 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT/ ISO 37830306000097/ COD 1 VER/SEF
22196 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2018-11-25 08:31 | 2018-11-25 10:05 | 1 | 94 | 4474961 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout door replaced all pwr restored.. please close ticket LRM/ 38830018000076/ 1 L3/HFP
22197 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2011-03-24 17:18 | 2011-03-24 18:52 | 1 | 94 | 59015-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2150105--PART OF 58295-1 // OPENED REC 1017B-443A TAKEN OUT 54 CUST // OFF 1718 // ON 1852 VER/BRM IDC XXXX
22198 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-12-27 12:41 | 2013-12-27 14:15 | 1 | 94 | 4205021 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1-8T XFMER FUSE OUT ON 2 CAN BANK..RESTORED @ 14:15 MP COD-1 ISO TF 38830070B33071 VER/HFP L3/HFP
22199 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-10-01 09:41 | 2022-10-01 11:15 | 1 | 94 | 4955631 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout
22200 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-08-21 17:11 | 2019-08-21 18:45 | 1 | 94 | 4923251 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke // replaced and restored power @ 1845
22201 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-02-05 11:47 | 2010-02-05 13:21 | 1 | 94 | 63476-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE IDC XXXX
22202 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-10-05 11:20 | 2016-10-05 12:54 | 1 | 94 | 4961741 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT 1 CUST BAD CUT-OUT CHG OUT POWER RESTORED KWB COD-1 ISO TF 38830279000155 VER/HFP L3/HFP
22203 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2018-12-20 12:03 | 2018-12-20 12:50 | 2 | 47 | 4582571 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 447-167, replaced cutout restored power at 12:50. L3/HFP
22204 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-07-06 15:11 | 2010-07-06 16:45 | 1 | 94 | 62684-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE BURNT INTO AT SECONDARY POLE, NO VISIBLE REASON. CHANGED SERVICE DROP// VER/DBM IDC XXXX
22205 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-01-25 15:51 | 2016-01-25 17:25 | 1 | 94 | 4649721 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FAILED CONNECTION ON XFMR RISER TO 1/0 SECONDARY. THREE CUSTOMERS AFFECTED - PART OUT. OPENED XFMR 882-149 @ 16:50, REWORKED CONNECTIONS AND CLOSED @ 17:25 RESTORING ALL OUTAGED CUSTOMERS. SH RELEASED BY CREW 076S02// VER/ ADH
22206 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2017-08-13 14:16 | 2017-08-13 15:50 | 1 | 94 | 4255681 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE BAD LEG ON SECONDARY UNDERGROUND/ CALL EDDIE MATNEY BEFORE GOING ON THIS SO HE CAN SHOW YOU WERE SEPTIC TANK IS/ WILL NEED SMALL SERVIVE BUCKET/ FINE TO HOLD FOR MONDAY PER CUSTOMER OPS 032991129 RELEASED BY CREW 079S02/ VER/BOW
22207 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-02-10 17:13 | 2011-02-10 18:00 | 2 | 47 | 55983-1 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION MIDSPAN ON OUR 1/0 SECONDARY. I REPLACED THE CONNECTION.//VER/CRB IDC XXXX
22208 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-03-14 19:33 | 2016-03-14 20:20 | 2 | 47 | 4847131 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGE ARRESTOR ON POLE 38831111000015/ ISO 38831111000015/ COD 2/ VER/BOW
22209 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-09-09 02:36 | 2008-09-09 04:10 | 1 | 94 | 60514-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/ARN IDC XXXX
22210 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2019-06-18 10:41 | 2019-06-18 12:15 | 1 | 94 | 4536231 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | restored xfmer in xfmer bank
22211 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-03-11 17:18 | 2010-03-11 18:52 | 1 | 94 | 65203-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HAVE A BAD CUTOUT ON POLE 37820074000161 THIS IS A TRANSFORMER CUTOUT I WILL REPLACE.REPLACED CUTOUT AND LIGHTING ARRESTOR AND RESTORED POWER AT 18:52 TIM MCCOY //COD 1// VER/DBM IDC XXXX
22212 | Pikeville | 3403001 | PIKEVILLE | CITY | 2010-03-26 10:41 | 2010-03-26 12:15 | 1 | 94 | 54650-1 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURN-IN TWO//VER/CRB IDC XXXX
22213 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-10-07 09:25 | 2020-10-07 10:59 | 1 | 94 | 4532921 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
22214 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-11-10 14:41 | 2019-11-10 16:15 | 1 | 94 | 4017151 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced 2 connection
22215 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-06-26 18:26 | 2009-06-26 20:00 | 1 | 94 | 63774-1 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HAS PULLED LOOSE ON POLE. I AM GOING TO CLIMB POLE AND FIX PROBLEM. I REPLACED CONNECTIONS ON BOTH SEC. AND TRANS. POLES.//COD 1// VER/DBM
22216 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2008-07-29 13:46 | 2008-07-29 15:20 | 1 | 94 | H61762-1A | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ON SITE, POLETOP BROKE OFF , POLE#1064-67, MAKING REPAIRS, TWO PHASES ALREADY OUT, OPENED OTHER PHASE AT 1346// BACK ON @ 1520 IDC BELFRY TOLER CUSTOMERS WERE TRANSFERED TEPORARILY TO BARENSHEE POUNDING XXXX
22217 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-07-17 16:41 | 2021-07-17 17:28 | 2 | 47 | 4926751 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | this was on pole 150-618 transformer fuse pulled
22218 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-09-19 18:33 | 2015-09-19 19:20 | 2 | 47 | 4251321 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN ON XFM CUT OUT, REFUSED AND RESTORED POWER AT 1920/ ISO 37830426B00297/ COD 2/ VER/BOW
22219 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-11-23 07:27 | 2022-11-23 09:01 | 1 | 94 | 4175291 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad insulink/replaced pls close. tre
22220 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2008-05-25 10:55 | 2008-05-25 12:29 | 1 | 94 | 51157-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400101// BROKE IN SERVICE DROP WILL REPLACE SERVICE VER/TOM IDC XXXX
22221 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-06-30 00:33 | 2008-06-30 01:20 | 2 | 47 | 59773-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402002//BAD CUTOUT,ARESSTOR// OPENED WHEN ARRIVED // VER/TOM IDCC TOF0033 6/29, CNT1 XXXX
22222 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-02-05 17:11 | 2017-02-05 18:45 | 1 | 94 | 4359991 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACE CONNECTIONS/ ISO 38830198000108/ COD 1/ VER/BOW L3/HFP XXXHFP
22223 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-02-06 12:05 | 2017-02-06 13:39 | 1 | 94 | 4361311 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED 2 BAD CONNECTIONS VER/CRB L3/HFP XXXHFP
22224 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-03-13 07:01 | 2010-03-13 08:35 | 1 | 94 | 66207-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER WENT BAD ON PLE 328 == CUT ARRESTER IN THE CLEAR == REFUSED LINE == POWER OK IDC XXXX
22225 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-02-03 04:44 | 2009-02-03 06:18 | 1 | 94 | 54979-1 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | 3314402/3314402 REPLACED CONNECTIONS ON POLE //VER/GAH
22226 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-12-07 23:26 | 2008-12-08 01:00 | 1 | 94 | 55291-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3110903/// FOUND 1/0 SECONDARY LASH, BURNTED INTO, HAD TO OPEN TRANSFORMER ON POLE 1098-286, TO MAKE REPAIRS, ALL REPAIRS ARE MADE, AND EVERYTHING IS FINE AT THIS LOCATION VER/JHM L3/KEP IDC XXXX
22227 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-08-12 19:11 | 2020-08-12 20:45 | 1 | 94 | 4317001 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Customers service drop burnt down, repaired/ ISO 39831099B33024/ COD 1
22228 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-05-27 08:41 | 2013-05-27 10:15 | 1 | 94 | 4187641 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVICE NEUTRAL BROKE INTO AT THE XFMR POLE, I REPAIRED IT . I OPENED THE XFMR AT 10:00 AND CLOSED IT BACK AT 10:15. CUSTOMER SEEMS TO HAVE A LOT OF DAMAGES HE WILL BE CALLING DUP IN HOIS FOR 6 CUST........SEF SEE DUPLICAT #4187641 FOR 6 VER/SEF IDC XXXX
22229 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2015-05-10 20:04 | 2015-05-10 20:51 | 2 | 47 | 4408701 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE . XFMR OUT . CLOSED BACK @ 20:51/COD 2// VER/ ADH
22230 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2015-03-17 09:32 | 2015-03-17 11:06 | 1 | 94 | 4202741 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SINGLE ALL OUT, BROKEN FUSE LINK,POWER RESTORED REPLACED 6-T FUSE KWB COD-1 ISO TF 39831147A00856 VER/HFP L3/HFP
22231 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-04-14 09:34 | 2011-04-14 11:08 | 1 | 94 | 56586-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN//FUSE LINK APPEARED TO HAVE BROKEN
22232 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-12-04 10:08 | 2014-12-04 10:55 | 2 | 47 | H4832491 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN, OPENED TRANSFORMER AT 10:08, REPAIRED SERVICE, CLOSED TRANSFORMER AT 10:55, POWER RESTORED.// DUPLICATE IN HOIS FOR 2 CUSTOMERS/ ISO 37830344000015/ COD TOTAL 3/ VER/BOW
22233 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-09-06 16:15 | 2016-09-06 17:49 | 1 | 94 | 4872291 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | HAVE BAD UNDERGROUND SERVICE ONE LEG BAD . TALKED TO CUST. OK FOR CREW TO COME FIX IN MORNING .TALK TO JIM M. HE GOING TO GET CREW ON THIS FIRST THING . VER/CRB
22234 | Pikeville | 3311401 | REEDY STATION | DEANE | 2011-12-14 07:29 | 2011-12-14 09:03 | 1 | 94 | 4175851 | 94 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | PH 3 34KV REGULATOR FAILED IN STATION, SAME ISOLATED & STATION RESTORED AT 0903 //VER/GAH NOTE TO DALE: NEED TO 820 CUSTS BETWEEN PIKEVILLE, HAZARD & WHITESBURG IDC XXXX
22235 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-11-04 18:51 | 2010-11-04 20:25 | 1 | 94 | 51970-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE INTO ,REPLACED FUSE RESTORED POWER AT 20:25, ONLY ONE CUSTOMER AFFECTED XFMR POLE 424-2251//ISO//COD 1// VER/DBM IDC XXXX
22236 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2017-11-20 16:26 | 2017-11-20 18:00 | 1 | 94 | 4590341 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Replaced service drop/ ISO 37820104000073/ COD 1
22237 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-05-31 09:56 | 2016-05-31 11:30 | 1 | 94 | 4274701 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT ON POLE 269D-1476 , FUSE BROKE , CLOSED XFMR @ 11:30 . VER/CRB
22238 | South Williamson | 3411401 | DEWEY | INEZ | 2008-07-11 21:06 | 2008-07-11 22:40 | 1 | 94 | 51413-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401....//......JRV ON SITE @ 22:53......BROKEN CUTOUT ON XFRMR POLE 672A67......CAN REPLACE...//...REPLACED CUTOUT...FUSE NOT BLOWN....CLOSED IN....POWER ON....JRV....07/11/08// VER/TOM IDC XXXX
22239 | Hazard | 3303902 | LESLIE | WOOTON | 2016-04-07 17:56 | 2016-04-07 19:30 | 1 | 94 | 4068531 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9KV CUTOUT/ ISO 37830438B20406/ COD 1/ VER/BOW
22240 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-12-01 11:11 | 2009-12-01 12:45 | 1 | 94 | 53342-1 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT//FUSE WASNT BLOWN, DOOR ON CUTOUT HAD FALLEN OPEN IDC XXXX
22241 | South Williamson | 3200302 | BELFRY | TOLER | 2020-09-05 17:56 | 2020-09-05 19:30 | 1 | 94 | 4435721 | 94 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customers service nuetral broken at the mast.repaired nuetral
22242 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-12-06 13:29 | 2011-12-06 15:03 | 1 | 94 | 4145091 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON POLE 470-18, BAD DEADEND INSULATOR ON POLE 470-53.. REPLACED INSULATOR RESTORED POWER AT 15:03 ////VER/CRB IDC XXXX
22243 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-06-26 16:06 | 2018-06-26 17:40 | 1 | 94 | 4672741 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Service drop burned down due to tape being wrapped around all 3 conductors. only one customer affected.
22244 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-03-23 14:38 | 2018-03-23 15:25 | 2 | 47 | 4045501 | 94 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Open 1438-1525. replaced service opened xfmr at 14:38 closed at 15:25
22245 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-09-24 15:24 | 2019-09-24 15:55 | 3 | 31 | 4053791 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | changing transformer open transformer 1524 to 1555
22246 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-01-29 17:22 | 2018-01-29 18:55 | 1 | 93 | 4782381 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired bad connection on service drop one customer only affected.
22247 | Paintsville | 3401802 | INDEX | HOSPITAL | 2018-04-20 18:49 | 2018-04-20 20:22 | 1 | 93 | 4259901 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | serve bad on pole 38830654D00213.. open transformer at 20:19 and closed back in at 20:22. after making repairs.. complete rn/ ISO 38830654D00213/ COD 4 (1 part out originally and 3 opened up)
22248 | Pikeville | 3403001 | PIKEVILLE | CITY | 2010-04-10 14:27 | 2010-04-10 16:00 | 1 | 93 | 61947-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED TRANSFORMER//VER/CRB IDC XXXX
22249 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-03-19 13:03 | 2020-03-19 14:36 | 1 | 93 | 4492331 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out, fuse broke
22250 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-06-21 14:49 | 2014-06-21 15:20 | 3 | 31 | 4135651 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CREW ON SITE///BROKEN TRANSFORMER FUSE. VER/CRB
22251 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2014-02-03 07:07 | 2014-02-03 08:40 | 1 | 93 | 4342571 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT. PLEASE SEND AN E-MAIL TO JOEY REED TO REPLACE CROSSARM, IT IS BURNED OFF ON ONE SIDE. VER/SEF
22252 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-12-06 18:10 | 2013-12-06 19:43 | 1 | 93 | 4109661 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I WILL PROBABLY HAVE TO CHANGE CUTOUT. CUSTOMER SAID I COULD WAIT UNTIL TOMORROW MORNING SINCE IT IS RAINING SO HARD. RELEASED BY CREW 074S01//OPS ORDER#039658768 VER/CRB L3/HFP
22253 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-03-06 06:42 | 2011-03-06 08:15 | 1 | 93 | 50347-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP WIRE FEEDING THIS LATERAL BURNT OUT OF BOTTOM OF CUTOUT......CAN REPLACE CUTOUT....//....COULD NOT REACH CUTOUT FROM OFF THE ROAD....WET SNOW ON HIGHWAY....FAST TRAFFIC COMING OFF MOUNTAI....TOO DANGEROUS TO SET UP IN THE ROAD....TOOK CUTOUT OFF-LINE WITH STICK....WIRED TAP STRAIGHT THRU WITH HOT LINE CLAMP...POWER ON...WILL GENERATE AN ORDER FOR CREW TO REPLACE CUTOUT LATER....THANX....JRV...03/06/11 //VER/GAH IDC CHANGED CLEARING POLE FROM 60 AND COUNT FROM 5, MISSMAPPED CUSTOMER? XXXX
22254 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2019-08-02 21:57 | 2019-08-02 23:30 | 1 | 93 | 4835771 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced bad connections at transformer everything ok
22255 | Hazard | 3303901 | LESLIE | HYDEN | 2022-06-23 16:17 | 2022-06-23 16:48 | 3 | 31 | 4294721 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | xfm lead had bare spot and burnt neutral down at pole 413-257. need line crew to put neutral up and remake connections. Released by crew 077S10
22256 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2009-12-17 08:39 | 2009-12-17 10:12 | 1 | 93 | 51712-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION @ WEATHERHEAD HEATING UP. RE-WORKED BOTH HOT CONNECTIONS. SH VER/HFP L3/HFP
22257 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-03-17 17:22 | 2015-03-17 18:55 | 1 | 93 | 4204991 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE IN SERVICE DROP, AT POLE 398-461, MADE REPAIRS RESTORED POWER AT 18:55.ONLY ONE CUSTOMER AFFECTED// VER/ ADH
22258 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-03-31 05:17 | 2010-03-31 06:50 | 1 | 93 | 56327-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XXMR FUSE BLOWN. WILL TRY TO RE-FUSE. FUSE LINK BROKE - DID NOT BLOW. RE-FUSED XFMR @ 06:50. SH COD-1 VER/HFP L3/HFP AJB
22259 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-10-31 11:30 | 2009-10-31 13:03 | 1 | 93 | 53548-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN DOWN,WILL REPLACE IT/REPLACED CUTOUT,RESTORED POWER.BELIEVE FIRE IS OUT.SEND TO TECH,POLE IS BURNED OVER HALF INTO,IS ALSO AN ANGLE POLE MD FILED SHOULD BE ON POLE#37830040C40010 COD-1 VER/KEP L3/KEP IDC CHANGED START TIME FROM 1108 ESTIMATED XXXX
22260 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2016-05-19 19:42 | 2016-05-19 21:15 | 1 | 93 | 4237311 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #4 SERVICE BURNT IN TWO. INSULINK CONNECTION HEATED UP AND BURNT WIRE DOWN. REPLACED WITH 2/3 AND RESTORED ONE CUSTOMER @ 21:15. SH/ ISO 38830954B20774/ COD 1/ VER/BOW
22261 | Pikeville | 3421001 | BREAKS | CITY | 2020-11-03 20:12 | 2020-11-03 21:45 | 1 | 93 | 4640761 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection @ weatherhead ////Replaced bad connection and restored service @ 21:45///Only 1 customer affected
22262 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-05-27 17:58 | 2009-05-27 19:31 | 1 | 93 | 57204-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP ,,BROKE CUTOUT I WILL CHANGE,,,,BACK ON POWER RESTORED COD - 1 ISO 38830427000099 L3/HFP IDC XXXX
22263 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-10-27 09:54 | 2019-10-27 11:27 | 1 | 93 | 4205971 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke. replaced. pls close. tre
22264 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-04-17 09:53 | 2013-04-17 11:26 | 1 | 93 | 4018021 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FIRE DEPT VER/KEP IDC XXXX
22265 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-28 01:00 | 2014-01-28 02:33 | 1 | 93 | 4318421 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CONNECTION HEATED UP AND BURNT SERVICE NEUTRAL OPEN. CLOSER INSPECTION REVEALED THAT NEUTRAL HAD PULLED OUT OF COMPRESSION SLEEVE. REPAIRED AND RESTORED @ 2:33. SH
22266 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-12-21 09:02 | 2010-12-21 10:35 | 1 | 93 | 54735-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMT FUSE I WILL BE REPLACING. I HAVE REPAIRS MADE EVERYTHING OK.//ISO //COD 1// VER/DBM IDC XXXX
22267 | Hazard | 3302704 | HAZARD | KENMONT | 2018-04-27 07:27 | 2018-04-27 09:00 | 1 | 93 | 4283401 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2 Leads brunt into at weather head
22268 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2017-11-11 14:27 | 2017-11-11 16:00 | 1 | 93 | 4549881 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | midspand connection fell,replace connection,only 1 meter affected 37830250B00044
22269 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-03-27 08:24 | 2011-03-27 09:57 | 1 | 93 | 59640-1 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | 2 FUSES OUT IN TRANSFORMER BANK ON POLE 39831123B00513--BANK NOT IN FIELDVIEW--BAD ARRESTER NEEDS REPLACED IN 3 PHASE BANK TRUCK OK // SENT EMAIL TO LLOYD RAYBURN ABOUT ARRESTOR...HFP COD-1 ISO TF 39831123B00513 VER/HFP L3/HFP IDC XXXX
22270 | Hazard | 3309302 | VICCO | JEFF | 2015-03-13 19:37 | 2015-03-13 21:10 | 1 | 93 | 4191441 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === CHANGED CUTOUT ==== POWER OK//COD 1 // VER/DBM
22271 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-06-13 17:12 | 2014-06-13 18:45 | 1 | 93 | 4088061 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE WILL CHANGE/// CHANGED BROKEN CUT OUT RESTORED SERVICE @18:45 COD-1 ISO TF 38831101D20327 VER/HFP L3/HFP
22272 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-02-18 06:37 | 2008-02-18 08:10 | 1 | 93 | 64621-1 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE ON SERVICE DROP//3001002//VER/CRB IDC XXXX
22273 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-02-09 12:16 | 2022-02-09 13:49 | 1 | 93 | 4461761 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xr cutout
22274 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-03-06 15:13 | 2009-03-06 16:46 | 1 | 93 | 55761-1 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE END...PARTIAL POWER...RE SQUEEZED SERVICE...BB//3401103//VER/CRB IDC XXXX
22275 | Hazard | 3303902 | LESLIE | WOOTON | 2008-11-25 12:11 | 2008-11-25 13:44 | 1 | 93 | 52203-1 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION//3303902//VER/CRB IDC XXXX
22276 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-05-19 21:48 | 2019-05-19 23:21 | 1 | 93 | 4302291 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | called cust//meter is blank//SERVE-IN BURNED IN TWO, REPLACED ALL CONNECTIONS, OK AFTERWARDS//cod 1//
22277 | Pikeville | 3421001 | BREAKS | CITY | 2022-10-18 16:17 | 2022-10-18 17:50 | 1 | 93 | 4040941 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | One leg iin service drop melted from xfm to the house///Replaced 75 service drop and restored full power///Restored @ 17:50///Send copy to Corey Farmer ROW IS AWFUL and needs attention ASAP//Also send copy to Bill Johnson pole 220-376 needs replaced
22278 | Hazard | 3308002 | JACKSON | PANBOWL | 2014-01-04 13:42 | 2014-01-04 15:15 | 1 | 93 | 4228541 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN SERVICE , RED/RED SERVE END BAD. ONLY 1 CUST HAVING TROUBLE. VER/CRB
22279 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-02-22 09:15 | 2015-02-22 10:48 | 1 | 93 | 4070691 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BAD CUTOUT,REPAIRS MADE ALL CUST RESTORED @ 1048 PLEASE CLOSE TICKET THANKS.BT/ ISO 38830302A40097/ COD 1/ VER/BOW
22280 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-05-13 22:31 | 2012-05-14 00:04 | 1 | 93 | 4787791 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SERVE END ON TRANSFORMER POLE HAVE REPAIRED AND EVERYTHING OK AT THIS LOC IDC XXXX
22281 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-12-10 18:26 | 2012-12-10 19:59 | 1 | 93 | 4458611 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION AT XFMR, REPAIRED ///VER/CRB L/3 CRB
22282 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-08-08 18:17 | 2009-08-08 19:50 | 1 | 93 | 64403-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR 31140255 OPEN TRANS. ON POLE 1123-4141 19.25 ON 19:50 4/3 SERVICE BURNT DOWN REPAIRED SEND NOTE TO TEC POLE 1123-4045 ROTTEN NEEDS LOOKED AT IDCC CNT3, CCU, TON2005 XXXX
22283 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-02-22 14:27 | 2019-02-22 16:00 | 1 | 93 | 4844531 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | burnted up c/o door on top of a 70 ft pole, clumb pole and rep door, all power is restored at this loc comp by amg
22284 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2017-09-29 09:57 | 2017-09-29 11:30 | 1 | 93 | 4399051 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 3 BAD TRANSFORMER CUTOUTSON PL 401-285 37830401A00285 VER/AWD
22285 | Pikeville | 3413401 | GARRETT | GARRETT | 2013-09-05 23:02 | 2013-09-06 00:35 | 1 | 93 | 4824091 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER DUE TO BAD CONNECTION AT TRANSFORMER. I HAVE REPAIRS MADE EVERYTHING OK. VER/PDP
22286 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-10-03 18:22 | 2019-10-03 19:55 | 1 | 93 | 4092561 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke into, I changed it out
22287 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-11-04 16:11 | 2009-11-04 17:44 | 1 | 93 | 61463-1 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE......DAH CUTOUT FAILED VER/KEP L3/KEP IDC XXXX
22288 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2022-07-21 08:07 | 2022-07-21 09:40 | 1 | 93 | 4539671 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout//cod 1
22289 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-12-02 12:32 | 2014-12-02 14:05 | 1 | 93 | 4826161 | 93 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 38830069A20526 SERVICE MELTED OFF POLE AGAIN 3-REQUEST SEC. 4/3 NEEDS CHGED TO 1/0 AND SERVICE DROP NEEDS CHGED TO SMALL CUST VERY UP SET 3- OUTAGE SEN TO TEC. ASAP VER/CRB
22290 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-04-08 10:18 | 2019-04-08 11:51 | 1 | 93 | 4068971 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | current limiting fuse bad. all repairs made. pls close. tre L3/HFP
22291 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2020-05-10 21:27 | 2020-05-10 23:00 | 1 | 93 | 4821631 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 30t fuse replaced door
22292 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-02-18 22:39 | 2015-02-19 00:12 | 1 | 93 | 4040811 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNT UP ///WILL REPLACE//// REPLACED BAD CURRENT LIMITING FUSE AND RESTORED SERVICE @ 00:12 VER/CRB L3/HFP XXX
22293 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2014-01-31 10:32 | 2014-01-31 12:05 | 1 | 93 | 4332651 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN SERVICE DROP WAS BAD AND BURNED THE NEUTRAL INTO. PLEASE SEND TO DON WASHINGTON TO HAVE A SECONDARY POLE SET TO GET PROPER CLEARANCE OVER THE CUSTOMERS HOUSE. ONLY ONE CUSTOMER WAS OUT.//EMAILED TO C FREEMAN// VER/DBM
22294 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-03-15 17:42 | 2012-03-15 19:15 | 1 | 93 | 4585631 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER ETA 1820 // OPENED XMF 1851 CLOSED AT 1915. SPICED SERVICE DROP CONN LOOKED LIKE THEY HAD RUBBED TOGETHER BURNNING HOTLEGS INTO APR AT 1915 CLOSE TICKET VER/KEP IDCC PN374, FP NONE, XXXX
22295 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-12-07 20:37 | 2011-12-07 22:10 | 1 | 93 | 4155081 | 93 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP, REPLACED CUTOUT AND RESTORED POWER AT 1010//COD 1.// VER/DBM IDC XXXX
22296 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2021-08-06 13:42 | 2021-08-06 15:14 | 1 | 92 | 4012471 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced secondary connections ,,complete//only 1 cust
22297 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2022-09-10 20:53 | 2022-09-10 22:25 | 1 | 92 | 4863581 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up on service drop at xfmr pole//repaired connections//restored to normal at 22:25//complete//em
22298 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-04-12 03:18 | 2012-04-12 04:50 | 1 | 92 | 4667621 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE PHASE WIRES ON THE SERVICE DROP HEATED UP, MELTING THE INSULATION CAUSING A PHASE TO PHASE FAULT, BURNING THE SERVICE DROP DOWN. ONLY ONE CUSTOMER AFFECTED. VER/TOM L3/TOM
22299 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-03-23 17:13 | 2013-03-23 18:45 | 1 | 92 | 4950461 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE DROP.// VER/DBM IDCC CNT2 XXXX
22300 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2016-02-05 11:08 | 2016-02-05 12:40 | 1 | 92 | 4677721 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-6101 BAD CUTOUT REPLACED/ VER/AWD
22301 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2012-11-12 16:58 | 2012-11-12 18:30 | 1 | 92 | 4389231 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE === REPLACED FUSE POWER OK COD-1 ISO TF 37830295D00088 VER/HFP L3/HFP IDC XXXX
22302 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-11-22 20:23 | 2008-11-22 21:55 | 1 | 92 | 51210-1 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SERVIN AT WEATHERHEAD WITH SQUEEZON / GXJ VER/LDA IDC XXXX
22303 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2020-03-24 13:43 | 2020-03-24 15:15 | 1 | 92 | 4506031 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Primary bushing lead burnt open @ xfm will make repairs/// Replaced primary bushing lead and restored service @ 15:15
22304 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-12-04 09:23 | 2014-12-04 10:55 | 1 | 92 | 4832491 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN, OPENED TRANSFORMER AT 10:08, REPAIRED SERVICE, CLOSED TRANSFORMER AT 10:55, POWER RESTORED.// DUPLICATE IN HOIS FOR 2 CUSTOMERS/ ISO 37830344000015/ COD TOTAL 3/ H4832491/ VER/BOW
22305 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-05-23 07:23 | 2011-05-23 08:09 | 2 | 46 | 4138391 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GATE ON POLE 421-291, REPLACED GATE RESTORED POWER AT 08:09 COD-2 ISO 37830421C20291 VER/HFP L3/HFP
22306 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-02-02 11:13 | 2012-02-02 12:45 | 1 | 92 | 4315701 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT CHANGED OUT BAD CUTOUT. VER/KEP IDC XXXX
22307 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-11-04 18:23 | 2013-11-04 19:55 | 1 | 92 | 4009771 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT HAVE CHANGED AND POWER IS RESTORED AT THIS LOC AT 1955 COD-1 ISO TF 39831121A00055 VER/HFP L3/HFP
22308 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-12-16 13:43 | 2008-12-16 15:15 | 1 | 92 | 59018-1 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT MAST VER/HFP L3/KEP IDC XXXX
22309 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-01-23 16:28 | 2013-01-23 18:00 | 1 | 92 | 4734411 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG BURNDT INTO AT POLE 356-7, ONLY 1 CUST. WAS AFFECTED. REPLACED CONN. ///VER/CRB L/3 CRB IDC XXXX
22310 | South Williamson | 3411401 | DEWEY | INEZ | 2018-04-02 11:56 | 2018-04-02 13:28 | 1 | 92 | 4164921 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | neutral pulled out of sleeve in service drop//i repared neutral//customer says they have some damages inside//i told them the could call in claim//please send to peggy wysong//complete//em//SENT TO CLAIMS
22311 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-10-28 08:15 | 2014-10-28 09:47 | 1 | 92 | 4666351 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 37830222D00226, LEAD ALMOST TOUCHING TEE BRACKET, TRANSFORMER FUSE BLOWN ALSO, WILL NEED TO OPEN RECLOSER ON 37830246C00439 TO CLEAR ARRESTER. NEED 1 MAN TO HELP./SERVICER OPENING RECLOSER 246-439 FOR 30 MIN TO SAFELY MAKE REAPIRS//FIX IT IN HOIS// COD 87 + 1// ORIGINAL TIME OFF 9:26 ON 9:47// VER/ ADH VER/DKG L3/DKGXXXX THIS OUTAGE FOR SINGLE CUST ON TRANSFORMER 226....SEE H4666351 FOR RECLOSER OUTAGE
22312 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-01-10 15:03 | 2008-01-10 16:35 | 1 | 92 | 55427-1 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3409302// ONE LEG OUT ON UNDERGROUND SERVICE. (500 MCM) CUSTOMER REQUESTS THAT WE WAIT UNTIL AFTER 3:00 P.M. FOR OUTAGE TO REPAIR. ROBERT OBRYAN IS PERSON TO CONTACT WITH INFO. RELEASED BY CREW 076S02// TC MILLER FOUND PROBLEM AT JCT BOX AT FOOT OF POLE WILL PULL OFF AT 15:00 AFTER SCHOOL LETS OUT TO MAKE REPAIRS.// VER/TOM IDC XXXX
22313 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-10-21 09:30 | 2021-10-21 11:02 | 1 | 92 | 4371461 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Looked like fuse had just melted out. Refust txmf apr at 1102 close ticket
22314 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-10-24 17:13 | 2011-10-24 18:45 | 1 | 92 | 4016781 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 373-84. REPLACED CUTOUT RESTORED POWER AT 18:45//COD 1// VER/DBM IDC XXXX
22315 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2022-02-14 14:23 | 2022-02-14 15:55 | 1 | 92 | 4481791 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke.//Replaced 19.9 cutout
22316 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2020-09-22 23:52 | 2020-09-23 01:24 | 1 | 92 | 4487831 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service drop connecter failed, opened xfmr at 23:52 closed at 01:24
22317 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-02-08 15:28 | 2014-02-08 17:00 | 1 | 92 | 4368181 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | NO CREWE REQUIRED REPAIRED BASKET ***CHANGE ISO POLE**** DID MD VER/SEF
22318 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-08-28 14:58 | 2019-08-28 16:30 | 1 | 92 | 4957661 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | bad 100 a meterbase lugs. repairs complete
22319 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2016-12-31 12:04 | 2016-12-31 12:50 | 2 | 46 | 4258751 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT. RELEASED BY CREW 079S02 VER/CRB
22320 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-12-30 09:23 | 2019-12-30 10:55 | 1 | 92 | 4194471 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole37830223D41612 Released by crew 077H11broke cutout on pole37830223D41612. power restored at 10:55//MD MADE
22321 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-04-22 21:40 | 2017-04-22 22:03 | 4 | 23 | 4669461 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER WAS SPARKING EARLIER IN DAY BEFORE OUTAGE. DIM LIGHTS IN HOUSE..CONNECTION BURNT INTO ON XFM. POLE 97-12.WILL HAVE TO OPEN TO MAKE REPAIRS..NEUTRAL BURNT INTO.CUSTOMER SAID EVERYTHING WORKING IN HOME..PLEASE SEND COPY TO PEGGY WYSONG JUST TO BE SAFE..OPENED XFM @ 21:40 CLOSED BACK IN @ 22:03..//COD 4//EMAILED TO P WYSONG//RELATED TO ORDER 4667461// VER/DBM L3/HFP XXXHFP
22322 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-12-25 11:15 | 2019-12-25 12:01 | 2 | 46 | 4181131 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on transformer
22323 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2019-10-17 21:58 | 2019-10-17 23:30 | 1 | 92 | 4164611 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced secondary connection ,,,complete//cod 1
22324 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2014-08-02 12:58 | 2014-08-02 14:30 | 1 | 92 | 4319591 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE END ON HOUSE SIDE HAVE REPAIRED AND POWER IS BACK TO FULL AT THIS LOC VER/CRB
22325 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-06-27 12:59 | 2013-06-27 13:45 | 2 | 46 | 4415421 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANSFORMER HAVE REPLACED AND POWER IS RESTORED AT THIS LOC AT 1345 COD-2 ISO TF 39831073A20515 VER/HFP L3/HFP
22326 | South Williamson | 3200302 | BELFRY | TOLER | 2010-11-02 18:23 | 2010-11-02 19:55 | 1 | 92 | 51126-1 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUST HAS PART POWER....BAD INSULINK CONNECTOR IN SERVICE DROP...//....SERVICE MELTED TOGETHER....REPLACED SERVICE DROP....POWER OK NOW....JRV....11/02/10// VER/DBM IDC XXXX
22327 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2020-06-10 13:23 | 2020-06-10 14:55 | 1 | 92 | 4991321 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SERVICE DROP
22328 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-01-16 23:17 | 2010-01-17 00:49 | 1 | 92 | 55039-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT CHANGED AND RESTORED POWER. TIM MCCOY RELEASED BY CREW 074H10 VER/ARN IDC XXXX
22329 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2010-02-21 10:18 | 2010-02-21 11:50 | 1 | 92 | 59488-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNED UP BLOWING TRANS. FUSE. I AM GOING TO BYPASS CLF. I REFUSED TRANS. AND IT STAYED IN.//COD 1// VER/DBM IDC XXXX
22330 | Hazard | 3310502 | HADDIX | CANOE | 2019-03-24 13:40 | 2019-03-24 15:12 | 1 | 92 | 4020281 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke into ON 37840168000024
22331 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-04-16 16:14 | 2012-04-16 17:00 | 2 | 46 | 4677731 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR. COD-2 ISO TF 38830186000124 VER/HFP L3/HFP IDC XXXX
22332 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-02-01 07:40 | 2008-02-01 09:12 | 1 | 92 | 63252-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404302//,VER/ARN IDC XXXX
22333 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-02-25 14:34 | 2018-02-25 15:20 | 2 | 46 | 4881941 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout door
22334 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-09-26 21:03 | 2010-09-26 22:35 | 1 | 92 | 53881-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. //VER/GAH IDC XXXX
22335 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-08-26 10:49 | 2010-08-26 12:21 | 1 | 92 | 60749-1 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS AT WEATHER HEAD VER/HFP L3/HFP IDC XXXX
22336 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-11-18 08:04 | 2021-11-18 09:36 | 1 | 92 | 4103401 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt into on one leg Xfm ////Replaced bad connection and restored service 123/123/246///Omly 1 customer was affected
22337 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2009-05-24 17:12 | 2009-05-24 17:58 | 2 | 46 | 62867-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED A 50 KVA TRANSF BIG BUCKET TRUCK & LINEMAN == CHSANGED TRANSF == TOOK POWER OFF AT 17:12 ON AT 17:55 === VER/TOM IDCC FEC57 XXXX
22338 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-10-13 15:29 | 2020-10-13 16:15 | 2 | 46 | 4552731 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans fuse is open on 144-A-447, ( Looking it Over ).We had a broke fuse,Replaced it and restored service at 16:15.
22339 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-12-14 16:58 | 2009-12-14 18:30 | 1 | 92 | 58635-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT GATE//COD 1// VER/DBM
22340 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-08-11 07:40 | 2021-08-11 09:12 | 1 | 92 | 4033521 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced service connections at xfr ,,complete
22341 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-10-25 16:03 | 2009-10-25 17:35 | 1 | 92 | 53222-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT == REPLACED CUTOUT == POWER OK COD-1 ISO TF 37830371000042 L3/HFP IDC XXXX
22342 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-05-31 07:18 | 2009-05-31 08:50 | 1 | 92 | 52926-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400302//NOT LINE FUSE OUTAGE, TRANFORMER 1078-80 OUT ONLY, BAD CUTOUT//ISO 38831078000080//COD 1// VER/DBM IDC XXXX
22343 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-11-18 08:08 | 2012-11-18 09:40 | 1 | 92 | 4406181 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND CONNECTION ON HOT LEG AT XFMR THAT HAD BEEN MELTED, CHANGED CONNECTION AND CHECKED ALL OTHERS AT WEATHERHEAD AND POLE, SHOULD TAKE CARE OF PROBLEM.. CUST ADVISED BY PHONE. CC 1 VER/SDB IDC XXXX
22344 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-12-26 08:13 | 2018-12-26 09:45 | 1 | 92 | 4598471 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired connections L3/HFP
22345 | Whitesburg | 3309302 | VICCO | JEFF | 2018-07-19 20:28 | 2018-07-19 22:00 | 1 | 92 | 4800871 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | xfmr lead fell out of xfmr bushing
22346 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-08-02 22:29 | 2015-08-02 23:15 | 2 | 46 | 4968611 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN, REPLACED FUSE AND CUTOUT FUSE HOLDER, ALL WORK COMPLETE / GXJ VER/KEP
22347 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-03-11 06:05 | 2010-03-11 07:37 | 1 | 92 | 64844-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BLOWN ON XFMR BANK. WILL TRY TO RE-FUSE. FUSE LINK HAD BROKE. RE-FUSED @ 07:37. SH VER/KEP L3/KEP IDC XXXX
22348 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-04-04 18:13 | 2020-04-04 19:45 | 1 | 92 | 4561181 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replace door
22349 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2010-02-20 04:43 | 2010-02-20 06:15 | 1 | 92 | 59296-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3404301// STS 33950374, ON SITE, SERVICE DROP DOWN, MAKING REPAIRS VER/LDA IDC XXXX
22350 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-09-29 10:44 | 2020-09-29 11:30 | 2 | 46 | 4507841 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Opened at 10:44 to make repairs closed at 11:30
22351 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-01-30 01:03 | 2021-01-30 01:49 | 2 | 46 | 4919471 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR fuse on pole 246-C3-658 appears to have just broken, not blown/operated. Power restored at 1:49.
22352 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-02-03 01:21 | 2021-02-03 02:53 | 1 | 92 | 4932281 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. fuse open @146-C3-260, checking. Trans. cutout busted here, will be making repairs. Got cutout replaced, power restored @0253.//cod 1
22353 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-08-28 12:43 | 2022-08-28 14:15 | 1 | 92 | 4804701 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 42-477..bad 12kv co. repaired / customer called in about barn service from primary residence
22354 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-12-01 16:39 | 2009-12-01 17:25 | 2 | 46 | 54424-1 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 2// VER/DBM IDC XXXX
22355 | Pikeville | 3421002 | BREAKS | GRASSY | 2010-10-18 15:13 | 2010-10-18 16:45 | 1 | 92 | 60731-1 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUSTOMER AFFECTED I REPLACED A BAD CONNECTION ON THE SERVICE AT THE WEATHERHEAD. VER/HFP L3/HFP IDC XXXX
22356 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-07-26 17:16 | 2014-07-26 18:48 | 1 | 92 | 4290661 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STURRIP , HOTTAP & FUSE NEED REPLACED ON POLE#38830954D40346. CSX WILL HIGH RAIL CREW TO LOCATION. FUSE ON POLE #38830954D40514 IS GOOD BUT ONLY OPEN & MARSHAL BAND IS ON POLE 38830954D40514 RELEASED BY CREW 074S04 //CUSTOMER AGREED TO WAIT UNTIL MONDAY 07/28/14 // WILL BE WORKED ON IO # 039717832 VER/HFP L3/HFP
22357 | Hazard | 3310502 | HADDIX | CANOE | 2020-03-06 14:47 | 2020-03-06 15:33 | 2 | 46 | 4457121 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
22358 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-01-27 11:03 | 2011-01-27 12:35 | 1 | 92 | 66287-1 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR SERVE -IN SLEEVE PULLED OUT, MADE REPAIRS RESTORED POWER AT 12:35 COD-1 ISO TF 37830422000194 VER/HFP L3/HFP IDC XXXX
22359 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-02-28 11:52 | 2017-02-28 13:24 | 1 | 92 | 4428291 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RESQUEEZED SERVICE ON HOUSE AND BOTH POLES COMPLETE VER/CRB
22360 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2011-12-22 13:28 | 2011-12-22 15:00 | 1 | 92 | 4195171 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 SERVICE BURNT MID SPAN, ONLY 1 CUST AFFECTED. POWER RESTORED.// VER/DBM IDC XXXX
22361 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-06-11 21:38 | 2022-06-11 23:10 | 1 | 92 | 4059041 | 92 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Bad current limiting fuse on XFM.//Restored @ 23:10
22362 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-07-13 10:43 | 2009-07-13 12:15 | 1 | 92 | 66422-1 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 PHASE OUT ON 3 PHASE BANK, REPLACED BROKEN 10T FUSE VER/TOM L3/TOM IDC XXXX
22363 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2015-12-14 10:34 | 2015-12-14 11:20 | 2 | 46 | 4529941 | 92 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLIT BOLTS HAD LOOSENED UP AT XFMR // REWORKED ALL CONNECTIONS // OPENED XFMR @ 10:34 // CLOSED 11:20 VER/HFP L3/HFP
22364 | South Williamson | 3411401 | DEWEY | INEZ | 2014-11-11 16:33 | 2014-11-11 16:52 | 25 | 19 | 4720451 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | CREW FOUND A RISER WHICH IS ARCING ON POLE 861-60//RECLOSERS ON POLE 861-A3-70 ARE BYPASSED AND CREW IS UNABLE TO LOADBUST TO ISOLATE THE BAD SWITCHES//OPENED RECLOSERS ON POLE 837-B-72 IN ORDER TO MAKE REPAIRS//COD 25//OPENED RECLSOERS @ _16:33__//CLOSED @ _16:36___/ CREW ON SITE STARTING REPAIRS TCM//SERVICER OPENING RECLOSER 837-B-72 TO CLOSE IN SWITCH// OPENED 16:51, CLOSED 16:52//VER/ ADH AJB
22365 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2016-02-24 17:59 | 2016-02-24 19:30 | 1 | 91 | 4764091 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORER ,MADE REPAIRES/ CUSTOMER HAD PART POWER BAD CONNECTION ON TRANSFORMER WHERE THE SERVICE DROP CONNECTS/ OPENED TRANSFORMER REPLACED CONNECTION/ POWER RESTORED/ ISO 37830110000104/ CDO 1/ VER/BOW
22366 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2017-06-20 16:24 | 2017-06-20 17:55 | 1 | 91 | 4008311 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE BAD ==== REPAIRED SPLICE === POWER OK/ ISO 37830248C00304/ COD 1/ VER/BOW
22367 | Hazard | 3309003 | JEFF | VIPER | 2020-12-31 08:28 | 2020-12-31 09:59 | 1 | 91 | 4837921 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Line fuse open on pole 416-94, broken service neutral on pole 37830416000096. Opened the XFMR cutout on pole 416-96 and closed the line fuse in on 416-94 at 9:28, not picking up any customers. Made repairs to the service and closed the XFMR fuse back in on pole 416-96 at 9:59.
22368 | South Williamson | 3202201 | LOVELY | LOVELY | 2013-03-13 16:15 | 2013-03-13 17:46 | 1 | 91 | 4904371 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUST. AFFECTED///HOT LEG PULLED OUT OF CONNECTOR ON SEC. POLE///HAS PART POWER//GOING TO REDO CONNECTION//REPAIRS MADE//RESTORED AT 1746//COMPLETE//EM VER/KEP IDCC TON1742 XXXX
22369 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2021-08-28 17:49 | 2021-08-28 19:20 | 1 | 91 | 4166571 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | found two burnt transformer risers on pole 92-4011.repairs made. complete
22370 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-09-20 14:56 | 2009-09-20 16:27 | 1 | 91 | 55566-1 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 31800168 // POLE 20-7584 3- CUTOUTS CHGED L3/HFP IDC MAP DISCREPENCY XXXX
22371 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-10-20 17:29 | 2015-10-20 19:00 | 1 | 91 | 4364811 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING BROKKE CUTOUT/ ISO 38830198000169/ COD 1/ VER/BOW
22372 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2020-03-16 15:27 | 2020-03-17 19:21 | 7 | 14 | 4483201 | 91 | TRANSMISSION STATION | EQUIPMENT FAILURE | MOAB | DOL 1001076 & 1001150/ Failed MOLDLR at Hazard station load transfer for repairs/ Open CB at 1527 Closed N.O. at 1528/
22373 | Hazard | 3303902 | LESLIE | WOOTON | 2008-11-05 17:45 | 2008-11-05 19:16 | 1 | 91 | 62519-1 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303902//CUTOUT BROKEN, GILLEY COMMING TO HELP WITH TRAFFIC/// POWER RESTORED//COD 1// VER/DBM IDC XXXX
22374 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-12-02 13:02 | 2011-12-02 14:33 | 1 | 91 | 4136441 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | APPEARS CUTOUT DOOR HAS BURNED OUT,MAY HAVE A REPLACEMENT,IF NOT,WILL REPLACE CUTOUT///////REPLACED DOOR AND RESTORED POWER COD-1 ISO TF 38830983B40111 VER/HFP L3/HFP IDC XXXX
22375 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2018-05-04 16:32 | 2018-05-04 18:03 | 1 | 91 | 4307281 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fuse door burnt up. repaired @ 1803. pls close/ ISO 38830453000127/ COD 1
22376 | Pikeville | 3413402 | GARRETT | LACKEY | 2012-07-26 14:29 | 2012-07-26 16:00 | 1 | 91 | 4833671 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE HAS BURNT DOWN, POWER RESTORED// VER/DBM IDC XXXX
22377 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-08-27 19:59 | 2013-08-27 21:30 | 1 | 91 | 4712721 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED/ REPAIRED SERVICE//COD 1// VER/DBM IDC XXXX
22378 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-03-01 08:29 | 2009-03-01 10:00 | 1 | 91 | 52691-1 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411901// CUSTOMERS SERVICE DROP HAD A BARE PLACE IN IT . A HOT LEG GOT AGAINST THE NEUTRAL AND BURNED SERVICE DOWN. I MADE REPAIRS AND RESTORED POWER. VER/KEP L3/KEP IDC XXXX
22379 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-04-07 17:33 | 2008-04-07 19:04 | 1 | 91 | 64975-1 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT ON POLE 41A133. WILL BE CHECKING. REFUSED 6T. EVERYTHANG OK . FUSE MAY HAVE BROKE. NOT SHURE.//3413401//VER/CRB IDC XXXX
22380 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-01-12 12:57 | 2016-01-12 14:28 | 1 | 91 | 4610071 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | SERVICE WIRE MELTED @ WEATHER HEAD..REPAIRED OPENED XFM @ 13:50 CLOSED BACK IN @ 14:15./ONLY 1 CUSTOMER// VER/ ADH
22381 | Paintsville | 3410602 | E.PRESTON | LANCER | 2021-06-14 10:50 | 2021-06-14 12:21 | 1 | 91 | 4745191 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse in center phase cutout door had broke causing partial power. I installed new fuse and restored @12:21
22382 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-12-30 17:14 | 2014-12-30 18:45 | 1 | 91 | 4893461 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK/ ISO 38830197000107/ COD 1/ VER/BOW
22383 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-07-09 15:44 | 2013-07-09 17:15 | 1 | 91 | 4492881 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE///////////////FUSE APPEARS TO HAVE BROKEN,RE-FUSED AND RESTORED,ALL OK AFTERWARDS,THIS IS A 3PHASE SERVICE. VER/CRB L/3 CRB IDCC PN221 XXXX
22384 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-04-19 12:59 | 2012-04-19 14:30 | 1 | 91 | 4687631 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT. ///VER/CRB IDC XXXX
22385 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-12-10 15:03 | 2019-12-10 16:34 | 1 | 91 | 4142371 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers neutral and one hot leg burndt into on their service drop, trans. pole #38831150000194 will be making repairs. Only 1 customer affected.Spliced out and restored power @1634. Please send a copy to Peggy Wysong where customers neutral was into.
22386 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-01-13 13:24 | 2016-01-13 14:55 | 1 | 91 | 4617351 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED UP AT WEATHER HEAD AND NOT GETTING GOOD CONNECTION//REPAIRED CONNECTION//RESTORED AT 14:55//COMPLETE//EM VER/CRB
22387 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-05-09 20:24 | 2019-05-09 21:55 | 1 | 91 | 4246911 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced broke cutout//cod 1
22388 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-06-04 17:59 | 2022-06-04 19:30 | 1 | 91 | 4019021 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfn fuse will refuse///Changed bad 19.9 cutout on pole 170-47 and restored service @ 19:30
22389 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-07-20 14:58 | 2017-07-20 15:05 | 13 | 7 | 4147441 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO OUTAGE AT THIS TIME , POLE GROUND HAS COME LOOSE ON CROSSARM ON POLE 427-14 & BLOWING INTO LOOP, WILL HAVE TO OPEN LINE FUSE ON POLE 427-9 TO ISOLATE TO REMOVE GROUND WIRE..//NO OUTAGE AT THIS TIME , POLE GROUND HAS COME LOOSE ON CROSSARM ON POLE 37830427B00017 & BLOWING INTO LOOP, WILL HAVE TO OPEN LINE FUSE ON POLE 427-9 TO ISOLATE TO REMOVE GROUND WIRE..OPENED AT 14:58 MADE REPAIRS RESTORED AT 15:05.. VER/CRB
22390 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2020-05-03 21:56 | 2020-05-03 23:27 | 1 | 91 | 4792731 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connections on pole. replaced insulinks at house & bad connections on pole. pls close. tre
22391 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-12-22 19:44 | 2008-12-22 21:15 | 1 | 91 | 62820-1 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3314402// REPAIRED SERVICE DROP I WILL GET A CREW TUESDAY TO REPLACE SERVICE DROP TO 1/0 TRIPLEX// VER/DBM L3/KEP IDC XXXX
22392 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-01-20 18:09 | 2014-01-20 19:40 | 1 | 91 | 4297341 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST. S/D HAS A CONNECTION IN TWO // WILL REPAIR// REWORKED S/D// POWER IS RESTORED// VER/DBM
22393 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-11-20 15:04 | 2017-11-20 16:35 | 1 | 91 | 4590091 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired bad hotleg and neut, connections/ ISO 38830045D26718/ COD 1
22394 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-04-19 18:29 | 2012-04-19 20:00 | 1 | 91 | 4688711 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BAD CURRENT LIMETER FUSE COD-PER POWERON 0 ISO TF 38830115D26062 VER/HFP L3/HFP IDC XXXX
22395 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-11-17 22:14 | 2022-11-17 23:45 | 1 | 91 | 4156931 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse melted out. refusing
22396 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2008-08-24 12:27 | 2008-08-24 13:58 | 1 | 91 | 54540-1 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 6T FUSE BROKE. I WILL BE OUT OF TRUCK FUSING UP. FUSED UP EVERYTHANG OK. FUSE WAS BROKEN.//COD 1//ISO 38831027D00515// VER/DBM IDC XXXX
22397 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-02-25 07:39 | 2022-02-25 09:10 | 1 | 91 | 4544111 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on primary metering at pole 200-D1-444. This will need to opened in order to make repairs. Power restored at 09:10.
22398 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-11-25 12:23 | 2011-11-25 13:54 | 1 | 91 | 4114011 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP SHORTED OUT AT SPLICE IN MID SPAN AND BURNED NEUTRAL AND 1 HOT LEG INTO. I AM GOING TO REPLACE SERVICE DROP. I REPLACED DROP.// VER/DBM IDC XXXX
22399 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-03-19 09:59 | 2010-03-19 11:30 | 1 | 91 | 51673-1 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TRANSFORMER IN ORDER TO MAKE REPAIRS @ 1045 (SEE 51673-1)//REPAIRED SERVICE DROP.//COD 1// VER/DBM IDC XXXX
22400 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-01-21 13:00 | 2011-01-21 14:31 | 1 | 91 | 63363-1 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION VER/HFP L3/HFP IDC XXXX
22401 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-06-22 18:54 | 2015-06-22 20:25 | 1 | 91 | 4641531 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CLAMP BURNT INTO REPAIRED VER/CRB
22402 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2021-01-18 13:00 | 2021-01-18 14:31 | 1 | 91 | 4875501 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power, repairs made. pls close. tre
22403 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-01-08 19:24 | 2019-01-08 20:55 | 1 | 91 | 4644441 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm fuse blown will refuse// Broke 19.9 cutout will change/// Changed bad cutout and refused xfm @ 20:55 and restored service
22404 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-05-27 19:04 | 2018-05-27 20:35 | 1 | 91 | 4505931 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required
22405 | Paintsville | 3410602 | E.PRESTON | LANCER | 2019-11-29 07:34 | 2019-11-29 09:05 | 1 | 91 | 4101601 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse blown will check and refuse//Fuse had pulled apart inside cutout door. I refused and restored power @ 09:05//cod 1//
22406 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-08-23 13:14 | 2011-08-23 14:45 | 1 | 91 | 4748031 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1T FUSE OUT LOOKS LIKE FUSE BROKE. FUSED UP EVERYTHING OK //VER/CRB IDC XXXX
22407 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-06-04 19:17 | 2017-06-04 20:48 | 1 | 91 | 4905211 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT LEG BURNT INTO ON CUSTOMERS SERVICE IN 2 DIFFERENT PLACES, MADE REPAIRS @2048. VER/KEP
22408 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-09-17 17:59 | 2014-09-17 19:30 | 1 | 91 | 4506951 | 91 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN AT XMF SEC BUSHINGS REDONE CONN TEMP, PLEASE SEND TO STEVE M TP HAVE CSP WITH NO CUTOUT REPLACED. GOOD JOB FOR THE TRACK MACHINE. APR AT 1930 CLOSE TICKET // SENT EMAIL AS REQUESTED COD-1 ISO SO @ 38830405000071 VER/HFP L3/HFP
22409 | Pikeville | 3421002 | BREAKS | GRASSY | 2012-05-15 19:24 | 2012-05-15 20:55 | 1 | 91 | 4798981 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN /// GOING TO TRY FUSE /// POWER RESTORED AND VOLTAGE CHECKS GOOD//FUSE BROKE ///VER/CRB L/3 CRB IDC XXXX
22410 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2014-09-16 11:05 | 2014-09-16 11:18 | 7 | 13 | 4503081 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING TRANSFORMER TO CHANGE CUTOUT AT POLE 3177 OPENED AT 1105 CLOSED AT 1118 VER/CRB
22411 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-09-01 17:49 | 2012-09-01 19:20 | 1 | 91 | 4992531 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT AND LA COD-1 ISO PO @ 38830019D00266 VER/HFP L3/HFP IDC XXXX
22412 | Paintsville | 3409302 | KENWOOD | AUXIER | 2010-12-31 23:41 | 2011-01-01 01:12 | 1 | 91 | 57456-1 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP. REPLACED DOOR AND RE-FUSED @ 1:12. SH VER/ARN IDC XXXX
22413 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-07-22 14:49 | 2012-07-22 16:20 | 1 | 91 | 4794951 | 91 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OLD BOX TYPE CUTOUT APPEARS TO HAVE FAILED. REPLACED XFMR CUTOUT AND RESTORED @ 16:20. SH COD-1 ISO TF 38830882B00178 VER/HFP L3/HFP
22414 | Hazard | 3310502 | HADDIX | CANOE | 2022-09-28 13:19 | 2022-09-28 13:37 | 5 | 18 | 4933251 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Span of neutral down between poles 37840216000008 and 37840216000009--also srvc drop needs tightened at pole 216-8 // abnormal DAE# 1000074101.opened @13:19---closed @13:37 Released by crew 077H13
22415 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-05-18 08:16 | 2012-05-18 09:01 | 2 | 45 | 4805741 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000303-BROKEN FUSE LINK CC2 IDC XXXX
22416 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2012-10-08 19:35 | 2012-10-08 21:05 | 1 | 90 | 4124571 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. VER/KEP IDC XXXX
22417 | Hazard | 3303902 | LESLIE | WOOTON | 2010-03-29 14:15 | 2010-03-29 15:00 | 2 | 45 | 55588-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT/ NO POWER OFF AT THIS TIME OPENED AT 1415 CLOSED AT 1500 COD-5 VER/KEP L3/KEP AJBC TOF12:57 CALL WAS TO REPORT TROUBLE. LOC #37830365C00080 ( DOES NOT COME UP IN SYS.)
22418 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-06 19:51 | 2015-02-06 21:21 | 1 | 90 | 4997651 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKE ON POLE 207-274, REPLACE C/O POWER RESTORED.//COD3// VER/ ADH L3/HFP HFPC CNT3 PN37830207D00104
22419 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-10-06 10:23 | 2014-10-06 11:08 | 2 | 45 | H4556201 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT START TIME, BAD 19.9 KV CUTOUT AND ARRESTER, RELEASED BY CREW 077S04// SERVICER OPENING TAP ON POLE 343-A-44 TO MAKE REPAIRS//WILL WORK AT START TIME, BAD 19.9 KV CUTOUT AND ARRESTER, RELEASED BY CREW 077S04 OPEN AT 1023 CLOSED AT 1108 RELEASED BY CREW 077H04 // 1 OUT INITALLY THEN OPENED TAP @ 1023 INTERRUPTING 2 MORE CUSTOMERS /// DUP OF 4556201 FOR 2 ADDITIONAL CUST INTERRUPTED// VER/HFP L3/HFP
22420 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2009-04-28 15:40 | 2009-04-28 17:10 | 1 | 90 | 55523-1 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3200204//ON SITE CHECKING CONNECTIONS.PART POWER FOR W.MARCUM ONLY. HAD A BAD INSULINK ON SERVICE DROP. L3/HFP IDC XXXX
22421 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-09-13 12:03 | 2015-09-13 13:33 | 1 | 90 | 4234381 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE IT//////////REPLACED XFR CUTOUT AND RESTORED POWER,ALL OK AFTERWARDS// VER/ ADH
22422 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2012-05-21 16:35 | 2012-05-21 17:05 | 3 | 30 | 4814131 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUST HERE FED OFF POLE 1087D98.XFMR FEEDS 3 METERS..533595063, 533595064, & 532358368.BAD CONNECTIONS ON SECONDARY RISERS.HOT & NUETRAL CONNECTIONS..OPENED XFMR @ 16:35.REPLAXCED ALL BAD CONNECTIONS.CLOSED XFMR @ 17:05..JRV.05/21/12//MD FILED//COD 3// VER/DBM IDC XXXX
22423 | Whitesburg | 3309302 | VICCO | JEFF | 2018-02-05 14:10 | 2018-02-05 15:40 | 1 | 90 | 4807071 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr , restored power at 15:40..
22424 | Paintsville | 3409302 | KENWOOD | AUXIER | 2020-06-12 12:30 | 2020-06-12 14:00 | 1 | 90 | 4009891 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection on hot leg at weather had had went bad and burnt conductor n2. I was able to repair and restore customer to full power @14:00
22425 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-05-25 14:27 | 2012-05-25 14:36 | 10 | 9 | 4830781 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FAILED CONNECTION AT THE TRANSFORMER ON THE SECONDARY SIDE. I OPENED THE TRANSFORMER AT 1427 AND CLOSED BACK AT 1436 ///VER/CRB L/3 CRB IDC XXXX
22426 | South Williamson | 3200302 | BELFRY | TOLER | 2021-10-30 19:45 | 2021-10-30 20:30 | 2 | 45 | 4042051 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | cust service had a bad spot in a hot lead and it burned the neutral into.i opened transformer on pole 1063A-6 up @ 19:45 .cut bad spot out of cust service and splice new wire in.got the fuse on pole 1063A-6 back in at 20:30
22427 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-06-30 15:06 | 2020-06-30 15:21 | 6 | 15 | 4094281 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Checked voltage at METER and only had one hot leg,Opened underground cabinet and found one hot leg burned into,Called Steve Ray and there bringing add a Phase so we can get customer back on until we get it fixed..Opened XFM at 15:06 and closed it back in at 15:21.//MADE DAE
22428 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2013-08-05 13:30 | 2013-08-05 14:15 | 2 | 45 | 4623541 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 69-6032 TRANS. LEAKING OIL NEEDS CHGED TODAY NO OUTAGE NEED 25KVA ALSO NEED FLAGGERS TRUCK TO POLE RELEASED BY CREW 078S08,,,REPLACED XFMR,,,OFF 13:30, ON 14:15 VER/CRB L/3 CRB
22429 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2014-01-30 14:25 | 2014-01-30 15:10 | 2 | 45 | H4329681 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3309104 // REMOVED JUMPER ON WRONG ORDER MADE ORDER DUP // BAD 25 KVA XFMR ON POLE 401-13, WILL NEED FLAGGERS TOOK 2 POLE TAP OFF @ 1425 ON @ 1510 1 CUST // 7 CUST ON THIS TR ON POLE 37830401C00013 DUP IN HOIS VER/HFP L3/HFP
22430 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2018-12-08 17:50 | 2018-12-08 19:20 | 1 | 90 | 4518431 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | wait till monday morning, ok per customer ops order # 033445191, storms wr 71936765 Released by crew 077S12//bad 300 kva transformer 37830449A21007//WILL WORK ON MONDAY//COD 1//SENT TO WHITESBURG LINE DEPT// L3/HFP
22431 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-04-05 10:11 | 2014-04-05 11:41 | 1 | 90 | 4577371 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XMF FUSE BLOWN, ARRESTER AND CUTOUT HAD JUST BEEN REPLACED LAST WEEK LOOKED LIKE FUSE HAD PULLED LOOSE, REFUSED XMF APR AT 1141 CLOSE TICKET//COD 1// VER/DBM IDC XXXX
22432 | Whitesburg | 3312902 | JENKINS | JENKINS | 2014-04-30 08:00 | 2014-04-30 09:30 | 1 | 90 | 4650101 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON UNDERGROUND RISER POLE . WE CHANGED TWO CUTOUTS AND MADE BACK HOT//COD 1// VER/DBM
22433 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2021-07-11 12:45 | 2021-07-11 14:15 | 1 | 90 | 4891151 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad xfm cutout on 38831146A20307//Will be replacing
22434 | Whitesburg | 3312901 | JENKINS | KONA | 2008-05-22 21:00 | 2008-05-22 21:30 | 3 | 30 | 50630-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3312901// HOT LINE CLAMP IS BURNED OFF I WILL BE REPLACING REPLACED HOT LINE CLAMP//COD 3// VER/DBM IDC XXXX
22435 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-02-19 12:55 | 2020-02-19 14:25 | 1 | 90 | 4418421 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | Broke cutout on pole#247-640. XFMR bank opened from 14:10 closed back at 14:25 L3/HFP
22436 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2011-07-25 09:25 | 2011-07-25 10:55 | 1 | 90 | 4616801 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT. VER/KEP IDC XXXX
22437 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2010-12-26 10:04 | 2010-12-26 11:34 | 1 | 90 | 55780-1 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN SERVICE DROP ONLY ONE CUSTOMER AFFECTED, MADE REPAIRS RESTORED POWER AT 11:34// VER/DBM IDC XXXX
22438 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-05-10 22:45 | 2017-05-11 00:15 | 1 | 90 | 4778821 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED CONNECTIONS ON POLE 150-77//COD 1//ISO// VER/DBM
22439 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-12-16 12:35 | 2013-12-16 14:05 | 1 | 90 | 4165841 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT POLE 139-B-408 REPLACED BAD CUTOUT EVERYTHING OK//COD 1// VER/DBM L3/HFP
22440 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2012-08-17 09:35 | 2012-08-17 10:05 | 3 | 30 | 4946001 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUTOUT CHGED BAD CUT OUT POLE 139-235 OPENED LINE 09;35 TO 10;05 SEND NOTE TO TREE PEOPLE LINE NEEDS CUT BAD NEED BACK YARD THING IDC XXXX
22441 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-05-04 19:11 | 2008-05-04 19:20 | 10 | 9 | 56988-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000301//SERVICER OPENED TRANSFORMER TO REPAIR BAD CONNECTION... SEE ORDER 56984-1//COD 10// VER/DBM IDC XXXX
22442 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-09-30 13:20 | 2011-09-30 13:50 | 3 | 30 | 4934131 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND TWO BAD CONNECTIONS, AND CHANGED BAD ARRESTER TIME OFF 1320---TIME ON 1350 CLOSE TICKET COD-3 ISO PO 38830454B33134 VER/HFP L3/HFP IDC XXXX
22443 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-09-10 15:19 | 2011-09-10 16:49 | 1 | 90 | 4855181 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET BROKE COD-1 ISO TF 38830045A10163 VER/HFP L3/HFP IDC XXXX
22444 | Hazard | 3303902 | LESLIE | WOOTON | 2008-10-30 14:30 | 2008-10-30 15:00 | 3 | 30 | 60900-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP FUSE ROTTED INTO REPLACED FUSE COD-3 IDC XXXX
22445 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2012-07-15 18:51 | 2012-07-15 19:21 | 3 | 30 | 4734081 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OPENED LINE FUSE ON POLE 38830045D16045 AT 19:00--E MAIL TO MARTIN--POLE 38830045D16045 NEEDS REPLACED---HOT LEG TO GROUND WIRE CAUSED POLEFIRE//COD 18//ISO//EMAILED TO S MARTIN
22446 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-10-16 23:42 | 2017-10-17 01:12 | 1 | 90 | 4464061 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SECONDARY/// REPAIRED BAD CONNECTION AND RESTORED SERVICE// GOOD VOLTAGE NOW 124/124/248/// ONLY ONE CUSTOMER AFFECTED// VER/DBM L3/HFP XXXHFP
22447 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-09-01 07:50 | 2022-09-01 09:20 | 1 | 90 | 4824991 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | current limiting fuse bad on a phase xfmer/crew reqd Released by crew 078S04///Complete BR
22448 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-11-14 17:30 | 2013-11-14 19:00 | 1 | 90 | 4039601 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE. VER/CRB L3 / JP
22449 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2012-04-30 09:15 | 2012-04-30 10:45 | 1 | 90 | 4722451 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP. I AM GOING TO CHANGE CUTOUT DOOR. I CHANGED DOOR. ///VER/CRB L/3 CRB IDC XXXX
22450 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2013-04-16 10:57 | 2013-04-16 11:15 | 5 | 18 | 4012941 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER UP AT 10:57, AND CLOSED IT AT 11:15. COD-5 ISO TF 38821137A00347 VER/HFP L3/HFP IDC XXXX
22451 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-05-14 19:30 | 2015-05-14 21:00 | 1 | 90 | 4431071 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY RISER IN XFMER BROKE AT HOTTAP///MAKING REPAIRS///REPAIRS MADE///XFMER BACK ONLINE AT 21:00///COMPLETE BR VER/CRB
22452 | Whitesburg | 3312901 | JENKINS | KONA | 2022-10-25 08:45 | 2022-10-25 10:15 | 1 | 90 | 4061631 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer had bad neutral. replaced service. open transformer @ 08:45 closed @ 10:15
22453 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-06-04 14:42 | 2012-06-04 16:12 | 1 | 90 | 4880661 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 141-239. I HAVE CUTOUT REPLACE FUSED UP EVERYTHING OK. 6T FUSE COD-1 ISO TF 37830141000239 VER/HFP L3/HFP IDC XXXX
22454 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-02-28 16:10 | 2017-02-28 17:40 | 1 | 90 | 4429361 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: FUSE OUT ON POLE. BAD C/O POLE 92 B 4081 38830092B34081 VER/AWD
22455 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-04-25 13:45 | 2013-04-25 14:30 | 2 | 45 | 4047581 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT HAS WENT BAD ON POLE # 302-214, REPLACED CUTOUT AND RE-FUSED VER/KEP IDC XXXX
22456 | Pikeville | 3421001 | BREAKS | CITY | 2014-10-03 17:50 | 2014-10-03 18:20 | 3 | 30 | H4548791 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN ON SERVICE DROP//// OPENED TRANSFORMER BANK ON POLE #220-C2-83 @ 17:50 MADE REPAIRS AND CLOSED TRANSFORMERS BACK IN @ 18:20 ///RESTORED SERVICE VER/CRB
22457 | Pikeville | 3408101 | SALISBURY | PRINTER | 2011-12-26 16:35 | 2011-12-26 17:20 | 2 | 45 | 4202741 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 074S11 LOOKS LIKE SPAN OF OPEN WIRE BURNT DOWN UNDERNEATH COMPRESSION CONNECTOR. I OPENED TRANSFORMER UP AT 16:35 BACK ON AT 17:20. I HAVE OPEN WIRE BACK UP EVERYTHING OK ///VER/CRB IDCC TON1730 XXXX
22458 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-08-21 09:45 | 2020-08-21 10:15 | 3 | 30 | 4353491 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING DEFECTIVE CUTOUT ¦¦ COD-3 ISO TF 37830247A00153 OFF@ ON@ XFMR off at 9:45 back on at 10:15.
22459 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2013-06-12 16:00 | 2013-06-12 16:18 | 5 | 18 | 4265131 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED ARRESTER AND CUTOUT ON 38830454D40079. TIME OFF 1600 TIME ON 1618 APR CLOSE TICKET VER/KEP IDC XXXX
22460 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-04-05 13:15 | 2010-04-05 14:45 | 1 | 90 | 58853-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT == CHANGED CUTOUT == POWER OK COD-1 VER/HFP L3/HFP IDC XXXX
22461 | South Williamson | 3411401 | DEWEY | INEZ | 2016-03-12 11:40 | 2016-03-12 12:10 | 3 | 30 | 4838831 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 769-21//REPAIRS MADE//RESTORED AT 12:10///COMPLETE//EM // COD-3 ISO TF 38820770A00021 VER/HFP L3/HFP
22462 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2015-01-28 07:00 | 2015-01-28 08:30 | 1 | 90 | 4968981 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNT DOWN/OPEN TRANSFORMER POLE 37830068000096/SPLICE IN 2/3 DROP HEATED UP AND BURNT 2/3 SERVICE DROP DOWN. I OPENED UP AT 07:00 REPLACED 2/3 DROP WITH NEW 2/3 SERVICE DROP CLOSED TRANSFORMER BACK IN AT 08:30. SEND COPY TO PEGGY IN DAMAGE CLAIMS CUST COULD POSSIBLY CALL IN. DROP WAS BURNT INTO ABOUT 15 FOOT FROM WEATHER HEAD DROP HAD BEEEN SPLICED // COD 2/MAP DESCREPANCY MADE/ADH HARVEY SAID THIS WAS ACUTALLY ON POLE 96 WITH 2 CUSTOMERS ON IT//VER/ ADH
22463 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-11-16 09:00 | 2015-11-16 10:30 | 1 | 90 | 4450511 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | REPAIRING UNDERGROUND AND REMOVING ADDAPHASE/// ON SITE TO MAKE REPAIRS./// MADE REPAIRS AND RESTORED POWER AT 10:30 TIM MCCOY RELEASED BY CREW 074H10/ OPENED 0900/ ISO 38831126A00316/ COD 1/ VER/BOW
22464 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-08-29 13:01 | 2018-08-29 13:31 | 3 | 30 | 4011551 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4011101 - CREW HAD OUTAGE ON LINE AND FOUND CUTOUT BAD. HAD TO OPEN THIS TRANSFORMER TO ALLOW THEM TO REPLACE THEM SAFELY// COD-3 ISO TF 37830426D00009 // opened @ 1301 Closed @ 1331
22465 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-01-30 20:35 | 2013-01-30 22:05 | 1 | 90 | 4763891 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BURNT UP CUTOUT DOOR. REPLACED DOOR FUSED UP EVERYTHING OK//COD 1// VER/DBM IDC XXXX
22466 | Pikeville | 3413402 | GARRETT | LACKEY | 2017-10-08 22:35 | 2017-10-08 23:20 | 2 | 45 | 4424901 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BAD POLE 32 , OPENED XFMR POLE 37830087D00032 @ 22:35. REPLACED CUTOUT AND RESTORED @ 23:20, ALL WORK COMPLETE / GXJ //ISO //COD 2// VER/DBM VER/HFP L3/HFP
22467 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-07-24 16:00 | 2018-07-24 16:45 | 2 | 45 | 4847841 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 7200 c/o. trk to pole 117-133. to l. mccoy Released by crew 078S07 crew on site open xfmr @ 16:00 complete xfmr in @ 16:45 please close ticket LRM
22468 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-12-20 22:40 | 2021-12-20 23:10 | 3 | 30 | 4215391 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Neutral connection and 1 hot leg connection was burnt open @ xfm///Opened xfm @ 22:40 and made repairs ///Closed xfm back in @ 11:10 and restored service//Good voltage @ meter 123/123/246
22469 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-01-01 14:16 | 2010-01-01 15:46 | 1 | 90 | 55699-1 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHESD VER/HFP L3/HFP IDC XXXX
22470 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-04-18 14:45 | 2016-04-18 16:15 | 1 | 90 | 4100741 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED A CONNECTION ON ONE OF THE SECONDARY PHASE WIRES AT THE WEATHERHEAD. VER/CRB
22471 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-07-16 22:09 | 2013-07-16 23:39 | 1 | 90 | 4534271 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE-IN CONNECTIONS ON XFR POLE.RE-WORKED THESE AND CORRECTED PROBLEM.ALSO AN ANCIENT XFR HERE THAT IS LEAKING A LITTLE OIL,IT SHOULD BE REPLACED.SEND TO TECHNICIAN FREEMAN IN PVILLE VER/CRB L/3 CRB
22472 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2010-10-17 11:50 | 2010-10-17 12:35 | 2 | 45 | 60400-1 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPEN-WIRE-SECONDARY DOWN. CUSTOMERS SERVED FR XFMR 785-554 WERE NOT AFFECTED UNTIL I OPENED XFMR @ 11:50 TO MAKE REPAIRS. TWO CUSTOMERS HAD PART POWER AND THREE HAD FULL POWER. REPAIR UNDERWAY. ONE HOT CONDUCTOR PULLED OUT OF SLEEVE AT XFMR POLE. REPAIRED AND RE-SQUEEZED SECONDARY RISER CONNECTIONS. RESTORED @ 12:35. SH//VER/CRB IDC XXXX
22473 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-05-27 10:00 | 2017-05-27 10:15 | 6 | 15 | 4869561 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD NEUT. IN SD. NXFMER OFF @ 10:00, ON @ 10:15 VER/CRB
22474 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-12-22 11:40 | 2010-12-22 13:10 | 1 | 90 | 55036-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WORK REQ 38188025 // UPGRADE FROM 15-50 MAP DISC FILED// VER/TOM IDC XXXX
22475 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2020-11-19 12:34 | 2020-11-19 12:49 | 6 | 15 | 4708661 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 37830067A00108//OFF AT 1234 ON AT 1249
22476 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2012-12-28 14:10 | 2012-12-28 14:40 | 3 | 30 | 4545051 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER WIRE IN BANK OF TRANSFORMERS IS ABOUT TO BURN INTO. PAUL LAYNE IS COMING TO CHANGE WIRES. RELEASED BY CREW 074S01,, WORK COMP. POWER BACK ON TOOK XFMR BANK OFF AT 14:10 CLOSED BACK ON AT 14:40//COD 3// VER/DBM
22477 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-09-27 12:30 | 2011-09-27 13:15 | 2 | 45 | 4924311 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RESQUIZED ALL GROUNDS ON XFORMER POLE. PRIMARY NEUTRAL DOWN FROM POLE 286-106 TO 286-105.XFORMER OPENED AT 12:30 BACK ON AT 13:15. /// VER/KEP IDC XXXX
22478 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2012-12-26 10:20 | 2012-12-26 11:50 | 1 | 90 | 4523951 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | HOT TAP LEAD BROKEN ON B PHASE CUTOUT ON 3 PHASE PRIMARY UG POLE-RAYBURN GETTING CREW RELEASED BY CREW 078S07CORRECT CUSTOMER COUNT IS ONE (HAGAER ELEMENTARY SCHOOL)..BLR //VER/GAH
22479 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2018-02-06 09:44 | 2018-02-06 11:14 | 1 | 90 | 4808631 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | bad meter#190 218 524,change meter
22480 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2020-08-11 23:30 | 2020-08-12 00:15 | 2 | 45 | 4311201 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | per fieldview 10kva leaking--will need to remove 5 circle of dirt Released by crew 078S01
22481 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-01-24 12:50 | 2011-01-24 14:20 | 1 | 90 | 63909-1 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD PLACE IN SERVICE CONDUCTOR, REPLACED SERVICE//VER/CRB IDC XXXX
22482 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-12-05 13:45 | 2016-12-05 15:15 | 1 | 90 | 4166621 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTON AT XFMR , REPLACED LEADS & CONNECTIONS , RESTORED POWER AT 15:15.. VER/CRB L3/HFP XXXHFP
22483 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-03-03 10:39 | 2022-03-03 12:09 | 1 | 90 | 4562931 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINEF IS OUT//////XFR CUTOUT BROKEN POLE 1105-267,WILL REPLACE IT,THEN RE-FUSE LINEF@1105-22/////////REPAIRS COMPLETED,POWER RESTORED@12:09
22484 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2017-11-27 12:07 | 2017-11-27 12:52 | 2 | 45 | 4604451 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED L/F 37830030000016 TO REPLACE CUTOUT ON POLE 37830030000102 OFF 1230 ON 1252
22485 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-10-30 21:00 | 2010-10-30 21:30 | 3 | 30 | 50334-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37557848 //NO CREW REQUIRED REPLACED BAD CUTOUT /// COD-3 VER/HFP L3/HFP IDCC TOF 2012 ALLOWED TIME FOR REPAIR XXXX
22486 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-06-09 13:00 | 2020-06-09 13:45 | 2 | 45 | 4984331 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad 12kv door
22487 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-12-05 13:49 | 2009-12-05 13:59 | 9 | 10 | 56660-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER AT 13:49 TO MAKE REPAIRS-BACK ON AT 13:56 VER/KEP L3/KEP IDC XXXX
22488 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-04-09 17:40 | 2014-04-09 18:10 | 3 | 30 | 4590101 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XFORMER AT 17:40 BACK ON AT 18:10 , 4/3 SERVICE DROP VER/CRB
22489 | Whitesburg | 3312901 | JENKINS | KONA | 2011-06-23 19:30 | 2011-06-23 20:00 | 3 | 30 | 4402171 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I OPENED XFMR AT 19:30 AND CHANGED CENTER LEAD IN THE XFMR AND CLOSED BACK AT 20:00 VER/ARN IDC CHANGED START TIME FROM 1711 XXXX
22490 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-04-24 23:00 | 2009-04-24 23:30 | 3 | 30 | H59225-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUSTOMER SAW FIRE SHOOTING OUT OF XFMR. COULD NOT SEE ANYTHING WRONG, BUT WILL OPEN XFMR AND CLIMB UP TO CHECK SECONDARY CONNECTIONS. WHEN I RE-ENERGIZED XFMR ARRESTER BLEW APART AND BLEW LINE FUSE ON POLE 787-1 AT 23:00. REPAIR IN PROGRESS. ISOLATED AND CLOSED LINE FUSE AT 23:30. PROBLEM ON XFMR NOW. REPAIRED A CONNECTION. ALL OK. SH ALSO SEE 59225-1 VER/LDA IDC XXXX
22491 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-02-06 12:05 | 2008-02-06 12:35 | 3 | 30 | 51052-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409301//..NEUTRAL BROKEN IN MID SPAN..CANNOT GET TRUCK TO BREAK WILL HAVE TO CLIMB POLE AND LET SEC DOWN...OPEN CUTOUT ON XFMR// VER/TOM L3/DEBBIE IDC XXXX
22492 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2020-05-02 10:00 | 2020-05-02 11:30 | 1 | 90 | 4787331 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse
22493 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-12-23 08:15 | 2022-12-23 09:45 | 1 | 90 | 4304561 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse melted out. replaced 6t fuse..
22494 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2020-09-18 11:25 | 2020-09-18 12:55 | 1 | 90 | 4475591 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING TO CHANGE BAD CUTOUT // COD 1 // OFF@1125 ON@ 1255 power restored at 12:55
22495 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-09-15 18:45 | 2009-09-15 20:15 | 1 | 90 | 59665-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK REQUEST # 31729256 /// 50KVA 199, 480 THIS IS AT COCHRAN INDUSTRIES, THE OLD COLLEY BLOCK, OUT BACK NEXT TO THE CREEK. RELEASED BY CREW 074S08WORK REQUEST # 31729256 /// 50KVA 199, 480. RELEASED BY CREW 074S08//TRANSF LEAKING OIL FROM SECONDARY BUSHING. OPENED BANK UP AT 18:45 TO CHANGE X-FMR. , BACK IN SERVICE AT 20:15. OIL SPILL CLEAN UP COMPLETE. DEH. RELEASED BY CREW 074H03 VER/KEP L3/KEP IDCC TOF1815 XXXX
22496 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-11-21 16:25 | 2022-11-21 17:10 | 2 | 45 | 4169761 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored 17:10
22497 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-11-14 08:15 | 2012-11-14 09:00 | 2 | 45 | 4396051 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT SERV TO CHANGE,REPAIRS MADE ALL CUST RESTORED@0900 PLEASE CLOSE TICKET THANKS.BT VER/KEP IDC XXXX
22498 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2013-03-23 12:40 | 2013-03-23 13:25 | 2 | 45 | H4949751 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 4949751// LINE FUSE BUSTED ON POLE 517-14, WILL NEED 1 MAN AND BIG BUCKET TO HELP CHANGE. WILL HAVE TO OPEN RECLOSER AND STEP DOWN AT POLE 517-85 TO ISOLATE C/O. WILL KEEP TRACK OF TIMES.OPENED AT 12:40 CLOSED AT 13:25. ALL POWER RESTORED.//COD 2 // VER/DBM IDC XXXX
22499 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-05-15 14:07 | 2022-05-15 14:52 | 2 | 45 | 4892811 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed on 760-1022. Replaced and restored @ 14:52. sh
22500 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-02-26 18:29 | 2012-02-26 19:14 | 2 | 45 | H1165380-1 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TENSION SPLICE IN 2/3 TRIPLEX NEUTRAL PULLED FREE. REPLACED POWER RESTORED. OPENED TRANSFORMER AT 1829 CLOSED AT 1914 COD-3 ISO TF 37830202000040 DUP FROM 4509201 VER/HFP L3/HFP IDC XXXX
22501 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-08-21 17:21 | 2015-08-21 17:51 | 3 | 30 | 4161911 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS ON SERVICE AND IN CUSTOMERS BREAKER BOX/// RE-DONE CONNECTONS ON OUR SIDE AND CUSTOMER MADE REPAIRS ON THEIR SIDE/// OPENED XFM @ 17:21 AND CLOSED BACK IN @ 17:51/ ISO 37830071000161/ COD 3/ VER/BOW
22502 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-11-30 08:15 | 2012-11-30 09:45 | 1 | 90 | 4432651 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO LET SERVICEDROP DOWN AND RESPICE NEUTRAL COND. XMF OFF AT 0815 ON AT 0945 APR CLOSE TICKET DWEST. ////VER/CRB L/3 CRB IDCC TON1028 XXXX
22503 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-02-01 17:50 | 2008-02-01 18:05 | 6 | 15 | 64677-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410602//WILL BE REPLACEING BAD CUTOUT ON POLE#38830979D00025 WILL HAVE APROX. 7 CUOSTOMERS OUT FOR APROX 15 MIN. G.R.//COD 6//OFF 1750 ON @ 1805//CROSSARMS ARE BURNT... OK FOR NOW BUT SEND TO ENGINEERING// VER/DBM IDCC PN NULL XXXX
22504 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-04-02 15:20 | 2008-04-02 16:50 | 1 | 90 | 63176-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3410501//3410501 PULLEND LOOSE AT TRANSORMER CONNECTION - // REPLCAED SERVICE DROP /// VER/TOM IDC XXXX
22505 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-02-24 15:15 | 2009-02-24 16:45 | 1 | 90 | 51135-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR 10 KVA 19.9 KV-120/240 NSPOKE WITH DAVE SAMMONS IN PIKEVILLE HE IS SENDING CREW TO REPLACE XFMR RELEASED BY CREW 074S04 CREW ON SITE TAKE APPROX. 45 MINS R RAY VER/KEP L3/KEP IDC XXXX
22506 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-10-22 22:00 | 2011-10-22 22:45 | 2 | 45 | 4010901 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN SPAN OF SECONDARY CONDUCTOR HAS BURNED INTO. I AM GOING TO SPLICE NEUTRAL. I OPENED TRANS. ON POLE 216-61 LONG ENOUGH TO SPLICE WIRE. THIS CUSTOMER WAS ONLY ONE ON TRANS. I CLOSED TRNS AT 22:45. SEND TO JOHN FREEMAN IN ENG. DEPT. WE NEED TO CHANGE LONG SPAN OF 2/3 SECONDARY BETWEEN POLES 216-61 AND 204. WIRE HEATED UP IN SPLICE AND BURNED NEUTRAL INTO.CUSTOMER HAS DAMAGES. HE WILL CALL IN COMPLAINT MONDAY. IDCC TOF2056 ESTIMATED TIME OFF XXXX
22507 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-11-08 14:18 | 2019-11-08 15:48 | 1 | 90 | 4012681 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral was broke @ customer weather head made repairs..
22508 | Hazard | 3309302 | VICCO | JEFF | 2010-10-03 15:45 | 2010-10-03 16:30 | 2 | 45 | H56429-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 56429-1//OPEN X-FMR AT 15:45 (INTERRUPTING 2 MORE CUSTOMERS) CLOSED AT 16:30 POWER RESTORED. // SENT TO D CHRISTIAN AND P WYSONG // VER/DBM IDC XXXX
22509 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-03-11 23:45 | 2009-03-12 00:30 | 2 | 45 | 57415-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKEN IN SERVICE. DIFFICULT LOCATION - WILL HAVE TO OPEN XFMR ON POLE 38830782000029 TO MAKE REPAIRS. CUSTOMERS NOTIFIED. REPAIRS COMPLETE. HAD XFMR OPEN FROM 11:45 TO 00:30. SH //VER/GAH IDCC MCCNI TOF TON XXXX
22510 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-09-24 16:01 | 2015-09-24 16:46 | 2 | 45 | 4266781 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 21-2058 6T TRANS FUSE BROKE REPAIRED/ ISO 38830021B12058/ COD 2/ VER/BOW
22511 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-06-15 09:25 | 2013-06-15 10:55 | 1 | 90 | 4341391 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED APART AT POLE 520-04, REFUSED AT 10:55.//COD 1// VER/DBM IDC XXXX
22512 | Hazard | 3303902 | LESLIE | WOOTON | 2014-05-30 19:20 | 2014-05-30 20:50 | 1 | 90 | 4955371 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT//COD 1// VER/DBM
22513 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-03-31 08:01 | 2008-03-31 09:31 | 1 | 90 | 62287-1 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309104//REPLACED CONNECTIONS ON POLE//COD 1// VER/DBM IDC XXXX
22514 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-10-11 08:30 | 2011-10-11 10:00 | 1 | 90 | 4963621 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACEING SEVERAL CONN,, MADE TWO NEW CONN AT XMF BANK B AND C CONN. ALSO CHECKED CONN AT WEATHER HEAD, HAD A AND B PHASES OUT ALL POWER RESTORED AT 1000 CLOSE TICKET//COD 1// VER/DBM IDC XXXX
22515 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-12-03 10:50 | 2010-12-03 11:20 | 3 | 30 | 62701-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STEVE MARTIN REPORTED A BROKEN NEUTRAL HERE THAT NEEDS CHECKED REPAIRED 1/0 SEC TRANS OPEN 10;50 TO 11;20 VER/KEP L3/KEP IDC XXXX
22516 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-04-02 19:50 | 2009-04-02 21:20 | 1 | 90 | 64310-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHG CUTOUT..BB VER/TOM L3/TOM IDC XXXX
22517 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-01-01 19:35 | 2014-01-01 21:05 | 1 | 90 | 4217611 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 21:05 VER/KEP
22518 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-06-11 10:45 | 2018-06-11 12:15 | 1 | 90 | 4582881 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burndt into in 2 different locations on a service, made repairs @1215.
22519 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2017-10-16 16:25 | 2017-10-16 17:55 | 1 | 90 | 4463211 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION AT THE TRANSFORMER, ONLY ONE CUSTOMER AFFECTED./ ISO 37830188C00012/ COD 1/ VER/BOW L3/HFP XXXHFP
22520 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-01-09 16:51 | 2010-01-09 18:21 | 1 | 90 | 51500-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | MADE REPAIRS AND RESTORED,CONNECTIONS GOT TOGETHER AT XFR,SHORTED AND BURNED ONE INTO.SAID SPARKS FELL ONTO HOOD OF TRUCK UNDER POLE AND DAMAGED THE HOOD.WILL PROBABLY HEAR FRM CUST ABT THIS,TOO DARK TO VERIFY AT THE TIME VER/KEP L3/KEP1 IDC XXXX
22521 | Whitesburg | 3312901 | JENKINS | KONA | 2015-03-11 21:00 | 2015-03-11 21:30 | 3 | 30 | 4184861 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CHANGED OUT CUTOUT AND PUT OUT POLE FIRE, I OPENED XFMR AT 21:00 CLOSED BACK AT 21:30 VER/CRB L3/DKGXXXX
22522 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-01-15 11:25 | 2012-01-15 12:55 | 1 | 90 | 4262301 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. VER/KEP IDC XXXX
22523 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-05-27 10:00 | 2013-05-27 10:15 | 6 | 15 | H4187641 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE NEUTRAL BROKE INTO AT THE XFMR POLE, I REPAIRED IT . I OPENED THE XFMR AT 10:00 AND CLOSED IT BACK AT 10:15. CUSTOMER SEEMS TO HAVE A LOT OF DAMAGES HE WILL BE CALLING DUP IN HOIS FOR 6 CUST........SEF DUPLICATE FROM 4187641 VER/SEF IDC XXXX
22524 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-01-06 14:00 | 2015-01-06 14:30 | 3 | 30 | 4910791 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFROMER 37830175000121/ ISO 37830175000121/ COD 3 OPENED TRANSFORMER AT 14:00, REMADE CONNECTIONS, CLOSED AT 14:30, POWER RESTORED./ VER/BOW L3/DKGXXXX
22525 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-04-16 09:51 | 2014-04-16 11:21 | 1 | 90 | 4611361 | 90 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION..RE SQUEEZED CONN. TRIMMED TREE. VER/HFP L3/HFP
22526 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-07-10 12:07 | 2019-07-10 13:37 | 1 | 90 | 4689721 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1126-C-789, checking.Fuse had melted out, refused @1337.
22527 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2009-08-07 09:38 | 2009-08-07 10:23 | 2 | 45 | 57821-1 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE APPEARS TO HAVE BROKE. RE-FUSED XFMR. SH//COD 2// VER/DBM IDC XXXX
22528 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-10-01 13:50 | 2020-10-01 15:20 | 1 | 90 | 4518091 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke in cutout causing door to drop,Refused and restored at 15:20..
22529 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-07-09 15:15 | 2012-07-09 16:00 | 2 | 45 | 4640471 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACE SOME 2/3 SERVICE DROP AND REWORK TRANSFORMER POLE, CHECK VOLTAGE AT TRANSFORMER AND METER, WAS ALL GOOD AT 1600 CHANGED TIME OFF TO AFTER SERVICER ARRIVED COD-2 ISO TF 39831073B22518 VER/HFP L3/HFP IDC XXXX
22530 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2015-02-14 13:00 | 2015-02-14 13:15 | 6 | 15 | 4015201 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING TRANSFORMER 45-7508 TO REPAIR BROKEN HOT TAP/REPLACE CUTOUT AND BROKEN HOT TAP CONN. OFF 13:00 TO 13:15/NO ONE OUT UNTIL SERVICER OPENED/COD 6// VER/ ADH L3/HFP XXX
22531 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-05-20 15:01 | 2013-05-20 16:31 | 1 | 90 | 4139661 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT . NO TRUCKS ,NEED LINE CREW. RELEASED BY CREW 078S01/CREW ON SITE/FETR1700/VEM COD-1 ISO TF 38830164000188 VER/HFP L3/HFP IDC XXXX
22532 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2012-02-16 13:30 | 2012-02-16 15:00 | 1 | 90 | 4353491 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A CUTOUT FAILED ON THIS PRIMARY METERING POLE. I REPLACED THE BAD CUTOUT. ///VER/CRB IDC XXXX
22533 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-06-23 13:38 | 2022-06-23 15:08 | 1 | 90 | 4300401 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Bad arrestor on a CSP on pole 251-87 blew the line fuse on pole 251-4. I cut this arrestor in the clear and restored this 15T fuse at 15:08.//L/F NOT SHOWN ON MAP//MADE MD
22534 | Pikeville | 3401001 | ELWOOD | DORTON | 2012-04-17 14:00 | 2012-04-17 14:45 | 2 | 45 | 4679971 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN SPAN OF SECONDARY CONDUCTOR HAD RUBBED AGAINST A BOLT ON SEC. POLE AND BROKEN INTO. I AM GOING TO SPLICE NEUTRAL. I SPLICED NEUTRAL.// VER/DBM IDCC NOT PART POWER, DIM LIGHTS TOF1306 ESTIMATED TIME OFF FOR REPAIR, PN129 XXXX
22535 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-07-02 11:39 | 2015-07-02 12:24 | 2 | 45 | 4708881 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACING SECONDARY/ SECONDARY WAS TORE UP/ ISO 37830247A01189/ COD 2/ OPENED AT 11 39 CLOSED BACK AT 12 24 REPAIRS MADE/ VER/BOW
22536 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-05-17 18:15 | 2016-05-17 19:00 | 2 | 45 | 4227551 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED TRANSFORMER ON POLE 67-102 AT 18:15 DUE TO BAD CUTOUT. BURNT PLACE BACK IN POLE. I CHANGED CUTOUT AND CLOSED TRANSFORMER FUSE BACK IN AT 19:00. SEND COPY TO ENG WILL NEED TO LOWER THINGS DOWN ON POLE OR CHANGE POLE AT SOME TIME/ ISO 37830067A00102/ COD 2/ VER/BOW
22537 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-07-09 22:15 | 2013-07-09 23:45 | 1 | 90 | 4493921 | 90 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | BY PASSED PRIMARY METERINGON POLE164-411, NEED LINE CREW TO REPLACE ASAP. IDCC TOF2052, ESTIMATED TIME OFF XXXX
22538 | Paintsville | 3409302 | KENWOOD | AUXIER | 2010-02-15 16:40 | 2010-02-15 18:09 | 1 | 89 | 58038-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE HAS SPLICE WHERE CUSTOMER SAW SMOKE. REPLACED #4 SERVICE WITH #2. <<ONLY ON CUSTOMER AFFECTED>> SH VER/KEP L3/KEP IDC CHANGED START TIME FROM 1512 XXXX
22539 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-11-29 12:31 | 2013-11-29 14:00 | 1 | 89 | 4087751 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | AFTER RESQUEEZING EVERYTHING ON THE HOUSE AND POLE FOUND A BROKEN NEUTRAL ON A 2/3 SERVICE DROP, HAVE REPAIRS MADE AND EVERYTHING IS OK AT THIS LOC VER/CRB
22540 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-07-12 01:41 | 2012-07-12 03:10 | 1 | 89 | 4692731 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKE AND BURNT CUTOUT DOOR UP. REPLACING DOOR AND RE-FUSING. RESTORED @ 3:10. SH //VER/GAH
22541 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-01-05 17:11 | 2015-01-05 18:40 | 1 | 89 | 4908771 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POWER RESTORED/ ISO 37830353B00027/ COD 1/ VER/BOW
22542 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-07-17 12:03 | 2011-07-17 13:32 | 1 | 89 | 4555611 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRING CONNECTION//VER/CRB IDC XXXX
22543 | Hazard | 3302703 | HAZARD | HAZARD | 2012-11-13 15:57 | 2012-11-13 17:26 | 1 | 89 | 4394731 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE BAD ON SERV ==HOT LEG === REPLACED SERV === VER/HFP L3/HFP IDC XXXX
22544 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-02-16 22:06 | 2009-02-16 23:35 | 1 | 89 | 62814-1 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE HOT LEG OF THE SERVICE DROP WAS BURNED APART. VER/KEP L3/KEP
22545 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-10-23 16:46 | 2013-10-23 18:15 | 1 | 89 | 4957641 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN ON POLE 472-12, CUTOUT IS BROKEN WILL REPLACE. REPLACED CUTOUT & RESTORED POWER AT 1815 VER/CRB L/3 CRB
22546 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-02-28 15:41 | 2016-02-28 17:10 | 1 | 89 | 4784091 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD INSULINK @ WEATHERHEAD REPAIRS MADE CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/HFP L3/HFP
22547 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2012-01-13 15:42 | 2012-01-13 17:11 | 1 | 89 | 4259081 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVIN HAD FROZEN APART . REPLACED SERVICE DROP VER/KEP IDC XXXX
22548 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-12-27 12:46 | 2015-12-27 14:15 | 1 | 89 | 4564281 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | S/D BURNED IN TWO//WILL REPLACE// SERVE-IN HEATED UP AND BURNED NEUT IN TWO //REPLACED S/D // POWER RESTORED @ 14:15 // CUST. WANTS TECH. TO CHECK POLE 37830048C31078 // SEND TO C. FREEMAN/EMAILED TECH/ADH// VER/ ADH
22549 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-12-02 00:15 | 2009-12-02 01:44 | 1 | 89 | 54923-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | STS SEC LEAD BURNED OFF VER/PDP IDC XXXX
22550 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2013-12-12 08:41 | 2013-12-12 10:10 | 1 | 89 | 4155601 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE IN S/D HAS FAILED// WILL REPAIR// REPAIRS MADE //POWER IS RESTORED VER/SEF L3/HFP HFPC FEC46
22551 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-06-19 13:44 | 2013-06-19 15:13 | 1 | 89 | 4372611 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUSTOMER AKING ME TO THE TROUBLE.BAD XFMER WILL WORK IN THE MORNING .CUSTOMER RENT HOUSE NO ONE LIVING IN HOUSE SAID COULD WAIT TILL TOMORROW.TALKED TO CREW VER/KEP IDC XXXX
22552 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2020-02-11 08:18 | 2020-02-11 09:47 | 1 | 89 | 4391411 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Secondary burnt into wll make repairs/// Repaired burnt up secondary ///Restored service @ 09:47
22553 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-01-12 10:35 | 2020-01-12 12:04 | 1 | 89 | 4286231 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke in sec. on pole 237-247.will make repairs..repairs made..restored..
22554 | Hazard | 3309302 | VICCO | JEFF | 2018-10-01 12:37 | 2018-10-01 14:06 | 1 | 89 | 4185381 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broke fuse COD-1 ISO TF 37830323D00573
22555 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-12-14 10:47 | 2014-12-14 12:16 | 1 | 89 | 4859731 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED FUSE// VER/ ADH
22556 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2019-02-08 09:14 | 2019-02-08 10:43 | 1 | 89 | 4769351 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | service drop burnt up from bad insulinks. repairs made. pls close. tre
22557 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-05-17 17:58 | 2022-05-17 19:27 | 1 | 89 | 4904611 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up at xfmr//repairs made//restored at 19:27//complete//em
22558 | South Williamson | 3411401 | DEWEY | INEZ | 2008-06-16 13:29 | 2008-06-16 14:58 | 1 | 89 | 65592-1 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | BAD CONN IN METER BASE VER/HFP
22559 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-05-19 10:22 | 2010-05-19 11:51 | 1 | 89 | 65044-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKKEN FUSE//VER/CRB IDC XXXX
22560 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-01-01 09:06 | 2018-01-01 10:35 | 1 | 89 | 4692071 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Door in cutout burnt up replaced door, apr at 1035 close ticket/ ISO 38830645000107/ COD 1
22561 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-08-27 07:31 | 2012-08-27 09:00 | 1 | 89 | 4974971 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD, REPLACED ALL CONNECTIONS AT WEATHERHEAD. --- POWER RESTORED. VER/HFP L3/HFP IDC XXXX
22562 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-04-21 18:43 | 2015-04-21 20:12 | 1 | 89 | 4350471 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SINGLE ALL OUT OUT LINE FUSE BAD CUT OUT AT LINE FUSE POLE POWER RESTORED KWB VER/CRB
22563 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-03-19 11:28 | 2020-03-19 12:57 | 1 | 89 | 4491821 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | Cutout broke on stepdown 37820073A00616// will have to open primary metering on pole 73-221 to make repairs
22564 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-04-11 19:53 | 2015-04-11 21:22 | 1 | 89 | 4308751 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGE CUTOUT VER/KEP
22565 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-09-20 10:30 | 2018-09-20 11:59 | 1 | 89 | 4133631 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE//OPENED @ 1030 ON 1159
22566 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-01-15 12:46 | 2018-01-15 14:15 | 1 | 89 | 4749131 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout , changing
22567 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-10-01 17:41 | 2011-10-01 19:10 | 1 | 89 | 4938561 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE WIRE CONNECTOR BURNT INTO//// RESPLICED SERVICE POWER RESTORED. COD-1 ISO TF 37830295A00017 VER/HFP L3/HFP IDC XXXX
22568 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-02-20 09:31 | 2015-02-20 11:00 | 1 | 89 | 4053881 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNED DOWN, ONE LEG AND THE NEUTRAL VER/HFP L3/HFP
22569 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-10-12 00:22 | 2014-10-12 01:51 | 1 | 89 | 4607831 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTOMER HAS A BAD DISCONNECT OUT ON SERVICE POLE. HE WANTED IT LEFT ON TONIGHT. HE HAS PARTIAL POWER. HE WILL CALL IN TOMORROW FOR DISC. SO HE CAN CHANGE BREAKER. AJB
22570 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-02-20 13:11 | 2017-02-20 14:40 | 1 | 89 | 4409421 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD 19.9 KV, 25 KVA XFMR, WILL ALSO NEED CUTOUT AND ARRESTER, T-BRK, CAN WORK WITH BIG BUCKET. PLEASE SEND TO T. SMITH/ ISO 37830205C00334/ COD 1/ REPAIRS MADE AND POWER RESTORED AT 14:40/ VER/BOW L3/HFP XXXHFP
22571 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-10-01 09:41 | 2008-10-01 11:10 | 1 | 89 | 52529-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP RELEASED BY CREW 074S02 A SPAN OF 2/3 SECONDARY BURNED DOWN. I AM GOING TO SPLICE WIRE. I HAVE TO OPEN TRANS. ON POLE 26-22. 1 CUSTOMER IS OUT. FAULT 37830216000022 /OUTAGE FOR ADDITIONAL 1 CUSTOMER IN ORDER 52563-1 RELEASED BY CREW 074S02 WIRE BURNED DOWN IN SPLICE IN MID SPAN. SERVE END GOT HOT AND MELTED INTO NEUTRAL AND BURNED DOWN. I OPENED TRANSFORMER AT 11:10 AND CLOSED IDC XXXX
22572 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2008-12-18 10:34 | 2008-12-18 12:03 | 1 | 89 | 59827-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402202// REPLOACED BAD CUTOUT POLE 67-108. NO DAMAGE EVERYTHING OK.// VER/DBM CHANGED FROM NO INTER L3/KEP IDC XXXX
22573 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-12-03 07:41 | 2008-12-03 09:10 | 1 | 89 | 54116-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT APART ON SECONDARY POLE. REPAIRED. SH//3409301//VER/CRB L3/KEP IDC XXXX
22574 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-01-09 13:01 | 2014-01-09 14:30 | 1 | 89 | 4265561 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER OUT DUE TO BAD CURRENT LIMIT FUSE. MADE REPAIRS EVERYTHING OK VER/CRB IDC XXXX
22575 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-09-25 16:11 | 2020-09-25 17:40 | 1 | 89 | 4496191 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing
22576 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-12-27 20:26 | 2017-12-27 21:55 | 1 | 89 | 4683181 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot secondary connection burnt in two at mast pipe replaced both hot entrance connections at mast pipe/ ISO 37830239000145/ COD 1
22577 | South Williamson | 3411401 | DEWEY | INEZ | 2010-09-11 20:43 | 2010-09-11 22:12 | 1 | 89 | 65653-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN POLE768-192 CHECKING NOW/// CUTOUT HAD BURNT INTO RPLACED AND BACK ON AT 22:12 EM IDC XXXX
22578 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-05-18 17:31 | 2012-05-18 19:00 | 1 | 89 | 4807981 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 SERVICE NEUTRAL BURNT OPEN MID-SPAN. (100 AMP SVC). <<ONLY ONE CUSTOMER AFFECTED>> REPLACED #4 SERVICE WITH #2. RESTORED @ 19:00. SH ///VER/CRB L/3 CRB IDC XXXX
22579 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-04-18 13:52 | 2010-04-18 15:21 | 1 | 89 | 64803-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END IN SPLICE IN MID SPAN OF SERVICE DROP GOT HOT AND MELTED. IT GOT AGAINST NEUTRAL IN DROP AND BURNED DOWN THE SERVICE DROP TO GROUND. I REPLACED THE WHOLE SERVICE DROP.// VER/DBM IDC XXXX
22580 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-03-12 21:51 | 2010-03-12 23:20 | 1 | 89 | 65946-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR//COD 1//ISO 37830470000004//MD FILED ON MISSING FUSE// IDCC PN98 XXXX
22581 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2019-01-22 17:21 | 2019-01-22 18:50 | 1 | 89 | 4705761 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew vrequired replace cutout L3/HFP
22582 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-04-05 18:19 | 2010-04-05 19:48 | 1 | 89 | 59007-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CREW REQUIRED; POLE 547/95 BURNT OFF AT TRANSF BOLTS; 404 POLE AND 10KVA 7200, CUTOUT, ARRESTOR AND BRACKET NEEDED; DEAD-END POLE; CARETAKER ACROSS DRIVEWAY HAS KEY TO GATE AND STATES NO ONE IS LIVING THERE WE CAN SCHEDULE AS WE CAN GET TO IT; POLE IS NOT BY TRUCK BUT CAN BE WITH TRACK MACHINE; TAP LIFTED ON LINE FUSE POLE 547/50 AND GROUNDED THERE; RELEASE TO LINE DEPT. // UNKNOWN WHAT FAILED AND STARTED POLE FIRE... /SENT 2 CREW// VER/DBM IDCC FP50, PN104 XXXX
22583 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-01-19 21:16 | 2009-01-19 22:45 | 1 | 89 | 58428-1 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401001//SERVICE DROP GOT HOT IN A SPLICE IN MIDSPAN AND BURNED HOT LEG INTO. I RESPLICED CONDUCTOR.//VER/CRB L3/KEP
22584 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-01-24 09:49 | 2018-01-24 11:18 | 1 | 89 | 4769991 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Replaced a bad connection on the transformer secondary riser. L3/HFP
22585 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-12-06 08:25 | 2009-12-06 09:54 | 1 | 89 | 61306-1 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | VER/HFP 90 DEGREE ELBOW ON METER BASE HAD FAILED L3/HFP IDC XXXX
22586 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-12-21 02:52 | 2016-12-21 04:21 | 1 | 89 | 4225871 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 1072F5501 CAN MAKE REPAIRS LRM CUTOUT CHANGED PWR RESTORED @ 04:21 PLEASE CLOSE TICKET//COD 1
22587 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-04-07 09:01 | 2011-04-07 10:30 | 1 | 89 | 51198-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON XFMR IS BROKE, WILL HAVE TO REPLACE//VER/CRB
22588 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2013-11-11 14:54 | 2013-11-11 16:23 | 1 | 89 | 4029101 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WIRE PULLED APART IN SPLICE FIXED BAD CONNECTER POWER BACK TO NORMAL KWB VER/SEF
22589 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-05-07 13:56 | 2018-05-07 15:25 | 1 | 89 | 4320491 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt into on service drop /// replaced bad connections and restored service// only 1 customer affected/ ISO 37820242000337/ COD 1
22590 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-01-07 13:40 | 2018-01-07 15:09 | 1 | 89 | 4718021 | 89 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced bad connection complete/ ISO 38830206A31088/ COD 1
22591 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-11-18 14:46 | 2008-11-18 16:15 | 1 | 89 | 66280-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP NO CREW REQUIRED REPAIRING CONNECTIONS1 IDC XXXX
22592 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-11-06 08:41 | 2010-11-06 10:10 | 1 | 89 | 53425-1 | 89 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 1/0 SECONDARY BURNT IN HALF AT SECONDARY POLE, REPAIRED WIRE VER/TOM IDC XXXX
22593 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-12-06 10:07 | 2013-12-06 11:35 | 1 | 88 | 4106451 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKING TRANSFORMER FOR HAZ FUSE WAS BROKE WIRE ROTTED OUT IN FUSE NOT BLOWN VER/SEF L3/HFP
22594 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-09-20 15:09 | 2010-09-20 15:53 | 2 | 44 | 51602-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON 448-277 TOOK LINE FUSE OUT ON 448-121 ONLY SERVES ON XFMR, CLEARED ARRESTER UP RESTORED POWER AT 15:53//COD 2// AED CREATED// VER/DBM IDC XXXX
22595 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-06-30 16:57 | 2022-06-30 18:25 | 1 | 88 | 4352951 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired srv drop .replacing 2 of drop--allgood-ds063022
22596 | Pikeville | 3407101 | TOPMOST | DEMA | 2016-05-07 23:07 | 2016-05-08 00:35 | 1 | 88 | 4186131 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE PUT NEW FUSE IN EVERYTHING OK VER/KEP
22597 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-05-23 12:24 | 2022-05-23 13:52 | 1 | 88 | 4933431 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutout broke on193-487 will be making repairs///Changed bad cutout and restored @ 13:52
22598 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-12-12 17:23 | 2012-12-12 18:51 | 1 | 88 | 4465131 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | THINK SURGE ARRESTOR IS BLOWN,WILL REPAIR IT////////BY-PASSED ARRESTOR,CLOSED XFR AND RESTORED,ALL OK AFTERWARDS ///VER/CRB L/3 CRB
22599 | Hazard | 3303902 | LESLIE | WOOTON | 2009-01-21 20:50 | 2009-01-21 22:18 | 1 | 88 | 58948-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3303902// RELEASED BY CREW 077S01 SERVICE DROP BURNT DOWN AT WEATHER HEAD//VER/CRB L3/KEP
22600 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-05-16 12:03 | 2011-05-16 12:47 | 2 | 44 | 4100511 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REMOVED SOME TREE LIMBS IN OPEN WIRE SECONDARY. MAY HAVE BEEN CAUSE - WILL TRY XFMR FUSE. UPON CLOSER INSPECTION IT APPEARS FUSE LINK BROKE. RE-FUSED @ 12:47. ALSO RE-ATTACHED GUY TO ANC. SH//COD 2// VER/DBM
22601 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-03-04 18:46 | 2008-03-04 19:30 | 2 | 44 | 53099-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3002107// CUTOUT FELL APART ALSO CHGED LA//COD 2 IDC XXXX
22602 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-01-29 22:11 | 2015-01-29 22:55 | 2 | 44 | 4974021 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MD TO SHOW MIS-MAPPED CUST AND CORRECT COD TO 2// BAD CUTOUT ON POLE 38830502000162/MADE MDC TO SHOW TRANS ON THIS POLE 15KVA// REPLACED CUTOUT APR AT 1055 CLOSE TICKET VER/CRB L3/HFP XXX
22603 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-01-27 21:32 | 2011-01-27 23:00 | 1 | 88 | 66642-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SPLICE ON SERVICE DROP.// VER/DBM IDC XXXX
22604 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2015-01-11 09:12 | 2015-01-11 10:40 | 1 | 88 | 4927341 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOSE UG CONN MADE REPAIRS CUST RESTORED PLEASE CLOSE TICKET THANKS.BT/ ISO 38830206C02182/ COD 1/ VER/BOW
22605 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2019-05-27 18:22 | 2019-05-27 19:50 | 1 | 88 | 4351111 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 service down, scuffed white jeep when it fell on it, no major damage, power restored 19:50 GRF//SENT TO PEGGY WYSONG
22606 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2016-01-18 11:33 | 2016-01-18 13:01 | 1 | 88 | 4628331 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED SECONDARY CONNECTIONS/// NOT SECONDARY IT WAS ACTUALLY SERVICE DROP CONNECTIONS/ ISO 37830024A10181/ COD 1 VER/CRB
22607 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-03-23 10:36 | 2012-03-23 12:04 | 1 | 88 | 4608201 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE TO OUTDOOR SIGN HAD NEUTRAL AND ONE HOT LEG BURNT INTO// I HAVE REPAIRS MADE//COMPLETE//EM ///VER/CRB IDC XXXX
22608 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2016-06-05 11:16 | 2016-06-05 12:00 | 2 | 44 | 4307421 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1123-6085 6T ME FUSE LINK BROKE REPAIRED VER/CRB
22609 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-11-03 14:06 | 2016-11-03 14:50 | 2 | 44 | 4072641 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED APART AT THIS LOCATION, REFUSED @1450. VER/CRB
22610 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-05-30 21:58 | 2011-05-30 22:42 | 2 | 44 | 4211761 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT OUT ON POLE 818-17// CHANGED OUT DOOR// RESTORED AT 22:42//COMPLETE//EM //VER/GAH IDCC FEC49 XXXX
22611 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-04-08 14:32 | 2021-04-08 16:00 | 1 | 88 | 4431711 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans fuse open on 37830238000043,Going to replace fuse..Trans fuse open on 238-43,Got fuse replaced and restored at 16:00..
22612 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-03-20 09:32 | 2021-03-20 11:00 | 1 | 88 | 4357211 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced connections on secondary pole
22613 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2021-03-21 13:47 | 2021-03-21 15:15 | 1 | 88 | 4359561 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced a broken, manual cutout on pole 273-D-32. Power restored at 15:15.
22614 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-12-31 13:40 | 2015-12-31 14:02 | 4 | 22 | H4578671 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 CUS ORIGINALLY, 4 OPENEDLOOP BURNED INTO AT POLE 785-988 AND FELL ACROSS CENTER PHASE///CENTER PHASE ALMOST BURNED INTO///OPENED SWITCHES ON POLE AT 13:40 TO MAKE SAFE FOR REPAIRS////CREW ON SITELOOP BURNED INTO AT POLE 785-988 AND FELL ACROSS CENTER PHASE///CENTER PHASE ALMOST BURNED INTO// VER/ ADH
22615 | Pikeville | 3414901 | FISHTRAP | DISTRIBUTION | 2016-04-14 14:02 | 2016-04-14 14:24 | 4 | 22 | 4091671 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OPENED @ 1402 CLOSED @ 1424, NON-SCHEDULED CREW WENT TO CHANGE REGULATOR AND REQUESTED OUTAGE TO ISOLATE. SHAWN SUMNERS NOTIFIED. VER/ARN
22616 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-07-29 08:01 | 2014-07-29 08:45 | 2 | 44 | 4304861 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | REPLACED ONE DOOR BURNT UP ON XMFBANK POLE APR AT 0845 CLOSE TICKET. VER/CRB
22617 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-05-02 11:38 | 2022-05-02 13:06 | 1 | 88 | 4823631 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a broke Neutral in service drop,going to pull Meter and make repairs.Restored at 13:06..
22618 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-02-13 20:07 | 2012-02-13 21:35 | 1 | 88 | 4346771 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CREW HAS BEEN INSTALLING NEW CUTOUT & ARRESTERS ON POLE 329-138 FUSE BROKE TAKING XFMR OUT , ONLY TWO CUSTOMERS AFFECTED RESTORED POWER AT 21:35 COD-2 ISO TF 37830329000138 VER/HFP L3/HFP IDC XXXX
22619 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-06-03 11:47 | 2008-06-03 13:15 | 1 | 88 | 54901-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | 3407401// REPLACED BAD METER. VER/HFP
22620 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-01-12 09:15 | 2013-01-12 10:43 | 1 | 88 | 4597521 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEU .BROKE AT HOUSE KNOB ,REPAIRED POWER RESTORED WILL HAVE TO CHANGE SERVICE OUT WHEN CUST DOES SER. CHANGE ///VER/CRB L/3 CRB IDCC TOF0720 ESTIMATED TIME OFF FOR REPAIR XXXX
22621 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2016-05-19 12:23 | 2016-05-19 13:51 | 1 | 88 | 4235401 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | HAD OH SPLICE PULL OUT WERE CUST SERVICE POLE IS ROTTEN AND WIRE HOLDER PULL OUT, NEED TO NOTE ACC, THAT THEY NEED TO CHANGE THEIR POLE OUT, METER HAS 00000 HOURS ON METER VER/CRB
22622 | Pikeville | 3403001 | PIKEVILLE | CITY | 2014-05-05 14:49 | 2014-05-05 15:33 | 2 | 44 | 4665301 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 XFMR. FUSE BLOWN IN BANK// WILL REFUSE// FUSE LINK APPEARS TO HAVE BROKEN// POWER IS RESTORED @ 15:33/ 5-5-14 VER/CRB L3/HFP
22623 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-11-01 09:22 | 2018-11-01 10:50 | 1 | 88 | 4349531 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required bad cutout L3/HFP
22624 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-09-19 14:02 | 2014-09-19 15:30 | 1 | 88 | 4511861 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR CUTOUT FUSE BROKEN.RE FUSED @ 15:30// COD 1// VER/ ADH
22625 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2018-02-05 08:52 | 2018-02-05 10:20 | 1 | 88 | 4805771 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 37830187B00372.cust out due to bad cutout 6t fuse at transformer. replaced cutout everything ok
22626 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-12-29 13:27 | 2020-12-29 14:55 | 1 | 88 | 4833561 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke cutout,Going to change it and restore service.Went ahead and changed 2 porcelin cutouts on 480 Bank,Restored at 14:55.
22627 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-04-08 07:47 | 2020-04-08 09:15 | 1 | 88 | 4570841 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at pole
22628 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-07-28 16:37 | 2011-07-28 16:48 | 8 | 11 | H4633981 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CONNECTION BAD IN UG JUNCTION BOX. DUTY SUPERVISOR ENROUTE TO ASSIST. ONE CUSTOMER OUT BUT WILL NEED TO OPEN XFMR 38830979C00130 WHEN READY TO START. <<ONLY ONE CUSTOMER AFFECTED>> FOUND UG SERVICE CABLE BAD. OPENED XFMR @ 16:37, INSTALLED AUTO-XFMR AND CLOSED XFMR @ 16:48. SH RELEASED BY CREW 076S02//COD 1 + 8 IDCC DUP TO OPEN TRANSFORMER XXXX
22629 | South Williamson | 3200302 | BELFRY | TOLER | 2017-07-27 16:56 | 2017-07-27 18:24 | 1 | 88 | 4189411 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38821039A10530.TRANS CUTOUT BROKEN ON 10039-A530 REPLACED CUTOUT RESTOORED POWER AT 18:24 VER/AWD
22630 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-11-19 11:31 | 2008-11-19 12:15 | 2 | 44 | 66623-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKE. 2 CUSTOMERS OUT. RE-FUSED XFMR. BOTH CUSTOMERS ARE SERVED FROM POLE 784-97. SH MD FILED COD-2 VER/KEP IDC XXXX
22631 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-01-02 10:45 | 2008-01-02 11:29 | 2 | 44 | 52686-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE//3400301.//VER/CRB IDC XXXX
22632 | Hazard | 3309003 | JEFF | VIPER | 2016-08-15 17:49 | 2016-08-15 19:17 | 1 | 88 | 4785111 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANSF === REPLACED POWER OK/ ISO 37830418000280/ COD 1/ VER/BOW
22633 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-08-13 10:04 | 2011-08-13 10:48 | 2 | 44 | 4702161 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 2// VER/DBM IDC XXXX
22634 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2019-12-01 09:57 | 2019-12-01 11:25 | 1 | 88 | 4110911 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed at weather head. Reworked connections and restored @ 11:25. sh//cod 1
22635 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-02-03 08:32 | 2008-02-03 10:00 | 1 | 88 | 65815-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000801// NO CREW REQUIRED REPAIRING SPLICES // ISO/FLT 38830292D00189 COD -1// IDC XXXX
22636 | Hazard | 3309003 | JEFF | VIPER | 2017-12-17 11:52 | 2017-12-17 13:20 | 1 | 88 | 4654441 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | secondary connector burnt into..restored power at 13:20/ ISO 37830392000079/ COD 1
22637 | Hazard | 3310502 | HADDIX | CANOE | 2018-04-08 13:57 | 2018-04-08 15:25 | 1 | 88 | 4201521 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hot leg burned into
22638 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-02-25 08:12 | 2008-02-25 09:40 | 1 | 88 | 50091-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3000201// BAD SERVICE SPLICE// VER/TOM IDC XXXX
22639 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-11-26 08:27 | 2009-11-26 09:55 | 1 | 88 | 65950-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ETA CALL BACK .//2/3 SERVICE WIRE BURNED DOWN//REPLACE PORTION OF SERVICE DROP IDC XXXX
22640 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2010-03-10 09:47 | 2010-03-10 11:15 | 1 | 88 | 64562-1 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN PULLED OUT, REPLACED CONNECTIONS, POWER RESTORED VER/KEP L3/KEP IDCC MCCDL XXXX
22641 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2016-12-24 09:27 | 2016-12-24 10:11 | 2 | 44 | H4233861 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4233861*** B PHASE L/F OPEN @48-D2-107 (4 CUSTOMERS ORIGINALLY), PATROLLING. CUT OUT BUSTED ON POLE 48-D2-682, WILL HAVE TO OPEN A AND C PHASE 37830048D20107 TO CHANGE OUT WILL KEEP TRACK OF TIMES. OPENED AAND C PHASE @0927, MADE REPAIRS AND CLOSED ALL 3 @1011./ DUPLICATE IN HOIS/ VER/BOW
22642 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-02-01 14:32 | 2015-02-01 16:00 | 1 | 88 | 4978781 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 295B-332 . CHANGED CUTOUT , CLOSED XFMR FUSE BACK @ 16:00/ ISO 37830295B10332/ COD 1/ VER/BOW L3/HFP XXX
22643 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-07-07 16:37 | 2014-07-07 18:05 | 1 | 88 | 4201411 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HEATED UP AT WEATHERHEAD AND BURNT SERVICE NEUTRAL IN TWO. REPAIRED NEATRAL AND RE-WORKED CONNECTIONS. SH VER/CRB
22644 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2009-03-02 14:02 | 2009-03-02 15:30 | 1 | 88 | 54060-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3309104// REPLACED CONNECTION ON POLE// VER/DBM IDC XXXX
22645 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-02-24 12:47 | 2015-02-24 14:15 | 1 | 88 | 4078371 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR FROZE OPEN AT WEATHERHEAD. RE-WORKED CONNECTIONS AND RESTORED @ 14:15. SH// VER/DBM
22646 | Hazard | 3302704 | HAZARD | KENMONT | 2011-09-03 21:04 | 2011-09-03 22:32 | 1 | 88 | 4799791 | 88 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3302704 - 3302704 BAD CONNECTION ON POLE //VER/GAH IDC XXXX
22647 | Hazard | 3310502 | HADDIX | CANOE | 2011-02-19 20:55 | 2011-02-19 22:23 | 1 | 88 | 59411-1 | 88 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | TRANSFORMER FUSE BLOWN ONLY ONE OUTAGE IN HOIS. VER/HFP L3/HFP IDC XXXX
22648 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-12-09 09:18 | 2016-12-09 10:45 | 1 | 87 | 4180401 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNDT INTO ON HOT LEG AT TRANS. POLE, MADE REPAIRS @1045. VER/CRB L3/HFP XXXHFP
22649 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-06-15 08:58 | 2015-06-15 10:25 | 1 | 87 | 4572381 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON THE SECONDARY. ONLY ONE CUSTOMER AFFECTED.// VER/ ADH
22650 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-05-28 17:33 | 2011-05-28 19:00 | 1 | 87 | 4204461 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK COMPLAINT/////FOUND BAD SQUEEZON CONNECTION ON XFR POLE,REPLACED ALL COD-1 ISO SO VER/HFP L3/HFP IDC XXXX
22651 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2022-07-09 21:13 | 2022-07-09 22:40 | 1 | 87 | 4447711 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection at service pole.//Made repair @ 22:40
22652 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-10-24 20:36 | 2014-10-24 22:03 | 1 | 87 | 4660251 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 SERVICE BURNT DOWN BETWEEN 37830247D00769 AND 37830247D00869, OPENED TRANSFORMER ON 37830247D00769 AT 21:27, CLOSED AT 22:03...NO OBVIOUS REASON FOR WIRE TO BE BURNT DOWN. VER/KEP L3/HFP
22653 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-11-05 09:33 | 2014-11-05 11:00 | 1 | 87 | 4700961 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE OUTAGE, NEUTRAL BURNT, REPAIRING NOW// INSULINK FAILED AND BURNT NEUTRAL IN TWO. REPAIRED. ONLY ONE CUSTOMER AFFECTED RESTORED @ 11:00. SH//COD1// VER/ ADH
22654 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-07-14 04:33 | 2013-07-14 06:00 | 1 | 87 | 4520771 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK VER/KEP IDC XXXX
22655 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-04-27 09:40 | 2014-04-27 11:07 | 1 | 87 | 4638711 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK REPLACE WITH NEW FUSE POWER RESTORED KWB//COD 1// VER/DBM IDC XXXX
22656 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2014-12-29 20:53 | 2014-12-29 22:20 | 1 | 87 | 4890801 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CUTOUT BROKEN..WILL LIFT HOT TAP 37820103000207 FEEDING CUTOUT DOES NOT SERVE ANYTHING WILL HAVE TO CLIMB AND PUT POLE OUT//////POLE 103-207 WILL HAVE TO LOWER POLE TOP PIN OR POSSIBLY CHANGE POLE OUT AT A LATER DATE..DOES HAVE INACTIVE XFMR PLEASE SEND COPY TO TIM HALL../ ISO 37820103000207/ COD 1
22657 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2011-05-03 08:03 | 2011-05-03 09:30 | 1 | 87 | 4000151 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 139-B-408. I OPENED TRANSFORMER BANK AT 09:00 BACK ON AT 09:30. REPLACED BAD CUTOUT EVERYTHING OK. PART POWER COD-1 ISO TF 37830139B00408 VER/HFP L3/HFP IDC XXXX
22658 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-22 15:45 | 2011-01-22 17:12 | 1 | 87 | 63640-1 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEM////////SERVE-IN FROZEN OUT,MADE REPAIRS AND RESTORED,ALL OK AFTERWARDS VER/HFP L3/HFP IDC XXXX
22659 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-12-24 19:58 | 2014-12-24 21:25 | 1 | 87 | 4882471 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUST HAS PART POWER GOING TO TROUBLE SHOOT,,,ALL REPAIRS MADE POWER BACK ON ON 21:25//COD 1// VER/ ADH
22660 | Hazard | 3309003 | JEFF | VIPER | 2017-02-15 17:54 | 2017-02-15 18:23 | 3 | 29 | H4400261 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE BAD IN SECONDARY NEED 2 MEN OR CREW === NEED DROPE SECONDARY DOWN TO WORK ONIT OVER ROAD WAY ===REPAIRED SECONDARY === POWER OK OPEN TRANSF AT 17:54 CLOSED 18:23/ ISO 37830394A00133/ COD 4/ VER/BOW L3/HFP HFPC DUP
22661 | South Williamson | 3411401 | DEWEY | INEZ | 2019-03-29 15:58 | 2019-03-29 17:25 | 1 | 87 | 4036171 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse door burnt up on 768A212.replaced door,everything checked ok,restored power at 17:25
22662 | Hazard | 3303902 | LESLIE | WOOTON | 2015-05-19 09:15 | 2015-05-19 10:42 | 1 | 87 | 4444641 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT/ARRESTER HAS STATIC NOISE. CHANGED C.O. AND BRACKET.NOISE STOPPED..OPENED TAP ON POLE 341-10 AT 09:15 CLOSED AT 09:42 VER/HFP L3/HFP
22663 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-01-05 22:35 | 2014-01-06 00:02 | 1 | 87 | 4231521 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER , BAD CONNECTION IN SERVICE, MADE REPAIRS RESTORED POWER AT 00:02 VER/CRB
22664 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-02-13 22:18 | 2014-02-13 23:45 | 1 | 87 | 4385871 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN SERVICE HEATED UP AND BURNT NEUTRAL IN TWO. REPAIRING. REPLACED #4 SERVICE WITH # 2 AND RESTORED @ 23:45. OOONLY ONE CUSTOMER AFFECTEDOO SH VER/KEP
22665 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-03-22 13:25 | 2011-03-22 14:52 | 1 | 87 | 56740-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 39260581 // SERVICE DROP NEUTRAL BROKEN ON SEC POLE CUST. HAVING TROUBLE WITH STOVE ECT. NO POLE ON GR. INSTALLED NEW 2/3 SERVICE DROP CUST. POWER OK VER/HFP L3/HFP IDC XXXX
22666 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-03-12 17:48 | 2011-03-12 19:15 | 1 | 87 | 53873-1 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER--CALLED DRT TO HELP//WR#39141994--RESQUEZED CONNECTIONS//VER/CRB IDC XXXX
22667 | South Williamson | 3411401 | DEWEY | INEZ | 2015-12-01 12:38 | 2015-12-01 14:05 | 1 | 87 | 4499181 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE HOT LEG BURNED INTO ON SERVICE DROP///I REPAIRED CONDUCTOR//RESTORED TO NORMAL AT 14:05//COMPLETE//EM VER/HFP L3/HFP
22668 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-10-27 09:46 | 2010-10-27 11:13 | 1 | 87 | 65581-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED REPAIRING SERVICE// VER/DBM IDC XXXX
22669 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-04-02 10:58 | 2018-04-02 12:25 | 1 | 87 | 4164571 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broke nuetral in service drop.. pulled meter and climbed pole to repair.. customer said everything was working fine..plug meter in at 12:25
22670 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-07-10 12:03 | 2012-07-10 13:30 | 1 | 87 | 4668401 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAD NEUTRAL AND HOT LEGS PULL APART ON A 4/3 SERVICE DROP, HAVE REPAIRS MADED AND POWER IS RESTORED AT THIS LOC AT 1330 IDC XXXX
22671 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-05-12 17:18 | 2010-05-12 18:45 | 1 | 87 | 60733-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, NO TRUCK, CHANGED CUTOUT VER/HFP L3/HFP IDC XXXX
22672 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-07-25 16:48 | 2010-07-25 18:15 | 1 | 87 | 56852-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. VER/KEP L3/KEP IDC XXXX
22673 | Pikeville | 2974101 | BIG ROCK STATION | CONAWAY | 2010-03-05 11:48 | 2010-03-05 13:15 | 1 | 87 | 63146-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE WEATHERHEAD ON ONE OF THE PHASE CONDUCTORS. VER/KEP L3/KEP IDC XXXX
22674 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2008-07-01 19:23 | 2008-07-01 20:50 | 1 | 87 | 61101-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3202203//....JRV ON SITE @ 20:15.....XFRMER FUSE OUT....WILL RE-FUSE..//....FUSE LINK JUST BROKE IN CUTOUT DOOR...NO FAULT...RE-FUSED..POWER ON...JRV...07/01/08 // VER/TOM IDC XXXX
22675 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-01-17 12:28 | 2015-01-17 13:55 | 1 | 87 | 4941221 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY CONNECTION ON THE TRANSFORMER LEAD. VER/CRB L3/HFP HFPC MCCDL
22676 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2019-04-22 12:07 | 2019-04-22 15:04 | 1 | 177 | 4147061 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE NECESSARY TO ISOLATE FAULT AT POLE 38821137D00318 - POLE FIRE I opened recloser on pole 38821137A00331 at 12:07, source side riser removed and tagged to Matney. Released by crew 079S02
22677 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-05-04 10:39 | 2021-05-04 12:06 | 1 | 87 | 4520851 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT///////REPLACED BROKEN CUTOUT&RESTORED POWER,ALL OK AFTERWARDS
22678 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2020-04-10 19:58 | 2020-04-10 21:25 | 1 | 87 | 4619681 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke will be making repairs/// Changed bad cutout and restored service @ 21:25
22679 | Hazard | 3303901 | LESLIE | HYDEN | 2009-12-05 17:48 | 2009-12-05 19:15 | 1 | 87 | 58835-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKEN, CHANGED OUT, POWER RESTORED VER/KEP L3/KEP IDC XXXX
22680 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-03-11 12:24 | 2016-03-11 13:51 | 1 | 87 | 4837221 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FULL POWER @ METER, RESQUEEZED 3 CONNECTIONS/ DID HAVE AN ISSUE WHEN ARRIVED AFTER FIXING CONNECTION AT WEATHER HEAD THERE WAS FULL POWER/ ISO 38830045D26681/ COD 1/ VER/BOW
22681 | South Williamson | 3411401 | DEWEY | INEZ | 2008-05-16 09:18 | 2008-05-16 10:45 | 1 | 87 | 64649-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411401/ SERV DROP BURNED INTO VER/HFP IDC XXXX
22682 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-12-01 23:03 | 2010-12-02 00:30 | 1 | 87 | 62294-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD. VER/TOM IDC XXXX
22683 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-05-15 19:45 | 2017-05-15 21:12 | 1 | 87 | 4802401 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | # 2 SECONDARY CONNECTION BURNT UP GIVING ONE CUSTOMER PARTIAL POWER OPENED METER AT 19:45 MADE REPAIRS AND CLOSED METER RESTORING POWER AT 21;12 VER/CRB
22684 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-11-28 11:08 | 2010-11-28 12:35 | 1 | 87 | 60275-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE OUT ON POLE 787-48 FUSE DIDNT BLOW JUST BROKE.. CLOSED BACK IN AT 12:35 TO RESTORE CUSTOMER..RN /VER/CRB11-28-10 IDC XXXX
22685 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-01-11 09:03 | 2008-01-11 10:30 | 1 | 87 | 55896-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3413402//ACTUAL OUTAGE ON POLE # 40-119, FUSE BROKEN, REFUSED 50KVA TRANSFORMER, ALL WORK COMPLETE / GXJ//COD 1//ISO 37830040000119// VER/DBM IDC XXXX
22686 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-01-31 15:18 | 2011-01-31 16:45 | 1 | 87 | 52597-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR# 38637317 // SEC BURNT LOOSE //COD 1//ISO 38830020D47619// VER/DBM IDC XXXX
22687 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-01-04 07:18 | 2011-01-04 08:45 | 1 | 87 | 58450-1 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE REPLACED FUSE POWER RESTORED AT 845 CLOSE TICKET//VER/CRB IDC XXXX
22688 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-01-23 12:18 | 2022-01-23 13:45 | 1 | 87 | 4398171 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmer cutout. repaired, restored
22689 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-08-03 19:13 | 2020-08-03 20:40 | 1 | 87 | 4283191 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester had blown. cut arrester in the clear. power restored/ ISO 37830470000101/ COD 1
22690 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2016-03-23 13:28 | 2016-03-23 14:55 | 1 | 87 | 4874151 | 87 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED-RED SERVE-IN PULLED APART IN THEIR SERVICE , I REPLACED SQUEEZE ON ISO 37830379D00317 COD 1 VER/AWD
22691 | Pikeville | 3402002 | KEYSER | STONECOAL | 2021-02-03 10:52 | 2021-02-03 12:19 | 1 | 87 | 4933531 | 87 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad trans. cutout @24-C-694, will be changing. Got cutout replaced and power restored @1219.
22692 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-11-08 08:34 | 2020-11-08 10:00 | 1 | 86 | 4652171 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no creew required 6t
22693 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2011-09-17 08:54 | 2011-09-17 10:20 | 1 | 86 | 4879021 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN THE SERVICE DROP CAUSED A PHASE TO GROUND FAULT, BURNING THE NEUTRAL AND ONE OF THE PHASE WIRES IN THE SERVICE DROP. //VER/CRB IDC XXXX
22694 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2016-05-28 18:54 | 2016-05-28 20:20 | 1 | 86 | 4269151 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIREDREPLACED CUTOUT/ ISO 38830270D00216/ COD 1/ VER/BOW
22695 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-07-24 10:13 | 2017-07-24 11:39 | 1 | 86 | 4171741 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR FAILED ON SEC CONNECTIONS. REWORKED TWO SETS OF CONNECTIONS AND RESTORED @ 11:30. OOONE CUSTOMER AFFECTEDOO SH VER/CRB L3/HFP XXXHFP
22696 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-06-18 00:29 | 2009-06-18 01:12 | 2 | 43 | 51726-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//VER/CRB IDC XXXX
22697 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-02-04 17:41 | 2013-02-04 18:24 | 2 | 43 | 4791151 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK COD-2 ISO TF 38830117A00254 VER/HFP L3/HFP IDC XXXX
22698 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-07-12 02:19 | 2011-07-12 03:45 | 1 | 86 | 4522161 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD XFMR CUTOUT.//VER/CRB IDC XXXX
22699 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-01-19 22:04 | 2011-01-19 23:30 | 1 | 86 | 62867-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A 19.9 KV ARRESTER FAILED, SCATTERING DEBRIS OVER THE DRIVEWAY. I PICKED UP WHAT I COULD FIND.//VER/CRB IDC XXXX
22700 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-02-25 15:34 | 2019-02-25 17:00 | 1 | 86 | 4917271 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Customer had a secondary connection burn into, made repairs @1700.
22701 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-10-20 07:02 | 2008-10-20 08:28 | 1 | 86 | 57155-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP STS WR # 26855485 // FUSE LINK APPEARS TO HAVE BROKEN. RE-FUSED XFMR. SH COD1 IDC XXXX
22702 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-11-14 04:14 | 2012-11-14 05:40 | 1 | 86 | 4395621 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. CC 1 VER/SDB IDC XXXX
22703 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-03-14 12:19 | 2015-03-14 13:45 | 1 | 86 | 4193391 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT ON 851-584 APPEARS TO BE BROKE. ONLY ONE CUSTOMER AFFECTED REPLACED CUTOUT AND RESTORED @ 13:45. SH// ISO 38830851C00584/ COD 1 PER SERVICER CCC*******/ VER/BOW
22704 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2009-07-07 18:57 | 2009-07-07 19:40 | 2 | 43 | 58842-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE67-146 VER/TOM L3/TOM IDC XXXX
22705 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2020-08-21 19:46 | 2020-08-21 21:00 | 2 | 74 | 4355871 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg connection burnt in two @ trans. #49-30, had to open to make repairs, opened @2048, made repairs and closed back in @2100. Only 1 customer had part power until I opened trans.//cod 1 (+1)
22706 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2019-07-09 17:45 | 2019-07-09 19:11 | 1 | 86 | 4686241 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neut burnt up in service drop. repairs made. pls close. tre
22707 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-11-07 13:49 | 2021-11-07 15:15 | 1 | 86 | 4064401 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 30t fuse open @ 878-76. restored @ 15:15
22708 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-01-13 11:59 | 2010-01-13 12:42 | 2 | 43 | 53563-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK COD-2 VER/HFP L3/HFP IDCC CCO XXXX
22709 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2008-03-05 13:29 | 2008-03-05 14:55 | 1 | 86 | 53940-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000105//45-385 CUTOUTS BURNT UP CHGED 3- CUTOUTS // 1 COD// IDCC PN4395 XXXX
22710 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-12-06 21:34 | 2020-12-06 23:00 | 1 | 86 | 4749761 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up in service. made repaires
22711 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2022-11-04 10:02 | 2022-11-04 10:45 | 2 | 43 | 4096871 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Customer called todd reporting that hot leg is burnt in twohot leg burnt in 2 at connection, will have to open XFM bank to make repairs will keep up with times// off @ 10:02hot leg burnt in 2 at connection, will have to open XFM bank to make repairs will keep up with times// off @ 10:02// on @ 10:45
22712 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2014-02-10 09:54 | 2014-02-10 11:20 | 1 | 86 | 4370461 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OOONLY ONE CUSTOMER AFFECTEDOO INSULINK CONNECTION IN 1/0 SECONDARY FROZE OPEN. REPAIRED AND RESTORED @ 11:20. SH VER/CRB
22713 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-12-28 18:34 | 2019-12-28 20:00 | 1 | 86 | 4187851 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on riser rep riser and rep dtodlight at this loc comp at 2000 by amg
22714 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-07-23 19:34 | 2014-07-23 21:00 | 1 | 86 | 4278161 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ETA 2000// REPLACE 2/3 SD WITH NEW VER/CRB
22715 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2012-10-27 13:33 | 2012-10-27 14:59 | 1 | 86 | 4176221 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BURNT DOWN 4/3 REPAIRED// VER/DBM IDC XXXX
22716 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2013-12-05 17:05 | 2013-12-05 17:48 | 2 | 43 | H4102281 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 517-15, OPENED LINE FUSE ON POLE 517-14 AT 17:05 TO ISOLATE , MADE REPAIRS RESTORED POWER AT 17:48. VER/CRB L3/HFP
22717 | Pikeville | 3402002 | KEYSER | STONECOAL | 2022-03-28 08:59 | 2022-03-28 10:25 | 1 | 86 | 4682391 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burned in 2 at XFM, made repairs and restored service @1025.
22718 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2018-12-08 14:37 | 2018-12-08 16:03 | 1 | 86 | 4518161 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | resqueezed bad connection complete L3/HFP
22719 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-05-23 12:39 | 2013-05-23 14:05 | 1 | 86 | 4172021 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 078S09 FUSE OUT ON TRANSFORMER FUSE WAS BROKE NOT BLOWN REPLACED 8-T FUSE POWER RESTORED KWB ///VER/CRB L/3 CRB IDC XXXX
22720 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-02-08 19:49 | 2022-02-08 21:15 | 1 | 86 | 4459671 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | current limiting fuse bad/replaced. tre
22721 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-07-06 16:49 | 2011-07-06 18:15 | 1 | 86 | 4477821 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE WENT BAD ON TRANSF == REPAIRED SPLICE//COD 1 IDC XXXX
22722 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2021-08-28 19:27 | 2021-08-28 20:10 | 2 | 43 | 4166911 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse blown and door didnt drop///it was tracking andfiring up on the cutout door//i replaced with new door and refused//restored at 20:10//complete//em
22723 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-04-26 14:44 | 2022-04-26 16:10 | 1 | 86 | 4803341 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had a bad 19.9 cutout on xformer pole 117-38.//// changed it out and got restored at 16:10
22724 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-03-17 09:43 | 2016-03-17 11:09 | 1 | 86 | 4858101 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVIN BURNED INTWO REPLACED ALL SERVINS WITH SQUEEZONS VER/HFP L3/HFP
22725 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2020-04-21 16:49 | 2020-04-21 18:15 | 1 | 86 | 4730741 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Fixed connection on pole
22726 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-08-21 23:19 | 2011-08-22 00:45 | 1 | 86 | 4739721 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-7044 BAD CUTOUT AND LA REPLACED VER/KEP IDC XXXX
22727 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-08-01 15:55 | 2010-08-01 17:21 | 1 | 86 | 60220-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT//VER/CRB IDC XXXX
22728 | South Williamson | 3411401 | DEWEY | INEZ | 2009-03-06 11:49 | 2009-03-06 13:15 | 1 | 86 | 55671-1 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN BAD ON TRANSF POLE//3411401//VER/CRB IDC XXXX
22729 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-12-13 14:29 | 2010-12-13 15:55 | 1 | 86 | 66043-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | HAD SERVIN FROZEN OUT//VER/CRB IDC XXXX
22730 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-04-16 18:14 | 2012-04-16 19:40 | 1 | 86 | 4678251 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT..CAN REPLACE..//..REPLACED CUTOUT..FUSE WAS NOT BLOWN.POWER ON NOW..JRV..04/16/12 COD-1 ISO PO 38821138C00130 VER/HFP L3/HFP IDC XXXX
22731 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-07-31 14:29 | 2018-07-31 15:55 | 1 | 86 | 4879501 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse pulled into on pole 95-171, refused @1555.
22732 | Hazard | 3303902 | LESLIE | WOOTON | 2014-09-08 10:17 | 2014-09-08 11:00 | 2 | 43 | 4479451 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/CRB
22733 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2015-02-22 14:37 | 2015-02-22 15:20 | 2 | 43 | 4072181 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RESTORED/ FUSE BROKE/ ISO 38830114000249/ COD 2/ VER/BOW
22734 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-07-04 20:51 | 2020-07-04 22:17 | 1 | 86 | 4110911 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | rplaced broke cutout, power restored at 2217
22735 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-10-13 15:39 | 2019-10-13 17:05 | 1 | 86 | 4136621 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection @ splice burnt into.repairs made.
22736 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-09-19 08:16 | 2012-09-19 09:42 | 1 | 86 | 4067261 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER DUE TO BAD INSULINK WIRE HEATED UP AND GOT TOGEATHER. BURNT INTO. I HAVE REPAIRS MADE EVERYTHING OK VER/KEP IDC XXXX
22737 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-01-13 12:23 | 2012-01-13 13:49 | 1 | 86 | 4257761 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SEND THIS TO TIM HALL, U.G. CABLE OUT RELEASED BY CREW 074S05 VER/KEP IDC XXXX
22738 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-02-07 18:22 | 2014-02-07 19:05 | 2 | 43 | 4367221 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT DOOR VER/CRB IDCC FEC49 XXXX
22739 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-09-26 12:57 | 2011-09-26 13:40 | 2 | 43 | 4918641 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT ON POLE 211-42, LINE FUSE OPENED ON POLE 211-219(30 T ). ENTERED MD - COD- 2 ISO LF 38830211000219 VER/HFP L3/HFP IDC XXXX
22740 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-08-06 20:24 | 2014-08-06 21:50 | 1 | 86 | 4338111 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD HOT TAP. POWER BACK ON. COD-1 ISO PO @ 38830142A00385 VER/HFP L3/HFP
22741 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-10-19 16:09 | 2015-10-19 17:35 | 1 | 86 | 4361681 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE DROP ///WILL REPAIR/// REPAIRED BROKEN NEUTRAL AND RESTORED SERVICE 124/124/248/// ONLY 1 CUSTOMER AFFECTED// VER/ ADH
22742 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2017-06-26 19:58 | 2017-06-26 21:24 | 1 | 86 | 4048941 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA @ POLE 37830163A00066//CUST SAYS ITS OK TO HOLD TILL TOMORROW//HOMER IS MAKING AN OPS ORDER//ADDRESS 20204 EAST RT 122// VER/CRB
22743 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-07-23 14:34 | 2011-07-23 16:00 | 1 | 86 | 4599831 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE, REPLACED 6T FUSE, ALL POWER RESTORED VER/KEP
22744 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-02-05 13:25 | 2010-02-05 14:08 | 2 | 43 | 63604-1 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN AND BURNED TOP OF POLE. I AM GOING TO CHANGE CUTOUT AND CREW WILL COME NEXT WEEK AND REPAIR POLE. SEND TO RON RYE. TIM HALL SAID HE WOULD HAVE SOMETHING WROTE UP ON IT. I CHANGED CUTOUT//VER/CRB. IDCC MCCNI XXXX
22745 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-07-04 11:59 | 2019-07-04 13:25 | 1 | 86 | 4653321 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm cutout broke on pole 145-240..will make repairs..restored.
22746 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2013-04-18 13:24 | 2013-04-18 14:50 | 1 | 86 | 4022381 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT VER/KEP IDC XXXX
22747 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-03-07 11:22 | 2015-03-07 12:05 | 2 | 43 | H4156101 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. WILL BE OUT OF TRUCK CHANGING CUTOUT. DUE TO BAD CUTOUT I OPENED 3 POLE SIDE TAP ON POLE 810-C-42 AT 11:22 AND CLOSED SIDE TAP BACK IN AT 12:05/FIX IT IN HOIS/ LINE FUSE THEN HARVEY OPENED TRANSFORMER AND SIDE TAP TO FIX BAD CUTOUT// VER/ ADH
22748 | Pikeville | 3421001 | BREAKS | CITY | 2012-05-05 14:16 | 2012-05-05 15:42 | 1 | 86 | 4750571 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE TRANSFORMER FUSE BROKE, AND THE CUTOUT DOOR DID NOT DROP OUT. THE CUTOUT DOOR BURNED UP. I REPLACED THE DOOR.///VER/CRB L/3 CRB IDC XXXX
22749 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2022-03-14 00:34 | 2022-03-14 02:00 | 1 | 86 | 4621741 | 86 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Reported multiple units in apartment building having dim light/flickering issues. Showing 1 cc on 50kVa///Connection burnt into @ xfm ////One service feeds multiple apartments here///Repaired connection and restored service @ 02:00
22750 | Hazard | 3310502 | HADDIX | CANOE | 2021-06-27 08:17 | 2021-06-27 09:43 | 1 | 86 | 4810901 | 86 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
22751 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2015-10-19 20:38 | 2015-10-19 22:03 | 1 | 85 | 4362441 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | BAD METER PART POWER REPLACED METER/ ISO 38830020A10438/ COD 1/ VER/BOW L3/HFP HFPC CNT4
22752 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-01-29 12:35 | 2011-01-29 14:00 | 1 | 85 | 51952-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND FAILED LIGHTNING ARRESTER HAD BLOWN UP, CAUSING ARM BRACKET TO FALL OFF ARM, CAUSING THIS OUTAGE, HAVE ARRESTER CUT IN THE CLEAR AND REPAIRS ARE MADED, POWER IS RESTORED AT THIS LOC, SEND COPY TO MR. RAYBURN TO HAVE CREW TO COME AND REPAIR THIS ARRESTER, ON POLE 926-8//MADE AN AED//VER/CRB IDC XXXX
22753 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-02-05 09:50 | 2011-02-05 11:15 | 1 | 85 | 54170-1 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER ON THE SERVICE DROP ONLY ONE CUSTOMER AFFECTED.// VER/DBM IDC XXXX
22754 | Whitesburg | 3312902 | JENKINS | JENKINS | 2008-09-26 13:39 | 2008-09-26 15:04 | 1 | 85 | 50956-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT ON POLE 381-793 WHICH SERVES A TRANSFORMER WITH ONE CUSTOMER IS BROKEN COD-1 IDCC PN788 XXXX
22755 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-11-13 13:20 | 2012-11-13 14:45 | 1 | 85 | 4393831 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT ON POLE 165-37. NO TRUCKS TO POLE. RELEASED BY CREW 078S01// FETR 15:30 JEH// REPAIRS COMPLETE POWER REST. @ 14:45 JEH( THIS FEEDS 1 MTR AND 1 D/D LIGHT ) VER/KEP IDC XXXX
22756 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-06-14 16:06 | 2008-06-14 17:31 | 1 | 85 | 64817-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402204POLE FIRE DUE TO BAD CUTOUT, REPLACED CUTOUT AND EXTINQUISHED FIRE, CREATED OPS ORDER TO REPLACE POLE / GXJ//VER/CRB
22757 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-02-12 15:27 | 2008-02-12 16:52 | 1 | 85 | 61438-1 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3000701//CREW ON SITE /SLEEVE PULLED OUT OF SERVICE NEUTRAL/CREW TO REPAIR/PLEASE COPY TICKET TO PEGGY WYSONG/POSSIBLE DAMAGE COMPLAINT/VEM/ SENT EMAIL TO PEGGY--HFP /// VER/TOM IDC XXXX
22758 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-02-13 11:25 | 2012-02-13 12:50 | 1 | 85 | 4345011 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | THIS SERVES A UTILITY ROOM. UG CABLE IS IN TROUBLE HERE. PLEASE SEND THIS TO TIM HALL IN PIKEVILLE .HE WILL HAVE UG LOCATED & REPAIRED. RELEASED BY CREW 074S04//SENT TO TIM HALL, TO BE WORKED TOMORROW PER SERVICER//NOT REPORTED BY CUSTOMER // VER/DBM IDC XXXX
22759 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-02-10 12:28 | 2022-02-10 13:53 | 1 | 85 | 4465091 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | customer had a broke neutral in service drop.//// fixed and re-deadended service to house.
22760 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-02-01 13:45 | 2012-02-01 15:10 | 1 | 85 | 4313071 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR FROZE OPEN. RE-SQUEEZED ALL CONNECTIONS @ WEATHERHEAD. RESTORED @ 15:10. SH VER/KEP IDC XXXX
22761 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2013-01-29 16:00 | 2013-01-29 17:25 | 1 | 85 | 4751631 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | REPLACED CROSSARM ///VER/CRB L/3 CRB IDC XXXX
22762 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-08-12 12:15 | 2012-08-12 13:40 | 1 | 85 | 4929931 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SERVICE MADE REPAIRS VER/HFP L3/HFP IDC XXXX
22763 | Hazard | 3303902 | LESLIE | WOOTON | 2017-01-14 16:40 | 2017-01-14 18:05 | 1 | 85 | 4298251 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER,MADE REPAIRED/ ISO 37830341000026/ COD 1/ VER/BOW L3/HFP XXXHFP
22764 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-03-29 12:25 | 2019-03-29 13:50 | 1 | 85 | 4035291 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad servend connection at the transformer replaced connections everything ok
22765 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-11-09 13:10 | 2019-11-09 14:35 | 1 | 85 | 4015101 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection full power back on at 14:35
22766 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2022-05-21 19:15 | 2022-05-21 20:40 | 1 | 85 | 4922801 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop down
22767 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2010-10-27 19:10 | 2010-10-27 20:35 | 1 | 85 | 65947-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#37518060// ONLY ONE CUSTOMER OUT.//PRIMARY MTRING //VER/CRB IDCC CNT10 OUT EARLIER? SEE 65843-1 XXXX
22768 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-10-17 15:47 | 2016-10-17 17:12 | 1 | 85 | 4022951 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED C/O AND 6T TRAN FUSE--IN AT 17:12--ALLGOOD--DS101716/ ISO 38830162C00107/ COD 1/ VER/BOW L3/HFP XXXHFP
22769 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-10-18 15:35 | 2009-10-18 17:00 | 1 | 85 | 55700-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT.//COD 1// VER/DBM IDC XXXX
22770 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-02-16 09:50 | 2011-02-16 11:15 | 1 | 85 | 58099-1 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | XFR FUSE OUT,WILL RE-FUSE/////FAILED SURGE ARRESTOR TOOK XFR FUSE OUT,MADE NECESSARY REPAIRS AND RESTORED,ALL OK AFTERWARDS // COD-1 ISO TF 38821058B00277 VER/HFP L3/HFP IDC XXXX
22771 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-05-03 14:45 | 2015-05-03 16:10 | 1 | 85 | 4385941 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL CONNECTION PULLED APART IN SERVICE DROP/// WILL REPAIR//// REPAIRED BAD CONNECTION IN SERVICE DROP AND RESTORED SERVICE @ 16:10/// ONLY 1 CUSTOMER AFFECTED VER/CRB
22772 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2014-05-04 14:45 | 2014-05-04 16:10 | 1 | 85 | 4661841 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF THE SERVICE AT THE CUSTOMER SERVICE POLE. ONLY ONE CUSTOMER HAD PART POWER. VER/SEF
22773 | Pikeville | 3408103 | SALISBURY | MARTIN | 2019-04-17 10:21 | 2019-04-17 11:46 | 1 | 85 | 4125321 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | cust on wrong line fuse, LF 38830020C31008 ONLY 1 CUST OUTlooks like 15t line fuse on pole 1174-A-242 may have broken. this feeds towards transformer on pole 1074-A-494 is the one we had out. fuse was broken fused up everything ok
22774 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-04-26 14:30 | 2020-04-26 15:55 | 1 | 85 | 4753701 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad splice on sec
22775 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-09-05 14:05 | 2012-09-05 15:30 | 1 | 85 | 4018831 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T TRANSFORMER FUSE BROKE-REPLACED FUSE AND POWER RESTORED AT 15:30 COD-1 ISO TF 38830189000139 VER/HFP L3/HFP IDC XXXX
22776 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-06-15 11:55 | 2013-06-15 13:20 | 1 | 85 | 4342651 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 19.9 CUTOUT DOOR.//COD 1//ISO// VER/DBM IDC XXXX
22777 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2014-09-22 21:45 | 2014-09-22 23:10 | 1 | 85 | 4520911 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON THE SECONDARY POLE. POWER IS BACK ON. VER/CRB
22778 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-11-19 13:45 | 2014-11-19 14:02 | 5 | 17 | 4746411 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830045D47578 BAD CUTOUT ON THIS POLE //COD 5//OPENED XFMR @ 13:45---BACK ON @ 14:02---TBL TKT C0MP---RMV VER/CRB
22779 | South Williamson | 3411401 | DEWEY | INEZ | 2011-03-09 07:15 | 2011-03-09 08:40 | 1 | 85 | 51999-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT DOOR BURNT IN TWO ON POLE 672-74//CHANGED DOOR OUT//RESTORED AT 8:40//COMPLETE//EM VER/KEP IDC XXXX
22780 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2017-10-16 17:33 | 2017-10-16 18:58 | 1 | 85 | 4463571 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 255-92 RESAGED OPEN WIRE COMPLETE/ ISO 38830255000092/ COD 1/ VER/BOW L3/HFP XXXHFP
22781 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2009-01-03 14:11 | 2009-01-03 15:36 | 1 | 85 | 51073-1 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309104// NO TROUBLE VISIBLE. I AM GOING TO CHECK VOLTAGE AND CONNECTIONS. FOUND #2 SERVICE CONNECTOR BURNED OFF AT TRANSFORMER ONLY AFFECTED 1 CUSTOMER // VER/TOM L3/TOM IDC XXXX
22782 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-02-11 10:35 | 2015-02-11 12:00 | 1 | 85 | 4007691 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN ON SERV REPAIRS MADE PLEASE CLOSE TICKET THANKS.BT 38830255000180 VER/CRB L3/HFP XXX
22783 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2015-12-09 19:13 | 2015-12-09 20:38 | 1 | 85 | 4521751 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON UG VER/CRB
22784 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-03-10 13:25 | 2011-03-10 14:50 | 1 | 85 | 52933-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | KWH METER HAD WATER VER/KEP IDC XXXX
22785 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-08-23 19:40 | 2015-08-23 21:05 | 1 | 85 | 4165911 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 5 KVA XFMR LEAKING. OPENED XFMR @ 19:40, REPLACED AND CLOSED @ 21:05. SH VER/ARN
22786 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-01-02 19:25 | 2008-01-02 20:50 | 1 | 85 | 52939-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001002//BROKEN FUSE ON XFMR CUTOUT//COD 1// VER/DBM IDC XXXX
22787 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-02-14 16:50 | 2018-02-14 18:15 | 1 | 85 | 4841111 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t transformer fuse out due to bad cutout . replaced cutout everything ok
22788 | Hazard | 3311103 | STINNETT | WENDOVER | 2019-01-26 16:13 | 2019-01-26 17:38 | 1 | 85 | 4725031 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | cutout gate burnt up
22789 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2018-09-05 20:35 | 2018-09-05 22:00 | 1 | 85 | 4047121 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called customer no answer/no crew required/ ISO 38830273000066/ COD 1
22790 | Hazard | 3311101 | STINNETT | REDBIRD | 2013-02-16 03:25 | 2013-02-16 04:50 | 1 | 85 | 4823211 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT GATE // NO FETR ON OUTAGE// ONLY 1 CUSTOMRE ON THIS TRANSFORMER VER/TOM L3/TOM IDC XXXX
22791 | Pikeville | 3407101 | TOPMOST | DEMA | 2009-03-09 09:00 | 2009-03-09 10:25 | 1 | 85 | 56479-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP RELATED TO ORDER 56454-1 L3/HFP IDC XXXX
22792 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-12-11 09:38 | 2009-12-11 11:03 | 1 | 85 | 63247-1 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD CONNECTION AT XFR POLE, RE-WORKED AND RESTORED.ALL OK AFTERWARDS L3/HFP
22793 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2016-09-01 09:35 | 2016-09-01 11:00 | 1 | 85 | 4859591 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND FEEDING FROM SECONDARY PEDESTAL 1150-165, GOING TO WASTE WATER PUMP, WILL BE MAKING REPAIRS. RESTORED AT 11:00. VER/CRB
22794 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2014-11-25 06:35 | 2014-11-25 08:00 | 1 | 85 | 4778681 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK BURNT INTO REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/HFP L3/HFP
22795 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-10-04 13:16 | 2022-10-04 14:41 | 1 | 85 | 4975571 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a Hot Leg into at Trans in Splice,Will be making repairs.Restored at 14:41.
22796 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-12-13 17:38 | 2022-12-13 19:03 | 1 | 85 | 4257521 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Had Hot Leg into in Bushing on Trans,Replaced and Restored at 19:03.
22797 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2019-07-15 12:00 | 2019-07-15 13:25 | 1 | 85 | 4710331 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 leg of service burned open. will make repairs. complted
22798 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2013-12-12 12:55 | 2013-12-12 14:20 | 1 | 85 | 4156721 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 65-4 BAD CUTOUT MAYBE TRUCK TO POLE ACROSS CK. RED TAPE ON POLE RELEASED BY CREW 078S08 ***CHANGE ISO POLE*****POLE 65-4 BAD CUTOUT MAYBE TRUCK TO POLE ACROSS CK. RED TAPE ON POLE RELEASED BY CREW 078S08 CHANGE ISO POLE CREW ON SITE, REPAIRS MADE.ALL POWER RESTORED VER/SEF L3/HFP
22799 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-04-11 11:10 | 2009-04-11 12:35 | 1 | 85 | 51453-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3110903 - FOUND A CRACKED CUTOUT ON THIS POLE, THAT CAUSED THE FIRE, POLE WAS CHARRED BUT IS OK, I CHANGED THE CUTOUT AND EVERYTHING IS OK AT THIS LOC/VER/CRB IDC XXXX
22800 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-01-12 09:21 | 2009-01-12 10:46 | 1 | 85 | 54388-1 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3402002/NEUTRAL BROKE IN SERVICE DROP, CUSTOMER HAS EQUIPMENT DAMAGE//VER/CRB L3/KEP IDC XXXX
22801 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-01-04 10:47 | 2012-01-04 12:12 | 1 | 85 | 4232511 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CUTOUT VER/KEP IDC XXXX
22802 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-02-06 05:55 | 2015-02-06 07:20 | 1 | 85 | 4995341 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPAN OF SECONDARY AND PRIMARY NEUTRAL FELL AND CAUSED NEUTRAL AND HOT CONDUCTOR IN OPEN WIRE SEC TO CONTACT EACH OTHER. XFMR FUSE BLOWN. CLOSED XFMR FUSE 834-70 @ 7:20. SH VER/CRB L3/HFP XXX
22803 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-12-12 14:30 | 2012-12-12 15:55 | 1 | 85 | 4464731 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN ON ONE HOTLEG, REDONE ONE CONN APR CLOSE TICKET. DWEST//COD 1// VER/DBM
22804 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-05-10 12:38 | 2020-05-10 12:55 | 5 | 17 | 4819401 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | neutral pulled out of sleeve. will make repaires. had line fuse on pole 1061-11 open from 12:38 to 12:55
22805 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-12-31 13:13 | 2008-12-31 14:38 | 1 | 85 | 66585-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801//NO CREW REQUIRED BAD CUTOUT DOOR//VER/CRB L3/KEP IDC XXXXX
22806 | Pikeville | 3413401 | GARRETT | GARRETT | 2019-12-15 14:52 | 2019-12-15 16:17 | 1 | 85 | 4156091 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t fuse out due to bad cutout bottom of cutout broke off hanging down pole. replaced bad cutout everything ok/ ISO 37830041B00018/ COD 1
22807 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-12-13 09:26 | 2008-12-13 10:51 | 1 | 85 | 57932-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3201001//, ON SITE, BAD CUTOUT, REPLACING CUTOUT//COD 1// VER/DBM L3/KEP IDC XXXX
22808 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-07-19 16:50 | 2013-07-19 18:15 | 1 | 85 | 4555921 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS///////BAD CONNECTION ON XFR POLE,RE-WORKED,ALL OK AFTERWARDS//////ALSO HAD TO TRIM TREES TO GET TO XFR POLE// VER/DBM
22809 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-11-03 15:55 | 2014-11-03 17:20 | 1 | 85 | 4697201 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL HAS GOT AGIANST HOT LEG AND BURNT INTO/// WILL RESPLICE NEUTRAL AND BOTH HOT LEGS IN SERVICE @ TRANSFORMER//// RE-SPLICED NEUTRAL AND RE-SQUEEZED HOT LEGS @ TRANSFORMER //// CHECKED VOLTAGE EVERYTHING OK NOW 123/123/246/// PLEASE SEND COPY TO PEGGY WYSON CUSTOMER MAY HAVE DAMAGES VER/HFP L3/HFP
22810 | Whitesburg | 3312901 | JENKINS | KONA | 2019-01-29 12:25 | 2019-01-29 13:50 | 1 | 85 | 4731521 | 85 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr, made repairs restored power at 13:50.. Just one customer out ¦¦ L3/HFP
22811 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-10-06 09:40 | 2008-10-06 11:05 | 1 | 85 | 53551-1 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP LOOSE CONNECTION ON POLE....RE SQUEEZED...BB IDC XXXX
22812 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-01-31 11:05 | 2022-01-31 12:30 | 1 | 85 | 4418351 | 85 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830876B00100.changing//OPENED 1105 CLOSED 1230
22813 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-09-15 22:46 | 2018-09-16 00:10 | 1 | 84 | 4103281 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | xfm. cutout door burnt into on pole 167-113..will replace.restored..
22814 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-01-10 02:21 | 2016-01-10 03:45 | 1 | 84 | 4598301 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BROKEN CUTOUT VER/ARN
22815 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2017-11-27 12:17 | 2017-11-27 12:45 | 3 | 28 | 4604461 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37820217D00056//OPENED @ 1217 CLOSED 1245
22816 | Whitesburg | 3401301 | FLEMING | NEON | 2017-05-16 15:06 | 2017-05-16 16:30 | 1 | 84 | 4805141 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE INTO SERVING XFMR ON POLE 355-393 HELP ON ITS WAY/ ISO 37830355D30089/ COD 1/ VER/BOW
22817 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2018-09-08 19:12 | 2018-09-08 20:36 | 1 | 84 | 4060061 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout
22818 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-01-24 14:21 | 2022-01-24 15:45 | 1 | 84 | 4401181 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp is burnt off at pole 183-266, making repairs, power restored
22819 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-11-20 12:06 | 2018-11-20 13:30 | 1 | 84 | 4463761 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse out, cutout is bad but i have power restored, contacting DSS to see what he wants to do with it. pole 37830227A00051 R. Rice crew coming to replace, cutout replaced L3/HFP
22820 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2019-10-07 10:08 | 2019-10-07 10:22 | 6 | 14 | 4106201 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | recl 771-D-433//cc35 (middle / A phase hot tap burnt off). Opening other phases at B,C off@ 1008 cc 291 all 3 on@1022/// only 6 cust on KY side per POR
22821 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-04-26 21:44 | 2016-04-26 23:08 | 1 | 84 | 4129621 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUSTOMER AT&T CELL TOWER/ THEY GOT AN ALARM HAVE NOT HAD ANYONE ON SITE TO VERIFY IF THEY ARE OUT/ CUSTOMER WANTS TO KNOW IF THEY NEED TO HOOK UP GENERATOR./NO CRRW REQUIRED REPLACED CONNECTION/ ISO 38830175000045/ COD 1/ VER/BOW
22822 | Hazard | 3309302 | VICCO | JEFF | 2017-02-04 10:50 | 2017-02-04 11:02 | 7 | 12 | H4358371 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ***SEE 4358371*** OPEN TRANSFORMER AT 10:50 AND CLOSE AT 11:02///TRANSFORMER LEAD CONNECTION FAILED AT OPEN SECONDARY POINT DUE TO LOAD/ PER SERVICER THERE WAS 3 CUSTOMERS PART POWER ORIGINALLY/ ISO 37830348A00135/ COD 10/ VER/BOW L3/HFP XXXHFP
22823 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-04-28 12:01 | 2009-04-28 13:25 | 1 | 84 | 54782-1 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE DROP RELEASED BY CREW 078S11//3001201//VER/CRB IDC XXXX
22824 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-05-03 14:21 | 2021-05-03 15:45 | 1 | 84 | 4516831 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout broke on 770-b-73//there is a line down here that is cable co.//need one man and big bucket to reach cutout//
22825 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-05-05 10:48 | 2017-05-05 11:30 | 2 | 42 | 4754791 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-5 6T BAD CUTOUT DOOR REPLACED COD-2 ISO TF 38830069D16005. L3/HFP XXXHFP
22826 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-10-11 13:06 | 2015-10-11 14:30 | 1 | 84 | 4338601 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FISE LINK BROKE REPLACED 6T FUSE/ ISO 37830048A41301/ COD 1/ VER/BOW L3/HFP XXXHFP
22827 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2020-05-06 10:11 | 2020-05-06 11:35 | 1 | 84 | 4805411 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed at weatherhead. Only one customer affected. Replaced 65 ft service due to multiple splices. Restored @ 11:35. sh
22828 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-06-14 21:09 | 2010-06-14 22:33 | 1 | 84 | 64653-1 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | GUY WIRE BROKE AND FELL AGAINST XFMR PRIMARY RISER BLOWING XFMR FUSE. WORKING TO SECURE GUY WIRE TAIL AND CHANGE RISER BECAUSE IT IS DAMAGED. GUY WIRE SECURED, RISER REPLACED AND ANIMAL GUARD INSTALLED. SUSPECT GUY HAS BEEN BROKEN A LONG TIME AND A BIRD LANDED ON IT PUSHING IT INTO RISER. RESTORED @ 22:33. WILL SEND A JOB TO T. MILLER TO HAVE GUY REPAIRED. SH
22829 | Hazard | 3309002 | JEFF | JEFF | 2014-12-29 09:52 | 2014-12-29 10:13 | 4 | 21 | 4889051 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD SOLID BLADE CUTOUT// SERVICER OPENING RECLOSER 321-D3-621 TO SAFELY MAKE REPLACE SOLIDE BLADE/BAD SOLID BLADE CUTOUT === BDA CUTOUT ON POLE 37830321D00416 ==== OPEN RECLOSER ONPOLE 37830321D30621 TO TAKE LOAD OFF CUTOUTS OPEN AT 09:52 CLOSED AT 10:13 === CHANGED CUTOUT === POWER ON AT 10:13 ==// COD 4// VER/ ADH
22830 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-01-07 15:21 | 2015-01-07 16:45 | 1 | 84 | 4913841 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON ONE LEG OFF THE SERVICE DROP HAS BURNED INTO AT THE TRANSFORMER SECONDARY LEAD. I ALSO HAD TO REWORK THE CONNECTIONS ON SECONDARY POLE 38820987A00085. VER/CRB
22831 | Hazard | 3420001 | SOFT SHELL | VEST | 2019-12-10 18:21 | 2019-12-10 19:45 | 1 | 84 | 4143091 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad secondary splice. power restored at 19:45
22832 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2018-02-04 20:06 | 2018-02-04 21:30 | 1 | 84 | 4804221 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse
22833 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-06-07 11:41 | 2012-06-07 12:23 | 2 | 42 | 4890911 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XMF FUSE.. FUSE HAD PULLED LOOSE WAS NOT BLOWN, APR CLOSE TICKET //VER/GAH IDC XXXX
22834 | Hazard | 3309003 | JEFF | VIPER | 2014-09-16 11:08 | 2014-09-16 11:36 | 3 | 28 | 4502531 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | TV BOOSTER, BAD SPLICE IN SERVICE NEUTRAL , OPENED XFMR AT 11:08 MADE REPAIRS RESTORED POWER AT 11:36 VER/CRB
22835 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-11-30 11:14 | 2012-11-30 11:56 | 2 | 42 | 4433211 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN TRANSFORMER FUSE. ///VER/CRB L/3 CRB IDC XXXX
22836 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-07-06 20:11 | 2020-07-06 20:32 | 4 | 21 | 4119981 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse had melted out refused txmf apr at 2032 close ticket
22837 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-11-28 17:03 | 2019-11-28 17:45 | 2 | 42 | 4100951 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Burnt door, time on 17:45
22838 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2017-05-03 16:27 | 2017-05-03 17:51 | 1 | 84 | 4740841 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW ON SITE---FOUND BURNT HOT LINE CLAMP ON B PH. CUTOUT--CHANGED ALL 3 CUTOUTS AND HOTTAPS--CHECKED AND ALL SEEMS OK--VOLT GOOD---T BURTON TO FOLLOW UP WITH CUSTOMER----TBL TKT COMP---RMV/ 1627-1751/ ISO 38830068B00661/ COD 1/ VER/BOW
22839 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-12-21 10:18 | 2014-12-21 11:00 | 2 | 42 | 4873011 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER POLE, GOING UP TO FIX NOW..P.HICKS.BAD SERV ENDS ON TRANSFORMER POLE./ OPENED TRANSFORMER TO MAKE REPAIRS 10:18/ ALL POWER RESTORED@ 11:00 HRS..P.HICKS/ ISO 37830410B00054/ COD 2/ VER/BOW
22840 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-04-15 17:06 | 2015-04-15 18:30 | 1 | 84 | 4323421 | 84 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP GOES THROUGH A TREE THAT ASPLUNDH WAS TRIMMING. THERE IS A SPLICE MID SPAN OF THE DROP THAT THE NEUTRAL HAS BURNED INTO FROM INSULINKS GOING BAD. I WILL MAKE REPAIRS ON THE SPLICE. REPAIRS ARE MADE AND POWER IS ON, ONLY ONE CUSTOMER WAS OFF.
22841 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-10-21 15:39 | 2012-10-21 17:03 | 1 | 84 | 4161161 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY 1 COUSTOMER AFFECTED.LOOSE CONNECTION ON XFMR POLE. REPLACED CONNECTION ///VER/CRB L/3 CRB IDC XXXX
22842 | Hazard | 3303901 | LESLIE | HYDEN | 2017-07-21 12:46 | 2017-07-21 14:10 | 1 | 84 | 4151121 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 5 KVA 37830266000034 WILL NEED R/W CREW AND LINE CREW/// CUST AGREED TO DO THIS MONDAY, NO ONE LIVING IN CABIN/ OPS #039584372/ ISO 37830266000034/ COD 1/ VER/BOW L3/HFP XXXHFP
22843 | Whitesburg | 3312901 | JENKINS | KONA | 2012-10-18 17:00 | 2012-10-18 17:12 | 7 | 12 | 4153751 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING.HOT LEG MELTED ON POLE 404-7, WILL HAVE TO OPEN THIS TRANS. TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES.OPENED AT 17.:00, CLOSED BACK AT 17:12. JOB COMPLETE. VER/KEP IDC XXXX
22844 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-12-29 12:49 | 2013-12-29 13:10 | 4 | 21 | 4209711 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AT 1249 - OPENED CUTOUJT AT POLE 245-32 TO CLEAR UP FAILED CUTOUT. ON @ 1310 // COD 4BAD CUTOUT ON POLE 245D-205 . OPENED LINE FUSE ON POLE 245D-32 @ 12:48 TO CHANGE CUTOUT ON POLE 205 & PUT OUT FIRE . CLOSED LINE FUSE BACK ON POLE 245D-32 @ 13:10 COD-4 ISO LF 37830245D00032 VER/HFP L3/HFP
22845 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2021-09-22 10:40 | 2021-09-22 12:04 | 1 | 84 | 4269321 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burnt in two, moved out span guy, and repaired
22846 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-02-18 16:51 | 2020-02-18 18:15 | 1 | 84 | 4416171 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout L3/HFP
22847 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-06-01 20:03 | 2014-06-01 20:45 | 2 | 42 | 4959461 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE, VER/CRB
22848 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-07-07 19:48 | 2020-07-07 21:12 | 1 | 84 | 4124861 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @24-D2-446, checking. Trans. fuse had melted, refused @2112.
22849 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-01-08 10:00 | 2014-01-08 10:42 | 2 | 42 | 4258631 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEC CABLE SHORTED OUT,BURNED INTO,WILL TRY TO REPAIR//////MADE REPAIRS & RESTORED.POOR SERVE-IN CONNECTIONS HEATED UP AND BURNT NEUTRAL INTO.POSSIBLE DAMAGES///XFR OFF 10:00,ON AT 10:42.ALSO POSSIBLY TAPED DROP NEAR POLE ALSO CONTRIBUTED TO THIS VER/CRB
22850 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-11-24 14:48 | 2018-11-24 15:30 | 2 | 42 | 4473831 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced fuse door L3/HFP
22851 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-10-09 02:06 | 2008-10-09 03:30 | 1 | 84 | 54506-1 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT D VER/ARN IDC XXXX
22852 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-03-19 09:13 | 2008-03-19 10:37 | 1 | 84 | 58449-1 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, CONNECTION BAD ON XFMR LEADS RELEASED BY CREW 077S02 VER/HFP IDC XXXX
22853 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-07-26 16:26 | 2015-07-26 17:50 | 1 | 84 | 4944171 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN. @ XFMR MELTED OUT . 4/0-4/0 CONN. REPLACED CONN. TOLD CUST. THEY NEED TO DO LOAD CHECK , MAY HAVE TO MUCH LOAD ON 1 LEG. THIS HS ONLY BEEN IN HERE 1 MOUNTH . THIS IS NEW DQ IN JACKSON . VER/CRB
22854 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-05-07 15:30 | 2011-05-07 16:54 | 1 | 84 | 4017261 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL CONNECTOR IN SERVICE PULLED OUT//// RESPLICED NEUTRAL. POWER OK VER/HFP L3/HFP IDC XXXX
22855 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-07-06 16:06 | 2018-07-06 17:30 | 1 | 84 | 4741821 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke into , I replaced it
22856 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-06-14 18:00 | 2009-06-14 19:24 | 1 | 84 | 63461-1 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK VER/KEP L3/KEP IDC XXXX
22857 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-06-26 11:38 | 2009-06-26 13:02 | 1 | 84 | 62472-1 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE WILL NEED TOBE CHANGED IN FUTURE BURN HOLE IN BACK OF POLE OK FOR NOW
22858 | Pikeville | 3413401 | GARRETT | GARRETT | 2019-08-22 13:21 | 2019-08-22 14:45 | 1 | 84 | 4928291 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 10t fuse out due to bad coutout broke into. replaced cutout fused up everything ok
22859 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-01-16 18:17 | 2012-01-16 19:41 | 1 | 84 | 4265731 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE, REPAIRED CONNECTION// VER/DBM IDC XXXX
22860 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-04-30 09:38 | 2018-04-30 10:06 | 3 | 28 | 4289951 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Found bad insulink connection had burnt service neutral open at xfmr pole. Opened xfmr @ 9:38 to make repairs. Repaired and closed xfmr @ 10:06
22861 | Hazard | 3309302 | VICCO | JEFF | 2009-01-18 21:21 | 2009-01-18 22:45 | 1 | 84 | 58147-1 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309302/ WR#28113258 / CONNECTION IN METERBASE WENT BAD == REPAIRED == THIS A FEED THROUGHT METERBASE == VER/LDA L3/KEP
22862 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-04-06 08:26 | 2015-04-06 09:50 | 1 | 84 | 4279091 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 SERVICE DROP BURNT DOWN , REPLACED WITH #2 DROP RESTORED POWER AT 09:50 VER/CRB
22863 | Hazard | 3301401 | COMBS | COMBS | 2011-11-04 16:58 | 2011-11-04 18:22 | 1 | 84 | 4051951 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN TRANSFORMER CUTOUT, WILL REPLACE.P.HICKS..ALL POWER RESTORED @ 18:22 HRS..P.HICKS//COD 1// VER/DBM IDC XXXX
22864 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2020-10-20 17:51 | 2020-10-20 18:33 | 2 | 42 | 4571651 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @26-182, checking. Trans. fuse melted out, refused @1833.
22865 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2022-11-19 21:56 | 2022-11-19 23:20 | 1 | 84 | 4163191 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse door burnt in two
22866 | Pikeville | 3421002 | BREAKS | GRASSY | 2008-01-10 16:21 | 2008-01-10 17:03 | 2 | 42 | 55581-1 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CC=2 CUTOUT BROKE WHEN SERVICER OPENED IT IN ORDER TO CLEAR UP BAD ARRESTER. 222-B-245 ***THIS AFFECTED VA CUSTOMERS ONLY, NO KY CUSTOMERS WERE INTERRUPTED*** VER/CKG IDC XXXX
22867 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-03-14 12:00 | 2022-03-14 12:28 | 3 | 28 | 4623351 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfr fuse complete,,,cutout door broke
22868 | Paintsville | 3409302 | KENWOOD | AUXIER | 2013-10-22 12:51 | 2013-10-22 14:15 | 1 | 84 | 4954371 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY ONE CUSTOMER AFFECTED WRONG ACCOUNT. THIS IS FOR THE HOUSE NEXT DOOR SERVED FROM XFMR POLE 38830905000168. XFMR CUTOUT DOOR BURNT UP. REPLACED CUTOUT DOOR AND RESTORED @ 14:15. SH COD-1 ISO TF 38830905000168 VER/HFP L3/HFP
22869 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-04-13 14:32 | 2016-04-13 15:56 | 1 | 84 | 4088691 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BARREL CONNECTOR PULLED INTO ON POLE 472-145, RESQUEEZED, EVERYTHING OK.//COD 1 VER/CRB
22870 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-12-06 12:54 | 2009-12-06 13:08 | 6 | 14 | 62845-1 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP OPENED TRANSFORMER AT 12:54 AND CLOSED AT 13:08 FOR 6 CUSTOMERS FROM ORDER 61604-1 L3/HFP IDC XXXX
22871 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2014-01-06 12:30 | 2014-01-06 13:54 | 1 | 84 | 4237361 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I CHANGED OUT CONNECTION ON XFMR LEAD//COD 1// VER/DBM
22872 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-02-26 14:56 | 2013-02-26 16:20 | 1 | 84 | 4853021 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTOR ON XFMR LEAD. WE REPLACED XFMR LEAD//COD 1// VER/DBM IDCC PN106 XXXX
22873 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-10-14 14:56 | 2019-10-14 16:20 | 1 | 84 | 4139191 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connections pulled loose in service drop, repaired
22874 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-10-19 18:44 | 2021-10-19 20:08 | 1 | 84 | 4367001 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Call first thing in the morning. 15kva transformer is under sized may need a 25 or 50kva replacment and 1/o service.
22875 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-06 10:54 | 2014-01-06 12:18 | 1 | 84 | 4236531 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED. RE-WORKED CONNECTIONS AT WEATHERHEAD. RESTORED @ 12:18. SH// VER/DBM
22876 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-08-21 19:13 | 2011-08-21 19:55 | 2 | 42 | 4737421 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | COD-2 ISO TF 38831098B00549FUSE BROKEN . REFUSED TRANSFORMER, ALL WORK COMPLETE / GXJ IDC XXXX
22877 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-03-11 09:58 | 2018-03-11 11:22 | 1 | 84 | 4984511 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pull into/ ISO 38831135000035/ COD 1
22878 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-03-07 16:17 | 2014-03-07 16:59 | 2 | 42 | 4459951 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR VER/CRB
22879 | South Williamson | 3200302 | BELFRY | TOLER | 2013-07-10 14:32 | 2013-07-10 15:00 | 3 | 28 | 4497221 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY LEG CONNECTION AT THE TRANSFORMER.//COD 3// VER/DBM IDC XXXX
22880 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-05-08 15:08 | 2012-05-08 15:50 | 2 | 42 | 4761271 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 2T FUSE BROKE BEEN OFF 10;30 AM//COD 2// VER/DBM IDC XXXX
22881 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-05-06 10:26 | 2012-05-06 11:50 | 1 | 84 | 4752471 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTOR ON XFMR SECONDARY RISER ///VER/CRB L/3 CRB IDC XXXX
22882 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-06-10 15:19 | 2017-06-10 16:43 | 1 | 84 | 4929351 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE . WILL REPLACE. COMPLTED POWER IS RESTORED./ ISO 38831148000276/ COD 1/ VER/BOW
22883 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-05-21 09:21 | 2015-05-21 10:45 | 1 | 84 | 4451951 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..CHGING. COD-1 ISO TF 38830900000024 VER/HFP L3/HFP
22884 | Hazard | 3309301 | VICCO | REDFOX | 2014-06-11 20:00 | 2014-06-11 20:42 | 2 | 42 | 4065691 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 CUTOUT DOOR BURNED OUT NEEDS REPLACED RELEASED BY CREW 074R01 CAN CLOSE POWER RESTROED AT 2042 MWL VER/HFP L3/HFP
22885 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2020-07-30 19:51 | 2020-07-30 21:15 | 1 | 84 | 4258801 | 84 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | customer had bad connection @ weatherhead..repiars made...
22886 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-07-11 12:11 | 2014-07-11 13:35 | 1 | 84 | 4229511 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE FUSED UP EVERYTHING OK COD1// VER/ ADH
22887 | Paintsville | 3401802 | INDEX | HOSPITAL | 2022-10-20 07:21 | 2022-10-20 08:45 | 1 | 84 | 4045981 | 84 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse melted out, changing.
22888 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-11-02 11:46 | 2015-11-02 13:09 | 1 | 83 | 4403191 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN SERVICE DROP , MADE REPAIRS RESTORED POWER AT 13:09.. VER/CRB
22889 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-02-10 18:22 | 2015-02-10 19:45 | 1 | 83 | 4006561 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED FUSE/ ISO 38830244000061/ COD 1/ VER/BOW L3/DKGXXXX
22890 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-12-11 14:07 | 2018-12-11 15:30 | 1 | 83 | 4553381 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broke fuse L3/HFP
22891 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2020-10-14 09:37 | 2020-10-14 11:00 | 1 | 83 | 4554471 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connetin @ weatherhead. repaired / restored
22892 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-01-11 13:37 | 2019-01-11 15:00 | 1 | 83 | 4659751 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot connection fail,1 customer L3/HFP
22893 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-10-06 18:37 | 2014-10-06 20:00 | 1 | 83 | 4559981 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT . FUSE BROKE . CLOSED XFMR FUSE @ 20:00// ISO 37830177B10539// COD 1// VER/BOW
22894 | South Williamson | 3411401 | DEWEY | INEZ | 2015-08-31 21:37 | 2015-08-31 23:00 | 1 | 83 | 4186711 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SEVONDARY RISER LOOSE IN TRANSFORMER LUG REPLACED LUG VOLTAGE TESTED GOOD VER/CRB
22895 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-11-26 18:17 | 2019-11-26 19:40 | 1 | 83 | 4070981 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired hot tap/ Hot Tap burnt off/ ISO 38830198000008/ COD 1
22896 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-02-06 23:05 | 2020-02-07 00:28 | 1 | 83 | 4372871 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000801/gaj/2309/all out contacted customer to check breakers inside & outside, cannot reset breaker disp 3327 J Moreland/no crew required failed 6t fuse
22897 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-09-28 18:45 | 2016-09-28 20:08 | 1 | 83 | 4938621 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPLACED BAD CONNETION @ ENTRANCE VER/HFP L3/HFP
22898 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-05-05 20:47 | 2014-05-05 22:10 | 1 | 83 | 4666341 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-232 BAD CUTOUT AND LA CHGED
22899 | Hazard | 3309301 | VICCO | REDFOX | 2010-12-14 16:18 | 2010-12-14 17:41 | 1 | 83 | 50105-1 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FROZE OUT ON XFMR POLE // VER/DBM IDC XXXX
22900 | South Williamson | 3411401 | DEWEY | INEZ | 2019-09-12 18:19 | 2019-09-12 19:42 | 1 | 83 | 4011271 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | insulaink melted and burned neutral into on service drop//repairs made//restored at 19:42//complete//em
22901 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-02-11 06:48 | 2011-02-11 08:11 | 1 | 83 | 56075-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIUMITING FUSE BAD CHANGING FUSE 0759 CHANGED FUSE ALL POWER RESTORED AT 0811 CLOSE TICKET VER/KEP IDC XXXX
22902 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2016-06-03 09:15 | 2016-06-03 10:38 | 1 | 83 | 4291151 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-6132 BAD METER ALSO CHGED OLD CUTOUT VER/CRB
22903 | Hazard | 3303902 | LESLIE | WOOTON | 2010-12-30 17:52 | 2010-12-30 19:15 | 1 | 83 | 57156-1 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED ALL OH SPLICES GOING TO CUSTOMERS HUOSE. VER/KEP L3/KEP IDC XXXX
22904 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-12-21 09:39 | 2021-12-21 11:02 | 1 | 83 | 4216551 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | made per tonya black appears to be broken cutout crew on site to make repairs replaced broke cutout on pole 38-217 transformer back in at 11:02 complete
22905 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-04-15 13:07 | 2008-04-15 14:30 | 1 | 83 | 51282-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.//3008702//VER/CRB IDC XXXX
22906 | Hazard | 3309302 | VICCO | JEFF | 2015-07-07 16:07 | 2015-07-07 17:30 | 1 | 83 | 4739021 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER/ ISO 37830275000158/ COD 1, WILL NEED 15 KVA, 7.2 KV, BUCKET TRUCK WILL REACH POLE RELEASED BY CREW 077S02// VER/ ADH
22907 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-06-02 12:27 | 2008-06-02 13:50 | 1 | 83 | 54509-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3000901// LOAD SIDE PRIMARY LEAD BROKE AT CUTOUT-REPAIRED RISER VER/ARN
22908 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-12-05 09:03 | 2016-12-05 10:26 | 1 | 83 | 4165401 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | CHANGED OUT METER VER/CRB L3/HFP XXXHFP
22909 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-02-21 14:10 | 2010-02-21 15:33 | 1 | 83 | 59526-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN ... REPLACED FUSE, ALL WORK COMPLETE / GXJ //COD 1// VER/DBM IDC XXXX
22910 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-07-07 12:37 | 2015-07-07 14:00 | 1 | 83 | 4737561 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD BROKE REFUSED XMF APR AT 1400 CLOSE TICKET, PLEASE SEND THIS 453-118 TO TECH POLE IS IN BAD SHAPE POLE SHOULD BE REPLACED/EMAILED TECH/ADH// VER/ ADH
22911 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2011-01-21 10:27 | 2011-01-21 11:50 | 1 | 83 | 63301-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR FUSE OUT ON POLE 1113-A-201....(XFMR NOT SHOWN ON MAP....ALSO ALL 3 PHASES OF LINE ARE DE-ENERGIZED PAST THIS POLE)....LOOKS LIKE BAD ARRESTER PROB BLEW XFMR FUSE....WILL RE-FUSE...//....CLEARED UP ARRESTER...RE-FUSED XFMR...POWER ON.....JRV...01/21/11 ENTERED MD...HFP COD-1 38821113A00201 VER/HFP L3/HFP IDCC PN181 XXXX
22912 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2019-02-15 13:29 | 2019-02-15 14:52 | 1 | 83 | 4797751 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 280-201 xfr cutout broke ,, Released by crew 078S05 Repairs made, ticket complete.
22913 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-03-29 20:23 | 2018-03-29 21:46 | 1 | 83 | 4152481 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARCOS SERVICER OUT @ 0815//cutout broke on pole 38830853D10133. talked to customer.. he has gate locked and will come unlock in the morning at nine oclock.. just feeds his barn and said would be fine til tomorrow..rn go #030071852 ing to work on ops side ops Released by crew 076H03
22914 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-09-07 16:01 | 2014-09-07 17:24 | 1 | 83 | 4478011 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | XFMR FUSE BLOWN // WILL REFUSE/// RISER WAS LOOSE FROM TOP OF XFMR PRI. BUSHING // REPAIRS MADE // POLE 37830071000149 NEEDS A GUY INSTALLED, LEANING BAD // SEND TO C. FREEMAN// ISO 37830071000149// COD 1//// VER/BOW
22915 | Whitesburg | 3401301 | FLEMING | NEON | 2013-07-14 09:17 | 2013-07-14 10:40 | 1 | 83 | 4521321 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE ON XFMR POLE VER/HFP L3/HFP IDC XXXX
22916 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-03-07 18:52 | 2017-03-07 20:15 | 1 | 83 | 4532321 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE-REPLACED -ALLGOOD-DS030717/ ISO 38830212000160/ COD 1/ VER/BOW
22917 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2020-07-13 09:35 | 2020-07-13 10:58 | 1 | 83 | 4158391 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced 6t
22918 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-05-24 01:29 | 2012-05-24 02:52 | 1 | 83 | 4825331 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY SERVICE CONNECTION BURNED INTO AT MAST,WILL REPLACE CONNECTION///////REPLACED CONNECTION,ALL OK ON OUR SIDE AFTERWARDS,THIS IS A 480V WATER PUMP SERVICE. CC 1 VER/SDB IDCC CNT4 XXXX
22919 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-03-12 16:42 | 2009-03-12 18:05 | 1 | 83 | 57611-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP SERVICE DROP BURNT DOWN L3/HFP IDC XXXX
22920 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-11-02 13:45 | 2013-11-02 15:08 | 1 | 83 | 4004181 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD NUET CONECTION AT WEATHER HEAD VER/CRB
22921 | Pikeville | 3421001 | BREAKS | CITY | 2010-06-15 11:37 | 2010-06-15 13:00 | 1 | 83 | 65059-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRIMARY METERING FUSE OUT ON POLE 244-109. REPLACED CUTOUT THAT WAS BURNED UP.
22922 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-05-29 08:10 | 2012-05-29 09:33 | 1 | 83 | 4839011 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE IS MELTED OUT, CHECKING TRANSFORMER REPLACED 10-T FUSE POWER RESTORED KWB VER/KEP IDC XXXX
22923 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2017-12-18 18:38 | 2017-12-18 20:01 | 1 | 83 | 4657141 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection @ service, 1 cust.
22924 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2009-12-02 13:17 | 2009-12-02 14:40 | 1 | 83 | 56593-1 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION BURNED INTO, MADE REPAIRS RESTORED POWER AT14:40 IDCC TON1535, CNT0 XXXX
22925 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-08-20 12:45 | 2019-08-20 14:08 | 1 | 83 | 4911871 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken c/o-allgood-ds082019
22926 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2009-07-13 19:57 | 2009-07-13 21:20 | 1 | 83 | 53404-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, CHECKING TROUBLE, LINE FUSE OUT AT POLE#992-D-58, BAD CUTOUT DOOR, TWO CUST OUT//ISO 38820992D00058//COD 1// VER/DBM IDC XXXX
22927 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-11-23 15:10 | 2022-11-23 16:33 | 1 | 83 | 4177031 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CLAMP BURNT OFF
22928 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-08-28 13:12 | 2021-08-28 14:35 | 1 | 83 | 4165731 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke on 760-208//replaced cutout//restored at 14:35//complete//em
22929 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2021-06-14 12:15 | 2021-06-14 13:38 | 1 | 83 | 4746341 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout was bad and fuse door had fell open. I replaced cutout and restored @ 13:38
22930 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-11-19 14:37 | 2013-11-19 16:00 | 1 | 83 | 4057381 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON SECONDARY. VER/CRB
22931 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-06-08 18:26 | 2021-06-08 19:49 | 1 | 83 | 4691561 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad neut. in sd. repaired
22932 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-02-04 09:00 | 2013-02-04 10:23 | 1 | 83 | 4789321 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR//COD 1// VER/DBM IDC XXXX
22933 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-10-19 01:16 | 2008-10-19 02:39 | 1 | 83 | 56947-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RESAGGED SERVICE DROP VER/ARN IDC XXXX
22934 | South Williamson | 3411401 | DEWEY | INEZ | 2013-05-27 19:02 | 2013-05-27 20:25 | 1 | 83 | 4188831 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE HAD PULLED OUT ON ONE OF HOT LEGS IN SERVICE AND WASNT GETTING GOOD CONNECTION//I REPAIRED SPLICE///COMPLETE//EM VER/HFP L3/HFP IDCC PN67 XXXX
22935 | Paintsville | 3410602 | E.PRESTON | LANCER | 2018-09-24 16:55 | 2018-09-24 18:18 | 1 | 83 | 4151711 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Released by crew 079H03--- FUSE LINK BROKEN AT BOTTOM OF BARRELL. NOT BLOWN. OLD C/O. REFUSED/RESTORED.
22936 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-04-06 13:37 | 2014-04-06 15:00 | 1 | 83 | 4579631 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON 618-17 APR AT 1500 CLOSE TICKET RELEASED BY CREW 078S11 VER/ARN
22937 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-03-10 18:55 | 2016-03-10 20:18 | 1 | 83 | 4835731 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILLL REPLACE BAD CUTOUT. CUT OUT CHANGED & POWER RESTORED @ 20:18 VER/KEP
22938 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2014-02-08 09:37 | 2014-02-08 11:00 | 1 | 83 | 4367611 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | HAD C PHASE FUSE OUT ON TRANSFORMER BANK, REFUSE AND POWER IS RESTORED AT THIS LOC AT 1100, BAD FUSE LINK VER/SEF
22939 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2013-02-10 17:07 | 2013-02-10 18:30 | 1 | 83 | 4806861 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP NEUTRAL BROKE AT SPLICE. REPLACED SPLICE AND ADDED SLAKE TO SERVICE DROP. POWER RESTORED AT 18:30.// VER/DBM IDC XXXX
22940 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-11-07 10:52 | 2010-11-07 12:15 | 1 | 83 | 53679-1 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER BAD CONNECTION AT XFMR... MADE REPAIRS RESTORED POWER AT 12:15, ALSO CUSTOMERS SERVICE IS OFF XFMR 424-149//MADE A MD//VER/CRB IDC XXXX
22941 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-12-12 04:07 | 2013-12-12 05:30 | 1 | 83 | 4155351 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. VER/TOM L3/TOM
22942 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-10-19 18:57 | 2015-10-19 20:20 | 1 | 83 | 4362121 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR, MADE REPAIRS RESTORED POWER AT 20:20../ ISO 37830447000043/ COD 1/ VER/BOW
22943 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-02-08 09:58 | 2010-02-08 11:21 | 1 | 83 | 53144-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SURGE ARRESTOR HAS BURNED INTO,WILL REPAIR/////////MADE NECESSARY REPAIRS AND RESTORED,ALL OK AFTERWARDS IDC XXXX
22944 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-05-24 18:42 | 2021-05-24 20:05 | 1 | 83 | 4617261 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Splice had went bad in service drop and burnt 1 hot leg and neutral n2. This was #4 drop with multiple splices so we removed and upgraded to #2 service drop. Restored @20:05//cod 1
22945 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-05-09 10:32 | 2021-05-09 11:55 | 1 | 83 | 4552871 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | current limiting fuse went bad at xfmr. repairs made power restored at 1155
22946 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-08-27 13:27 | 2009-08-27 14:50 | 1 | 83 | 53580-1 | 83 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | 3007905//LEAD BURNT IN TWO//COD 1// VER/DBM IDC XXXX
22947 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-12-25 12:22 | 2009-12-25 13:45 | 1 | 83 | 52549-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1147-714 6T MELTED OUT
22948 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-05-28 15:22 | 2016-05-28 16:45 | 1 | 83 | 4268541 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ATTEMPTED TO CALL CUSTOMER/ REPLACED BROKEN CUT-OUT RESTORED POWER AT 16:45 PLEASE CLOSE TICKET T CANTRELL/ ISO 38830234000060/ COD 1/ VER/BOW
22949 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-05-26 07:00 | 2011-05-26 08:23 | 1 | 83 | 4171221 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CRACKED 19.9 CUTOUT CHANGED CUTOUT ALL POWER RESTORED AT 0823 CLOSE TICKET//COD 1// VER/DBM
22950 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-01-07 15:07 | 2017-01-07 16:30 | 1 | 83 | 4275731 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACE CONNECTIONS 38830181C00005 VER/AWD L3/HFP XXXHFP
22951 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-11-30 09:10 | 2009-11-30 10:33 | 1 | 83 | 51105-1 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BURNT OPEN AT SECONDARY POLE. ONLY ONE CUSTOMER AFFECTED. BAD HOT CONNECTION WAS CAUSE. REPAIRED AND RE-SQUEEZED ALL CONNECTIONS. SH IDC XXXX
22952 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-07-24 13:47 | 2011-07-24 15:10 | 1 | 83 | 4608501 | 83 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | APPEARS NEUTRAL OF SERV INTO,WILL REPAIR//////UPDT-WILL CHANGE SD OUT////REPLACED 4/3 SERV W 2/3.POSSIBLE DAMAGES.SPLICE HEATED UP & CAUSED INSULATION FAILURE// VER/DBM IDC XXXX
22953 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-10-13 11:38 | 2019-10-13 13:00 | 1 | 82 | 4136321 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
22954 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-01-06 14:24 | 2014-01-06 15:05 | 2 | 41 | 4238341 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITTING FUSE APR AT 1505 CLOSE TICKET. DEW VER/KEP IDCC CDC96, PN161 XXXX
22955 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-12-19 15:40 | 2021-12-19 16:21 | 2 | 41 | 4212461 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned up change cutout
22956 | Pikeville | 3409502 | BURDINE | LEVISA | 2008-02-14 01:23 | 2008-02-14 02:45 | 1 | 82 | 63066-1 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED A BAD CONNECTION ON ONE OF THE HOT LEGS OF THE SECONDARY AT THE TRANSFORMER. VER/ARN IDC XXXX
22957 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-04-08 14:38 | 2012-04-08 16:00 | 1 | 82 | 4655191 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE SERVICE PHASE WIRES AT THE WEATHERHEAD. ONLY ONE CUSTOMER AFFECTED. VER/HFP L3/HFP IDC XXXX
22958 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2017-04-27 17:28 | 2017-04-27 18:50 | 1 | 82 | 4688861 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE VER/CRB L3/HFP XXXHFP
22959 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2022-05-19 23:58 | 2022-05-20 01:20 | 1 | 82 | 4914741 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burnt down through tree in back yard. Repaired
22960 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-01-17 16:56 | 2015-01-17 18:18 | 1 | 82 | 4941881 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED OFF WERE TRANSFORMER LEAD AND UNDERGROUND SERVICE VER/CRB L3/HFP XXX
22961 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-10-11 13:27 | 2016-10-11 14:08 | 2 | 41 | 4985581 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED INTO ON POLE 37820001000210, REFUSED @1408. VER/HFP L3/HFP
22962 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-08-07 06:55 | 2018-08-07 08:17 | 1 | 82 | 4916741 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap lead broken/FETR 0830/vem/repairs madeand power restored to all cust 0817/please close ticket/thanks/vem
22963 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-02-05 21:34 | 2020-02-05 22:15 | 2 | 41 | 4366391 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3120101/gaj/1911/all out disp 3543 G Ratliffwill eed 1 a lineman ,cutout & arrestor this is 19.9 will have to pull tap feeding 1100000162.i will keep times,pulled tap off @ 21:34 all back on @ 22;15
22964 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2010-08-09 14:24 | 2010-08-09 15:46 | 1 | 82 | 51602-1 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | FOUND A 4/3 SERVICE DROP WITH FIVE SPLICES IN IT, SO I REPLACED SERVICE DROP WITH NEW SERVICE, 2/3 SERVICE DROP NOW, EVERYTHING IS OK HERE NOW VER/HFP L3/HFP IDC XXXX
22965 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-03-28 11:18 | 2014-03-28 12:40 | 1 | 82 | 4531241 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON TRANSF POLE BAD == REPAIRED === POWER OK VER/CRB
22966 | Paintsville | 3409302 | KENWOOD | AUXIER | 2009-10-17 19:15 | 2009-10-17 20:37 | 1 | 82 | 54266-1 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED XFMR. SH //COD 1// VER/DBM IDC XXXX
22967 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-07-25 15:47 | 2017-07-25 16:28 | 2 | 41 | 4178741 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUES FAILED ON 168-30 RESTORED POWER AT 16;30 37830168000030 VER/AWD L3/HFP HFPC CCU FEC57 FP
22968 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-11-16 02:25 | 2022-11-16 03:47 | 1 | 82 | 4144871 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | crew required 40/5 pole broken no outage at time/need tech also //LF on 197-30 opened @ 0225 to transfer broke pole/ repairs made/ LF on 197-30 back in @ 0347/ please close ticket/ MLH//iso 38830197000030// cod 1 //
22969 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-04-12 14:33 | 2010-04-12 15:55 | 1 | 82 | 62404-1 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | TRANSFORMER LEAKING OIL AND PRIMARY METERING BAD ON POLE 387-633//BYPASSED PRIMARY METERING UNTIL CAN BE REPLACED//CLEANUP CREW DISPATCHED TO TAKE CARE OF THE OIL //AED CREATED// VER/DBM IDCC PN53 XXXX
22970 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-05-01 13:23 | 2008-05-01 14:45 | 1 | 82 | 56000-1 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON UG RISER POLE.//3409301 REPLACED CUTOUT AND RE-FUSED. PLEASE SEND TO MAPPING TO ADD FUSE SIZE(25T) TO UG RISER POLE 38830786B00342. THANKS, SH//MADE MAP DISCREPENCY//VER/CRB IDC XXXX
22971 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-07-04 18:54 | 2019-07-04 20:16 | 1 | 82 | 4655021 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | A phase trans. fuse open on bank pole 95-190, fuse had melted refused @2016.//cod 1
22972 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2022-05-02 08:53 | 2022-05-02 10:15 | 1 | 82 | 4822521 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer restored
22973 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2012-06-01 04:59 | 2012-06-01 06:21 | 1 | 82 | 4858351 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT DOOR FAILED TRIED TO CARRY LOAD AND BURNT INTO POWER RESTORED KWB COD-1 ISO TF 38830042000016 VER/HFP L3/HFP IDC XXXX
22974 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-07-19 09:03 | 2020-07-19 10:25 | 1 | 82 | 4182041 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | porcelain cut out broke. repairs made power restored at 1025
22975 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-02-05 18:44 | 2015-02-05 19:25 | 2 | 41 | 4994321 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING LINE FUSE TO REPAIR BROKEN 162-28 TO SAFELY REPAIR BROKEN CUT OUT/COD 13/OPENED LINE FUSE 162-28 19:00 CLOSED 19:25 CHGED TWO CUTOUTS LINE FUSE AND TRANS FUSE2+11/1844 ORIGINAL 2 CUS// VER/ ADH L3/HFP XXX
22976 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-07-06 21:18 | 2021-07-06 22:40 | 1 | 82 | 4863051 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 374-D-92.. replaced cutout repairs made. power restored
22977 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-07-26 13:48 | 2016-07-26 15:10 | 1 | 82 | 4682751 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 92-742 6T ME FUSE LINK BROKE REPAIRED/ ISO 38830092B00742/ COD 1/ VER/BOW
22978 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-01-03 07:08 | 2012-01-03 08:30 | 1 | 82 | 4227801 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS NOT BLOWN, IT HAD PULLED LOOSE. REFUSED XMF APR AT 0830 CLOSE TICKET//COD 1// VER/DBM IDC XXXX
22979 | Hazard | 3310502 | HADDIX | CANOE | 2015-01-05 13:57 | 2015-01-05 14:38 | 2 | 41 | 4908071 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CHANGING INSULATOR 37830052000013/ ISO 37830051000017/ COD 2 OPEN AT 1357 CLOSED AT 1438/ VER/BOW L3/DKGXXXX
22980 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-11-06 15:39 | 2020-11-06 16:20 | 2 | 41 | 4649241 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @166-125, checking. Fuse had melted out, refused @1620.
22981 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2012-02-25 11:59 | 2012-02-25 12:40 | 2 | 41 | 4504211 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP ON 3 PHASE BANK COD-2 ISO PO @ 38830020C35112 VER/HFP L3/HFP IDC XXXX
22982 | Hazard | 3310502 | HADDIX | CANOE | 2012-02-03 11:53 | 2012-02-03 13:15 | 1 | 82 | 4318231 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHANGE CUTOUT VER/KEP IDC XXXX
22983 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-10-01 17:43 | 2020-10-01 19:05 | 1 | 82 | 4518731 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | xfmr lead has come out. will make repairs
22984 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-07-15 23:43 | 2017-07-16 01:05 | 1 | 82 | 4129901 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE. REPLACED AND RESTORED @ 1:05. SH
22985 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-07-07 14:32 | 2018-07-07 15:54 | 1 | 82 | 4748621 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout,,changing
22986 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2015-05-03 22:59 | 2015-05-03 23:40 | 2 | 41 | 4386591 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV CO DOOR, RESTORED VER/ARN
22987 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-01-23 14:24 | 2017-01-23 15:46 | 1 | 82 | 4322921 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TRFM AT 1515 TO REPAIRE BROKEN NEUTRAL IN SERVICE DROP, APR AT 1546 CLOSE TICKET///DWEST 38830598000018 VER/AWD L3/HFP XXXHFP
22988 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-03-20 22:10 | 2015-03-20 22:51 | 2 | 41 | 4215111 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE OF THE WIRES ON OPEN WIRE SECONDARY BROKE DUE TO BAD PLACE IN WIRE///MADE REPAIRS///OPENED XFMER FUSE ON POLE 737-333 @ 22:10 AND CLOSED @ 22:51///COMPLETE BR/COD 2// VER/ ADH L3/DKGXXXX
22989 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-03-21 16:39 | 2022-03-21 17:20 | 2 | 41 | 4654731 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR GOING TO NEED 25KVA 19.9 XFMR.opened tap @16:39,closed @ 17:20 Released by crew 077H13
22990 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2017-07-04 17:00 | 2017-07-04 18:22 | 1 | 82 | 4072161 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER HAD POWER UNTIL I OPENED XFMR CUTOUT @ 17:00 TO INSPECT. FOUND CUTOUT TO BE CRACKED SO I LEFT OFF LINE UNTIL ADDITIONAL HEL ARRIVES WITH NEW 19.9 CUTOUT. ADVISED CUSTOMER WE WILL BE REPAIRING IN A COUPLE HOURS. REPLACED CUTOUT AND RESTORED @ 18:22. SH VER/CRB
22991 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-04-03 09:48 | 2020-04-03 11:10 | 1 | 82 | 4557071 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bPHASE TRANS FUSE BLOWN DUE TO BAD ARRESTOR.REPLACED ARRESTOR.RESTORED POWER AT 11:10
22992 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2008-12-09 17:34 | 2008-12-09 18:15 | 2 | 41 | 55870-1 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117602//S/C CUTOUT DOOR BURNT UP//COD 2 VER/KEP L3/KEP IDC XXXX
22993 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-12-18 16:58 | 2016-12-18 18:20 | 1 | 82 | 4217611 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD CUTOUT ON POLE#169-218 RESTORED SERVICE @18:20/ ISO 37820169000218/ COD 1/ VER/BOW
22994 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-11-22 11:54 | 2010-11-22 12:35 | 2 | 41 | 58678-1 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RESQUESED ONE HOT LEG BAD CONN//VER/CRB IDC XXXX
22995 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-10-15 17:46 | 2022-10-15 19:08 | 1 | 82 | 4031561 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | transformer riser burned in the clear on pole 746A-75.made repairs and got cust back in service at 19:08
22996 | Hazard | 3302704 | HAZARD | KENMONT | 2015-05-27 12:39 | 2015-05-27 13:20 | 2 | 41 | 4472061 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE AT POLE , CALLED RUSSEL TO COME AND HELP ME.OPENED XFMR AT 12:39 CLOSED XFMR AT 13:20//// NEUTRAL WIRE BROKE ABOUT 6 INCHES PASS A SPLICE, SPLICED NEUTRAL AND REMADE CONNECTIONS. POWER RESTORED. SEND THIS TO CLAIMS DEPT. THERE WERE DAMAGES VER/CRB
22997 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2014-05-28 10:46 | 2014-05-28 12:08 | 1 | 82 | 4942901 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SER. DROP LAY ON ROOF RESAG POWER RESTORED 1 CUST VER/KEP
22998 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-01-05 04:45 | 2013-01-05 06:07 | 1 | 82 | 4569911 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE, I REFUSED XFMR VER/TOM L3/TOM IDCC PN124, CNT2 XXXX
22999 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-11-11 13:47 | 2020-11-11 15:09 | 1 | 82 | 4662581 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had line fuse out on pole37830005000003 and bad cutout on pole37830005000180
23000 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2018-11-06 10:58 | 2018-11-06 12:20 | 1 | 82 | 4371521 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9 CUTOUT L3/HFP
23001 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-03-01 22:18 | 2016-03-01 23:40 | 1 | 82 | 4798311 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 818-219/ 2340/ ISO 38820818A00219/ COD 1BROKE CUTOUT ON POLE 818-219//HAVE CUTOUT REPLACED//RESTORED A 23:40//COMPLETE//EM/ VER/BOW
23002 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-11-13 19:43 | 2019-11-13 20:24 | 2 | 41 | 4032041 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Customer called back-still part out. Shane on site. ¦¦ replaced connection on pole
23003 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2021-08-07 12:59 | 2021-08-07 14:21 | 1 | 82 | 4015151 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | changed connections on pole/all working good. pls close. tre
23004 | South Williamson | 3411401 | DEWEY | INEZ | 2008-01-23 03:55 | 2008-01-23 05:17 | 1 | 82 | 59046-1 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BAD ON POLE 791-B-135/VER/CRB IDC XXXX
23005 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-09-23 10:48 | 2009-09-23 12:10 | 1 | 82 | 60355-1 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP SMALL TRUCK ON WAY TO TAKE ME UP ON MTN, XFMR FUSE OUT, POWER RESTORED, FUSE BROKE, NO PROBLEM L3/HFP IDC XXXX
23006 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-09-22 18:38 | 2022-09-22 20:00 | 1 | 82 | 4911341 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke 19.9 cutout
23007 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-05-10 10:47 | 2014-05-10 11:28 | 2 | 41 | 4680861 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP. I AM GOING TO TRY AND REPLACE DOOR. I CHANGED CUTOUT DOOR AND REFUSED TRANSFORMER AND IT STAYED IN VER/CRB
23008 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-03-07 18:36 | 2009-03-07 19:58 | 1 | 82 | 56110-1 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN, FIXED//3103101//VER/CRB IDC XXXX
23009 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-09-19 15:06 | 2018-09-19 16:28 | 1 | 82 | 4131711 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Opening switches 37830555C00136 to replace 37830579B00148 primary metering/ ISO 37830555C00136/ COD 1 - opened at 1508 and closed at 1628
23010 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2022-09-05 13:39 | 2022-09-05 15:01 | 1 | 82 | 4840541 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | FAULT POLE 38820966D00654//ENROUTE TO GET CREW//GOING TO TRY AND ISOLATE AT SWITCHES 38820966D00027 THIS WILL OUT 3- 3 PHASE CUSTOMERS//opened at 1455 at pole 38820966D00027 // closed at 2330 //
23011 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-05-05 16:13 | 2012-05-05 17:35 | 1 | 82 | 4750891 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED CREW BAD 15 KVA TRANSFORMER--SMALL OIL LEAK NEED TRANSFORMER BAG--CAN USE MATERIAL HANDLER RELEASED BY CREW 078S07 ///VER/CRB L/3 CRB IDC XXXX
23012 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-10-29 19:48 | 2016-10-29 21:10 | 1 | 82 | 4062661 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKE. REPLACED CUTOUT AND RESTORED @ 21:10. SH VER/TOM L3/TOM
23013 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2016-02-14 14:53 | 2016-02-14 16:15 | 1 | 82 | 4696001 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED-RED FROOZE OUT I REPLACED IT VER/TOM L3/TOM
23014 | Pikeville | 3413401 | GARRETT | GARRETT | 2012-04-20 18:33 | 2012-04-20 19:55 | 1 | 82 | 4691291 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | REPLACED 2 CUOUTS, ONE BROKEN APART AND ONE CRACKED , ALL WORK COMPLETE / GXJ COD-1 ISO TF 37830065D00584 VER/HFP L3/HFP IDC XXXX
23015 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-10-04 23:38 | 2011-10-05 01:00 | 1 | 82 | 4947881 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN//CUTOUT DOOR BURNED UP// REPLACED DOOR// POWER IS RESTORED AT 0100. CC = 1. VER/SDB IDC XXXX
23016 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-05-17 23:51 | 2022-05-18 01:13 | 1 | 82 | 4905231 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on 1052-B-324, replaced cutout, customer restored
23017 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-05-09 09:13 | 2011-05-09 10:35 | 1 | 82 | 4021341 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE//VER/CRB IDC XXXX
23018 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-12-21 09:39 | 2013-12-21 10:20 | 2 | 41 | 4180801 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-306 BAD CUTOUT 6T FUSE//COD 2// VER/DBM L3/HFP
23019 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2008-06-02 13:48 | 2008-06-02 15:10 | 1 | 82 | 54558-1 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3002105// BROKEN HOT TAP RISER/REPAIRED RISER VER/ARN
23020 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2018-02-08 08:18 | 2018-02-08 09:40 | 1 | 82 | 4816161 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Insulink connection failed in secondary to 38830858A20450. Have to let sec down to repair. Repaired and restored @ 9:40. sh
23021 | Pikeville | 3402002 | KEYSER | STONECOAL | 2020-02-17 14:54 | 2020-02-17 15:35 | 2 | 41 | 4413031 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Neutral burnt into on secondary @trans. 1-43, will have to open to make repairs, will keep track of times. Trans. cutout is also busted. Opened up @1454, made repairs and closed in @1535. was only an open neutral until xfer opened L3/HFP
23022 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-09-07 19:23 | 2008-09-07 20:45 | 1 | 82 | 60224-1 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308503//HOT CONECTION BAD ON TRANSF POLE == REPAIRED == POWER OK VER/LDA IDC XXXX
23023 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-05-11 16:53 | 2010-05-11 18:15 | 1 | 82 | 59685-1 | 82 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED == REFUSED == POWER OK COD-1 VER/HFP L3/HFP IDC XXXX
23024 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2011-03-23 10:28 | 2011-03-23 11:50 | 1 | 82 | 56997-1 | 82 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON THE POLE ON THE SERVICE DROP ONLY ONE CUSTOMER AFFECTED.// VER/DBM IDC XXXX
23025 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-07-29 12:54 | 2012-07-29 14:15 | 1 | 81 | 4860871 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SERVICE VER/KEP
23026 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-05-09 16:19 | 2019-05-09 17:40 | 1 | 81 | 4246081 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutral was broke next to the xfmr pole , I opened the xfmr and repaired the neutral. open xfmr at 17: 15 and closed back at 17:40
23027 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2020-07-05 13:09 | 2020-07-05 14:30 | 1 | 81 | 4111951 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Made temp repaires to dn guy at 38830524A20352 please send copy to Vernon M to have crew make proper repaires. apr at 1430 close ticket//SENT TO LINE DEPT
23028 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-01-26 19:39 | 2015-01-26 21:00 | 1 | 81 | 4966221 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK FROZE OUT AT WEATHERHEAD. ONLY AFFECTED ONE CUSTOMER. REPLACE CONNECTIONS AT WEATHERHEAD AND RESTORED @ 21:00. SH VER/CRB
23029 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-10-16 15:49 | 2016-10-16 17:10 | 1 | 81 | 4020881 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. REPLACED CUTOUT AND RESTORED @ 17:10. SH VER/AWD L3/HFP XXXHFP
23030 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2013-07-01 12:45 | 2013-07-01 14:06 | 1 | 81 | 4437131 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT..WILL CHECK & RE-FUSE.//..FUSE LINK WAS JUST BROKEN WHERE IT COMES OUT OF BOTTOM OF CUTIUT DOOR..REPLACED LINK & RE-FUSED..JRV.07/01/13 COD-1 ISO TF 38820917B00139 VER/HFP L3/HFP IDC XXXX
23031 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-12-29 03:04 | 2013-12-29 04:25 | 1 | 81 | 4208111 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT -OUT BROKE WILL REPLACE. REPLACED CUT-OUT RESTORED SERVICE @04:25 ONLY HAD 1 CUSTOMER OUT //VER/GAH L3/HFP
23032 | Whitesburg | 3401301 | FLEMING | NEON | 2008-03-31 10:18 | 2008-03-31 11:39 | 1 | 81 | 62347-1 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3401301//REPLACED CONNECTIONS ON POLE//VER/CRB IDC XXXX
23033 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-11-26 07:34 | 2022-11-26 08:55 | 1 | 81 | 4181281 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | cutout gate was burned up, replaced gate . power restored @ 08:55
23034 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-03-17 08:39 | 2020-03-17 10:00 | 1 | 81 | 4484521 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse
23035 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-02-12 08:58 | 2012-02-12 10:19 | 1 | 81 | 4341271 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | HAD SERVIN PUSH OUT IDC XXXX
23036 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-06-12 21:10 | 2020-06-12 21:37 | 3 | 27 | 4011981 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | conductor 4 ft off of the ground per customer// customers house knob pulled out of pole, replaced knob and put service up. transformer opened at 21:10 closed at 21:37 // cod 3 //
23037 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-03-09 11:15 | 2018-03-09 12:36 | 1 | 81 | 4981571 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | insalink burned out, recconnected/ ISO 38830070A10045/ COD 1
23038 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-05-13 08:19 | 2016-05-13 09:40 | 1 | 81 | 4212011 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON XFMR POLE 783-164. REPLACED AND RESTORED @ 9:40. SH VER/CRB
23039 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-04-15 19:49 | 2015-04-15 21:10 | 1 | 81 | 4323731 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT DOOR RESTORED/ ISO 38830116B00648/ COD 1
23040 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2021-01-06 17:09 | 2021-01-06 18:30 | 1 | 81 | 4852801 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed on 738-217 in difficult location. Replaced cutout and restored @ 18:30. sh
23041 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-03-04 19:27 | 2022-03-04 20:48 | 1 | 81 | 4567991 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke Trans cutout on pole 165-193,Will be making repairs.Restored @ 20:48.
23042 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-08-28 08:00 | 2014-08-28 09:21 | 1 | 81 | 4431701 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-4011 BAD CUTOUT NEED 3-CUTOUTS LINE CREW TRUCK TO POLE RELEASED BY CREW 078S08,,CUTOUTS REPLACED, ALL POWER RESTORED VER/SEF
23043 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2014-12-26 09:07 | 2014-12-26 10:28 | 1 | 81 | 4885381 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE IN SERVICE, I REPLACED IT VER/CRB
23044 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2013-06-07 09:06 | 2013-06-07 10:27 | 1 | 81 | 4234831 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE VER/KEP IDC XXXX
23045 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-01-17 16:49 | 2010-01-17 18:10 | 1 | 81 | 55598-1 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER ONE CUSTOMER. BAD CONNECTION IN THE SERVICE TO THIS ONE HOUSE. VER/TOM L3/TOM IDCC CNT2 XXXX
23046 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-12-11 10:45 | 2015-12-11 12:06 | 1 | 81 | 4525671 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DOOR ON CUTOUT HAD BEEN OPEN FOR SEVERAL MONTHS AND WAS CLOSED IN YEASTERDAY ON A RECONNECT, LOOKS LIKE FUSE HAD GOTTEN WET AND BURNT OUT. APR AT 1206 CLOSE TICKET COD-1 ISO TF 38830501000210 VER/HFP L3/HFP
23047 | Paintsville | 3410602 | E.PRESTON | LANCER | 2019-05-30 20:34 | 2019-05-30 21:55 | 1 | 81 | 4392731 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout door has burned up I will make repairs/// Replaced door xfmr checked good power restore @ 21:55
23048 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-05-02 07:58 | 2016-05-02 09:19 | 1 | 81 | 4157161 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 375-16, REPLACED CUTOUT RESTORED POWER AT 09:19..37830375A00016 VER/AWD
23049 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-03-05 07:14 | 2020-03-05 08:35 | 1 | 81 | 4453231 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed and burned both hot conductors in two in service. oo ONE CUST AFFECTED oo Repaired & restored @ 8:35. sh
23050 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-11-01 19:49 | 2020-11-01 21:10 | 1 | 81 | 4623471 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired neutral conducter,,at weather head,,complete
23051 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-06-15 13:53 | 2017-06-15 15:14 | 1 | 81 | 4973481 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD EPOXILATOR ON POLE 122-126. PLEASE SEND TO DAVE SAMMONS FOR CREW TO WORK IN THE MORNING. OPS ORDER #039518290/ CUSTOMER OK WITH LEAVING OFF UNTIL TOMORROW/ ISO 37820122000108/ COD 1/ VER/BOW
23052 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-12-09 13:24 | 2019-12-09 14:45 | 1 | 81 | 4138491 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout, manuel pole, calling for help
23053 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-08-11 09:27 | 2020-08-11 10:48 | 1 | 81 | 4309311 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out, broken fuse, power restored
23054 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2011-02-08 09:19 | 2011-02-08 10:40 | 1 | 81 | 55218-1 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 6T FUSE BROKEN. FUSED UP EVERYTHING OK. // COD-1 ISO TF 37830259000054 VER/HFP L3/HFP IDC XXXX
23055 | Hazard | 3303902 | LESLIE | WOOTON | 2022-01-24 12:54 | 2022-01-24 14:15 | 1 | 81 | 4400821 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
23056 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2021-09-17 14:56 | 2021-09-17 16:17 | 1 | 81 | 4252441 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Opened txmf at 1603 to repaire riser, apr at 1617 close ticket LR- Part out came in at 14:56 on 9/17/21.
23057 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-03-08 11:03 | 2015-03-08 12:24 | 1 | 81 | 4166691 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 147-71 . REPLACED// VER/ ADH
23058 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-10-07 18:58 | 2013-10-07 19:25 | 3 | 27 | H4919901 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER OPENED LINE FUSES TO MAKE REPAIRS TO A STYRUP THAT IS BURNT OFF /// RELATED TO 4919901 COMMENTS FROM THAT ORDER STIRRUP BURNT IN TWO ALLOWING PHASE B LINE FUSE RISER TO FALL AGAINST PHASE A RISER. GOING TO PAINTSVILLE OFFICE TO GET A 556 MCM STIRRUP TO MAKE REPAIRS. REPLACED STIRRUP AND CUTOUT. OPENED THREE FUSES ON 785-967 @ 18:58 AND CLOSED @ 19:25. SH COD-3 ISO LF 38830785A40967 VER/HFP L3/HFP IDC XXXX
23059 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-09-08 21:02 | 2015-09-08 22:23 | 1 | 81 | 4215661 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNT INTO , MADE REPAIRS RESTORED POWER AT 22:23../ ISO 37830352C00032/ COD 1/ VER/BOW
23060 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-12-10 18:14 | 2013-12-10 19:35 | 1 | 81 | 4149461 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BURNT INTO IN SERVICE GOING TO REPAIR. REPAIRED SERVICE GOOD VOLTAGE 120/120/240// VER/DBM L3/HFP
23061 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-10-30 22:29 | 2008-10-30 23:50 | 1 | 81 | 60998-1 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3404302//, ON SITE, BAD CONNECTION AT XFORMER, MAKING REPAIRS//VER/CRB IDCC MCCDL XXXX
23062 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-07-05 11:53 | 2013-07-05 12:20 | 3 | 27 | 4469771 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XMF FUSE OPEN, FUSE APPEARED TO HAVE JUST PULLED LOOSE. APR AT 1220 CLOSE TICKET1220//COD 3// VER/DBM IDCC CCU XXXX
23063 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2022-10-13 13:44 | 2022-10-13 15:05 | 1 | 81 | 4023971 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken 7.2 c/o // repairs made and RESTORED @ 15:05
23064 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-11-30 13:37 | 2016-11-30 14:58 | 1 | 81 | 4150281 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 256-24, RESTORED POWER AT 14:58..VER/AWD L3/HFP XXXHFP
23065 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-03-26 15:27 | 2018-03-26 16:48 | 1 | 81 | 4119551 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Released by crew 074S07 replaced broken cutout on 1008-A-189 restored power at 16:48
23066 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2015-04-16 18:05 | 2015-04-16 19:26 | 1 | 81 | 4327351 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | X-FMR CUT-OUT BROKE ON POLE 420C-182. POWER RESTORED AT 19:26. 4/16/2015/ VER/BOW
23067 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-07-19 13:39 | 2017-07-19 15:00 | 1 | 81 | 4143231 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9/120/240 WILL REPLACE IN THE MORNING. CREATED OPS ORDER 031505338. VER/CRB
23068 | South Williamson | 3200301 | BELFRY | BELFRY | 2015-01-14 17:40 | 2015-01-14 19:01 | 1 | 81 | 4936001 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY CONNECTIONS AT THE TRANSFORMER. I ALSO CHANGED THE METER OUT, THE METERBASE SEAL WAS CUT AND THE LAB SEAL IS GONE ON THE METER. ONLY ONE CUSTOMER WAS OFF./ ISO 38821014D00140/ COD 1/ VER/BOW
23069 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-09-18 11:44 | 2019-09-18 13:05 | 1 | 81 | 4033221 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Insalink pulled loos, repaired
23070 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-06-30 23:04 | 2015-06-30 23:31 | 3 | 27 | 4701981 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SAME AS 4700441
23071 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-04-17 19:07 | 2015-04-17 20:28 | 1 | 81 | 4330701 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SINGLE ALL OUT BROKEN FUSE LINK REPAIR POWER RESTORED 6-T KWB/ ISO 39831024B00212/ COD 1/ VER/BOW
23072 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-02-06 12:30 | 2018-02-06 13:51 | 1 | 81 | 4809271 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Crew reqd. cutout broke on pole 38830526000065. Service bucket may get to pole Released by crew 078H17 closed 1351
23073 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-11-03 12:44 | 2010-11-03 14:05 | 1 | 81 | 51324-1 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 478-1080 NEED CREW TO REPLACE,, CUTOUT IS IN HAZARDOUS PLACE AND BIG BUCKET NEEDED,,,POWER RESTORED VER/HFP L3/HFP IDC XXXX
23074 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-05-01 08:02 | 2012-05-01 09:23 | 1 | 81 | 4728121 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN ON 786-353// WILL CHANGE//MADE MDC//COD 1 ///VER/CRB L/3 CRB IDC XXXX
23075 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-01-27 09:52 | 2014-01-27 11:13 | 1 | 81 | 4316451 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | APPEARS TO BE A FROZEN-OUT SERVE-IN CONNECTOR,WILL REPAIR///////MADE NECESSARY REPAIRS.HOME IS VACANT AT PRESENT VER/HFP L3/HFP
23076 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-03-07 12:16 | 2015-03-07 13:37 | 1 | 81 | 4158601 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHER HEAD. REPLACED CONNECTION EVERYTHING OK// VER/ ADH
23077 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-06-20 10:35 | 2015-06-20 11:56 | 1 | 81 | 4616021 | 81 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION AT THE WEATHERHEAD. OPENED TRANSFORMERS AT 1142 CLOSED AT 1156.// VER/ ADH
23078 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-04-05 15:04 | 2012-04-05 16:25 | 1 | 81 | 4650561 | 81 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REMOVED LEAKING 50KVA CSP INSTALLED 25KVA & NEW CUTOUT & ARRESTOR ( FEEDING ONLY ONE HOUSE 320 AMP SERVICE & ONE STREET LIGHT)//COD 1// VER/DBM IDC XXXX
23079 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-09-02 09:25 | 2019-09-02 10:45 | 1 | 80 | 4972561 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse out, broke cutout, power restored
23080 | Hazard | 3310502 | HADDIX | CANOE | 2009-12-30 19:12 | 2009-12-30 20:32 | 1 | 80 | 50884-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | HOUSE KNOB BROKE AND ONE HOT WIRE IN TWO VER/KEP L3/KEP IDC XXXX
23081 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2021-11-11 18:49 | 2021-11-11 20:09 | 1 | 80 | 4080501 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required 15t inactive transformer
23082 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-04-12 14:25 | 2012-04-12 15:45 | 1 | 80 | 4669061 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT ON POLE 429-235. COD-1 ISO TF 38830429B00235 VER/HFP L3/HFP
23083 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2019-08-15 19:42 | 2019-08-15 21:02 | 1 | 80 | 4893321 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout servicer to make repairs LRM FETR 21:00 all pwr restored @ 21:02 please close ticket LRM L3/HFP
23084 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2012-10-14 11:10 | 2012-10-14 12:30 | 1 | 80 | 4138461 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1124-2079 BAD LA AND CUTOUT CHGED CUSTOMER CALLED FOR NEIGHBOR COD-1 ISO TF 39831124B12079 VER/HFP L3/HFP IDC XXXX
23085 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-08-23 16:04 | 2018-08-23 17:24 | 1 | 80 | 4994111 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad cutout, apr at 1724 close ticket
23086 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2020-04-21 14:12 | 2020-04-21 15:32 | 1 | 80 | 4728311 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connections at house. repaired
23087 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2008-12-10 08:52 | 2008-12-10 09:08 | 5 | 16 | 56043-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3309102// SERVICE CONNECTION IS BURNING OFF AT TRANSFORMER. CECIL SEXTON IS GOING TO SEND BIG BUCKET TO ME. POLE IS ACROSS CRK WHICH IS UP TOO BIG TO CROSS. OPENED TRANSFORMER AT 0852 AND CLOSED BACK AT 0908// VER/TOM L3/TOM IDC XXXX
23088 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2013-12-28 20:15 | 2013-12-28 20:31 | 5 | 16 | 4207411 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SEC BURNT INTO LINE CREW TO REPLACE RELEASED BY CREW 078S05 OFF 2015 ON 2031 COD-5 ISO TF 38830206A10117 VER/HFP L3/HFP
23089 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-04-26 19:04 | 2020-04-26 20:24 | 1 | 80 | 4754571 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burned down, wire up
23090 | Hazard | 3310502 | HADDIX | CANOE | 2010-04-04 18:27 | 2010-04-04 19:07 | 2 | 40 | 58516-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT STS FUSE BROKE VER/KEP L3/KEP IDCC PN184 XXXX
23091 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-02-21 07:05 | 2012-02-21 08:25 | 1 | 80 | 4454341 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFORM FUSE BLEW ON PUMP STATION, REFUSE 6T POWER RESTORED. FUSE BROKE VER/HFP L3/HFP
23092 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-09-22 14:30 | 2008-09-22 14:50 | 4 | 20 | 66259-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP CREW OPENED TRANSFORMER TO REPLACE IT. OIL REPORTED LEAKING FROM TRANSFORMER IN ORDER 66136-1 IDC XXXX
23093 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-07-14 22:05 | 2022-07-14 23:25 | 1 | 80 | 4492591 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replace door
23094 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2017-10-08 17:42 | 2017-10-08 18:22 | 2 | 40 | 4422821 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 380-55, OPENED LINE FUSE ON 380-54 AT 17:42 MADE REPAIRS RESTORED POWER AT 18:22../ ISO 37830380C00054/ COD 2/ VER/BOW L3/HFP XXXHFP
23095 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-04-29 16:28 | 2017-04-29 17:48 | 1 | 80 | 4695531 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O @ 1125-A-711, WILL BE CHANGING. CHANGED C/O AND CLOSED BACK IN @1748./ ISO 38831125A00711/ COD 1/ VER/BOW L3/HFP XXXHFP
23096 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-10-27 12:21 | 2014-10-27 12:41 | 4 | 20 | 4664181 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER CHANGING CUTOUT ON POLE 70-1020//CHANGED CUTOUT AND ARRESTOR---PWR OFF @ 12:21---BACK ON @ 12:41---PWR CK OK// COD 4// VER/ ADH VER/DKG L3/DKGXXXX
23097 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-11-11 11:35 | 2010-11-11 12:15 | 2 | 40 | 54849-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION AT ENTRANCE BURN IN TWO// //VER/CRB IDC XXXX
23098 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-11-15 16:05 | 2011-11-15 16:45 | 2 | 40 | 4079361 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COUPLE OF CONNECTIONS ON SECONDARY SIDE OF TRANSFORMER HAVE HEATED UP AND IS ARCING. I CALLED PIKEVILLE AND THEY ARE SENDING MATERIAL . THIS SERVES A SCHOOL AND THEY DONT WANT DISCONNECTED UNTIL AFTER 16:00. RELEASED BY CREW 074S01 ///VER/CRB IDC XXXX
23099 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2016-02-15 18:00 | 2016-02-15 18:20 | 4 | 20 | 4697731 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFMR LEAD BURNED INTO @ XFMR . NEED 1 MAN . OPENED XFMR @ 18:00 CLOSED BACK @ 18:20// VER/ ADH L/3 CRB
23100 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-06-29 16:30 | 2022-06-29 17:50 | 1 | 80 | 4347541 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke in shoe @ xfm ////Repaired broken neutral everything ok now 123/123/246
23101 | Hazard | 3308002 | JACKSON | PANBOWL | 2018-01-06 17:50 | 2018-01-06 19:10 | 1 | 80 | 4713491 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced service from pole 1083-181 to house/ ISO 38831083C20181/ COD 1
23102 | Pikeville | 3403001 | PIKEVILLE | CITY | 2008-10-11 17:40 | 2008-10-11 19:00 | 1 | 80 | 55083-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3403001//TRANSFORMER FUSE OUT // VER/TOM IDC XXXX
23103 | Hazard | 3309302 | VICCO | JEFF | 2011-05-02 11:17 | 2011-05-02 11:57 | 2 | 40 | 53501-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP L3/HFP IDC XXXX
23104 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-10-02 15:30 | 2012-10-02 16:50 | 1 | 80 | 4108711 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT DOOR FAILURE PATROLED LINE-OUT RE-PLACED CUT-OUT DOOR CHECK VOLTAGE POWER RESTORED KWB//COD 1// VER/DBM IDC XXXX
23105 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-09-28 20:44 | 2018-09-28 20:52 | 10 | 8 | 4179981 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | servicer making repairs to street light circuit
23106 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-12-19 17:15 | 2022-12-19 17:25 | 8 | 10 | 4277401 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Squeeze on bad. Also Xfrm cutout is cracked going to make repairs. Opened xfrm at 17:15 closed at 17:25. Repairs made. Power restored.
23107 | Whitesburg | 3401301 | FLEMING | NEON | 2015-11-22 14:44 | 2015-11-22 16:04 | 1 | 80 | 4478441 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED - RED PULLED APART, I REPLACED IT/ ISO 37830332A00028/ COD 1/ VER/BOW
23108 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2010-03-21 12:00 | 2010-03-21 13:20 | 1 | 80 | 52147-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED REPAIRED BROKE NEUTRAL// VER/DBM IDC XXXX
23109 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-04-28 15:55 | 2013-04-28 16:35 | 2 | 40 | 4054151 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE..CUTOUT GOING BAD..1089D323.MAP DISCREPANCY.POLE NOT SHOWN ON MAP.IT IS A SINGLE PHASE DEAD END POLE WITH A 50KVA FEEDS 2 SERVICES.TAKES OFF MAIN LINE POLE 1089D74.TAP IS FUSED ON 1089D74.SPAN IS 80 FT LONG GOING TOWARDS THE EAST OFF POLE 1089D74.OPENED XFMR FUSE @ 15:55.EXTINGUISHED FIRE.WILL REPLACE CUTOUT.//.REPLACED CUTOUT & ARRESTER.CLOSED CUTOUT.POWER ON.WILL CREATE & SEND ORDER FOR ENGNRNG TO REPLACE POLE..JRV..04/28/13//MADE MDC //////VER/CRB L/3 CRB. IDCC PN323 XXXX
23110 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2020-07-23 14:55 | 2020-07-23 16:15 | 1 | 80 | 4217721 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUST MIS MAPPED AND ACTUALLY ON XFMR POLE 869-A2-151failed cutout on 869-A2-151.i think i can make repairs.replaced cutout,restored power at 16:15
23111 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-05-10 18:13 | 2013-05-10 19:33 | 1 | 80 | 4098781 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. ///VER/CRB L/3 CRB IDCC CCU XXXX
23112 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-01-11 18:20 | 2022-01-11 19:00 | 2 | 40 | 4337211 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfm fuse failed. Power restored at 19:00.
23113 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-09-07 19:30 | 2014-09-07 20:50 | 1 | 80 | 4478381 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RESTORED @ 20:50. SH// ISO 38830954D30758/// COD 1// VER/BOW
23114 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2016-11-19 19:19 | 2016-11-19 19:27 | 10 | 8 | H4115091 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | NEEDS RISERS REPLACED//TRUCK ASSESSIBLE THROUGH ALLEY//CREW ON SITE/WILL NEED TO OPEN XFMR FOR REPAIRS APROX 30 MINUTE OUTAGE/VEM/OPEN XFMR 1919/TO REPAIR RISERS/FETR 1945/VEM/REPAIRS MADE AND FULL POWER RESTORED TO ALL CUST 1927/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
23115 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-08-17 15:50 | 2020-08-17 16:30 | 2 | 40 | 4340091 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened transformer on pole 1098-b-589 @ 15:50 to replaced broken cutout replaced cutout closed back in @ 16:30 everything ok
23116 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2009-01-16 09:25 | 2009-01-16 10:45 | 1 | 80 | 55778-1 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3309101//TROUBLE IS NOT VISIBLE, I AM GOING TO CHECK VOLTAGE AND CONNECTIONS BACK TO TRANSFORMERTROUBLE IS NOT VISIBLE, I AM GOING TO CHECK VOLTAGE AND CONNECTIONS BACK TO TRANSFORMER. FOUND SERVICE CONNECTOR BURNED OFF AT TRANSFORMER L3/HFP
23117 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-05-29 18:45 | 2008-05-29 20:05 | 1 | 80 | 52702-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3309104// REPLACED CONNECTIONS ON TRANSFORMER VER/HFP IDC XXXX
23118 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-09-21 07:55 | 2015-09-21 09:15 | 1 | 80 | 4255291 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKING XFMR - 37830144A00317 FUSE BROKE COD-1 ISO TF 37830144A00317 VER/HFP L3/HFP
23119 | Whitesburg | 3409503 | BURDINE | JENKINS | 2012-11-14 10:10 | 2012-11-14 10:50 | 2 | 40 | 4396721 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER BROKE OUT OF TOP OF CUT-OUT FOR XFMR . I REPLACED RISER AND REFUSED CUTOUT VER/KEP IDC XXXX
23120 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-08-17 18:15 | 2017-08-17 19:35 | 1 | 80 | 4272861 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, BAD CUTOUT, OPENED LINE FUSE AT 19:00, CHANGED CUTOUT AND ARRESTER, ALL POWER RESTORED AT 19:35 37830230A00124 37830230A00123 VER/AWD
23121 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2018-02-24 13:25 | 2018-02-24 14:05 | 2 | 40 | 4878621 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
23122 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2014-10-15 14:40 | 2014-10-15 15:00 | 4 | 20 | H4633951 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER STOPPED BY CUSTOMER TO LOOK AT PROBLEM ON POLE 1145-84// A PHASE OPEN AT POLE 1145-84, OPENED B & C PHASES AT 14:40 MADE REPAIRS AND CLOSED ALL PHASES AT 15:00 / ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03// COD-4 DUPLICATE OF 4633951 FOR B&C PHASE OUTAGE VER/HFP L3/HFP
23123 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-07-06 10:29 | 2011-07-06 11:49 | 1 | 80 | 4474241 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ENROUTE TO JOB BAD HOT TAP CONNECTOR REPLACED BAD HOT, TAP CLAMP//COD 1 IDC XXXX
23124 | Hazard | 3310502 | HADDIX | CANOE | 2014-03-14 09:40 | 2014-03-14 11:00 | 1 | 80 | 4491511 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREATED TICKET FOR CREW TO REPLACE BAD TR. FOUND BY SERVICER.REPLACE TRANSFORMER//COD 1// VER/DBM
23125 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2021-05-12 14:08 | 2021-05-12 14:48 | 2 | 40 | 4580561 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout and restored @ 14:48. sh
23126 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2017-12-07 18:30 | 2017-12-07 19:50 | 1 | 80 | 4629181 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | customer was having flickering lights replaced connections on 963C20 and sec pole 963C211 nuetral connection was bad on pole 20/ 38820963C00020 // CHANGED TIME OFF TO ALLOW TIME TO REPLACE SERVICE CONNECTIONS.
23127 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-10-20 14:28 | 2020-10-20 15:48 | 1 | 80 | 4571171 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @37820026000009, trans. cutout @26-9 went bad and blew the L/F. Will be making repairs. Got trans. cutout replaced and closed the L/F back in @1548. Xfer on pole 37820026000193 was never out of power
23128 | Hazard | 3310502 | HADDIX | CANOE | 2012-04-23 10:01 | 2012-04-23 11:21 | 1 | 80 | 4696431 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVIN OUT ON TRANSFORMER, GOING TO OPEN TRANSFORMER AND HAVE TO TRIM TREE THAT IS IN TRANSFORMER BEFORE I CAN GET REPAIRS MADE VER/KEP
23129 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-04-03 11:30 | 2016-04-03 11:50 | 4 | 20 | H4040201 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAVE A HOTTAP LEADE BURNED OFF @ POLE # 38830760B00201 .WILL OPEN LINE FUSE ON POLE #38830760B00200 & MAKE REPAIRS. OPENED ON 200 @ 11:30 MADE REPAIRS & CLOSED @ 11:50 /// DUP OF 4040201 FOR FUSE OUTAGE FOR 4 CUST VER/HFP L3/HFP
23130 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-11-30 23:00 | 2008-12-01 00:20 | 1 | 80 | H53252-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR - DIFFICULT LOCATION. DUTY SUPERVISOR NOTIFIED, CREW EN-ROUTE.//3401801BAD XFMR - DIFFICULT LOCATION. DUTY SUPERVISOR NOTIFIED, CREW EN-ROUTE. REPAIRS COMPLETE. HAD FUSE ON POLE 38830655B00028 OPEN FROM 11:00 TO 12:20 INTERRUPTING 2 CUSTOMERS. SH //VER/GAH IDC XXXX
23131 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2012-04-25 13:49 | 2012-04-25 15:09 | 1 | 80 | 4706981 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE SHORTED OUT, MAY EVEN BE BAD ENTRANCE CABLE POLE IS MIS -MAP 42-9 BROKEN NEU, FIXED VER/KEP
23132 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2019-11-08 09:51 | 2019-11-08 11:11 | 1 | 80 | 4011161 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opened xfmer at 10:41 back in @ 11:11. lash burnt up, repairs made. pls close. tre.//PART POWER FROM BEGINNING
23133 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-08-31 14:40 | 2008-08-31 15:00 | 4 | 20 | H58002-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP LINE FUSE OUT ON POLE 198-95.BAD ARRESTOR ON POLE198-216 .PHASE BEING OUT WAS CAUSING BACKFEED THROUGH XFMR BANK GIVING CUSTOMER LOW VOLTAGE.OPENED OTHER 2 PHASES AT 1440 ,CLOSED BACK IN AT 1500 ISO POLE 37830198D00095 COD - 7 //C PHASE 3 CUSTOMERS// A&B 4 IDC XXXX
23134 | Hazard | 3302703 | HAZARD | HAZARD | 2011-04-07 15:10 | 2011-04-07 16:30 | 1 | 80 | 51437-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN AGAIN, NEED TO REPLACE SERVICE, NEED TWO MEN, BIG BUCKET, NOTIFIED DUTY SUPERVISOR --POWER RESTORED.--//COD 1//VER/CRB
23135 | Pikeville | 3408401 | KIMPER | LONGFORK | 2008-12-04 00:10 | 2008-12-04 01:30 | 1 | 80 | 54343-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3408401//WILL REPLACE SERVICE DROP VER/KEP L3/KEP IDC CHANGED TIME OFF FROM 2223 XXXX
23136 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-03-01 14:34 | 2020-03-01 15:54 | 1 | 80 | 4442511 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout has failed. I will be replacing/// Replaced cutout and restored power @ 15:54
23137 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-10-15 11:00 | 2015-10-15 11:20 | 4 | 20 | 4351041 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELATED TO 4350171/ OPENING LINE FUSE TO REPLACE TRANSFORMER 38831100000036/ ISO 38831100000036/ COD 4 11 TO 1120/ VER/BOW
23138 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-05-14 11:37 | 2016-05-14 11:57 | 4 | 20 | 4216461 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT// REPLACED CUT-OUT AND RESTORED POWER AT 11:57 VER/CRB
23139 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2022-07-13 10:35 | 2022-07-13 11:15 | 2 | 40 | 4481371 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad trans. cutout @25-B-136, opened @1035 changed out and restored @1115.
23140 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-06-30 23:10 | 2015-07-01 00:30 | 1 | 80 | 4702031 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN ON POLE 121-3. I CHANGED CUTOUT.
23141 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2021-04-19 15:50 | 2021-04-19 16:30 | 2 | 40 | 4462141 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Xfm neutral connection burnt off ///Opened xfm @ 15:50 (no outage till this time)////Made repairs and closed xfm back in @ 16:30 and restored service
23142 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-12-02 14:45 | 2008-12-02 16:05 | 1 | 80 | 53970-1 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 27506712 //FOUND BAD CONNECTION AT POLE 1123-4525// VER/DBM L3/KEP IDCC FP4520 XXXX
23143 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2010-07-13 22:25 | 2010-07-13 22:45 | 4 | 20 | 66510-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESSTOR CLEAR UP OPEN TRAN AT 22;25 CLOSE BACK 22;45 VER/KEP L3/KEP IDC XXXX
23144 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-11-08 14:27 | 2012-11-08 15:47 | 1 | 80 | 4374901 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN, REPLACED SERVICE DROP VER/HFP L3/HFP IDCC CCO XXXX
23145 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2020-01-06 16:19 | 2020-01-06 17:39 | 1 | 80 | 4218431 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired service connections complete
23146 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-07-16 17:20 | 2008-07-16 17:40 | 4 | 20 | 53325-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPEN TRANSFORMER AT 17:20 AND ON AT 17:40//3403003//VER/CRB IDCC CNT1 XXXX
23147 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-10-14 12:01 | 2011-10-14 12:41 | 2 | 40 | H4977551 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED, BAD 15 KVA CSP, NEED 15KVA 7200 XFMR AND CUTOUT AND BRACKET, TRUCK OK, WILL HAVE TO SET UP ON ROAD, TRANSFORMER WOULD NOT RESET. RELEASED BY CREW 078S05//COD 2//FETR NEEDED ONCE CREW ARRIVES ON SITE //OPENED LINEFUSE 207-122 @ 12;01 BACK ON @ 12;41////XFMR VOLT CK OK 117/117/246V---//COD 2 IDCC DUP TO OPEN LINE FUSE XXXX
23148 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-01-05 13:23 | 2011-01-05 14:03 | 2 | 40 | 58963-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMETTING FUSE BURNED UP REPLACED FUSE POWER RESTORED AT 1403 CLOSE TICKET COD-2 ISO PO 38830453000079 VER/HFP L3/HFP IDC XXXX
23149 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2015-06-05 13:25 | 2015-06-05 14:45 | 1 | 80 | 4515561 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | GEORGE OPENING BANK TO MAKE REPAIRS ON PIN INSULATOR OPEN AT 13:25 CLOSED AT 14:45 REPAIRS MADE/ ISO 37830307000121/ COD 1/ VER/BOW
23150 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-10-06 10:28 | 2014-10-06 11:48 | 1 | 80 | 4557031 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN // WILL REFUSE /// FUSE LINK BROKE // POWER RESTORED @ 11:48// COD 1// VER/ ADH VER/DKG L3/DKGXXXX
23151 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-12-05 13:10 | 2016-12-05 14:30 | 1 | 80 | 4166521 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKEN RE-FUSING.BAD CUTOUT DOOR REPLACING VER/CRB L3/HFP XXXHFP
23152 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2019-12-25 13:01 | 2019-12-25 14:21 | 1 | 80 | 4181251 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout , changing..
23153 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-12-03 09:01 | 2008-12-03 10:21 | 1 | 80 | 54155-1 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP SERVICE CONNECTOR IS FROZEN LOOSE AT TRANSFORMER POLE IDC XXXX
23154 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2016-06-21 13:50 | 2016-06-21 14:10 | 4 | 20 | 4395411 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | .. POLE 1098-554 BAD ARRESTER,CREW TO CHANGE. BEHIND 1524 ELMHURST /// OPENED XFMR @ 1350 CLOSED @1410 COD-4 ISO TF 39831098C00554 VER/CRB
23155 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-02-25 15:02 | 2020-02-25 16:22 | 1 | 80 | 4431751 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | was not a outage, a part power, reworked all connections, rem srv ends,check with cust everything seems to be ok at this time L3/HFP
23156 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-03-26 20:40 | 2011-03-26 21:00 | 4 | 20 | 59561-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 39319137 // BAD CONNECTION AT TRANSFORMER. OPENED TRANSFORME @ 2040. --- SDB / OUTAGE FROM 2040-2100. POWER RESTORED. VER/SDB IDC XXXX
23157 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2019-10-08 19:55 | 2019-10-08 20:15 | 4 | 20 | 4121451 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 91-100 opened @ 19:55, closed 20:15.repaired connection on sec. cable
23158 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-09-17 13:41 | 2015-09-17 15:01 | 1 | 80 | 4246551 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD NEUTRAL CONN. ON SEC. POLE WILL MAKE REPAIRS/////RECONNECTED NEUTRAL.// VER/ ADH
23159 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-02-03 22:28 | 2017-02-03 23:48 | 1 | 80 | 4357921 | 80 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | WILL CHECK FOR PROBLEMS///////SERVE-IN FROZE OUT AT XFR POLE.MADE REPAIRS,ALL OK AFTERWARDS VER/KEP L3/HFP XXXHFP
23160 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-05-03 09:10 | 2016-05-03 10:30 | 1 | 80 | 4168411 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE MELTED OUT WHEN RECLOSER WAS CLOSED IN EARLIER. REFUSED AND RESTORED SERVICE.//COD 1// VER/DBM
23161 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-02-08 15:34 | 2009-02-08 16:54 | 1 | 80 | 56754-1 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3404302//ON SITE, LINE FUSE BLOWN ON POLE#1036-D-50, CUST SERVED OFF POLE# 1036-D-57, 6/A COPPERWELD COND. ONE STRAND BROKE, BECOME UNRAVELED AND GOT INTO NEUTRAL, BLOWING FUSE, 12T FUSE // MAP DISC ISSUED// VER/TOM L3/TOM IDCC PN55 XXXX
23162 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-04-30 18:40 | 2021-04-30 19:00 | 4 | 20 | 4505271 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Customer was seeing flicker due to xfmr cutout being broke and loosing contact. Opened xfmr @ 18:40 and replaced cutout. Restored @ 1900
23163 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2012-11-10 12:40 | 2012-11-10 13:00 | 4 | 20 | 4379671 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-5103 DOOR FELL OPEN CLOSED ///VER/CRB L/3 CRB IDC XXXX
23164 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-05-05 13:55 | 2016-05-05 15:15 | 1 | 80 | 4178211 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BAD CURRENT LIMITER VER/AWD
23165 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-08-05 20:50 | 2020-08-05 22:10 | 1 | 80 | 4291161 | 80 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Wire tore down last week. Still had bad place and burnt down. (1 CC)Repaired
23166 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-02-27 11:26 | 2019-02-27 12:45 | 1 | 79 | 4932511 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | xfmr lead to secondary had bad splice, I replaced it.
23167 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-03-07 08:41 | 2014-03-07 10:00 | 1 | 79 | 4458561 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY HOT LEG BURNT INTO @ POLE 247-227 REPAIRS MADE ALL CUST RESTORED @ 1000 PLEASE CLOSE TICKET THANKS.BT VER/CRB
23168 | Hazard | 3310502 | HADDIX | CANOE | 2009-03-05 19:50 | 2009-03-05 21:09 | 1 | 79 | 55495-1 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | VER/HFP STS METER WAS BURNED UP, I DONT KNOW IF POWER WAS OFF BUT THE METER WAS BLACK AND HE SAID HE DIDNT TRY IT. CHANGE METER (TURTLE METER) L3/HFP IDC XXXX
23169 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-07-10 17:53 | 2013-07-10 19:12 | 1 | 79 | 4499861 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEW CUTOUT BROKE VER/KEP IDC XXXX
23170 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-01-14 17:41 | 2009-01-14 19:00 | 1 | 79 | 55063-1 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3401002//REPAIRED BAD CONNECTION ON POLE. ONE LEG OUT....DAH //VER/GAH L3/KEP
23171 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-07-21 22:22 | 2013-07-21 23:41 | 1 | 79 | 4573251 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON TRANS. POLE REPAIRED VER/SDB
23172 | Pikeville | 3413401 | GARRETT | GARRETT | 2019-01-13 20:41 | 2019-01-13 22:00 | 1 | 79 | 4669531 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t fuse and cutout door burnt up replace cutout door everything ok//cod 1 L3/HFP
23173 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-08-10 09:56 | 2013-08-10 11:15 | 1 | 79 | 4644701 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON B PHASE TRANSFORMER.==== POWER RESTORED. VER/CRB L/3 CRB
23174 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-08-10 16:11 | 2014-08-10 17:30 | 1 | 79 | 4350831 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7200 CUTOUT,/ COD 1 //VER/ ADH
23175 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-05-03 09:26 | 2009-05-03 10:45 | 1 | 79 | 63900-1 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CHANGED CUT OUT AND RESTORED POWER M.D.I. COD-1 37830402A00213 L3/HFP IDC XXXX
23176 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-03-08 20:52 | 2009-03-08 22:11 | 1 | 79 | 56335-1 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WR#28830568//BAD CONN. ON POLE AND HOUSE REPAIRED//VER/CRB IDC XXXX
23177 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-06-02 04:27 | 2020-06-02 05:46 | 1 | 79 | 4942071 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse link appears to have broke. Restored @ 5:46. sh
23178 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-02-07 20:51 | 2018-02-07 22:10 | 1 | 79 | 4815231 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out, pole # 255-94, one customer, fuse broke/ ISO 37830255B00094/ COD 1
23179 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-01-21 20:43 | 2013-01-21 22:02 | 1 | 79 | 4725001 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PART POWER , BAD SPLICE IN SERVICE NEUTRAL BROKE CAUSING ONE HOT LEAD IN SERVICE DROP TO BURN INTO, REPAIRED SERVICE RESTORED POWER AT 22:02.. ///VER/CRB L/3 CRB IDC XXXX
23180 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-10-08 14:09 | 2016-10-08 15:28 | 1 | 79 | 4972201 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SINGLE ALL OUT BROKEN CUT-OUT DOOR REPLACED WITH NEW ONE 6-T POWER RESTORED VER/CRB L3/HFP XXXHFP
23181 | Pikeville | 3401001 | ELWOOD | DORTON | 2010-06-03 13:01 | 2010-06-03 14:20 | 1 | 79 | 55929-1 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP. I AM GOING TO CHANGE DOOR. I CHANGED DOOR. VER/KEP L3/KEP IDC XXXX
23182 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-04-17 17:29 | 2012-04-17 18:48 | 1 | 79 | 4680991 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK PULLED APART IN SPLICE IN SERVICE. REPAIRED AND RESTORED @ 18:48. SH VER/HFP L3/HFP IDC XXXX
23183 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-09-26 17:21 | 2011-09-26 18:40 | 1 | 79 | 4920781 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AT POLE 351-235, EXTINGUISHED FIRE, CHANGED CUTOUT, ALL POWER RESTORED COD-1 ISO TF 38830351000235 VER/HFP L3/HFP IDC XXXX
23184 | Paintsville | 3401102 | FALCON | SALYERSVI | 2021-10-06 13:25 | 2021-10-06 14:44 | 1 | 79 | 4323761 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, changing.
23185 | South Williamson | 3411401 | DEWEY | INEZ | 2020-01-21 00:16 | 2020-01-21 01:35 | 1 | 79 | 4324591 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burned down//i replaced service drop//restored at 1:35//complete//em L3/HFP
23186 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-05-30 22:56 | 2016-05-31 00:15 | 1 | 79 | 4273571 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED . REPLACED C LIMITIG FUSE AND REFUSED CUTOUT , ALL WORK COMPLETE / GXJ VER/TOM L3/TOM
23187 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2022-07-24 15:41 | 2022-07-24 17:00 | 1 | 79 | 4568591 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o.. repaired . restored 15:00 Released by crew 078S07
23188 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-02-18 10:23 | 2015-02-18 11:42 | 1 | 79 | 4038861 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN ON KVA CUTOUT REPLACED FUSE CLOSED DOOR CUTOUT FELL APART CHANGED CUTOUT RESTORED POWER AT 11;4 2 PLEASE CLOSE TICKET THANKS DWW//COD 1// VER/DBM // NOTE CUST COUNT CORRECT AT TIME OF OUTAGE = L3/HFP XXX
23189 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2016-01-21 14:02 | 2016-01-21 15:21 | 1 | 79 | 4638881 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT APR AT 1521 CLOSE TICKET
23190 | South Williamson | 3411401 | DEWEY | INEZ | 2011-09-04 21:39 | 2011-09-04 22:58 | 1 | 79 | 4812461 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE F USE OPEN ON POLE 743-159 CHECKING NOW.CUTOUT DOOR BURNT UP CHANGED DOOR BACK TO NORMAL//COD 34 IDC ASSUMING ONLY ONE PHASE OUT CHANGED COUNT FROM 34 XXXX
23191 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-06-07 11:41 | 2019-06-07 13:00 | 1 | 79 | 4445581 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tree grown up around transformer trimmed tree back away from transformer, then found broken c/o, have changed power is restored at this loc at 1300 by amg
23192 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-07-09 23:31 | 2010-07-10 00:50 | 1 | 79 | 64560-1 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830292C00139, LINE WAS HOT WHEN I ARRIVED, OPENED XFMR AT 00:40, CLOSED AT 00:50, POLE IS BURNT ABOUT HALF THROUGH, PUT OUT FIRE AND CHANGED CUTOUT, SAFE FOR NOW BUT WILL NEED CHANGED AT LATER DATE. IDCC PN271, TOF2331CNT3 XXXX
23193 | Hazard | 3301101 | CHAVIES | CHAVIES | 2021-05-17 16:16 | 2021-05-17 17:35 | 1 | 79 | 4593641 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
23194 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2014-07-16 11:01 | 2014-07-16 12:20 | 1 | 79 | 4253311 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT DOOR IS BURNT IN TWO. REPLACED AND RESTORED @ 12:20. SH COD 1// VER/ADH
23195 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2013-11-07 15:26 | 2013-11-07 16:45 | 1 | 79 | 4020071 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STRUP BURN OFF PRIMARY METER === REPAIRED STURP === POWER OK VER/CRB L3/HFP HFPC PN320-451
23196 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2018-06-03 18:01 | 2018-06-03 19:20 | 1 | 79 | 4551321 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Released by crew 077S03 1920
23197 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2019-01-27 13:35 | 2019-01-27 14:54 | 1 | 79 | 4726181 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr , made repairs restored power at 14:54.
23198 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-07-19 18:43 | 2011-07-19 20:02 | 1 | 79 | 4564391 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING.SERVICE NEUTRAL BURNDT INTO WILL HAVE TO SPLICE, WILL HAVE THIS TRANS. OPEN, MANUAL POLE, WILL KEEP TRACK OF TIMES.OPENED AT 18:43, REPAIRED AND CLOSED BACK IN AT 19:48 VER/HFP L3/HFP
23199 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-08-02 12:19 | 2011-08-02 13:38 | 1 | 79 | 4655401 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1147-865 6T TRANS FUSE BROKE REPLACED//VER/CRB IDC XXXX
23200 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-07-07 18:08 | 2015-07-07 19:27 | 1 | 79 | 4739761 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON SERVICE DROP BURNT INTO///MAKING REPAIRS//REPAIRS MADE///COMPLETE BR/ ISO 38830875D00634/ COD 1/ VER/BOW
23201 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2019-12-11 15:31 | 2019-12-11 16:50 | 1 | 79 | 4145701 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | customer was having part power.replaced a splice in the service drop.
23202 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2016-06-27 17:23 | 2016-06-27 18:42 | 1 | 79 | 4487711 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN,WILL REPLACE IF POSSIBLE//////////////REPLACED CUTOUT AND RESTORED SERVICE,ALL OK AFTERWARDS///////APPEARS CUTOUT HAD BEEN BREAKING DOWN FOR SOME TIME,CHARRING EVIDENT ON XARM VER/HFP L3/HFP
23203 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-07 10:31 | 2015-02-07 11:50 | 1 | 79 | 4998121 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 38830648B10690//CUTOUT BROKE ON POLE 648-B-690//CUTOUT REPLACED//RESTORED AT 11:50//COMPLETE//EM VER/CRB L3/HFP XXX
23204 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-05-29 07:41 | 2022-05-29 09:00 | 1 | 79 | 4978621 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burnt up
23205 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-11-21 23:46 | 2011-11-22 01:05 | 1 | 79 | 4098891 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED VER/PDP IDC XXXX
23206 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-08-11 14:41 | 2013-08-11 16:00 | 1 | 79 | 4650281 | 79 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED AT XFMR WAS BAD. REDONE CONN. POWER GOOD VER/CRB L/3 CRB
23207 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-07-09 18:06 | 2017-07-09 19:25 | 1 | 79 | 4099941 | 79 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED#//VOICEMAIL// TRANS. FUSE OPEN ON38831056B00099, CHECKING.CALLED#//VOICEMAIL// TRANS. FUSE OPEN ON 1056-B-99, CHECKING. TRANS. FUSE PULLED APART, REFUSED @1925. VER/CRB
23208 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-10-25 12:52 | 2016-10-25 14:10 | 1 | 78 | 4052331 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING CUTOUT VER/AWD L3/HFP XXXHFP
23209 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-10-21 19:37 | 2021-10-21 20:55 | 1 | 78 | 4373761 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse blown on 170-33 will be checking//Cutout broke on pole 170-34 will be making repairs//cod 1
23210 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-04-03 23:39 | 2008-04-04 00:05 | 3 | 26 | 63642-1H | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202201// CUTOUT BAD ON POLE 697-D-104 @ 2339 OPENED LF ON POLE 697-57 TO C/O CUTOUT.CC 5 TOTAL VER/PDP IDCC DUP TO OPEN FUSE XXXX
23211 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-05-25 08:27 | 2021-05-25 09:45 | 1 | 78 | 4618881 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp broke--repaired-allgood-ds052521
23212 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2013-03-14 09:47 | 2013-03-14 11:05 | 1 | 78 | 4905251 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT DOOR BURNT UP. REPLACED DOOR AND REFUSED XFMR @ 11:05. SH VER/KEP IDC XXXX
23213 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2013-01-07 16:27 | 2013-01-07 17:45 | 1 | 78 | 4575851 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOU DOOR MELTED OUT ON 820-178//GOING TO REFUSE//RESTORED AT 1745//COMPLETE//COD 1// VER/DBM IDC XXXX
23214 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2021-01-07 22:57 | 2021-01-08 00:15 | 1 | 78 | 4855481 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Nuetral broke in service drop. Removed meter to make repairs. Restored @ 00:15
23215 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-02-02 13:12 | 2010-02-02 14:30 | 1 | 78 | 62364-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE IN SER INTO----SER. HAD OUTHER BAD PLACES, CHANGED OUT TO A NEW SER. VER/KEP L3/KEP IDC XXXX
23216 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-10-09 18:54 | 2013-10-09 20:12 | 1 | 78 | 4926011 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR FUSE IS OUT,WILL RE-FUSE////////RE-FUSED AND RESTORED,APPEARED TO HAVE BROKEN COD-1 ISO TF 38821132000043 VER/HFP L3/HFP
23217 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-11-14 10:18 | 2016-11-14 11:36 | 1 | 78 | 4099381 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | B PHASE FUSE PULLED INTO ON TRANSFORMER BANK POLE, 72-D1-666, REFUSED @1136. VER/CRB
23218 | Whitesburg | 3312901 | JENKINS | KONA | 2011-07-12 15:29 | 2011-07-12 16:08 | 2 | 39 | 4532271 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHECKING. CUST. METER POLE BROKE, SERVICE IS STILL HOT. GOING TO DISCONNECT SERVICE AT POLE 404-88 AND INFORM CUST. TO CALL BACK IN WHEN REPAIRS ARE MADE TO RECONNECT, WE ALSO HAVE A BAD C/O AT THIS POLE, WILL ISOLATE , KENNY BROOME COMING TO CHANGE OUT.2 CUST. OUT. OPENED C/O AT 15:29, CLOSED BACK IN AT 16:08 VER/KEP
23219 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-02-10 22:57 | 2009-02-11 00:15 | 1 | 78 | 57557-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT COD-1 L3/HFP
23220 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-02-20 11:54 | 2020-02-20 13:12 | 1 | 78 | 4420801 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt open at xfm will make repairs/// Replaced bad connection and restored @ 13:12 L3/HFP
23221 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-02-14 10:32 | 2015-02-14 11:50 | 1 | 78 | 4014941 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRING BAD CONNECTION//ON @1150// VER/ ADH L3/HFP XXX
23222 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-11-04 12:57 | 2008-11-04 14:15 | 1 | 78 | 62113-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP PLEASE DON`T FORGET THE FETR...THANKSRESEND RELEASED BY CREW 078S07 IDC XXXX
23223 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-07-13 19:07 | 2013-07-13 20:25 | 1 | 78 | 4519921 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED DAMAGED SERVICE VER/HFP L3/HFP IDCC CCU XXXX
23224 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-01-18 11:49 | 2020-01-18 13:07 | 1 | 78 | 4318091 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hot leg & neut burnt up on service. making repairs. pls close. tre L3/HFP
23225 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-07-08 13:38 | 2009-07-08 14:56 | 1 | 78 | 61520-1 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTOMER HAS EQUIPMENT DAMAGE, NEUTRAL ON SERVICE DROP PULL LOOSE. NO 4/3 SERVICE DROP REPLACE WITH 2/3 SERVICE DROP//EMAILED TO P WYSONG// VER/DBM IDC XXXX
23226 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-02-06 14:45 | 2010-02-06 14:58 | 6 | 13 | 50515-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE TEMP. FOR TODAY 92-2014 OPENED LINE FUSE 14;45 TO MAKE REPAIRES RELEASED BY CREW 078S08 IDC XXXX
23227 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-12-25 11:02 | 2015-12-25 12:20 | 1 | 78 | 4558641 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE RUSTED INTO AND GOT AGIANST PRIMARY RISER ON XFM/// BLEW XFM FUSE/// RE-PULLED GUY AND RE-FUSED XFM @ 12:20 AND RESTORED SERVICE// VER/ ADH
23228 | Hazard | 3309302 | VICCO | JEFF | 2020-02-21 14:11 | 2020-02-21 15:29 | 1 | 78 | 4423161 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout need crew and flaggers L3/HFP
23229 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-01-30 23:11 | 2022-01-31 00:29 | 1 | 78 | 4417361 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required
23230 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-03-20 15:51 | 2011-03-20 16:30 | 2 | 39 | 56088-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 39229613 // BAD CUTOUT //COD 2// VER/DBM IDC XXXX
23231 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-12-24 12:07 | 2017-12-24 13:25 | 1 | 78 | 4672161 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Released by crew 078S11/on site RM cutout door burnt up all pwr restored @ 13:25 please close ticket RM
23232 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-09-10 14:42 | 2019-09-10 16:00 | 1 | 78 | 4000551 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on 2-202.replaced cutout,restored at 16;00.
23233 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-11-11 15:22 | 2020-11-11 15:48 | 3 | 26 | 4662901 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout on pole 37820002000058 is cracked// will have to lift hottap to de-energize XFM will keep up with times/// off at 15:22 on at 15:48
23234 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-03-12 19:40 | 2021-03-12 20:58 | 1 | 78 | 4332711 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, opened line fuse on pole 458-54 at 19:40 closed at 20:58/ ISO 37830458000054/ COD 1
23235 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-01-16 18:52 | 2015-01-16 20:10 | 1 | 78 | 4940071 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP NEUTRAL AND PHASE BURNED DN.// VER/ ADH
23236 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-08-17 13:21 | 2015-08-17 14:00 | 2 | 39 | 4142881 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN. REPLACED FUSE AND RESTORED @ 14:00. SH// VER/ ADH
23237 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-11-19 14:04 | 2021-11-19 15:22 | 1 | 78 | 4108991 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | cutout fuse broken.replaced 6t fuse
23238 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-04-04 16:33 | 2008-04-04 16:59 | 3 | 26 | 63995-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3116701// FUSE BROKE- CUTOUT NEEDS REPLACED-TRUCK WHEN DRY-ACESS THROUGH BELHAVEN- STATION-2 POLE OUT OF STATION SEND TO LLOYD RAYBURN VER/HFP IDCC TOF1552 XXXX
23239 | Hazard | 3303903 | LESLIE | HALSFORK | 2021-04-07 15:59 | 2021-04-07 17:17 | 1 | 78 | 4427931 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | replaced connection
23240 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-02-25 17:07 | 2012-02-25 18:25 | 1 | 78 | 4506141 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THERE IS NO OPEN METERBASE JUST TRANSFORMER FUSE BROKE, NOT SURE WHY CALL CENTER PUT IN AS HAZARD, WRONG CALL. REPLACED FUSE, COD-1 ISO TF 38830180000044 VER/HFP L3/HFP IDC XXXX
23241 | Hazard | 3307301 | BULAN | ARY-HEINE | 2016-09-01 13:17 | 2016-09-01 14:35 | 1 | 78 | 4860911 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUT OUT VER/CRB L3/HFP XXXHFP
23242 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2016-10-04 07:33 | 2016-10-04 08:51 | 1 | 78 | 4957951 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT COMPLETE VER/CRB L3/HFP XXXHFP
23243 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-05-31 09:05 | 2011-05-31 10:23 | 1 | 78 | 4212551 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR PART POWER, MADE REPAIRS RESTORED POWER AT 10:23//VER/CRB IDC XXXX
23244 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-06-20 15:00 | 2018-06-20 15:39 | 2 | 39 | 4627611 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LEAKING XFR IS ACTUALLY ON POLE 217-200.NOT LEAKING A LOT BUT SOME.IS A 50KVA 7.2CSP.CAN USE MAT HANDLER.TIM HALL SENDING CREW W XFR SHORTLY. Released by crew 074S06//opened 1500 closed 1539
23245 | Whitesburg | 3409503 | BURDINE | JENKINS | 2015-02-26 17:55 | 2015-02-26 19:13 | 1 | 78 | 4084521 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN WILL HAVE TO OPEN TRANSFORMER 358-D-128 TO SAFELY MAKE REPAIRS/SERVICE NEUTRAL BROKE OFF OF HOUSE, HAD TO OPEN TRANS. AT POLE 358-128 TO MAKE REPAIRS, OPENED AT 1900, CLOSED BACK IN AT 1913, ALL REPAIRS MADE.1 PART POWER, THEN TOOK TRANSFORMER OFF/COD 1+1// VER/ ADH
23246 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-06-06 19:55 | 2019-06-06 20:34 | 2 | 39 | 4441121 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Copper riser had come loose from the top of the cutout/ ISO 38830829000090/ cOD 2/ 2034
23247 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2019-02-02 15:42 | 2019-02-02 17:00 | 1 | 78 | 4749121 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | splice burned up in service both hot legs , I replaced it
23248 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-08-14 12:17 | 2020-08-14 13:35 | 1 | 78 | 4325261 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | wire got togeather on sec pole off of pole 38830761000013 burnt neutral and one hot conductor into. the contractor for claton mobile home cust said he said he got shocked but he said he was ok and had other work to do so he left. made repairs everything ok//SENT TO CLAIMS AN MANAGEMENT
23249 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-02-22 15:52 | 2013-02-22 17:10 | 1 | 78 | 4840761 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | C PHASE TRANSFORMER FUSE BROKE. ONLY ONE THREE PHASE CUSTOMER HAD PART POWER. IDC XXXX
23250 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-02-17 10:10 | 2009-02-17 11:28 | 1 | 78 | 63086-1 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | VER/HFP SECONDARY RISER ON XFMR BROKE, REPAIRED RISER L3/HFP
23251 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-05-10 16:58 | 2019-05-10 17:24 | 3 | 26 | 4250041 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 19.9 xfmer cutout on pole 164-48///rick morgan enroute to observe for me to replace//changed cutout///back on at 17:24///complete BR
23252 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-07-01 19:44 | 2015-07-01 20:10 | 3 | 26 | H4706321 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE WILL CHANGE/// OPENED LINE FUSE @ 19:44 AND ALSO REPLACED BROKEN CUTOUT ON POLE # 1057-76 AND CHANGED XFM CUTOUT/// RESTORED SERVICE @ 20:10 ON XFM AND LINE FUSE// VER/ ADH
23253 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2017-12-29 18:00 | 2017-12-29 19:18 | 1 | 78 | 4688141 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout in process of changing cutoutcutout failed on 124-30 replaced curout restored power at 19:18/ ISO 37820124000030/ COD 1
23254 | Pikeville | 3421001 | BREAKS | CITY | 2010-11-10 11:32 | 2010-11-10 12:50 | 1 | 78 | 54601-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNED DOWN DUE TO A BAD CONNECTION. ONLY ONE CUSTOMER AFFECTED. I REPAIRED THE SERVICE. //VER/CRB IDC XXXX
23255 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2019-03-07 09:54 | 2019-03-07 11:12 | 1 | 78 | 4958841 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | REPLACING BROKE ARM 849-43.. Opened @ pole 825-50 @ 10:25 closed @ 11:12 COD-1
23256 | Hazard | 3303902 | LESLIE | WOOTON | 2022-07-13 11:47 | 2022-07-13 13:05 | 1 | 78 | 4482111 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
23257 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-04-03 11:57 | 2010-04-03 13:15 | 1 | 78 | 57882-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR BROKE CUT IN CLEAR, POWER RESTORE VER/KEP IDCC PN1018, CNT3 XXXX
23258 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2021-05-07 10:01 | 2021-05-07 11:19 | 1 | 78 | 4547241 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout bad on 231-247, line fuse out on 231-47 replaced cutout and arrestor, all power restored
23259 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-01-08 14:47 | 2015-01-08 16:05 | 1 | 78 | 4921311 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR ON POLE 115-D-93/BAD 19.9 CUTOUT DOOR RESTORED// COD 1// VER/ ADH
23260 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-05-12 07:16 | 2017-05-12 08:34 | 1 | 78 | 4785121 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT, APR AT 0834 CLOSE TICKET. DWEST 38830624000049 VER/AWD
23261 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-04-06 15:57 | 2014-04-06 17:15 | 1 | 78 | 4579811 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT//COD 1// VER/DBM
23262 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-02-27 18:17 | 2011-02-27 19:35 | 1 | 78 | 63538-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN DOWN ON POLE 142-111. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT.//COD 1// VER/DBM IDC XXXX
23263 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-06-06 13:37 | 2016-06-06 14:55 | 1 | 78 | 4314871 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1094406//.. CONNECTION BURNT INTO AT WEATHERHEAD WILL B MAKING REPAIRS.. MADE REPAIRS, ALL POWER BACK ON..///VER ALS
23264 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-03-15 09:35 | 2013-03-15 10:53 | 1 | 78 | 4907451 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END PULLED LOOSE.PARTIAL POWER. ///VER/CRB L/3 CRB IDC XXXX
23265 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-12-05 19:19 | 2009-12-05 19:58 | 2 | 39 | 55621-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, CHECKING TROUBLE RELEASED BY CREW 080S01 NO CUSTOMERS OUT UNTIL WE OPENED XFMR TO PULL NEUTRAL WIRE XFMR ON POLE 37830285000009 OPENED AT 19:19 CLOSED AT 19:58 VER/KEP L3/KEP IDC XXXX
23266 | Hazard | 3309003 | JEFF | VIPER | 2018-04-27 10:10 | 2018-04-27 11:28 | 1 | 78 | 4283481 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Replce service wire been spliced and brunt up opened transformer 10:10 on 1128
23267 | Hazard | 3310502 | HADDIX | CANOE | 2017-03-17 21:22 | 2017-03-17 22:40 | 1 | 78 | 4566041 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WERE OPEN SEC IS SOMEONE HAS PUT 1 / 4 GUY WIRE FOR #4 AL AND HAD BAD CONNECTION ON SERVICE, NEED TO SEND TO DOUG CHRISTIAN TO REPLACE GUY WIRE WITH #4 AL OR HANG TRANSFORMER NEXT POLE DOWN VER/KEP
23268 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-10-26 17:30 | 2015-10-26 18:48 | 1 | 78 | 4378281 | 78 | TRANSMISSION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | EMERGENCY OUTAGE TO MAKE REPAIRS TO FACILITIES//TOM DAVOX SENT//TOM CLOSED @ 1843
23269 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-11-29 20:08 | 2010-11-29 20:47 | 2 | 39 | 60785-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 37913947 //....XFMR FUSE OUT....LOOKS LIKE IT MELTED OUT....WILL RE-FUSE..//....FUSE WAS JUST BROKEN....RE-FUSED....POWER ON.....JRV....11/29/10 COD-2 VER/HFP L3/HFP IDCC CCO XXXX
23270 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2009-07-05 11:15 | 2009-07-05 11:54 | 2 | 39 | 65824-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 2// VER/DBM IDC XXXX
23271 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-07-31 08:42 | 2014-07-31 10:00 | 1 | 78 | 4312831 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKEN.RE-FUSED XFMR
23272 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-01-21 11:17 | 2015-01-21 12:35 | 1 | 78 | 4949271 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FAILED CURRENT LIMITING FUSE. 37820193A00368 VER/CRB
23273 | South Williamson | 3411401 | DEWEY | INEZ | 2010-06-11 14:24 | 2010-06-11 15:42 | 1 | 78 | 60135-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BROKE. REPLACED. SH//COD 1// VER/DBM
23274 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-06-14 12:02 | 2010-06-14 13:20 | 1 | 78 | 63508-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35554508 //NO CREW REQUIRED REPLACED CUTOUT DOOR VER/HFP L3/HFP
23275 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-01-29 14:18 | 2019-01-29 15:36 | 1 | 78 | 4731931 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open in service drop will ,make repairs/// Replaced connections in service drop//everything is good now 121/121/242 ¦¦ L3/HFP
23276 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-04-05 08:42 | 2014-04-05 10:00 | 1 | 78 | 4577141 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7200 CUTOUT//COD 1// VER/DBM
23277 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-11-07 06:52 | 2010-11-07 08:10 | 1 | 78 | 53628-1 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE-END FROZE OUT AT TRANS. POLE. I RESQUEEZED CONNECTION. VER/TOM IDC XXXX
23278 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2020-03-18 12:47 | 2020-03-18 14:05 | 1 | 78 | 4488641 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Primary metering fuse appears to have melted out on 809-325 - Phase C. Restored @ 14:05. sh
23279 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-01-29 17:03 | 2011-01-29 18:21 | 1 | 78 | 52083-1 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | NO CREW REQUIRED RESET BREAKER ON ADAPHASE//VER/CRB IDC XXXX
23280 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-11-19 22:12 | 2015-11-19 23:30 | 1 | 78 | 4473111 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | POLE 91-430 PRI. LOOP LAYING ON POLE POLE 91-52 20T LINE FUSE VER/KEP
23281 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2020-04-27 09:32 | 2020-04-27 10:50 | 1 | 78 | 4756591 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required6t
23282 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-07-19 19:24 | 2022-07-19 20:42 | 1 | 78 | 4526431 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutrual broke in service drop.
23283 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-07-06 23:36 | 2009-07-07 00:54 | 1 | 78 | 55022-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000902//CHANGED BAD CUTOUT DOOR. //VER/GAH IDC XXXX
23284 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-12-14 13:14 | 2013-12-14 14:32 | 1 | 78 | 4161301 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT SERV TO CHANGE,REPAIRS MADE ALL CUST RESTORED @1432 PLEASE CLOSE TICKET THANKS.BT VER/CRB L3/HFP
23285 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2017-12-07 15:42 | 2017-12-07 17:00 | 1 | 78 | 4629051 | 78 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | splice burned up, I changed it out
23286 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-04-15 17:35 | 2012-04-15 18:14 | 2 | 39 | 4674651 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OLD CUTOUT DOOR HAS DETERIORATED.CAUSED XFMR FUSE TO BLOW.WILL REPLACE DOOR & RE-FUSE..//.REPLACED & RE-FUSED CUTOUT DOOR..POWER IS ON NOW.JRV.04/15/12 ///VER/CRB IDCC FEC49 XXXX
23287 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-06-21 18:24 | 2015-06-21 18:50 | 3 | 26 | 4632701 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 45-5685 NEW 6T FUSE BROKE REFUSED// VER/ ADH
23288 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2008-04-20 08:00 | 2008-04-20 08:26 | 3 | 26 | 52647-1 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 33401703// AT 0800 OPENED FUSE ON POLE 242-108 TO REPLACE CUTOUT ON POLE 242-340// COD-3 // CLOSED FUSE BACK IN AT 0826/VER/CRB IDC XXXX
23289 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-11-15 11:44 | 2022-11-15 12:23 | 2 | 39 | 4144301 | 78 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | Tie wire broke - phase is laying on the cross arm burning. Opened line fuses on 38830805000251 @ 11:44 to isolate. Made repairs and closed line fuses 805-251 @ 12:23. sh
23290 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2008-10-24 08:23 | 2008-10-24 09:40 | 1 | 77 | 58350-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP INSTALLED ANIMAL GUARD--REPLACED BAD CUTOUT COD-1 IDC XXXX
23291 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-02-14 10:41 | 2011-02-14 11:58 | 1 | 77 | 56756-1 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAD SERVIN FROZZEN OUT, REPLACE CONNECTION//VER/CRB IDC XXXX
23292 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2019-04-22 14:03 | 2019-04-22 15:20 | 1 | 77 | 4147711 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke. replaced cutout on pole 540-008.. power restored.. 15:20
23293 | Hazard | 3301401 | COMBS | COMBS | 2011-09-28 15:28 | 2011-09-28 16:45 | 1 | 77 | 4929341 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER//COD 1// VER/DBM IDC XXXX
23294 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2017-03-28 13:40 | 2017-03-28 14:57 | 1 | 77 | 4592121 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7.2KV CAN USE TRUCK. THIS HOUSE IS EMPTY, ALTHOUGH THE SERVICE IS ACTIVE. WE WILL REPLACE THIS TRANSFORMER TOMORROW AS PER TIM HALL.//SENT TO LINE DEPT//SERVICER SAYS ONLY 1 CUST// VER/CRB // NOTE THIS WAS REPORTED OUT BY THE MRO GROUP & NOT A CUSTOMER = L3/HFP XXXHFP
23295 | South Williamson | 3411401 | DEWEY | INEZ | 2015-07-18 21:48 | 2015-07-18 23:05 | 1 | 77 | 4909071 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK HAD BROKEN IN CUTOUT DOOR///RESTORED AT 23:05//COMPLETE//EM VER/SEF
23296 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-01-12 07:34 | 2017-01-12 08:51 | 1 | 77 | 4289551 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE C/O REPLACED--ALLGOOD--DS011217 38830162B46025VER/AWD L3/HFP HFPC CDC96
23297 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2008-02-02 20:48 | 2008-02-02 22:05 | 1 | 77 | 65739-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3202203//BAD CON BURNED 4/3 SERV DROP DOWN COD 1// VER/TOM IDC XXXX
23298 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-08-19 03:23 | 2011-08-19 04:40 | 1 | 77 | 4727941 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT ON POLE 38830351000136, REPLACED CUTOUT, ALL POWER RESTORED IDC XXXX
23299 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2019-01-28 08:46 | 2019-01-28 10:03 | 1 | 77 | 4727211 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr, made repairs restored power at 10:43..
23300 | Whitesburg | 3409503 | BURDINE | JENKINS | 2010-07-26 19:32 | 2010-07-26 20:49 | 1 | 77 | 57590-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICER ETA 20:10 // REPLACED 4/3 SERVICE WITH 2/3// VER/DBM IDC XXXX
23301 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-02-09 22:13 | 2011-02-09 23:30 | 1 | 77 | 55791-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL BROKE. RE-FUSED @ 23:30. SH.//VER/CRB IDC XXXX
23302 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-05-31 11:03 | 2011-05-31 12:20 | 1 | 77 | 4213341 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL ROTTED AND BROKE, POWER RESTORED.//VER/CRB IDC XXXX
23303 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2013-03-31 09:58 | 2013-03-31 11:15 | 1 | 77 | 4969471 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-381 CHGED BAD CUTOUT 20T POLE 68-381 12T LINE FUSE REMOVED INACTIVE TRANS .CUTOUT ON 68-890 COD-1 ISO LF 38830068B00381 VER/HFP L3/HFP IDC XXXX
23304 | Hazard | 3310502 | HADDIX | CANOE | 2015-05-08 09:18 | 2015-05-08 10:35 | 1 | 77 | 4402991 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT// VER/ ADH
23305 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-06-04 16:03 | 2008-06-04 17:20 | 1 | 77 | 56565-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3003701 LINE FUSE ON POLE 38830162D00124, 1 CUST OUT
23306 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2017-10-11 13:03 | 2017-10-11 14:20 | 1 | 77 | 4446841 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEE 4447091 FOR CKT OUTAGE TO MAKE REPAIRSBASKETBURNT @ 1124-578, NEW BSKT & HOT TAP INSTALLED VER/HFP L3/HFP ACB
23307 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2019-04-10 19:28 | 2019-04-10 20:45 | 1 | 77 | 4080131 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout
23308 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-01-22 12:43 | 2013-01-22 14:00 | 1 | 77 | 4728561 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7200 INCLOSED CUTOUT ON POLE 262-160 COD-1 ISO TF 38830262000160 VER/HFP L3/HFP IDC XXXX
23309 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-05-17 22:28 | 2009-05-17 23:45 | 1 | 77 | 61611-1 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3103101 -NO CREW REQUIRED REPLACING CONNECTION //VER/GAH IDC XXXX
23310 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-09-25 11:58 | 2018-09-25 13:15 | 1 | 77 | 4155351 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad hot tap on 975-19, have rep and all power restored at this loc at 1315 by amg
23311 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2018-10-12 09:55 | 2018-10-12 11:12 | 1 | 77 | 4240261 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired secondary hot leg burnt neu into--allgood-ds101218 L3/HFP
23312 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-06-21 21:07 | 2008-06-21 22:24 | 1 | 77 | 51622-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3408402//XFR FUSE IS OUT,WILL RE-FUSE, FUSE HAD ROTTED IN TWO, RE-FUSED CUTOUT, ALL OK AFTERWARDS VER/LDA
23313 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-06-11 23:33 | 2010-06-12 00:50 | 1 | 77 | 60508-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35538349 // POLE 92-311 CUTOUT FELL APART VER/ARN
23314 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2008-06-30 13:48 | 2008-06-30 15:05 | 1 | 77 | 60229-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JRV ON SITE @ 14:32...BROKEN CUTOUT ON LATERAL ON POLE 795-C-96.....CAN CHANGE OK...//...CUTOUT REPLACED...POWER RESTORED......JRV 06/30/08 COD-1 VER/HFP IDC XXXX
23315 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2008-02-08 11:18 | 2008-02-08 12:35 | 1 | 77 | 52705-1 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3410503//SECONDARY LUG ON TRANSFORMER IS BURNED BADLY. I AM GOING TO TRY TO TIGHTENED LUG. I TIGHTENED LUG THE BEST I COULD. TIM HALL IS GOING TO HAVE TRANS. CHANGED TOMORROW// VER/DBM IDC XXXX
23316 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2020-11-24 16:43 | 2020-11-24 18:00 | 1 | 77 | 4721041 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Secondary fire, burned in the clear. Repairs made and power restored at 18:00.
23317 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2016-03-23 19:13 | 2016-03-23 20:30 | 1 | 77 | 4875621 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED SEND A COPY TO RAYBURN AND TECH TO HAVE THIS SECONDARY AND SERVICE UPGRADED SENT TO L. RAYBURN AND TECH VER/AWD
23318 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2022-11-06 15:43 | 2022-11-06 17:00 | 1 | 77 | 4107161 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt into @ xfm///Replaced bad connection and restored full power @ 17:00
23319 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-09-18 13:43 | 2014-09-18 15:00 | 1 | 77 | 4509221 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP. REPLACED AND RESTORED @ 15:00. SH //// ISO 38830904000024/// COD 1// VER/BOW
23320 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-09-07 11:23 | 2020-09-07 12:40 | 1 | 77 | 4438991 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cut out
23321 | South Williamson | 3411401 | DEWEY | INEZ | 2008-02-10 18:55 | 2008-02-10 20:12 | 1 | 77 | 57782-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT BROKE /// VER/TOM IDC XXXX
23322 | South Williamson | 3411401 | DEWEY | INEZ | 2011-12-28 07:23 | 2011-12-28 08:40 | 1 | 77 | 4209701 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG ON SECONDARY PULLED LOOSE FROM CRIMPIT// I CLIMBED POLE AND REDID CONNECTION///RESTORED AT 8:40//COMPLETE//EM VER/KEP IDCC PN537 XXXX
23323 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2014-11-18 16:58 | 2014-11-18 18:15 | 1 | 77 | 4743191 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG BURNT INTO @ XFMR,REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT COD-1 VER/HFP L3/HFP
23324 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-08-13 12:26 | 2019-08-13 13:43 | 1 | 77 | 4879481 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | old cutout door burned up. replaced. power restored @ 13:43
23325 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-08-05 13:14 | 2017-08-05 14:31 | 1 | 77 | 4229761 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTION AT SERVICE WEATHERHEAD 38831052D00243 VER/AWD
23326 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2011-10-19 18:46 | 2011-10-19 20:03 | 1 | 77 | 4000881 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR FUSE IS OUT,WILL RE-FUSE///////APPEARS FUSE ROTTED INTO,RE-FUSED AND RESTORED ///VER/CRB IDC XXXX
23327 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2012-05-28 11:28 | 2012-05-28 12:45 | 1 | 77 | 4837291 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE CUT-OUT DOOR TRIED TO CARRY LOAD BURNT INTO RELACED AND POWER WAS RESTORED//COD 1// VER/DBM IDC XXXX
23328 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-04-03 19:43 | 2012-04-03 21:00 | 1 | 77 | 4644791 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER KICKED OFF..RE SET BACK ON NOW. MILLER WILL CHG TOMORROW VER/KEP IDC XXXX
23329 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-08-22 18:32 | 2019-08-22 19:49 | 1 | 77 | 4932771 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced c/o--allgood-ds082219
23330 | Hazard | 3309302 | VICCO | JEFF | 2015-02-24 14:47 | 2015-02-24 16:04 | 1 | 77 | 4078701 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BAD ON XFMR, REPAIRED CONNECTION// VER/DBM
23331 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-02-18 17:53 | 2011-02-18 19:10 | 1 | 77 | 59008-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED BACK CUTOUT DOOR//VER/CRB IDCC FEC49 XXXX
23332 | South Williamson | 3411401 | DEWEY | INEZ | 2016-01-18 22:08 | 2016-01-18 23:25 | 1 | 77 | 4630211 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP BURNED INTO//REPAIRS MADE//RESTORED AT 23:25//COMPLETE//EM VER/CRB
23333 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-12-31 16:48 | 2016-12-31 18:05 | 1 | 77 | 4259411 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SQEEZE ON BURNT OFF OF SERVICE DROP /// MADE REPAIRS EVERYTHING OK NOW 123/123/246// ONLY 1 CUSTOMER AFFECTED VER/CRB
23334 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-09-21 21:04 | 2015-09-21 22:21 | 1 | 77 | 4258461 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION ON TRANSFORMER
23335 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-05-30 10:25 | 2009-05-30 11:42 | 1 | 77 | 51302-1 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3103101//NO CREW REQUIRED REPAIRING BROKEN NEUTRAL VER/JHM
23336 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-01-19 00:02 | 2020-01-19 01:19 | 1 | 77 | 4320011 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse open on pole 222-562. The fuse had pulled apart, not blown. Power restored at 01:19 L3/HFP
23337 | Pikeville | 3421002 | BREAKS | GRASSY | 2022-03-09 16:43 | 2022-03-09 18:00 | 1 | 77 | 4594841 | 77 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Neutral connection burnt into will be making repairs///Repaired neutral and restored full power @ 18:00///124/124/248//Only 1 customer affected
23338 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2022-06-10 09:34 | 2022-06-10 09:45 | 7 | 11 | 4053161 | 77 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changed bad cut out complete
23339 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-10-20 10:39 | 2008-10-20 11:55 | 1 | 76 | 57271-1 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | VER/HFP WIRE BURN-INTO ON SECONDARY,OPEN TRANSFORMER AT 11:40, SEND TICKET TO RON RYE CREW TO HAVE A TECT WRITE A JOB TO UPGRADE SECONDARY TO 1/0 /// COD-3 NEED OUTAGE FOR 2 CUST CREATED IN HOIS IDC XXXX
23340 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-10-20 19:23 | 2008-10-20 20:39 | 1 | 76 | 57478-1 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT POLE, VOLTAGE 120, 90//3001002//VER/CRB IDC XXXX
23341 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-07-21 14:15 | 2013-07-21 15:31 | 1 | 76 | 4569581 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 078S08--BROKEN FUSE LINK VER/CRB L/3 CRB IDC XXXX
23342 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2013-03-24 21:56 | 2013-03-24 23:12 | 1 | 76 | 4952871 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 1// VER/DBM IDC XXXX
23343 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-04-21 12:39 | 2011-04-21 13:55 | 1 | 76 | 61725-1 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT IT WAS OLD AND LOOKED LIKE IT HAD A CRACK IN IT ALL POWER RESTORED AT 1355 CLOSE TICKET COD-1 ISO TF 38830547000048 VER/HFP L3/HFP IDC XXXX
23344 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2016-07-11 11:37 | 2016-07-11 11:56 | 4 | 19 | 4609261 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW FOUND BAD XARMS ON POLE 893-A-237// COD 4 //OPENED @ 1137 // CLOSED @ 1156// VER/DBM
23345 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-09-30 12:49 | 2016-09-30 14:05 | 1 | 76 | 4948421 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW ON SITE/BAD XFMR/OPENING FUSE 38830501C11521/APROX ONE HOUR OUTAGE/VEM/OPEN FUSE AT 1249/POWER RESTORED RESTORED TO ALL CUST 1405/PLEASE CLOSE TICKET/THANKS/VEM/ VER/BOW
23346 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2022-08-06 11:20 | 2022-08-06 12:36 | 1 | 76 | 4691321 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got cut out changed and customer back on at 12:35canged cutoud got customer on at 12:36
23347 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-12-26 22:44 | 2021-12-27 | 1 | 76 | 4228611 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repaired connection
23348 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2020-03-24 06:56 | 2020-03-24 08:12 | 1 | 76 | 4504311 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 38830206B02016,,,opened xfr bank to replace connections opened @ 07:42 closed @ 08:12206-2016,,,opened xfr bank to replace connections opened @ 07:42 closed @ 08:12
23349 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-03-14 08:47 | 2012-03-14 10:03 | 1 | 76 | 4577671 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE-IN PULLED APART ON POLE,WILL REPAIR///////////MADE NECESSARY REPAIRS,ALL OK AFTERWARDS// VER/DBM IDC XXXX
23350 | Hazard | 3303902 | LESLIE | WOOTON | 2011-05-29 13:13 | 2011-05-29 14:29 | 1 | 76 | 4206211 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BA D NEUTRAL CONNECTION VER/HFP L3/HFP IDC XXXX
23351 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2012-10-08 15:31 | 2012-10-08 15:50 | 4 | 19 | 4124071 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN XFMR FUSE, REPLACED FUSE, ALL POWER RESTORED COD-4 ISO TF 38830183D00150 VER/HFP L3/HFP IDC XXXX
23352 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-12-31 21:41 | 2009-12-31 22:57 | 1 | 76 | 54157-1 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN TRANSFORMER FUSE...CHG 6 T FUSE BB VER/KEP L3/KEP IDC XXXX
23353 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-10-26 10:44 | 2014-10-26 12:00 | 1 | 76 | 4662281 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | COULD NOT FIND ANCHOR, GUY WIRE WAS LOOSE FROM ANCHOR. REMOVED DOWN GUY FROM POLE TEMP, UNTILL LINECREW CAN REPLACE ANCHOR TRUCK OK. PLEASE SEND TO STEVE M. REFUSED XMF APR AT 1200 CLOSE TICKET VER/CRB VER/DKG L3/DKGXXXX
23354 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-10-01 18:50 | 2010-10-01 20:06 | 1 | 76 | 56112-1 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE PHASE OF THE PRIMARY UG IS IN TROUBLE HERE WE WILL WORK IT ON OPS ORDER #030308430 AS PER D. MASSEY. RELEASED BY CREW 074S02 //VER/CRB IDC NOT SURE WHERE THE FUSES ARE SO I AM NOT SURE IF IT IS A DIP FUSE OR LINE FUSE XXXX
23355 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-11-02 08:45 | 2021-11-02 10:01 | 1 | 76 | 4048571 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 10:01. sh
23356 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2017-10-02 08:59 | 2017-10-02 10:15 | 1 | 76 | 4403891 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | **SEE H4403891** POLE 1148-186 BAD CONN. ON POLE REPAIRED/ OPENED XFMR 0955-1015/ ISO 39831148A00186/ COD 7/ VER/BOW L3/HFP XXXHFP
23357 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-08-29 08:29 | 2020-08-29 09:45 | 1 | 76 | 4397981 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | fouond bad conn. at mast, bad split bolt, have rep, and transformer bank closed back in at 0945, all is good at this loc
23358 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-12-24 22:34 | 2019-12-24 23:50 | 1 | 76 | 4180511 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | service connection had bare spot and burnt service into//cod 1//
23359 | South Williamson | 3200302 | BELFRY | TOLER | 2008-12-22 21:44 | 2008-12-22 22:03 | 4 | 19 | 62784-1 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3200302//CENTER MAIN-LINE CUTOUT IS BREAKING DOWN AND NEEDS TO BE REPLACED.MARCUM IS ENROUTE WITH CREW//CUTOUT BURNED THROUGH AND OUTAGED MIDDLE PHASE @ 2144 (COD 4)//REPLACED BAD CUTOUT AND RESTORED,ALL OK AFTERWARDS// VER/DBM L3/KEP IDC XXXX
23360 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-12-15 12:44 | 2011-12-15 14:00 | 1 | 76 | 4179501 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE6T FUSE BROKE. FUSED UP EVERYTHING OK. SEND COPY TO ROW PIKEVILLE ROW IS COVERED UP NEEDS CUT FROM POLE 141-58 TO POLE 141-108. VER/KEP IDC XXXX
23361 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-09-15 18:04 | 2015-09-15 19:20 | 1 | 76 | 4241181 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN LINE FUSE CUTOUT ON POLE 38830307000077 VER/CRB
23362 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-10-27 17:41 | 2017-10-27 18:57 | 1 | 76 | 4504211 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED CUTOUT. VER/AWD L3/HFP XXXHFP
23363 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-09-18 15:45 | 2016-09-18 17:01 | 1 | 76 | 4904221 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED 6T TRANSFORMER FUSE UP AT 15:45 REPLACED BAD CUTOUT AND CLOSED TRANSFORMER FUSE BACK IN AT 16:48 EVERYTHING OK VER/CRB
23364 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-01-29 13:44 | 2014-01-29 15:00 | 1 | 76 | 4324611 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION IN SERVICE AND REPLACED CRACKED CUTOUT AT TRANSFORMER. OPENED TRANSFORMER AT 14:24, CLOSED AT 15:00, POWER RESTORED. DUP FOR 2 WHEN TR OPENED /// COD-3 ISO TF 37830272A40446 VER/HFP L3/HFP
23365 | Whitesburg | 3309302 | VICCO | JEFF | 2010-01-26 14:03 | 2010-01-26 15:19 | 1 | 76 | 60128-1 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE PULLED OUT OF NEUTRAL IN SERVICE, MADE REPAIRS RESTORED POWER AT 15:17 VER/HFP L3/HFP IDC XXXX
23366 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-03-20 14:08 | 2012-03-20 15:24 | 1 | 76 | 4598451 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LIGHTNING ARRESTOR ON POLE 1145-192, TOOK OUT LINE FUSE ON POLE 1145-13, LINE FUSE CUTOUT WAS BAD, HAD TO CHANGE IT SEND TO MR RAYBURN TO HAVE L/A REPLACED AT A LATER DATE ///VER/CRB IDC XXXX
23367 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-07-26 23:08 | 2016-07-26 23:46 | 2 | 38 | 4685371 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTOMERS NEUTRAL IS BROKE ON THEIR SERVICE, THIS POLE IS UP ON THE HILL, I WILL HAVE TO OPEN THEIR TRANS. AT POLE 25-15 TO MAKE REPAIRS, I WILL KEEP TRACK OF TIMES. OPENED @ 2308 AND CLOSED BACK IN @2346. VER/CRB
23368 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2020-09-24 09:44 | 2020-09-24 11:00 | 1 | 76 | 4491201 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | crew on site to repair ug service. power temp was installed over weekend 9/19 at this location. 1 customer will be out of power LRM fetr 13:00 all pwr restored @ 11:00 please close ticket LRM
23369 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2017-07-19 20:53 | 2017-07-19 22:09 | 1 | 76 | 4144621 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CUSTOMER IS LETTING US WAIT UNTIL MORNING TO MAKE REPAIRS MADE A IWA1 OPS #036767475 SENT OPS ORDER TO DENNIS MASSEY VER/CRB
23370 | Pikeville | 3402003 | KEYSER | MULLINS | 2018-06-14 09:16 | 2018-06-14 09:35 | 4 | 19 | 4600771 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse tail pulled into on trans. pole 1151-A-599, refused @0935./ ISO 38831151A00599/ COD 4
23371 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-12-20 17:56 | 2016-12-20 19:12 | 1 | 76 | 4225521 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE VER/CRB
23372 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-07-10 17:48 | 2010-07-10 19:04 | 1 | 76 | 64913-1 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | METER # 533729512, SERV-IN PULLED APART, ONLY ONE CUSTOMER AFFECTED / ALL WORK COMPLETE / GXJ//ISO// VER/DBM IDC XXXX
23373 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-04-03 17:34 | 2010-04-03 18:50 | 1 | 76 | 58264-1 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE. REPLACED CUTOUT IN XFMR BANK AND RESTORED SERVICE @ 18:50. SH VER/KEP L3/KEP IDC XXXX
23374 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-08-28 12:29 | 2010-08-28 13:45 | 1 | 76 | 61490-1 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE DOOR BURNT IN HALF; REPLACED DOOR; PWR RESTORED AT 1345HRS; CLOSE TICKET VER/KEP L3/KEP IDC XXXX
23375 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-11-08 09:17 | 2014-11-08 10:33 | 1 | 76 | 4713131 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP TO REPAIR////////SERV HAD SHORTED OUT,BURNED INTO////// SERVICE BURNT INTO 3 TIMES/ MADE NECESSARY REPAIRS,ALL OK AFTERWARDS/////BURNED INTO AGAIN,WILL REPLACE AGAIN.CUST HAS PROBLEM,TOLD TO GET ELECTRICIAN TO REPAIR,THEN CALL US BACK/ 2 CUSTOMERS SHARING 1 METER HERE/ CUSTOMER TROUBLE AFTER SERVICE DROP REPAIR/ WILL NEED TO CALL IN FOR TRANSFORMER RECONNECT/ ISO 38821105C00331/ COD 1/ VER/BOW AJB
23376 | South Williamson | 3200302 | BELFRY | TOLER | 2011-05-04 20:54 | 2011-05-04 22:10 | 1 | 76 | 4010241 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION HAS BURNT SERVICE DROP UP....1 HOT LEG & NUETRAL IN TWO....WILL REPAIR..//...CUT OUT BAD INSULINK CONNECTIONS & SLICED SERVICE....POWER ON ....ONLY 1 CUST AFFECTED...JRV....05/04/11//VER/CRB IDC XXXX
23377 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-02-09 20:26 | 2017-02-09 21:42 | 1 | 76 | 4381821 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION BURNT UP ON 1129B287 REPLACED BOTH CONNECTIONS ON ENERGIZED CONDUCTORS RESTORED 21:42 38821129B00287 VER/AWD L3/HFP XXXHFP
23378 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-11-20 17:29 | 2022-11-20 18:45 | 1 | 76 | 4166501 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse melted out.. changing fuse
23379 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-12-14 23:09 | 2015-12-15 00:25 | 1 | 76 | 4533101 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY RISER CAME OUT OF XFMR . MADE REPAIRS// VER/DBM
23380 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-02-08 12:04 | 2011-02-08 13:20 | 1 | 76 | 55294-1 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN ON POLE 38830454B33009 BAD ALL POWER RESTORED AT 1320 CLOSE TICKET VER/KEP IDC XXXX
23381 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-03-20 09:04 | 2017-03-20 10:20 | 1 | 76 | 4571501 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, BROKE CUTOUT, REPLACED CUTOUT, POWER RESTORWED COD-1 ISO PO @ 37830302D00142 VER/HFP L3/HFP
23382 | Hazard | 3303902 | LESLIE | WOOTON | 2019-11-20 15:11 | 2019-11-20 16:27 | 1 | 76 | 4051651 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse, broke cutout phillip hicks will come and change Released by crew 077H14 (REPLACED ORDER 4051221 THAT WAS ACCIDENTLY CLOSED)xfmr fuse, broke cutout phillip hicks will come and change Released by crew 077H14, changed cutout, arr, and brkt. p.hicks..all power restored @ 16:27
23383 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-06-11 07:44 | 2009-06-11 09:00 | 1 | 76 | 57000-1 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT DOOR, REPLACED POWER OK. COD-1 ISO 38830282000018 L3/HFP IDC XXXX
23384 | Pikeville | 3413401 | GARRETT | GARRETT | 2020-11-17 18:04 | 2020-11-17 19:20 | 1 | 76 | 4703061 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t transformer fuse out looks like fuse broke or melted out fused up everything ok
23385 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-12-17 23:23 | 2013-12-18 00:39 | 1 | 76 | 4171671 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1098-500 BAD CUTOUT 1-CUST ON TRANS. RELEASED BY CREW 078S08 //VER/GAH L3/HFP
23386 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-07-06 16:35 | 2010-07-06 17:51 | 1 | 76 | 62720-1 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 35869643 // BAD CONN. AT 4/3 SERVICE BURNT INTO VER/HFP L3/HFP IDCC FP NONE XXXX
23387 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-09-09 14:25 | 2011-09-09 15:41 | 1 | 76 | 4852131 | 76 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION VER/HFP L3/HFP
23388 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-01-01 10:34 | 2008-01-01 11:50 | 1 | 76 | 52394-1 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3116102//SPLICE CAME APART AT POLE 38830182B43559, GOING TO OPEN XFMR TEMPORARILY TO MAKE REPAIRS. XFMR OFF AT 11:47, ON AT 11:50 IDCC TOF1147 XXXX
23389 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-01-21 20:14 | 2021-01-21 21:30 | 1 | 76 | 4884121 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | customer had a bad meter, changed his meter out// ROW needs cut at pole 1102-17/ ISO 38831102000017/ COD 1/ off 2121 on 2130. LR- All out call came in at 20:14
23390 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-05-03 07:24 | 2016-05-03 08:40 | 1 | 76 | 4167801 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR./ ISO 38830185000211/ COD 1/ VER/BOW
23391 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-06-03 20:39 | 2014-06-03 21:55 | 1 | 76 | 4967471 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT AND REMOVED BAD EXTRA ARRESTER NEW ONE IS ON XMF, APR AT 2155 CLOSE TICKET COD-1 38830478B20074 VER/HFP L3/HFP
23392 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2020-07-10 22:14 | 2020-07-10 23:30 | 1 | 76 | 4149271 | 76 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | bad current liminting fuse all pwr restored 23:30 please close ticket LRM
23393 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-02-04 23:50 | 2010-02-05 00:15 | 3 | 25 | 63135-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED A BAD TRANS//WR#33752238// CHANGING TRANSFORMER//OPENED TRANS AT 2350 CLOSED AT 0015// COMPLETE I HOPE TT //VER/GAH IDC XXXX
23394 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2015-06-08 09:51 | 2015-06-08 11:06 | 1 | 75 | 4523431 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COMPANY CREW CHANGING BAD CUTOUT AND ARRESTOR////TBL TKT COMP.. RELEASED BY CREW 078H16 VER/CRB
23395 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2017-05-04 19:40 | 2017-05-04 19:55 | 5 | 15 | 4745941 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SEND BACK RELEASED BY CREW 078S08SEND TO LUKE ON SITE FETR 19:55 OPENED XFMR @ 19:40 IN @ 19:55 PLEASE CLOSE TICKET 38830045B22759 VER/AWD
23396 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-12-17 14:40 | 2014-12-17 15:05 | 3 | 25 | 4866861 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED ON POLE 37830379B00184, SERVICER OPENING ON POLE 37830379B00182TO SAFELY MAKE REPAIRS// I OPENED LINE TAP ON POLE 379-182 AT 14:40 AND PUT BACK ON AT 15:05/COD3// VER/CRB
23397 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-09-11 14:45 | 2020-09-11 16:00 | 1 | 75 | 4452301 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | current limiting fuse went bad. installed new one power restored at 1600
23398 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2017-12-14 17:45 | 2017-12-14 19:00 | 1 | 75 | 4650661 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse out on 38821065B00079 re-fused cutout restored power at 19:00
23399 | Whitesburg | 3312901 | JENKINS | KONA | 2019-05-31 11:50 | 2019-05-31 13:05 | 1 | 75 | 4396711 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout was broke into , I changed it out
23400 | Hazard | 3303902 | LESLIE | WOOTON | 2014-11-03 13:05 | 2014-11-03 14:20 | 1 | 75 | 4696431 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT GATE/ ISO 37830462000166/ COD 1// VER/BOW
23401 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-02-27 13:35 | 2010-02-27 13:50 | 5 | 15 | 61563-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION ON OPEN WIRE SECONDARY; PWR RESTORED; CLOSE TICKET VER/HFP L3/HFP IDCC TOF1224 DIM LIGHTS ALLOWED 15 MIN FOR REPAIR XXXX
23402 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-03-31 12:28 | 2022-03-31 13:43 | 1 | 75 | 4703911 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout in the process of changing cutout/////// apr at 1343 close ticket
23403 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2012-02-10 13:30 | 2012-02-10 14:45 | 1 | 75 | 4332731 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | I REPLACED 4/3 SERVICE DROP WITH 2/3 DROP THIS IS A 200AMP CUST . ONE HOT SIDE BURNT OPEN. REPAIRS MADE EVERYTHING OK///VER/CRB VER/HFP L3/HFP IDC XXXX
23404 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2018-07-16 12:10 | 2018-07-16 13:25 | 1 | 75 | 4780311 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed at weatherhead. Replaced connections and restored @ 13:25. sh L3/HFP
23405 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-09-11 21:55 | 2013-09-11 22:10 | 5 | 15 | 4840121 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND SECONDARY OPEN ON TRANSFORMER HAD TO OPEN UP TRANSFORMER, OPENED AT 955, CLOSED BACK IN AT 1010, BAD CONNECTION ON THE RISER OF THE TRANSFORMER, EVERYTHING IS OK AT THIS LOC NOW VER/CRB L/3 CRB
23406 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2012-06-16 08:53 | 2012-06-16 10:08 | 1 | 75 | 4920021 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 1// VER/DBM IDC XXXX
23407 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2020-03-09 19:55 | 2020-03-09 21:10 | 1 | 75 | 4464211 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | refused cutout
23408 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-07-17 16:35 | 2020-07-17 16:50 | 5 | 15 | 4175691 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced cut-out on pole 37830361000108 Opened @ 16:35 Closed @ 16:50
23409 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-02-04 14:55 | 2022-02-04 16:10 | 1 | 75 | 4442261 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 263-16 will be making repairs//Changed bad cutout and restored @ 16:10
23410 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-01-14 21:57 | 2017-01-14 23:12 | 1 | 75 | 4299091 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT HAS BROKEN DOWN,WILL REPLACE IT////////REPLACED CUTOUT&RESTORED POWER//COD 1 L3/HFP
23411 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-09-07 11:40 | 2010-09-07 12:05 | 3 | 25 | 64143-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTORS MELTED OUT ON XFMR, WILL HAVE TO OPEN UP XFMR TO REPAIR.OPENED XFMR AT 11:40, BACK ON AT 12:05, COMPLTED /// COD-3 VER/HFP L3/HFP IDC XXXX
23412 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-06-18 08:30 | 2019-06-18 09:45 | 1 | 75 | 4534811 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | P MUNCY ///customer mismapped//problems here 911 addresses//trouble is on pole 794-c-4//lateral fuse cutout broke here//back on hillcustomer mismapped//problems here 911 addresses//trouble is on pole 794-c-4//lateral fuse cutout broke here//back on hill Released by crew 079S01
23413 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2022-01-03 09:11 | 2022-01-03 10:26 | 1 | 75 | 4270301 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | riser fuse out on 1152-B1-357// checking Cutout gate burned up and caused fuse to blow inside pad mount XFM, changed fuses and restored @ 11:10
23414 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2016-08-10 12:00 | 2016-08-10 13:15 | 1 | 75 | 4757941 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE ON XFMR BANK POLE// REFUSED XFMR POWER RESTORED// VER/ ADH
23415 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-10-07 17:25 | 2019-10-07 17:40 | 5 | 15 | 4113151 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke will make repair Open 1725 Close 1740/cod-5/37820194A00007
23416 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-29 13:25 | 2016-02-29 13:40 | 5 | 15 | 4788231 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION @ XFMER.. NEW CONNECTION COMP. OFF @ 13:25, ON @ 13:40/ ISO 38830093B00227/ COD 5/ VER/BOW
23417 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-11-30 12:15 | 2022-11-30 13:30 | 1 | 75 | 4210371 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | tran lead come out of c/o--repaired at 13:30--allgood-ds113022
23418 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-02-10 13:45 | 2009-02-10 15:00 | 1 | 75 | 57376-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308502//NOT 2 CUSTOMER OUTAGE, THIS IS FOR CITY OF HAZARD, UNMETERED ACCT// BAD CUTOUT ON TRANSF POLE == REPAIRED ==//VER/CRB
23419 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-04-23 17:45 | 2017-04-23 18:00 | 5 | 15 | 4671681 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPICES BAD IN SECONDARY SPAN, GOING INTO COMPANY FOR NEW WIRE AND MATERIAL..ALL POWER RESTORED AT 18:00 HRS.P.HICKS 37830180000053 OFF FROM 1745 TO 1800. VER/AWD L3/HFP XXXHFP
23420 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-03-09 08:39 | 2016-03-09 09:54 | 1 | 75 | 4829471 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | KEN COLEMAN (TELECOM) REPORTS LINE FUSE OPEN FOR VVO REPEATER//////////XFR TO RE-FUSE/////////RE-FUSED AND RESTORED,ALL OK AFTERWARDS///////FUSE APPEARED TO HAVE BROKEN/ ISO 38821057D00060/ COD 1/ VER/BOW
23421 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-12-23 19:10 | 2014-12-23 19:25 | 5 | 15 | 4877751 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT,GOING TO CHANGE//// OPENED CUTOUT AT 19:10 CLOSED BACK IN AT 19:25, POWER RESTORED// COD 5
23422 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-09-16 15:30 | 2010-09-16 15:55 | 3 | 25 | 50666-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT OFF AT 1530 ON AT 1555 COD-3//VER/CRB IDC XXXX
23423 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-04-19 15:45 | 2012-04-19 17:00 | 1 | 75 | 4687541 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL PULLED OUT OF TENSION SPLICE... HEAVY EQUIPMENT WORKING NEAR POLE.. REPLACED ENTIRE SERVICE DROP.. ///VER/CRB IDCC TOF1245, ESTIMATED TIME OFF XXXX
23424 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-07-03 10:30 | 2019-07-03 11:45 | 1 | 75 | 4646001 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required broken hottap
23425 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-09-02 12:00 | 2021-09-02 13:15 | 1 | 75 | 4202071 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DAE # 1000060354 crew trying to make repairs on bad ug. installed PT on 9/1 LRM fetr 13:50 off @ 12:00 in at 13:15 please close LRM//Located fault but will have to come back to make repairs--customer advised
23426 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-09-16 11:35 | 2020-09-16 12:50 | 1 | 75 | 4468771 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse link was broke. replaced fuse
23427 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-12-20 23:24 | 2016-12-21 00:39 | 1 | 75 | 4225801 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE//COD 1
23428 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2012-05-22 07:00 | 2012-05-22 08:15 | 1 | 75 | 4816431 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE, ALL POWER RESTORED ///VER/CRB L/3 CRB IDC XXXX
23429 | Paintsville | 3401802 | INDEX | HOSPITAL | 2020-03-31 03:00 | 2020-03-31 03:25 | 3 | 25 | 4547261 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout.. opened xfmr at 3:00 back on at 3.25.
23430 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-05-24 20:40 | 2013-05-24 21:05 | 3 | 25 | 4181991 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN NEUTRAL ON POLE 158-13 OPENED XFMR @ 20:40 CLOSED BACK IN @ 21:05 COD-3 ISO TF37830158000013 VER/HFP L3/HFP IDC XXXX
23431 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2013-04-08 08:45 | 2013-04-08 10:00 | 1 | 75 | 4986911 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND LEAD BURNTED OF BOTTOM OF LINE FUSE CUTOUT ON POLE 1098-4002, I HAVE REPAIRS MADE AND POWER IS RESTORED AT THIS LOC AT 1000//COD 1//ISO 39831098C04002// VER/DBM IDC XXXX
23432 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-02-02 14:35 | 2015-02-02 15:50 | 1 | 75 | 4984611 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER , BAD CONNECTION AT TRL POLE, MADE REPAIRS RESTORED POWER AT 15:50, ONLY ONE CUSTOMER AFFECTED// VER/ ADH L3/HFP XXX
23433 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-21 17:30 | 2011-01-21 18:45 | 1 | 75 | 63461-1 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED A BAD CONNECTION AT THE TRANSFORMER ON ONE HOT LEG OF THE SERVICE. VER/KEP L3/KEP IDC XXXX
23434 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2017-01-14 13:10 | 2017-01-14 13:25 | 5 | 15 | 4297631 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ***SEE 4297591*** OPENING LINE FUSE TO REPLACE TRANSFORMER 38830810D00074/ ISO 38830810D00052/ COD 5/ OPENED @1310/ CLOSED 1325/ VER/BOW L3/HFP HFP
23435 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2013-11-09 10:50 | 2013-11-09 12:05 | 1 | 75 | 4024001 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK 6T 1 CUSTOMER/CORECTION ON POLE NUMBER IS 181D95//COD 1//MD FILED//ISO// VER/DBM
23436 | Pikeville | 3413401 | GARRETT | GARRETT | 2020-08-07 11:28 | 2020-08-07 12:43 | 1 | 75 | 4298891 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t fuse out looks like fuse broke or maybe melted out fused up everything ok
23437 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-11-20 17:20 | 2010-11-20 17:35 | 5 | 15 | H58383-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 37840541 // OPENED LINE FUSE @ 1720 STS WR# 37840541 // REPLACED BAD CUT OUT DOOR. DUPLICATE FOR 58383-1 COD-7 VER/HFP L3/HFP IDC XXXX
23438 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2010-04-07 12:33 | 2010-04-07 13:48 | 1 | 75 | 60241-1 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BROKEN HOT TAP LEAD-CALLED CWT TO ASSIST BTCOM VER/HFP L3/HFP IDC XXXX
23439 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-12-07 11:15 | 2018-12-07 12:30 | 1 | 75 | 4515281 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | blackburm 279 connection failed on secondary hot leg on transformer,customer states some equiment not working correctly,only one customer affected L3/HFP
23440 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2018-03-04 10:36 | 2018-03-04 11:51 | 1 | 75 | 4959831 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on a hot leg,customer said heat pump might be damage,
23441 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2016-02-11 09:50 | 2016-02-11 11:05 | 1 | 75 | 4688661 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE WIRE NEUTRAL BURNED IN TWO.REPLACED 75 OF 2/3 SEVICE WIRE . TESTED VOLTAGE 120/240. ISO 38830067B00231 COD 1 ESTIMATED TIME OFF. VER/AWD
23442 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2017-05-27 13:45 | 2017-05-27 14:10 | 3 | 25 | 4869991 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED 1 MAN AND R/W CREW//BAD NETURAL CONNECTIONS ON TRANSFORMER POLE,REMADE ALL CONNECTIONS//OPEN TRANSFORMER AT 13:45 AND CLOSE AT 14:10 VER/CRB
23443 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-03-03 12:20 | 2011-03-03 13:35 | 1 | 75 | 66152-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S11// P R TOLLIVER ON SITE//REPLACED CUT OUT AND ARRESTOR// DONE DWAYNES WORK AGAIN P R TOLLIVER VER/KEP IDC XXXX
23444 | Hazard | 3309302 | VICCO | JEFF | 2018-02-01 11:15 | 2018-02-01 11:40 | 3 | 25 | 4789271 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew opening transformer to replace cutout breaking down/ ISO 37830348D00113/ COD 3/ open 11:15 closed at 11:40
23445 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-03-09 16:15 | 2012-03-09 17:30 | 1 | 75 | 4567591 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE OF THE PHASES OF THE SERVICE DROP. ONLY ONE CUSTOMER AFFECTED. VER/HFP L3/HFP IDC XXXX
23446 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-02-16 10:45 | 2015-02-16 12:00 | 1 | 75 | 4032481 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRL POLE, MADE REPAIRS RESTORED POWER AT 12:00./ ISO 37830447000186/ COD 1 VER/HFP L3/HFP
23447 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2021-05-29 14:50 | 2021-05-29 15:15 | 3 | 25 | 4646851 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had to replace bad cutout and arrestor, pulled power off at 14:50, put back on at 15:15
23448 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-10-21 09:45 | 2011-10-21 11:00 | 1 | 75 | 4007161 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACE TRANSFORMER OPENED TRANSFORMER AT 0945 CLOSED IN AT 1100 COD-1 ISO TF 37830378B00109 VER/HFP L3/HFP IDC XXXX
23449 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-06-04 20:55 | 2011-06-04 22:10 | 1 | 75 | 4232281 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | VER/TOM L3/TOM IDC XXXX
23450 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-06-22 16:00 | 2014-06-22 16:25 | 3 | 25 | 4138331 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAD NEUTRAL BROKEN ON 4/3 SERVICE HAD TO OPEN TRANSFORMER AT 1600, CLOSED BACK INT AT 1625, POWER IS RESTORED AT THIS LOC AND EVERYTHING IS OK, VER/CRB
23451 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-01-12 13:51 | 2022-01-12 15:06 | 1 | 75 | 4339831 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WAITING ON GUY TO COME&OPEN GATE SO I CAN GET UP HOLLOW TO FUSE/////////XFRF WAS OUT///////RE-FUSED&RESTORED/////////NO EVIDENT REASON FOUND
23452 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-10-19 22:33 | 2008-10-19 23:48 | 1 | 75 | 57130-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN 6T FUSE VER/ARN IDC XXXX
23453 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-06-26 15:45 | 2012-06-26 16:10 | 3 | 25 | 4964771 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING CUTOUT AT POLE 926-76 LOOSE CONNECTIONS AT TRANSFORMER OFF AT 15:45 ON AT 16:10 ///VER/CRB L/3 CRB
23454 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-05-03 09:24 | 2019-05-03 10:39 | 1 | 75 | 4207151 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout door burnt up/FETR1130/vem/replaced cutout door power restored to all cust 1039/please close ticket/thanks/vem
23455 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-02-03 09:30 | 2014-02-03 09:45 | 5 | 15 | 4342951 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN XFORM O 117- 215 MAKE REPAIRS ON SEC. OPEN 09;30 ON 09:45 POWER RESTORED VER/CRB
23456 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-11-11 17:10 | 2014-11-11 17:25 | 5 | 15 | 4720321 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANS OFF @ 17:10 ON AT 17:25 TIGHTEN ALL CONN. TOLD CUST TO CALL BACK IN IF MORE TROUBLES PLEASE CLOSE TICKET THANK YOU LRM VER/CRB
23457 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-10-27 19:25 | 2022-10-27 20:40 | 1 | 75 | 4072811 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | Changed meter out.
23458 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-01-05 20:15 | 2011-01-05 21:30 | 1 | 75 | 59043-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMER REPLACED// VOLTAGE 125.8//251/// OFF@20:15 ON @21:30 J. HEMLEPP 078H05 WR# 38331508 INSTALLED RECORDING VOLT METER PER. G. BELL // COD 1// VER/DBM IDC XXXX
23459 | Pikeville | 3410602 | E.PRESTON | LANCER | 2009-03-09 09:29 | 2009-03-09 10:44 | 1 | 75 | 56480-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP COD-1 FUSE LINK BROKE ON @ 1040 L3/HFP IDC XXXX
23460 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2016-03-09 10:04 | 2016-03-09 11:19 | 1 | 75 | 4830171 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE IN SERVICE DROP , MADE REPAIRS RESTORED POWER AT 11:19..ONLY CUSTOMER AFFECTED./ ISO 37830354000043/ COD 1/ VER/BOW
23461 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-08-29 20:50 | 2019-08-29 22:05 | 1 | 75 | 4963431 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o. pole 1124-2043 Released by crew 078S07/ xfmr opened @ 2150/ xfmr in @ 2205/ please close ticket/ MLH
23462 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2012-12-09 12:15 | 2012-12-09 13:30 | 1 | 75 | 4453921 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD TRANSFORMER CUTOUT, HAD CHANGED OUT AND POWER IS RESTORED AT THIS LOC AT 1330//COD 1// VER/DBM IDC XXXX
23463 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-02-20 12:50 | 2010-02-20 13:05 | 5 | 15 | H59329-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BROKEN//COD 5//PHASE C CUTOUT BROKE//HAD TO OPEN OTHER PHASE (PHASE A) @ 12:50// RESTORED ALL CUSTOMERS @ 13:05 ... ALL WORK COMPLETE / GXJ IDCC CNT21 ONLY ONE PHASE OUT INITIALLY XXXX
23464 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-04-16 18:30 | 2010-04-16 19:45 | 1 | 75 | 63990-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 34713056 //ON SITE CKING TROUBLE == CHANGE SERV OUT == POWER OK VER/HFP L3/HFP IDC CHANGED TIME OFF FROM 1727 ASSUMING POWER ON TIL WE ARRIVED XXXX
23465 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-04-28 14:15 | 2010-04-28 15:30 | 1 | 75 | 52479-1 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN 4/0 SERVICE DROP, REPAIRED// VER/DBM IDC XXXX
23466 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-10-30 10:20 | 2019-10-30 10:45 | 3 | 25 | 4218061 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | customer says that all power in the home is affected when turning even small appliances on// bri/dim condition, possible lost neutral // advised cust to turn off main breaker but customer was reluctant to do so, unsure if they will or not // opened xfmr at 10:20 closed AT 10:45
23467 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-01-29 21:51 | 2016-01-29 23:06 | 1 | 75 | 4659211 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT APR AT 2206 CLOSE TICKET// VER/ ADH L3/GDK
23468 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-06-21 21:00 | 2020-06-21 22:15 | 1 | 75 | 4056251 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout. made repairs customer restored at 22:15
23469 | Pikeville | 3413402 | GARRETT | LACKEY | 2009-02-15 21:50 | 2009-02-15 23:05 | 1 | 75 | 62275-1 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3413402// RISER WIRE BURNT OUT OF TRANSFORMER I WILL BE MAKING REPAIRS. I HAVE MADE REPAIRS CUST ARE BACK ON. VER/KEP L3/KEP
23470 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-04-15 19:00 | 2015-04-15 20:15 | 1 | 75 | 4323581 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN SERVICE HAS PULLED APART WILL REPAIR/// REPAIRED BAD NEUTRAL SPLICE IN SERVICE/// ONLY 1 CUSTOMER AFFECTED/// NO ONE HOME LEFT NOTE IN DOOR/ ISO 37830095000086/ COD 1
23471 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-12-10 12:45 | 2012-12-10 14:00 | 1 | 75 | 4456481 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQ, WIRE FROM POLE 38830182B22566 TO SECONDARY POLE 182-597 TO HOUSE INSULATION IS GONE AND WIRE IS ALMOST BURN IN HALF IN SPOTS, NEED ROLL OF 1/0,, TRUCK TO XFMR BUT NOT SECONDARY. DOES NOT HAVE TO BE TODAY/ BUT NEEDS REPLACED VERY SOON, INSULATION IS COMPLETELY GONE FOR LENGTH OF WIRE.//REPLACED 90 1/0TT SEC AND 50 1/0TT S.D.////OPENED SEC 12:45 BACK ON 14:00///VOLT CK GOOD/// COD-1 ISO SO @ 3883182B22566 VER/HFP L3/HFP
23472 | Whitesburg | 3401301 | FLEMING | NEON | 2015-01-06 11:17 | 2015-01-06 12:32 | 1 | 75 | 4910351 | 75 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REMADE SPLICE AT THE XFMR/ ISO 37830355C00621/ COD 1 CCC*******/ VER/BOW
23473 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2008-12-13 12:30 | 2008-12-13 13:45 | 1 | 75 | 57960-1 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKEN IN SD ..... CUSTOMER OUT OF SERVICE FROM 12:30 TO 13:45 , REPAIRED, ALL WORK COMPLETE / GXJ// VER/DBM L3/KEP IDC XXXX
23474 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-08-25 16:50 | 2011-08-25 18:05 | 1 | 75 | 4757391 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKE---REPAIRED VOLT CK OK---// COD 1// VER/DBM IDCC CCU XXXX
23475 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-07-10 11:45 | 2012-07-10 13:00 | 1 | 75 | 4665191 | 75 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NO OUTAGE CUST HAD POWER BUT VOLTAGE WAS NOT RIGHT. I OPENED TRANSFORMER 11:45 DUE TO TRANSFORMER BEING BAD CREW ON THE WAY WITH TRANSFORMER. WE HAVE BAD TRANSFORMER CHANGED OUT AND CLOSED BACK IN AT 13:00 EVERYTHING OK IDC XXXX
23476 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-08-10 16:56 | 2008-08-10 18:10 | 1 | 74 | 50711-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE CONNECTION AT WEATHERHEAD BURNT OPEN. REPAIRED. SH//3409302//VER/CRB IDC XXXX
23477 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-06-29 20:00 | 2015-06-29 21:14 | 1 | 74 | 4693881 | 74 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED AT ENTRANCE CABLE, ALL POWER RESTORED// VER/ ADH
23478 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2019-12-21 16:01 | 2019-12-21 17:15 | 1 | 74 | 4175301 | 74 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad conn on pole, have repairs made all good at this loc
23479 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2017-03-26 23:22 | 2017-03-27 00:36 | 1 | 74 | 4586981 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR F IS OUT,WILL RE-FUSE////////ACTUALLY,CUTOUT DOOR WAS BURNED OUT,REPLACED IT AND RESTORED,ALL OK AFTERWARDS
23480 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2010-12-09 09:12 | 2010-12-09 09:49 | 2 | 37 | 64729-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE XFORMER FUSE BROKE. GOING TO REPLACE FUSE AND CHECK VOLTAGE.//COD 2// VER/DBM IDC XXXX
23481 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2010-01-27 19:40 | 2010-01-27 20:54 | 1 | 74 | 60515-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RESQUEZED CONNECTOR VER/KEP L3/KEP IDC XXXX
23482 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-12-04 15:31 | 2014-12-04 16:08 | 2 | 37 | 4834011 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T XMFER RESTORED BY D. TRAUGOTT// ISO 38830069D16127/ COD 2/ VER/BOW
23483 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-11-13 15:10 | 2019-11-13 16:24 | 1 | 74 | 4031391 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout
23484 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-12-08 17:06 | 2009-12-08 18:20 | 1 | 74 | 57722-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 32991241 POLE 1146-182 BAD CUTOUT DOOR 6T FUSE//COD 1// VER/DBM IDC XXXX
23485 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-02-15 18:01 | 2019-02-15 19:15 | 1 | 74 | 4798501 | 74 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open @ weatherhead// replaced bad connection and restored service @ 19:15// oly 1 customer affected
23486 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-09-05 14:21 | 2015-09-05 15:35 | 1 | 74 | 4206851 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEC. CONDUCTOR ALMOST BURNT INTO.CUSTOMER WAS SEEING VOLTAGE DROP..RECRIMPED CONDUCTORS. VER/CRB
23487 | South Williamson | 3411401 | DEWEY | INEZ | 2015-04-05 15:51 | 2015-04-05 17:05 | 1 | 74 | 4278251 | 74 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LUG ON XFMR BUSHHING BROKE AND HOT LEG RISER HAD FALLEN OUT///REPAIRS MADE//RESTORED AT 17:05//COMPLETE// ISO 38830790A00037/ COD 1
23488 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-06-02 14:28 | 2015-06-02 15:42 | 1 | 74 | 4502011 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED 6T VER/CRB
23489 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2022-10-07 17:36 | 2022-10-07 18:50 | 1 | 74 | 4005381 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required fuse link broke
23490 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-04-26 20:16 | 2018-04-26 21:30 | 1 | 74 | 4282971 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout failed on 1081D44.replaced cutout .restored power at 21:30
23491 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-03-04 12:39 | 2017-03-04 13:53 | 1 | 74 | 4520181 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BROKE XFR CUTOUT COMPLETE VER/CRB
23492 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2022-02-11 23:08 | 2022-02-12 00:22 | 1 | 74 | 4475971 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | crew reqd/truck ok/may need observer hot line clamp was off basket & cant get it unscrewed w stick may have to replace on buckarm pole. Released by crew 078S04,repairs made please close ticket thanks.bt//cod 1
23493 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-10-17 09:46 | 2008-10-17 11:00 | 1 | 74 | 56515-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRING CONNECTIONS/NO CREW REQUIRED//3103101//VER/CRB IDC XXXX
23494 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-05-30 22:36 | 2008-05-30 23:50 | 1 | 74 | 53064-1 | 74 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3001201// 4/3 SERVICE BURNT DOWN REPLACED WITH 2/3 IDC XXXX
23495 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-03-22 20:41 | 2012-03-22 21:55 | 1 | 74 | 4607071 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE//COD 1// VER/DBM IDC XXXX
23496 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-04-24 11:44 | 2010-04-24 12:58 | 1 | 74 | 50152-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF AND LINES DOWN. TALKED TO CUSTOMER ABOUT THIS AND HE AGREED TO WAIT UNTIL MONDAY AS LONG AS THIS IS DONE MONDAY. TALK TO LLOYD MCCARTY ABOUT THIS ON SATURDAY @ 1155 /// IO #34817277 ORDER HUNG ON LLOYD RAYBURNS DOOR PER LLOYD MCCARTY...HFP VER/HFP L3/HFP IDC XXXX
23497 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2021-09-06 11:06 | 2021-09-06 12:20 | 1 | 74 | 4213911 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cut out, replaced. Power restored.
23498 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-04-16 13:02 | 2011-04-16 14:16 | 1 | 74 | 58508-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION VER/HFP L3/HFP IDC XXXX
23499 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-01-21 10:06 | 2010-01-21 11:20 | 1 | 74 | 57149-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY LEAD COME OUT OF TRANSFORMER; FIXED SECONDARY LEAD; PWR RESTORED AT 1120HRS; CLOSE TICKET//VER/CRB IDC XXXX
23500 | Hazard | 3311103 | STINNETT | WENDOVER | 2015-04-30 12:16 | 2015-04-30 13:30 | 1 | 74 | 4378401 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS ROTTEN REPLACED IT/ OLD FUSE BROKE INTO/ ISO 37830436000031/ COD 1/ VER/BOW
23501 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-07-12 02:23 | 2009-07-12 03:00 | 2 | 37 | 60543-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD AND GREEN POLE IS BURNING AT T BRKT. WILL TRY TO EXTINGUISH AND REPLACE T BRKT, AND C/O P.HICKS WILL BE OPENING XFMR.........EXTINGUISHED FIRE AND CHANGED C/O. ALL POWER RESTORED AT 3:00HRS//COD 2// VER/DBM IDCC TOF2103, CDC83 XXXX
23502 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-02-28 12:06 | 2011-02-28 13:20 | 1 | 74 | 64525-1 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN 1149-243--BAD CUTOUT ON 1149-244 WILL CHANGE VER/HFP L3/HFP IDC XXXX
23503 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2019-05-29 15:16 | 2019-05-29 16:30 | 1 | 74 | 4364891 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout on xfmr burned up , I changed it out
23504 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2017-01-27 13:35 | 2017-01-27 14:12 | 2 | 37 | 4337101 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | OPENING XFMR TO REMOVE RUSTED GUY FROM LINE ON 37830090000011 COD 2.OPENED XFMR ON POLE 90-11 AT 13:35 DUE TO GUY WIRE THAT HAD RUSTED INTO AND FELL DOWN ON SEC SIDE OF XFMR CONNECTIONS CLEARED UP GUYWIRE CLOSED XFMR BACK IN AT 14:12. SEND COPY TO ENG PIKEVILLE GUYWIRE WILL NEED TO BE REPLACED I THINK ANCHOR AND GUYWIRE HAD BEEN FILLED IN AROUND NO EVIDENCE OF GUY WRAP WHERE GUYWIRE HAD RUSTED INTO AT GROUND LINE NOT ABLE TO FIND ANCHOR EITHER/SENT TO TECH/AWD VER/AWD L3/HFP HFPC TON1422
23505 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-09-28 13:31 | 2022-09-28 14:45 | 1 | 74 | 4933601 | 74 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection @ weatherhead.. repaired
23506 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-10-27 07:36 | 2010-10-27 08:50 | 1 | 74 | 65457-1 | 74 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR# 37505345 // SER END PULLED LOOSE REPAIRED TRANS OFF 08;40 TO 08;50//COD 4// VER/DBM IDC THIS CUSTOMER STATED DIM LIGHTS BUT FROM COMMENTS IT APPEARS TO BE PART POWER CHANGED START TIME FROM 0840 AND CREATED SEPARATE OUTAGE H65457-1 FOR TRANSFORMER XXXX
23507 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-01-01 08:46 | 2014-01-01 10:00 | 1 | 74 | 4216671 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 140-608 BAD CURRENT LIMITING FUSE REPLACED VER/SEF IDC XXXX
23508 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2016-03-24 15:52 | 2016-03-24 17:06 | 1 | 74 | 4878671 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WAS NOT LINE FUSE WAS CUTOUT ON TRANSFORMER ON POLE 1146-234, LIFTED HOT TAP ON 1146-53, GROUNDED AND TAGGED TO MYSELF, CHANGED CUTOUT AND ALL POWER IS RESTORED TO THIS CUST AT 1706 ISO 39831146D00053 COD 1 VER/AWD
23509 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-01-16 15:46 | 2013-01-16 17:00 | 1 | 74 | 4612601 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT DOOR ON POLE 206-57, REPLACED CUTOUT, ALL POWER RESTORED COD-1 ISO LF 38830206D02057 VER/HFP L3/HFP IDC XXXX
23510 | Pikeville | 3421001 | BREAKS | CITY | 2011-09-20 14:56 | 2011-09-20 16:10 | 1 | 74 | 4889611 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD BURNED OUT OF HOT TAP SERVING SIDE TAP ON POLE 221-161. I AM GOING TO REPLACE HOT TAP. I REPLACED HOT TAP AND RESTORED POWER AT 16:10//COD 1//ISO 37820221B20161 // IDCC PN206 XXXX
23511 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-02-04 23:00 | 2020-02-05 00:14 | 1 | 74 | 4362941 | 74 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no outage to begin/ bad cutout and arrester on pole 38831125C40534/ opened xfmr at 2300/ back on at 0014/ ISO 38831125C40534/ COD 1
23512 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-01-05 20:39 | 2015-01-05 21:53 | 1 | 74 | 4909141 | 74 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN AT WEATHER HEAD APR AT 2153 CLOSE TICKET VER/CRB
23513 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-07-19 04:47 | 2009-07-19 06:00 | 1 | 73 | 60521-1 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT IN HALF, REPLACED DOOR VER/PDP IDC XXXX
23514 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2021-08-01 19:12 | 2021-08-01 20:25 | 1 | 73 | 4991651 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Customer had a hot leg burndt into @trans. pole, got it repaired @2025, only 1 cust. was affected.
23515 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-05-12 14:32 | 2017-05-12 15:45 | 1 | 73 | 4787551 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3 BAD CONNECTION ON BANK TRANSFORMERS 37830247A31290 VER/AWD
23516 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2016-04-30 18:23 | 2016-04-30 19:36 | 1 | 73 | 4145551 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ALSO FUSE OUT ON 523-16, REPLACED CUTOUT AND REFUSED LINEFUSE APR AT 1936 CLOSE TICKET VER/AWD
23517 | Pikeville | 3421001 | BREAKS | CITY | 2009-07-13 07:47 | 2009-07-13 09:00 | 1 | 73 | 65254-1 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400901//PARTIAL POWER ONE CUSTOMER. SECONDARY HOT LEG BURNED APART. //VER/GAH IDC XXXX
23518 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2009-07-27 20:12 | 2009-07-27 21:25 | 1 | 73 | 66485-1 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD FUSE//COD 1// VER/DBM IDC XXXX
23519 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-09-19 09:58 | 2013-09-19 11:11 | 1 | 73 | 4866791 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1061-177 AND LINE FUSE BLOWN ON POLE1061-53 GOING TO CHANGE CUTOUT AND PUT LINE FUSE BACK IN FUSE SIZE WAS 30 T AND POLE 1061-53 *** CHANGE ISO POLE*** DID MD VER/SEF
23520 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-12-24 09:24 | 2016-12-24 10:37 | 1 | 73 | 4234131 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT, POWER RESTORED./ ISO 38821137B00360/ COD 1/ VER/BOW
23521 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-04-14 15:23 | 2022-04-14 16:36 | 1 | 73 | 4764451 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 16:36. sh
23522 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-12-16 18:19 | 2013-12-16 19:32 | 1 | 73 | 4166811 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | THIS IS UNDERGROUND, CHECKED VOLTAGE AT THEIR BREAKER, VOLTAGE 175V, 72V, 247 ACROSS. LOST NEUTRAL SOMEWHERE. WILL HAVE TO DIG TO GET TO BOTTOM OF METER PEDISTAL AND FIND WERE JUNCTION BOX IS. CUSTOMER SAID IT WILL BE OK TO WORK ON THIS IN MORNING. SEND TO BRUCE AND JIM. RELEASED BY CREW 077S08 VER/SEF L3/HFP HFPC CNT7
23523 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-12-10 16:45 | 2013-12-10 17:58 | 1 | 73 | 4148971 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR , PART POWER , MADE REPAIRS RESTORED POWER AT 17:58//COD 1// VER/DBM L3/HFP
23524 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2009-09-15 11:05 | 2009-09-15 12:18 | 1 | 73 | 58220-1 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP LEG BURNED INTO AT MASK, ONLY ONE CUSTOMER .. RESTORED FULL POWER AT 12:15 L3/HFP IDC XXXX
23525 | Cannonsburg | 3001401 | LOUISA | CITY | 2018-02-22 15:22 | 2018-02-22 16:35 | 1 | 73 | 4873621 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrestor on csp transformer bad. line fuse back in at 16:35. pls close. tre 38830454B22520
23526 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-05-20 17:32 | 2017-05-20 18:45 | 1 | 73 | 4829511 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ***SEE 4827201*** OPENING LINE FUSE TO CHANGE TRANSFORMER/ ISO 38820721D00019/ COD 2/ 1740-1845
23527 | South Williamson | 3411401 | DEWEY | INEZ | 2015-09-02 12:42 | 2015-09-02 13:55 | 1 | 73 | 4191441 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN ON LEFT HAND XFMR//BAD CURRENT LIMITING FUSE///REPAIRS MADE/RESTORED AT 13:55//COMPLETE//EM/ ISO 38830744D00016/ COD 1/ VER/BOW
23528 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-06-26 17:22 | 2011-06-26 18:35 | 1 | 73 | 4417121 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP. I AM GOING TO CHANGE DOOR. I CHANGED DOOR.//VER/CRB IDC XXXX
23529 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-10-10 07:17 | 2016-10-10 08:30 | 1 | 73 | 4981451 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNT DOWN. REPLACED DROP COMPLETE VER/AWD L3/HFP XXXHFP
23530 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-02-07 22:02 | 2008-02-07 23:15 | 1 | 73 | 52593-1 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309104// CUTOUT IS BAD I WILL REPLACE THIS REPLACED CUTOUT COD-1 VER/KEP IDC XXXX
23531 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-04-24 13:42 | 2021-04-24 14:55 | 1 | 73 | 4476201 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XCO broke on pole 74-14 will be making repairs
23532 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-06-21 13:47 | 2013-06-21 15:00 | 1 | 73 | 4382061 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL IS BROKEN IN SERVICE DROP I AM GOING TO SPLICE NEUTRAL. I SPLICED NEUTRAL. CUSTOMER SAID EVERYTHING IS OK NOW. VER/HFP L3/HFP
23533 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-06-03 16:41 | 2011-06-03 17:54 | 1 | 73 | 4229231 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BROKEN HOTTAP VER/KEP IDC XXXX
23534 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2014-10-15 13:47 | 2014-10-15 15:00 | 1 | 73 | 4633951 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER STOPPED BY CUSTOMER TO LOOK AT PROBLEM ON POLE 1145-84// A PHASE OPEN AT POLE 1145-84, OPENED B & C PHASES AT 14:40 MADE REPAIRS AND CLOSED ALL PHASES AT 15:00 / ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03// COD-1 SEE H4633951 FOR B&C PHASE OUTAGE VER/HFP L3/HFP
23535 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-09-12 11:47 | 2019-09-12 13:00 | 1 | 73 | 4009201 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | b phase xfmer restored
23536 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-08-10 20:47 | 2011-08-10 22:00 | 1 | 73 | 4694901 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK NO CREW REQUIRED COD-1 ISO TF 38830150000087 VER/HFP L3/HFP IDC XXXX
23537 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2009-02-22 18:19 | 2009-02-22 19:32 | 1 | 73 | 50436-1 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | NO TROUBLE VISIBLE. I ONLY HAVE 125 VOLTS AT MTR BASE. I AM GOING TO OPEN TRANSFORMER AND CHECK CONNECTIONS. I WILL BE AWAY FROM TRUCK FOR A WHILE. ONE SIDE OF TRANSFORMER IS BAD, IT WILL HAVE TO BE REPLACED. CUSTOMER HAS AGREED TO WAIT UNTIL IN THE MORNING ON THIS SINCE HE STILL HAS LIGHTING AND A GAS FIRE PLACE RELEASED BY CREW 077S07//3301701//VER/CRB IDC XXXX
23538 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-04-04 21:15 | 2008-04-04 22:28 | 1 | 73 | 64082-1 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 881-172. POLE HAS A PLACE ABOUT 10 INCHES LONG AND BURNT ABOUT HALF WAY THROUGH THIS IS STRAIGHT LINE POLE NOT NO PRESURE ON POLE. SEND COPY TO RON RYE PIKEVILLE. POLE WILL NEED TO BE CHANGED BUT IS SAFE. VER/HFP IDC CHANGED TIME OFF FROM 1936 XXXX
23539 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-04-13 09:17 | 2016-04-13 10:30 | 1 | 73 | 4087421 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/0 SECONDARY BURNED INTO.OPENED XFMR ON 875-198..AT 09.50 CLOSED BACK IN AT.10.30.// VER/ ADH
23540 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-05-30 14:37 | 2012-05-30 15:50 | 1 | 73 | 4850061 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED CONNECTION ///VER/CRB L/3 CRB IDC XXXX
23541 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-01-02 20:47 | 2011-01-02 22:00 | 1 | 73 | 58052-1 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE ON CUSTOMERS WEATHERHEAD PULLED LOOSE REDONE CONN FULLPOWER RESTORED AT 2200 CLOSE TICKET VER/ARN IDCC CDC89 XXXX
23542 | Cannonsburg | 3001401 | LOUISA | CITY | 2018-07-07 18:16 | 2018-07-07 19:29 | 1 | 73 | 4749501 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Repaired broke neutral in service drop. Only one customer affected. repaires made close ticket
23543 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-12-31 08:30 | 2010-12-31 09:43 | 1 | 73 | 57253-1 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOTTAP AT 930 REPLACED CUTOUT POWER BACK ON AT 943 CUTOUT WAS BRAKING DOWN POWER RESTORED AT 943 CLOSE TICKET COD-1 ISO TF 38830576B00091 VER/HFP L3/HFP IDC EVEN THOUGH THIS IS NOT PART POWER THE CUSTOMER SAYS THEY WERE HAVING PART POWER. CHANGED TIME OFF FROM 0930 XXXX
23544 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-08-26 08:17 | 2013-08-26 09:30 | 1 | 73 | 4706461 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 FUSE OUT IN XFER BANK--BROKEN FUSE LINK VER/CRB L/3 CRB IDC XXXX
23545 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2022-11-15 14:15 | 2022-11-15 15:28 | 1 | 73 | 4145151 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Secondary connection burndt into off trans. pole 24-D2-482, only 1 customer was affected. Got repairs made @1528.
23546 | South Williamson | 3411401 | DEWEY | INEZ | 2020-09-24 19:12 | 2020-09-24 20:25 | 1 | 73 | 4493201 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg conection burned almost into at xfmr//reworked connection//everything good now//restored at 20:25//complete//em
23547 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-02-16 17:12 | 2020-02-16 18:25 | 1 | 73 | 4410261 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced connection @ pole L3/HFP
23548 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-11-26 21:57 | 2010-11-26 23:10 | 1 | 73 | 59993-1 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. VER/PDP IDC XXXX
23549 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-01-12 17:12 | 2015-01-12 18:25 | 1 | 73 | 4931191 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 126-216 , CHANGED CUTOUT . CLOSED FUSE @ 18:25//COD 1// VER/ ADH
23550 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-01-01 09:21 | 2010-01-01 10:34 | 1 | 73 | 55089-1 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT MAST// RESQUEZED CONNECTORS VER/HFP L3/HFP IDC XXXX
23551 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-12-07 18:36 | 2015-12-07 19:49 | 1 | 73 | 4517141 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN LASH WAS BAD , 1/0-1/0 SERVE END . REPAIRED LASH . VER/CRB
23552 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-09-10 08:56 | 2012-09-10 10:09 | 1 | 73 | 4034981 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPLACED CONN ON XMF BANK. TIME OFF WAS 0953 TIME ON 1009. APR CLOSE TICKET//COD 1// VER/DBM IDC XXXX
23553 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-02-23 00:12 | 2014-02-23 01:25 | 1 | 73 | 4427471 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE LINK APPEARS TO HAVE MELTED OUT OR BROKE. REPLACED FUSE AND RESTORED @ 1:25. SH //VER/GAH
23554 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2022-04-19 15:08 | 2022-04-19 16:21 | 1 | 73 | 4780351 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced door
23555 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-12-03 11:17 | 2018-12-03 12:30 | 1 | 73 | 4503901 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15kva 12kv txmf, truck to pole. talked to customer service at this location is not being used at this time can replace anytime this week. crew required Released by crew 078S11 L3/HFP
23556 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-06-30 21:27 | 2022-06-30 22:19 | 4 | 52 | 4353801 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad Trans cutout//cod 1//Opening L/F on same pole to change cutout //opened L?F @ 2212-2219
23557 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2017-07-06 15:47 | 2017-07-06 17:00 | 1 | 73 | 4082241 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT ON POLE 38820965C00145. SERVICER MAKING REPAIRS.TRANS CUTOUT BROKE ON 965C145 REPLACED CUTOUT RESTORED PWER AT 17:00 38820965C00145 VER/AWD
23558 | Hazard | 3310502 | HADDIX | CANOE | 2020-11-20 11:27 | 2020-11-20 12:40 | 1 | 73 | 4711141 | 73 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout. restored power at 12:40
23559 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-12-09 15:17 | 2008-12-09 16:30 | 1 | 73 | 55821-1 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3401002//HOTTAP BURNED OFF ON POLE #37830190B00361// VER/DBM L3/IDC IDC XXXX
23560 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-12-31 16:10 | 2015-12-31 17:23 | 1 | 73 | 4579081 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BURNT INTO IN SECONDARY/// REPAIRED BROKEN NEUTRAL/// PLEASED SEND COPY TO PEGGY WYSONG/// 1 CUSTOMER AFFECTED//SENT TO CLAIMS VER/CRB
23561 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-04-17 16:37 | 2008-04-17 17:50 | 1 | 73 | 51913-1 | 73 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SQUEEZE CONNECTION. MADE REPAIRS. VER/HFP IDC XXXX
23562 | Whitesburg | 3312901 | JENKINS | KONA | 2008-01-21 23:53 | 2008-01-22 01:05 | 1 | 72 | 58817-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BROKEN FUSE LINK. VER/PDP IDC XXXX
23563 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2020-08-13 09:28 | 2020-08-13 10:40 | 1 | 72 | 4318681 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer c/o broken on 1000-277, just one cust, not 3, time on 1040, all power restored at this loc only one customer off at this location per servicer
23564 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-12-15 14:40 | 2010-12-15 15:52 | 1 | 72 | 50673-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTS 4/3 SERVICE DROP MELTED....NUETRAL BURNT IN TWO....WILL REPLACE DROP WITH 2/3....//....SERVICE REPLACED....ALL OK.....JRV....12/15/10 // CHANGED TIME OFF TO REFLECT TIME TO REPLACE DROP AFTER SERIVCER ARRIVED..HFP VER/HFP L3/HFP IDCC FEC57 XXXX
23565 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-09-22 17:18 | 2010-09-22 18:30 | 1 | 72 | 52389-1 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUSTOMER AFFECTED. WE HAD A BAD CONNECTION ON ONE OF THE HOT LEGS AT THE HOUSE. //VER/CRB IDC XXXX
23566 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-12-28 14:03 | 2014-12-28 15:15 | 1 | 72 | 4888311 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED NEVER SEEN A SQUIRREL REPLACED BURNT UP DOOR VER/CRB
23567 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-07-26 22:12 | 2008-07-26 23:24 | 1 | 72 | 60650-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3003701// RELEASED BY CREW 078S08BROKEN 6T FUSE IDC XXXX
23568 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-09-09 21:43 | 2015-09-09 22:55 | 1 | 72 | 4220331 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT, APR AT 1055 CLOSE TICKET VER/ARN
23569 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-02-01 16:09 | 2011-02-01 16:45 | 2 | 36 | 52850-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 38654330 //FUSE LINK DETERIORATED & BROKE AT BOTTOM OF CUTOUT DOOR....NO FAULT....WILL RE-FUSE...//FUSE LINK DETERIORATED & BROKE AT BOTTOM OF CUTOUT DOOR....NO FAULT....WILL RE-FUSE...//...REPLACED FUSE...POWER ON....JRV...02/01/11 // COD-2 ISO TF 38821064A00073 VER/HFP L3/HFP IDC XXXX
23570 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-01-08 11:43 | 2019-01-08 12:55 | 1 | 72 | 4639931 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changeing bad cutout on pole 54:52
23571 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-10-23 13:26 | 2013-10-23 14:38 | 1 | 72 | 4956721 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE WEATHER HEAD, NOT ENOUGH ENTRANCE CABLE LEFT TO MAKE REPAIRS. I HAD TO CUT THE SECONDARY LOOPS AT THE WEATHER HEAD SO THE CUSTOMER CAN REPLACE THE ENTRANCE CABLE. THEY WILL CALL WHEN READY// VER/DBM
23572 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2022-12-06 10:13 | 2022-12-06 11:25 | 1 | 72 | 4233241 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced heated up wire and con--allgood-ds120622
23573 | Whitesburg | 3312901 | JENKINS | KONA | 2018-01-04 12:36 | 2018-01-04 12:48 | 6 | 12 | 4705891 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | voltage checked good at meter, open xfmr at 12:36 to replace old connections at xfmr, restored at 12:48, advised customer to have inside light checked..
23574 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-01-24 14:36 | 2015-01-24 15:48 | 1 | 72 | 4959941 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | ONLY ONE LEG COMING IN, BAD CONNECTION ON SECONDARY POLE, ALL POWER RESTORED VER/SEF
23575 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-09-26 09:58 | 2018-09-26 11:10 | 1 | 72 | 4160341 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Neutral sleeve failed at xfmr sec risers. Made repairs and closed xfmr @ 11:10. sh
23576 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-02-16 13:28 | 2012-02-16 14:40 | 1 | 72 | 4353481 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | S/DROP IS BURNED DOWN. I AM GOING TO REPLACE DROP. I REPLACED DROP. ///VER/CRB VER/HFP L3/HFP IDC XXXX
23577 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-08-21 13:04 | 2011-08-21 13:28 | 3 | 24 | 4735571 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LOOKED LIKE IT HAD JUST PULLED LOOSE, REFUSED XMF APR AT 1328 CLOSE TICKET // COD-3 ISO TF 38830454A41646 VER/HFP L3/HFP IDC XXXX
23578 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2018-11-17 13:38 | 2018-11-17 14:14 | 2 | 36 | 4450191 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | C phase URD riser out on pole 1151-D3-960, fuse pulled into, refused @1414. L3/HFP
23579 | Hazard | 3309301 | VICCO | REDFOX | 2016-08-25 11:16 | 2016-08-25 11:22 | 12 | 6 | 4834851 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-12 ISO LF 37830253000014 VER/HFP L3/HFP
23580 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2011-09-19 21:42 | 2011-09-19 22:18 | 2 | 36 | 4886141 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BROKENFUSE BURNT UP CUTOUT DOOR IN 3 PHASE BANK--CUSTOMER WAS SINGLE PHASING AND CALLED FIRE DEPT COD-2 ISO TF 39831148D26569 VER/HFP L3/HFP IDC XXXX
23581 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-06-08 18:53 | 2017-06-08 20:05 | 1 | 72 | 4925001 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//NO ANSWER// BAD 12KV DOOR, REPLACED DOOR VER/CRB
23582 | South Williamson | 3411401 | DEWEY | INEZ | 2014-09-28 10:53 | 2014-09-28 12:05 | 1 | 72 | 4533901 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT//CUTOUT REPLACED//RESTORED AT12:05//COMPLETE//EM VER/CRB
23583 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2019-01-23 15:53 | 2019-01-23 17:05 | 1 | 72 | 4711021 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced hot tap L3/HFP
23584 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-04-20 12:18 | 2018-04-20 13:30 | 1 | 72 | 4258881 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUSTOMER STRAIGHT TO VOICEMAIL, Bad connection at trailer pole, power restored at 13:30
23585 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-03-17 12:33 | 2010-03-17 13:45 | 1 | 72 | 51086-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNED DOWN DUE TO A LOOSE CONN ON A SPLIT BOLT. VER/KEP L3/KEP IDC XXXX
23586 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2013-07-12 06:43 | 2013-07-12 07:01 | 4 | 18 | 4511441 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN LINE TO SAFELY MAKE REPAIRS/ASSOCIATED WITH OUTAGE 4511381 OPENED AT 0643 AND CLOSED AT 0701 IDC XXXX
23587 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-09-30 12:10 | 2014-09-30 12:18 | 9 | 8 | 4538631 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//NO OUTAGE TIL FUSE WAS OPENED//XFMR CUTOUT FAILED. OPENED XFMR @ 12:10, REPLACED CUTOUT AND CLOSED XFMR FUSE @ 12:18. SH RELEASED BY CREW 076S02 VER/CRB
23588 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-12-08 07:28 | 2011-12-08 08:40 | 1 | 72 | 4157971 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, BAD CONNECTION IN SERVICE DROP. COMPLTED VER/HFP L3/HFP IDC XXXX
23589 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-10-18 21:06 | 2015-10-18 21:30 | 3 | 24 | 4359331 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULL INTO VER/ARN
23590 | Pikeville | 3421001 | BREAKS | CITY | 2019-01-07 17:30 | 2019-01-07 17:42 | 6 | 12 | 4638131 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection about burnt into @ xfm /// will have to open xfm on pole243-109 to make repairs// Opened xfm @ 17:30 made repairs and restored service @ 17:42
23591 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-07 11:18 | 2015-02-07 12:30 | 1 | 72 | 4998251 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT INTO AT XFMR ON 38820649B00169//REPAIRS MADE//RESTORED AT 12:30//COMPLETE VER/CRB L3/HFP XXX
23592 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-12-22 10:43 | 2010-12-22 11:55 | 1 | 72 | 55019-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUST. SER. BURNED DOWN//VER/CRB IDC XXXX
23593 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-02-13 13:48 | 2015-02-13 15:00 | 1 | 72 | 4013861 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | SERVICER WAS INFORMD PART POWER FROM CITY OF MARTIN, FOUND BROKE CUTOUT, OPENING OTHER PHASE/COD1/ OPENED AT 14:15 AND CLOSED AT 15:00 , ALL WORK COMPLETE / GXJ// VER/ ADH L3/HFP XXX
23594 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2018-05-08 13:50 | 2018-05-08 14:08 | 4 | 18 | 4324051 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Secondary riser connection going bad on xfmr pole 954-1145. Opened xfmr @ 13:50, reworked secondary connections and closed xfmr @ 14:08. sh/ ISO 38830954B41145/ COD 4
23595 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-05-08 15:56 | 2013-05-08 16:20 | 3 | 24 | H4086811 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONLY ONE CUSTOMER AFFECTED HERE..ONE LEG OF UNDERGROUND SERVICE BAD.ADDED ADD-A-PHASE FOR TEMPORARY SERVICE.TOOK TRANSFORMER OFF AT 15:56 AND BACK ON AT 16:20.WILL MAKE REPAIRS TOMORROW. ///VER/CRB L/3 CRB IDCC DUP TO OPEN TRANSFORMER XXXX
23596 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2019-03-25 14:28 | 2019-03-25 15:40 | 1 | 72 | 4023711 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 service drop burnt into, replaced service restored power at 15:40..
23597 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-04-15 08:04 | 2013-04-15 09:16 | 1 | 72 | 4009481 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE PHASE CONN BURNT INTO REPLACED CONN. CLOSE TICKET. DWEST VER/HFP L3/HFP IDC XXXX
23598 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2018-01-23 19:55 | 2018-01-23 21:07 | 1 | 72 | 4768951 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUST//CKD BREAKERS lose connection in s/d was able to replace
23599 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2013-01-14 11:03 | 2013-01-14 12:15 | 1 | 72 | 4602561 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I AM GOING TO ISOLATE AT POLE357-133 AND CHANGE BAD CUTOUT ON POLE 357-187 COD-1 CUST MISMAPPED/MD FILED VER/KEP IDC XXXX
23600 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2012-11-28 13:47 | 2012-11-28 14:59 | 1 | 72 | 4428561 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK COD-1 ISO TF 38830118B00050 VER/HFP L3/HFP IDC XXXX
23601 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-01-15 14:36 | 2009-01-15 15:12 | 2 | 36 | 55261-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3401002// CURRENT LIMITING FUSE IS BAD. I AM GOING TO FIX PROBLEM. I REMOVED CURRENT LIMITING FUSE AND MADE TRANS HOT.//COD 2// VER/DBM L3/KEP
23602 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-08-03 19:41 | 2011-08-03 20:53 | 1 | 72 | 4661641 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ROTTEN FUSE LINK/CUST CONNECTED EARLIER TODAY/FETR 2115/VEM/XFMR FUSE BACK IN AND POWER RESTORED 2053/PLEASE CLOSE TICKET/THANKS/VEM//COD 1// VER/DBM IDC XXXX
23603 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-02-07 07:04 | 2012-02-07 07:40 | 2 | 36 | 4324691 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR. VER/KEP IDC XXXX
23604 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-12-19 09:18 | 2016-12-19 10:30 | 1 | 72 | 4219831 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON HOUSE/ ISO 38830045B12171/ COD 1/ VER/BOW
23605 | Hazard | 3303902 | LESLIE | WOOTON | 2011-01-21 10:19 | 2011-01-21 10:55 | 2 | 36 | 63137-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED BIG BUCKET/CUSTOMER AGREED TO WAIT TILL AM REPLACED ALL CONNECTIONS ON THE TRANSFORMER // ADJUSTED TIMES OFF TO ALLOW FOR TIME TO REPLACE CONNECTIONS..... COD-2 ISO TF 37830389D00049 VER/HFP L3/HFP IDC XXXX
23606 | South Williamson | 3200302 | BELFRY | TOLER | 2013-12-30 15:17 | 2013-12-30 16:29 | 1 | 72 | 4213391 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED A BAD HOT LEAD CONNECTION AT THE CUSTOMER SERVICE POLE. THEY ARE CLAIMING DAMAGES, THREE TVS AND THE HEAT PUMP HAD TO BE REPAIRED.//EMAILED TO P WYSONG// VER/DBM
23607 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-02-15 10:18 | 2008-02-15 11:30 | 1 | 72 | 63465-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO POLE FIRE, JUST SERVICE DROP, BURNTED INTO, 2/3 SERVICE DROP, HAVE REPLACED SERVICE WITH NEW DROP VER/HFP IDC XXXX
23608 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-09-13 10:08 | 2013-09-13 11:20 | 1 | 72 | 4850611 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON HOT LEAD AT TRANSFORMER HAS BURNED INTO. I AM GOING TO FIX CONNECTION. I REPLACED CONNECTION. VER/SEF
23609 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-06-25 18:48 | 2012-06-25 20:00 | 1 | 72 | 4962101 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFMR LUG WAS LOOSE AND LET ONE HOT LEG FALL IN CLEAR /// REPAIRED CONNECTION AND VOLTAGE CHECKS GOOD ///VER/CRB L/3 CRB
23610 | Hazard | 3302704 | HAZARD | KENMONT | 2010-11-20 11:48 | 2010-11-20 13:00 | 1 | 72 | H58333-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 37839710 // ON SITE CKING TROUBLE//BAD CUTOUT CALL DUTY FOR 1 MAN AND BIG BUCKET.ON SITE CKING TROUBLE//BAD CUTOUT CALL DUTY FOR 1 MAN AND BIG BUCKET.OPEN TAP AT 11;48AM AND CLOSE AT 1300//REPLACE TRANSFORMER AND CUTOUT ..BROKE BUSHING .. COD-3 TAP COD-1 OUTAGE FOR 1 CUST WHEN TAP OPENED VER/HFP L3/HFP IDC XXXX
23611 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-07-12 15:58 | 2013-07-12 17:10 | 1 | 72 | 4514411 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN.RE-FUSED COD-1 ISO TF 38830875B30945 VER/HFP L3/HFP IDC XXXX
23612 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-01-29 14:24 | 2014-01-29 15:00 | 2 | 36 | H4324611 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION IN SERVICE AND REPLACED CRACKED CUTOUT AT TRANSFORMER. OPENED TRANSFORMER AT 14:24, CLOSED AT 15:00, POWER RESTORED. DUP FOR 2 WHEN TR OPENED /// COD-3 ISO TF 37830272A40446 VER/HFP L3/HFP
23613 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-04-04 13:33 | 2014-04-04 14:45 | 1 | 72 | 4574041 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED 7200 CUTOUT//COD 1// VER/DBM
23614 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-08-17 16:41 | 2016-08-17 17:05 | 3 | 24 | H4802311 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S01FOUND CLAMP BURNED OUT OFF STIRRUP ON POLE 362:38 WILL OPEN RECL. 0N POLE 368 TO MAKE REPAIRS OPENED AT 16:41 CLOSED BACK AT 17:05 ALL POWER RESTORED VER/AWD ///DUP OF 4802311 FOR RECL OUTAGE TO MAKE REPAIRS - 3 CUST L3/HFP HFPC DUP CDC86 CNT 147
23615 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-02-27 23:43 | 2014-02-28 00:55 | 1 | 72 | 4439671 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | WILL REPAIR SURG PROTECTOR
23616 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2021-04-27 13:28 | 2021-04-27 14:40 | 1 | 72 | 4484501 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced connections at xfr complete
23617 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-06-14 17:45 | 2021-06-14 18:57 | 1 | 72 | 4750181 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV DROP BROKE LOOSE AT SERV POLE,WILL REPAIR/////////MADE NECESSARY REPAIRS,ALL OK AFTERWARDS////////HOUSE KNOB HAD PULLED OUT OF POLE,LETTING SERV ONTO MH ROOF
23618 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-09-27 12:18 | 2010-09-27 13:30 | 1 | 72 | 54201-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THIS IS PART OF ORDER 54124-1//BAD CUTOUT HERE//HAS BEEN ISOLATED//NEEDS REPLACED BY CREW//ALSO POLE TAG NEEDS CHANGED TO 1146-197//COD 1// VER/DBM IDC XXXX
23619 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-03-24 09:33 | 2015-03-24 10:45 | 1 | 72 | 4221781 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE IN SERVICE DROP , MADE REPAIRS RESTORED POWER AT 10:45, ONLY ONE CUSTOMER AFFECTED..// VER/ ADH
23620 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-06-02 20:08 | 2008-06-02 21:20 | 1 | 72 | 54704-1 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 2T FUSE OUT......DAH//3400301//VER/CRB IDC XXXX
23621 | Hazard | 3303902 | LESLIE | WOOTON | 2010-10-08 09:55 | 2010-10-08 11:07 | 1 | 72 | 58025-1 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON NEUTRAL ON XFMR POLE VER/HFP L3/HFP IDC CUSTOMER REPORTING POWER BELOW ACCEPTABLE ON ONE LEG, LEFT AS PART POWER XXXX
23622 | South Williamson | 3200302 | BELFRY | TOLER | 2014-08-22 12:42 | 2014-08-22 13:18 | 2 | 36 | 4401931 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | GUY BOND BROKE AND WAS LAYING ON EXTENTION LINK. MADE REPAIRS TO GUY AND INSTALLED GUY BREAKER. ALSO REDONE CONNECTIONS ON SERVICE NEUTRALS.OPENED TRANSFORMER AT 12:42 AND CLOSED IN AT 13:18. VER/CRB
23623 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2014-12-16 09:48 | 2014-12-16 11:00 | 1 | 72 | 4863941 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | @ 1015 SERVICR REPLACING BROKEN CUTOUT ON XFMRREPLACE CUTOUT ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT // COD-1 ISO TF 38830207C12119 VER/HFP L3/HFP
23624 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-11-28 10:45 | 2009-11-28 11:03 | 4 | 18 | 50236-1 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD CONNECTION ON TRANSFORMER // COD-4 L3/HFP IDC CHANGED FROM PART POWER, ALLOWED 15 MIN FOR REPAIR, CHANGED TIME OFF FROM 0934 XXXX
23625 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-01-30 15:33 | 2018-01-30 16:45 | 1 | 72 | 4784861 | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tran and lat c/os broke--crew req-ds013018 Released by crew 078S01
23626 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-12-09 18:54 | 2011-12-09 19:30 | 2 | 36 | H4165901B | 72 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN TRANSFORMER AT 17:18 CLOSE AT 17:25. 1/0 SECONDARY BURNT DOWN THEIR WILL BE TWO CUSTOMER OUT OF SERVICE UNTIL I CAN MAKE REPAIRS. OFF AT 18:54 ON AT 19:30//COD 4 IDCC DUP TO OPEN TRANSFORMER XXXX
23627 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-04-26 10:48 | 2013-04-26 12:00 | 1 | 72 | 4049541 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP TROUBLE NO POLE FIRE REPAIRED ///VER/CRB L/3 CRB IDC XXXX
23628 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2019-09-10 11:48 | 2019-09-10 13:00 | 1 | 72 | 4999771 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral was broken on 4/3 srv drp, have repairs made all seems to be good at this loc, comp by amg
23629 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-06-28 19:42 | 2017-06-28 20:54 | 1 | 72 | 4055861 | 72 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER ,MADE NEW CONNECTION VER/CRB
23630 | Whitesburg | 3312902 | JENKINS | JENKINS | 2016-01-11 10:03 | 2016-01-11 11:14 | 1 | 71 | 4605981 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICES ON SERVICE BURNED UP ON SECONDARY POLE, I REPLACED BAD SPLICES.// VER/ ADH
23631 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-11-17 11:31 | 2013-11-17 12:42 | 1 | 71 | 4045701 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEU WIRE BROKE AT POLE WILL NEED TO OUTAGE TRANFORMER TO MAKE REPAIRSOFF AT 12;30 BACK ON AT 12;42 ALL POWER RESTORED KWB SEE H4045701 DUP IN HOIS FOR 3 CUST VER/HFP L3/HFP
23632 | Whitesburg | 3309302 | VICCO | JEFF | 2017-12-28 14:10 | 2017-12-28 15:21 | 1 | 71 | 4685821 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cut-out broke on pole 373-99. Replaced cut-out and restored power at 15:21
23633 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-09-12 08:49 | 2014-09-12 10:00 | 1 | 71 | 4492951 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 174-C- 516 ; CHANGED CUTOUT AND RESTORED POWER AT 10:00 VER/CRB
23634 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2018-10-25 19:19 | 2018-10-25 20:30 | 1 | 71 | 4323341 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned up, I changed it out/ ISO 37830356B00030/ COD 1 L3/HFP
23635 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-03-17 21:09 | 2010-03-17 22:20 | 1 | 71 | 51277-1 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 34297666 BAD WESTINGHOUSE CUTOUT AND LA VER/HFP L3/HFP IDC XXXX
23636 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2022-08-11 15:39 | 2022-08-11 16:50 | 1 | 71 | 4729281 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection @ house. reaired
23637 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-12-03 14:09 | 2020-12-03 15:20 | 1 | 71 | 4742501 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING TO REPLACE BAD CUTOUT // COD 1 // OFF@ ON@ repairs made power restored at 15:20
23638 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-10-04 15:49 | 2014-10-04 17:00 | 1 | 71 | 4553321 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION BURNED INTO AT RISER VER/CRB
23639 | South Williamson | 3200302 | BELFRY | TOLER | 2020-01-30 11:39 | 2020-01-30 12:50 | 1 | 71 | 4348751 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED O REPLACE XFMR /// OPENED @ 11:39 // CLOED @ 12:50
23640 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-11-12 17:34 | 2009-11-12 18:45 | 1 | 71 | 52481-1 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT == REPLACED POWER OK//COD 1 IDC XXXX
23641 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-02-11 11:34 | 2013-02-11 12:45 | 1 | 71 | 4809031 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CHANGED CUTOUT AND REFUSED IT VER/KEP IDC XXXX
23642 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-03-09 18:12 | 2010-03-09 19:23 | 1 | 71 | 64443-1 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PARTIAL POWER LOOSE CONNECTION...RE SQUEEZED..CK VOLTAGE. GOOD ..BB// VER/DBM IDC XXXX
23643 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-02-26 16:59 | 2013-02-26 18:10 | 1 | 71 | 4854971 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION AT WEATHER HEAD ON ONE LEG OFF SERVICE DROP. VER/HFP L3/HFP IDC XXXX
23644 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2021-08-19 10:49 | 2021-08-19 12:00 | 1 | 71 | 4118071 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Crew replacing pole 330-22 replaced pole restored power at 1200
23645 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-06-21 15:54 | 2022-06-21 17:05 | 1 | 71 | 4270891 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke//repairs made//restored at 17:05//complete//em
23646 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2021-05-17 08:53 | 2021-05-17 10:04 | 1 | 71 | 4591251 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Repaired a bad secondary connection on pole 224-C1-492.
23647 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-06-30 13:45 | 2014-06-30 14:56 | 1 | 71 | 4175061 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND MELTED CONNECTION ON 1 HOT LEG OF SERVICE DROP///MADE REPAIRS///VOLT CK 125/125/249V///POSSIBLE DAMAGE COMPLAINT???///TBL TKT COMP VER/HFP L3/HFP AJB
23648 | Paintsville | 3401802 | INDEX | HOSPITAL | 2016-10-03 17:43 | 2016-10-03 18:54 | 1 | 71 | 4957281 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON SERVICE DROP.REPLACING.VER/AWD L3/HFP HFPC CDC89 CNT5
23649 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2014-03-08 15:21 | 2014-03-08 16:32 | 1 | 71 | 4461651 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON ONE LEG OF SERVICE AT THE SECONDARY POLE. THE CUSTOMER HAD PART POWER.. VER/CRB
23650 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2013-11-18 07:14 | 2013-11-18 08:25 | 1 | 71 | 4050951 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE SERV TO CHANGE,REPAIRS MADE ALL CUST RESTORED @ 0825 PLEASE CLOSE TICKET THANKS.BT VER/CRB
23651 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2016-12-30 14:04 | 2016-12-30 15:15 | 1 | 71 | 4256911 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED NEUT IN SD VER/CRB
23652 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-12-01 08:52 | 2011-12-01 10:03 | 1 | 71 | 4132191 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 424-2221, REPLACED XFMR RESTORED POWER AT 10:03//COD 1// VER/DBM IDCC PN110 XXXX
23653 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2016-01-18 10:15 | 2016-01-18 11:26 | 1 | 71 | 4627861 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL WAS BROKE IN SECONDARY ON POLE 38820820B11770/ TRANSFORMER OFF 10-15 ISO 38820820B11770/ COD 1 VER/CRB
23654 | Hazard | 3310502 | HADDIX | CANOE | 2019-06-09 20:23 | 2019-06-09 21:34 | 1 | 71 | 4470701 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pull into
23655 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2015-07-29 09:44 | 2015-07-29 10:55 | 1 | 71 | 4954601 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTIONS GOT AGAINST GROUND AND BURNT OPEN SEC. @ WEATHER HEAD RECONNECTED.. VER/CRB
23656 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-03-11 17:59 | 2013-03-11 19:10 | 1 | 71 | 4898861 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIREED AT THIS TIME SENDING ORDER TO TECH TO WRITE A ORDER TO REPLACE POLE/126F70 VER/KEP IDC XXXX
23657 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-06-02 14:24 | 2021-06-02 15:35 | 1 | 71 | 4659651 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans fuse open @ 236-121 cause UNKNOWN,going to refuse and restore service..Trans fuse open @ 236-121,Had a broke Trans Cutout,Made repairs and restored @ 15:35.
23658 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-06-05 19:10 | 2010-06-05 20:21 | 1 | 71 | 57376-1 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFR POLE,WILL REPAIR///////MADE REPAIRS AND RESTORED,ALL OK AFTERWARDS,BAD SERVE-IN CONNECTION ON 1 HOT LEG//VER/CRB IDC XXXX
23659 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2013-01-07 22:09 | 2013-01-07 23:20 | 1 | 71 | 4576481 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SEND TO ENG. DEPT. WE NEED TO SET A SECONSARY POLE TO SHORTEN SERVICE DROP. IT IS ABOUT 120. ITS A #4 DROP. TOO FAR TO CHANGE TO #2 DROP. SERVICE DROP BURNED INTO AT SPLICE. I AM GOING TO REPAIR DROP. I SPLICED DROP.//EMAILED TO CLIFF FREEMAN// VER/DBM IDCC CDC89, FEC44 XXXX
23660 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-04-17 10:09 | 2013-04-17 11:20 | 1 | 71 | 4018101 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 C.O. RESTORED @ 11:20 VER/KEP IDC XXXX
23661 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2015-05-16 18:34 | 2015-05-16 19:45 | 1 | 71 | 4436241 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT/ ISO 38830227000016/ COD 1/ VER/BOW
23662 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-03-17 15:19 | 2011-03-17 16:30 | 1 | 71 | 55240-1 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR SECONDARY LEAD....ONE HOT LEG ONLY....POLE 1041-A-36......CUST MIS-MAPPED....WILL REPLACE CONNECTIONS.....//....REPLACED CONNECTION....VOLTAGE OK NOW.....JRV....03/17/11 COD-1 ISO TF 38821041A00036 VER/HFP L3/HFP IDC XXXX
23663 | Pikeville | 3408103 | SALISBURY | MARTIN | 2010-03-11 16:44 | 2010-03-11 17:55 | 1 | 71 | 65183-1 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ... REPLACED CUTOUT, ALL WORK COMPLETE / GXJ// COD 1// VER/DBM IDC XXXX
23664 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-02-15 20:49 | 2014-02-15 22:00 | 1 | 71 | 4391611 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONECTION CAME APART ON SERVICE DROP//I REWORKED CONNECTIONS RESTORED AT 22:00//COMPLETE//EM VER/ARN
23665 | South Williamson | 3411401 | DEWEY | INEZ | 2010-05-05 16:29 | 2010-05-05 17:40 | 1 | 71 | 56138-1 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 34988197 //STS WR # 349 SERVICE DROP BURNT IN TO GOING TO FIX VER/HFP L3/HFP IDC XXXX
23666 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-09-21 09:53 | 2010-09-21 11:04 | 1 | 71 | 51802-1 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, BAD CONNECTION ON TRL POLE VER/KEP L3/KEP IDCC MCCNI , CNT3 XXXX
23667 | Hazard | 3309302 | VICCO | JEFF | 2013-12-25 09:49 | 2013-12-25 11:00 | 1 | 71 | 4200481 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON TRANSF POLE BAD === REPAIRED === POWER OK// VER/DBM L3/HFP
23668 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-12-02 08:31 | 2013-12-02 09:42 | 1 | 71 | 4092081 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED NEUT. THAT HAD PULLED OUT OF SLEEVE VER/SEF L3/HFP
23669 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2018-10-18 07:49 | 2018-10-18 09:00 | 1 | 71 | 4265021 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1 PHASE OF UNDERGROUND RISER OUT @ POLE 37830513D00131fuse broke
23670 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2013-04-01 08:04 | 2013-04-01 09:15 | 1 | 71 | 4970461 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 45-4198 10T TRANS FUSE BROKE REPLACED FUSE ///VER/CRB L/3 CRB IDC XXXX
23671 | Hazard | 3303902 | LESLIE | WOOTON | 2010-06-15 11:49 | 2010-06-15 13:00 | 1 | 71 | 65071-1 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKE CUTOUT COD-1 VER/HFP L3/HFP
23672 | South Williamson | 3411401 | DEWEY | INEZ | 2010-01-11 17:29 | 2010-01-11 18:40 | 1 | 71 | 52829-1 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | CHANGED ONE SIDE OF METER BASE IDC XXXX
23673 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-11-02 10:04 | 2012-11-02 11:15 | 1 | 71 | 4335131 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE BURNT IN TWO AT CONNECTION NEAR SEC. POLE. -- OPENED TRANSFORMER AT 11:00 = CLOSED AT 11:15. COD-3 ISO TF 37830224D00158 SEE H4335131 FOR 2 CUST WHEN TR OPENED // VER/HFP L3/HFP IDC XXXX
23674 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-11-10 20:11 | 2017-11-10 21:22 | 1 | 71 | 4548111 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans fuse melted out, refused @2122. L3/HFP XXXHFP
23675 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-05-13 13:44 | 2021-05-13 14:55 | 1 | 71 | 4583871 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/2 security light conductor, repaired
23676 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2011-09-26 19:11 | 2011-09-26 20:22 | 1 | 71 | 4921281 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT LEGS BURNT INTO ON SERVICE DROP TO 509 MAIN STR// MADE REPAIRS// MAY NEED BIGGER SERVICE AND SECONDRY//PLEASE SEND TO TECH TO COME OUT AND CHECK// COMPLETE//EM//VER/CRB IDC XXXX
23677 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2011-11-18 11:04 | 2011-11-18 12:15 | 1 | 71 | 4090291 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON BUILDING /// VER/CRB IDC XXXX
23678 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-09-18 19:52 | 2016-09-18 21:03 | 1 | 71 | 4905471 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT APR AT 2103 CLOSE TICKET DWEST/// VER/DKM
23679 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-12-27 17:43 | 2021-12-27 18:54 | 1 | 71 | 4230731 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRF IS OUT,WILL RE-FUSE//////////////RE-FUSED&RESTORED@18:54///////FUSE HAD EITHER ROTTED INTO OR HAD SIMPLY MELTED OUT,HARD TO TELL,BUT HAS BEEN RESTORED
23680 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-05-22 12:34 | 2018-05-22 13:45 | 1 | 71 | 4393491 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFR CUTOUT,WILL REPLACE///////////REPLACED CUTOUT,RESTORED POWER,ALL OK AFTERWARDS // Restored @ 1345
23681 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2008-03-22 20:13 | 2008-03-22 21:24 | 1 | 71 | 60003-1 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV END SPLICE FROZED OUT == REPAIRED VER/HFP IDC XXXX
23682 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-09-25 19:39 | 2016-09-25 20:50 | 1 | 71 | 4924891 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SINGLE ALL OUT BROKEN FUSE LINK REPLACED POWER RESTORED KWB VER/KEP
23683 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-05-10 18:19 | 2008-05-10 19:30 | 1 | 71 | 59596-1 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3002001//FUSE LINK ROTTEN AND BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC//VER/CRB IDC XXXX
23684 | Hazard | 3303902 | LESLIE | WOOTON | 2020-11-11 17:08 | 2020-11-11 18:19 | 1 | 71 | 4664111 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | need to replace cutout t-bracket at 37830413D00084 and arrester, maybe truck access with flaggers replaced gate Released by crew 077S07
23685 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-07-28 12:29 | 2011-07-28 13:40 | 1 | 71 | 4634021 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER DOOR BURNT UP. REFUSED NEW DOOR. GOT POWER RESTORED 1340. DR//COD 1// VER/DBM IDC XXXX
23686 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-11-03 16:37 | 2021-11-03 17:48 | 1 | 71 | 4054331 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT/////////REPLACED XFR CUTOUT&RESTORED@17:48
23687 | Hazard | 3309302 | VICCO | JEFF | 2018-05-03 17:53 | 2018-05-03 19:04 | 1 | 71 | 4303681 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION/ ISO 37830372A10215/ COD 1
23688 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-04-07 15:09 | 2020-04-07 16:20 | 1 | 71 | 4568161 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS//////FOUND REALLY BAD SQUEEZON CONNECTION@THE XFR.I REPLACED WITH BETTER CONNECTIONS,ALL OK AFTERWARDS.PROBABLY AFFECTED 2 SERVICES TO 2 DIFFERENT ACCNTS.SHOULD BE OK NOW
23689 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2014-12-08 07:49 | 2014-12-08 09:00 | 1 | 71 | 4845901 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND C PHASE FUSE OUT REPLACED AND FOUND HOT TAP LEAD BURNTED OFF HOT TAP LEAD IS LAYING ON C PHASE, CUST HAS FULL POWER, BUT NEED CREW TO MAKE REPAIRS TO HOT TAP, AT THIS LOC RELEASED BY CREW 078S06// ON @ 9:00,,CREW ON SITE, OPENED XFMR AT 11:15 FOR REPAIRS, CLOSED AT 11:18, ALL POWER RESTORED// COD 1// VER/ ADH
23690 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-08-03 10:19 | 2017-08-03 11:30 | 1 | 71 | 4220031 | 71 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERV-IN RESTORED/ VER/HFP L3/HFP
23691 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-02-17 20:49 | 2014-02-17 22:00 | 1 | 71 | 4395511 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OOOONE CUSTOMER AFFECTEDOOO INSULINK CONNECTION FROZE OPEN AT WEATHERHEAD. REPLACED CONNECTION AND RESTORED @ 22:00. SH VER/HFP L3/HFP
23692 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2017-12-07 13:16 | 2017-12-07 14:27 | 1 | 71 | 4628771 | 71 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | looks like 6t transformer fuse broke fused up everything ok
23693 | Hazard | 3303902 | LESLIE | WOOTON | 2019-01-10 18:05 | 2019-01-10 19:15 | 1 | 70 | 4657511 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
23694 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2019-10-11 15:15 | 2019-10-11 15:29 | 5 | 14 | 4131311 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830020C45646, crew required//NO OUTAGE UNTIL OPENED @ 1515// 38830020C45646, crew required Released by crew 078H04,open xfmr @ 1515 replaced cutout closed @ 1529 please close ticket thanks.bt
23695 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-02-03 14:46 | 2020-02-03 15:00 | 5 | 14 | 4358191 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew changing cutout. open xfmr @ 14:46 in @ 15:00
23696 | South Williamson | 3411401 | DEWEY | INEZ | 2018-11-01 13:05 | 2018-11-01 13:19 | 5 | 14 | 4350611 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no outage until i arrived///found cutout buzzing loud and cracked//i replaced cutout//opened xfmr at 13:05//restored at 13:19//complete//em
23697 | South Williamson | 3411401 | DEWEY | INEZ | 2008-03-20 09:00 | 2008-03-20 10:10 | 1 | 70 | 59323-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401//CUTOUT BROKE VER/HFP IDC XXXX
23698 | South Williamson | 3411401 | DEWEY | INEZ | 2011-10-11 21:55 | 2011-10-11 23:05 | 1 | 70 | 4966721 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 672-82//CHANGED CUTOUT//RESTORED AT 2305//COMPLETE//EM COD-1 ISO TF 38830672A00082 VER/HFP L3/HFP IDC XXXX
23699 | Hazard | 3302704 | HAZARD | KENMONT | 2019-07-15 18:05 | 2019-07-15 18:15 | 7 | 10 | 4712131 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on transformer repaired. powered restored at 18:15 // off @ 1805 on @ 1815
23700 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-07-20 07:00 | 2012-07-20 07:35 | 2 | 35 | 4771991 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GATE IS LOCKED, CUSTOMER SAYS OK TO WAIT TILL 7:00AM / GXJ RELEASED BY CREW 074S03GATE IS LOCKED, CUSTOMER SAYS OK TO WAIT TILL 7:00AM / GXJ . REPLACED CUTOUT AND ARRESTER POLE 179, ALL WORK COMPLETE / GXJ.... START OUTAGE AT 0700. CC 1. VER/SDB
23701 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-12-04 13:00 | 2022-12-04 13:07 | 10 | 7 | 4227001 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad squeezon open tranformer at 13:00 back in at 13:07. complete
23702 | Pikeville | 3413401 | GARRETT | GARRETT | 2011-03-21 09:15 | 2011-03-21 09:25 | 7 | 10 | 56142-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL DISPATCH AT REG WK TIME ON 3/21/11 UNLESS OUTAGE OCCURS OR PROBLEMS BECOMES BRIGHT DIM CONDITION OR CUSTOMERS CALL BE WITH MORE INFORMATION TONIGHT, OR SERVICER IS CALLED OUT IN AREA FOR OUTAGES.... LOOSE CONNECTION AT TRANSFORMER , OPENED XFMR AT 09:15 AND RESTORED AT 09:25, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 COD-7 ISO TF 37830016C00016 VER/HFP L3/HFP IDCC TOF DATE 3/20 XXXX
23703 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2016-10-26 17:40 | 2016-10-26 18:15 | 2 | 35 | 4055711 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPEN TRANSFORMER AT 1740, BACK ON AT 1815, BY AMG, BAD L/A SEND MAIL TO RAYBURN TO TAKE CARE OF THIS, THANKS, BY AMG ENTERED INTO AED/AWD VER/AWD
23704 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-02-11 09:40 | 2015-02-11 10:50 | 1 | 70 | 4007421 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE END HAS FAILED. I AM GOING TO RESQUEEZE CONNECTIONS. I RESQUEEZED CONNECTIONS. 37830287000089 1 CUST AFFECTED VER/CRB L3/HFP XXX
23705 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-02-11 13:31 | 2019-02-11 14:41 | 1 | 70 | 4778181 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | burnt up neut in serv drop. making repairs. repairs made. psl close. tre. Time back on @ 14:41
23706 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-05-21 18:10 | 2015-05-21 19:20 | 1 | 70 | 4454581 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRS TO 2/3 SD, CONNECTION @ WEATHER HEAD// VER/ ADH
23707 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2015-10-27 16:32 | 2015-10-27 17:42 | 1 | 70 | 4381311 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER IS FED OFF OF CLOSED DELTA BANK C PHASE CUTOUT FAILED BURNING POLE AT BOTTOM OF CLUSTER MOUNT THERE IS NO 3 PHASE CUSTOMERS FED FROM THIS BANK SO I ISOLATED A PHASE AND C PHASE TRANSFORMER AND FED CUSTOMER FROM B PHASE TRANSFORMER COULD NOT REACH CUTOUT TO CHANGE IT VER/CRB
23708 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-28 20:20 | 2012-02-28 20:30 | 7 | 10 | 4515441 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL SLEVE PULLED LOOSE IN SECONDARY GOING TO POLE 37820097000202, AFFECTING TWO CUSTOMERS.WILL HAVE TO OPEN XFMR TO MAKE REPAIRS.OPEN AT 20:20, CLOSED AT 20:30 // COD 7 // VER/DBM IDC XXXX
23709 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-04-28 16:30 | 2022-04-28 17:05 | 2 | 35 | 4812751 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BUZZING COMING FRO TOP OF POLE//STIRRUP BURNED IN TWO//CHANGED 19.9 C/O//OPENED @ 16:30 CLOSED @ 17:05
23710 | Hazard | 3310502 | HADDIX | CANOE | 2014-05-04 22:35 | 2014-05-04 23:45 | 1 | 70 | 4663311 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERV PATROLLING LINE. *** REPLACING TR CUTOUT.CUTOUT BROKE ON POLE37830025000128 VER/PDP
23711 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-08-17 17:05 | 2008-08-17 18:15 | 1 | 70 | 52718-1 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3001201//RESQUEZED CONNECTIONS // VER/TOM IDC XXXX
23712 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-03-02 18:37 | 2011-03-02 19:47 | 1 | 70 | 65994-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED BAD PLACE IN SERVICE//VER/CRB IDC XXXX
23713 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-05-30 18:00 | 2015-05-30 19:10 | 1 | 70 | H4485941 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACE 2/3 SD BECAUSE OPEN NEUT. XFMER OFF @ 18:00, ON @ 19:10// VER/ ADH L3/DKG
23714 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-03-10 09:50 | 2022-03-10 11:00 | 1 | 70 | 4596401 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t no crew
23715 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2018-06-29 09:10 | 2018-06-29 10:20 | 1 | 70 | 4688201 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Opened padmount 930-313 @ 9:10 for AEP Meter Dept to replace CTs. Replaced CTs and restored @ 10:20. sh
23716 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2012-06-28 15:30 | 2012-06-28 16:40 | 1 | 70 | 4971931 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 118-171 BAD CUTOUT AND LA
23717 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-06-10 09:55 | 2020-06-10 11:05 | 1 | 70 | 4989951 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on step down. replaced and restored power at 11:05
23718 | Hazard | 3307301 | BULAN | ARY-HEINE | 2016-08-22 21:45 | 2016-08-22 22:55 | 1 | 70 | 4827021 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.... POWER RESTORED. VER/AWD
23719 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2010-11-16 15:50 | 2010-11-16 16:25 | 2 | 35 | 56416-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK.//VER/CRB IDC XXXX
23720 | Hazard | 3308002 | JACKSON | PANBOWL | 2021-03-09 09:50 | 2021-03-09 11:00 | 1 | 70 | 4318161 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutouts broke while closeing in for an open connect replaceing cutouts ;;;cutouts replaced and power rstored at 11:00
23721 | South Williamson | 3411401 | DEWEY | INEZ | 2012-01-03 15:50 | 2012-01-03 17:00 | 1 | 70 | 4229771 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 768-237//ONLY ONE CUSTOMER OUT//CHANGED OUT//RESTORED AT 17:00//COMPLETE//EM COD-1 (PER ERIC) ISO TF 38830768C00237 VER/HFP L3/HFP IDC XXXX
23722 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-04-25 19:09 | 2017-04-25 20:19 | 1 | 70 | 4682541 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED XFR CUTOUT ,,CUSTOMER RESTORED COMPLETE VER/CRB L3/HFP XXXHFP
23723 | South Williamson | 3200301 | BELFRY | BELFRY | 2012-11-29 18:25 | 2012-11-29 18:35 | 7 | 10 | H4432021 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 4432021//SERV DROP N BURNED INTO,HAVE TO OPEN XFR TO CLEAR,WILL CLOSE XFR BACK IN,THEN WILL MAKE REPAIRS//OPND XFR 18:25,CLOSD 18:35/////EDDIE ENROUTE W WIRE//////MADE NECESSARY REPAIRS//COD 7// VER/DBM IDC XXXX
23724 | South Williamson | 3411401 | DEWEY | INEZ | 2014-05-14 16:15 | 2014-05-14 17:25 | 1 | 70 | 4702551 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECION BURNED INTO ON SERVICE DROP//HOT LEAD REPAIRED//RESTORED AT 17:25//COMPLETE//EM VER/HFP L3/HFP
23725 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-10-04 15:20 | 2016-10-04 16:30 | 1 | 70 | 4959621 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CUSTOMER PART OUT DUE TO BAD 100 KVA 277 VOLT XFMR. CREW TO BRING XFMR TOMORROW MORNING TO REPAIR. CUSTOMER ADVISED HE WOULD RATHER WE WAIT UNTIL TOMORROW TO REPLACE. CREW WILL CALL FOR NEW TICKET IN THE MORNING. SH VER/CRB L3/HFP XXXHFP
23726 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-10-01 11:03 | 2014-10-01 11:38 | 2 | 35 | 4541441 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | COMPANY CHANGING BAD LIGHTNING ARRESTER---ABNORMAL CONDITION---CUST OFF @ 11:03--BACK ON @ 11:38---REMOVE FROM ABNORMAL DATABASE---TBL TKT COMP /// COD-2 ISO TF 38830115D00288 VER/HFP L3/HFP
23727 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-08-14 08:05 | 2016-08-14 09:15 | 1 | 70 | 4773061 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CUSTOMER RESTORED AT 0915.. BROKEN FUSE LINK PLEASE CLOSE TICKET CY VER/AWD
23728 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-09-26 12:05 | 2012-09-26 13:15 | 1 | 70 | 4089141 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7,200 INCLOSED CUTOUT. VER/KEP IDC XXXX
23729 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-02-12 08:27 | 2008-02-12 09:37 | 1 | 70 | 60728-1 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308401/BAD CONNECTION ON XFMR POLE, PART OUT VER/HFP IDC XXXX
23730 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2009-01-09 18:10 | 2009-01-09 19:20 | 1 | 70 | 53851-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP WR # 28007806 // 4/3 SERV BURNED INTO AT HOUSE L3/HFP IDC XXXX
23731 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2014-04-04 19:50 | 2014-04-04 20:00 | 7 | 10 | 4576001 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP LEAD BROKE AND REPAIRED OPEN AT 1950 BACK ON 2000 COD-7 ISO TF 38830045C14309 VER/HFP L3/HFP
23732 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-04-24 17:20 | 2013-04-24 18:30 | 1 | 70 | 4044991 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKED VOLTAGE 223 PHASE TO GROUND AND 23 PHASE TO GROUND. 1/0 NEUTRAL BROKE OFF AT CONN. ON SEC. POLE 165-186. THIS IS THE WRIGHT XFORMER NUMBER 165-185.// VER/DBM IDCC PN367 XXXX
23733 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2012-07-07 17:25 | 2012-07-07 18:35 | 1 | 70 | 4581441 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT HSE, REPAIRED KWB 7-7-12
23734 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-10-29 21:10 | 2015-10-29 22:20 | 1 | 70 | 4395731 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE//FUSE ROTTED VER/CRB
23735 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-10-01 18:05 | 2013-10-01 19:15 | 1 | 70 | 4903281 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TOLD CUSTOMER TO TURN HIS BREAKER OFF TILL I FIXED THE NEUTRAL. BROKEN AT NEUTRAL CLEVIS. COMPLTED CUSTOMERS POWER RESTORED. VER/CRB L/3 CRB IDC EVEN THOUGH NEUTRAL WAS BROKEN ONLY THE CUSTOMER SAID PART POWER XXXX
23736 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-08-15 22:45 | 2011-08-15 23:20 | 2 | 35 | 4714621 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 140-45 25KVA TRANS LECKING OIL NEEDS CHGED 37.5 TRUCK OK RELEASED BY CREW 078S08//WILL OPEN WHEN CREW ARRIVES//WILL BE OPENING THE TRANSFORMER @ 22:45 RELEASED BY CREW 078H07//VER/CRB IDC XXXX
23737 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-12-12 15:50 | 2018-12-12 15:57 | 10 | 7 | 4558781 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutrel broke//crew in route..Opened @15:50 closed@n15:57//OPENED TRANSFORMER TO MAKE REPAIRS ¦¦¦¦¦ L3/HFP
23738 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-05-04 19:05 | 2009-05-04 20:15 | 1 | 70 | 53520-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//3308002BAD CUTOUT REPLACED CUTOUT/VER/CRB IDC XXXX
23739 | Hazard | 3309302 | VICCO | JEFF | 2016-12-09 12:02 | 2016-12-09 12:12 | 7 | 10 | 4180661 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | POLE 37830346A00154 GUY IS BROKE LETTING POLE LAY OVER PRIMARY AND NEUT LOW == NEEDS REPAIRED NEED LINE CREW NO POWER OFF AT THIS TIME ===//OPENED 1202/CLOSED 1212 VER/CRB L3/HFP XXXHFP
23740 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2013-03-20 15:55 | 2013-03-20 17:05 | 1 | 70 | 4927821 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | BROKEN HOT TAP JUMPER ON 3 PHASE BANK--DON JENT ENROUTE TO REPAIR COD-1 ISO PO @ 38830045C35079 VER/HFP L3/HFP IDC XXXX
23741 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-10-26 13:20 | 2018-10-26 14:30 | 1 | 70 | 4325981 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link broke. Restored @ 14:30. sh L3/HFP
23742 | Hazard | 3307301 | BULAN | ARY-HEINE | 2017-12-08 09:22 | 2017-12-08 10:32 | 1 | 70 | 4629901 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
23743 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-12-19 14:25 | 2021-12-19 15:35 | 1 | 70 | 4212251 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced door
23744 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2015-12-05 14:30 | 2015-12-05 15:40 | 1 | 70 | 4512431 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD LOOPS ON POLE 45-631 OPENED TRAN. 45-666 14:30 BACK ON 15:40 REPLACED 3-1/0 SEC. LOOPS// VER/ ADH
23745 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2009-05-14 12:30 | 2009-05-14 13:40 | 1 | 70 | 55144-1 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOPS BURNT OPEN ON SERVICE TO PAWN SHOP AT 21ST. ST. REPAIRED LOOPS AND CLEANED UP MESS ON POLE#45-5781 VER/KEP L3/KEP
23746 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2017-08-16 07:50 | 2017-08-16 09:00 | 1 | 70 | 4265521 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, BAD CONNECTION @ ENTRANCE. RESTORED VER/HFP L3/HFP
23747 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-12-29 10:50 | 2022-12-29 12:00 | 1 | 70 | 4374381 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | Bad meter at location. Going to get a new meter to install.Changed out meter. Power restored at 12:00.
23748 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-05-12 12:00 | 2021-05-12 13:10 | 1 | 70 | 4578271 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 38830222D00209 broke at phone line deadend single phase primary pole with transformer and 1 service Released by crew 078H09,open line fuse @ 222-48 @ 1200 repairs made all cust restored @1310 please close ticket thanks.bt
23749 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-25 21:45 | 2009-06-25 22:20 | 2 | 35 | 59669-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA TRANSFORMER BAD 19.9 120/240 ON POLE 1125-517 BY TRK ON AT 21:45 ALSO XFMR ON POLE 1125-179 REFUSED IT AT 22:20 D SAMMONS//COD 2// VER/DBM IDC XXXX
23750 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-06-22 14:30 | 2011-06-22 15:40 | 1 | 70 | 4365241 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUST. HAD BROKEN SERV. NEUT. AT POLE. PULLED METER. BLANKED OUT AND RESEALED. CUST. HAS HAD DAMAGES AND LYCOM GUY GOY SHOCKED ON CABLE YESTERDAY. NEED TO FIX TODAY. SGM. RELEASED BY CREW 078E01;;;; REPAIRED NEUTRAL CONDUCTOR CHECKED VOLTAGE WITH VOLT METER AND BEAST VOLTAGE CHECKED GOOD CLOSE TICKET //VER/GAH IDC TOF1642, CCO, CNT3 XXXX
23751 | South Williamson | 3200302 | BELFRY | TOLER | 2020-05-10 15:25 | 2020-05-10 16:00 | 2 | 35 | 4819911 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout on 1015A58,replaced cutout,restored power at 16;00
23752 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-09-23 18:10 | 2008-09-23 19:20 | 1 | 70 | 66634-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//3001102//VER/CRB IDC XXXX
23753 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-01-27 13:30 | 2020-01-27 14:40 | 1 | 70 | 4341501 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3 19.9 cutouts cracked on primary under ground pole truck acess Released by crew 077S07..replaced bad cutouts..all power restored @ 14:40 OFF 1330//NO OUTAGE TILL 1330
23754 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-06-21 17:41 | 2017-06-21 18:51 | 1 | 70 | 4012251 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE # 453-168. POWER RESTORED AT 1851, PLS CLOSE/ ISO 38830453000168/ COD 1/ VER/BOW
23755 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-01-26 12:15 | 2011-01-26 13:25 | 1 | 70 | 64535-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38581636 // BAD CUTOUT ON POLE 376-358... REPLACED CUTOUT RESTORED POWER AT 13:25 COD-0 PER PO ISO TF 37830376C00358 VER/HFP L3/HFP IDC XXXX
23756 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-01-18 14:50 | 2022-01-18 16:00 | 1 | 70 | 4382301 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole, repaired
23757 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-10-30 22:35 | 2021-10-30 23:10 | 2 | 35 | 4042421 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | we were here on 10-18, changed all connections and customer is still having same issue, need A lineman with 25kva 7200 XFM// no outage until we opened XFM// opened XFM 1150-28 @ 22:35 closed @ 23:10
23758 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-02-10 23:45 | 2009-02-11 00:20 | 2 | 35 | 57555-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP WR # 284610002 OPENED TR @ 2345 BACK ON @ 0020 L3/HFP
23759 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-12-10 09:50 | 2008-12-10 11:00 | 1 | 70 | 56137-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000303// S/C CUTOUT DOOR//VER/CRB IDC XXXX
23760 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2009-09-18 19:48 | 2009-09-18 20:23 | 2 | 35 | 53507-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSF FUSE BROKE VER/KEP L3/KEP IDC XXXX
23761 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2011-02-10 15:16 | 2011-02-10 15:51 | 2 | 35 | H55934-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED CREW--SEND TO TRAVIS RELEASED BY CREW 078S07 CREW ON SITE WILL HAVE TRANSFOMER OPEN AT POLE 212B43526 AFFECTING 2 MORE CUST WHILE MAKING REPAIRS,, NOTIFIED CUSTOMERS OPEN AT 1516//COD 1 + 6 IDCC DUP TO OPEN TRANSFORMER XXXX
23762 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-01-06 18:15 | 2015-01-06 18:50 | 2 | 35 | 4911561 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNT UP WILL REPLACE// REPLACED BAD CURRENT LIMITING FUSE AND RESTORED SERVICE @ 18:50//// OOPENED TRANSFORMER @18:15/ ISO 37830141000161/ COD 2/ VER/BOW L3/DKGXXXX
23763 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-12-11 11:00 | 2020-12-11 12:10 | 1 | 70 | 4761181 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power due to bad lug on transformer. i was able to clean up lug power back on @ 12:10 everything ok
23764 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-04-24 14:50 | 2010-04-24 16:00 | 1 | 70 | 50195-1 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, FOUND LOOSE CONNECTION ON XFMR POLE, RECONNECTED HOT LEG, POWER OK, COMPLTED VER/HFP L3/HFP IDC XXXX
23765 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2019-11-20 13:00 | 2019-11-20 14:10 | 1 | 70 | 4050471 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1740 roe crk 38830333000064 heated up connections at tran--replaced--AND at 1812 roe crk 38830333000055 replaced #4 tran risers and connections--allgood-ds112019
23766 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-03-04 15:31 | 2021-03-04 16:06 | 2 | 35 | 4303471 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced a broken cutout, power restored at 16:06.
23767 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-05-07 16:32 | 2009-05-07 17:42 | 1 | 70 | 66512-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP FALUT POLE 38820941D00476 ON SITE, BAD CUTOUT AT POLE#941-476, CHANGING IT OUT COD-1 ISO POLE 38820941D00476 ENTERED MD-HFP L3/HFP IDCC PN281 XXXX
23768 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2009-10-09 19:25 | 2009-10-09 20:35 | 1 | 70 | 52669-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, BAD CUTOUT, REPLACING IT VER/KEP L3/KEP IDC XXXX
23769 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-08-06 07:30 | 2008-08-06 08:40 | 1 | 70 | 65854-1 | 70 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 2 BAD L. ARRESTORS ON POLE 190-107. LOCATED AT 14501 U.S. 23 LOCKWOOD DIVISION COLUMBIA GAS NEED TO BE REPLACED. SENT EMAIL TO LLOYD RAYBURN VER/HFP IDCC PN36 XXXX
23770 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2016-01-20 14:25 | 2016-01-20 15:35 | 1 | 70 | 4636871 | 70 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER DUE TO BAD SPLICE IN SERVICE DROP.REPAIRED SERVICE , RESTORED POWER AT 15:35, ONLY ONE CUSTOMER AFFECTED.// VER/ ADH
23771 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-01-04 07:21 | 2012-01-04 08:30 | 1 | 69 | 4231571 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN..RE FUSED TRANSFORMER. VER/KEP IDC XXXX
23772 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-01-04 13:42 | 2012-01-04 14:51 | 1 | 69 | 4233351 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE CUST HAD PART POWER, FOUND BAD SQUEEZON ON SECONDARY SIDE, HAVE REPLACED WITH THE RIGHT SQUEEZON, AND EVERYTHING IS BACK TO FULL POWER AT THIS LOC ///VER/CRB IDC XXXX
23773 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-08-22 13:17 | 2016-08-22 14:26 | 1 | 69 | 4825171 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 900-171..CHANGING VER/CRB
23774 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-03-27 19:01 | 2010-03-27 20:10 | 1 | 69 | 55027-1 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMEROPENED TRANSFORMER AT 1955 CLOSED IT AT 2010 DUPLICATE IN HOIS SEE RECORD H1133773-1 VER/HFP L3/HFP IDC XXXX
23775 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-12-19 15:46 | 2011-12-19 16:55 | 1 | 69 | 4189261 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BROKEN 6T XFMR FUSE COD-1 ISO TF 38831101C40359 VER/HFP L3/HFP IDC XXXX
23776 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-12-13 11:59 | 2010-12-13 13:08 | 1 | 69 | 65926-1 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WR#38087294// 6T CHANCE FUSE BROKE//VER/CRB IDC XXXX
23777 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2011-05-30 12:12 | 2011-05-30 13:21 | 1 | 69 | 4209411 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BURNT UP FUSE DOOR//VER/CRB IDCC CCO XXXX
23778 | Hazard | 3311103 | STINNETT | WENDOVER | 2009-05-29 14:46 | 2009-05-29 15:55 | 1 | 69 | 50000-1 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A//COD 1// VER/DBM IDC XXXX
23779 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2014-04-09 14:26 | 2014-04-09 15:35 | 1 | 69 | 4589681 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED LOOP VER/SEF
23780 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2016-11-13 20:01 | 2016-11-13 21:10 | 1 | 69 | 4098601 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED XFR CUTOUT COMPLETE/// VER/DKM
23781 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-12-31 12:53 | 2015-12-31 14:02 | 1 | 69 | 4578671 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 CUS ORIGINALLY, 4 OPENEDLOOP BURNED INTO AT POLE 785-988 AND FELL ACROSS CENTER PHASE///CENTER PHASE ALMOST BURNED INTO///OPENED SWITCHES ON POLE AT 13:40 TO MAKE SAFE FOR REPAIRS////CREW ON SITELOOP BURNED INTO AT POLE 785-988 AND FELL ACROSS CENTER PHASE///CENTER PHASE ALMOST BURNED INTO// VER/ ADH
23782 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-09-16 07:24 | 2019-09-16 08:33 | 1 | 69 | 4022511 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @7-118, checking. Trans. fuse had pulled into, refused @0833.
23783 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2021-09-02 13:52 | 2021-09-02 14:15 | 3 | 23 | 4203021 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out, fuse broke, power restored
23784 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2012-03-09 19:33 | 2012-03-09 20:42 | 1 | 69 | 4567991 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED BROKEN NEUTRAL IN SERVICE VER/HFP L3/HFP IDC XXXX
23785 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2019-12-28 21:06 | 2019-12-28 22:15 | 1 | 69 | 4188111 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | meter is blank per cust// Xfm fuse blown on 197-116 will refuse/// Changed bad cutout and refused xfm @ 22:15 and restored service//cod 1//iso 37820197000116//
23786 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-09-11 17:44 | 2019-09-11 18:53 | 1 | 69 | 4005461 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke, repairs made. pls close. tre
23787 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-04-08 17:16 | 2017-04-08 18:25 | 1 | 69 | 4631121 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE REPAIRED/ ISO 38830092D00722/ COD 1/ VER/BOW L3/HFP XXXHFP
23788 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-03-23 21:11 | 2008-03-23 22:20 | 1 | 69 | 60136-1 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN 6T FUSE VER/ARN IDCC CNT1 XXXX
23789 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-04-13 10:35 | 2012-04-13 11:44 | 1 | 69 | 4670631 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | X-FMR FUSE OPEN ON POLE 354-110. GOING TO CHECK X-FMR AND CUT-OUT BEFORE ENERGIZING. FUSE TAIL PULLED OUT. RE-ENERGIZED X-FMR AT 11:44, RESTORING POWER. 4/13/2012. J.S.B. METER #: 533 767 049.//MADE MDC ///VER/CRB IDC XXXX
23790 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2017-07-25 12:10 | 2017-07-25 12:33 | 3 | 23 | 4177891 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPENED XFMR @ 12:10 TO REMOVE AND INSTALL NEW 1/0 SERVICE DROP DUE TO SERVERAL SPLICES. FETR 13:00 LRM// ALL PWR RESTORED @ 12:33 PLEASE CLOSE TICKET LRM VER/CRB L3/HFP XXXHFP
23791 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-04-03 19:57 | 2014-04-03 21:06 | 1 | 69 | 4569141 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT // COD-1 ISO TF 38830272000196 VER/HFP L3/HFP
23792 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2015-05-11 21:41 | 2015-05-11 22:50 | 1 | 69 | 4416251 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SPLIT BOLT VER/CRB
23793 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-02-22 10:56 | 2021-02-22 12:05 | 1 | 69 | 4216891 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout//repairs made power restored at 12:05
23794 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-08-04 09:01 | 2008-08-04 10:10 | 1 | 69 | 64889-1 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3008001// RESQUEZED BAD CONNECTION AT MAST// VER/DBM IDC XXXX
23795 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-01-30 11:04 | 2019-01-30 12:13 | 1 | 69 | 4734201 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | servicer on site/part power/vem/one cust affected/bad serv-in/replace connections/full power restored 1213/please close ticket/thanks/vem ¦¦ L3/HFP
23796 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-01-19 08:01 | 2018-01-19 09:10 | 1 | 69 | 4756341 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Appears xfmr fuse broke. Restored @ 9:10. sh
23797 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-06-23 13:10 | 2012-06-23 14:19 | 1 | 69 | 4954661 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | WILL CHANGE BAD CUTOUT.ONLY ONE COUSTOMER OUT. ONLY PART POWER. // COD-1 - 3 PHASE CUSTOMER ONLY ISO LF 37830023000310 VER/HFP L3/HFP
23798 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-05-17 20:24 | 2010-05-17 21:33 | 1 | 69 | 64265-1 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED UP CHANGE GATE OUT VER/KEP L3/KEP IDC XXXX
23799 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2014-11-02 22:41 | 2014-11-02 23:50 | 1 | 69 | 4694291 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STREET LIGHT CIRCUT HOT LEG CONNECTION RESTORED VER/ARN VER/DKG L3/DKGXXXX
23800 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2011-01-04 22:06 | 2011-01-04 23:15 | 1 | 69 | 58730-1 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER./// VER/DBM IDC XXXX
23801 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-01-14 14:07 | 2022-01-14 15:16 | 1 | 69 | 4346681 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | service drop burned in 2 at splice, replaced service drop and restored customer
23802 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2021-01-04 10:49 | 2021-01-04 11:12 | 3 | 23 | 4846721 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t broken
23803 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2013-07-05 15:36 | 2013-07-05 16:45 | 1 | 69 | 4471201 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT LEG ON SERV BURNT INTO SERV TO REPAIR,ALL REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT// VER/DBM IDC XXXX
23804 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2018-03-22 07:06 | 2018-03-22 08:15 | 1 | 69 | 4041011 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke /// COD-1 ISO TF 37830296A21152
23805 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-02-26 11:56 | 2013-02-26 13:05 | 1 | 69 | 4849181 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD. ONLY 1 CUSTOMER WITH PART POWER, RESTORED AT 13:05//COD 1// VER/DBM IDC XXXX
23806 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-03-16 10:29 | 2014-03-16 11:38 | 1 | 69 | 4496661 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BAD CUTOUT 7.2KV//COD 1// VER/DBM
23807 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-08-15 19:56 | 2016-08-15 21:05 | 1 | 69 | 4788751 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CUTOUT ALL CUST RESTORED @2105 PLEASE CLOSE TICKET THANKS.BT
23808 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2018-12-19 09:21 | 2018-12-19 10:30 | 1 | 69 | 4579071 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Bad insulink in service drop. GH
23809 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-12-30 10:26 | 2020-12-30 11:35 | 1 | 69 | 4835311 | 69 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | fuse had pulled apart, refused and restored
23810 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2018-05-10 10:06 | 2018-05-10 11:15 | 1 | 69 | 4330501 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout
23811 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-03-09 11:11 | 2008-03-09 12:20 | 1 | 69 | 55652-1 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3001102// SERVE-END MELTED OUT ON CUSTOMERS SD// VER/DBM IDC XXXX
23812 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-02-08 12:39 | 2012-02-08 13:48 | 1 | 69 | 4328111 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECONNECTED LOOSE HOT TAP--EMAIL TO RAYBURN--CUTOUT ARRESTOR AND HOT TAP NEEDS REPLACED--NO TRUCKS VER/KEP IDC XXXX
23813 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-12-22 20:10 | 2008-12-22 21:19 | 1 | 69 | 62828-1 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3103101//REPAIRING CONNECTIONS AND SPLICING W//COD 1// VER/DBM L3/KEP IDC XXXX
23814 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-07-23 19:03 | 2022-07-23 20:12 | 1 | 69 | 4562651 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SD BROKE
23815 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-04-03 20:51 | 2013-04-03 22:00 | 1 | 69 | 4977521 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 1// VER/DBM IDC XXXX
23816 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-02-03 14:31 | 2009-02-03 15:40 | 1 | 69 | 55186-1 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401103 - BAD ARRESTER ON POLE 901-83. 6 T FUSE OUT FUSED UP EVERYTHING OK. // VER/TOM L3/TOM
23817 | Paintsville | 3401102 | FALCON | SALYERSVI | 2012-09-21 16:41 | 2012-09-21 17:50 | 1 | 69 | 4075911 | 69 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN CUTOUT FUSE.CHG OUT CUTOUT FUSE..6 T ///VER/CRB L/3 CRB IDC XXXX
23818 | South Williamson | 3411401 | DEWEY | INEZ | 2018-04-22 08:52 | 2018-04-22 10:00 | 1 | 68 | 4262341 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke on pole 743-198/only feeds car wash///repairs made//restored at 10:00//complete//em/ ISO 38830743C40198/ COD 1 L3/HFP
23819 | South Williamson | 3411401 | DEWEY | INEZ | 2017-11-20 00:07 | 2017-11-20 01:15 | 1 | 68 | 4587161 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | dept highways representative currently on site //xfmr cutout broke on pole 744-454//repairs made//restored at 1:15//cod 1
23820 | South Williamson | 3411401 | DEWEY | INEZ | 2018-12-13 10:44 | 2018-12-13 11:52 | 1 | 68 | 4561431 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WATER COMPANY CALLED, LINE FUSE OUT. BROKE CUTOUT 38830767C30266 ON @ 1152 L3/HFP
23821 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2009-12-07 09:21 | 2009-12-07 10:29 | 1 | 68 | 65863-1 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD CONNECTION L3/HFP IDCC CCU XXXX
23822 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-04-09 21:44 | 2015-04-09 22:52 | 1 | 68 | 4300651 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTTAP LEAD ON XFMER @ POLE 832-22 HAS BURNED INTO///REPAIRS MADE///CLOSED XFMER BACK IN ON POLE 832-22 @ 22:52///COMPLETE BR//COD 1// VER/DBM
23823 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-03-08 13:52 | 2017-03-08 15:00 | 1 | 68 | 4537471 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SEC. LEAD BURNT OPEN ON XFM...REPAIRED/ ISO 38831101D30418/ COD 1/ VER/BOW
23824 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-02-12 08:42 | 2014-02-12 09:50 | 1 | 68 | 4375091 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY CONNECTIONS AT SECONDARY POLE 37820032A00110. ONLY ONE CUSTOMER WAS OUT.***CHANGE ISO POLE*** VER/SEF
23825 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2015-04-05 16:22 | 2015-04-05 17:30 | 1 | 68 | 4278291 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK BURN INTO REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT/ ISO 38830207A00198/ COD 1
23826 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-09-07 19:30 | 2010-09-07 20:38 | 1 | 68 | 64393-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED BAD CONNECTIONS AMD SERVICE1 IDC XXXX
23827 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-06-24 11:59 | 2018-06-24 13:07 | 1 | 68 | 4656891 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Called customer multiple times and left message still no answer fuse broke/ ISO 38831040000072/ COD 1
23828 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2011-08-28 12:20 | 2011-08-28 13:28 | 1 | 68 | 4769911 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK PULLED APART AND BROKEN NOT BLOWED // VER/CRB IDC XXXX
23829 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-01-16 00:45 | 2010-01-16 01:53 | 1 | 68 | 54883-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT DOOR HAS BURNT UP WILL REPLACE. TIM MCCOY VER/ARN IDC XXXX
23830 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-03-31 14:11 | 2008-03-31 14:45 | 2 | 34 | 62316-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3314401//POLE 473-175 IS ROTTED OFF AND LEANING OVER WILL NEED TO REPLACE ASAP PLEASE SEND THIS TICKETT TO G WHITAKER RELEASED BY CREW 074S07//COD 2//OPENED UP TO MAKE REPAIRS @ 1411//CLOSED @ 1445// VER/DBM IDC XXXX
23831 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2015-05-02 06:52 | 2015-05-02 08:00 | 1 | 68 | 4383281 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV DOOR REPLACED VER/KEP
23832 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-11-27 08:41 | 2017-11-27 09:15 | 2 | 34 | 4603571 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link appeared to have broken. Restored @ 9:15. sh
23833 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-05-05 09:07 | 2016-05-05 10:15 | 1 | 68 | 4176451 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACED OLD FUSE DOOR VER/AWD
23834 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-03-14 16:59 | 2014-03-14 18:07 | 1 | 68 | 4493421 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER , BAD SPLICE IN SERVICE DROP MADE REPAIRS RESTORED POWER AT 18:07 VER/SEF
23835 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2012-05-04 22:34 | 2012-05-04 23:42 | 1 | 68 | 4745711 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | MADE TEMPOARY REPAIRS---E MAIL TO RAYBURN--NEED 556 BASKET AND HOT TAP LEAD REPLACED ON PRIMARY UG SERVICE//EMAILED TO RAYBURN//COD 1//ISO// VER/DBM IDCC PN4721 XXXX
23836 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-03-27 08:02 | 2020-03-27 09:10 | 1 | 68 | 4515021 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Bad section of 1/0 secondary, fixed, power restored
23837 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-06-24 11:40 | 2021-06-24 12:48 | 1 | 68 | 4802771 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | re-energizing line after intalling new pole// off at 1140 -- on at 1248 bad dead end ins. on pole 37830262000122, made repairs and restored
23838 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-06-28 08:49 | 2022-06-28 09:57 | 1 | 68 | 4338581 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | cutout door burnt up/repairs made. tre
23839 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-03-08 16:59 | 2011-03-08 18:07 | 1 | 68 | 51904-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SQUEEZE ON PULLED APART ON SERVICE NEUTRAL I REPLACED IT// VER/DBM IDC XXXX
23840 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2009-03-10 13:57 | 2009-03-10 15:05 | 1 | 68 | 56965-1 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP COD-1 HOT TAP BURNT BASKET INTO// REPLACED HOTTAP AN ARRESTOR L3/HFP IDC XXXX
23841 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-09-01 16:26 | 2012-09-01 17:34 | 1 | 68 | 4992321 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER/// OPENED XFMR FUSE ON POLE 172-51, TO SEC. LEADS WERE RUBBING TOGETHER AND BURN,T ONE INTO. FIXED LEAD, POWER RESTORED. OPENED XFMR AT 17:15 CLOSED XFMR AT 17:34. DUPLICATE IN HOIS FOR THIS ONE COD-9 ISO TF 37830172A00051 SEE DUP H4992321 VER/HFP L3/HFP IDC XXXX
23842 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-02-23 20:55 | 2016-02-23 21:12 | 4 | 17 | 4752621 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENING FUSE ON 620-62, REPAIRING BAD CONN, OPENED FUSE AT 2055 APR AT 2112 CLOSE TICKET/ ISO 38830620000062/ COD 4/ VER/BOW
23843 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-01-11 15:17 | 2022-01-11 16:25 | 1 | 68 | 4336791 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got broke cutout
23844 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2020-05-01 15:27 | 2020-05-01 16:35 | 1 | 68 | 4785991 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad secondary connection on pole 296-B4-326, power restored at 16:35.
23845 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-09-28 14:32 | 2018-09-28 15:40 | 1 | 68 | 4178061 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service neutral was broke loose at the house knob, opened trans. @1124-C-37 @1432 to make repairs. Made repairs and closed back in @1540.//NO OUTAGE TILL TRANS OPEN
23846 | Pikeville | 3421001 | BREAKS | CITY | 2017-01-16 18:45 | 2017-01-16 19:53 | 1 | 68 | 4303681 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE FAILED DUE TO AGE RE-FUSED CUTOUT RESTORED POWER AT 19:53 37820220D10383 VER/AWD L3/HFP XXXHFP
23847 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2016-02-18 09:37 | 2016-02-18 10:45 | 1 | 68 | 4732271 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | A PHASE OUT ON ARRIVAL, OPENED ALLXMF AT 1036 REPLACED CURRENT LIMMITING FUSE APR AT 1045 CLOSE TICKET //DC CLEARING POLE AND ISOLATING POLE SHOULD BE THE SAME. INCORRECT LOCATION ORIGINALLY. BAD CURRENT LIMITING FUSE
23848 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-04-24 20:02 | 2018-04-24 21:10 | 1 | 68 | 4275181 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cut out broke on pole # 266-17/// will replace// Put pole fire out and replaced broken cutout on pole #266-17 @ 21:10/// Send copy to Mike hatfield pole is halfway burnt into/// Only 1 customer affected// 3401703 37820266000017 L3/HFP
23849 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-06-11 17:23 | 2010-06-11 18:31 | 1 | 68 | 60228-1 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT METER POLE ,MADE REPAIRS RESTORED POWER AT 18:31 VER/HFP L3/HFP
23850 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-01-08 20:12 | 2011-01-08 21:20 | 1 | 68 | 59944-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV-IN FROZE OUT REPLACED WITH NEW CONNECTIONS. // VER/TOM IDC XXXX
23851 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-01-18 09:26 | 2015-01-18 10:00 | 2 | 34 | 4942461 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830019D00013 BAD CUTOUT CHGED IT 2-CUST ON TRANS. VER/CRB L3/HFP XXX
23852 | Hazard | 3301401 | COMBS | COMBS | 2016-02-15 17:14 | 2016-02-15 18:22 | 1 | 68 | 4698281 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT..REPLACED CUTOUT, POWER RESTORED @ 18:22 VER/CRB L/3CRB
23853 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-01-31 10:30 | 2013-01-31 10:47 | 4 | 17 | H4766981 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S08 CREW REQ, NO 4 CU,TRUCK O.K WIRE BROKE AT RUN-AROUND SHOE, LINE STILL HOT WILL NEED TO OPEN UP LINE FUSE TO WORK FAULT POLE 137-13 WIRE NEED RE-SAG ON POLE 137-297SLIP THRU TIE WIRES TWO POLES TO WORK RELEASED BY CREW 078S09 ///VER/CRB L/3 CRB IDC DUP TO OPEN FUSE XXXX
23854 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-03-28 12:02 | 2008-03-28 13:10 | 1 | 68 | 61579-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116102//BROKEN CUTOUT ON BANK POLE, SOMEONE FROM SHOP IS BRINGING ME A CUTOUT, ALL THREE XFMRS ARE OPEN UNTIL REPAIRS ARE MADE// COD 1 - GRAYSON UTILITIES COMMISSION ONLY ONES ON THIS THREE PHASE //// VER/TOM IDC XXXX
23855 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2020-03-12 12:52 | 2020-03-12 14:00 | 1 | 68 | 4471951 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad c/o on transformer, i have chg all good here at this time, time on 1400 by amg
23856 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-08-24 15:23 | 2018-08-24 15:40 | 4 | 17 | 4995481 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole greg shouse will bring big bucket to make repaires Released by crew 077H14 1523-1540
23857 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2012-01-08 14:47 | 2012-01-08 15:55 | 1 | 68 | 4241321 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED CONNECTIONS// VER/DBM IDC XXXX
23858 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-08-04 22:22 | 2021-08-04 23:30 | 1 | 68 | 4005851 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRF IS OUT,WILL RE-FUSE/////////RE-FUSED&RESTORED,FUSE APPEARED TO HAVE MELTED OUT
23859 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-06-11 18:36 | 2008-06-11 19:10 | 2 | 34 | 62822-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3117601// 10T ME FUSE LINK BROKE // VER/TOM IDC XXXX
23860 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-05-29 15:06 | 2009-05-29 15:40 | 2 | 34 | 50106-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BAD....//COD 2// VER/DBM IDC XXXX
23861 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-01-04 11:37 | 2022-01-04 12:45 | 1 | 68 | 4299001 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans cutout broke @ 358-C1-490,Will be making repairs.
23862 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-01-11 13:37 | 2019-01-11 14:45 | 1 | 68 | 4659761 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout, apr at 1445 close ticket L3/HFP
23863 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-12-11 20:45 | 2022-12-11 21:02 | 4 | 17 | 4250601 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 11B-57. will make repairs. opened at 20:45 closed at 21:02
23864 | Paintsville | 3409302 | KENWOOD | AUXIER | 2020-06-15 19:52 | 2020-06-15 21:00 | 1 | 68 | 4024431 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout was broke. I replaced and restored customer @21:00
23865 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-03-28 20:17 | 2012-03-28 21:25 | 1 | 68 | 4629411 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE CKING TROUBLE//TRANSFORMER LEAD SPLICE // THIS IS 499 SANDLICK FORK//WRONG ADDRESS FOR THIS ACCOUNT COD-1 ISO TF 37830155000133 VER/HFP L3/HFP IDC XXXX
23866 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-10-02 14:11 | 2019-10-02 14:45 | 2 | 34 | 4086741 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer went bad when we opened it up to change cutout// opened at 1355 closed at 1445 transformer changed power restored complete RN
23867 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-04-29 10:31 | 2010-04-29 10:48 | 4 | 17 | 52683-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | REMOVED PRIMARY & SECONDARY GUY WIRE. PLESE SEND TO DON WASHINGTON TO GET THEM RELOCATED. OPENED XFORMER AT 10:31, AND CLOSED AT 10:48.//COD 4// VER/DBM IDC XXXX
23868 | Pikeville | 3421001 | BREAKS | CITY | 2014-03-16 08:42 | 2014-03-16 09:50 | 1 | 68 | 4496471 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON ONE PHASE WIRE AT THE HOUSE// VER/DBM
23869 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-06-28 09:23 | 2010-06-28 10:31 | 1 | 68 | 58824-1 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER CONNECTION BAD, ONLY ONE CUSTOMER AFFECTED... REPLACED CONNECTION RESTORED POWER AT 10:25, CUSTOMER WAS MAPPED TO WRONG XFMR RELEASED BY CREW 077S11//VER/CRB IDCC PN303 XXXX
23870 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2009-03-11 15:25 | 2009-03-11 15:59 | 2 | 34 | 57260-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP ON SITE, POLE ON FIRE, CALLED CREW FOR HELP, PULLED XFORMER OFF AT1525, BACK ON AT 1559 L3/HFP IDC XXXX
23871 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2018-06-25 15:15 | 2018-06-25 16:23 | 1 | 68 | 4663791 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutouts serving a bank on this pole. Cutouts remained open for customer to make repairs on their side and they stated that they will call back when their repairs are complete.
23872 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2009-01-03 10:17 | 2009-01-03 11:25 | 1 | 68 | 51016-1 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3010602// REPLACED BAD CONNECTOR - 1 CUST AFFECTED// VER/TOM L3/TOM IDC XXXX
23873 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2019-09-25 18:26 | 2019-09-25 19:34 | 1 | 68 | 4058541 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | nuetral broken on service drop.repaired service drop.opened trans on 965C16 at 19:21 and restored power at 19:34
23874 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2014-03-11 14:32 | 2014-03-11 15:40 | 1 | 68 | 4468391 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE SERV BAD === REPAIRED == POWER OK VER/HFP L3/HFP
23875 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-10-26 20:22 | 2015-10-26 21:30 | 1 | 68 | 4378731 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE IN XFMER FUSE ON POLE 857-161///REFUSED AT 21:30///COMPLETE BR VER/CRB
23876 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2019-01-30 17:19 | 2019-01-30 18:27 | 1 | 68 | 4739661 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | red-red serve in was frooze apart , I remade splice ¦¦ L3/HFP
23877 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2020-07-22 17:41 | 2020-07-22 18:49 | 1 | 68 | 4205211 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse was in ,,,replaced broke xfr cutout 184-71 ,,only 1 customer off ,,,complete
23878 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-03-23 11:04 | 2018-03-23 12:12 | 1 | 68 | 4045181 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout on 37830158000119. power restored
23879 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-11-11 21:17 | 2014-11-11 22:25 | 1 | 68 | 4720981 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNED DN DUE TO A FAILED SPLICE. ONLY ONE CUSTOMER AFFECTED.// VER/ ADH
23880 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-11 12:59 | 2008-07-11 13:33 | 2 | 34 | 51103-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 30087BACK01// NEEDS 10 KVA 19.9 TRANS TRUCK TO POLE POWER IS ON //OPENING XFR @ 12:59 TO REPLACE XFR/BACK ON @ 13:33REPLACED XFR AND CHECKED ALL CONNECTIONS VOLTAGE CHECKED 124 VOLTS . THIS IS A 120 VOLT SER//VER/CRB IDCC TOF0903, TON0944 XXXX
23881 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-06-29 16:10 | 2015-06-29 17:18 | 1 | 68 | 4692611 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITED FUSE ON XFMR , REMOVED FUSE , RESTORED POWER AT 17:18 VER/CRB
23882 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-03-20 15:52 | 2010-03-20 17:00 | 1 | 68 | 52022-1 | 68 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRING CONNECTION// VER/DBM IDC XXXX
23883 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-12-19 18:17 | 2014-12-19 19:25 | 1 | 68 | 4871351 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG AND NEUTRAL BURNT INTO IN SERVICE WILL REPAIR/// REPAIRED BAD CONNECTIONS IN SERVICE DROP @ WEARHERHEAD//// EVERYTHING OK NOW VER/CRB
23884 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-06-18 21:20 | 2010-06-18 22:28 | 1 | 68 | 51150-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED AND RESTORED @ 22:28. SH VER/KEP L3/KEP
23885 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2018-12-26 18:32 | 2018-12-26 19:40 | 1 | 68 | 4600151 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 19:40. sh L3/HFP
23886 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2014-12-16 18:42 | 2014-12-16 19:50 | 1 | 68 | 4865431 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED TRANSFORMER FUSE THAT HAD BROKE. ONLY ONE CUSTOMER WAS OUT.//CORRECT ISO POLE IS 38820941B00462 MADE MDC VER/CRB
23887 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2017-04-22 23:19 | 2017-04-23 00:27 | 1 | 68 | 4669871 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED THE TRANSFORMER FUSE THAT BROKE.//COD 1// VER/DBM L3/HFP XXXHFP
23888 | Whitesburg | 3312901 | JENKINS | KONA | 2014-03-07 05:02 | 2014-03-07 06:10 | 1 | 68 | 4458161 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE TAIL ROTTED INTO VER/KEP IDC XXXX
23889 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-05-13 12:55 | 2013-05-13 13:29 | 2 | 34 | 4109831 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON BANK OF TRANSFORMER VER/SEF IDCC XXXX
23890 | Hazard | 3303902 | LESLIE | WOOTON | 2011-04-29 09:32 | 2011-04-29 10:40 | 1 | 68 | 52210-1 | 68 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9KV CUTOUT OPENED LINE FUSE @1020 AND CLOSED BACK @1040
23891 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-10-18 13:57 | 2008-10-18 15:04 | 1 | 67 | 56864-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3002107// BROKE 6T TRANS FUSE LINK// BACK ON @ 1504 VER/TOM IDC XXXX
23892 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-10-02 18:33 | 2014-10-02 19:40 | 1 | 67 | 4545741 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION AT TRANSFOMER IN SERVICE WAS BURNT INTO///// RE-DONE CONNECTION AND RESTORED SERVICE/// ONLY 1 CUSTOMER WAS AFFECTED// VER/DBM VER/DKG L3/DKGXXXX
23893 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2016-11-12 12:23 | 2016-11-12 13:30 | 1 | 67 | 4095941 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION @ ENTRANCE/ ISO 39831123D16048/ COD 1/ VER.BOW
23894 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-05-10 16:38 | 2020-05-10 17:45 | 1 | 67 | 4820001 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burnt up on pole 351-B-195. line fuse in on 351-B-11. cutout gate replaced.. power restored @17:45
23895 | Hazard | 3303901 | LESLIE | HYDEN | 2013-10-28 08:53 | 2013-10-28 10:00 | 1 | 67 | 4968771 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT GATE //VER/GAH
23896 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-01-21 19:32 | 2011-01-21 20:39 | 1 | 67 | 63483-1 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS//////SERVE-IN HAD FROZEN OUT,REPAIRED AND RESTORED,ALL OK AFTERWARDS VER/KEP L3/KEP IDC XXXX
23897 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-10-23 11:26 | 2015-10-23 12:33 | 1 | 67 | 4371231 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL SPLICE PULLED OUT ON SERVICE DROP, REPAIRED NEUTRAL RESTORED POWER AT 12:33.. VER/KEP
23898 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2010-08-28 09:43 | 2010-08-28 10:50 | 1 | 67 | 61449-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN//// LOOKED LIKE FUSE BROKE, REFUSED POWER RESTORED. VER/KEP L3/KEP IDC XXXX
23899 | Hazard | 3309302 | VICCO | JEFF | 2017-03-27 11:24 | 2017-03-27 12:31 | 1 | 67 | 4588271 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE BAD ON SECODARY POLE === REPAIRED VER/CRB
23900 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-05-03 15:33 | 2022-05-03 16:40 | 1 | 67 | 4829211 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | made repairs, power restored
23901 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-08-24 13:28 | 2015-08-24 14:35 | 1 | 67 | 4168421 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD XMFER & CURRENT LIMITER FUSE./ ISO 38830092A00377/COD 1/ VER/BOW
23902 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2012-04-15 17:53 | 2012-04-15 19:00 | 1 | 67 | 4674681 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP FAILED ON THE PRIMARY METERING POLE. I REPLACED THE CLAMP. ///VER/CRB IDC XXXX
23903 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-05-06 17:23 | 2013-05-06 18:30 | 1 | 67 | 4078581 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT..POLE 1013B69.CUST MIS-MAPPED..CAN REPLACE SAFELY..// ENTERED MD CCC COD-1 ISO TF 38821013B00069 VER/HFP L3/HFP IDC XXXX
23904 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-08-25 10:53 | 2015-08-25 12:00 | 1 | 67 | 4170661 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HAD FAILED ON SECONDARY POLE, REPLACED/ ISO 37830229000141/ COD 1
23905 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2022-09-01 15:13 | 2022-09-01 16:20 | 1 | 67 | 4827181 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection repaired and power restored 16:20
23906 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-05-18 18:38 | 2013-05-18 19:45 | 1 | 67 | 4131771 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 177D-28 @ MOUTH OF COMBS BR. @ DWARF . 15 KVA-7200. FEEDS TV BOOSTER - MADE SERVICE UP ON OPEN WIRE SECONDARY THATS ON POLE, MAY LEAVE LIKE IS OR HANG NEW XFMR NEXT WEEK TO PUT BACK LIKE WAS. CAN GET TRUCK TO POLE. ///VER/CRB L/3 CRB IDC XXXX
23907 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-08-31 19:38 | 2014-08-31 20:45 | 1 | 67 | 4442171 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS MELTED OUT DOOR ON CUTOUT DIDNT DROP, APR AT 2045 CLOSE TICKET//COD 1
23908 | Hazard | 3303902 | LESLIE | WOOTON | 2013-11-26 15:18 | 2013-11-26 16:25 | 1 | 67 | 4076441 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANSF === CHANGED CUTOUT === POWER OK === PUT POLE FIRE OUT ===//COD 1// VER/DBM
23909 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-01-10 11:38 | 2016-01-10 12:45 | 1 | 67 | 4600621 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | HAD ONE TRANSFORMER FUSE BROKE INTO POWER RESTORED VER/CRB
23910 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-06-02 11:23 | 2010-06-02 12:30 | 1 | 67 | 55323-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTIONS @ WEATHERHEAD VER/KEP L3/KEP IDC XXXX
23911 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2009-12-04 11:13 | 2009-12-04 12:20 | 1 | 67 | 53444-1 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP NEUTRAL WAS BURNED APART. MR. MULLINS STATED THAT THIS HAS BEEN IN THIS CONDITION SINCE SUNDAY MORNING. IDCC CDC89 XXXX
23912 | South Williamson | 3411401 | DEWEY | INEZ | 2012-11-26 16:46 | 2012-11-26 17:53 | 1 | 67 | 4422741 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CUSTOMER HAS OPEN NEUTRAL IN UNDERGROUND COMING TO METER PEDESTAL// NOT LIVING HERE YET SO HE IS OK WITH US REPAIRING TOMORROW//PLEASE HAVE PAINTSVILLE LINE CREW WORK IN THE MORNING// RELEASED BY CREW 079S01//SERVICER CREATED OPS ORDER 036290870 FOR THIS//CUSTOMER HAS NOT MOVED IN YET AND IS OK IF WE WORK THIS TOMORROW MORNING // VER/DBM IDC XXXX
23913 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-05-25 12:59 | 2021-05-25 14:06 | 1 | 67 | 4620391 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced a burnt out cutout gate and restored power at 14:06.
23914 | Pikeville | 3407103 | TOPMOST | KITE | 2013-11-21 11:00 | 2013-11-21 12:07 | 1 | 67 | 4061041 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED TIM HALL CREW ON THE WAY TO CHANGE 10KVA TO A 25KVA. RELEASED BY CREW 074S11..GOT XFMR CHANGED OUT.SERVICE RESTORED 12:07.. VER/SEF
23915 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2009-10-17 09:53 | 2009-10-17 11:00 | 1 | 67 | 53420-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000304// CREWS REPLACING POLE INSIDE AK STEELE SLAG PLANT // DDC CONTACTED CSX, ONE OF THIER METERS WILL BE AFFECTED FOR 2 HRS // COD 1 // RELATED TO 52283-1 // VER/DBM IDC XXXX
23916 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2019-03-03 10:08 | 2019-03-03 11:15 | 1 | 67 | 4946431 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | meter burnt up, replaced on @ 1115burn up meter,1 customer L3/HFP
23917 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-11-06 15:05 | 2015-11-06 16:12 | 1 | 67 | 4416031 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED CUST 4/3 SER. DROP POWER RESTORED,1 CUST VER/CRB
23918 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-12-13 12:49 | 2017-12-13 13:56 | 1 | 67 | 4646431 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse 37830246D00122
23919 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2012-11-15 11:33 | 2012-11-15 12:40 | 1 | 67 | 4399881 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | I REDID XFMR LEADS VER/KEP IDC XXXX
23920 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-10-23 09:44 | 2018-10-23 10:51 | 1 | 67 | 4313721 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line cutout on pole 519-20 is bad, replaced cutout restored power at 10:51 L3/HFP
23921 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-06-01 17:18 | 2015-06-01 18:25 | 1 | 67 | 4495601 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING FAILED TRANSFORMER CUTOUT VER/CRB
23922 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2021-04-22 09:23 | 2021-04-22 10:30 | 1 | 67 | 4470531 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection @ secondary. repaired
23923 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2012-12-21 08:07 | 2012-12-21 09:14 | 1 | 67 | 4497901 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE-IN CONNECTIONS WERE HEATING UP AND EVENTUALLY CAUSED AN INSULATION FAILURE AND SHORTED HOT LEGS INTO.MADE NECESSARY REPAIRS,ALL OK AFTERWARDS ////VER/CRB L/3 CRB
23924 | Paintsville | 3409302 | KENWOOD | AUXIER | 2011-01-19 15:13 | 2011-01-19 16:20 | 1 | 67 | 62775-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. REPLACED CUTOUT. SH //COD 1// VER/DBM IDC XXXX
23925 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2020-03-11 13:53 | 2020-03-11 15:00 | 1 | 67 | 4469311 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Service neutral had burndt into midspan, I changed out entire service, power restored @1500.
23926 | Hazard | 3308002 | JACKSON | PANBOWL | 2022-05-18 13:49 | 2022-05-18 14:56 | 1 | 67 | 4907261 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp broke open line fuses on pole 1060b1 423 20 t fuses
23927 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-04-09 13:50 | 2010-04-09 14:57 | 1 | 67 | 61624-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT IS BROKEN,HANGING IN CLEAR,WILL REPLACE IT.//////////REPLACED CUT-OUT,RESTORED POWER,ALL OK AFTERWARDS//VER/CRB IDC XXXX
23928 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2010-06-02 18:41 | 2010-06-02 19:48 | 1 | 67 | 55563-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE CONNECTION BURNT OPEN ON XFMR POLE. RE-SQUEEZED SECONDARY CONNECTIONS. SH// VER/DBM IDCC CDC89 XXXX
23929 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2015-09-19 11:13 | 2015-09-19 12:20 | 1 | 67 | 4250621 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP AND BROKE. REPLACED GATE AND REFUSED POWER AT 1220/ ISO 37830469000087/ COD 1/ VER/BOW
23930 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-01-16 14:10 | 2012-01-16 15:17 | 1 | 67 | 4264891 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SLIC E BURNED INTO ON XFMR POLE COULD NOT MAKE REPAIRS POLE IS ROTTEN AND NEEDS CHANGED ASAP PLEASE FORWARD TO GLEN COMBS AND DOUG CHRISTIAN WILL BE MANUAL JOB CREW 077H01 1445HRS RELEASED BY CREW 077H01 ////VER/CRB IDC XXXX
23931 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-11-08 07:18 | 2009-11-08 08:25 | 1 | 67 | 50765-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE DOWN FUSE BROKE INTO TR CC 1 VER/PDP IDC XXXX
23932 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-07-20 11:48 | 2012-07-20 12:55 | 1 | 67 | 4784781 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-512 BAD CUTOUT DOOR 6T TRANS. FUSE SEND NOTE TO RAYBURN BAD LA NEED CUTOUT AND LA CHGED NO TRUCK TALK TO CUST DOGS IN YARD SENT EMAIL AS REQUESTED // COD-1 ISO TF 38830091C00512 VER/HFP L3/HFP
23933 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-12-15 10:44 | 2010-12-15 11:51 | 1 | 67 | 50488-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XFMR AND RE-MADE NEUTRAL CONNECTIONS COD-1 ISO TF 37830179D00041 VER/HFP L3/HFP IDC XXXX
23934 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2016-06-22 21:23 | 2016-06-22 22:30 | 1 | 67 | 4411441 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REMOVED RED TAG, NEW CONNECTION @ XFMER VER/AWD
23935 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-11-09 12:29 | 2012-11-09 13:36 | 1 | 67 | 4377101 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD 25 KVA, 7.2 KV, CORRECT POLE # IS 155-290, ALL THIS FEEDS IS STREET LIGHT AND ACTIVE METER THAT IS NOT FEEDING ANYTHING RELEASED BY CREW 077S02//PAM FORD MADE MDC//1 CUST ///VER/CRB L/3 CRB IDCC PN196 XXXX
23936 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2018-06-19 20:44 | 2018-06-19 21:51 | 1 | 67 | 4625391 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout complete
23937 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-04-11 22:17 | 2016-04-11 23:24 | 1 | 67 | 4083111 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUST AND THEY CHECKED BREAKERS////HOT TAP BURNT OFF WILL REPAIR..REPAIRS MADE.. VER/CRB
23938 | Pikeville | 3421001 | BREAKS | CITY | 2015-01-12 09:53 | 2015-01-12 11:00 | 1 | 67 | 4929921 | 67 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON PHASE ON SECONDARY ON THE SECONDARY POLE. ONE CUSTOMER ONLY VER/CRB L3/DKGXXXX
23939 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-05-08 09:23 | 2008-05-08 10:30 | 1 | 67 | 58155-1 | 67 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007904//,,,,BROKE CUTOUT ON POLE 621-70,, I WILL REPLACE,,,,I REPLACED CUTOUT AND RESTORED POWER// COD 1 // VER/TOM IDC XXXX
23940 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-04-24 21:17 | 2011-04-24 22:23 | 1 | 66 | 63780-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WR#39675505 POLE 20-3512 ROTTEN 40/4 POLE TRUCK OK PRI. DEAD END OPEN WIRE DEAD END RELEASED BY CREW 078S08. WINDSTREAM POLE. RELEASED BY CREW 078E01/WILL OUTAGE ONE CUST TO CHANGE POLE/FETR 2230/VEM// OPENED AT 2117 & RESTORED AT 2223 //VER/GAH IDC XXXX
23941 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-01-13 09:02 | 2016-01-13 10:08 | 1 | 66 | 4616481 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL WIRE BROKE INTO AT CUSTOMERS TRL. POLE VER/CRB
23942 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-08-25 10:10 | 2012-08-25 11:16 | 1 | 66 | 4970971 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE//COD 1// VER/DBM IDC XXXX
23943 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-07-15 14:49 | 2010-07-15 15:55 | 1 | 66 | 50639-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK HAS BROKEN AND POWER TRACKING THROUGH DOOR. I AM GOING TO REFUSE TRANS. I REFUSED TRANS//VER/CRB IDC XXXX
23944 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-02-15 14:15 | 2019-02-15 14:48 | 2 | 33 | 4797971 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | arrived RM line fuse cutout broke on pole 187-12 crew replacing cutout time on 14:48 please cloce tic RM
23945 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2012-09-27 16:19 | 2012-09-27 17:25 | 1 | 66 | 4093241 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR MELTED OUT ON POLE 796-112///REPLACED DOOR/////RESTORED AT 1725//COMPLETE//EM COD-1 ISO LF 38820796B00112 VER/HFP L3/HFP IDC XXXX
23946 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2020-01-13 07:19 | 2020-01-13 08:25 | 1 | 66 | 4295741 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003702/gaj/all out disp bobby reynolds 3345. He was leaving parking lot and customer flagged him down. He reports broken cutout L3/HFP
23947 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-04-05 12:35 | 2013-04-05 13:08 | 2 | 33 | 4981711 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ///VER/CRB L/3 /CRB IDC XXXX
23948 | Hazard | 3302704 | HAZARD | KENMONT | 2015-12-19 15:49 | 2015-12-19 16:55 | 1 | 66 | 4545591 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SEC. CONNECTION. VER/CRB
23949 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-03-04 20:21 | 2013-03-04 20:54 | 2 | 33 | 4870411 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED BASE HAD TRANSFORMER FUSE OFF AT 2021 HRS TO 2054 HRS ///VER/CRB L/3 CRB IDC XXXX
23950 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2022-04-19 15:50 | 2022-04-19 16:12 | 3 | 22 | 4779821 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Repaired neutral connection on transformer. Opened xformer @ 15:50. Closed @ 16:12
23951 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-01-22 11:44 | 2013-01-22 12:50 | 1 | 66 | 4728271 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER, REPLACED WIRE, ALL POWER RESTORED COD-1 VER/HFP L3/HFP IDC XXXX
23952 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-01-22 17:15 | 2016-01-22 17:37 | 3 | 22 | H4641801 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | *****SEE 4641801*** BAD CUT OUT ON POLE 227-293, B PHASE WILL OPEN A AND C PHASE TO REPLACE CUT OUT ( OPENED A&C @1715),,,B AND C PHASE CUT OUTS WHER BAD REPLACE BOTH../ BACK ON AT 1737/ ISO 37830227A10293/ COD 23/ VER/BOW
23953 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-07-29 16:42 | 2017-07-29 17:15 | 2 | 33 | 4204831 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830069A10201 BAD CUTOUT DOOR REPLACED VER/CRB
23954 | Pikeville | 3413401 | GARRETT | GARRETT | 2017-05-17 15:14 | 2017-05-17 16:20 | 1 | 66 | 4808301 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SD PULLED LOOSE, REPLACED 4/3 SD WITH 2/3 SD AND PERFORMED BUDEN TEST AT METER, ALL VOLTAGE CHECKS OK, ALL WORK COMPLETE / GXJ VER/CRB /// CHANGING TO SERVICE OUTAGE 10 MINUTES AFTER SERVICER ARRIVED = L3/HFP HFPC MCCNI CC CDC85 FEC57
23955 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-01-25 15:34 | 2020-01-25 16:40 | 1 | 66 | 4339051 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout will replace power restored at 16:40
23956 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-11-18 10:55 | 2022-11-18 12:01 | 1 | 66 | 4158611 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 service is broken mid span and held by hot leg . opened transformer @12:01 . talked with CSX unavailable for access. CSX will contact us when they can get us through the gate customer is aware of the power being out and is OK.
23957 | Hazard | 3420001 | SOFT SHELL | VEST | 2019-01-16 18:38 | 2019-01-16 19:44 | 1 | 66 | 4679771 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | broke fuse L3/HFP
23958 | Hazard | 3308001 | JACKSON | S.JACKSON | 2021-05-21 15:43 | 2021-05-21 16:05 | 3 | 22 | 4607941 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout
23959 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-10-21 09:53 | 2020-10-21 10:15 | 3 | 22 | 4572381 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout going bad @74-35, had to open trans. to change out. Opened @0953, closed back in @1015.
23960 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-08-31 13:27 | 2020-08-31 14:33 | 1 | 66 | 4407811 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required 6t
23961 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-05-05 20:22 | 2009-05-05 21:28 | 1 | 66 | 57367-1 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR FAILED ON SECONDARY RISER PART OUT ONLY//3300601//VER/CRB
23962 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-10-01 13:49 | 2014-10-01 14:55 | 1 | 66 | 4542121 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25KVA BAD LARRY KINNEY CALLED IN ON THIS CHANGING OUT S RAY COD-1 ISO TF 38831151B10775 VER/HFP L3/HFP
23963 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-01-06 16:10 | 2021-01-06 17:16 | 1 | 66 | 4852691 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse appears to have broke. Restored @ 17:16. sh
23964 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-02-19 09:40 | 2010-02-19 10:46 | 1 | 66 | 59097-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT ON TRANSFORMER ON POLE 1084-308, FUSE BROKE INTO//COD 1//ISO 38831084A00308// VER/DBM IDC XXXX
23965 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-08-12 12:50 | 2022-08-12 13:12 | 3 | 22 | 4733021 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Reported by Dave lewis said a cutout is broken no truck access crew required 1250-1312Reported by Dave lewis said a cutout is broken no truck access crew required. opened Xfmr at 12:50. repairs made and restored at 13:12 Released by crew 074H01
23966 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2009-01-10 14:37 | 2009-01-10 15:10 | 2 | 33 | 53983-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402204//REPLACED BAD CUTOUT / COD-2 / HAD TO OPEN TRANSF TO REPLACE CUTOUT VER/LDA L3/KEP IDC XXXX
23967 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-03-12 21:22 | 2012-03-12 21:55 | 2 | 33 | 4573721 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE VER/KEP IDC XXXX
23968 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2014-12-03 15:43 | 2014-12-03 16:05 | 3 | 22 | 4830721 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BROKE CUTOUT/ ISO 38830254C00412/ COD 3/NO CUST OUT AT THIS TIME/WILL NEED TO OUTAGE XFMR TO CHG CUTOUT/APROX ONE HOUR OUTAGE/VEM/OPEN XFMR @1543/REPAIRS MADE AND POWER RESTORED TO ALL CUST1605/PLEASE CLOSE TICKET/THANKS/VEM/ VER/BOW
23969 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-06-09 21:31 | 2011-06-09 22:37 | 1 | 66 | 4280881 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED LOOSE REFUSED TRANSFORMER ALL POWER RESTORED AT 2237 CLOSE TICKET COD-1 ISO TF 38830404C20384 VER/HFP L3/HFP IDC XXXX
23970 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-05-18 15:54 | 2011-05-18 17:00 | 1 | 66 | 4110651 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 40021258 ////REPLACING CUTOUT COD-1 ISO TF 38830174000105 VER/HFP L3/HFP IDC XXXX
23971 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-03-15 15:50 | 2019-03-15 16:56 | 1 | 66 | 4990221 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfer out on 37830222C00136 only / showing no custmers but 1 is on itbroken fuse
23972 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-04-09 14:19 | 2014-04-09 15:25 | 1 | 66 | 4589651 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BARREL ON XFMR CUTOUT HAS BURNT UP..GOING TO REPLACE AND REFUSEPOWER RESTORED @ 15:25 VER/SEF
23973 | Pikeville | 3402003 | KEYSER | MULLINS | 2017-06-21 11:09 | 2017-06-21 12:15 | 1 | 66 | 4010461 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BROKE ON SERVICE GOING TO CUSTOMERS HOUSE, WILL BE MAKING REPAIRS. MADE REPAIRS AT 1215. VER/CRB
23974 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2016-10-23 09:44 | 2016-10-23 10:50 | 1 | 66 | 4046311 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED BAD SECONDARY CONNECTIONS AT POLE 38821089A00316. VER/TOM L3/TOM
23975 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-02-09 17:19 | 2013-02-09 18:25 | 1 | 66 | 4805421 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVIN BURNED IN TWO.REPLACED ALL SECONDARY CONNECTIONS AT XFMR// VER/DBM IDC XXXX
23976 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-01-05 19:54 | 2015-01-05 21:00 | 1 | 66 | 4909081 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPS ORDER 034192394 CREATED TO REPLACE BAD TRANSFORMER 01-06-15...PLEASE SEND COPY TO BRUCE LINDON AND GLEN COMBS FOR CREW TO REPAIR TOMORROW.//FOR A GATE CUSTOMER OKD IT VER/CRB
23977 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2019-07-08 14:03 | 2019-07-08 14:25 | 3 | 22 | 4677541 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad secondary connection on service neutral on trans. pole 48-A3-529, pole was covered in vines had to open trans. to make repairs, opened up @1403 made repairs and closed back in @1425.//FLICKERING LIGHTS TILL FUSE OPEN PER SERVICER
23978 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2013-06-24 13:55 | 2013-06-24 15:01 | 1 | 66 | 4392171 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUSTOMER ADVISED OK TO HOLD UNTIL 6/25/2013
23979 | Pikeville | 3407101 | TOPMOST | DEMA | 2015-02-23 11:09 | 2015-02-23 12:15 | 1 | 66 | 4074901 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN . REPLACED CUTOUT, ALL WORK COMPLETE / GXJ // COD 1// VER/DBM L3/HFP XXX
23980 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2021-12-04 15:34 | 2021-12-04 16:40 | 1 | 66 | 4148421 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crw required replaed connetion
23981 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-01-19 08:19 | 2015-01-19 09:25 | 1 | 66 | 4943671 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS/////////SERVE-IN CONNECTION HAD FROZEN OUT.REPLACED ALL.OK AFTERWARDS// VER/ ADH
23982 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-11-08 10:49 | 2021-11-08 11:55 | 1 | 66 | 4066501 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed at weather head and damaged service wire. Replaced 50 ft 2/3 service and restored @ 11:55. sh
23983 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-02-01 12:03 | 2013-02-01 12:25 | 3 | 22 | 4781111 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | GAURDING LOW PRIMARY UNTILL LINECREW ARRIVES TO ASSIST. OPENED AT 454-7702 AT 1203 CLOSED AT 1225 APR CLOSE TICKET. DWEST ///VER/CRB L/3 CRB IDC XXXX
23984 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-08-16 21:45 | 2015-08-16 22:18 | 2 | 33 | 4140831 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP TO REPLACE///////REPLACED SERV DROP,ALL OK AFTERWARDS/////HAD XFR OFF FRM 21:45 TO 22:18 TO REPLACE DROP VER/SEF
23985 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-02-18 16:49 | 2020-02-18 17:55 | 1 | 66 | 4416181 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burnt up on pole 221-240. replaced and restored power at 17:55 L3/HFP
23986 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-07-02 02:35 | 2022-07-02 02:57 | 3 | 22 | 4360011 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr, opened xfmr at 02:35 closed at 02:55//cod 3
23987 | Hazard | 3420001 | SOFT SHELL | VEST | 2012-05-01 15:09 | 2012-05-01 16:15 | 1 | 66 | 4731271 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE FELL OUT OF SECONDARY SIDE OF XFMR.//// CONNECTOR ON SECONDARY BUSHING OF XFMR BROKE, REPLACED. POWER RESTORED. ///VER/CRB L/3 CRB IDC XXXX
23988 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-07-31 11:39 | 2009-07-31 12:45 | 1 | 66 | 65748-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN XFMR FUSE IDC XXXX
23989 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-02-12 13:24 | 2008-02-12 14:30 | 1 | 66 | 61235-1 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE WIRE BROKE AWAY FROM OPEN WIRE VER/HFP IDC XXXX
23990 | Hazard | 3309302 | VICCO | JEFF | 2019-06-04 12:57 | 2019-06-04 13:19 | 3 | 22 | 4426261 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfmr Replaced. Opened Xfmr @ 12:57 to 13:19
23991 | Hazard | 3307301 | BULAN | ARY-HEINE | 2010-09-21 13:24 | 2010-09-21 14:30 | 1 | 66 | 51897-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE, REPLACED, POWER RESTORED VER/KEP L3/KEP IDC XXXX
23992 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-10-18 09:34 | 2015-10-18 10:40 | 1 | 66 | 4358261 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE HAD BROKE. THE CHURCH BUILDING WAS THE ONLY CUSTOMER THAT WAS OFF. VER/CRB
23993 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-05-14 10:38 | 2013-05-14 11:44 | 1 | 66 | 4112361 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE CURRENT LIMITING FUSE FAILED. /// VER/CRB L/3 CRB IDC XXXX
23994 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-12-07 14:32 | 2011-12-07 15:38 | 1 | 66 | 4149311 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN DOWN,WILL REPLACE IT,POLE ABT HALFWAY BURNED INTO,WILL TRY TO PUT OUT FIRE//////REPLACED CUTOUT @ RESTORED,FIRE APPEARS TO BE OUT AFTER DOWSING W WATER ON 1526 COD-1 ISO TF 38831127A00538 VER/HFP L3/HFP IDC XXXX
23995 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-01-06 15:32 | 2010-01-06 15:54 | 3 | 22 | 63853-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-3 ISO LF VER/HFP L3/HFP IDC XXXX
23996 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-11-14 08:59 | 2013-11-14 10:05 | 1 | 66 | 4037901 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED SQUEESE -ON CONNECTOR, POWER OK VER/HFP L3/HFP
23997 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-11-09 09:04 | 2010-11-09 10:10 | 1 | 66 | 54211-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT ON POLE 189-192.//COD 1// VER/DBM IDC XXXX
23998 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-05-05 08:19 | 2009-05-05 09:25 | 1 | 66 | 54260-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT I WILL REPAIR,,,BACK ON VER/TOM L3/TOM IDC XXXX
23999 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-04-06 18:44 | 2014-04-06 19:50 | 1 | 66 | 4580031 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 182-3544/NO CREW REQUIRED REPAIRED CONNECTION// VER/DBM
24000 | Whitesburg | 3312901 | JENKINS | KONA | 2016-02-02 22:14 | 2016-02-02 23:20 | 1 | 66 | 4668751 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RER-RED SERVICE LINK FROOZE APART,I REPLACED IT/ ISO 37830404B00052/ COD 1/ VER/BOW
24001 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-08-07 21:48 | 2015-08-07 22:54 | 1 | 66 | 4111031 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION,,,, COMPLETE VER/CRB
24002 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-07-10 22:53 | 2011-07-10 23:15 | 3 | 22 | 4501351 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SDB / ASSOCIATED W/ ORDER 4501071. CREWS DE-ENERGIZED TAP TO SAFELY REPLACE CSP TR AT POLE 38831151D00102. SDB / 2315 / RESTORED. CC= 3. IDCC PN89 XXXX
24003 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2012-03-21 15:45 | 2012-03-21 16:07 | 3 | 22 | 4603621 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE COD-3 ISO TF 38830118D16116 VER/HFP L3/HFP IDC XXXX
24004 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-10-01 10:03 | 2014-10-01 10:25 | 3 | 22 | 4541061 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PWR OFF @ 10:03 BACK ON @ 10:25---REPLACED L/A PWR CK GOOD---TBL TKT COMP COD-3 ISO TF 38830138D00261 VER/HFP L3/HFP
24005 | South Williamson | 3200302 | BELFRY | TOLER | 2010-10-20 17:34 | 2010-10-20 18:40 | 1 | 66 | 61431-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRMR FUSE OUT.....CUTOUT DOOR DID NOT DROP DOWN....FUSE MAY HAVE JUST BROKEN....WILL RE-FUSE...//....REPLACED BROKEN FUSE LINK, & ENERGIZED XFMR.....JRV.....10/20/10 // COD-1 VER/HFP L3/HFP IDC CHANGED FROM OTHER XXXX
24006 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-04-21 15:23 | 2011-04-21 15:45 | 3 | 22 | 61788-1 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE // COD-3 ISO TF 37830196A00110 VER/HFP L3/HFP IDCC FEC57 XXXX
24007 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-06-28 09:48 | 2012-06-28 10:54 | 1 | 66 | 4970641 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK
24008 | Hazard | 3309301 | VICCO | REDFOX | 2010-04-03 18:27 | 2010-04-03 19:33 | 1 | 66 | 58291-1 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LEAD HAS COME LOOSE FROM XFMR VER/KEP L3/KEP IDC XXXX
24009 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-07-18 12:24 | 2015-07-18 13:30 | 1 | 66 | 4906741 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | B PHASE ONLYREPLACED BURNED UP CUTOUT DOOR ON POLE 38831126A00190// POWER RESTORED @ 13:30/ ISO 38831126A00190/ COD 1
24010 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-07-05 09:12 | 2022-07-05 10:18 | 1 | 66 | 4376031 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN NEUTRAL IN SERVICE WIRE // REPAIRS MADE AND COMPLETE @ 10:18
24011 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-10-11 13:54 | 2013-10-11 15:00 | 1 | 66 | 4930671 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | MADE NEW SPLICE AT ENTRANCE CABLE VER/CRB L/3 CRB
24012 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2018-12-04 08:42 | 2018-12-04 09:48 | 1 | 66 | 4506031 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, made repairs restored power at 09:48 L3/HFP
24013 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-04 20:48 | 2008-12-04 21:54 | 1 | 66 | 54575-1 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308401// PART POWER, BAD CONNECTION ON SERVICE POLE// VER/DBM L3/KEP IDC XXXX
24014 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-01-29 23:04 | 2014-01-30 00:10 | 1 | 66 | 4326281 | 66 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SECONDARY CONNECTION AT TRANSFORMER. VER/KEP
24015 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-02-15 15:03 | 2012-02-15 16:09 | 1 | 66 | 4351081 | 66 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ///VER/CRB IDCC PN NULL XXXX
24016 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-08-08 09:15 | 2011-08-08 10:20 | 1 | 65 | H4677301 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9KV 120/240 VOLT TRANSFOMER NO TRUCK WILL NEED YARD DOG, NEED TO TAKE YARDDOG UP SECOND DRIVE WAY ON LEFT AROUND BIG CURVE, CAN GET OFF ROAD WITH TRUCKS TO UNLOAD CLOSED FUSE IN ON TRANSFORMER AND IT BLEW 50T LINE FUSE BACKING IT UP, ALSO NEED TO RECONNECT 4/2 SEC CUT ON POLE DURING TROUBLESHOOTING, REFUSED CUTOUT WITH1.6 (REFUSED LINE FUSE AT10:20 OUT AT 09:15) VER/KEP IDC XXXX
24017 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-01-12 19:46 | 2009-01-12 20:51 | 1 | 65 | 54562-1 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3003703// BAD CONN , REPAIRED IT , VOLTAGE OK. VER/TOM L3/TOM IDC XXXX
24018 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-01-08 18:55 | 2020-01-08 20:00 | 1 | 65 | 4226121 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | customer has voltage issue on AEP side of meter per j combs (AEP) bad secondary connection
24019 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-01-27 11:55 | 2012-01-27 13:00 | 1 | 65 | 4299001 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CUTOUT//COD 1// VER/DBM IDC XXXX
24020 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2021-07-07 15:41 | 2021-07-07 16:46 | 1 | 65 | 4866981 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 427-B-150.. cutout replaced.. power restored
24021 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-05-12 11:25 | 2015-05-12 12:30 | 1 | 65 | 4420121 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVEND GOT HOT BURNED INTO NEUT === BURNING NEUT INTO == REPAIRED POWER OK VER/HFP L3/HFP
24022 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2022-10-18 23:55 | 2022-10-19 01:00 | 1 | 65 | 4041621 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Secondary burnt into///Repairs made and restored service @ 01:00///only 1 customer was affected
24023 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-12-11 04:35 | 2008-12-11 04:48 | 5 | 13 | 56494-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403201// BAD CUTOUT DOOR ON POLE 117-252. REPLACED BAD DOOR EVERYTHING OK. VER/LDA L3/KEP IDC XXXX
24024 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-05-14 23:03 | 2020-05-15 00:08 | 1 | 65 | 4837311 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Splice went bad, repaired
24025 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2019-09-09 12:55 | 2019-09-09 14:00 | 1 | 65 | 4995831 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer fuse and current limiting fuse bad
24026 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2014-01-27 08:33 | 2014-01-27 09:38 | 1 | 65 | 4316091 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | S/D BURNED OPEN AT POLE// WILL REWORK// CONNECTION OVER HEATED & BURNED WIRE IN TWO// REPAIRS MADE// IDCC CNT3 XXXX
24027 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-07-25 08:00 | 2008-07-25 09:05 | 1 | 65 | 60052-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409303//ETA 0830//SERVICE DROP BURNT DOWN AT WEATHERHEAD. WILL REPAIR AND INSPECT CUSTOMER ENTRANCE FOR DAMAGE. // REPLACING BAD 1/0 SERVICE. REPLACED DAMAGED SERVICE AND RE-FUSED XFMR. SH//COD 1// VER/DBM IDC XXXX
24028 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-06-23 19:55 | 2015-06-23 21:00 | 1 | 65 | 4647421 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT/CUSTOMER IS ON POLE 245C183 / //COD 1 VER/CRB
24029 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-01-29 16:47 | 2014-01-29 17:52 | 1 | 65 | 4325101 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202 - REPORT OF XFMR FIRE AT 11B37 - REPORTED BY TRK 12933 REPLACED BAD TRANSFORMER CUTOUT ON POLE 11-B-37. THE CROSSARM IS BURNED HALFWAY THROUGH, PLEASE SEND AN E-MAIL TO JOEY REED TO REPLACE THE CROSSARM, HE CAN USE THE BUCKET TRUCK TO CHANGE THE ARM. VER/SEF ***CHANGE ISO POLE***
24030 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-07-27 19:00 | 2021-07-27 20:05 | 1 | 65 | 4968871 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 1125-B-209 TR fuse, will be making repairs
24031 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-10-08 22:15 | 2008-10-08 23:20 | 1 | 65 | 54485-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3008701// BAD SERVE END ON XFORMER.POLE.// VER/DBM IDC XXXX
24032 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2017-08-02 23:55 | 2017-08-03 01:00 | 1 | 65 | 4218501 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE CONDUCTOR NUETRAL BADLY CORRODED AND BROKEN 10 FEET AWAY FROM MAST PIPE IN MID SPAN REPLACED 20 FT OF SERVICE CONDUCTOR AND REMOVED OLD CONNECTIONS AT WEATHERHEAD VER/ARN
24033 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-03-31 15:55 | 2017-03-31 17:00 | 1 | 65 | 4603761 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 156-84, REPLACE CUTOUT 37830156000184 VER/AWD
24034 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-07-19 12:15 | 2010-07-19 13:20 | 1 | 65 | 53153-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED A 25KVA TRANSFORMER AND 1 BARRELL CUTOUT ARRESTOR AND BRACKETT ALSO A CREW RELEASED BY CREW 074S07 REPLACED TRANS CLEAN UP OIL OFF 1215 ON @1320 IDC XXXX
24035 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-05-20 20:20 | 2016-05-20 21:25 | 1 | 65 | 4240791 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED TRASFORMER ON POLE 66-201 20:20 DUE TO BAD CUTOUT AND POLE BURNING//COD 1// ISO 37830066C00201// VER/DBM
24036 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2012-03-27 09:05 | 2012-03-27 10:10 | 1 | 65 | 4621331 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP FAILED. I REPLACED IT AND THE STIRRUP.// VER/DBM IDCC PN271 XXXX
24037 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-06-17 13:25 | 2009-06-17 13:38 | 5 | 13 | 60042-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN WIRE DOWN-NO OUTAGE--OPENED TRANSFORMER ON POLE 38830117C00133 AT13:25 TO CLEAR TROUBLE--BACK ON 13:38--REMOVED IA SPAN OF WIRE// VER/DBM IDC XXXX
24038 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-11-17 08:45 | 2010-11-17 09:50 | 1 | 65 | 57224-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED TAP TO SAFELY REPAIR CUTOUT// OFF TIME TO MAKE REPAIRS 08:45. OPEN ON POLE 1132-102 // COD 1//ISO 38821132000102 // VER/DBM IDC XXXX
24039 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-09-22 03:00 | 2010-09-22 04:05 | 1 | 65 | 52031-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED NEED TO CHG FROM 15 TO 25 KVA TRUCKS OK HOUSE AT BOTTOM OF HILL ON LEFT BEFORE ROWAN CO. LINE/SEND TO P TOLLIVER RELEASED BY CREW 078S03//REPLACED XFORMER W/25KVA POWER RESTORED AT 04:05 PR TOLLIVER/// IDCC TOF2316 XXXX
24040 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-05-08 22:30 | 2008-05-08 23:35 | 1 | 65 | 58403-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRANSFORMER. TWO ALL ELECTRIC MHS. NEED TO REPLACE WITH A 25 SINGLE BUSHING 120/240 7200.//3401702 IDC XXXX
24041 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-04-14 18:40 | 2015-04-14 19:45 | 1 | 65 | H4318051 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WAITING ON CREW TIME OFF 18:40 ON @ 19:45. SD NEUT SQUEZED TO MAIN LINE NEUT. EXPECT DAMAGE COMP/EMAILED PEGGY/ADH// NEUTRAL BAD IN METER, HAD TO OPEN LINE FUSE FOUND BAD INSULATOR ON LINE FUSE ON POLE 52 WHILE OUT THERE EVERYONE ON @ 1945// VER/ ADH
24042 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-01-31 16:55 | 2008-01-31 18:00 | 1 | 65 | 62873-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CLAMP ON CUTOUT HIGH SIDE FELL OFF OF STIRRUP ON PRIMARY//3001002// VER/CRB IDC XXXX
24043 | Hazard | 3302704 | HAZARD | KENMONT | 2012-01-23 06:40 | 2012-01-23 07:45 | 1 | 65 | 4283691 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLINE CLAMP BURN OFF PRIMARY METERING == REPLACE CLAMP == POWER OK//COD 1 VER/KEP IDC XXXX
24044 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2021-01-06 15:05 | 2021-01-06 16:10 | 1 | 65 | 4852611 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad netral connection on transformer pole. redid neutral connection. voltage checked good
24045 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-07-07 09:29 | 2009-07-07 10:34 | 1 | 65 | 55623-1 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CONNECTION WENT BAD AT WEATHERHEAD L3;/HFP IDC XXXX
24046 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-10-20 09:40 | 2013-10-20 10:45 | 1 | 65 | 4949341 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SPLICE IN SERVICE DROP. NON TENSION SPLICE HEATED UP, BURNING THE SERVICE NEUTRAL APART.// VER/DBM
24047 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2009-01-16 14:55 | 2009-01-16 16:00 | 1 | 65 | 56215-1 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3008002//REPAIRED SERVICE DROP L3/HFP
24048 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-12-19 14:30 | 2011-12-19 15:35 | 1 | 65 | 4188281 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | NO OUTAGE AT THIS TIME, SECONDARY LEAD ON XFMR BANK IS GETTING HOT ,CREW WILL REPLACE WIRE AFTER HOTELS LUNCH HOUR IS OVER RELEASED BY CREW 077S11 // OPENED TR @ 1430______ ON @ _1535____ COD-1 ISO TF 37830424000177 VER/HFP L3/HFP IDC XXXX
24049 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-04-11 12:00 | 2013-04-11 13:05 | 1 | 65 | 4998811 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | THIS TICKET REPLACED TICKET # 4998591//MDH//OPEND FUSE TO REPLACE POLE (POLE TOP SPLIT DUE TO ROT ;TIME OFF 12:00, TIME ON 13:05) ///VER/CRB L/3 CRB IDC XXXX
24050 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-11-19 08:49 | 2021-11-19 09:54 | 1 | 65 | 4107801 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Power restored @ 09:54
24051 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-09-11 11:40 | 2016-09-11 12:45 | 1 | 65 | 4885281 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHGED 6T FUSE/ ISO 38830116A00357/ COD 1/ VER/BOW
24052 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-09-02 11:30 | 2014-09-02 12:35 | 1 | 65 | 4448001 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BAD ALL PWR RESTORED PLEASE CLOSE TICKET THANK YOU.. LRM// ISO 38830453000243// COD 1// VER/BOW
24053 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-09-02 19:15 | 2011-09-02 20:20 | 1 | 65 | 4788861 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHGED BAD 19.9 CUTOUT 20T LINE FUSE VER/KEP IDC XXXX
24054 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-09-03 17:47 | 2009-09-03 18:52 | 1 | 65 | 64193-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR# 31571085//CHANGING OUT XFR BANK THAT FUSES KEEP BLOWING// ALL XFRS TAKEN DOWN TESTED GOO WITH XFR TESTER 2 XFRS HAD 6T FUSES ONE HAD A 10 T ALL 3 CURRENT LIMITING FUSES TESTED GOOD/ BIRD CRAP ALL OVER TOPS OF XFRS CANT SEE ANY PLACE WHERE THEY ARE GETTING INTO XFRS OR RISERS//COD 1// VER/DBM IDC XXXX
24055 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-07-12 18:48 | 2017-07-12 19:53 | 1 | 65 | 4112051 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE.. POWER RESTORED AT 19:53./ ISO 37830400A00012/COD 1/ VER/BOW
24056 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-05-26 20:15 | 2012-05-26 21:20 | 1 | 65 | H4833731 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NEED TO REPLACE U.G.SERVICE. SEND TO D. HAMILTON RELEASED BY CREW 074S05//BAD URD SVC, WILL TRY TO PULL SVC OUT OF CONDUIT AND REPLACE CABLE. OPENED XFMR 1151-782 TO MAKE REPAIRS AT 20:15, REPAIRS MADE, CLOSED AT 21:20. INTERRUPTION OUTAGED 1 MORE CUST. //VER/GAH IDCC CCO, CDC96 XXXX
24057 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2016-05-08 08:13 | 2016-05-08 09:18 | 1 | 65 | 4186911 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK/ ISO 38830248000215/ COD 1/ VER/BOW
24058 | Hazard | 3303902 | LESLIE | WOOTON | 2018-06-20 12:30 | 2018-06-20 13:35 | 1 | 65 | 4623861 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called this number and she said to come wednesday would be fine please send to gilley to check Released by crew 077S05 CHECKED VOLTAGE 139.7 ON BOTH LEGS, RETIGHTEN LUGS ON XFMR AND CHECKED CONNECTIONS. WENT TO NEXT XFMR AND IT READ FINE. WILL NEED CREW TO CHANGE OUT 25 KVA 7200 120/240 Released by crew 077S01
24059 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2018-01-08 13:15 | 2018-01-08 14:20 | 1 | 65 | 4721131 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED CUST//NO RDG ON MTR// service burnt in two
24060 | Hazard | 3303901 | LESLIE | HYDEN | 2011-01-23 16:20 | 2011-01-23 17:25 | 1 | 65 | 63739-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED 7.2 KV CUTOUT COD-1 ISO TF 37830315000045 VER/HFP L3/HFP IDC XXXX
24061 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-06-08 21:24 | 2008-06-08 22:29 | 1 | 65 | 60295-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, NEUTRAL INTO IN SERVICE DROP, MAKING REPAIRS, CONNECTION FAILED WHERE SERVICE MAKES UP TO CUST ENTRANCE VER/ARN IDC XXXX
24062 | Whitesburg | 3309301 | VICCO | REDFOX | 2022-10-11 09:38 | 2022-10-11 10:43 | 1 | 65 | 4014231 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Open switch on pole 37830325C00264 to isolate and repair 37830326A00005replaced bad conn. opened 325c-264 @09:38, closed @ 10:43 Released by crew 077H13
24063 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-08-21 09:35 | 2009-08-21 10:40 | 1 | 65 | 58423-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN SERVICE NETRUAL REPAIRED NET VOLTAGE OK RELEASED BY CREW 078S11 VER/KEP L3/KEP IDC XXXX
24064 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-06-09 12:30 | 2011-06-09 13:35 | 1 | 65 | 4275101 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4/3 SERVICE BURNT DOWN REPAIRED VER/KEP IDC XXXX
24065 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2022-06-02 09:41 | 2022-06-02 10:46 | 1 | 65 | 4997261 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Replacing failed TR.. restored power @ 10:46
24066 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-01-05 15:40 | 2014-01-05 16:45 | 1 | 65 | 4230591 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CLF REPLACED FUSE APR AT 1645 CLOSE TICKET. DEW VER/CRB IDC XXXX
24067 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2020-04-18 09:30 | 2020-04-18 10:35 | 1 | 65 | 4713971 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr 37830188C00198, hold for crew///Bushing broke on 15 KVA transformer///off 09:30// on@ 10:35
24068 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-10-24 20:30 | 2010-10-24 21:35 | 1 | 65 | 62619-1 | 65 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GATE, THEY HAD AHOUSE FIRE HERE TODAY REPLACED CUTOUT GATE RESTORED POWER AT 21:35 //VER/GAH IDC CHANGED TIME OFF FIRST CALL FULL POWER XXXX
24069 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-12-11 15:22 | 2012-12-11 16:27 | 1 | 65 | 4461671 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RESQUEZED CONNECTION AT TRANSFORMER ////VER/CRB L/3 CRB
24070 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-12-11 11:30 | 2010-12-11 12:35 | 1 | 65 | 65304-1 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE END ON POLE...REMOVED ALL 3 SERVE ENDS AND RE-SPLICED,,, VER/HFP L3/HFP IDC XXXX
24071 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2022-11-02 18:20 | 2022-11-02 19:25 | 1 | 65 | 4091721 | 65 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | power restored to single customer at 19:25
24072 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-12-04 10:28 | 2009-12-04 11:00 | 2 | 32 | 53062-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | HAD LEAD TO OPEN SEC BURNED INTO VER/KEP L3/KEP IDC XXXX
24073 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2010-12-21 23:36 | 2010-12-22 00:40 | 1 | 64 | 54955-1 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SQUEEZE-ON CONNECTION ON ONE HOT LEG, THAT I MISSED EARLIER THIS EVENING....JUST THIS ONE CUSTOMER.....REPLACED CONNECTION....ALL OK NOW.....JRV....12/22/10 VER/ARN IDCC CNT4 XXXX
24074 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-08-22 16:54 | 2010-08-22 17:58 | 1 | 64 | 59343-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OLD BOX TYPE CUTOUT DOOR BROKE,, CUTOUT IS NEXT TO PRIMARY CUSTOMER SAID IT CAN WAIT TILL TOMMOROW IT FEEDS AN OIL WELL THAT HE WONT BE USING FOR AWHILE,, WILL ASK FOR CREW IN THE MORNING RELEASED BY CREW 078S02//VER/CRB IDC XXXX
24075 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-07-13 13:41 | 2010-07-13 13:57 | 4 | 16 | 66108-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER OPENED FUSE TO ALLOW HIM TO SAFELY REPAIR HOT TAP IN ORDER 66033-1 // COD-4 VER/HFP L3/HFP IDC XXXX
24076 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-03-17 11:55 | 2015-03-17 12:59 | 1 | 64 | 4202831 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP HAD BAD PLACES IN NEUTRAL , REPLACED DROP ..ADJUSTED TIME OFF TO AFTER SERVICER ARRIVED VER/HFP L3/HFP
24077 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-07-24 12:44 | 2013-07-24 13:48 | 1 | 64 | 4588301 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN,WILL REPLACE/////////REPLACED BROKEN CUTOUT,RESTORED AT 13:48 VER/CRB L/3 CRB IDC XXXX
24078 | South Williamson | 3411401 | DEWEY | INEZ | 2017-06-03 12:41 | 2017-06-03 13:45 | 1 | 64 | 4901701 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE//REPAIRS MADE//RESTORED AT 13:45//COMPLETE//EM 38830791A00126 VER/AWD
24079 | Hazard | 3309302 | VICCO | JEFF | 2015-06-02 09:50 | 2015-06-02 10:54 | 1 | 64 | 4500031 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === REPLACED CUTOUT POWER OK/ ISO 37830323C00122/ COD 1/ VER/BOW
24080 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-30 10:16 | 2014-01-30 11:20 | 1 | 64 | 4329041 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION BURNT OPEN AT CUSTOMER WEATHERHEAD. REWORKED CONNECTIONS AT WEATHERHEAD AND RESTORED @ 11:20. SH VER/HFP L3/HFP
24081 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2018-01-11 14:35 | 2018-01-11 15:39 | 1 | 64 | 4730621 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | splice burnt open in secondary/// Repaired bad splice and restored service @15:39/ ISO 37820126000043/ COD 1
24082 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-06-17 19:26 | 2016-06-17 20:30 | 1 | 64 | 4382111 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BAD---REPLACED---OK//COD 1// VER/DBM
24083 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-02-21 15:11 | 2016-02-21 16:15 | 1 | 64 | 4744451 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION @ WEATHER HEAD VER/CRB
24084 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-05-15 16:50 | 2009-05-15 17:54 | 1 | 64 | 57581-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SERVICE DROP//VER/CRB
24085 | Pikeville | 3413402 | GARRETT | LACKEY | 2013-09-05 15:16 | 2013-09-05 16:20 | 1 | 64 | 4823071 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 40T FUSE OUT . FUSE BROKE FUSED UP EVERYTHING OK. VER/CRB L/3 CRB IDCC XXXX
24086 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-03-03 19:26 | 2014-03-03 20:30 | 1 | 64 | 4448631 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD FUSE LINK REPLACED FUSE AND POWER IS RESTORED AT THIS LOC AT 2030//COD 1// VER/DBM IDC XXXX
24087 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-08-10 14:58 | 2018-08-10 16:02 | 1 | 64 | 4938141 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection/repaired/ ISO 38830070A20612/ COD 1
24088 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2020-04-10 18:46 | 2020-04-10 19:50 | 1 | 64 | 4619491 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Repaired service drop, Neighbors wire ripped off pole, mast broke off home, caused partial
24089 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-09-19 18:29 | 2011-09-19 19:33 | 1 | 64 | 4885481 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT NEEDS SENT TO TECH TO HAVE POLE FIXED AND RELOCATE FROM CROSSING POOL AREA // SENT EMAIL AS REQUESTED...HFP COD-1 ISO TF 38830197000182 VER/HFP L3/HFP IDC XXXX
24090 | Hazard | 3303902 | LESLIE | WOOTON | 2008-06-04 19:41 | 2008-06-04 20:45 | 1 | 64 | 57125-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303902//--BAD TR ON HILL-WILL TAKE FLAGMEN-MAY MOVE 1 POLE CLOSER AND BE OUT OF RD--1 CUSTOMER --15 KVA 19.9-CUTOUT AND ARRESTOR--WILL DO 1ST TOMORROW--JIM RELEASED BY CREW 077S06 JIM GOING TO WORK AS OPS ORDER COD-1 TOMMOROW SPOKE TO CUSTOMER VER/KEP
24091 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-04-12 14:28 | 2013-04-12 15:32 | 1 | 64 | 4004851 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION// VER/DBM IDCC CNT8 XXXX
24092 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-02-23 14:20 | 2022-02-23 15:24 | 1 | 64 | 4537111 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 19.9 cutout, crew required. Noone lives here, house is empty. Vernon said to hold till tommorow and he would have it taken care of. Thanks Released by crew 078S11
24093 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2021-10-29 21:30 | 2021-10-29 22:02 | 2 | 32 | 4039441 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830550000039 pole top burnt off line hanging by lower bolt of ridgepin--crew req-ds102921 Released by crew 078S01,lifted hottap @ pole 550-38 @ 2130 closed hottap @ 2202 please close ticket thanks.bt
24094 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2015-12-28 11:21 | 2015-12-28 12:25 | 1 | 64 | 4566991 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTION FAILED AT WEATHERHEAD. OOONLY ONE CUSTOMER AFFECTEDOO RE-WORKED CONNECTIONS AND RESTORED @ 12:25. SH VER/HFP L3/HFP
24095 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-02-21 09:05 | 2010-02-21 10:09 | 1 | 64 | 59477-1 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR# 33951806 // LOOSE CONN. ON HOUSE// VER/DBM IDC XXXX
24096 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-12-02 10:11 | 2015-12-02 11:15 | 1 | 64 | 4503511 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//THEY FLIPPED BREAKERS //NO POWER//NO CREW REQUIRED REPLACING FUSE DOOR VER/CRB
24097 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-10-28 18:03 | 2015-10-28 18:11 | 8 | 8 | 4389901 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENING SWITCH 305-64 TO MAKE UP LOOPS/ RELATED TO OUTAGE 4384751 & H4384751 // VER/ ADH L3/HFP HFPC FP38830305000125 AJB
24098 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-04-06 08:18 | 2008-04-06 08:50 | 2 | 32 | 64467-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008702//19.9 CUTOUT DOOR BURNT UP//COD 2// VER/DBM IDC XXXX
24099 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-11-09 08:26 | 2019-11-09 09:30 | 1 | 64 | 4014351 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replacing failed cutout//// Apr at 0930 close ticket. dwest
24100 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-03-01 07:41 | 2011-03-01 07:57 | 4 | 16 | 65285-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | STS WR # 38985158 //---- SECONDARY CODUCTOR BURN-INTO AT TRANSFORMER, SEND E-MAIL TO CLIFF FREEMAN WE NEED TO CHANGE 1/0 SECONDARY TO 4/0 AND UPGRADE TRANSFORMER . CORNER OF SCOTT AVE AND LILLYCIR, 24-396 OPEN 0741 CLOSE 0757 COD-4 VER/KEP IDC XXXX
24101 | Paintsville | 3401802 | INDEX | HOSPITAL | 2014-06-07 16:56 | 2014-06-07 18:00 | 1 | 64 | 4993311 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTNING ARRESTOR BLEW UP IN SWITCHING ENCLOSER..HOSPITAL SINGLE PHASING.65T FUSE BLOWN..REFUSED.//COD 1// AED ENTRY CREATED// VER/DBM
24102 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-01-06 10:17 | 2013-01-06 11:21 | 1 | 64 | 4572841 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMING FUSE REPLACED VOLAGE OK COD-1 ISO TF 38830141A36215 VER/HFP L3/HFP IDC XXXX
24103 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-03-23 13:53 | 2015-03-23 14:57 | 1 | 64 | 4219981 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BROKEN 19.9 CUTOUT,POWER RESTORED// VER/ ADH L3/DKGXXXX
24104 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2019-10-16 11:15 | 2019-10-16 12:19 | 1 | 64 | 4147761 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout going bad. repairs made. pls close. tre L3/HFP
24105 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-11-27 00:56 | 2014-11-27 02:00 | 1 | 64 | 4809401 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON HOT LEG OF SD AJBC CNT7
24106 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-08-16 14:21 | 2016-08-16 15:25 | 1 | 64 | 4794611 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIR SERVICE/ ISO 38830292B00069/ COD 1 VER/HFP L3/HFP
24107 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2021-06-21 15:56 | 2021-06-21 17:00 | 1 | 64 | 4782391 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repair neut in sd & hotlegs. complete
24108 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2021-12-14 12:58 | 2021-12-14 13:30 | 2 | 32 | 4195741 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fus link
24109 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-09-15 15:21 | 2009-09-15 16:25 | 1 | 64 | 59722-1 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP # 6 COPPER SECONDARY BROKEN AT DEADEND MAKING REPAIRS /// OPENED TRANSFORMER @ 1605 CLOSED @ 1625 # 6 COPPER SECONDARY BROKEN AT DEADEND MAKING REPAIRS//REPAIRS COMPLETE PLEASE SEND COPY TO DOUG CHRISTIAN FOR REBUILD ON # 6 SECONDARY DUPLICATING FOR 5 CUST OUTAGE L3/HFP IDC XXXX
24110 | Pikeville | 3407101 | TOPMOST | DEMA | 2008-08-26 19:30 | 2008-08-26 20:34 | 1 | 64 | 55301-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30T LINE FUSE OUT ON POLE 113-.18. BAD CUTOUT I WILL BE CHANGING. POLE HAS A LITTLE PLACE BURNT BACK IN IT BUT POLE IS SAFE.DROP COPY OF THIS DOWN TO RON RYE PIKEVILLE.THEY MAY WANT TO CHANGE METAL BRACKET. AND LOOK AT POLE. I PUT ONE OF THE NEW POLIMER CUTOUTS UP.//3407101//VER/CRB IDCC TOF1912 XXXX
24111 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-03-06 11:36 | 2015-03-06 12:40 | 1 | 64 | 4144831 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | HAD BAD SPLICE AND WEATHERHEAD ON THREE GAIN METERBASE REPAIRS COMPLTED// VER/ ADH
24112 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-01-29 14:14 | 2015-01-29 14:46 | 2 | 32 | H4973251 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 1 CUSTOMER ORGINALLY, OPEN TRANS AT 1414 AND CLOSED AT 1446 1+2/FIX IT IN HOIS// VER/ ADH L3/HFP XXX
24113 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-06-13 19:41 | 2019-06-13 20:45 | 1 | 64 | 4503001 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got pole fire put out cutout changed and transformer back in at 20:45
24114 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-12-14 11:07 | 2016-12-14 12:11 | 1 | 64 | 4193471 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAD A HOT LEG CONNECTION ALMOST BURNDT INTO AT CUSTOMERS WEATHERHEAD, MADE REPAIRS. VER/CRB L3/HFP XXXHFP
24115 | Paintsville | 3401101 | FALCON | FALC-OILS | 2012-07-23 13:08 | 2012-07-23 14:12 | 1 | 64 | 4799151 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE.RE FUSED TRANSFORMER.. VER/KEP
24116 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-05-18 13:21 | 2008-05-18 14:25 | 1 | 64 | 65461-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3314401// CUTOUT IS BAD WILL REPLACE REPLACED CUTOUT ALSO CUST BREAKER DOES NOT WORK CUST WANTED LEFT OFF SO HE CAN REPLACE BREAKER CUST WILL CALL BACK WHEN REPAIRS ARE MADE VER/HFP IDC XXXX
24117 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-01-30 10:57 | 2019-01-30 12:01 | 1 | 64 | 4734141 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad insulink at mast. replaced all connections, all good. pls close. tre
24118 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-07-01 10:28 | 2009-07-01 11:00 | 2 | 32 | 57140-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS TRANSFORMER FUSE OUT ,GOING TO REFUSE TRANDFORMER, LOOK LIKE FUSE BROKE VER/KEP L3/KEP IDC XXXX
24119 | South Williamson | 3411401 | DEWEY | INEZ | 2010-06-28 19:40 | 2010-06-28 20:44 | 1 | 64 | 59899-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING NOW//COD 1// VER/DBM
24120 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2008-05-19 23:51 | 2008-05-20 00:55 | 1 | 64 | 66201-1 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3302701 - BAD TRANSF 15 KVA == CUST SAID TO IT CHANGE IT OUT AT DAYLIGHT == HE IS OK WITH IT == SERVICER TALKED TO CUSTOMER & WILL MAKE ORDER TO CHANGE IN MORNING - VER//GAH IDC XXXX
24121 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-10-20 15:45 | 2010-10-20 16:49 | 1 | 64 | 61390-1 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | BAD METER.....REPLACED AND RESTORED @ 16:49 J.GARRETT VER/HFP L3/HFP IDC XXXX
24122 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-11-05 11:56 | 2012-11-05 12:12 | 4 | 16 | 4362401 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE, POWER RESTORED. ///VER/CRB L/3 CRB IDC XXXX
24123 | Hazard | 3303902 | LESLIE | WOOTON | 2019-11-20 13:21 | 2019-11-20 14:25 | 1 | 64 | 4051221 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse, broke cutout phillip hicks will come and change Released by crew 077H14
24124 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-01-10 03:18 | 2019-01-10 04:22 | 1 | 64 | 4654561 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cut out
24125 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-07-11 13:51 | 2016-07-11 14:23 | 2 | 32 | 4610091 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 149-8RELEASED BY CREW 077S05/ ISO 37830149B00008/ COD 2/ VER/BOW
24126 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-05-06 20:12 | 2015-05-06 20:28 | 4 | 16 | 4398241 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830378C00026/ ISO 37830378C00026/ COD 4BAD CUT-OUT ON POLE 378-26. OPENED X-FMR AT 20:12, REPLACED CUT-OUT, AND RE-ENERGIZED X-FMR AT 20:36. 5/6/2015/ VER/BOW
24127 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2019-02-04 16:46 | 2019-02-04 17:50 | 1 | 64 | 4753961 | 64 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | resqueezed connections ,,,complete//POLE 38830182D00052//
24128 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-04-08 10:11 | 2019-04-08 10:27 | 4 | 16 | 4068911 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opening xfmer to splice service drop that is deteriorating. opened at 10:11 back in @ 10:27 L3/HFP
24129 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-09-11 17:26 | 2014-09-11 18:30 | 1 | 64 | 4491201 | 64 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD LINE FUSE CUTOUT.//BACK ON @ 18:30// COD 1//VER/ ADH
24130 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-11-08 07:17 | 2008-11-08 08:20 | 1 | 63 | 63203-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/PDP IDC XXXX
24131 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-11-29 07:06 | 2010-11-29 08:09 | 1 | 63 | 60429-1 | 63 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV DROP BURNED INTO,WILL REPAIR.1 LEG OF SERV BURNED INTO,MADE REPAIRS.POLE # IS WRONG.CORRECT IS 1130-18.XFR OFF 07:42 TO 08:09 TO REPAIR.CHARLIE HALL IS CUSTOMER//COD 1 (+ 1, SEE ORDER H60429-1) //ISO 38821130000018// VER/DBM IDC XXXX
24132 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-02-10 09:57 | 2017-02-10 11:00 | 1 | 63 | 4383171 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLAED ALL CONNECTIONS ON WEATEHER HEAD VER/CRB L3/HFP HFPC CDC89
24133 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2010-08-31 16:12 | 2010-08-31 17:15 | 1 | 63 | 62344-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I REPLACED A FAILED CUTOUT ON THIS PRIMARY METERING.// COD 1// VER/DBM IDC XXXX
24134 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-01-15 09:12 | 2013-01-15 10:15 | 1 | 63 | 4606281 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE.//COD 1// VER/DBM IDC XXXX
24135 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-08-06 15:12 | 2009-08-06 16:15 | 1 | 63 | 55000-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP SQUEEZE ON FAILED CONNECTION WAS BAD ... CUST HAD 16 VOLTS ONE LEG AND 120 ON THE OTHER .... MADE CONNECTIONS BACK.. RESTORED 16:15 L3/HFP IDC XXXX
24136 | Whitesburg | 3312902 | JENKINS | JENKINS | 2021-11-18 13:06 | 2021-11-18 13:15 | 7 | 9 | 4105461 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Had a fuse fail. Got it closed back in at 13:15. Power restored.
24137 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-09-04 20:18 | 2012-09-04 21:21 | 1 | 63 | 4005951 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PER JASON BRADSHAW, THERE IS A CUTOUT HERE WHICH IS ARCING AND THE DOOR IS HANGING DOWN//THIS SERVES 1 CUSTOMER PER P.O. MAPS//--BROKEN FUSE//COD 1// VER/DBM IDC XXXX
24138 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-09-19 21:17 | 2015-09-19 22:20 | 1 | 63 | 4251611 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | BAD CURRENT LIMMING FUSE 1.6 19.9 FUSE VER/ARN
24139 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2011-09-22 18:02 | 2011-09-22 19:05 | 1 | 63 | 4897271 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POWER OFF AT 1802 POWER ON AT 1905 REPLACE TRANSFORMER COD-1 ISO TF 37830449A20466 VER/HFP L3/HFP IDCC TOF1738 XXXX
24140 | Pikeville | 3408101 | SALISBURY | PRINTER | 2018-08-02 15:52 | 2018-08-02 16:55 | 1 | 63 | 4896951 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout/ will be changing/ ISO 38831123B00094/ COD 1 replaced 2 bad cutout pole 1123-b-94 everything ok/ ISO 38831123B00094/ COD 1
24141 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2020-06-01 08:24 | 2020-06-01 09:27 | 1 | 63 | 4938161 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 151-B3-302, power restored at 9:27.
24142 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-05-27 17:12 | 2016-05-27 18:15 | 1 | 63 | 4265701 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED 2 HOT LEGS & NEUT. IN SD, RESTORED VER/CRB
24143 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2009-01-17 14:27 | 2009-01-17 15:30 | 1 | 63 | 57633-1 | 63 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BAD CONNECTION ON THE HOT LEG AT THE TRANSFORMER. L3/HFP
24144 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-12-31 08:27 | 2014-12-31 09:30 | 1 | 63 | 4894261 | 63 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS////////CONNECTIONS AT SERVICE ENTRANCE BURNED NEARLY INTO,REPLACED THEM.ALL OK AFTERWARDS VER/CRB
24145 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-08-13 18:27 | 2018-08-13 19:30 | 1 | 63 | 4949881 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse link broke
24146 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-01-14 22:32 | 2022-01-14 23:35 | 1 | 63 | 4347681 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced fuse
24147 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-05-23 15:04 | 2016-05-23 16:07 | 1 | 63 | 4252351 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT . FUSE WAS BROKE ./ 247-1802 NEW POLE NOT ON MAP WAS WHAT WAS OUT IT HAD 1 CUSTOMER ON IT/ ISO 37830247B31802/ VER/BOW
24148 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-02-04 09:20 | 2021-02-04 10:23 | 1 | 63 | 4936301 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse is blown will check and restore/// Fuse link had broke inside cutout door. I installed new fuse and restored @ 10:23
24149 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-09-09 14:27 | 2014-09-09 15:30 | 1 | 63 | 4483381 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NEED LINE CREW TO REPAIR, OR PUT ON THE POWER TEMP. ALSO NEED HAND DIG ANCHOR AND GUY ONPOLE 165-194. CUST SAID OK TO DO TOMARROW. CUT BAD LEG ON POLE. OPS ORDER MADE VER/CRB
24150 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2013-10-22 13:52 | 2013-10-22 14:55 | 1 | 63 | 4954521 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER BAD ---REPLACE WITH 25KVA -- INSTALL NEW CUTOUT COD-1 ISO TF 38830113000045 VER/HFP L3/HFP
24151 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-05-31 14:01 | 2008-05-31 15:04 | 1 | 63 | 53371-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000801//REPAIRING SLEEVE// VER/DBM IDC XXXX
24152 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-06-21 20:30 | 2021-06-21 21:33 | 1 | 63 | 4786421 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Neutral connection burnt off on service drop @ xfm///Replaced bad connection and restored @ 21:33///Only 1 customer was affected///This was a non metered account for Suddenlink
24153 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-01-07 14:59 | 2009-01-07 16:02 | 1 | 63 | 52787-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303903// 1 CUSTOMER VER/KEP L3/KEP IDC XXXX
24154 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2017-08-09 20:47 | 2017-08-09 21:50 | 1 | 63 | 4245181 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER POLE 90-400 BAD CUTOUT VER/KEP
24155 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-05-02 11:37 | 2008-05-02 12:40 | 1 | 63 | 56311-1 | 63 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3409303//ON SITE, CHECKING TROUBLE, BAD CONNECTION WHERE SERVICE MAKES UP TO XFORMER LEAD// VER/DBM IDCC MCCDL XXXX
24156 | Hazard | 3309302 | VICCO | JEFF | 2010-06-08 17:02 | 2010-06-08 17:09 | 9 | 7 | 58907-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER MAPPED TO WRONG POLE // SHOULD BE 323-83 // OPENED TR ON POLE 323-83 @ 1702 TO MAKE REPAIRS TO RISER THAT IS BURNT OFF.CONNECTOR ON SECONDARY RISER AT XFMR 37830323D00083 FAILED OPENED XFMR AT 17:02 AND CLOSED BACK AT 17:09 ENTERED MD...HFP COD-9 ISO TF 37830323D00083 VER/HFP L3/HFP IDC XXXX
24157 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-07-01 09:54 | 2018-07-01 10:57 | 1 | 63 | 4694351 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//HEARD LOUD NOISE//replace fuse door
24158 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-01-07 11:11 | 2018-01-07 12:14 | 1 | 63 | 4717171 | 63 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | called customer no 220v/ One leg of service drop burnt open in squeeze on/// Repairs made and restored service 245/122/122// One customer affected/ ISO 37820266000151/ COD 1
24159 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-10-28 07:57 | 2010-10-28 09:00 | 1 | 63 | 66025-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 37525420 // POLE 68-811 BAD CUTOUT AND LA //SERVICER REPLACED CUTOUT AND ARRESTER// ALSO INSTALLED ANIMAL GUARD // COD 1 // VER/DBM IDC XXXX
24160 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-01-16 09:51 | 2022-01-16 10:54 | 1 | 63 | 4350081 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 294-105, power restored at 10:54.
24161 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2011-02-09 11:32 | 2011-02-09 12:35 | 1 | 63 | 55624-1 | 63 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER DUE TO BAD INSUALINK. I HAVE REPAIR MADE EVERYTHING OK. VER/ARN IDC XXXX
24162 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-11-11 18:12 | 2009-11-11 19:15 | 1 | 63 | 62843-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK.//COD 1// VER/DBM IDCC PN224 XXXX
24163 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2020-02-17 11:22 | 2020-02-17 12:25 | 1 | 63 | 4412141 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken c/o on transformer pole, have changed all power restored at this loc at 1225 by amg L3/HFP
24164 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-02-08 15:50 | 2020-02-08 16:53 | 1 | 63 | 4384741 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crequired replaced connection
24165 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-08-26 13:47 | 2015-08-26 14:50 | 1 | 63 | 4174501 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE DROPCONDUCTOR BROKE AT CONNECTION ON SECONDARY POLE NEUTRAL.. FIXED AND RESTORED POWER.. COMPLETE RN VER/HFP L3/HFP
24166 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-09-24 15:57 | 2014-09-24 17:00 | 1 | 63 | 4526011 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR FAILED AND BURNT NEUTRAL IN TWO. OOONLY ONE CUSTOMER AFFECTEDOO REPAIRED WIRE AND RESTORED @ 17:00. SH VER/CRB
24167 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-11 17:42 | 2008-12-11 18:45 | 1 | 63 | 56914-1 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP LINE FUSE OUT, BAD CUTOUT ON 101. INACTIVE XFMR ON POLE, REMOVED HOT TAP COD-1 L3/HFP IDC XXXX
24168 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-12-23 15:00 | 2020-12-23 16:03 | 1 | 63 | 4797851 | 63 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 OF 3 XFR BANK FUSES IS OUT,WILL RE-FUSE//////RE-FUSED&RESTORED.SEND TO TECHNICIAN,LAST 2OR3 TIMES THIS HAS BEEN OUT,IT APPEARED THAT FUSES WERE MELTING OUT(POSSIBLE OVERLOADED XFRS?).MAY NEED BIGGER BANK.25S AT PRESENT TIME
24169 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-11-25 14:24 | 2011-11-25 15:27 | 1 | 63 | 4114451 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE DOOR BURNT UP, MAY HAVE TO CHANGE CUTOUT. REPLACED CUTOUT APR AT 1527 CLOSE TICKET//COD 1// VER/DBM IDCC FPNONE FEC49 XXXX
24170 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2021-10-13 17:12 | 2021-10-13 18:15 | 1 | 63 | 4347731 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv cut out door. replaced, restored
24171 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2012-05-05 15:27 | 2012-05-05 16:30 | 1 | 63 | 4750791 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN.CHG CUTOUT.RE FUSED..///VER/CRB L/3 CRB IDC XXXX
24172 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-08-30 14:12 | 2017-08-30 15:15 | 1 | 63 | 4310701 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE///////FUSE BROKEN,SEEMED TO BE EXCESSIVELY STRONG SPRING ON CUTOUT.RE-FUSED&RESTORED 38821106A20366 VER/AWD L3/HFP XXXHFP
24173 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-11-20 09:24 | 2022-11-20 10:27 | 1 | 63 | 4164931 | 63 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found cutout door burning open transformer to replace cutout.. transformer back in at 10:27
24174 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-03-15 13:37 | 2016-03-15 14:08 | 2 | 31 | 4851531 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | COMPETED FUSELINK BROKE REPLACED PUT BACK IN SERVICE 14:08 ISO 38831079000005 COD 2 VER/AWD
24175 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-05-17 16:13 | 2022-05-17 17:15 | 1 | 62 | 4904081 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service broke. Making repairs. Restored at 17:15.
24176 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-12-11 08:38 | 2022-12-11 09:40 | 1 | 62 | 4249761 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced fuse door
24177 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2022-11-15 09:01 | 2022-11-15 09:32 | 2 | 31 | 4143791 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @24-A3-57, checking. Fuse melted out, refused @0932. (COD 2)
24178 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-03-01 15:08 | 2016-03-01 16:10 | 1 | 62 | 4792751 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 378-708 . REPLACED CUTOUT , CLOSED FUSE BACK @ 16:10 ./ ISO 37830387A10708/ COD 1/ VER/BOW
24179 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-25 17:03 | 2019-06-25 17:34 | 2 | 31 | 4595781 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout was broke when crew got there to change it. did not have a trouble call. have no idea when the actual outage started. closed transformer @ 1734/ not sure what time the outage started. The crew told me the cutout was broke and that they changed it/ ISO 38820769D00070/ COD 2
24180 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-02-22 13:59 | 2019-02-22 14:30 | 2 | 31 | 4844401 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout changed, power restored at 14:30
24181 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-03-15 08:33 | 2019-03-15 09:35 | 1 | 62 | 4987421 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced hottap
24182 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-08-10 20:19 | 2014-08-10 21:21 | 1 | 62 | 4351391 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REFUSED XFMR2121 VER/TOM L3/TOM
24183 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-09-22 19:22 | 2011-09-22 20:24 | 1 | 62 | 4897561 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE COD-1 ISO TF 38830069D16024 VER/HFP L3/HFP IDC XXXX
24184 | Hazard | 3308001 | JACKSON | S.JACKSON | 2018-12-06 16:01 | 2018-12-06 16:32 | 2 | 31 | 4513521 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke L3/HFP
24185 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-09-23 14:38 | 2012-09-23 15:40 | 1 | 62 | 4080641 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE COD-1 ISO TF 37830410B00036 VER/HFP L3/HFP IDC XXXX
24186 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-03-03 17:58 | 2015-03-03 19:00 | 1 | 62 | 4095171 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VINES AND CUT-OUT///COD 1// VER/DBM L3/HFP XXX
24187 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-04-07 11:44 | 2008-04-07 12:15 | 2 | 31 | 64840-1 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 10T TRANS. FUSE VER/HFP IDC XXXX
24188 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-10-25 11:12 | 2014-10-25 12:14 | 1 | 62 | 4660941 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 ALUMINUM LEADS IN THE SECONDARY LUGS OF THE TRANSFORMER HAS BURNED UP. I WILL REPLACE WITH #2 COPPER. I OPENED TRANSFORMER AT 11:58 AND CLOSED AT 12:14. PLEASE SEND TO RYAN ROWE TO HAVE DEAD TREE CUT OFF THE LASH CABLE. VER/CRB
24189 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-02-17 09:06 | 2020-02-17 10:08 | 1 | 62 | 4411131 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop burnt into will make repairs OPENED XFMR @ 0940 CLOSED @ 1008 ¦¦¦ NOTE ONLY 1 CUSTOMER ON XFMR
24190 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-02-14 08:58 | 2012-02-14 10:00 | 1 | 62 | 4347211 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BURNED INTO, CUSTOMER HAS DAMAGES/COD-1 VER/KEP VER/HFP L3/HFP IDC XXXX
24191 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-08-28 12:19 | 2015-08-28 13:21 | 1 | 62 | 4179571 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 2ND TIME THIS HAS HAPPENED TRANSFORMER LUG BROKEN NO CREW REQUIRED/ ISO 38830198000070/ COD 1/ VER/BOW
24192 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-05-19 22:50 | 2017-05-19 23:52 | 1 | 62 | 4823591 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD 25 AMP BAYONET FUSE IN THREE PHASE PADMOUNT TRANSFORMER VER/CRB
24193 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-12-10 10:28 | 2015-12-10 11:30 | 1 | 62 | 4522991 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 15T LF @ 67-51 RESTORED. BAD C/O DOOR// VER/ ADH
24194 | Hazard | 3303902 | LESLIE | WOOTON | 2009-02-03 13:10 | 2009-02-03 14:12 | 1 | 62 | 55160-1 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | GUY WIRE BROKEN GOT INTO XFMR RISER REMOVED GUY NOT NEEDED VER/KEP L3/KEP AJBC CCO FEC57
24195 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-01-31 14:28 | 2022-01-31 15:30 | 1 | 62 | 4419261 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | neutral had pulled out of barrel.. redid connection, voltage checks good
24196 | South Williamson | 3411401 | DEWEY | INEZ | 2020-11-09 12:56 | 2020-11-09 13:58 | 1 | 62 | 4654751 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replacing bad xfmer.. back to normal
24197 | South Williamson | 3202201 | LOVELY | LOVELY | 2012-09-15 17:13 | 2012-09-15 18:15 | 1 | 62 | 4050651 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE DROP//MAKING REPAIRS//REPAIRS MADE//COMP;LETE//EM// VER/DBM IDCC CNT12 XXXX
24198 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-11-19 10:33 | 2016-11-19 11:35 | 1 | 62 | 4113091 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK VER/CRB
24199 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-01-24 11:41 | 2019-01-24 12:43 | 1 | 62 | 4717431 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad connection @weatherhead, replaced/repaired
24200 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2012-01-21 16:38 | 2012-01-21 17:40 | 1 | 62 | 4281111 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN, REPLACED CUTOUT AND REFUSED XFMR, POWER RESTORED AT 17:40 ///VER/CRB IDC XXXX
24201 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-10-10 17:09 | 2008-10-10 18:11 | 1 | 62 | 54944-1 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3300601// BAD CONNECTION ONWEATHERHEAD REPLACED CONNECTOR ON WEATHERHEAD P HICKMAN// VER/DBM IDCC MCCDL XXXX
24202 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-05-18 12:58 | 2019-05-18 14:00 | 1 | 62 | 4293831 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ad connection at pole, repaired
24203 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-05-09 09:31 | 2008-05-09 10:33 | 1 | 62 | 59022-1 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT.//3409302BROKEN CUTOUT. REPLACED BAD CUTOUT AND ANOTHER ONE THAT WAS CRACKED. SH/VER/CRB IDC XXXX
24204 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-10-29 12:19 | 2008-10-29 12:50 | 2 | 31 | 60512-1 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3117601// BAD S/C CUTOUT DOOR COD-2 IDC XXXX
24205 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2015-12-23 14:43 | 2015-12-23 15:45 | 1 | 62 | 4553071 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL AND 1 HOT WIRE BURNT IN TWO, POWER RESTORED. ONLY 1 CUST. OUT. VER/CRB
24206 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-11-14 23:07 | 2014-11-15 00:09 | 1 | 62 | 4729061 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE DROP BURNED INTO,WILL REPLACE IT//////////REPLACED 4/3 DROP W 2/3.BURNED INTO NEAR WHERE SPLICE HAD TAPE AROUND DROP,MAY HAVE BEEN A FACTOR IN FAILURE VER/CRB
24207 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-12-01 09:55 | 2012-12-01 10:26 | 2 | 31 | 4434141 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM REPLACED BAD 19.9 CUTOUT ON POLE 165-132. RELEASED BY CREW 078S01 ///VER/CRB L/3 CRB
24208 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2022-06-10 17:02 | 2022-06-10 17:33 | 2 | 31 | 4055471 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection,, complete
24209 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2021-12-11 17:37 | 2021-12-11 18:39 | 1 | 62 | 4183061 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad insulink/repair made. tre
24210 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-03-05 15:54 | 2018-03-05 16:56 | 1 | 62 | 4968391 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | insalink pulled apart, fixed/ ISO 38830045B33076/ COD 1
24211 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-03-04 12:03 | 2010-03-04 13:05 | 1 | 62 | 62769-1 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION VER/HFP L3/HFP IDCC MCCDL XXXX
24212 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-06-18 14:00 | 2012-06-18 15:02 | 1 | 62 | 4927221 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RE-MADE SECONDARY CONNECTIONS AND CUT TREELIMBS OUT VER/HFP L3/HFP IDCC TOF1146, ESTIMATED TIME OFF XXXX
24213 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-06-03 01:21 | 2009-06-03 02:23 | 1 | 62 | 63520-1 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR//VER/CRB IDC XXXX
24214 | Hazard | 3308001 | JACKSON | S.JACKSON | 2021-01-14 15:06 | 2021-01-14 16:08 | 1 | 62 | 4869511 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on transformer
24215 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2011-02-06 14:26 | 2011-02-06 15:28 | 1 | 62 | 54851-1 | 62 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WR# 38708197 // BAD CONN. ON BUILDING// VER/DBM IDC XXXX
24216 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-01-29 07:58 | 2015-01-29 09:00 | 1 | 62 | 4971731 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR TO RE-FUSE//////////RE-FUSED AND RESTORED,ALL OK AFTERWARDS//////APPEARS FUSE SIMPLY BROKE INTO/COD 1// VER/ ADH L3/HFP XXX
24217 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2020-01-12 17:03 | 2020-01-12 18:05 | 1 | 62 | 4292351 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole 178-5 does not exist. Broke 19.9 cut out pole 178-261. Need two men and a big bucket. From Hwy 80, turn right onto hey 476 toward Dwarf. Turn on to Turkey Ridge Rd. Will be first house on right. power restored at 18:05
24218 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-08-09 15:42 | 2012-08-09 16:44 | 1 | 62 | 4916781 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKING. FUSE PULLED APART ON THIS TRANS., REFUSED AT 16:44. ///VER/CRB L/3 CRB IDC XXXX
24219 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2019-02-22 19:07 | 2019-02-22 20:09 | 1 | 62 | 4845751 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse
24220 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2013-08-28 14:23 | 2013-08-28 15:25 | 1 | 62 | 4715151 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTIONS AT THE TRANSFORMER. JOEY REED IS GOING TO REPLACE THE TRANSFORMER TOMARROW. VER/SEF IDC XXXX
24221 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-12-23 11:03 | 2022-12-23 12:05 | 1 | 62 | 4315611 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed in service. Replaced connections and restored @ 12:05. sh
24222 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-01-17 16:53 | 2012-01-17 17:55 | 1 | 62 | 4270481 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 42-159 CUT OUT BAD//MADE MDC COD 1. ////VER/CRB IDCC PN14 XXXX
24223 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-07-09 08:14 | 2010-07-09 08:45 | 2 | 31 | 63852-1 | 62 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830182B22512, REPLACED CUTOUT//COD 2//ISO IDCC PN2508, CNT4 XXXX
24224 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-11-12 10:04 | 2012-11-12 11:05 | 1 | 61 | 4384941 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD, ALL POWER RESTORED, ONLY 1 CUSTOMER.//COD 1?// VER/DBM IDC XXXX
24225 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2017-03-19 08:13 | 2017-03-19 09:14 | 1 | 61 | 4570021 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NETURAL BROKE IN SERVICE,MADE REPAIRES ,OPEN TRANSFORMER AT9:08 AND CLOSE AT9:14///ORIGINAL OUTAGE RECORD/// VER/DKM
24226 | Pikeville | 3413402 | GARRETT | LACKEY | 2022-04-05 19:54 | 2022-04-05 20:55 | 1 | 61 | 4726451 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad nuetral barrel splice.// Repaired nuetral and restored @ 20:55
24227 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2014-01-30 02:11 | 2014-01-30 03:12 | 1 | 61 | 4326311 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD HEATING UP ON BANK OF XFMRS ON POLE 37830048A30854 RELEASED BY CREW 074S05 CONNECTOR OVERHEATED OPENED XFMR BANK AT 2:11 REPAIRS MADE ON AT 3:12 D SAMMONS VER/KEP IDC CHANGED FROM CONTAMINATION XXXX
24228 | Whitesburg | 3401301 | FLEMING | NEON | 2017-03-30 13:21 | 2017-03-30 14:22 | 1 | 61 | 4597621 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | ONLY ONE CUSTOMER AFFECTED , BAD SPLICE IN SERVICE DROP , MADE REPAIRS RESTORED POWER AT 14:22.. VER/HFP L3/HFP
24229 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-11-21 15:14 | 2008-11-21 16:15 | 1 | 61 | 50670-1 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT IDC XXXX
24230 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2008-01-09 05:29 | 2008-01-09 06:30 | 1 | 61 | 55007-1 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION AT CUSTOMERS WEATHERHEAD. REPAIRED. SH VER/KEP IDC XXXX
24231 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2017-06-03 15:18 | 2017-06-03 16:19 | 1 | 61 | 4902261 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY RED TO RED BURNT OUT. REDONE ALL CONNECTIONS ON POLE. POWER RESTORED @ 16:19 37830449A10107 VER/AWD
24232 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-05-08 13:16 | 2011-05-08 14:17 | 1 | 61 | 4019821 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 39869811 // REPLACED BAD CONNECTER ON XFORMER ON UNDERGROUND. VER/HFP L3/HFP IDC XXXX
24233 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-01-27 09:04 | 2021-01-27 10:05 | 1 | 61 | 4897661 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 19-231 bad squeeze on. opened xfmer at 0945 , restored @ 10:05
24234 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2020-03-07 15:23 | 2020-03-07 16:24 | 1 | 61 | 4459831 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | xfmr lead in xfmr burned up we had to change out xfmr lug. please send this to engineering to look at this xfmr bank at the secondary wiring.
24235 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-10-13 18:11 | 2012-10-13 19:12 | 1 | 61 | 4137551 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKING.FUSE BROKE AT POLE 329-93, REFUSED AT 19:12. COD-1 ISO TF 37830329000093 VER/HFP L3/HFP IDC XXXX
24236 | Hazard | 3302703 | HAZARD | HAZARD | 2022-09-06 10:14 | 2022-09-06 11:15 | 1 | 61 | 4845631 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | I repaired a broken service neutral at the weather head from pole 272-D2-596.
24237 | South Williamson | 3200302 | BELFRY | TOLER | 2018-12-08 12:44 | 2018-12-08 13:45 | 1 | 61 | 4517961 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I replaced the bad transformer cutout, power is restored. L3/HFP
24238 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-12-30 12:23 | 2021-12-30 13:24 | 1 | 61 | 4239081 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Broken hotline clamp on pole 222-D2-634. Power restored at 13:24.
24239 | Hazard | 3303901 | LESLIE | HYDEN | 2012-06-01 16:44 | 2012-06-01 17:45 | 1 | 61 | 4866791 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED XFMR//COD 1// VER/DBM IDC XXXX
24240 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-12-23 22:44 | 2014-12-23 23:45 | 1 | 61 | 4878141 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT DOOR// COD 1// VER/ ADH VER/DKG L3/DKGXXXC FEC
24241 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2016-12-21 13:38 | 2016-12-21 14:39 | 1 | 61 | 4227221 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION @ XFMER. VER/HFP L3;/HFP
24242 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-11-04 18:11 | 2019-11-04 19:12 | 1 | 61 | 4291831 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt into @ xfm.repairs made..restored.
24243 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-08-11 11:09 | 2009-08-11 12:10 | 1 | 61 | 50451-1 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP 3000902// BAD ARRESTOR--SEND TO L RAYBURN /// SENT EMAIL TO LLOYD RAYBURN TO HAVE ARRESTOR REPLACED...HFP COD-1 ISO TF 39831123C24607 L3/HFP IDC XXXX
24244 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2018-02-05 11:11 | 2018-02-05 12:12 | 1 | 61 | 4806371 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t fuse out looks like fuse melted out replaced fuse everything ok
24245 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2009-10-19 10:41 | 2009-10-19 11:42 | 1 | 61 | 57100-1 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP NO CREW REQUIRED/REPLACED CUTOUT DOOR /// COD-1 L3/HFP IDC XXXX
24246 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-11-09 15:22 | 2008-11-09 16:23 | 1 | 61 | 63492-1 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING CUTOUT DOOR// VER/TOM IDCC PN128 XXXX
24247 | Pikeville | 3421001 | BREAKS | CITY | 2010-08-06 09:24 | 2010-08-06 10:25 | 1 | 61 | 50195-1 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE WEATHERHEAD ON ONE HOT LEG. I REPAIRED THE CONNECION. ONLY ONE CUSTOMER AFFECTED.
24248 | Hazard | 3309302 | VICCO | JEFF | 2010-07-16 23:25 | 2010-07-17 00:26 | 1 | 61 | 51213-1 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309302// CONNECTOR BURNED INTO ON 2/3 SERVICE PART OUT ONLY IDCC PN244 XXXX
24249 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-08-16 14:12 | 2020-08-16 15:13 | 1 | 61 | 4335521 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutralbroke into , I repaired it
24250 | Hazard | 3303902 | LESLIE | WOOTON | 2021-06-22 10:10 | 2021-06-22 11:11 | 1 | 61 | 4790861 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cut-out. Power restored @ 11:11
24251 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-28 01:49 | 2011-01-28 02:50 | 1 | 61 | 50139-1 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FAILED CURRENT LIMITING FUSE ON POLE 193-191 VER/ARN IDCC PN190 XXXX
24252 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-04-16 10:34 | 2012-04-16 11:35 | 1 | 61 | 4675741 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LOOKED BAD .. CLOSED BACK IN AT 11:35 RESTORED.. CAY //COD 1// VER/DBM IDC XXXX
24253 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2018-05-19 19:56 | 2018-05-19 20:57 | 1 | 61 | 4379401 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//no crew required
24254 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-09-02 21:05 | 2017-09-02 22:06 | 1 | 61 | 4325641 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE XFMR CUTOUT ON POLE 278-297, REPLACED CUTOUT, CLOSED AT 22:06. TICKET COMPLETE VER/KEP
24255 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-02-01 17:24 | 2021-02-01 18:25 | 1 | 61 | 4926911 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse appears to have broke. Restored @ 18:25. sh
24256 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-07-16 08:33 | 2010-07-16 09:34 | 1 | 61 | 50797-1 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE COD-1 VER/HFP L3/HFP IDC XXXX
24257 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-06-17 14:44 | 2011-06-17 15:45 | 1 | 61 | 4334811 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER. COD-1 ISO SO 37830295A00018 VER/HFP L3/HFP
24258 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2017-12-08 18:06 | 2017-12-08 19:07 | 1 | 61 | 4631261 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Replaced connection at the customers weatherhead. One customer only affected./ ISO 37820098A00120/ COD 1
24259 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-10-13 15:44 | 2012-10-13 16:45 | 1 | 61 | 4137281 | 61 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL CONNECTOR ON SERVICE PULLED OUT, CHANGED OUT CONNECTOR POWER RESTORED. VER/HFP L3/HFP IDC XXXX
24260 | Hazard | 3302704 | HAZARD | KENMONT | 2013-05-14 15:35 | 2013-05-14 16:36 | 1 | 61 | 4113871 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR LEADS BURNT UP WILL HAVE TO REPLACE///// OPENED XFMR 16:15 CLOSED 16:36. POWER OK. ///VER/CRB L/3 CRB IDCC TOF 1615 XXXX
24261 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-03-12 11:24 | 2009-03-12 12:25 | 1 | 61 | 57520-1 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP BROKEN FUSE LINK COD-1 L3/HFP IDC XXXX
24262 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-06-29 13:29 | 2020-06-29 14:30 | 1 | 61 | 4089591 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke // power restored @ 1430
24263 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-10-18 21:24 | 2013-10-18 22:25 | 1 | 61 | 4947581 | 61 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | THE RISER LEAD BROKE OUT OF THE TOP OF THE CUTOUT, I REPLACED THE RISER VER/SEF
24264 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-09-14 17:30 | 2011-09-14 18:30 | 1 | 60 | 4870181 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I WILL BE CHANGING 4/3 DROP TO 2/3 DROP. I HAVE SERVICE DROP REPLACED EVEYTHING OK. VER/HFP L3/HFP IDCC TOF1539, ESTIMATED TIME OFF XXXX
24265 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2022-02-11 22:00 | 2022-02-11 22:10 | 6 | 10 | 4475281 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4 homes with 1 hot leg; either secondary squeeze or bad xfmr, bring 37.5 KVA in case; Truck OK; Flaggers Required Released by crew 078E02,open xfmr @ 2200 in @ 2210 please close ticket thanks.bt
24266 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-10-26 19:10 | 2021-10-26 20:10 | 1 | 60 | 4022791 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced service connects to weatherhead restored @2010
24267 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-11-01 09:10 | 2009-11-01 09:30 | 3 | 20 | H54509-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3417602// SERVICE BURN DOWN AT POLE 965-D-29. MAKING REPAIRS. OPENED TRANSFORMER AT 09:10 CLOSED IN AT 09:30 //VER/GAH IDC XXXX
24268 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-10-06 14:48 | 2010-10-06 15:48 | 1 | 60 | 57455-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPEN TRANSFORMER AND REMOVED HOT TAP AT 14:48//REPLACED TRANSFORMERS//COD 1// VER/DBM IDCC TOF1404 XXXX
24269 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-02-21 15:25 | 2020-02-21 15:45 | 3 | 20 | 4423211 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Opened xfm cutout on pole 37830069000047 @ 15:25 closed @ 1545 to replace broken arrester. Replaced cutout also L3/HFP
24270 | Pikeville | 3401001 | ELWOOD | DORTON | 2019-03-28 10:07 | 2019-03-28 10:27 | 3 | 20 | 4032081 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OUTAGE NECESSARY TO ALLOW CREW TO REPLACE DEFECTIVE INSULATOR THEY FOUND DOING ANOTHER JOB ¦¦ COD-3 ISO PO @ 37830214D00176 OFF@ 1007 ON@ 1027
24271 | Whitesburg | 3401301 | FLEMING | NEON | 2014-01-30 22:45 | 2014-01-30 23:00 | 4 | 15 | 4332071 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY LEAD BURNT INTO AT XFMR ON POLE 356-159 , OPENED XMER @22:45 MADE REPAIRS RESTORED POWER AT 23:00 VER/SEF
24272 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2016-10-13 13:35 | 2016-10-13 14:05 | 2 | 30 | 4990701 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT GOING BAD ON POLE 37830048B11400, MILES R. ON THE WAY TO HELP WITH BIG BUCKET. NO OUTAGE YET BUT WILL HAVE TAKE 3 CLAMPS OFF @ POLE48-B3-1399 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. TOOK CLAMPS OFF @1335, PUT BACK ON @1405, ALL POWER RESTORED. VER/CRB L3/HFP XXXHFP
24273 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2019-01-23 17:58 | 2019-01-23 18:58 | 1 | 60 | 4712171 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse was broken, apr at 1658 close ticket. dwest L3/HFP
24274 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2022-08-05 15:05 | 2022-08-05 15:15 | 6 | 10 | 4681001 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | had to open line fuse to put on a new hot tap that was broke opened at 15:05 and restored at 15:15
24275 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-06-23 15:10 | 2015-06-23 15:30 | 3 | 20 | 4645251 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE ON 37830328D00014 TO CHANGE CUTOUT ON POLE 37830328D00187/ ISO 37830328D00014/ COD 1/ OPEN LINE FUSE AT 15:10 CLOSED AT 15:30 VER/HFP L3/HFP
24276 | Hazard | 3309302 | VICCO | JEFF | 2013-11-30 18:50 | 2013-11-30 19:10 | 3 | 20 | 4090081 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4089891//OPENED FUSE @ 1850 TO MAKE REPAIRS//RESTORED @ 1910//COD 3// VER/DBM L3/HFP
24277 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-07-01 10:49 | 2020-07-01 11:19 | 2 | 30 | 4098751 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | A 1.6 T fuse failed at pole 247-C1-1350. Fuse was not blown just broken apart. Power restored at 11:19.
24278 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-10-15 15:15 | 2015-10-15 15:25 | 6 | 10 | 4352061 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING CUTOUT/ 1515 1525/ ISO 37820050000032/ COD 6/// CHANGED BAD CUTOUT ON POLE#50-32////OPENED TAP @ 15:15 AND CLOSED BACK IN @ 15:25/ VER/BOW L3/HFP XXXHFP
24279 | Hazard | 3311103 | STINNETT | WENDOVER | 2017-02-21 11:45 | 2017-02-21 12:45 | 1 | 60 | 4411951 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 7.2 CUTOUT/ ISO 37830412B00441/ COD 1/ VER/BOW L3/HFP XXXHFP
24280 | Hazard | 3303902 | LESLIE | WOOTON | 2013-06-14 14:30 | 2013-06-14 15:00 | 2 | 30 | 4334181 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 19.9 CUTOUT OPEN @1430 CLOSED @1500 IDCC TOF1407 XXXX
24281 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-04-15 01:15 | 2017-04-15 01:45 | 2 | 30 | 4647111 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DKM/UNIT 3524 REPORTS HOT LINE CLAMP WAS FAILIMNG ON POLE 850-26 AND HE REMOVED AT 0115(NO OUTAGE TILL THEN) HE REMOVED IT TO REPLACE IT AND A BELL--HE RESTORD IT AT 0145 VER/CRB L3/HFP XXXHFP
24282 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-07-12 21:45 | 2018-07-12 22:45 | 1 | 60 | 4768511 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned into had old gate and power restored
24283 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-03-25 13:10 | 2014-03-25 14:10 | 1 | 60 | 4523891 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S01 REPLACED CONN, ON SERVICE DROP. VER/CRB
24284 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-02-09 13:30 | 2018-02-09 14:00 | 2 | 30 | 4820931 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr. fuse open from 13:30 to 14:00
24285 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2020-07-03 13:15 | 2020-07-03 14:15 | 1 | 60 | 4106471 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer leaking on pole 379-158. transformer looks to have small hole on bottom side of can.. need to go ahead and change it out. need one man and big bucket to change transformer. open transformer @ 13:15 closed @ 14:15
24286 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-08-14 13:10 | 2013-08-14 14:10 | 1 | 60 | 4664961 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE BURNT DOWN, REPLACED WITH 2/3 SERVICE. OPENED TRANSFORMER ON POLE 37830248A00172 AT 13:10, CLOSED AT 14:10 POWER RESTORED.//MADE MDC VER/CRB L/3 CRB HFPC CDC89 CMCCDL
24287 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-06-18 13:06 | 2018-06-18 13:26 | 3 | 20 | 4616471 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repaired floating phase and changed cutout/ ISO 38830728000010/ COD 3
24288 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-07-22 22:30 | 2022-07-22 23:30 | 1 | 60 | 4551031 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ETA 2215//open tran 38830449000073 srv drop shorted and burnt down-repaired-open tran at 22:30 in at 23:30 cust going to replace entrance cable and call back for a reconnect--ds072222 Only ! customer affected, individual calling had bad service entrance
24289 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2014-08-20 10:20 | 2014-08-20 10:30 | 6 | 10 | 4388141 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | SECONDARY LOOP BURNT OPEN @ POLE 654-240///GOING TO OPEN XFMER ON 654-240 TO MAKE REPAIRS///OPENED XFMER AT 10:20 AND CLOSED AT 10:30///ALL CUST RESTORED///COMPLETE BR
24290 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-04-05 19:30 | 2018-04-05 20:30 | 1 | 60 | 4193701 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutral broke at weatherhead, repaired neutral, opened transformer at 20:15, closed at 20:30 all power restored.// can close mwl cod 1 iso 37830508000010
24291 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-03-28 17:21 | 2019-03-28 17:36 | 4 | 15 | 4033471 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | METER IS BLANK broke cutout on pole 150-101 OFF 1721 ON @ 1736
24292 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2013-01-23 23:11 | 2013-01-23 23:23 | 5 | 12 | H4735281 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART POWER SERVICE DROP BURNT INTO ONE HOT LEG HOLDING WIRE UP. OPENED XFMR AT 23:11 MADE REPAIRS RESTORED POWER AT 23:23 VER/KEP IDC XXXX
24293 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-11-27 20:15 | 2008-11-27 20:35 | 3 | 20 | 52710-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP SERVICE WIRE BURNED DOWN AT CUST SERV POLE. HAD XFMR 38830783000148 OPEN FROM 20:15 TO 20:35 TO MAKE REPAIRS. REPAIRS COMPLETE. SH ON @ 2047//VER/CRB IDC XXXX
24294 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-12-20 23:55 | 2018-12-21 00:25 | 2 | 30 | 4584481 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | arcing transformer. Cutout busted on pole 190-B-154, customer had full power until I took trans. off @2355, made repairs and closed back in @0025. L3/HFP
24295 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2022-11-01 09:10 | 2022-11-01 09:30 | 3 | 20 | 4085201 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer restored
24296 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-12-25 15:45 | 2021-12-25 16:15 | 2 | 30 | 4225741 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Transformer off from 15:45 to 16:16. Bad neutral connection on pole//cod 2
24297 | South Williamson | 3411401 | DEWEY | INEZ | 2008-08-21 13:30 | 2008-08-21 14:00 | 2 | 30 | 53786-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401////VER/CRB IDCC PN216 XXXX
24298 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-07-06 12:35 | 2022-07-06 13:35 | 1 | 60 | 4397421 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 478-404, restored at 1335. complete
24299 | Hazard | 3309302 | VICCO | JEFF | 2020-02-25 13:50 | 2020-02-25 14:00 | 6 | 10 | 4430861 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cracked 34kv cutout on pole 348-64. Need flaggers, pole is beside road in Montgomery Creek of Vicco. Customers still have power at this time. Released by crew 077H20 opened at 13:50 and restored at 14:00 replaced cutout L3/HFP
24300 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-09-24 00:45 | 2019-09-24 01:15 | 2 | 30 | 4052361 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | off 1245-0115
24301 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2021-11-26 12:30 | 2021-11-26 13:00 | 2 | 30 | 4126471 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad 19.9 bcutout on pole 329-253. Changed out and power restored at 13:00
24302 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-02-22 16:10 | 2009-02-22 17:10 | 1 | 60 | 50381-1 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I AM GOING TO OPEN TRANSFORMER LONG ENOUGH TO CHECK CONNECTIONS. ONE OF THEM APPEARS TO BE BURNED ALMOST APART. #2 SERVICE CONNECTOR WAS FROZEN APART//VER/CRB IDC XXXX
24303 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-06-07 07:40 | 2018-06-07 08:40 | 1 | 60 | 4564451 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Appears xfmr fuse link broke. Restored @ 8:40. sh
24304 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-03-22 15:33 | 2014-03-22 16:33 | 1 | 60 | 4518451 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SEC. PLEASE SENT TO STEVE M SEC NEEDS REPLACED BETWEEN POLES 502-86 &140 OLD #4 COD TO SMALL TRUCK OK WILL NEED FLAGGERS. APR CLOSE TICKET. DWEST NEEDS TO BE 1/0 VER/SEF
24305 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-05 07:11 | 2011-01-05 07:23 | 5 | 12 | 58778-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE WAS BURNING ON TOP OF TRANS. AT POLE 215-334. I REMOVED CURRENT FUSE. ADJUSTED TIME OFF TO ALLOW TIME TO OPEN & ISOLATE BAD CLF COD-5 ISO TF 37830215D00334 VER/HFP L3/HFP IDCC PN368 XXXX
24306 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2019-09-29 14:25 | 2019-09-29 15:25 | 1 | 60 | 4071591 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | l/f not out, transformer fuse out on pole 1121-236, power restored at this loc at 1525 by amg
24307 | Pikeville | 3409502 | BURDINE | LEVISA | 2014-08-01 12:00 | 2014-08-01 12:30 | 2 | 30 | 4316171 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. IS LEAKING OIL. LINE CREW IS ON THE WAY TO CHANGE IT OUT. LINE CREW CHANGED OUT TRANS. ON POLE 335-197. WE OPENED TRANS AT 12:00 AND CLOSED NEW ONE IN AT 12:30. THERE WERE 2 METERS ON THIS TRANS. VER/CRB
24308 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2011-11-15 08:15 | 2011-11-15 08:25 | 6 | 10 | H4077621 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED TRANSFORMER CUTOUT OPENED LINE FUSE AT 0815 CLOSED AT 0825.//MADE MDC /// VER/CRB IDCC DUP TO OPEN LINE FUSE XXXX
24309 | Hazard | 3303902 | LESLIE | WOOTON | 2015-07-31 11:35 | 2015-07-31 12:05 | 2 | 30 | 4963341 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE FELL OPEN, DONT BELIEVE IT HADNT BEEN CLOSED IN ALL THE WAY// VER/ ADH
24310 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2011-06-02 14:15 | 2011-06-02 15:15 | 1 | 60 | 4224611 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT POLE 991-D2-101....WILL RAISE UP & GIVE IT A LOOK & TRY FUSE....//....OLD FUSE JUST DETERIORATED....RE-FUSED....POWER ON....JRV....05/02/11 // COD-1 ISO TF 38820991D20101 VER/HFP L3/HFP IDC XXXX
24311 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2018-08-13 15:05 | 2018-08-13 16:05 | 1 | 60 | 4948281 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t transformer fuse broke. fused up e verything ok
24312 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-09-17 19:30 | 2012-09-17 20:00 | 2 | 30 | 4054591 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830231B00010 WE HAVE LINE FUSE BLOWN, NO OUTAGE. LOOKS LIKE FUSE TAIL HANGING DOWN BUT POWER STILL ON C PHASE./// CHECKED C/O, GATE BURNT UP, REPLACED CUTOUT GATE, POWER RESTORED.//C PHASE ONLY COD 2 ///VER/CRB L/3 CRB IDC XXXX
24313 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2019-12-17 09:40 | 2019-12-17 10:00 | 3 | 20 | 4159091 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required can reach with bucket Released by crew 078S03, no outage. crack in cutout. deenergized line at 9:40, power restored at 10:00
24314 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-07-17 12:45 | 2017-07-17 13:45 | 1 | 60 | 4134181 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BUSTED ON TRANS. ON POLE 25-A-354, MADE REPAIRS @1345./ ISO 37820025A00354/ COD 1/ VER/BOW L3/HFP XXXHFP
24315 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-08-15 14:00 | 2013-08-15 14:30 | 2 | 30 | 4668671 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, I HAVE IT CHANGED OUT, TOOK POWER OFF AT 1400 AND RESTORED AT 1430 VER/CRB L/3 CRB
24316 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-04-13 19:20 | 2015-04-13 19:35 | 4 | 15 | 4313921 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP LEAD ON POLE 785-635 BURNT INTO///OPENED 3 LINE FUSES ON POLE 785-635 @ 19:20 TO MAKE REPAIRS///REPAIRS MADE AND CLOSED 3 SWITCHES BACK IN @ 19:35 RESTORING ALL CUST///COMPLETE BR/ NO OUTAGE UNTIL OPENED FUSES/ ISO 38830785D20635/ COD 4/ VER/BOW
24317 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-04-22 21:00 | 2016-04-22 22:00 | 1 | 60 | 4118241 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT VER/AWD
24318 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-05-18 06:30 | 2011-05-18 07:00 | 2 | 30 | 4107511 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED/CHG DOOR VER/KEP IDCC TOF0509 ESTIMATED TIME OFF XXXX
24319 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-07-04 16:30 | 2016-07-04 17:00 | 2 | 30 | 4522701 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOMETHING ON POLE MAKING FRYING NOISE, REPLACED BAD CUTOUT, PULLED POWER OFF AT 16:30, RESTORED AT 17:00 HRS/ ISO 38831086000001/ COD 2/ VER/BOW
24320 | Whitesburg | 3401301 | FLEMING | NEON | 2014-02-03 14:20 | 2014-02-03 14:40 | 3 | 20 | 4343951 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTIONS ON POLE OPENED TRANSFORMER AT 1420 CLOSED IT AT 1440 VER/CRB
24321 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-11-26 12:00 | 2021-11-26 13:00 | 1 | 60 | 4125921 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg almost burndt into @1125-D-573, will have to open trans. to make repairs, will keep track of times. Opened trans. @1200, made repairs and closed back in @1300.
24322 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-12-16 11:15 | 2015-12-16 11:25 | 6 | 10 | 4536961 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD BURNT OFF AT TRANSFORMER. OPENED TRANSFORMER@ 11:15 POWER RESTORED @ 11:25 VER/CRB
24323 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-11-07 17:30 | 2008-11-07 18:30 | 1 | 60 | 63090-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3003703// SERVICE NEUTRAL BURNED IN TWO//OPENED XFORMER AT 17:30 BACK ON AT 18:30//COD 1// VER/DBM IDC XXXX
24324 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-01-30 22:45 | 2014-01-30 23:00 | 4 | 15 | 4332071 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY LEAD BURNT INTO AT XFMR ON POLE 356-159 , OPENED XMER @22:45 MADE REPAIRS RESTORED POWER AT 23:00 VER/SEF
24325 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-02-11 04:20 | 2011-02-11 05:20 | 1 | 60 | 56067-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER REPORTED TR NEEDS CHANGE // WILL RE-FUSE TR & HAVE CREW CHANGE AT REGULAR WORKTIME// 3RD FUSE IN TWO DAYS. SERVICE LOOKS OK - XFMR MUST BE GOING BAD. RE-FUSED @ 5:20 AND WILL HAVE CREW INSTALL NEW XFMR WHEN THEY START WORK. POWER IS ON - WILL LEAVE ON UNTIL CREW ARRIVES TO CHANGE. WILL BE APPROX 9 OR 10 AM. SH //VER/GAH IDC XXXX
24326 | Hazard | 3311103 | STINNETT | WENDOVER | 2013-11-20 16:30 | 2013-11-20 17:30 | 1 | 60 | 4059761 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACE 3 XFMRS POWER OFF @ 1630 AND RESTORED @ 1730//COD 2// VER/DBM
24327 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-06-15 23:30 | 2008-06-16 00:30 | 1 | 60 | 65335-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUIND ROTTEN AND BROKEN FUSE LINK, HAVE REPLACED AND POWER IS RESTORED TO THIS CUSTOMER L3/DKG
24328 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-07-07 19:20 | 2016-07-07 20:20 | 1 | 60 | 4559201 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE CUTOUT DOOR DIDNT DROP DOWN AND TRYED TO TRACK THROUGH DOOR BURNING DOOR REPLACED FUSE AND DOOR EVERYTHING OK VER/CRB
24329 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-06-22 13:00 | 2018-06-22 14:00 | 1 | 60 | 4644501 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout
24330 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2012-07-18 07:53 | 2012-07-18 08:53 | 1 | 60 | 4753601 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT..POLE 966A4-642.CAN REPLACE.//.REPLACED BROKEN CUTOUT.POWER ON..JRV..07/18/12 VER/KEP
24331 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-01-22 17:18 | 2020-01-22 18:18 | 1 | 60 | 4330211 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced secondary connections at weather head L3/HFP
24332 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-01-16 13:29 | 2017-01-16 14:29 | 1 | 60 | 4302741 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION VER/CRB L3/HFP XXXHFP
24333 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2013-07-07 12:25 | 2013-07-07 12:45 | 3 | 20 | H4478901 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S09 SERVICER FOUND LOOP OPEN NEAR RECLOSER ** OPENED RECL TO MAKE REPAIRS.RELEASED BY CREW 078S09 POLE 44-5521 LOOP BURNT OPEN REPAIRED OPEN REC. 12;25 ON 12;45//COD 56 + 3 // IDC XXXX
24334 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-06-07 18:20 | 2019-06-07 18:50 | 2 | 30 | 4447421 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changed bad cutout off @ 1820 on @ 1850
24335 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2013-09-24 11:10 | 2013-09-24 12:10 | 1 | 60 | 4882231 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-480 BAD CUTOUT DOOR HOT TAP LED BROKE OFF REPAIRED//COD 1// VER/DBM IDC XXXX
24336 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2012-04-21 11:45 | 2012-04-21 12:45 | 1 | 60 | 4692081 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 752-49. I WILL BE CHANGING OUT. I WILL KEEP UP WITH TIME TRANSFORMER IS OFF. I HAD TRANSFORMER OFF FROM 11: 45 TO 12:45. REPLACED CUTOUT EVERYTHING OK//COD 1// VER/DBM IDC XXXX
24337 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-09-02 12:25 | 2011-09-02 13:25 | 1 | 60 | 4785311 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED HOT LINE CLAMP//COD 1// VER/DBM IDC XXXX
24338 | Hazard | 3311103 | STINNETT | WENDOVER | 2017-09-19 14:00 | 2017-09-19 15:00 | 1 | 60 | 4372951 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER//OUTAGED CUSTOMER @ 1400, REPLACED TRANSFORMER AND RESTORED POWER AT 1500, PER JAMES GILLEY, LINE SERVICER//COD 1// VER/DBM L3/HFP XXXHFP
24339 | Hazard | 3310502 | HADDIX | CANOE | 2015-07-21 16:30 | 2015-07-21 17:30 | 1 | 60 | 4927321 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHECKING TRANSFORMER//REPLACE LEAKING TRANSFORMER //OPEN BANK AT 16;30 AND CLOSE AT 17;30.. VER/HFP L3/HFP
24340 | Pikeville | 3421002 | BREAKS | GRASSY | 2008-12-07 15:35 | 2008-12-07 16:35 | 1 | 60 | 55173-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3400902// REPLACED BAD CONNECTION AT THE POLE. VER/TOM L3/TOM IDC XXXX
24341 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-01-13 20:39 | 2020-01-13 21:39 | 1 | 60 | 4300771 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Txmf fuse had melted out. refused txmf apr at 2139 close ticket
24342 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-08-31 13:21 | 2017-08-31 13:51 | 2 | 30 | 4313341 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REPLACED D/E INS. AND CUTOUT 37830336000082 VER/AWD L3/HFP XXXHFP
24343 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-03-20 20:36 | 2013-03-20 21:36 | 1 | 60 | 4928771 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE IS BAD. I AM GOING TO FIX. I FIXED PROBLEM COD-1 ISO PO 37820073A00293 VER/HFP L3/HFP IDC XXXX
24344 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-08-21 11:30 | 2020-08-21 11:50 | 3 | 20 | 4354201 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfmr cutout on pole 747-38//i replaced cutout//restored at 11:50//complete//em
24345 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-03-30 11:30 | 2009-03-30 11:50 | 3 | 20 | 63036-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT CRACKED. OPENED XFMR ON POLE 834-70 AT 11:30. CHANGED CUTOUT AND ARRESTER AND CLOSED XFMR AT 11:50. SH//COD 3//ISO 38830834A00070// VER/DBM IDC XXXX
24346 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-09-27 13:25 | 2010-09-27 13:37 | 5 | 12 | 54081-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THERE IS NO OUTAGE, BUT CUST STATES THAT THE TOP OF THE POLE WAS MAKING NOISE AND FIRE WAS COMING OFF IT, WILL NEED TO CHANGE OUT CUTOUT,TIME OUT 13:25 TIME ON13:37//COD 5// VER/DBM IDC XXXX
24347 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-02-05 08:53 | 2015-02-05 09:53 | 1 | 60 | 4991961 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN THE SERVICE DROP/ REPAIRED SERVICE DROP/ ISO 38831083D30029/ COD 1RELEASED BY CREW 077S05/ VER/BOW L3/DKGXXXX
24348 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-01-05 08:57 | 2008-01-05 09:57 | 1 | 60 | 53974-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3116101/CALLED FOR CREW TO REPAIR SPLICE// VER/TOM IDC ALLOWED AN HOUR FOR REPAIR XXXX
24349 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2021-12-02 09:30 | 2021-12-02 10:30 | 1 | 60 | 4140581 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Matt Adams opened riser fuse 38820966A32769 (1 COD) to transfer underground to new pole///Off at 0930 -- On at 1030
24350 | Paintsville | 3401802 | INDEX | HOSPITAL | 2020-04-06 10:50 | 2020-04-06 11:10 | 3 | 20 | 4563561 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Changing xfmer due to low volage drop..opned @ 10:50 closed @11:10
24351 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-09-22 14:15 | 2008-09-22 14:35 | 3 | 20 | 66202-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3411802//TOTAL OF 3 CUSTOMER ON TRANSFORMER. OPEN AT 14:15 IDC XXXX
24352 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-01-08 12:45 | 2015-01-08 13:15 | 2 | 30 | 4918961 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER LEAKING CREW WILL MAKE REPAIRS/COD2/...OPENED AT 12:45 CLOSED AT 13:15// VER/ ADH L3/DKGXXXX
24353 | Pikeville | 3403001 | PIKEVILLE | CITY | 2008-04-06 16:54 | 2008-04-06 17:54 | 1 | 60 | 64686-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3403001//SERVICE DROP BURN INTI, REPLACE SERVICE DROP// VER/DBM IDC XXXX
24354 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-03-11 20:30 | 2015-03-11 21:30 | 1 | 60 | 4184421 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 19.9 DEAD END INSULATOR GOING BAD. CREW ON THE WAY. WILL KEEP UP WITH TIMES ONCE I OPEN TAP//19.9 DEAD END INSULATOR GOING BAD. CREW ON THE WAY. WILL KEEP UP WITH TIMES ONCE I OPEN TAP.ON POLE 38831100000125 CHANGED ARRESTER AND CUTOUT ALSO . POENED LINE UP AT2030 CLOSED LINE BACK IN AT 21:30 VER/CRB
24355 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2011-06-19 20:20 | 2011-06-19 21:20 | 1 | 60 | 4346421 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK... CC= 1
24356 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2018-02-05 12:18 | 2018-02-05 12:33 | 4 | 15 | 4806661 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse had broke. Replaced the fuse and power is restored.
24357 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-12-09 14:00 | 2012-12-09 14:15 | 4 | 15 | H4454081 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 4454081//BAD CUTOUT.CHANGING.HAD LINE FUSE OFF FRON 14.00 UNTIL 14.15//COD 4// VER/DBM IDC XXXX
24358 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-05-25 08:45 | 2011-05-25 09:15 | 2 | 30 | 4164991 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER OPENED TRANSFORMER AT 0845 CLOSED TRANSFORMER AT 0915//COD 2// VER/DBM
24359 | Hazard | 3308001 | JACKSON | S.JACKSON | 2016-05-06 12:50 | 2016-05-06 13:02 | 5 | 12 | 4180781 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT,NEED LINE CREW ,BIG BUCKET,FLAGGERS,72KV CUTOUT.//OPENED AT 1250 // CLOSED 1302 // COD 5// VER/DBM
24360 | Hazard | 3309002 | JEFF | JEFF | 2019-12-23 18:12 | 2019-12-23 19:12 | 1 | 60 | 4178951 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at transformer
24361 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-08-03 16:25 | 2014-08-03 17:25 | 1 | 60 | 4327931 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-821 BAD CUTOUT AND LA REPLACED VER/CRB
24362 | Hazard | 3307301 | BULAN | ARY-HEINE | 2022-05-18 11:39 | 2022-05-18 11:51 | 5 | 12 | 4906161 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | had bad connection on transformer open trans at 1139 and closed at 1151
24363 | South Williamson | 3200302 | BELFRY | TOLER | 2010-12-12 15:21 | 2010-12-12 15:51 | 2 | 30 | H65602-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV SHORTED OUT MIDSPAN,MADE REPAIRS,ALL OK AFTERWARDS.ALSO HAD XFR OPEN FRM ABT 15:21 TO 15:51 COD-3 ISO TF 38821063A00095 DUPLICATE IN HOIS THIS IS THE DUPLICATE FOR ORDER 65602-1 VER/HFP L3/HFP IDC XXXX
24364 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2014-10-07 16:38 | 2014-10-07 17:38 | 1 | 60 | 4566401 | 60 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE SEND TO TEC SEC. TO SMALL NEEDS 1/0 INSTALLED POLE LEANING BAD NEEDS ANCHOR INSTALLED VER/HFP L3/HFP
24365 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2021-04-22 13:30 | 2021-04-22 14:00 | 2 | 30 | 4471331 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 bolt connection heating up on customers URD service causing his lights to flicker, had to open transformer @25-D-132 to resqueeze. Opened @1330, closed back in @1400.
24366 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-03-14 12:55 | 2011-03-14 13:25 | 2 | 30 | 54154-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLOWN AND HANGING CLOSE TO XFMR CASE. OPENED TRANS @ 1255 // CLEARED OLD ARRESTER AND ENERGIZED XFMR @ 13:25. SH //ISO // COD 2// VER/DBM IDC XXXX
24367 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-02-14 12:49 | 2015-02-14 13:49 | 1 | 60 | 4015221 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT/COD1// VER/ ADH L3/HFP XXX
24368 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-03-09 17:39 | 2016-03-09 18:39 | 1 | 60 | 4831781 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR LEAKING OIL, WILL NEED TO REPLACE, CONTACTED J. COMBS CREW. OPENED XFMR AT 17:39, CLOSED BACK AT 18:39, POWER RESTORED/// VER/ ADH
24369 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-08-27 15:00 | 2013-08-27 16:00 | 1 | 60 | 4711891 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ,, CHANGING ALL 3 ,OPENED LIN AT 15 00 CLOSED BACK AT 16 00 VER/CRB L/3 CRB IDC XXXX
24370 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-06-22 10:15 | 2020-06-22 11:15 | 1 | 60 | 4058571 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transfuse outon1138-C-129.fuse failed.restoredpower a 11;15.
24371 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-10-28 19:30 | 2011-10-28 20:30 | 1 | 60 | 4031541 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 90-372 6T FUSE BROKE IDC XXXX
24372 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-09-10 11:20 | 2019-09-10 11:35 | 4 | 15 | 4999271 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | KYDDC TAGS DOL 953062 / T LEWIScrew required with manual tree crew tagged 223-20 to ddc/no groundscrew required with manual tree crew tagged 223-20 to ddc/no grounds Released by crew 078S03 OFF 1120 ON 1135
24373 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-08-28 09:29 | 2014-08-28 09:59 | 2 | 30 | 4432221 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHGED
24374 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-01-09 15:10 | 2015-01-09 15:30 | 3 | 20 | 4923641 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED NEED 25 KVA WITH RISERS TRUCKS OK /SEND TO BRENT TACKETT RELEASED BY CREW 078S03,,CREW ON SITE,XFMR UPGRADED,,OPENED AT 15:10,,CLOSED AT 15:30 RELEASED BY CREW 078H03/ ISO 38830245D00203/ COD 3 VER/CRB L3/DKGXXXX
24375 | South Williamson | 3200302 | BELFRY | TOLER | 2020-05-14 12:58 | 2020-05-14 13:58 | 1 | 60 | 4835441 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva transfomer
24376 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-10-10 13:05 | 2018-10-10 14:05 | 1 | 60 | 4215581 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Isolated blown tank-mounted arrester. Restored @ 14:05. sh L3/HFP
24377 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-12-17 13:05 | 2015-12-17 13:15 | 6 | 10 | 4539821 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT. I OPENED THE TRANSFORMER AT 13:05, AND CLOSED BACK IN AT 13:15. COD-6 ISO TF 37820032C00002 VER/HFP L3/HFP
24378 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2012-09-25 19:30 | 2012-09-25 20:30 | 1 | 60 | 4087251 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS FAILED ON POLE 38821040C00021 ISOLATED TAP TO CHANGE CUTOUT @ 19:30 POWER RESTORED @ 20:30//COD 1// VER/DBM IDC XXXX
24379 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-11-04 20:20 | 2015-11-04 20:50 | 2 | 30 | H4410011 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 075H04///BROKE CUTOUT ,NEED 72KV CUT OUT AND BRACKET,MANUAL.20:20 AND CLOSE AT20:50// VER/ ADH // DUP OF 4410011 FOR 2 CUST = L3/HFP HFPC CNT7 PN37830180000060
24380 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-07-06 22:25 | 2008-07-06 23:25 | 1 | 60 | 63495-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE DOOR STUCK SHUT AND TRACKED OVER, CHANGED CUTOUT DOOR VER/ARN IDC XXXX
24381 | South Williamson | 3411401 | DEWEY | INEZ | 2014-11-09 12:25 | 2014-11-09 13:25 | 1 | 60 | 4714971 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKNG NOW.FUSE BROKE ,, BACK TO NORMAL// ISO 38830768D20441// COD 1/ VER/BOW
24382 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-07-14 10:15 | 2016-07-14 11:15 | 1 | 60 | 4628911 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 140-432 BAD CUTOUT DOOR 6T TRANS FUSE/ ISO 38830140D00432/ COD 1/ VER/BOW
24383 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-11-02 10:39 | 2009-11-02 11:09 | 2 | 30 | 55320-1 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 32490225 // POLE 45-2257 10T TRANS FUSE BAD CUTOUT DOOR REPLACED COD-2 ISO TF 38830045002257 L3/HFP IDC XXXX
24384 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2018-11-10 14:32 | 2018-11-10 14:47 | 4 | 15 | 4386881 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out door burning will replace cutout. will have power off aprox 15 min. pulled off @14:32 on @ 14:47 L3/HFP
24385 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-02-15 16:48 | 2019-02-15 17:18 | 2 | 30 | 4797941 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 37830005B20199//COD 2 PER SERVICER// opened xfmr @16:48///closed @17:18//NO OUTAGE TILL TRANSFORMER OPENED//MADE MD//SENT TO TECH TO TRY AND MAP//
24386 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-07-13 18:00 | 2012-07-13 18:30 | 2 | 30 | 4717441 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER BOB SHURTLEFF: SMOKING XFMR AT LOWER BOWL`S ADDITION IN PIKEVILLE ON HICKORY LANE // PER BOB SHURTLEFF: SMOKING XFMR AT LOWER BOWLS ADDITION IN PIKEVILLE ON HICKORY LANE //BRKN DOWN CUTOUT AT 23-83,ISOLATED,CHANGED CUTOUT,RESTORED AT 18:30///////SEND TO TECH,POLE BURNED NEARLY INTO IDC XXXX
24387 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2016-04-18 13:15 | 2016-04-18 14:15 | 1 | 60 | 4099311 | 60 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THE NEUTRAL CONNECTION WAS BAD AT THE TRANSFORMER. I OPENED THE TRANSFORMER AT 13:15 TO REWORK ALL THE CONNECTIONS. POWER RESTORED AT 14:15. VER/CRB
24388 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2016-06-02 13:47 | 2016-06-02 14:46 | 1 | 59 | 4285631 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | METER BURNT UP CHGED METER/ ISO 38830092A00037/ COD 1/ VER/BOW
24389 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-03-22 14:05 | 2010-03-22 15:04 | 1 | 59 | 52856-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, CHECKING TROUBLE VER/HFP L3/HFP IDC XXXX
24390 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2016-04-15 16:01 | 2016-04-15 17:00 | 1 | 59 | 4094681 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEW CONNECTION @ WEATHERHEAD VER/CRB
24391 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-02-24 14:11 | 2010-02-24 15:10 | 1 | 59 | 60618-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD AMP OR SURGE ARRESTER. SEND COPY OF THIS TO PERRY FARMER PIKEVILLE WE HAVE HAD SOME TROUBLE OUT OF THIS EQUIPMENT. MADE REPAIRS EVERYTHING OK.//VER/CRB IDC XXXX
24392 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-02-27 08:31 | 2015-02-27 09:30 | 1 | 59 | 4085051 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER, BAD CONNECTION AT XFMR FROZE OUT, RESTORED POWER AT 09:30, ONLY ONE CUSTOMER AFFECTED.CUSTOMER IS OFF XFMR POLE 37830353A00076.//PART POWER, BAD CONNECTION AT XFMR FROZE OUT, RESTORED POWER AT 09:30, ONLY ONE CUSTOMER AFFECTED.CUSTOMER IS OFF XFMR POLE 353-76. VER/CRB
24393 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-11-28 21:36 | 2010-11-28 22:35 | 1 | 59 | 60364-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T TRANS, FUSE BROKE VER/PDP IDC XXXX
24394 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2020-12-20 16:26 | 2020-12-20 17:25 | 1 | 59 | 4789151 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neut broke into. repairs made. pls close. tre
24395 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-05-05 09:04 | 2015-05-05 10:03 | 1 | 59 | 4391291 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD. POWER RESTORED.// VER/ ADH
24396 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-11-22 11:01 | 2022-11-22 12:00 | 1 | 59 | 4172661 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad connection replaced connector
24397 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-05-07 03:51 | 2009-05-07 04:50 | 1 | 59 | 62172-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3117601 - BROKEN FUSE LINK //VER/GAH IDC XXXX
24398 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-06-01 22:21 | 2010-06-01 23:20 | 1 | 59 | 55126-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING CUTOUT DOOR//COD 1// VER/DBM IDCC FEC49 XXXX
24399 | Hazard | 3303902 | LESLIE | WOOTON | 2018-03-13 18:54 | 2018-03-13 19:53 | 1 | 59 | 4012861 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION
24400 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2014-03-19 12:27 | 2014-03-19 13:26 | 1 | 59 | 4509771 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED SERVE END BAD IN SERVICE . ONLY 1 CUST. WITH PART POWER.///COD 1// VER/DBM
24401 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-05-26 11:06 | 2020-05-26 12:05 | 1 | 59 | 4908701 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout, transformer fuse back in @ 12:05
24402 | Hazard | 3303902 | LESLIE | WOOTON | 2009-01-08 12:28 | 2009-01-08 13:27 | 1 | 59 | 53368-1 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3303902//REPLACED BAD CONNECTION ON 1 HOT LEG// VER/TOM L3/TOM IDC XXXX
24403 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-02-25 07:31 | 2013-02-25 08:30 | 1 | 59 | 4843641 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED CURRENT LIMMITING FUSE APR AT 0830 CLOSE TICKET DWEST//COD 1// VER/DBM IDC XXXX
24404 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2012-07-30 18:56 | 2012-07-30 19:55 | 1 | 59 | 4867661 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE , RESTORED POWER AT 19:55 COD-1 ISO TF 37830376A00331 VER/HFP L3/HFP
24405 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-22 22:16 | 2011-01-22 23:15 | 1 | 59 | 63677-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMIT FUSE BURNT INTO. I WILL BE MAKING REPAIRS. I HAVE REPAIRS MADE EVERYTHING OK SEND COPY OF THIS TO BOB SHURTLEFF PIKEVILLE AND TOM MAMINGVER/PDP IDC XXXX
24406 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2017-10-06 07:52 | 2017-10-06 08:51 | 1 | 59 | 4414291 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNDT STIRRUP INTO @48-C2-1520, CHANGED OUT CLAMP AND STIRRUP AND CLOSED BACK IN @0851. COD-1 ISO PO @ 37830048C21520 VER/HFP L3/HFP
24407 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-10-22 11:56 | 2014-10-22 12:55 | 1 | 59 | 4652521 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENING TRANSFORMER 37830272B21275/ BAD NEUTRAL CONNECTION AT TRANSFORMER..POWER RESTORED/ ISO 37830272B21275// COD 1// MAP DISCREPANCY DONE FOR CUSTOMERS PREMISE// VER/BOW
24408 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-12-14 10:49 | 2008-12-14 11:48 | 1 | 59 | 58180-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP 3202201// SERV NEUTRAL BROKE ON POLE746-201. CUST MAY HAVE DAMAGE VER/KEP L3/KEP IDC XXXX
24409 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-02-01 09:01 | 2015-02-01 10:00 | 1 | 59 | 4978461 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAD BAD SERVE ENDS ON MAST, REMOVED ALL SERVE ENDS AND RESQUEEZED, FULL POWER IS RESTORED AT THIS LOC AT 1000/ ISO 39831122C00181/ COD 1/ VER/BOW L3/HFP XXX
24410 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-07-17 19:16 | 2019-07-17 20:15 | 1 | 59 | 4724631 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer restored
24411 | Hazard | 3309301 | VICCO | REDFOX | 2008-08-28 19:52 | 2008-08-28 20:51 | 1 | 59 | 57142-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT BROKEN FUSE TAIL//3309301//VER/CRB IDC XXXX
24412 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-03-11 16:22 | 2019-03-11 17:21 | 1 | 59 | 4972281 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replacing broken cutout. All repaires made. apr at 1721 close ticket. dwest
24413 | South Williamson | 3411401 | DEWEY | INEZ | 2016-02-29 07:28 | 2016-02-29 08:27 | 1 | 59 | 4785951 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 38830767A00155/ CHJANGED AND RESTORED @ 0827/ ISO 38830767A00155/ COD 1CUTOUT BROKE ON POLE 767-155//REPAIRS MADE//RESTORED AT 8:27//COMPLETE//EM/ VER/BOW
24414 | South Williamson | 3411401 | DEWEY | INEZ | 2010-01-21 15:26 | 2010-01-21 16:25 | 1 | 59 | 57366-1 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN ON SERV POLE VER/HFP L3/HFP IDC XXXX
24415 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-06-08 11:28 | 2022-06-08 12:27 | 1 | 59 | 4037801 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | fixed neutral splice in service
24416 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-09-05 10:32 | 2014-09-05 11:31 | 1 | 59 | 4467961 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RESQUEEZE CONNECTION// ONE HOT LEG LOOSE/// COD 1 CCC*****// ISO 38830115C00497// VER/BOW
24417 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2012-08-01 21:04 | 2012-08-01 22:03 | 1 | 59 | 4881671 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN . REFUSED TRANSFORMER , ALL WORK COMPLETE / GXJ IDC XXXX
24418 | Hazard | 3309302 | VICCO | JEFF | 2013-06-26 16:30 | 2013-06-26 17:29 | 1 | 59 | 4404381 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE IN SERV HEATED UP AND BURNEDE NEUT INTO IN SERV === REPLACED SERV WITH NEW ONE === CUST HAS DAMAGES CUST TO CALL IN === POWER OK VER/SEF IDCC TOF1552 ESTIMTED TIME OFF FOR REPAIR XXXX
24419 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-08-13 15:55 | 2010-08-13 16:54 | 1 | 59 | 54360-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP CHANGING NOW CHANGED DOOR BACK TO NORMAL COD-1 VER/HFP L3/HFP
24420 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-08-30 14:36 | 2013-08-30 15:35 | 1 | 59 | 4802291 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE, FUSE HAD NOT BLOWN VER/CRB L/3 CRB IDC XXXX
24421 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-02-23 15:36 | 2016-02-23 16:35 | 1 | 59 | 4751961 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PARTIAL POWER ON 3 PHASE SD NOT BEING USED AT THIS TIME, WILL REPAIR AT LATER DATE / GXJ .... OPS ORDER # 034105778 CREATED FOR FUTURE WORK/// METER IS ACTIVE BUT NOT IN USE// WILL NEED HELP FIXING THIS SCHEDULED FOR LATER IN THE WEEK/ ISO 38831122C10823/ COD 1/ VER/BOW
24422 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-12-05 11:12 | 2018-12-05 12:11 | 1 | 59 | 4509691 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 37830024D10759 // CREW TO REPLACE AFTER CB PLACED IN NRO //
24423 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2016-01-12 11:00 | 2016-01-12 11:59 | 1 | 59 | 4609501 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PARTOUT B PHASE HOTTAP LEAD HAS PULLEN OUT OF HOTTAP, LINECREW IN ROUTE, OPENED OTHER TWO PHASES AT 1147 AND MADE REPAIRES APR AT 1159 CLOSE TICKET/./ VER/ ADH
24424 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-08-24 14:06 | 2010-08-24 15:05 | 1 | 59 | 60019-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP L3/HFP IDCC FPNULL XXXX
24425 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2008-10-18 15:40 | 2008-10-18 16:39 | 1 | 59 | 56856-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3417601// BOB ADVISED NEUTRAL BROKE IN SERVICE DROP// THIS DROP IS APPROX 130`// CUSTOMER ADVISES HE HAS DAMAGE - MENTIONED TV// OPENED UP @ 1540 TO MAKE SERVICE REPAIR AND CLOSED IN @ 1639// SENT TO PEGGY VER/TOM IDC XXXX
24426 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-11-07 14:41 | 2018-11-07 15:40 | 1 | 59 | 4377401 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no cre wrequired broken fuse link L3/HFP
24427 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-04-25 18:16 | 2010-04-25 19:15 | 1 | 59 | 51024-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING CUTOUT AND REPAIRING #4 COPPER PRIMARY COD=1 VER/HFP L3/HFP IDC XXXX
24428 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2019-05-13 09:46 | 2019-05-13 10:45 | 1 | 59 | 4262351 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | connection burnt open on xfmr// all repairs made power restored at 10:45
24429 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-01-21 15:56 | 2016-01-21 16:55 | 1 | 59 | 4639101 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FUSE DOOR BURNT UP. REPLACED AND RESTORED @ 16:55. SH// VER/ ADH
24430 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2018-07-23 13:05 | 2018-07-23 14:04 | 1 | 59 | 4841321 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON POLE 38820868D00160 BAD//NEED BIG BUCKET & CUTOUT & ARRESTOR & STANDOFF BRACKETT - 12KVReplaced bad cutout. I opened the transformer at 13:05. and closed back in at 14:04. Send to Cliff Freeman to have the pole replaced.
24431 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-03-10 15:26 | 2009-03-10 16:25 | 1 | 59 | 57006-1 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | THIS WAS FOR COMPRESSOR STATION FOR CLEAN GAS INC. AND WAS ON XFMR POLE 37830177C00547 HOT LINE CLAMP BROKE AND WAS PART OUT// VER/TOM L3/TOM IDC XXXX
24432 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2018-07-14 12:31 | 2018-07-14 13:30 | 1 | 59 | 4772641 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Ban connection on one of the hot legs at txmf, all repaires made close ticket
24433 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-10-06 11:36 | 2010-10-06 12:35 | 1 | 59 | 57373-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE PULLED APART ON OH SERVICE DROP, REPLCED SERVICE DROP.// VER/DBM IDC XXXX
24434 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-11-08 16:16 | 2008-11-08 17:15 | 1 | 59 | 63322-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 340900288XFMR FUSE BLOWN. WILL TRY TO RE-FUSE. XFMR IS BAD. DIFFICULT LOCATION - CUSTOMER NOT LIVING IN HOUSE YET AND SAID IT WOULD BE NO PROBLEM TO WAIT UNTIL MONDAY MORNING TO REPLACE XFMR. SH RELEASED BY CREW 076S02 - SENT TO ROGER MAYNARD// VER/TOM IDC XXXX
24435 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-12-29 02:49 | 2013-12-29 03:48 | 1 | 59 | 4208091 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK //VER/GAH
24436 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-12-31 09:46 | 2018-12-31 10:45 | 1 | 59 | 4615171 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10t restored 118-97 @ 10:45
24437 | Hazard | 3302704 | HAZARD | KENMONT | 2011-04-15 08:16 | 2011-04-15 09:15 | 1 | 59 | 56834-1 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 39583704 // BAD CUTOUT ON POLE 37830321A00005 == CHANGED CUTOUT == POWER OK COD-1 ISO TF 37830321A00005 VER/HFP L3/HFP IDC XXXX
24438 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-09-03 08:41 | 2014-09-03 09:40 | 1 | 59 | 4456601 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T RESTORED BAD DOOR// COD 1//VER/ ADH VER/DKG L3/DKG
24439 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-09-01 13:55 | 2020-09-01 14:54 | 1 | 59 | 4414391 | 59 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required
24440 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-11-24 10:01 | 2019-11-24 11:00 | 1 | 59 | 4063441 | 59 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVE-IN PULLED APART,WILL REPAIR//////////MADE NECESSARY REPAIRS&RESTORED SERVICE,ALL OK AFTERWARDS
24441 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-04-27 08:52 | 2015-04-27 09:50 | 1 | 58 | 4368631 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE LINK BROKE. RESTORED @ 9:50. SH VER/CRB
24442 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2018-08-14 12:43 | 2018-08-14 13:12 | 2 | 29 | 4952631 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | will pull water pump off to replace connector at xfmr riser to service drop that is burning./ opened 1243 closed 1313/ ISO 38831052A00406/ COD 2will pull water pump off to replace connector at xfmr riser to service drop that is burning.pulled off @ 12:43 back on @ 13:12
24443 | Paintsville | 3401802 | INDEX | HOSPITAL | 2020-06-18 14:55 | 2020-06-18 15:53 | 1 | 58 | 4042611 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad splice in service drop.. replaced.. XFM on 654-56 off at 14:55 back on at 15:53////Found A phase Reg at pole 654-B-445 at 131.6V and 10R, hsd Todd step down to 125.7V at 2R and leave ctrl sw in off/man pos and tagged ---voltage at this transformer is now 124 phase-grnd & 246 phase-phase
24444 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-03-15 12:12 | 2020-03-15 13:10 | 1 | 58 | 4479861 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replace door
24445 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-08-08 14:02 | 2011-08-08 15:00 | 1 | 58 | 4680031 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT // COD 1// VER/DBM IDCC PN9 XXXX
24446 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-10-20 13:40 | 2015-10-20 14:09 | 2 | 29 | 4364021 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XFR @ 13:40 BACK IN @ 14:09 COMPLETE// VER/ ADH
24447 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-03-02 10:17 | 2022-03-02 11:15 | 1 | 58 | 4559271 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have a Broke Neutral at secondary pole 214-B-373,Going to pull Meter and Make repairs..Pulled Meter at 10:17 made repairs restored @ 11:15.
24448 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-07-04 13:52 | 2011-07-04 14:50 | 1 | 58 | 4454561 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT UP AT SECONDARY ON POLE 206-2180,, CORRECT XFMR IS 38830206C04020, CLIMBED POLE AND MADE REPAIRS, ALL POWER RESTORED COD-1 ISO SO VER/HFP L3/HFP IDC XXXX
24449 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-01-25 10:43 | 2008-01-25 11:12 | 2 | 29 | 59811-1 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 KVA CSP XFMR KICKED OUT UNDER LOAD//3401103//VER/CRB IDC XXXX
24450 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-05-13 22:14 | 2017-05-13 22:43 | 2 | 29 | 4796751 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN LINE FUSE TO SAFELY REPLACE CUTOUTS//TOM OPENED 2100 CLOSED @ 2220 - 9 COD //
24451 | Pikeville | 3421001 | BREAKS | CITY | 2021-04-22 10:27 | 2021-04-22 11:25 | 1 | 58 | 4470901 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Meter was burnt up///Replaced meter and restored service @ 11:25
24452 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-01-06 09:03 | 2009-01-06 09:32 | 2 | 29 | 51832-1 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003//PER KEN RIGSBY (LID 3821), THERE IS A BROKEN CROSSARM HERE WITH PRIMARY ONLY ABOUT 1 INCH FROM CUSTOMERS SERVICE DROP//NO OUTAGE AT THIS TIME//3001003// PULLED METERS ON HOUSES, STATION IS ON NON RECLOSE, // HITCHENS/GRAYSON 12KV CKT IS ON NON RECLOSE, ROB COMPHER WITH DHE WILL BE WORKING JOB, BAD CUTOUT BURNT CROSSARM, ONLY ABOUT 1 IN FROM OPEN WIRE SEC. ** PLEASE HAVE ROB CONTACT SW DISP. FOR HOLD ORDE VER/KEP L3/KEP IDC XXXX
24453 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2017-05-27 20:28 | 2017-05-27 21:26 | 1 | 58 | 4873431 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY LEAD BURNT INTO AT XFMR ON POLE 449-207, MADE REPAIRS RESTORED POWER AT 21:26../ ISO 37830449A20207/ COD 1/ VER/BOW
24454 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2008-01-07 10:42 | 2008-01-07 11:40 | 1 | 58 | 54328-1 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3000105// HAD TO OPEN TRANSFORMER ON POLE 45-4004 FOR APX 5 MIN TO MAKE REPAIRS//VER/CRB IDC XXXX
24455 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-10-03 13:32 | 2014-10-03 14:30 | 1 | 58 | 4547891 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SLEEVE PULLED APART MID SPAN REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/CRB VER/DKG L3/DKGXXXX
24456 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-03-09 18:51 | 2010-03-09 19:49 | 1 | 58 | 64462-1 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED/REPLACED CUTOUT// COD 1// VER/DBM IDC XXXX
24457 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-11-27 13:32 | 2013-11-27 14:30 | 1 | 58 | 4082631 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NUETRAL BROKE IN SERVICE DROP. MADE REPAIRS AND BACK TO NORMAL AT 14:30 COMPLETE RN VER/CRB
24458 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2020-10-28 12:17 | 2020-10-28 13:15 | 1 | 58 | 4592261 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crrew required replaced fuse door
24459 | Pikeville | 3413402 | GARRETT | LACKEY | 2011-11-19 15:48 | 2011-11-19 16:46 | 1 | 58 | 4093411 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN, REPLACED FUSE . ALL WORK COMPLETE / GXJ /// VER/CRB IDC XXXX
24460 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-07-17 10:39 | 2009-07-17 11:37 | 1 | 58 | 53642-1 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER VER/KEP L3/KEP IDC XXXX
24461 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-10-24 10:28 | 2011-10-24 11:26 | 1 | 58 | 4014421 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY BURNT IN TWO NO CREW REQUIRED AT THIS TIME NEED TO SEND TO TECH TO HAVE SECONDARY UPGRADED//VER/CRB IDC XXXX
24462 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-18 06:12 | 2019-06-18 07:10 | 1 | 58 | 4533791 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt up on weather head// i repaired connections//restored to norma at 7:10//complete//em
24463 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-06-05 10:02 | 2009-06-05 11:00 | 1 | 58 | 63992-1 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION AT ENTRANCE CABLE//VER/CRB IDC XXXX
24464 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-01-18 07:27 | 2011-01-18 08:25 | 1 | 58 | 62083-1 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION AT SERVICE POLE BAD AND CAUSED SERVICED NEUTRAL TO BURN IN HALF, REPAIRS MADE, SERVICE RESAGGED, ONLY 1 CUSTOMER OUT VER/HFP L3/HFP IDC XXXX
24465 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-07-13 13:37 | 2009-07-13 14:35 | 1 | 58 | 51142-1 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3002002// BAD CONNECTION ON THE WEATHER HEAD, HAVE REPAIRS MADE AND EVERYTHING SHOULD BE OK AT THIS LOC //VER/GAH IDC XXXX
24466 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-11-24 13:07 | 2010-11-24 14:05 | 1 | 58 | 59345-1 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 37882209 // REPLACED SQUEEZE ON M.D.I. COD-1 VER/HFP L3/HFP IDC XXXX
24467 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2018-01-26 12:11 | 2018-01-26 13:09 | 1 | 58 | 4775281 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replaced xfmr fuse. Everett Young is to write job to replace xfmr./ ISO 38831027D00335/ COD 1
24468 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-10-26 13:22 | 2013-10-26 14:20 | 1 | 58 | 4965651 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVICE DROP BURNED INTO AT A SPLICE. I AM GOING TO REPAIR DROP. VER/HFP L3/HFP
24469 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-02-13 00:12 | 2018-02-13 01:10 | 1 | 58 | 4836111 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE BURNT OPEN IN SERVICE DROP/// REPAIRED CONNECTIONS AND RESTORED SERVICE 124/124/248/// ONLY 1 CUSTOMER AFFECTED
24470 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-02-09 10:27 | 2008-02-09 11:25 | 1 | 58 | 52891-1 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3000902// BAD N. 4 CON. ON HOUSE// VER/DBM IDC XXXX
24471 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-02-25 09:37 | 2012-02-25 10:35 | 1 | 58 | 4503231 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN SERVICE HAS HEATED UP AND BURNT OPEN. REPLACED SERVICE WIRE AND ALL CONNECTIONS. RESTORED @ 10:35. SH VER/HFP L3/HFP IDCC MCCDL XXXX
24472 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-01-11 17:32 | 2011-01-11 18:30 | 1 | 58 | 60716-1 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CONNECTION AT CURNET LIMET FUSE-REPLACED FUSE COD-1 ISO TF 38830140B02026 VER/HFP L3/HFP IDC XXXX
24473 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-03-27 15:17 | 2018-03-27 16:15 | 1 | 58 | 4130841 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no reading on the meter--c/o broke replaced 38830283000090--allgood-ds032718/ ISO 38830283000090/ COD 1
24474 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-06-05 11:02 | 2011-06-05 12:00 | 1 | 58 | 4236281 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT CHANGE//VER/CRB IDC XXXX
24475 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-02-25 08:07 | 2022-02-25 09:05 | 1 | 58 | 4544281 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced and restored @ 9:05. sh
24476 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-08-12 15:58 | 2018-08-12 16:56 | 1 | 58 | 4944001 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout complete
24477 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-08-08 12:47 | 2016-08-08 13:45 | 1 | 58 | 4749531 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..CHGING VER/AWD
24478 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2009-03-14 21:34 | 2009-03-14 22:03 | 2 | 29 | 58644-1 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3002105 // OPENED TRANSFORMER TO REPLACE CUTOUT // COD-2 VER/LDA IDC XXXX
24479 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2018-06-22 16:02 | 2018-06-22 17:00 | 1 | 58 | 4646291 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout, only fed a tv power supply
24480 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-05-31 19:32 | 2021-05-31 20:30 | 1 | 58 | 4652741 | 58 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS/////SERVE-IN PULLED APART@XFR,ONLY HAD PARTIAL POWER.MADE NECESSARY REPAIRS.ALL OK AFTERWARDS/ ISO 37820002000147/ COD 1
24481 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-04-08 14:08 | 2013-04-08 15:06 | 1 | 58 | 4988521 | 58 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON NEUTRAL WIRE I HAVE REPAIRS MADE EVERYTHING OK.// VER/DBM IDC XXXX
24482 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-01-05 18:04 | 2010-01-05 19:01 | 1 | 57 | 62207-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | REPLACED BAD METER AND EVERYTHING WAS FINEVER/TOM IDC XXXX
24483 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-05-15 17:20 | 2010-05-15 17:39 | 3 | 19 | 62761-1 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ARRIVED ON SIGHT , CHECKED VOLTAGE AND 106 ON ONE LEG AND 146 ON OTHER AT TOP OF BASE CHECKING CONNECTIONS . BAD CONNECTIONS ON SECONDARY POLE , MADE CONECTIONS AND CHECKED POWER JKC//COD 3// VER/DBM IDCC TOF1452, ESTIMAQTED TIME OFF XXXX
24484 | Hazard | 3302703 | HAZARD | HAZARD | 2012-07-17 08:28 | 2012-07-17 09:25 | 1 | 57 | 4745901 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD. VER/HFP L3/HFP
24485 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-12-28 11:09 | 2018-12-28 11:28 | 3 | 19 | 4602931 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Talked to customer and he said it was ok to check in the morning // no outage at this time bad cutout on pole 181-81replaced cutout opened at 11:09 to 11:28 L3/HFP
24486 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2019-07-12 17:00 | 2019-07-12 17:57 | 1 | 57 | 4703031 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced service connections at weather head,,,,complete
24487 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-05-26 20:23 | 2008-05-26 21:20 | 1 | 57 | 51491-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003// CUTOUT DOOR CAUGHT FIRE AND BURNT LEAVES AROUND POLE, REPLACED CUTOUT. VER/ARN IDC XXXX
24488 | Whitesburg | 3314401 | MAYKING | ERMINE | 2010-06-23 14:13 | 2010-06-23 15:10 | 1 | 57 | 55861-1 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON HOUSE REPAIRED CONNECTION IDCC PN92, CNT10, CDC92 XXXX
24489 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-03-10 20:06 | 2011-03-10 21:03 | 1 | 57 | H53075-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PART OF 53075-1//WILL HAVE TO REPLACE 10 KVA CSP TRANSFORMER 7200. LIFT HOT TAP ON POLE 1150-171 AND OPEN SERVICE 1150-301/302 AT 20:06//COD 1// VER/DBM IDC XXXX
24490 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-05-10 16:03 | 2017-05-10 17:00 | 1 | 57 | 4777571 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE ON 1107121 FAILED DUE TO AGE RE-FUSED CUTOUT RESTORED POWER AT 17:00/ ISO 38821107000121/ COD 1/ VER/BOW
24491 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2019-10-13 09:22 | 2019-10-13 10:19 | 1 | 57 | 4135991 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout door ,,,complete
24492 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-12-21 08:12 | 2015-12-21 09:09 | 1 | 57 | 4547491 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE // WILL CHANGE// POWER RESTORED @ 09:09// VER/ ADH
24493 | Hazard | 3420001 | SOFT SHELL | VEST | 2019-01-10 12:25 | 2019-01-10 13:22 | 1 | 57 | 4656291 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, replaced
24494 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-03-11 10:43 | 2013-03-11 11:40 | 1 | 57 | 4897041 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD//BAD CONNECTION AT WEATHERHEAD.BAD CONNECTION AT WEATHERHEAD. ---- POWER RESTORED. - ONLY 1 CUST. WITH PART POWER. ///VER/CRB L/3 CRB IDC XXXX
24495 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-02-19 02:33 | 2020-02-19 03:30 | 1 | 57 | 4417081 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced xfr connectons,,,complete/ ISO 38830326000033/ COD 1 L3/HFP
24496 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-09-27 13:09 | 2019-09-27 14:06 | 1 | 57 | 4064491 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | splice in service neutral wire pulled out, made repairs restored power at 14:06, customer stated that when crew made repairs earlier today stove lights were flashing & want work now, said she was going to call a claim in on it..//SENT TO CLAIMS
24497 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-04-08 09:48 | 2011-04-08 10:45 | 1 | 57 | 51527-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39486129 // XFR MUST HAVE JUST STARTED LEAKING,SOME DOWN TANK FRM BUSHING,VERY LITTLE IF ANY ON THE GRND THOUGH.IS A 15,NEED TO REPLACE W A 25.WILL HAVE TO BLOCK/WINCH.SEND TO TIM HALL,LAST HSE IN HOLLOW,LOTS OF DOGS AROUND -- SENT EMAIL TO TIMM & DENNIS ABOUT THIS.CANT CHANGE FETR 12:15 SHOULD BE OK. WE TOOK XFMR OFF AT 09:48 BACK ON AT 10:45.//COD 1// VER/DBM IDC XXXX
24498 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-10-09 09:48 | 2022-10-09 10:45 | 1 | 57 | 4008631 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crw required
24499 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2017-04-10 15:48 | 2017-04-10 16:45 | 1 | 57 | 4635121 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED 2 CONNECTIONS ON SD// VER/CRB L3/HFP XXXHFP
24500 | Pikeville | 3407101 | TOPMOST | DEMA | 2009-10-09 20:52 | 2009-10-09 21:49 | 1 | 57 | H52671-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING BAD CUTOUT AND HOT LINE CLAMP. I HAVE CUTOUT AND HOTLINE CLAMP CHANGED EVERYTHING OK. VER/KEP L3/KEP IDC XXXX
24501 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-12-27 11:33 | 2013-12-27 12:30 | 1 | 57 | 4204841 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED XFORMER RISER, BURNT INTO. OPENED XFORMER AT 12:00 BACK ON AT 12:30. COD-1 VER/HFP L3/HFP
24502 | Hazard | 3309302 | VICCO | JEFF | 2013-11-25 12:41 | 2013-11-25 13:00 | 3 | 19 | H4071771 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEAD BURNT INTO ON XFMR POLE, CALLING FOR BIGGER XFMR LEADS, P HICKS TO BRING WIRE // ALSO LIFTED TAP TO TR 185 @ 1240HOT LEAD BURNT INTO ON XFMR POLE, CALLING FOR BIGGER XFMR LEADS, P HICKS TO BRING WIRE. TOOK TAP OFF AT 12;41, BACK ON AT 13:00 COD-10 PART OUT & 3 OUT DUP OF 4071771 FOR 3 VER/HFP L3/HFP IDC XXXX
24503 | Pikeville | 3421001 | BREAKS | CITY | 2014-02-25 09:42 | 2014-02-25 10:39 | 1 | 57 | 4432871 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED THRU THE STIRRUP. I REPLACED BOTH. COD-1 ISO PO @ 37820244000109 VER/HFP L3/HFP
24504 | Hazard | 3309903 | SLEMP | BEECH FORK | 2021-03-24 15:15 | 2021-03-24 15:34 | 3 | 19 | 4370351 | 57 | TRANSMISSION LINE | EQUIPMENT FAILURE | CIRCUIT SWITCHER | Transmission line momentarily de-energized to drop SLemp Station to allow crews to safely open CB B due to trip coil burnt up OUtage shoul last 15 mins from start FTER 1530
24505 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2020-11-12 20:28 | 2020-11-12 21:25 | 1 | 57 | 4671661 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse broke . replaced fuse
24506 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2022-06-01 10:23 | 2022-06-01 11:20 | 1 | 57 | 4992331 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke @ 1145-264.//Will be making repairs.//Replaced 7200 cutout and bracket.//Restored @ 11:20
24507 | Pikeville | 3421001 | BREAKS | CITY | 2014-10-03 17:23 | 2014-10-03 18:20 | 1 | 57 | 4548791 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN ON SERVICE DROP//// OPENED TRANSFORMER BANK ON POLE #220-C2-83 @ 17:50 MADE REPAIRS AND CLOSED TRANSFORMERS BACK IN @ 18:20 ///RESTORED SERVICE VER/CRB
24508 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2011-02-24 12:19 | 2011-02-24 13:16 | 1 | 57 | 60731-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WR#38932530FUSE OUT CHECK FOR CAUSE OF OUTAGE FUSE LINK BROKE REPLACED 6-T FUSE//VER/CRB IDC XXXX
24509 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-08-27 21:33 | 2018-08-27 22:30 | 1 | 57 | 4004841 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 37830254C00027.. need 2 men and big bucket..no power out yet.. Released by crew 077H18restored @22:30
24510 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2019-02-07 15:09 | 2019-02-07 16:06 | 1 | 57 | 4760701 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lightning arrester, cutout and t-bracket need to be changed/sparking stopped by pushing away pole ground/held for normal hours per duty/pole 37830343C00210 opened at 1509 repairs made and power restored at 1606
24511 | Pikeville | 3421001 | BREAKS | CITY | 2018-05-15 14:53 | 2018-05-15 15:50 | 1 | 57 | 4352671 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt up @ weatherhead/// will make repairs// Repairs made restored service @ 15:50// only 1 customer affected
24512 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2017-10-23 19:03 | 2017-10-23 20:00 | 1 | 57 | 4487911 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT HOUSE, REMOVED SERVE ENDS AND RESQUEEZED ALL CONN. ALL GOOD AT THIS LOC AT 2000 BY AMG VER/AWD. VER/AWD L3/HFP XXXHFP
24513 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-09-24 14:51 | 2018-09-24 15:48 | 1 | 57 | 4151271 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 402-`102, replaced cutout restored power at 15:48. L3/HFP
24514 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-04-14 15:51 | 2016-04-14 16:10 | 3 | 19 | H4091861 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUN OPEN SECONDARY DOWN ON GROUND HOT BETWEEN 205-77 &205-259 OPENED TRANSFORMER ON POLE 78 AT 15:51 REPAIRS MADE POWER RESTORED AT 16:10// VER/ ADH
24515 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-12-19 16:45 | 2019-12-19 17:04 | 3 | 19 | 4170961 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replace bad 25kva xfmr open @1645 closed @ 1704 please close ticket thanks.bt
24516 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-12-13 23:23 | 2018-12-14 00:20 | 1 | 57 | 4563551 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad connection in service drop///opened xfmr at 23:23 closed at 00:20 L3/HFP
24517 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-01-25 21:45 | 2009-01-25 22:42 | 1 | 57 | H59790-1 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3310501// 3PHASE SERV MELTED TOGETHER NEAR SERV ENTRANCE .UNKNOWN CAUSE AT THIS TIME.POSSIBLY OVERLOADED.WILL HAVE TO OPEN XFMR BANK TO REPAIR./ WILL OPEN TRANSFORMER UP TO MAKE REPAIRS - ABOUT 1 HOUR OUTAGE /3310501// 3PHASE SERV MELTED TOGETHER NEAR SERV ENTRANCE .UNKNOWN CAUSE AT THIS TIME.POSSIBLY OVERLOADED.WILL HAVE TO OPEN XFMR BANK TO REPAIR.FOUND BAD SPLITBOLT CONNECTION WHICH CAUSED PROBLEM.OPENED XFMR BANK AT 2145 CLOSED BACK IN AT 22:42 / COD-2 // VER/LDA L3/KEP
24518 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-03-30 23:08 | 2018-03-31 00:05 | 1 | 57 | 4157681 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
24519 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-07-13 08:53 | 2013-07-13 09:50 | 1 | 57 | 4517841 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED LINE FUSE DOOR. COD-1 ISO LF 38830259000030 VER/HFP L3/HFP IDC XXXX
24520 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-03-12 18:33 | 2008-03-12 19:30 | 1 | 57 | 56693-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RESQUEZED CONNECTIONS//3000301//VER/CRB IDC XXXX
24521 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-07-22 10:03 | 2011-07-22 11:00 | 1 | 57 | 4578241 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT AND HOT TAP, HAVE IT CHANGED AND POWER IS RESTORED AT THIS LOC//COD 1// VER/DBM
24522 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-08-29 18:53 | 2008-08-29 19:50 | 1 | 57 | 57506-1 | 57 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BUSHING LOOSE ON TRANSFORMER, REPAIRS COMPLETE / 08-29-08 GXJ//3402801//VER/CRB IDC XXXX
24523 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-11-13 15:03 | 2014-11-13 16:00 | 1 | 57 | 4725631 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN LINK// COD1//VER/ ADH
24524 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-10-23 13:03 | 2013-10-23 14:00 | 1 | 57 | 4956651 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 137-280 6T FUSE BROKE REPLACED FUSE POWER ON//COD 1// VER/DBM L3/HFP
24525 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-11-02 16:13 | 2009-11-02 17:10 | 1 | 57 | 56244-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP BAD FUSE LINK. COD-1 ISO TF 38830187000071 L3/HFP IDC XXXX
24526 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-01-01 10:50 | 2011-01-01 11:47 | 1 | 57 | 57427-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38258167 // CALLED CUSTOMER AND SHE AGREED TO WAIT UNTIL TOMORROW.....REPLACED BAD CONNECTION ON SECONDARY/SERVICE LOOP (ONE HOT LEG ONLY) ON XFMR POLE....ALL OK NOW.....JRV....01/01/11 ADJUSTED TIME OFF TO GIVE TIME TO REPLACE CONNECTION AND CHECK OTHERS...HFP VER/HFP L3/HFP IDC XXXX
24527 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-02-11 14:15 | 2010-02-11 15:12 | 1 | 57 | 56888-1 | 57 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITED FUSE BURNT UP REPLACED BOTH THAT WAS LEFT AND RESTORED POWER RELEASED BY CREW 074H10 - EMAILED CDI FOR CAUSE CODES// VER/TOM L3/TOM IDC CHANGED CLEARING DEVICE FROM LINE FUSE XXXX
24528 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-11-04 10:30 | 2010-11-04 10:58 | 2 | 28 | 51625-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD-2 VER/HFP L3/HFP IDCC TOF816 ALLOWED TIME FOR REPAIR ORIGINAL CALL WAS BRIGHT DIM XXXX
24529 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2020-03-08 09:39 | 2020-03-08 10:35 | 1 | 56 | 4460561 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 service drop burnt down due to 200 amp meter base overloaded drop capability.replace 4/3 drop with 2/3 drop.restored power at 10:35.
24530 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-09-26 09:16 | 2014-09-26 10:12 | 1 | 56 | 4530151 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP , I CHANGED IT OUT/// 10T LINE FUSE @ 37830356D00454/// TRANSFORMER IS REMOVED ON POLE 37830356D00454/// COD 1/// MD// VER/BOW
24531 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-07-10 10:12 | 2010-07-10 10:40 | 2 | 28 | 64739-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | MISMAP,, BROKEN FUSE AT 38830226000009, 2564 GRAHN RD IS ON THIS XFMR, ALL CUSTOMERS OFF OF THIS POLE ARE ON THIS XFMR//COD 2//MD FILED//ISO// VER/DBM IDC XXXX
24532 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2017-07-25 16:04 | 2017-07-25 17:00 | 1 | 56 | 4178761 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | 500MCM RISER BURNTED OFF AT SPLIT BOLT, HAVE REPLACED AT THIS TIME, ALL GOOD AT THE WATER PLANT, SEND TO ENG, MAY NEED TO LOOK AT THIS MAY NEED A UPGRADE//SENT TO TECH AND LINE VER/CRB /// TROUBLE TICKET COMMENTS SAYS THEY HAVE LOST A PHASE = L3/HFP HFPC MCCDL
24533 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-05-12 13:49 | 2021-05-12 14:45 | 1 | 56 | 4580451 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
24534 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-03-02 21:22 | 2014-03-02 21:50 | 2 | 28 | 4444711 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HAD THE DDC TO DROP THE FLEMMING MCROBERTS BKR AT 21:22 TO ISOLATE A BAD XFMR CUTOUT THAT WAS BURNING BAD OVER A BIG CAMPER SITTING AGAINST THE POLE THEY PUT THE BREAKER BACK IN AT 21:23 . I REPLACED THE CUTOUT AND RESTORED THEIR POWER AT 21:50 VER/PDP IDCC TOF2031 XXXX
24535 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-07-08 12:44 | 2011-07-08 13:40 | 1 | 56 | 4487291 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER. COD-1 ISO SO 37830270A00191 VER/HFP L3/HFP IDC XXXX
24536 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-04-20 11:24 | 2016-04-20 12:20 | 1 | 56 | 4107521 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE LINK BROKE./ ISO 38830142A00397/ COD 1/ VER/BOW
24537 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-09-14 16:18 | 2021-09-14 16:32 | 4 | 14 | 4240341 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Open fuse 38830752000029 (4 COD) to straighten pole that is being washed out////Off at XXXX -- On at XXXXpole washed out making tempary repaires to make safe.. opened @ closed @pole washed out making tempary repaires to make safe.. opened @ 16:18 closed @ 16:32.. Changed out bad cutout
24538 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-10-06 09:22 | 2020-10-06 09:50 | 2 | 28 | 4529551 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 9:50. sh
24539 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-09-05 16:14 | 2013-09-05 17:10 | 1 | 56 | 4823351 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1124-3174 6T BAD CUTOUT DOOR REPLACED VER/CRB L/3 CRB IDC XXXX
24540 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-02-06 15:24 | 2015-02-06 16:20 | 1 | 56 | 4997291 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN. RESTORED @ 16:20. SH POLE 38830760B00338 VER/CRB L3/HFP XXX
24541 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-01-02 12:40 | 2016-01-02 13:08 | 2 | 28 | 4581381 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TOP OPEN TRANSFORMER ON POLE 38831076000039 TO CHANGE BAD CUTOUT IN ORDER 4581161/ 1240-1308/ ISO 38831076000039/ COD 2/ VER/BOW
24542 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2018-01-13 15:24 | 2018-01-13 16:20 | 1 | 56 | 4744721 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at xfmr, made repairs restored power at 16:20..
24543 | Hazard | 3302703 | HAZARD | HAZARD | 2019-03-22 16:12 | 2019-03-22 16:40 | 2 | 28 | 4011711 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | had to open xfer 37830296C10422 due to bad connections and make repairs off @ 1612 on @ 1640burnt connection opened xfmr,s at 16:12 closed back at 16:40
24544 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2018-09-24 17:52 | 2018-09-24 18:48 | 1 | 56 | 4151961 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Released by crew 076S02// fuse broke on xfrm// refused. restored at 18:48 L3/HFP
24545 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-09-16 08:37 | 2011-09-16 09:33 | 1 | 56 | 4876011 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XMF FUSE OPEN; FUSE HAD PULLED LOOSE, REFUSED XMF APR AT 0933 CLOSE TICKET //VER/CRB IDCC FP NULL XXXX
24546 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-01-22 13:19 | 2011-01-22 14:15 | 1 | 56 | 63619-1 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE PULLED LOOSE LOOKED LIKE POWER RESTORED AT 1415 CLOSE TICKET COD-1 ISO TF 38830381D20197 VER/HFP L3/HFP IDC XXXX
24547 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-03-26 16:00 | 2009-03-26 16:28 | 2 | 28 | 61803-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT//COD 2//ISO 37830174A00032//COD 2// VER/DBM IDC XXXX
24548 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-10-07 05:45 | 2009-10-07 06:13 | 2 | 28 | 57262-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CHANGED BAD CUTOUT ON POLE 163B94. THIS POLE IS A DOUBLE DEAD END FRONT ARM IS BURNT JUST ABOUT INTO. SEND COPY TO RON RYE ENG .NEED JOB WRITTEN UP TO CHANGE ARM //VER/CRB IDCC MCCNI ALLOWED 30 MIN FOR REPAIR XXXX
24549 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2013-02-26 20:47 | 2013-02-26 21:43 | 1 | 56 | 4856131 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// WILL REFUSE// FUSE APPEARED TO HAVE BROKEN// REFUSED// POWER IS RESTORED COD-1 ISO TF 37830048A21109 VER/HFP L3/HFP IDC XXXX
24550 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-11-28 20:59 | 2020-11-28 21:55 | 1 | 56 | 4727351 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @72-A-372, checking. Trans. fuse had melted, refused @2155.//cod 1
24551 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2009-11-14 12:07 | 2009-11-14 12:21 | 4 | 14 | 57041-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED CUTOUT ON 703-79 TO ISOLATE TROUBLE ON 703-29 // 3401801//LOOKING IT OVER NOW3401801//LOOKING IT OVER .CHANGED CUTOUT ON POLE703-29 OPENED AT POLE 703 79 AT 12:07 CLOSED AT 12:21 // CUSOTMERS OUTAGED ON ORDER 57041-1 /// VER/TOM L3/TOM IDCC TOF1010 XXXX
24552 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2013-03-01 14:45 | 2013-03-01 15:13 | 2 | 28 | 4865241 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER OPEND TR TO MAKE RISER REPAIRS.HAD LOOSE RISER IN TRANSFORMER I HAVE REPAIRES MADE AND EVERYTHING IS OK AT THIS LOC, NO ONE WAS HOME, CALLED CUST AND LET HER KNOW WHAT I FOUND VER/KEP IDCC TOF1358 XXXX
24553 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-11-13 17:19 | 2015-11-13 18:15 | 1 | 56 | 4445661 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED CONNECTIONS ON POLE// VER/ ADH
24554 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-04-24 16:24 | 2012-04-24 17:20 | 1 | 56 | 4704041 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HAD MELTED LOOSE AT SECONDARY POLE//HAD ONE HOT LEG OUT//I REWORKED CONNECTIONS//COMPLETE/EM VER/HFP L3/HFP IDC XXXX
24555 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-06-03 14:19 | 2008-06-03 15:15 | 1 | 56 | 55022-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN INTO. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT. VER/HFP IDC XXXX
24556 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-02-29 16:22 | 2012-02-29 17:18 | 1 | 56 | 4520561 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRING CONNECTION // VER/DBM IDC XXXX
24557 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-02-16 10:27 | 2008-02-16 10:55 | 2 | 28 | 63744-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3312202/// SERVICER OPENED TRANSFORME UP TO ALLOW HIM TO REPAIR PRIMARY NEUTRAL THAT IS DOWN/ NEUTRAL PULLED OUT OF SLEEVE// VER/HFP IDC XXXX
24558 | Pikeville | 3413402 | GARRETT | LACKEY | 2009-10-17 17:42 | 2009-10-17 18:38 | 1 | 56 | 54160-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3413402// FUSE BROKEN ... REPLACED FUSE, ALL WORK COMPLETE / GXJ//COD 1// VER/DBM IDC XXXX
24559 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-10-27 16:14 | 2016-10-27 17:10 | 1 | 56 | 4058701 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | C PHASE TRANS FUSE PULLED APART ON 1108-B-345 CAUSING PARTIAL POWER TO MOUNTIAN WATER PUMPING STATION REFUSED CUTOUT RESTORED POWER AT 17;10 VER/AWD L3/HFP HFPC CCO
24560 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-08-05 22:27 | 2013-08-05 23:23 | 1 | 56 | 4625941 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR. VER/KEP
24561 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-01-02 15:14 | 2011-01-02 16:10 | 1 | 56 | 57981-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK. COD-1 ISO TF 38830161D30181 VER/HFP L3/HFP IDC XXXX
24562 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-10-02 14:04 | 2008-10-02 15:00 | 1 | 56 | 52948-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP BROKEN LINK/GOING TO LEAVE BREAKER OFF OUTSIDE NOBODY HOME/LEFT NOTE/NO CREW REQUIRED// ENTERED A NOTE ON CUSTOMERS ACCOUNT TO TURN ON THERE OUTSIDE BREAKER - HFP COD-1 IDC XXXX
24563 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-09-22 10:20 | 2014-09-22 10:48 | 2 | 28 | 4517891 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION @ XFMR/ REWORKED CONNECTIONS // REPAIRS MADE // OPENED XFMR @ 10:20 // CLOSED 10:48/// ISO 38831126A00391/// COD 2 VER/DKG L3/DKG
24564 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2022-11-02 11:35 | 2022-11-02 12:31 | 1 | 56 | 4090061 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT OFF @38830021B43577 RESTORED @1231
24565 | South Williamson | 3411401 | DEWEY | INEZ | 2012-01-27 16:54 | 2012-01-27 17:50 | 1 | 56 | 4299541 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BROKE IN SERVICE DROP//LOOKS LIKE IT CONTACTED HOT LEG AT RED TO RED CRIMPIT//I SPLICED BACK AND REDID CONNECTIONS//CUSTOMER STATES TV CABLE BOX BURNED UP, SO MAY POSSIBLY HAVE DAMAGE CLAIM ??///REPAIRED AND BACK ON AT 17:47//COMPLETE//EM VER/HFP L3/HFP IDC XXXX
24566 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-02-28 16:16 | 2008-02-28 16:30 | 4 | 14 | 51307-1 | 56 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE//3000102//VER/CRB IDC XXXX
24567 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-09-08 09:34 | 2020-09-08 10:30 | 1 | 56 | 4440791 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout at 39830925000151 FETR 1100opened line fuse on pole 18 to replace broke cutout on pole 151. repairs made line fuse in at 1030
24568 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2008-12-20 12:16 | 2008-12-20 13:12 | 1 | 56 | 61216-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BROKE CUTOUT ISO POLE 38830552A00550 COD1 SENDING MD FOR FUSE...HFP L3/HFP IDC XXXX
24569 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-03-06 13:47 | 2018-03-06 14:15 | 2 | 28 | 4971821 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-2 ISO LF 37830205A00058 OFF @ 1347 ON @ 1415 COD-2 ISO LF & TF 37830205A00058
24570 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-07-01 13:39 | 2009-07-01 14:35 | 1 | 56 | 58340-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT COD-1 VER/KEP L3/KEP IDC XXXX
24571 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-07-10 23:14 | 2008-07-11 00:10 | 1 | 56 | 51039-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003//CUTOUT DOOR BURNT REPLACED DOOR RELEASED BY CREW 078S11 VER/PDP IDCC PN136 XXXX
24572 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-01-31 17:38 | 2018-01-31 18:34 | 1 | 56 | 4788201 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout complete/ ISO 38830350D40194/ COD 1
24573 | South Williamson | 3411401 | DEWEY | INEZ | 2014-07-21 23:39 | 2014-07-22 00:35 | 1 | 56 | 4271201 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE//REPALACED//RESTORED AT00:35 VER/DKG L3/DKG
24574 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2010-03-16 00:48 | 2010-03-16 01:16 | 2 | 28 | 50514-1 | 56 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34261472 //0N SITE, CHECKING TROUBLE, XFORMER OFF AT 0048, BACK ON AT 0116 VER/LDA IDC XXXX
24575 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-09-15 14:50 | 2011-09-15 15:45 | 1 | 55 | 4873761 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE TRANSFORMER CUTOUT HAS FAILED. COD-1 ISO TF 37830359000052 VER/HFP L3/HFP IDC XXXX
24576 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-01-16 15:09 | 2022-01-16 16:04 | 1 | 55 | 4352001 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse pulled into
24577 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2010-01-19 11:45 | 2010-01-19 12:40 | 1 | 55 | 56451-1 | 55 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION CAME INTO AT XFMR PART POWER,, MADE REPAIRS RESTORED POWER AT12:40//COD 1 IDC XXXX
24578 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-06-18 10:20 | 2019-06-18 11:15 | 1 | 55 | 4536011 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmer restored
24579 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-07-11 18:05 | 2018-07-11 19:00 | 1 | 55 | 4764041 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t fuse 181-64
24580 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2013-10-01 11:14 | 2013-10-01 12:09 | 1 | 55 | 4901621 | 55 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 FUSE OUT IN 3 PHASE BANK--BROKEN FUSE COD-1 ISO TF 38830021D26673 VER/HFP L3/HFP IDC XXXX
24581 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-07-26 14:20 | 2013-07-26 15:15 | 1 | 55 | 4595691 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM IS BROKEN OFF HANGING BY THE BRACES, WILL NEED CREW TO FIX RELEASED BY CREW 077S12 OPEN LINE FUSE@14:20 CLOSED@15:15 POWER RESTORED//COD 1// VER/DBM IDC XXXX
24582 | South Williamson | 3200302 | BELFRY | TOLER | 2021-01-21 20:20 | 2021-01-21 21:15 | 1 | 55 | 4884051 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers neutral burnt into midspan of their service drop, had to open Trans. @2020 to make repairs. Had to replace about a 30 ft. section of customers service drop, closed trans. back in @2115./ ISO 38820989D00068/ COD 1
24583 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-11-02 10:20 | 2018-11-02 11:15 | 1 | 55 | 4356201 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required broken fuse link
24584 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-09-09 16:55 | 2013-09-09 17:50 | 1 | 55 | 4832591 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE INTO. ALSO MAIN LINE 6A NETURAL IS STOLEN ON POLE 244-20,21 AND 22 NO TRUCK AND NO RIGHT OF WAY NEEDED//MADE AED VER/CRB L/3 CRB
24585 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-01-03 17:33 | 2022-01-03 18:28 | 1 | 55 | 4294181 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transfomer fuse link appears to have broke. Restored @ 18:28. sh
24586 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-02-13 16:52 | 2018-02-13 17:47 | 1 | 55 | 4838011 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connections on xfmr pole, will open xfmr when help arrives, replaced leads, ok now/ ISO 37830158000171/ COD 1/ opened @ 1652 closed @ 1747
24587 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-07-22 20:25 | 2009-07-22 21:20 | 1 | 55 | 62560-1 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPLACING FUSE VER/TOM L3/TOM IDC XXXX
24588 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2018-11-07 13:50 | 2018-11-07 14:45 | 1 | 55 | 4376831 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Will have 1 customer out of power while finding the fault of a burndt hot leg on a URD secondary. Took customer back off @1350, located fault under side walk, gonna have contractor go in and bore a new secondary, hooked add-a-phase back up @1445. Please place back in abnormal until contractor completes work. L3/HFP
24589 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-06-05 13:20 | 2018-06-05 14:15 | 1 | 55 | 4557771 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Checked regulator on 858-336 and found no problems. No interruption until I opened xfmr 857-1 @ 13:20. Replaced xfmr and closed @ 14:15. sh
24590 | Hazard | 3303902 | LESLIE | WOOTON | 2014-03-12 19:25 | 2014-03-12 20:20 | 1 | 55 | 4481981 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED 367-72 AT 367-2 RESTORING POWER AT 2020 CLEARED UP BURNING POLE//IT FORCE CLOSED
24591 | Hazard | 3309302 | VICCO | JEFF | 2012-09-26 22:55 | 2012-09-26 23:50 | 1 | 55 | 4091141 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE == REFUSED == POWER OK VER/ARN IDC XXXX
24592 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-12-08 20:05 | 2010-12-08 21:00 | 1 | 55 | 64530-1 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT BAD CURRENT LIMITING FUSE REPLACED FUSE POWER RESTORED 2000 CLOSE TICKET.//VER/CRB IDC XXXX
24593 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-05-17 18:25 | 2022-05-17 19:20 | 1 | 55 | 4904681 | 55 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | neutral failed at connection, made repairs and restored customer
24594 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-03-03 23:26 | 2010-03-04 00:21 | 1 | 55 | 62625-1 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE HANGING DOWN STS FUSE BROKE IN TWO VER/PDP IDC XXXX
24595 | South Williamson | 3411401 | DEWEY | INEZ | 2011-01-21 13:45 | 2011-01-21 14:40 | 1 | 55 | 63381-1 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT OUT ON POLE 673-20// CHANGING NOW//DOOR CHANGED OUT//RESTORED AT 14:40//COMPLETE EM COD-1 ISO TF 38820673A00020 VER/HFP L3/HFP IDC XXXX
24596 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-10-16 21:25 | 2010-10-16 22:20 | 1 | 55 | 60346-1 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT. SINGLE CUSTOMER ON TRANSFORMER// VER/TOM L3/TOM IDC XXXX
24597 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-11-14 11:25 | 2013-11-14 12:20 | 1 | 55 | 4038591 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003703 CHANGED OUT BROKEN 7200 CUTOUT. COD-1 ISO TF 38830187000130 VER/HFP L3/HFP
24598 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-03-24 14:05 | 2014-03-24 15:00 | 1 | 55 | 4522311 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKEN..RE FUSED VER/CRB IDC XXXX
24599 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-02-07 00:25 | 2010-02-07 01:20 | 1 | 55 | 51319-1 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | BAD URD SPLICE ON NEUTRAL INSIDE CONDUIT, REMOVED CONDUIT, REPLACED SPLICE, RESQUEEZED ALL CONNECTIONS, ALSO FOUND AND TIGHTENED LOOSE HOT LEGS IN METERBASE. ONLY 1 CUSTOMER AFFECTED. //VER/GAH IDC CHANGED TIME OFF FROM 2321 XXXX
24600 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-06-22 14:30 | 2015-06-22 15:25 | 1 | 55 | 4639371 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 HOLE PAD HAD BAD CONNECTION AND WIRE WAS HEATING UP AND STARTING TO BREAK///OPENED XFMER 954-1113 AT 14:30 TO MAKE REPAIRS///XFMER BACK ON AT 15:25///COMPLETE BR/ ISO 38830954A31113/ COD 1/ VER/BOW
24601 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-05-31 13:20 | 2013-05-31 14:15 | 1 | 55 | 4202421 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK. COD-1 ISO TF 38830188D00159 VER/HFP L3/HFP IDC XXXX
24602 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-05-24 15:50 | 2011-05-24 16:45 | 1 | 55 | 4161241 | 55 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY LUG ON XFMR HAD BEEN TIGHTENED TO TIGHT WHEN INSTALLED LAST WEEK//LUG HAD BROKE AND HOT LEG HAD FELL OUT//REPAIRED//COMPLETE//EM
24603 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-07-09 15:15 | 2010-07-09 16:10 | 1 | 55 | 64126-1 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOT TAP ON POLE 188-317 AT 15:15 TO CHANGE OUT BAD CUTOUT ON POLE 188-481. POWER BACK ON AT 16:10. NEED LINE CREW LATER TO MAKE REPAIRS TO POLE. TREES NEED CUT OUT OF PRIMARY TO LET LINE CREW WORK ON POLE 188=481.//ISO 38830188D00317 //COD 1 IDCC PN481, TOF1454 XXXX
24604 | Hazard | 3303902 | LESLIE | WOOTON | 2015-02-25 18:20 | 2015-02-25 19:15 | 1 | 55 | 4081821 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 463-74 . ONLY 1 CUST. ON XFMR// VER/ ADH
24605 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2008-11-26 10:22 | 2008-11-26 11:17 | 1 | 55 | 52443-1 | 55 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP REPLACED CONNECTIONS ON POLE IDC XXXX
24606 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-07-05 12:35 | 2021-07-05 13:30 | 1 | 55 | 4857971 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced door