## Outages
Kentucky Power Company Fuel Adjustment Clause Generating Unit Outages May 1,2024 -October 31, 2024
Unit Name | Event Start | Event End | Event Type | Event Description
Mitchell 2 | 2024-04-06 00:29 | 2024-05-21 02:50 | PO | MATS Outage, Boiler I/R, Coal Silo Inspection, FGD Electrical Feed Repair, Reclaim Tank Coating Replacement, CPS Tank Cleaning, NERC Relay Testing, Precipitator Inspect/Repair, Wind Box Casing Repairs, ID Fan Inspect/Repair
Mitchell 1 | 2024-04-14 01:36 | 2024-06-01 22:00 | PO | Boiler i/r, ID Fan i/r, Cooling Tower Canopy Beams i/r.
Mitchell 2 | 2024-05-29 01:20 | 2024-05-31 21:20 | MO | Repair steam leak on #1 Control Valve leak-off line,To i/r # 2 Turbine Control Valve LVDT, i/r the # 21 ID Fan high vibration issues.
Mitchell 1 | 2024-06-01 22:00 | 2024-06-03 01:13 | RS | Reserve Shutdown
Mitchell 1 | 2024-06-03 01:13 | 2024-06-04 17:30 | U1 | Packing Failure on BMO valve
Mitchell 2 | 2024-07-02 02:02 | 2024-07-07 07:19 | MO | Main Turbine Control Valve i/r. BFP Steam Supply valves ARV-542 i/r and AMO-542 i/r. Steam Generator i/r. #25 pulverizer PA Shutoff damper i/r. Generator Buss Duct i/r, 22 FD Fan Outlet Damper i/r cylinder and seals, ID Fan 21 AC Jacking Oil Pump i/r, Boiler/r.
Mitchell 1 | 2024-07-24 02:08 | 2024-07-26 21:06 | MO | Removed for EHC leak on #6 Governor Valve Actuator, 1st RH left Stop Valve Actuator i/r, ID Fans i/r, Steam Generator i/r.
Mitchell 1 | 2024-07-26 21:06 | 2024-07-27 10:40 | RS | Cover Maintenance Release to Parallel
Mitchell 1 | 2024-08-21 01:30 | 2024-08-27 23:59 | MO | Unit removed from service for the Hand Shut-off before FRV-101 Valve replacement,Steam Generator i/r, ID Fan i/r, ARV-542 packing replacement, stroke Turbine Valves and adjust limits. Replace actuator on 2nd Reheat Right Upper Intercept valve and inspect valve. During Hydro two tube leaks found on northside front wall and sidewall
Mitchell 1 | 2024-08-27 23:59 | 2024-08-28 12:08 | RS | Reserve Shutdown
Mitchell 2 | 2024-08-31 01:23 | 2024-09-05 | RS | Reserve Shutdown
Mitchell 1 | 2024-08-31 09:29 | 2024-09-02 09:56 | U1 | Stator water low flow.
Mitchell 1 | 2024-09-08 14:00 | 2024-09-11 15:00 | U1 | Removed unit from service due to high silica readings caused by a Condenser Leak. Two leaks were found and repaired
Mitchell 1 | 2024-09-11 15:00 | 2024-09-12 00:07 | SF | EHC Leak on Main Turbine
Big Sandy 1 | 2024-09-14 02:25 | 2024-12-04 16:00 | PO | Boiler i/r, Cooling Tower i/r, BFPT replacement, Generator balance shot, Outlet Duct replacement, BOP i/r.
Mitchell 1 | 2024-09-14 02:56 | 2024-09-17 19:15 | U1 | Unit was removed due to increase in sodium and conductivity Condenser Tube leak. Had to plug tubes when leak check was performed. Found broken condenser steam spray piping
Mitchell 1 | 2024-09-17 19:15 | 2024-09-23 | MO | Set UMO-1 limits, replace UMO 105 and 106 Motor operated valves and isolation hand shut-offs, replace positioner on FRV-101, Steam Generator i/r, and Ammonia Injection Steam Purge valves i/r, Boiler i/r.
Mitchell 1 | 2024-09-23 | 2024-09-27 | RS | Reserve Shutdown
Mitchell 1 | 2024-09-27 | 2024-10-02 23:54 | MO | Chemical cleaning common equipment preparation and to clean Unit 1 Waste Water Sump.
Mitchell 2 | 2024-09-05 | 2024-09-07 | MO | Began prepartion for U2 Chemical Clean,completed unit deslag, Steam Generator i/r, Cooling Tower i/r.
Mitchell 2 | 2024-09-07 | 2024-10-13 02:57 | PO | Boiler i/r, Chemical Clean, MATS testing, Cooling Tower i/r, BOP i/r.
Mitchell 1 | 2024-10-18 09:32 | 2024-10-21 07:09 | U1 | #3 Control Valve Main Steam lead drain valve socket weld failed
Mitchell 2 | 2024-10-21 08:29 | 2024-10-22 07:57 | U1 | Unit removed due to trip out on Low Stator Waterflow
Mitchell 2 | 2024-10-22 07:57 | 2024-10-25 | RS | Reserve Shutdown
Mitchell 2 | 2024-10-25 | 2024-10-30 06:00 | RS | Reserve Shutdown
Mitchell 2 | 2024-10-30 06:00 | 2024-10-30 08:52 | SF | Critical Temperatures needed Cooled Out to roll the turbine. Ice had to verify Flash Tank Return Temps & reaplce the PSO Temp Thermowell
PO = Planned Outage
MO = Maintenance Outage
RS = Reserve Shutdown
U1 = Forced Outage (Immediate)
SF = Startup Failure
i/r = Inspect and Repair