## Export
DEK FAC 2025-00342
PSC DR 1.14
Review Period: 11/1/2022 - 10/31/2024
Requested Data Period: 5/1/2024 - 10/31/2024 (Last six months of review period)
Unit | Event Type | Schedule Hours | Forced Hours | Actual Hours | Event Duration Hours | Event Start | Event End | Event Description
East Bend Steam-2 | MO | 21.767 | 0 | 21.767 | 21.767 | 2024-05-06 22:34 | 2024-05-07 20:20 | Tuning
East Bend Steam-2 | MO | 276.833 | 0 | 276.833 | 276.833 | 2024-05-11 04:42 | 2024-05-22 17:32 | Induced Draft (ID) Booster Fan (BF) Variable Inlet Vane (VIV) Repair
East Bend Steam-2 | MO | 4.067 | 0 | 4.067 | 4.067 | 2024-05-22 18:32 | 2024-05-22 22:36 | Tuning
East Bend Steam-2 | MO | 19.167 | 0 | 19.167 | 19.167 | 2024-05-22 23:10 | 2024-05-23 18:20 | Tuning
East Bend Steam-2 | PO | 1439.783 | 0 | 1439.783 | 1439.783 | 2024-09-06 16:30 | 2024-11-05 16:17 | 2024 Fall Outage - Flue Gas Desulfurization (FGD) Ductwork replacement - Coal Barge Unloader (CBU) Buckets - Soot Blowing Air Compressor (SBAC) Overhaul
Woodsdale CT-1 | PO | 2006.667 | 0 | 2006.667 | 2006.667 | 2024-03-01 05:01 | 2024-05-23 19:41 | Turbine blade replacement, rows 1-4
Woodsdale CT-1 | U1 | 0 | 255.85 | 255.85 | 255.85 | 2024-07-17 01:46 | 2024-07-27 17:37 | Instrumentation issues found during shutdown of unit
Woodsdale CT-1 | U1 | 0 | 151.217 | 151.217 | 151.217 | 2024-08-09 13:56 | 2024-08-15 21:09 | Out of service (OSS) until overheating issue can be resolved, no Estimated Time of Arrival (ETA)
Woodsdale CT-1 | PO | 119.967 | 0 | 119.967 | 119.967 | 2024-08-19 04:01 | 2024-08-24 03:59 | Control room consolidation
Woodsdale CT-1 | U1 | 0 | 0.733 | 0.733 | 0.733 | 2024-08-25 16:38 | 2024-08-25 17:22 | Remote start. Gas supply failure.
Woodsdale CT-1 | PO | 15.983 | 0 | 15.983 | 15.983 | 2024-09-12 04:01 | 2024-09-12 20:00 | Enbridge working on their regulating station.
Woodsdale CT-1 | PO | 349.817 | 0 | 349.817 | 349.817 | 2024-09-14 04:01 | 2024-09-28 17:50 | Fall Outage
Woodsdale CT-1 | MO | 53.75 | 0 | 53.75 | 53.75 | 2024-10-31 04:01 | 2024-11-02 09:46 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-2 | U1 | 0 | 19.833 | 19.833 | 19.833 | 2024-05-12 20:21 | 2024-05-13 16:11 | Generator close relay not picking up, cycled contacts, successful test run @ 1211
Woodsdale CT-2 | SF | 0 | 5.817 | 5.817 | 5.817 | 2024-05-19 17:15 | 2024-05-19 23:04 | Static Frequency Converter (SFC) fail to start
Woodsdale CT-2 | PO | 119.967 | 0 | 119.967 | 119.967 | 2024-08-19 04:01 | 2024-08-24 03:59 | Control room consolidation
Woodsdale CT-2 | U1 | 0 | 0.583 | 0.583 | 0.583 | 2024-08-25 16:47 | 2024-08-25 17:22 | Remote start. Gas supply failure.
Woodsdale CT-2 | PO | 15.983 | 0 | 15.983 | 15.983 | 2024-09-12 04:01 | 2024-09-12 20:00 | Enbridge working on their regulating station.
Woodsdale CT-2 | PO | 349.833 | 0 | 349.833 | 349.833 | 2024-09-14 04:01 | 2024-09-28 17:51 | Fall Outage
Woodsdale CT-2 | U1 | 0 | 1.667 | 1.667 | 1.667 | 2024-10-04 09:51 | 2024-10-04 11:31 | Tightened connections
Woodsdale CT-2 | U1 | 0 | 0.633 | 0.633 | 0.633 | 2024-10-11 19:58 | 2024-10-11 20:36 | Had to reset Automatic Voltage Regulator (AVR)
Woodsdale CT-2 | MO | 49 | 0 | 49 | 49 | 2024-10-31 04:01 | 2024-11-02 05:01 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-3 | PO | 323.283 | 0 | 323.283 | 323.283 | 2024-04-27 04:01 | 2024-05-10 15:18 | Spring outage/Borescope
Woodsdale CT-3 | PO | 119.967 | 0 | 119.967 | 119.967 | 2024-08-19 04:01 | 2024-08-24 03:59 | Control room consolidation
Woodsdale CT-3 | U1 | 0 | 0.733 | 0.733 | 0.733 | 2024-08-25 16:38 | 2024-08-25 17:22 | Remote start. Gas supply failure.
Woodsdale CT-3 | PO | 15.983 | 0 | 15.983 | 15.983 | 2024-09-12 04:01 | 2024-09-12 20:00 | Enbridge working on their regulating station.
Woodsdale CT-3 | PO | 342.65 | 0 | 342.65 | 342.65 | 2024-09-21 04:01 | 2024-10-05 10:40 | Fall Outage
Woodsdale CT-3 | U1 | 0 | 98.567 | 98.567 | 98.567 | 2024-10-13 11:29 | 2024-10-17 14:03 | Cooling pump breakers tripped. Test ran pumps all good, made alarm changes, test ran unit
Woodsdale CT-3 | MO | 53.75 | 0 | 53.75 | 53.75 | 2024-10-31 04:01 | 2024-11-02 09:46 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-4 | PO | 305.15 | 0 | 305.15 | 305.15 | 2024-04-27 04:01 | 2024-05-09 21:10 | Spring outage/Borescope
Woodsdale CT-4 | U1 | 0 | 2.6 | 2.6 | 2.6 | 2024-06-19 18:07 | 2024-06-19 20:43 | Remove unit due to blow off valves not closing, stroked slide valves
Woodsdale CT-4 | U1 | 0 | 0.1 | 0.1 | 0.1 | 2024-08-03 20:34 | 2024-08-03 20:40 | Remote start. Unit auto tripped due to no water injection.
Woodsdale CT-4 | U1 | 0 | 0.167 | 0.167 | 0.167 | 2024-08-06 15:53 | 2024-08-06 16:03 | Versa valve didn't open. No water injection and blow-offs didn't close.
Woodsdale CT-4 | PO | 119.967 | 0 | 119.967 | 119.967 | 2024-08-19 04:01 | 2024-08-24 03:59 | Control room consolidation
Woodsdale CT-4 | U1 | 0 | 0.517 | 0.517 | 0.517 | 2024-08-25 16:51 | 2024-08-25 17:22 | Remote start. Gas supply failure.
Woodsdale CT-4 | PO | 1789.917 | 0 | 1789.917 | 1789.917 | 2024-09-07 04:01 | 2024-11-20 17:56 | Unit Major (overhaul)
Woodsdale CT-5 | U1 | 0 | 16.283 | 16.283 | 16.283 | 2024-05-09 20:45 | 2024-05-10 13:02 | Trouble shot Automatic Voltage Regulator (AVR), nothing found, retested, successful start @ 0907
Woodsdale CT-5 | U1 | 0 | 2.7 | 2.7 | 2.7 | 2024-06-12 19:27 | 2024-06-12 22:09 | Data reviewed, decided to keep unit above 50MWs to prevent thrust probe from coming in.
Woodsdale CT-5 | U1 | 0 | 0.467 | 0.467 | 0.467 | 2024-06-29 19:28 | 2024-06-29 19:56 | Unit was remote started, tripped on thrust, dispatch could not move unit off of 5MW's
Woodsdale CT-5 | U1 | 0 | 0.167 | 0.167 | 0.167 | 2024-07-08 16:09 | 2024-07-08 16:19 | Blow off valves did not close, stroked, test ran, dispatch kept unit on
Woodsdale CT-5 | PO | 119.967 | 0 | 119.967 | 119.967 | 2024-08-19 04:01 | 2024-08-24 03:59 | Control room consolidation
Woodsdale CT-5 | U1 | 0 | 0.567 | 0.567 | 0.567 | 2024-08-25 16:48 | 2024-08-25 17:22 | Remote start. Gas supply failure.
Woodsdale CT-5 | PO | 15.983 | 0 | 15.983 | 15.983 | 2024-09-26 04:01 | 2024-09-26 20:00 | Enbridge working on their regulating station.
Woodsdale CT-5 | PO | 341.383 | 0 | 341.383 | 341.383 | 2024-09-28 04:01 | 2024-10-12 09:24 | Fall Outage
Woodsdale CT-5 | U1 | 0 | 9.85 | 9.85 | 9.85 | 2024-10-12 09:41 | 2024-10-12 19:32 | Dispatch did not raise unit load above 50MWs in time.
Woodsdale CT-5 | MO | 53.767 | 0 | 53.767 | 53.767 | 2024-10-31 04:01 | 2024-11-02 09:47 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-6 | PO | 558.1 | 0 | 558.1 | 558.1 | 2024-05-11 10:00 | 2024-06-03 16:06 | Spring outage/Borescope
Woodsdale CT-6 | U1 | 0 | 0.55 | 0.55 | 0.55 | 2024-07-15 18:04 | 2024-07-15 18:37 | Unit tripped due to breaker opening up, reset and brought unit back online
Woodsdale CT-6 | PO | 119.967 | 0 | 119.967 | 119.967 | 2024-08-19 04:01 | 2024-08-24 03:59 | Control room consolidation
Woodsdale CT-6 | U1 | 0 | 0.517 | 0.517 | 0.517 | 2024-08-25 16:51 | 2024-08-25 17:22 | Remote start. Gas supply failure.
Woodsdale CT-6 | PO | 15.983 | 0 | 15.983 | 15.983 | 2024-09-26 04:01 | 2024-09-26 20:00 | Enbridge working on their regulating station.
Woodsdale CT-6 | PO | 497.5 | 0 | 497.5 | 497.5 | 2024-09-28 04:01 | 2024-10-18 21:31 | Fall Outage
Woodsdale CT-6 | MO | 53.8 | 0 | 53.8 | 53.8 | 2024-10-31 04:01 | 2024-11-02 09:49 | Unit out of service for fuel oil wiring troubleshooting and repair.
Event Type Legend:
PO | Planned Outage
PE | Planned Outage Extension
MO | Maintenance Outage
ME | Maintenance Outage Extension
U1 | Unplanned (Forced) Outage – Immediate
U2 | Unplanned (Forced) Outage – Delayed
U3 | Unplanned (Forced) Outage – Postponed
SF | Startup Failure