## Data
Upgrade Id | Region | Description | Project Type | Voltage | Cost Estimate | Required Date | Transmission Owner | Proposal IDs | Schedule12 Location | (Non-Load Ratio Share) Cost Allocation Percent | (Load Ratio Share) Cost Allocation Percent | State | Location | Equipment | Task | Status | TEAC Cost | Driver | Projected In Service Date | Actual In Service Date | Immediate Need | Initial TEAC Date | Latest TEAC Date | Percent Complete | ISA In-Service Date | Revised In-Service Date | TEAC Materials
b0838 | PJM WEST | Hazard Area 138 kV and 69 kV Improvement Projects | Baseline | 138/69 | 44 | 6/1/2013 | AEP |  | Appendix | AEP:100 |  | KY | Hazard Area | Transmission Structures | Upgrade | IS | 44 | Baseline Load Growth Deliverability & Reliability | 12/31/2014 | 8/14/2014 | No | 9/16/2009 | 9/16/2009 | 100
b1093 | PJM WEST | Add a 43.2 MVAR capacitor bank at the Morgan Fork 138 kV Station | Baseline | 138 | 0.8 | 12/30/2013 | AEP |  | Appendix | AEP:100 |  | KY | Morgan Fork | Capacitor | Install | IS | 0.8 | Baseline Load Growth Deliverability & Reliability | 12/30/2013 | 12/31/2013 | No | 10/22/2009 | 10/27/2011 | 100
b1429 | PJM WEST | Perform a sag study on Fremont - Clinch River 138kV and upgrade the risers with 1590 ACSR. The new projected S/E is 310 MVA | Baseline | 138 | 0.1 | 12/31/2011 | AEP |  | Appendix | AEP:100 |  | KY | Fremont - Clinch River | Transmission Line | Sag Study | IS | 0.1 | Baseline Load Growth Deliverability & Reliability | 6/1/2015 | 4/21/2015 | No | 10/28/2010 | 3/19/2012 | 100 |  | 6/1/2015
b1443 | PJM WEST | Station work at Thelma and Busseyville Stations will be performed to replace bus and risers | Baseline |  | 0.2 | 6/1/2015 | AEP |  | Appendix | AEP:100 |  | KY |  | Bus | Replace | IS | 0.2 | Baseline Load Growth Deliverability & Reliability | 6/1/2015 | 6/1/2015 | No | 10/28/2010 | 10/28/2010 | 100
b1489 | PJM WEST | A sag study must be performed for the 5.40 mile Tristate – Chadwick 138 kV line to determine if a higher emergency rating can be used | Baseline | 138 | 0.3 | 12/31/2013 | AEP |  | Appendix | AEP:100 |  | KY | Tristate, Chadwick | Transmission Line | Sag Study | IS | 0.3 | Baseline Load Growth Deliverability & Reliability | 6/1/2015 | 10/23/2014 | No | 10/28/2010 | 10/28/2010 | 100 |  | 6/1/2015
b1491 | PJM WEST | Replace bus and risers at Thelma and Busseyville stations and perform a sag study for the Big Sandy – Busseyville 138 kV line | Baseline | 138 | 0.65 | 12/31/2013 | AEP |  | Appendix | AEP:100 |  | KY |  | Transmission Line | Sag Study | IS | 0.65 | Baseline Load Growth Deliverability & Reliability | 12/31/2013 | 2/18/2014 | No | 10/28/2010 | 9/12/2013 | 100 |  | 6/1/2015
b1491.1 | PJM WEST | Big Sandy - Thelma: SAG study mitigation work | Baseline | 138 | 0.11 |  | AEP |  | Appendix | AEP:100 |  | KY | Big Sandy - Thelman | Transmission Line | Mitigation Work | IS | 0.11 | Baseline Load Growth Deliverability & Reliability |  | 2/18/2014 | No | 6/24/2014 | 6/24/2014 | 100
b1491.2 | PJM WEST | Big Sandy - Thelma: Sag study mitigation work | Baseline | 138 | 0.05 |  | AEP |  | Appendix | AEP:100 |  | KY | Big Sandy - Thelman | Transmission Line | Mitigation Work | IS | 0.05 | Baseline Load Growth Deliverability & Reliability |  | 2/18/2014 | No | 6/24/2014 | 6/24/2014 | 100
b1492.1 | PJM WEST | Bellefonte Extension (KPCo): Sag study mitigation work | Baseline | 138 | 0.05 |  | AEP |  | Appendix | AEP:100 |  | KY | Bellefonte Extension | Transmission Line | Mitigation Work | IS | 0.05 | Baseline Load Growth Deliverability & Reliability |  | 5/29/2014 | No | 6/24/2014 | 6/24/2014 | 100
b1493 | PJM WEST | Perform a sag study for the Bellefonte – Grangston 138 kV line to increase its emergency rating | Baseline | 138 | 0.07 | 12/31/2013 | AEP |  | Appendix | AEP:100 |  | KY |  | Transmission Line | Sag Study | IS | 0.07 | Baseline Load Growth Deliverability & Reliability | 12/31/2013 | 2/8/2014 | No | 10/28/2010 | 10/28/2010 | 100 |  | 6/1/2015
b1494 | PJM WEST | Perform a sag study for the North Proctorville – Solida - Bellefonte 138 kV line to increase its emergency rating | Baseline | 138 | 0.09 | 12/31/2013 | AEP |  | Appendix | AEP:100 |  | KY,OH |  | Transmission Line | Sag Study | IS | 0.09 | Baseline Load Growth Deliverability & Reliability | 12/31/2013 | 5/29/2014 | No | 10/28/2010 | 10/28/2010 | 100 |  | 6/1/2015
b1665 | PJM WEST | Install a second 138/69 kV transformer at Thelma station | Baseline | 138/69 | 12.75 | 6/1/2015 | AEP |  | Appendix | AEP:100 |  | KY | Thelma | Transformer | Install | IS | 12.75 | Baseline Load Growth Deliverability & Reliability | 6/1/2015 | 10/30/2011 | No | 9/19/2011 | 3/19/2012 | 100
b1665.1 | PJM WEST | Construct a single-circuit 69 kV line from West Paintsville to the Mayo Trail Station | Baseline | 69 | 0 | 6/1/2015 | AEP |  | Appendix | AEP:100 |  | KY | West Painsville - Mayo Trail | Transmission Line | Construct | IS | 0 | Baseline Load Growth Deliverability & Reliability | 6/1/2015 | 10/30/2011 | No | 9/19/2011 | 3/19/2012 | 100
b1665.2 | PJM WEST | Install new 7.2 MVAR, 46 kV bank at Kenwood Station | Baseline | 46 | 0.4 | 6/1/2015 | AEP |  | Appendix | AEP:100 |  | KY | Kenwood | Capacitor | Install | IS | 0 | Baseline Load Growth Deliverability & Reliability | 6/1/2015 | 10/8/2009 | No | 3/19/2012 | 3/19/2012 | 100
b1866.1 | PJM WEST | Beaver Creek - Clinch River (KP): Sag study mitigation work | Baseline | 138 | 0.9 | 6/1/2015 | AEP |  | Appendix | AEP:100 |  | KY | Beaver Creek - Clinch River | Transmission Line | Mitigation Work | IS | 1.15 | Baseline Load Growth Deliverability & Reliability | 9/30/2014 | 3/19/2015 | No | 6/24/2014 | 6/24/2014 | 100
b1866.2 | PJM WEST | Dorton Loop: Sag study mitigation work | Baseline | 138 | 0.97 | 6/1/2015 | AEP |  | Appendix | AEP:100 |  | KY | Dorton Loop | Transmission Line | Mitigation Work | IS | 0.89 | Baseline Load Growth Deliverability & Reliability | 6/5/2014 | 4/21/2015 | No | 6/24/2014 | 6/24/2014 | 100
b1866.3 | PJM WEST | Dorton - Fleming: Sag study mitigation work | Baseline | 138 | 0.57 | 6/1/2015 | AEP |  | Appendix | AEP:100 |  | KY | Dorton - Fleming | Transmission Line | Mitigation Work | IS | 0.52 | Baseline Load Growth Deliverability & Reliability | 6/30/2014 | 4/21/2015 | No | 6/24/2014 | 6/24/2014 | 100
b1866.4 | PJM WEST | Beaver Creek - Clinch River (AP): Sag study mitigation work | Baseline | 138 | 1.45 | 6/1/2015 | AEP |  | Appendix | AEP:100 |  | KY | Beaver Creek - Clinch River | Transmission Line | Mitigation Work | IS | 0.87 | Baseline Load Growth Deliverability & Reliability | 6/30/2014 | 4/21/2015 | No | 6/24/2014 | 6/24/2014 | 100
b1866.5 | PJM WEST | Beaver Creek - Clinch River (KP): Sag study mitigation work | Baseline | 138 | 0.9 | 6/1/2016 | AEP |  | Appendix | AEP:100 |  | KY | Beaver Creek - Clinch River | Transmission Line | Mitigation Work | IS | 0 | Baseline Load Growth Deliverability & Reliability | 9/30/2014 | 3/19/2015 | No | 6/24/2014 | 6/24/2014 | 100
b1866.6 | PJM WEST | Beaver Creek - Clinch River (AP): SAG study mitigation work | Baseline | 138 | 1.45 | 6/1/2016 | AEP |  | Appendix | AEP:100 |  | KY | Beaver Creek - Clinch River | Transmission Line | Mitigation Work | IS | 0 | Baseline Load Growth Deliverability & Reliability | 6/30/2014 | 3/19/2015 | No | 6/24/2014 | 6/24/2014 | 100
b1866.7 | PJM WEST | Beaver Creek - Clinch River (AP): Sag study mitigation work | Baseline | 138 | 1.45 | 6/1/2016 | AEP |  | Appendix | AEP:100 |  | KY | Beaver Creek - Clinch River | Transmission Line |  | IS | 0 | Baseline Load Growth Deliverability & Reliability | 6/30/2014 | 4/21/2015 | No | 6/24/2014 | 6/24/2014 | 100
b1873 | PJM WEST | Install two 138 kV circuit breakers at Cedar Creek Station and primary side circuit switcher on the 138/69/46 kV transformer | Baseline | 138 | 2.5 | 6/1/2016 | AEP |  | Appendix | AEP:100 |  | KY | Cedar Creek | Circuit Breaker | Install | IS | 2.5 | Baseline Load Growth Deliverability & Reliability | 8/1/2016 | 4/16/2016 | No | 3/19/2012 | 3/19/2012 | 100
b2051 | PJM WEST | Install 3 138 kV breakers and a circuit switcher at Dorton station | Baseline | 138 | 3 | 5/1/2015 | AEP |  | Appendix | AEP:100 |  | KY | Dorton | Circuit Breaker | Install | IS | 3 | Generator Deactivation | 5/1/2015 | 6/21/2015 | No | 6/14/2012 | 6/14/2012 | 100 |  | 6/1/2015
b2233 | PJM WEST | Change transformer tap settings for the Baker 765/345 kV transformer | Baseline | 765/345 | 0.02 | 6/1/2016 | AEP |  | Appendix A | AEP:100 |  | KY | Baker | Transformer | Change Settings | IS | 0.03 | Operational Performance | 6/1/2016 | 7/31/2016 | No | 5/9/2013 | 7/11/2013 | 100
b2601 | PJM WEST | Fremont Station Improvements | Baseline | 138 | 3.3 | 6/1/2019 | AEP | 2014_2-2I | Appendix A | AEP:100 |  | KY | Fremont Station | Substation | Improve | IS | 2.5 | TO Criteria Violation | 6/1/2019 | 11/15/2016 | No | 1/7/2015 | 1/7/2015 | 100
b2601.1 | PJM WEST | Replace MOAB towards Beaver Creek with 138kV breaker | Baseline | 138 | 0 | 6/1/2019 | AEP | 2014_2-2I | Appendix A | AEP:100 |  | KY | Beaver Creek | Circuit Breaker | Replace | IS | 0 | TO Criteria Violation | 6/1/2019 | 11/15/2016 | No | 1/7/2015 | 1/7/2015 | 100
b2604 | PJM WEST | Bellefonte: Install new 138/69/34.5 kV 200 MVA transformer at Bellefonte station. Install circuit switcher and 34.5 kV 40 kA breaker on highside and lowside of transformer #5. | Baseline | 138/69/34.5 | 5.21 | 6/1/2019 | AEP | 2014_2-2L | Appendix A | AEP:100 |  | KY | Bellefonte | Transformer | Addition | IS | 3 | TO Criteria Violation | 6/1/2019 | 12/12/2017 | No | 1/7/2015 | 2/17/2021 | 100
b2750.1 | PJM WEST | Retire Betsy Layne 138/69/43 kV station and replace it with the greenfield Stanville station about a half mile north of the existing Betsy Layne station | Baseline | 138/69 | 7.63 | 12/1/2016 | AEP |  | Appendix A | AEP:100 |  | KY | Betsy Layne / Stanville | Substation | Retire | IS | 28.1 | TO Criteria Violation | 9/26/2018 | 9/26/2018 | Yes | 7/26/2016 | 1/24/2017 | 100
b2750.2 | PJM WEST | Relocate the Betsy Layne capacitor bank to the Stanville 69 kV bus and increase the size to 14.4 MVAR | Baseline | 69 | 7.63 | 12/1/2016 | AEP |  | Appendix A | AEP:100 |  | KY | Betsy Layne / Stanville | Capacitor | Relocate | IS | 0 | TO Criteria Violation | 9/26/2018 | 9/26/2018 | Yes | 7/26/2016 | 1/24/2017 | 100
b2761.1 | PJM WEST | Replace and relocate the Hazard 161/138 kV Transformer and circuit breaker 'M'. Upgrade protection scheme on the new Transformer including installation of low side breaker. | Baseline | 161/138 | 2.3 | 6/1/2021 | AEP | 2016_2-7A | Appendix A | AEP:100 |  | KY | Hazard | Transformer | Replace | IS | 3.8 | Baseline Load Growth Deliverability & Reliability | 11/15/2022 | 12/10/2021 | No | 10/6/2016 | 4/23/2019 | 100
b2761.2 | PJM WEST | Perform a Sag Study of the Hazard – Wooten 161 kV line to increase the thermal rating of the line | Baseline | 161 | 0 | 6/1/2021 | AEP | 2016_2-7A | Appendix A | AEP:100 |  | KY | Hazard – Wooten | Transmission Line | Sag Study | IS | 0 | Baseline Load Growth Deliverability & Reliability | 12/18/2020 | 12/18/2020 | No | 10/6/2016 | 10/6/2016 | 100
b2761.3 | PJM WEST | Rebuild the Hazard – Wooton 161 kV line utilizing 795 26/7 ACSR conductor (300 MVA rating). Replace line relaying and associated termination equipment. | Baseline | 161 | 16.48 | 6/1/2021 | AEP | 2016_2-7A | Appendix A | AEP:100 |  | KY |  | Transmission Line | Rebuild | IS | 16.8 | Baseline Load Growth Deliverability & Reliability | 12/18/2020 | 12/18/2020 | No | 11/2/2017 | 4/23/2019 | 100
b2880 | PJM WEST | Rebuild approximately 4.77 miles of the Cannonsburg – South Neal 69 kV line section utilizing 795 ACSR conductor (90 MVA rating, 83%) | Baseline | 69 | 17.39 | 6/1/2021 | AEP |  | Appendix A | AEP:100 |  | KY | Cannonsburg-South Neal | Transmission Line | Rebuild | IS | 12.5 | TO Criteria Violation | 12/13/2019 | 12/13/2019 | No | 5/31/2017 | 5/31/2017 | 100
b3087.1 | PJM WEST | Construct a new greenfield station to the west (~1.5 mi.) of the existing Fords Branch Station potentially in/near the new Kentucky Enterprise Industrial Park. . This new station will consist of 4 -138 kV breaker ring bus and two 30 MVA 138/34.5 kV transformers. The existing Fords Branch Station will be retired. | Baseline | 138 | 3.4 | 12/1/2018 | AEP |  | Appendix A | AEP:100 |  | KY | Fords Branch | Substation | Construct | IS | 2.8 | TO Criteria Violation | 10/1/2029 | 11/20/2024 | No | 11/29/2018 | 10/25/2019 | 100 |  | 12/1/2023
b3087.2 | PJM WEST | Construct approximately 5 miles of new double circuit 138 kV line in order to loop the new Fords Branch station into the existing Beaver Creek – Cedar Creek 138 kV circuit. | Baseline | 138 | 19.9 | 12/1/2018 | AEP |  | Appendix A | AEP:100 |  | KY | Fords Branch, Cedar Creek, Beaver Creeek | Transmission Line | Construct | IS | 19.9 | TO Criteria Violation | 9/21/2029 | 11/19/2024 | No | 11/29/2018 | 10/25/2019 | 100 |  | 12/1/2023
b3087.3 | PJM WEST | Remote end work will be required at Cedar Creek Station. | Baseline | 138 | 0.5 | 12/1/2018 | AEP |  | Appendix A | AEP:100 |  | KY | Cedar Creek | Substation | Modify | IS | 0.5 | TO Criteria Violation | 11/19/2024 | 11/19/2024 | No | 11/29/2018 | 10/25/2019 | 100 |  | 12/1/2023
b3087.4 | PJM WEST | Install 28.8MVar switching shunt at the new Fords Branch substation | Baseline | 138 | 0.5 | 12/1/2023 | AEP |  | Appendix A | AEP:100 |  | KY |  |  |  | IS | 0.5 | TO Criteria Violation | 11/19/2024 | 11/20/2024 | No | 10/25/2019 | 4/20/2020 | 100 |  | 12/1/2023
b3118.1 | PJM WEST | Expand existing Chadwick station and install a second 138/69 kV transformer at a new 138 kV bus tied into the Bellefonte – Grangston 138 kV circuit. The 69 kV bus will be reconfigured into a ring bus arrangement to tie the new transformer into the existing 69 kV via installation of four 3000A 63 kA 69 kV circuit breakers. | Baseline | 138/69 | 9.3 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Chadwick | Transformer | Install | IS | 9.3 | TO Criteria Violation | 11/19/2021 | 11/19/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3118.10 | PJM WEST | Replace 69 kV line risers (towards Chadwick) at Leach station | Baseline | 69 | 0.1 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Leach | Conductor | Replace | IS | 0.1 | TO Criteria Violation | 11/19/2021 | 11/9/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3118.2 | PJM WEST | Perform 138 kV remote end work at Grangston station. | Baseline | 138 | 0.5 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Grangston | Communication Equipment | Modify | IS | 0.5 | TO Criteria Violation | 11/19/2021 | 11/2/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3118.3 | PJM WEST | Perform 138 kV remote end work at Bellefonte station. | Baseline | 138 | 0.5 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Bellefonte | Communication Equipment | Modify | IS | 0.5 | TO Criteria Violation | 11/7/2022 | 11/2/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3118.4 | PJM WEST | Relocate the Chadwick – Leach 69 kV circuit within Chadwick station. | Baseline | 69 | 0.5 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Chadwick, Leach | Transmission Line | Modify | IS | 0.5 | TO Criteria Violation | 11/19/2021 | 11/19/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3118.5 | PJM WEST | Terminate the Bellefonte – Grangston 138 kV circuit to the Chadwick 138 kV bus | Baseline | 138 | 1.1 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Chadwick, Bellefonte, Grangston | Transmission Line | Modify | IS | 1.1 | TO Criteria Violation | 11/19/2021 | 10/23/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3118.6 | PJM WEST | Chadwick – Tri-State #2 138 kV circuit will be reconfigured within the station to terminate into the newly established 138 kV bus #2 at Chadwick due to construability aspects. | Baseline | 138 | 0.1 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Chadwick, Tri-State | Transmission Line | Modify | IS | 0.1 | TO Criteria Violation | 11/19/2021 | 11/17/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3118.7 | PJM WEST | Reconductor Chadwick-Leach and Chadwick-England Hill 69 kV lines with 795 ACSS conductor. Perform a LiDAR survey and a sag study to confirm that the reconductored circuits would maintain acceptable clearances. | Baseline | 69 | 3.3 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Chadwick, Leach, England Hill | Transmission Line | Reconductor | IS | 3.3 | TO Criteria Violation | 11/19/2021 | 11/19/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3118.9 | PJM WEST | Rebuild 336 ACSR portion of Leach - Miller S.S 69 kV line section (~0.3 miles) with 795 ACSS conductor. | Baseline | 69 | 1.5 | 6/1/2022 | AEP |  | Appendix A | AEP:100 |  | KY | Leach, Miller | Transmission Line | Rebuild | IS | 1.5 | TO Criteria Violation | 11/19/2021 | 5/31/2021 | No | 2/20/2019 | 5/20/2019 | 100
b3281 | PJM WEST | Install 138 kV circuit switcher on the 138/69 kV transformer #1 and 138/34.5 kV transformer #2 at Dewey. Install 138 kV 2000 A 40 kA breaker on Stanville line at Dewey 138 kV substation. | Baseline | 138 | 1.4 | 12/1/2025 | AEP |  | Appendix A | AEP:100 |  | KY | Dewey | Circuit Switcher | Install | IS | 1.4 | TO Criteria Violation | 11/5/2025 | 11/5/2025 | No | 2/17/2021 | 2/17/2021 | 100
b3283 | PJM WEST | Replace the existing Inez 138/69 kV 50 MVA autotransformer with a 138/69 kV 90 MVA autotransformer. | Baseline | 138/69 | 2.96 | 12/1/2025 | AEP |  | Appendix A | AEP:100 |  | KY | Inez | Transformer | Replace | IS | 2.96 | TO Criteria Violation | 12/1/2025 | 10/31/2022 | No | 2/17/2021 | 2/17/2021 | 100
b3288.1 | PJM WEST | Construct ~ 2.75 mi Orinoco - Stone 69 kV transmission line in the clear between Orinoco station and Stone station. | Baseline | 69 | 9.23 | 12/1/2025 | AEP |  | Appendix A | AEP:100 |  | KY | Orinoco - Stone | Transmission Line | Build | UC | 9.23 | TO Criteria Violation | 5/27/2027 |  | No | 1/15/2021 | 1/15/2021 | 75
b3288.2 | PJM WEST | Construct ~ 3.25 mi Orinoco – New Camp 69 kV transmission line in the clear between Orinoco station and New Camp station. | Baseline | 69 | 9.95 | 12/1/2025 | AEP |  | Appendix A | AEP:100 |  | KY | Orinoco – New Camp | Transmission Line | Build | UC | 9.95 | TO Criteria Violation | 11/8/2027 |  | No | 1/15/2021 | 1/15/2021 | 75
b3288.3 | PJM WEST | At Stone substation, circuit breaker A to remain in place and be utilized as T1 low side breaker, circuit breaker B to remain in place and be utilized as new Hatfield (via Orinoco and New Camp) 69 kV line breaker. Add new 69 kV circuit breaker E for Coleman Line exit. | Baseline | 69 | 0.66 | 12/1/2025 | AEP |  | Appendix A | AEP:100 |  | KY | Stone | Circuit Breaker | Install | UC | 0.66 | TO Criteria Violation | 5/27/2027 |  | No | 1/15/2021 | 1/15/2021 | 75
b3288.4 | PJM WEST | Reconfigure the New Camp 69 kV tap which includes access road improvements/installation, temporary wire and permanent wire work along with dead end structures installation. | Baseline | 69 | 0.45 | 12/1/2025 | AEP |  | Appendix A | AEP:100 |  | KY | New Camp | Substation | Modify | UC | 0.45 | TO Criteria Violation | 11/12/2027 |  | No | 1/15/2021 | 1/15/2021 | 75
b3288.5 | PJM WEST | At New Camp substation, rebuild the 69 kV bus, add 69 kV MOAB W and replace the 69 kV ground switch Z1 with a 69 kV circuit switcher on the New Camp transformer. | Baseline | 69 | 1.18 | 12/1/2025 | AEP |  | Appendix A | AEP:100 |  | KY | New Camp | Substation | Modify | UC | 1.18 | TO Criteria Violation | 11/8/2027 |  | No | 1/15/2021 | 1/15/2021 | 75
b3307 | PJM WEST | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69 kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12 kV 30 MVA transformer, replace 12 kV CB A and D. Retire existing Fleming substation. | Baseline | 138/69 | 21.1 | 12/1/2025 | AEP |  | Appendix A | AEP:100 |  | KY | Fleming subtation | Substation | Rebuild | UC | 21.1 | TO Criteria Violation | 6/25/2026 |  | No | 1/15/2021 | 1/15/2021 | 75
b3349 | PJM WEST | Replace Bellefonte 69 kV risers on the section between Bellefonte TR #3 and 69 kV Bus #2. | Baseline | 69 | 0.54 | 6/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | Bellefonte | Relay | Replace | UC | 0.54 | TO Criteria Violation | 6/10/2027 |  | No | 11/19/2021 | 11/19/2021 | 25
b3350.1 | PJM WEST | Replace overdutied 69 kV breakers C, G, I, Z, AB and JJ in place. The new 69 kV breakers to be rated at 3000 A 40 kA breakers. | Baseline | 69 | 2 | 6/1/2023 | AEP |  | Appendix A | AEP:100 |  | KY | Bellefonte | Circuit Breaker | Replace | UC | 2 | TO Criteria Violation | 6/10/2027 |  | Yes | 1/21/2022 | 1/21/2022 | 25
b3350.2 | PJM WEST | Upgrade remote end relaying at Point Pleasant, Coalton and South Point 69 kV substations. | Baseline | 69 | 0 | 6/1/2023 | AEP |  | Appendix A | AEP:100 |  | KY | Point Pleasant, Coalton and South Point 69KV subst | Relay | Upgrade | EP | 0 | TO Criteria Violation | 6/10/2027 |  | Yes | 1/21/2022 | 1/21/2022 | 15
b3352 | PJM WEST | Replace MOAB W, MOAB Y, line and bus side jumpers of both W and Y at 47th Street 69 kV station. Upgrade the 69 kV strain bus between MOABs W and Y to 795 KCM AAC. Change the connectors on the tap to MOAB X1 to accommodate the larger 795 KCM AAC. | Baseline | 69 | 0 | 6/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | 47th 69kV station | Disconnect Switch | Replace | IS | 0 | TO Criteria Violation | 12/1/2025 | 4/15/2025 | No | 11/19/2021 | 11/19/2021 | 100
b3353.1 | PJM WEST | Allen substation: Rebuild Allen station to the northwest of its current footprint utilizing a standard air-insulated substation with equipment raised by 7’ concrete platforms and control house raised by a 10’ platform to mitigate flooding concerns. Install five 69 kV 3000A 40 kA circuit breakers in a ring bus (operated at 46 kV) configuration with a 13.2 MVAR capacitor bank. Existing Allen station will be retired (does not include the distribution cost). Distribution scope of work: Install 69/46 kV-12 kV 20 MVA transformer along with 2-12 kV breakers on 7’ concrete platforms (conversion of S2405.1). | Baseline | 46 | 10.55 | 12/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | Allen | Substation | Rebuild | EP | 10.55 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.2 | PJM WEST | Allen-East Prestonsburg: A 0.20 mile segment of this 46 kV line will be relocated to the new station (SN/SE/WN/WE: 53/61/67/73MVA). (Conversion of S2405.2) | Baseline | 46 | 0.33 | 12/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | Allen – East Prestonsburg | Transmission Line | Modify | EP | 0.33 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.3 | PJM WEST | McKinney-Allen: The new line extension will walk around the south and east sides of the existing Allen station to the new Allen station being built in the clear. A short segment of new single circuit 69 kV line and a short segment of new double circuit 69 kV line (both operated at 46 kV) will be added to the line to tie into the new Allen station bays. (Conversion of S2405.3) | Baseline | 46 | 1.95 | 12/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | McKinney – Allen | Transmission Line | Install | EP | 1.95 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.4 | PJM WEST | Stanville-Allen: A segment of this line will have to be relocated to the new station (SN/SE/WN/WE: 50/50/63/63MVA). (Conversion of S2405.4) | Baseline | 46 | 0.17 | 12/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | Stanville – Allen | Transmission Line | Modify | EP | 0.17 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.5 | PJM WEST | Allen-Prestonsburg: 0.25 mile segment of this existing single circuit will be relocated. The relocated line segment will require construction of one custom self-supporting double circuit dead-end structure and single circuit suspension structure. A short segment of new double circuit 69 kV line (energized at 46 kV) will be added to tie into the new Allen station bays, which will carry Allen-Prestonsburg 46 kV and Allen-East Prestonsburg 46 kV lines. A temporary 0.15 mile section double circuit line will be constructed to keep Allen-Prestonsburg and Allen-East Prestonsburg 46 kV lines energized during construction. (Conversion of S2405.5) | Baseline | 46 | 2.66 | 12/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | Allen – Prestonsburg | Transmission Line | Modify | EP | 2.66 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.6 | PJM WEST | Remote end work will be required at Prestonsburg, Stanville and McKinney stations. (Conversion of S2405.6) | Baseline | 46 | 0.34 | 12/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | Prestonsburg, Stanville, McKinney | Substation | Modify | EP | 0.34 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3360 | PJM WEST | Replace Thelma Transformer #1 with a 138/69/46 kV 130/130/90 MVA transformer and replace 46 kV risers and relaying toward Kenwood substation. Existing TR#1 to be used as spare. | Baseline | 69 | 3.54 | 12/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | Thelma | Transformer | Replace | EP | 3.54 | TO Criteria Violation | 11/20/2026 |  | No | 11/19/2021 | 11/19/2021 | 15
b3361 | PJM WEST | Rebuild Prestonsburg - Thelma 46kV circuit connecting though Kenwood station, approximately 12.7 miles. Retire Jenny Wiley SS and Van Lear SS. | Baseline | 46 | 63.6 | 12/1/2026 | AEP |  | Appendix A | AEP:100 |  | KY | Prestonsburg - Thelma | Transmission Line | Rebuild | EP | 63.6 | TO Criteria Violation | 12/16/2027 |  | No | 11/19/2021 | 5/16/2025 | 15 |  | 12/16/2027
b3736.1 | PJM WEST | Establish 69kV bus and new 69 kV line CB at Dorton substation. | Baseline | 69 | 1.13 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Dorton | Bus | Construct | EP | 1.13 | TO Criteria Violation | 3/16/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.10 | PJM WEST | Henry Clay S.S Retirement: | Baseline | 46 | 0.3 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Henry Clay | Substation | Retire | EP | 0.3 | TO Criteria Violation | 9/1/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.11 | PJM WEST | Cedar Creek substation work | Baseline | 46 | 0.44 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Cedar Creek | Substation | Modify | EP | 0.44 | TO Criteria Violation | 1/9/2030 |  | No | 11/18/2022 | 11/18/2022 | 0
b3736.12 | PJM WEST | Breaks substation retire 46kV equipment: | Baseline | 46 | 0.25 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Breaks | Substation | Retire | EP | 0.25 | TO Criteria Violation | 5/18/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.13 | PJM WEST | Retire Pike 29 SS and Rob Fork SS | Baseline | 46 | 0.42 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Pike 29, Rob Fork | Substation | Retire | EP | 0.42 | TO Criteria Violation | 1/9/2030 |  | No | 11/18/2022 | 11/18/2022 | 0
b3736.14 | PJM WEST | Serve Pike 29 and Rob Fork customers from nearby 34kV Distribution sources. | Baseline | 46 | 0 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Pike 29 load, Rob Fork load | Distribution Line | Provide | EP | 0 | TO Criteria Violation | 1/9/2030 |  | No | 11/18/2022 | 11/18/2022 | 0
b3736.15 | PJM WEST | Poor Bottom substation install | Baseline | 69 | 0 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Poor Bottom | Substation | Install | EP | 0 | TO Criteria Violation | 3/16/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.16 | PJM WEST | Henry Clay 46kV substation retirement | Baseline | 46 | 0 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Henry Clay | Substation | Retire | EP | 0 | TO Criteria Violation | 3/16/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.17 | PJM WEST | New Draffin 69kV substation install | Baseline | 69 | 0 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | New Draffin | Substation | Install | EP | 0 | TO Criteria Violation | 3/23/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.18 | PJM WEST | Draffin 46kV substation retirement | Baseline | 46 | 0 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Draffin | Substation | Retire | EP | 0 | TO Criteria Violation | 9/1/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.2 | PJM WEST | At Breaks substation, reuse 72kV breaker A as the new 69kV line breaker. | Baseline | 69 | 0.71 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Breaks | Circuit Breaker | Modify | EP | 0.71 | TO Criteria Violation | 5/18/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.3 | PJM WEST | Rebuild ~16.7 mi Dorton – Breaks 46kV line to 69kV | Baseline | 69 | 58.52 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Dorton - Breaks | Transmission Line | Rebuild | EP | 58.52 | TO Criteria Violation | 3/16/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.4 | PJM WEST | Retire ~17.2 mi Cedar Creek – Elwood 46kV circuit. | Baseline | 46 | 11.15 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Cedar Creek - Elwood | Transmission Line | Retire | EP | 11.15 | TO Criteria Violation | 8/1/2030 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.5 | PJM WEST | Retire ~ 6.2 mi Henry Clay – Elwood 46kV line section. | Baseline | 46 | 4.3 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Henry Clay - Elwood | Transmission Line | Retire | EP | 4.3 | TO Criteria Violation | 11/8/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.6 | PJM WEST | Retire Henry Clay 46 kV substation and replace with Poor Bottom 69 kV station. Install a new 0.7 mi double circuit extension to Poor Bottom 69kV. | Baseline | 69 | 3.42 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Henry clay, Poor Bottom | Substation | Replace | EP | 3.42 | TO Criteria Violation | 3/16/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.7 | PJM WEST | Retire Draffin substation and replace with a new substation. Install a new 0.25 mi double circuit extension to New Draffin substation. | Baseline | 69 | 2.01 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Draffin, New Darffin | Substation | Replace | EP | 2.01 | TO Criteria Violation | 9/1/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.8 | PJM WEST | Remote End work at Jenkins substation | Baseline | 69 | 0.03 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Jenkins | Substation | Modify | EP | 0.03 | TO Criteria Violation | 3/16/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3736.9 | PJM WEST | Provide Transition fiber to Dorton, Breaks, Poor Bottom, Jenkins and New Draffin substations | Baseline | 69 | 0.41 | 12/1/2027 | AEP |  | Appendix A | AEP:100 |  | KY | Dorton, Breaks, Poor bottom, Jenkins, New Draffin | Communication Equipment | Provide | EP | 0.41 | TO Criteria Violation | 3/16/2028 |  | No | 11/18/2022 | 11/18/2022 | 15
b3787.1 | PJM WEST | Install a CCVT on three-phase stand and remove the single phase existing CCVT on the 69 kV Coalton to Bellefonte line exit. The existing CCVT is mounted to lattice on a single-phase CCVT stand, which will be replaced with the three-phase CCVT stand. The line riser between line disconnect and line takeoff is being replaced. This remote end work changes the MLSE of the line section between Coalton-Princess 69 kV line section. | Baseline | 69 | 0 | 12/1/2028 | AEP |  | Appendix A | AEP:100 |  | KY | Coalton--(38.3634,-82.7586)-{274FA529-5A8D-4542-9893-5AD1E756E319} | Relay | Replace | EP | 0 | TO Criteria Violation | 12/1/2028 |  | No | 11/17/2023 | 11/17/2023 | 0
b3847.1 | PJM WEST | Add a 765 kV breaker at Baker station for the reactor on the Broadford 765 kV line. | Baseline | 765 | 23.36 | 6/1/2024 | AEP | Immediate Need | Appendix A | AEP:70.68,EKPC:8.12,PEPCO:21.20 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41 | KY | Baker | Circuit Breaker | Install | EP | 23.36 | Operational Performance | 6/25/2027 |  | Yes | 6/5/2024 | 6/5/2024 | 15
b3948.1 | PJM WEST | Replace the existing 9.6 MVar 69kV capacitor bank at Johns Creek station with a 17.2 MVar capacitor bank. Circuit switcher "AA" will also be replaced. | Baseline | 138 | 1.48 | 4/15/2030 | AEP |  |  |  |  | KY | Johns Creek | Capacitor | Install | PL | 1.48 | TO Criteria Violation | 4/15/2030 |  | No | 11/14/2025 | 11/14/2025 | 0
b3951.1 | PJM WEST | To solve the voltage violations, a 69kV circuit switcher and a 11.5 MVar capacitor bank will be installed on the 69kV bus at Falcon station. Falcon station will need to be expanded to fit the capacitor bank. | Baseline | 69 | 3.35 | 4/15/2030 | AEP |  |  |  |  | KY | Falcon | Capacitor | Install | PL | 3.35 | TO Criteria Violation | 4/15/2030 |  | No | 11/14/2025 | 11/14/2025 | 0
b3974.1 | PJM WEST | Replace circuit breaker R with a new 69kV, 40 kA circuit breaker. | Baseline | 161 | 0.85 | 6/1/2030 | AEP |  |  |  |  | KY | Hazard | Circuit Breaker | Replace | PL | 0.85 | Short Circuit | 6/1/2030 |  | No | 11/14/2025 | 11/14/2025 | 0
s0354 | PJM WEST | Rebuild 2.83 miles of 69 kV line from Fleming Station to Jenkins Station (Kentucky) using 1033 MCM ACSR conductor | Supplemental | 69 | 22.5 |  | AEP |  |  |  |  | KY | Fleming - Jenkins | Transmission Line | Rebuild | IS | 22 | Equipment Material Condition, Performance and Risk | 10/30/2011 | 12/30/2011 | No | 10/27/2011 | 10/27/2011 | 100
s0357 | PJM WEST | Retire the SVC at Beaver Creek 138 kV station | Supplemental | 138 | 4.4 |  | AEP |  |  |  |  | KY | Beaver Creek | Reactive Device | Retire | IS | 4.4 | Equipment Material Condition, Performance and Risk | 12/30/2013 | 12/30/2013 | No | 10/27/2011 | 10/27/2011 | 100
s0406 | PJM WEST | Replace the MOAB switch at Morgan Fork 138 kV station with a 138 kV circuit breaker towards Hays Branch 138 kV metering station | Supplemental | 138 | 1 |  | AEP |  |  |  |  | KY | Morgan Fork | Disconnect Switch | Replace | IS | 1 | Operational Flexibility and Efficiency | 12/30/2013 | 12/31/2013 | No | 3/19/2012 | 3/19/2012 | 100
s0412 | PJM WEST | Rebuild the existing Paintsville 69 kV Station as a new station that will be called Mayo Trail station | Supplemental | 69 | 5.19 |  | AEP |  |  |  |  | KY | Paintsville | Substation | Rebuild | IS | 5.19 | Equipment Material Condition, Performance and Risk |  | 8/20/2011 | No | 3/19/2012 | 3/19/2012 | 100
s0466 | PJM WEST | Add two 138 kV breakers at Stone Station and one 138 kV breaker at Johns Creek Station. Add a circuit switcher at Johns Creek and Stone Station | Supplemental | 138 | 3.5 |  | AEP |  |  |  |  | KY | Stone and Johns Creek | Circuit Breaker | Add | IS | 3.5 | Operational Flexibility and Efficiency | 12/31/2019 | 12/19/2019 | No | 8/29/2012 | 8/29/2012 | 100
s1301 | PJM WEST | Replace circuit breakers at Chadwick, Leach, England Hill and Keonva | Supplemental | 138/69 | 9.84 |  | AEP |  |  |  |  | KY,WV | Chadwick, Leach, England Hill, Kenova | Circuit Breaker | Replace | IS | 10.94 | Equipment Material Condition, Performance and Risk | 6/7/2017 | 6/7/2017 | No | 5/31/2017 | 5/31/2017 | 100
s1301.1 | PJM WEST | At Chadwick 138kV station, install two 138 kV circuit breakers in place of the MOAB switches “V” and “Y”. | Supplemental | 138 | 0 |  | AEP |  |  |  |  | KY | Chadwick | Circuit Breaker | Replace | IS | 0 | Equipment Material Condition, Performance and Risk | 6/7/2017 | 6/7/2017 | No | 5/31/2017 | 5/31/2017 | 100
s1301.2 | PJM WEST | Replace 69kV circuit breakers C and D with 3000 A 40 kA breakers | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | Chadwick | Circuit Breaker | Replace | IS | 0 | Equipment Material Condition, Performance and Risk | 6/7/2017 | 6/7/2017 | No | 5/31/2017 | 5/31/2017 | 100
s1301.3 | PJM WEST | At Leach station, replace 69 kV breaker E with a 3000 A 40 kA breaker. | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | Leach | Circuit Breaker | Replace | IS | 0 | Equipment Material Condition, Performance and Risk | 6/7/2017 | 6/7/2017 | No | 5/31/2017 | 5/31/2017 | 100
s1301.4 | PJM WEST | At England Hill, replace 69 kV circuit breakers A and B with 3000 A 40 kA breakers. | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | England Hill | Circuit Breaker | Replace | IS | 0 | Equipment Material Condition, Performance and Risk | 6/7/2017 | 6/7/2017 | No | 5/31/2017 | 5/31/2017 | 100
s1412 | PJM WEST | Hazard station | Supplemental | 138 | 20 |  | AEP |  |  |  |  | KY |  |  |  | IS | 22.65 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 12/19/2023 | 12/19/2023 | No | 12/18/2017 | 6/15/2021 | 100
s1412.1 | PJM WEST | Install a new 3000A 40 kA 138kV circuit breaker at Hazard station on the line exit towards Beckham station. Add a 138kV circuit switcher to the high side of transformer #4 at Hazard station. | Supplemental | 138 | 0 |  | AEP |  |  |  |  | KY | Hazard | Circuit Breaker | Install | IS | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 12/19/2022 | 12/29/2022 | No | 12/18/2017 | 12/18/2017 | 100
s1412.2 | PJM WEST | Replace 138kV capacitor bank and switcher BB with a new switcher and 43.2 MVAR capacitor bank at Hazard station. | Supplemental | 138 | 0 |  | AEP |  |  |  |  | KY | Hazard | Capacitor | Replace | IS | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 12/15/2023 | 12/29/2022 | No | 12/18/2017 | 12/18/2017 | 100
s1412.3 | PJM WEST | Replace 138/69 kV transformers #1 and #2 with new 138/69 kV 130 MVA transformers with 138kV circuit switchers on the high side and 3000A 40 kA 69 kV breakers on the low side at Hazard station. | Supplemental | 138/69 | 0 |  | AEP |  |  |  |  | KY | Hazard | Transformer | Replace | IS | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 12/19/2022 | 12/29/2022 | No | 12/18/2017 | 12/18/2017 | 100
s1412.4 | PJM WEST | Replace 69 kV circuit breakers S, E, and F with 3000A 40 kA 69 kV circuit breakers and with a bus tie 3000A 69 kV circuit breaker being installed between the existing 69 kV box bays at Hazard station. | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | Hazard | Circuit Breaker | Replace | IS | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 12/15/2023 | 12/15/2023 | No | 12/18/2017 | 12/18/2017 | 100
s1412.5 | PJM WEST | Retire existing 69 kV capacitor bank and switcher CC. 69 kV capacitor bank and switcher AA will be retired | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | Hazard | Capacitor | Replace | IS | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 12/15/2023 | 12/15/2023 | No | 12/18/2017 | 6/15/2021 | 100
s1412.8 | PJM WEST | Address Safety and access issues associated with existing equipment platforms and drainage issues at the station at Hazard station. | Supplemental | 138/69 | 0 |  | AEP |  |  |  |  | KY | Hazard | Substation | Install | IS | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 12/15/2023 | 12/15/2023 | No | 12/18/2017 | 6/15/2021 | 100
s1417 | PJM WEST | Install two new 138kV circuit breakers at Beckham station placed on the line exists towards Hazard and Beaver Creek stations. The existing ground MOAB scheme on the high side of the distribution transformer will be replaced by a 138kV circuit switcher | Supplemental | 138 | 1.13 |  | AEP |  |  |  |  | KY | Beckham | Circuit Breaker | Install | IS | 1.2 | Operational Flexibility and Efficiency | 12/1/2017 | 11/28/2017 | No | 12/18/2017 | 12/18/2017 | 100
s1524 | PJM WEST | Replace existing 1200 A 12.5 kA 46 kV circuit breaker ‘B’ with a new 3000 A 40 kA 46 kV circuit breaker. Replace existing 1200 A 21 kA 69 kV circuit breaker ‘D’ with a new 3000 A 40 kA 69 kV circuit breaker. Replace existing 1200 A 30 kA 138 kV cap switcher ‘BB’ with a new 650 A 31.5 kA 138 kV cap switcher. | Supplemental | 46 | 1.19 |  | AEP |  |  |  |  | KY | Thelma | Circuit Breaker | Replace | IS | 1.7 | Equipment Material Condition, Performance and Risk | 6/5/2018 | 6/5/2018 | No | 2/14/2018 | 3/9/2018 | 100
s1547 | PJM WEST | Replace existing 90 MVA Leslie 161/69 kV transformer with a new 130 MVA 161/69 kV transformer. A second 161/69 kV transformer will be purchased as a non--switchable spare on site. Replace Leslie 161 kV 3000 A 50 kA circuit breaker “K” with a new 3000 A 40 kA 161 kV circuit breaker. | Supplemental | 161/69 | 6.3 |  | AEP |  |  |  |  | KY | Leslie | Transformer | Replace | IS | 6.3 | Equipment Material Condition, Performance and Risk | 11/27/2024 | 12/22/2024 | No | 3/9/2018 | 3/27/2018 | 100
s1562 | PJM WEST | Replace the existing 138/46 kV 45 MVA transformer bank with a new 138/69/46 kV 90 MVA transformer bank at Dorton Station. A lowside 69 kV circuit breaker (operated at 46 kV) will be added to the transformer. | Supplemental | 138/69 | 2.5 |  | AEP |  |  |  |  | KY | Dorton | Transformer | Replace | IS | 2.5 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 8/1/2019 | 7/23/2019 | No | 2/14/2018 | 3/9/2018 | 100
s1572 | PJM WEST | Replace the failed 138/69/46 kV 50 MVA transformer bank at Stone station with a new 138/69/46 kV 90 MVA transformer bank. Replace circuit breaker “A” with a new 69 kV 3000 A 40 kA circuit breaker. Replace circuit breaker “B” with a new 69 kV 3000 A 40 kA circuit breaker. | Supplemental | 138/69 | 3.3 |  | AEP |  |  |  |  | KY | Stone | Transformer | Replace | IS | 3.3 | Equipment Material Condition, Performance and Risk | 12/31/2019 | 8/28/2017 | No | 2/14/2018 | 3/9/2018 | 100
s1583 | PJM WEST | At Baker Station, replace the existing 765 kV 3000 A 50 kA circuit breakers “Q”, “Q2”, and “P2” with new 765 kV 4000 A 63 kA breakers. Install a new 345 kV 3000 A 63 kA breaker to complete the “J” string. Replace the existing 600 MVA transformer #200 with a new 345/138 kV 675 MVA unit that will be relocated from the 345 kV bus #2 position to the newly created position between the existing breakers “J” and the newly installed breaker “J1”. | Supplemental | 765/345 | 26.9 |  | AEP |  |  |  |  | KY | Baker | Circuit Breaker | Modify | IS | 26.9 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 11/20/2018 | 12/6/2018 | No | 3/8/2018 | 4/5/2018 | 100
s1687.1 | PJM WEST | Construct a new greenfield station named Moore Hollow. Six 138 kV CBs (3000 A 40 kA) will be installed as well as a 138/34.5 kV transformer (30 MVA) and a 57.6 MVAR capacitor at the station. | Supplemental | 138 | 13.6 |  | AEP |  |  |  |  | KY | Moore Hollow | Substation | Build | IS | 13.6 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 1/12/2023 | 12/22/2022 | No | 7/27/2018 | 8/31/2018 | 100
s1687.10 | PJM WEST | Construct 3.4 mile 138 kV line between Princess and Moore Hollow stations. | Supplemental | 138 | 11.5 |  | AEP |  |  |  |  | KY | Princess, Moore Hollow | Transmission Line | Build | EP | 11.5 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 6/23/2023 |  | No | 7/27/2018 | 8/31/2018 | 15
s1687.2 | PJM WEST | Construct a 2.7 mile 138 kV line extension between Moore Hollow and Kentucky Electric Steel. At this time the existing KES metering structure will be retired due to the announced closure of the KES plant. | Supplemental | 138 | 8.4 |  | AEP |  |  |  |  | KY | Moore Hollow, Kentucky Electric Steel | Transmission Line | Build | EP | 8.4 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 6/23/2023 |  | No | 7/27/2018 | 8/31/2018 | 15
s1687.3 | PJM WEST | At Chadwick Station, remote end relaying work will be required. | Supplemental | 138 | 0.4 |  | AEP |  |  |  |  | KY | Chadwick | Relay | Modify | EP | 0.4 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 6/23/2023 |  | No | 7/27/2018 | 8/31/2018 | 15
s1687.4 | PJM WEST | Construct a new greenfield 138/19 kV station, named Ramey, tapping the Bellefonte - Grangston 138 kV circuit. Four 138 kV CBs (3000 A 40 kA) will be installed as well as a 138/19 kV transformer (25 MVA). AEP already owns the land at the proposed Ramey station site. | Supplemental | 138/13 | 0 |  | AEP |  |  |  |  | KY | Bellefonte, Grangston, Ramey | Substation | Build | EP | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 6/23/2023 |  | No | 7/27/2018 | 8/31/2018 | 5
s1687.5 | PJM WEST | Construct a new 2.8 mile 138 kV extension from Ramey to the existing Bellefonte - Coalton line. | Supplemental | 138 | 10.5 |  | AEP |  |  |  |  | KY | Ramey, Bellefonte, Grangson | Transmission Line | Build | EP | 10.5 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 12/8/2023 |  | No | 7/27/2018 | 8/31/2018 | 15
s1687.6 | PJM WEST | Convert the existing Bellefonte to Coalton 69 kV line between Bellefonte and Princess to 138 kV (line is built to 138 kV standards). | Supplemental | 138 | 3.8 |  | AEP |  |  |  |  | KY | Bellefonte, Coalton | Transmission Line | Modify | EP | 3.8 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 12/8/2023 |  | No | 7/27/2018 | 8/31/2018 | 15
s1687.8 | PJM WEST | Convert Hoods Creek station to 138 kV by rebuilding the station in the adjacent lot with a 138/12 kV XF. | Supplemental | 138/34.5 | 0 |  | AEP |  |  |  |  | KY | Hoods Creek | Substation | Rebuild | EP |  | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 12/8/2023 |  | No | 7/27/2018 | 8/31/2018 | 15
s1687.9 | PJM WEST | Convert Princess station to 138 kV by installing five 138 kV CBs (3000 A 40 kA), a 138/69 kV XF (to Coalton), and a 138/34.5 kV XF. | Supplemental | 138 | 5.7 |  | AEP |  |  |  |  | KY | Princess | Substation | Upgrade | IS | 5.7 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency,Customer Service | 12/31/2020 | 12/19/2021 | No | 7/27/2018 | 8/31/2018 | 100
s2188.1 | PJM WEST | Construct 10.3 miles of single circuit 138kV from Soft Shell to Garrett picking up Salt Lick Co-op via Snag Fork along the way. Complete associated remote end relaying. | Supplemental | 138 | 35.3 |  | AEP |  |  |  |  | KY | Soft Shell - Garrett | Transmission Line | Construct | UC | 35.3 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 5/12/2027 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.10 | PJM WEST | Install a 138kV breaker (3000A 40kA) with an exit towards Garrett station (via Snag Fork) at Softshell substation. | Supplemental | 138 | 0 |  | AEP |  |  |  |  | KY | Softshell | Circuit Breaker | Install | IS | 0.8 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 11/15/2024 | 6/14/2024 | No | 2/21/2020 | 2/21/2020 | 100
s2188.11 | PJM WEST | Retire the ~25 miles of the 46kV Beaver Creek – McKinney #1 46 KV circuit. Retire Spring Fork Tap. | Supplemental | 46 | 17.3 |  | AEP |  |  |  |  | KY | Beaver Creek – McKinney #1 | Transmission Line | Remove | UC | 17.3 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 2/17/2028 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.2 | PJM WEST | Construct ~3 miles of single circuit 138kV from the Eastern station to Garrett station. A short extension will be required from the new station to the existing Hays Branch metering point. Construct short extension to existing Morgan Fork – Hays Branch 138 kV circuit from Eastern station | Supplemental | 138 | 11.5 |  | AEP |  |  |  |  | KY | Eastern station - Garrett, Morgan Fork - Hays Bran | Transmission Line | Construct | UC | 11.5 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 5/12/2027 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.3 | PJM WEST | Double circuit cut into existing Hays Branch - Morgan Fork line to tie into new Eastern Station. | Supplemental | 138 | 1.3 |  | AEP |  |  |  |  | KY | Hays Branch - Morgan Fork | Transmission Line | Modify | UC | 1.3 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 10/13/2027 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.4 | PJM WEST | Construct ~1.4 mi of double circuit 138kV line between Eastern and the tap point on the Morgan Fork-Hays Branch line. The proposed line will establish a direct feed to Hays Branch from Eastern and establishing a through path line between Eastern and Morgan Fork.. | Supplemental | 138 | 1.6 |  | AEP |  |  |  |  | KY | Hays Branch S.S – Eastern | Transmission Line | Construct | UC | 1.6 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 9/17/2027 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.5 | PJM WEST | New relaying at Hays Branch to accommodate new line from Eastern station | Supplemental | 138 | 0.5 |  | AEP |  |  |  |  | KY | Hays Branch | Circuit Switcher | Install | UC | 0.5 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 10/13/2027 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.6 | PJM WEST | Expand the Garrett station,Install a straight bus arrangement with two 138kV breakers and a circuit switcher on the high side of the transformer, 138/12kV 30MVA transformer | Supplemental | 138/12 | 0 |  | AEP |  |  |  |  | KY | Garrett | Substation | Modify | UC | 5.8 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 5/12/2027 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.7 | PJM WEST | Establish a new 138 kV substation Eastern south of the existing Hays Branch station. Install three 138kV breakers (3000A 40kA) at the new Eastern station in a ring bus arrangement. | Supplemental | 138 | 6 |  | AEP |  |  |  |  | KY | Eastern | Substation | Build | UC | 6 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 5/12/2027 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.8 | PJM WEST | Establish Snag Fork S.S. Install a 3 way phase over phase motorized (automated) switching structure near Saltlick to serve the EKPC co-op. | Supplemental | 138 | 1.1 |  | AEP |  |  |  |  | KY | Snag Fork S.S. | Circuit Switcher | Install | UC | 1.1 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 5/11/2026 |  | No | 2/21/2020 | 2/21/2020 | 25
s2188.9 | PJM WEST | Move the existing 69kV rated CB G to the Beaver Creek – McKinney #2 circuit exit at McKinney substation. | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | Beaver Creek – McKinney #2 | Circuit Breaker | Modify | UC | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 11/12/2027 |  | No | 2/21/2020 | 2/21/2020 | 25
s2200.1 | PJM WEST | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Install a 2MW BESS at Middle Creek substation. | Supplemental | 46 | 9.7 |  | AEP |  |  |  |  | KY | Middle Creek | Substation | Build | On Hold | 9.7 | Equipment Material Condition, Performance and Risk | 11/28/2025 |  | No | 1/17/2020 | 1/17/2020 | 0
s2200.2 | PJM WEST | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Rebuild ~8.5 miles of 46 kV line between Prestonsburg and Middle Creek station. | Supplemental | 46 | 25.5 |  | AEP |  |  |  |  | KY | Prestonsburg - Middle Creek | Transmission Line | Rebuild | On Hold | 25.5 | Equipment Material Condition, Performance and Risk | 11/28/2025 |  | No | 1/17/2020 | 1/17/2020 | 0
s2200.3 | PJM WEST | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Retire ~14.5 miles of 46 kV line between Falcon and Middle Creek. | Supplemental | 46 | 6.1 |  | AEP |  |  |  |  | KY | Falcon - Middle Creek | Transmission Line | Remove | On Hold | 6.1 | Equipment Material Condition, Performance and Risk | 12/31/2030 |  | No | 1/17/2020 | 1/17/2020 | 0
s2219 | PJM WEST | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12kV 30 MVA transformer, Replace 12 kV CB A and D. Retire existing Fleming substation. | Supplemental | 138/69/12 | 21.1 |  | AEP |  |  |  |  | KY | Fleming | Substation | Rebuild | UC | 21.1 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 6/25/2026 |  | No | 3/19/2020 | 3/19/2020 | 75
s2220 | PJM WEST | Install 138/12 kV 25 MVA transformer on the Cedar Creek 138kV Bus #1 to serve the new load. | Supplemental | 138/12 | 3.5 |  | AEP |  |  |  |  | KY | Cedar Creek | Transformer | Install | IS | 3.5 | Customer Service | 3/29/2020 | 10/25/2019 | No | 3/19/2020 | 3/19/2020 | 100
s2251.1 | PJM WEST | Establish a new station (Tygart) and install a 69/12 kV 25 MVA transformer and two 69kV breakers. | Supplemental | 69/12 | 2.6 |  | AEP |  |  |  |  | KY | Tygart | Substation | Build | IS | 2.6 | Customer Service | 6/5/2025 | 12/21/2023 | No | 4/20/2020 | 4/20/2020 | 100
s2251.2 | PJM WEST | Retire Siloam Station. | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | Siloam | Substation | Remove | IS | 0 | Customer Service | 6/5/2025 | 7/3/2025 | No | 4/20/2020 | 4/20/2020 | 100
s2251.3 | PJM WEST | Remote end relaying at Millbrook Park to coordinate with new breakers. | Supplemental | 69 | 0.4 |  | AEP |  |  |  |  | KY | Millbrook Park | Relay | Modify | EP | 0.4 | Customer Service | 3/2/2028 |  | No | 4/20/2020 | 4/20/2020 | 0
s2251.4 | PJM WEST | Tap the 69kV Central Portsmouth – Millbrook Park line and install 3 custom T-line structures due to proximity to the Railroad. | Supplemental | 69 | 0.9 |  | AEP |  |  |  |  | KY | Central Portsmouth – Millbrook Park | Transmission Line | Modify | UC | 0.9 | Customer Service | 10/7/2027 |  | No | 4/20/2020 | 4/20/2020 | 25
s2253.1 | PJM WEST | Construct a new station (Raccoon) and install a 138/34.5kV 30 MVA transformer and 138 kV MOABs. | Supplemental | 138/34.5 | 0 |  | AEP |  |  |  |  | KY | Raccoon | Substation | Build | IS | 0 | Customer Service | 11/18/2021 | 11/18/2021 | No | 4/20/2020 | 4/20/2020 | 100
s2253.2 | PJM WEST | Install 0.2 mi double circuit extension from the Cedar Creek – Johns Creek 138kV circuit to cut the line into Raccoon Station. | Supplemental | 138 | 1.3 |  | AEP |  |  |  |  | KY | Cedar Creek – Johns Creek, Raccoon | Transmission Line | Install | IS | 1.3 | Customer Service | 11/18/2021 | 11/18/2021 | No | 4/20/2020 | 4/20/2020 | 100
s2281.1 | PJM WEST | At Inez station, replace Breakers B, B2, C and C1. Install three new 138kV breakers and create third string in the existing breaker and half configuration. Replace 138/69kV Inez Transformer #1 with a 138/69kV/12kV 90 MVA autotransformer. Move the new Inez 139/69/12kV Transformer #1 and Martiki 138kV feed to the new string. Install Breaker B1 towards Johns Creek to complete the string. Installation of Breaker B1 and the third string addresses dissimilar zones of protection between the #1 bus and 20+ mile Inez to Johns Creek 138 kV circuit and dissimilar zones of protection between the 138 kV bus #2, 138/69 kV transformer #1, and the 138 kV circuit to the Martiki coal service point. Replace Cap bank switchers CS-BB and CS-CC with 138kV circuit breakers. Replace obsolete relays at Inez substation. Retire 69kV Capacitor Bank and the circuit switcher AA. | Supplemental | 138/69/12 | 10.7 |  | AEP |  |  |  |  | KY | Inez | Substation | Replace | IS | 10.7 | Equipment Material Condition, Performance and Risk | 11/18/2022 | 12/14/2022 | No | 6/19/2020 | 6/19/2020 | 100
s2281.2 | PJM WEST | Remote end work at Big Sandy, Logan, Sprigg and Dewey substations. | Supplemental | 138 | 1.7 |  | AEP |  |  |  |  | KY | Big Sandy, Logan, Sprigg and Dewey | Relay | Upgrade | IS | 1.7 | Equipment Material Condition, Performance and Risk | 11/18/2022 | 2/22/2023 | No | 6/19/2020 | 6/19/2020 | 100
s2405.1 | PJM WEST | Allen Substation: Rebuild Allen Station to the northwest of its current footprint utilizing a standard air-insulated substation with equipment raised by 7’ concrete platforms and control house raised by a 10’ platform to mitigate flooding concerns. Install five 69 kV 3000A 40 kA circuit breakers in a ring bus (operated at 46kV) configuration with a 13.2 MVAR capacitor bank. Existing Allen station will be retired. | Supplemental | 46 | 10.55 |  | AEP |  |  |  |  | KY | Allen | Substation | Rebuild | Cancelled | 10.55 | Equipment Material Condition, Performance and Risk | 12/31/2023 |  | No | 10/16/2020 | 10/16/2020 | 0
s2405.2 | PJM WEST | Allen – East Prestonsburg: A 0.20 mile segment of this 46 kV line will be relocated to the new station. (SN/SE/WN/WE: 53/61/67/73MVA). | Supplemental | 46 | 0.33 |  | AEP |  |  |  |  | KY | Allen – East Prestonsburg | Transmission Line | Modify | Cancelled | 0.33 | Equipment Material Condition, Performance and Risk | 12/31/2023 |  | No | 10/16/2020 | 10/16/2020 | 0
s2405.3 | PJM WEST | McKinney – Allen: The new line extension will walk around the south and east sides of the existing Allen Station to the new Allen Station being built in the clear. A short segment of new single circuit 69kV line and a short segment of new double circuit 69kV line (both operated at 46 kV) will be added to the line to tie into the new Allen Station bays. | Supplemental | 46 | 1.95 |  | AEP |  |  |  |  | KY | McKinney – Allen | Transmission Line | Install | Cancelled | 1.95 | Equipment Material Condition, Performance and Risk | 12/31/2023 |  | No | 10/16/2020 | 10/16/2020 | 0
s2405.4 | PJM WEST | Stanville – Allen: A segment of this line will have to be relocated to the new station (SN/SE/WN/WE: 50/50/63/63MVA). | Supplemental | 46 | 0.17 |  | AEP |  |  |  |  | KY | Stanville – Allen | Transmission Line | Modify | Cancelled | 0.17 | Equipment Material Condition, Performance and Risk | 12/31/2023 |  | No | 10/16/2020 | 10/16/2020 | 0
s2405.5 | PJM WEST | Allen – Prestonsburg: 0.25 mile segment of this existing single circuit will be relocated. The relocated line segment will require construction of one custom self-supporting double circuit dead end structure and single circuit suspension structure. A short segment of new double circuit 69kV line (energized at 46 kV) will be added to tie into the new Allen Station bays which will carry Allen – Prestonsburg 46kV and Allen – East Prestonsburg 46kV lines. A temporary 0.15 mile section double circuit line will be constructed to keep Allen – Prestonsburg and Allen – East Prestonsburg 46kV lines energized during construction. | Supplemental | 46 | 2.66 |  | AEP |  |  |  |  | KY | Allen – Prestonsburg | Transmission Line | Modify | Cancelled | 2.66 | Equipment Material Condition, Performance and Risk | 12/31/2023 |  | No | 10/16/2020 | 10/16/2020 | 0
s2405.6 | PJM WEST | Remote end work will be required at Prestonsburg, Stanville, and McKinney stations. | Supplemental | 46 | 0.34 |  | AEP |  |  |  |  | KY | Prestonsburg, Stanville, McKinney | Substation | Modify | Cancelled | 0.34 | Equipment Material Condition, Performance and Risk | 12/31/2023 |  | No | 10/16/2020 | 10/16/2020 | 0
s2428.1 | PJM WEST | At Wooton station, upgrade relaying to accommodate new OPGW fiber protection. | Supplemental | 161 | 1.1 |  | AEP |  |  |  |  | KY | Wooton | Relay | Upgrade | IS | 1.1 | Equipment Material Condition, Performance and Risk | 11/30/2027 | 12/22/2024 | No | 11/20/2020 | 11/20/2020 | 100
s2428.2 | PJM WEST | At Leslie station, reconductor the 161kV Bus, Relaying upgrades towards Wooton and Pineville, Replace 161kV MOAB W, Replace 161kV XF#1 high side switch. Install DICM. | Supplemental | 161 | 1.2 |  | AEP |  |  |  |  | KY | Leslie | Substation | Upgrade | IS | 1.2 | Equipment Material Condition, Performance and Risk | 11/30/2027 | 12/22/2024 | No | 11/20/2020 | 11/20/2020 | 100
s2428.3 | PJM WEST | Remote end work at Hazard substation. | Supplemental | 161 | 0.03 |  | AEP |  |  |  |  | KY | Hazard | Substation | Modify | IS | 0.03 | Equipment Material Condition, Performance and Risk | 11/30/2027 | 12/22/2024 | No | 11/20/2020 | 11/20/2020 | 100
s2428.4 | PJM WEST | Rebuild approximately ~40 miles of Wooton – Pineville 161kV line to address the identified asset condition needs. This work also includes line removal work as well as access road construction. Majority of proposed line rebuild is to be constructed on existing center line. | Supplemental | 161 | 115 |  | AEP |  |  |  |  | KY | Wooton – Pineville | Transmission Line | Rebuild | EP | 115 | Equipment Material Condition, Performance and Risk | 11/30/2027 |  | No | 11/20/2020 | 11/20/2020 | 0
s2428.5 | PJM WEST | Expand existing ROW for the Wooton – Pineville 161kV line. | Supplemental | 161 | 8.5 |  | AEP |  |  |  |  | KY | Wooton – Pineville | Transmission Line | Upgrade | EP | 8.5 | Equipment Material Condition, Performance and Risk | 11/30/2027 |  | No | 11/20/2020 | 11/20/2020 | 0
s2428.6 | PJM WEST | Relocate ~0.32 mi 69kV Leslie – Clover Fork which includes of one structure and reconfiguration of the existing line to cross underneath the proposed Wooton-Stinnett 161kV Line. | Supplemental | 161 | 0.7 |  | AEP |  |  |  |  | KY | Leslie – Clover Fork | Transmission Line | Modify | IS | 0.7 | Equipment Material Condition, Performance and Risk | 11/30/2027 | 12/22/2024 | No | 11/20/2020 | 11/20/2020 | 100
s2428.7 | PJM WEST | At Stinnett station, upgrade relaying to accommodate new OPGW fiber protection. Provide transition, entry and termination for OPGW connectivity to the Hazard-Pineville fiber route. | Supplemental | 161 | 0.7 |  | AEP |  |  |  |  | KY | Stinnett | Relay | Upgrade | IS | 0.7 | Equipment Material Condition, Performance and Risk | 11/23/2025 | 12/16/2025 | No | 11/20/2020 | 11/20/2020 | 100
s2428.8 | PJM WEST | Provide transition, entry and termination for OPGW connectivity at Leslie substation. | Supplemental | 161 | 0.1 |  | AEP |  |  |  |  | KY | Leslie | Substation | Modify | IS | 0.1 | Equipment Material Condition, Performance and Risk | 11/30/2027 | 12/22/2024 | No | 11/20/2020 | 11/20/2020 | 100
s2436.1 | PJM WEST | Construct a greenfield 69/12 KV Osborne Station to replace Burton Station, including a high-side 69KV Phase Over Phase switch, fiber connectivity, a circuit switcher, and one 69/12kV 12/16/20MVA transformer and associated distribution feeders. | Supplemental | 69/12 | 0.74 |  | AEP |  |  |  |  | KY | Osborne, Burton | Substation | Construct | IS | 0.74 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 11/30/2024 | 10/16/2024 | No | 12/18/2020 | 12/18/2020 | 100
s2436.10 | PJM WEST | Reconfigure the existing Beaver Creek - Fremont 138kV circuit to facilitate the construction of the new double circuit Myra Extension 138kV Line to feed the proposed Myra Substation. | Supplemental | 138 | 1 |  | AEP |  |  |  |  | KY | Beaver Creek - Fremont | Transmission Line | Modify | EP | 1 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 4/19/2030 |  | No | 12/18/2020 | 12/18/2020 | 0
s2436.11 | PJM WEST | Install two replacement structures in order to bypass Elwood station. Transfer wires from old structure to new structure. Tie new structure to Cedar Creek-Henry Clay 46kV Line. | Supplemental | 46 | 1.35 |  | AEP |  |  |  |  | KY | Elwood, Cedar Creek-Henry Clay | Transmission Structures | Install | EP | 1.35 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 8/13/2031 |  | No | 12/18/2020 | 12/18/2020 | 0
s2436.12 | PJM WEST | Retire ~10.48 mi Beaver Creek – Elwood 46kV line. | Supplemental | 46 | 6.47 |  | AEP |  |  |  |  | KY | Beaver Creek – Elwood | Transmission Line | Remove | EP | 6.47 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 8/1/2030 |  | No | 12/18/2020 | 12/18/2020 | 0
s2436.2 | PJM WEST | Construct a greenfield 138KV Myra Station to replace Elwood Station. Install 138KV double box bay with two 138kV circuit breakers and line exits to Fremont & Beaver Creek. Install 138/34.5 kV transformer with high-side circuit switcher and associated 34.5kV breakers. Install fiber connectivity for upgraded relaying. | Supplemental | 138/34.5 | 3.43 |  | AEP |  |  |  |  | KY | Myra, Elwood | Substation | Construct | EP | 3.43 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 9/12/2028 |  | No | 12/18/2020 | 12/18/2020 | 0
s2436.3 | PJM WEST | Remote end relaying work at Beaver Creek substation. Remove 46KV Elwood Line 46kV circuit breaker "G“ and associated equipment. | Supplemental | 46 | 0.17 |  | AEP |  |  |  |  | KY | Beaver Creek | Relay | Modify | EP | 0.17 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 9/12/2028 |  | No | 12/18/2020 | 12/18/2020 | 0
s2436.4 | PJM WEST | Remote end relaying work at Fremont substation. | Supplemental | 138 | 0.42 |  | AEP |  |  |  |  | KY | Fremont | Relay | Modify | EP | 0.42 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 9/12/2028 |  | No | 12/18/2020 | 12/18/2020 | 0
s2436.5 | PJM WEST | At Burton station, retire and remove all existing equipment. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Burton | Substation | Remove | IS | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 12/16/2025 | 1/9/2026 | No | 12/18/2020 | 12/18/2020 | 100
s2436.6 | PJM WEST | At Elwood station, retire and remove all existing equipment. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Elwood | Substation | Remove | EP | 0 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 1/9/2030 |  | No | 12/18/2020 | 12/18/2020 | 0
s2436.7 | PJM WEST | Construct a new ~0.5 mi double circuit 69 kV line to the proposed Osborne substation. | Supplemental | 69 | 2.56 |  | AEP |  |  |  |  | KY | Osborne | Transmission Line | Construct | IS | 2.56 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 11/30/2024 | 10/16/2024 | No | 12/18/2020 | 12/18/2020 | 100
s2436.8 | PJM WEST | Reconfigure the existing Beaver Creek - Fleming 69kV line to facilitate the construction of the new double circuit Osborne 69kV line to feed the proposed Osborne Substation. | Supplemental | 69 | 1.22 |  | AEP |  |  |  |  | KY | Beaver Creek - Fleming | Transmission Line | Modify | IS | 1.22 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 11/30/2024 | 7/14/2024 | No | 12/18/2020 | 12/18/2020 | 100
s2436.9 | PJM WEST | Construct a new ~2 mi double circuit 138 kV line to the proposed Myra substation. | Supplemental | 138 | 8.8 |  | AEP |  |  |  |  | KY | Myra | Transmission Line | Construct | EP | 8.8 | Equipment Material Condition, Performance and Risk,Operational Flexibility and Efficiency | 4/19/2030 |  | No | 12/18/2020 | 12/18/2020 | 0
s2446.1 | PJM WEST | Replace Belfry substation with Orinoco substation by installing a 69KV box bay and 12KV rural bay to be built in the clear southwest of existing Belfry station. Install 69/12kV 20 MVA transformer and two 12kV breakers. | Supplemental | 69/12 | 0.65 |  | AEP |  |  |  |  | KY | Belfry, Orinoco | Substation | Replace | UC | 0.65 | Equipment Material Condition, Performance and Risk | 5/27/2027 |  | No | 1/15/2021 | 1/15/2021 | 25
s2446.2 | PJM WEST | Retire Belfry 46kV substation. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Belfry | Substation | Remove | UC | 0 | Equipment Material Condition, Performance and Risk | 6/25/2027 |  | No | 1/15/2021 | 1/15/2021 | 25
s2446.3 | PJM WEST | Retire 46kV equipment from Stone substation. | Supplemental | 46 | 0.07 |  | AEP |  |  |  |  | KY | Stone | Substation | Remove | UC | 0.07 | Equipment Material Condition, Performance and Risk | 5/27/2027 |  | No | 1/15/2021 | 1/15/2021 | 25
s2446.4 | PJM WEST | At Hatfield substation, replace MOAB Y with a 69KV Circuit Breaker towards Stone 69kV line via New Camp and Orinoco. | Supplemental | 69 | 0.85 |  | AEP |  |  |  |  | KY | Hatfield | Circuit Breaker | Install | UC | 0.85 | Equipment Material Condition, Performance and Risk | 5/25/2028 |  | No | 1/15/2021 | 1/15/2021 | 25
s2446.5 | PJM WEST | Retire the 46kV equipment at Sprigg station towards Stone (via Belfry). | Supplemental | 46 | 0.05 |  | AEP |  |  |  |  | KY | Sprigg | Substation | Modify | UC | 0.05 | Equipment Material Condition, Performance and Risk | 6/25/2027 |  | No | 1/15/2021 | 1/15/2021 | 25
s2446.6 | PJM WEST | Retire Turkey Creek Tap. | Supplemental | 69 | 0.76 |  | AEP |  |  |  |  | KY | Turkey Creek Tap | Circuit Switcher | Remove | UC | 0.76 | Equipment Material Condition, Performance and Risk | 4/21/2026 |  | No | 1/15/2021 | 1/15/2021 | 25
s2446.7 | PJM WEST | Retire the ~8.23 miles of the 46kV Sprigg – Stone 46 KV circuit. | Supplemental | 46 | 6.73 |  | AEP |  |  |  |  | KY | Sprigg – Stone | Transmission Line | Remove | UC | 6.73 | Equipment Material Condition, Performance and Risk | 5/26/2027 |  | No | 1/15/2021 | 1/15/2021 | 25
s2470.1 | PJM WEST | A green field line is to be constructed (Kenwood 69kV Extension) and to be operated at 46kV. The new extension will provide looped service into Kenwood substation. It will be approximately 2.25 miles of single circuit construction through mountainous terrain in Floyd and Johnson Counties in Kentucky. The extension will tap the existing Prestonsburg-Thelma 46kV Line around structure K346-50. (SN:53 MVA , SE:61 MVA, WN:67 MVA, WE:73 MVA) | Supplemental | 46 | 5.8 |  | AEP |  |  |  |  | KY | Kenwood 69kV Extension, Prestonsburg-Thelma | Transmission Line | Build | Cancelled | 5.8 | Equipment Material Condition, Performance and Risk | 11/16/2026 |  | No | 5/16/2025 | 5/16/2025 | 0
s2470.2 | PJM WEST | Rebuild the existing ~1.77 mi Kenwood Tap line from Kenwood to Van Lear Tap Structure on the existing center line. (SN:53 MVA , SE:61 MVA, WN:67 MVA, WE:73 MVA) | Supplemental | 46 | 4.9 |  | AEP |  |  |  |  | KY | Kenwood Tap-Van Lear Tap | Transmission Line | Rebuild | Cancelled | 4.9 | Equipment Material Condition, Performance and Risk | 11/16/2026 |  | No | 5/16/2025 | 5/16/2025 | 0
s2470.3 | PJM WEST | Provide splicing for 2.25 miles of 96ct OPGW on the Kenwood 69kV Extension Line and 1.77 mi Kenwood TAP line. This extension spans from Kenwood Station to the Prestonsburg-Thelma 46kV line. | Supplemental | 46 | 0.1 |  | AEP |  |  |  |  | KY | Kenwood 69kV Extension, Kenwood Tap lines | Transmission Line | Modify | Cancelled | 0.1 | Equipment Material Condition, Performance and Risk | 11/16/2026 |  | No | 5/16/2025 | 5/16/2025 | 0
s2470.4 | PJM WEST | At Kenwood substation, Extend the walk bus and add second 46KV line to set up Kenwood station as a looped station with MOABS protecting each exit. Add new H-Frame dead end with MOAB and single phase CCVT. Add MOAB and single phase CCVT to existing line. Relocate 3 phase CCVT's from cap bank AA to 46KV Bus. Add 3-bay transclosure, and separate battery enclosure. Replace Battery and Charger. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Kenwood | Substation | Upgrade | Cancelled | 0 | Equipment Material Condition, Performance and Risk | 11/16/2026 |  | No | 5/16/2025 | 5/16/2025 | 0
s2470.5 | PJM WEST | Retire Van Lear SS. | Supplemental | 46 | 0.1 |  | AEP |  |  |  |  | KY | Van Lear SS | Circuit Switcher | Remove | Cancelled | 0.1 | Equipment Material Condition, Performance and Risk | 11/16/2026 |  | No | 5/16/2025 | 5/16/2025 | 0
s2470.6 | PJM WEST | Remote end work at Prestonsburg substation. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Prestonsburg | Substation | Upgrade | Cancelled | 0 | Equipment Material Condition, Performance and Risk | 11/16/2026 |  | No | 5/16/2025 | 5/16/2025 | 0
s2470.7 | PJM WEST | Retire the ~1.5 mi 46kV line section from str. 52 to Van Lear SS. | Supplemental | 46 | 1.2 |  | AEP |  |  |  |  | KY | str. 52-Van Lear SS | Transmission Line | Remove | Cancelled | 1.2 | Equipment Material Condition, Performance and Risk | 10/10/2028 |  | No | 5/16/2025 | 5/16/2025 | 0
s2813.1 | PJM WEST | At Dewey substation: Replace 138kV CB B towards Thelma with new 138kV 40kA circuit breaker. Provide new DICM with new relays for all equipment at station so that existing control house can be removed. Upgrade station service. | Supplemental | 138 | 2.4 |  | AEP |  |  |  |  | KY | Dewey | Circuit Breaker | Replace | IS | 2.4 | Equipment Material Condition, Performance and Risk | 12/1/2025 | 11/5/2025 | No | 8/19/2022 | 8/19/2022 | 100
s2813.2 | PJM WEST | At Dewey substation: Provide Transition fiber via underground from the existing Control House to the new DICM at Dewey Station. Retire existing fiber. | Supplemental | 138 | 0.18 |  | AEP |  |  |  |  | KY | Dewey | Communication Equipment | Replace | EP | 0.18 | Equipment Material Condition, Performance and Risk | 12/1/2025 |  | No | 8/19/2022 | 8/19/2022 | 0
s2813.3 | PJM WEST | At Thelma substation, Remote end relaying to replace line protection for Breaker A towards (Dewey) to match upgrade at Dewey Station. Provide MOS on existing 138kV HS of transformer XF #1 & #3 to provide additional control to stability system | Supplemental | 138 | 0.4 |  | AEP |  |  |  |  | KY | Thelma | Relay | Replace | IS | 0.4 | Equipment Material Condition, Performance and Risk | 12/1/2025 | 11/6/2025 | No | 8/19/2022 | 8/19/2022 | 100
s2814.1 | PJM WEST | Bellefonte: Replace XFR #2 with a 200MVA Auto unit and retire XFR #1 & #5. The U/G feeder for XFR #3 69kV riser is getting reconductored under B3349. Reconductor sections of 138kV Bus #1 and 138kV Bus #2. Replace remaining oil PTs connected to Bus #1 and Bus #2. Upgrade Primary and back up station service. Replace 69kV bus tie breaker H. Replace the hook stick disconnects switches for the tie breaker H and 69kV tie breaker location will be relocated one bay south of the existing location and 69kV buses will be reconfigured. Replace the hook stick disconnects switches for Raceland breaker D. Relocate the Raceland feeder to bus #1 after extending the 69kV bus #1. The cap bank switcher/moab Mark 5 combo unit will get replaced with 69kV breaker and set of breaker disconnects and relocated to bus #1. 69kV breaker is needed instead of circuit switcher due to the high fault current. Relocate the cap bank to bus #1 after extending the 69kV bus #1. 69kV Air Products line MOABs will be replaced with 2000A SW. Replace hook-stick switches for Oil CB – AB, JJ, I, G, Z, T and C. These Breakers are replaced as part of B3350. Install 16'x48' DICM for 69kV Yard and a 16'x48' DICM for the 138kV Yard. Replace cable trench, single phase AC system & cable work, entire fence replacement and ground grid extension for 100'X10' expansion toward the Northwest of the 69kV yard. Both 138kV and 69kV control house will be retired. | Supplemental | 138/69 | 12.59 |  | AEP |  |  |  |  | KY | Bellefonte | Transformer | Replace | UC | 12.59 | Equipment Material Condition, Performance and Risk | 10/28/2027 |  | No | 8/19/2022 | 8/19/2022 | 25
s2814.2 | PJM WEST | The customer served out of 34.5 kV Yard has plans for demolition of their facilities. Retire entire 34kV Yard, contingent on the timing of the customer being removed from service. | Supplemental | 34 | 2.67 |  | AEP |  |  |  |  | KY | Bellefonte | Transmission Structures | Retire | UC | 2.67 | Equipment Material Condition, Performance and Risk | 10/28/2027 |  | No | 8/19/2022 | 8/19/2022 | 50
s2814.3 | PJM WEST | Retirement of the Bellefonte 34.5kV Bus Tie Line that connects the Bellefonte 138kV Station to the Bellefonte 34kV Station. This removal involves removing 3- Double Circuit Lattice Towers, 1-Triple Circuit Lattice Towers, and 1 Single Wood Pole Structure. | Supplemental | 34.5 | 0.46 |  | AEP |  |  |  |  | KY | Bellefonte | Bus Tie | Retire | UC | 0.46 | Equipment Material Condition, Performance and Risk | 5/13/2027 |  | No | 8/19/2022 | 8/19/2022 | 50
s2814.4 | PJM WEST | Retire the existing Bellefonte – Armco 34.5kV operated line. The major removal work involves removing 4 lattice steel towers, 1 H-Frame wood structure, and 2 single wood poles. The line being removed is approximately 0.55 miles long. | Supplemental | 34.5 | 1 |  | AEP |  |  |  |  | KY | Bellefonte - Armco | Transmission Line | Retire | IS | 1 | Equipment Material Condition, Performance and Risk | 10/1/2026 | 6/19/2025 | No | 8/19/2022 | 8/19/2022 | 100
s2814.5 | PJM WEST | Remote end relaying at Raceland substation to install 2 new CCVTs on a custom two-phase single column stand for the Bellefonte 69kV line exit. The existing CCVT mounted on a single phase CCVT stand will be reused and will remain as it is. | Supplemental | 69 | 0.37 |  | AEP |  |  |  |  | KY | Raceland | Relay | Install | EP | 0.37 | Equipment Material Condition, Performance and Risk | 12/1/2025 |  | No | 8/19/2022 | 8/19/2022 | 0
s2814.6 | PJM WEST | Provide 0.2 miles of fiber from Distribution structures outside the station to the new DICMs. | Supplemental | 69 | 0.49 |  | AEP |  |  |  |  | KY | Bellefonte - Raceland | Communication Equipment | Install | UC | 0.49 | Equipment Material Condition, Performance and Risk | 10/28/2027 |  | No | 8/19/2022 | 8/19/2022 | 25
s2815.1 | PJM WEST | At Hatfield Substation, expand the substation yard. Relocate 138/69/46kV XF#1. Replace 138/69/46kV XF#1 Bushings, 138kV 3 phase Bus CCVTs, MOAB X1 and GND Switch Z1 with a new 138kV Circuit Switcher. Replace 138KV Sprigg Line metering, Line Switch "11" with a 138kV Circuit Breaker. Replace and relocate 69kV CB-B to standard Bay position. Replace 69KV CB-A and add 3 phase CCVTs to John's Creek 69kV line. Add 138kV Backup and 69kV Primary Station Service transformers and Station Service. Expand yard and install a 16' X 27' base DICM. Remove 111MVA 46/7.2KV Transformer #2 and associated equipment and 7.2KV 3 phase station service. Remove the control building. | Supplemental | 138/69 | 4.95 |  | AEP |  |  |  |  | KY | Hatfield | Substation | Expand | EP | 4.95 | Equipment Material Condition, Performance and Risk | 5/25/2028 |  | No | 8/19/2022 | 8/19/2022 | 0
s2815.2 | PJM WEST | On the Leslie No.1 – Hatfield 69kV circuit, remove existing guyed dead-end structure K357-29 and install a new single pole, single circuit, custom dead-end to remove the guy wires conflicting with station footprint plans. The existing guy anchors would conflict with station expansion plans, and it is not feasible to span guy over top of proposed control house as the anchors would land in the proposed station drive path. The proposed custom dead-end structure will be placed 20' downhill from existing structure K357-29. | Supplemental | 69 | 0.5 |  | AEP |  |  |  |  | KY | Hatfield | Transmission Structures | Remove | EP | 0.5 | Equipment Material Condition, Performance and Risk | 5/25/2028 |  | No | 8/19/2022 | 8/19/2022 | 0
s3147.18 | PJM WEST | Sprigg - Wharncliffe 46kV line - Remove approximately 1.29 miles of Sprigg - Wharncliffe 46kV line in KY. | Supplemental | 46 | 1.1 |  | AEP |  |  |  |  | KY | Sprigg - Wharncliffe | Transmission Line | Remove | EP | 1.1 | Equipment Material Condition, Performance and Risk,Customer Service | 6/1/2030 |  | No | 8/18/2023 | 8/18/2023 | 0
s3303.1 | PJM WEST | At Gund Metering Point, install new revenue metering for a 20 MW customer load connection. Install a new 69kV manual switch on the customer side of the hard tap. | Supplemental | 69 | 1.15 |  | AEP |  |  |  |  | KY | Gund Metering Point | Meter | Install | IS | 1.15 | Customer Service,Operational Flexibility and Efficiency | 11/15/2024 | 11/22/2024 | No | 3/15/2024 | 3/15/2024 | 100
s3303.2 | PJM WEST | At Bevins Metering Point, motorize the existing switch at Bevins towards Gund to facilitate the connection of a 7 MW customer load to existing delivery point. | Supplemental | 69 | 0.59 |  | AEP |  |  |  |  | KY | Bevins Metering Point | Circuit Switcher | Modify | IS | 0.59 | Customer Service,Operational Flexibility and Efficiency | 11/15/2024 | 12/16/2024 | No | 3/15/2024 | 3/15/2024 | 100

## Definitions-Mapping
Column Name | Definition
Upgrade ID | PJM-assigned project identifier
Region | Region of the project (PJM West, PJM MAAC, PJM South, MISO)
Description | Description
Project Type | Identifies the policies and procedures governing the transmission project: baseline, supplemental or network type
Voltage (kv) | Operating voltage of the transmission asset
Cost Estimate | Cost Estimate
Required Date | Date when the criteria violation will impact the system
Transmission Owner | Owner of the transmission asset
Proposal IDs | List of proposal IDs
Schedule 12 Location | Tariff Schedule 12 Appendix
NLRS Cost Allocation (%) | Non-Load Ratio Share Cost Allocation Percentage
LRS Cost Allocation (%) | Load Ratio Share Cost Allocation Percentage
State | State in which the asset is located
Location | Electrical location of the transmission asset
Equipment | Type of transmission asset being worked on
Task | Type of work to be performed
Status | Current status of the project: Planning (active), Engineering and Procurement, Under Construction, In-Service, On Hold, Withdrawn or Canceled
TEAC Cost (Millions) | Estimated cost presented at the TEAC of performing the upgrade
Driver | Fundamental motivation for performing the upgrade
Projected In-Service Date | Date when the Transmission Owner expects the upgrade to be placed in service
Actual In Service Date | The date the upgrade is placed in service
Immediate Need | Immediate Need
Initial TEAC Date | Initial TEAC Date
Latest TEAC Date | Latest TEAC Date
Percent Complete | Percent Complete
ISA In-Service Date | ISA In-Service Date
Revised In-Service Date | Revised In-Service Date
TEAC Materials | Committee presentations of the projects as well as other projects in the area