## Project List
Upgrade Id | Region | Description | Project Type | Voltage | Cost Estimate | Required Date | Actual / Forecasted Date (as of 2.27.26) | Transmission Owner | Proposal IDs | Schedule12 Location | (Non-Load Ratio Share) Cost Allocation Percent | (Load Ratio Share) Cost Allocation Percent | State | Location | Equipment | Task | Status | TEAC Cost | Driver | Projected In Service Date | Actual In Service Date | Immediate Need | Initial TEAC Date | Latest TEAC Date | Percent Complete | ISA In-Service Date | Revised In-Service Date | TEAC Materials
b3281 | PJM WEST | Install 138 kV circuit switcher on the 138/69 kV transformer #1 and 138/34.5 kV transformer #2 at Dewey. Install 138 kV 2000 A 40 kA breaker on Stanville line at Dewey 138 kV substation. | Baseline | 138 | 1.4 | 2025-12-01 | 2025-11-05 | AEP |  | Appendix A | AEP:100 |  | KY | Dewey | Circuit Switcher | Install | IS | 1.4 | TO Criteria Violation | 2025-11-05 | 2025-11-05 | No | 2021-02-17 | 2021-02-17 | 100
b3283 | PJM WEST | Replace the existing Inez 138/69 kV 50 MVA autotransformer with a 138/69 kV 90 MVA autotransformer. | Baseline | 138/69 | 2.96 | 2025-12-01 | 2022-10-31 | AEP |  | Appendix A | AEP:100 |  | KY | Inez | Transformer | Replace | IS | 2.96 | TO Criteria Violation | 2025-12-01 | 2022-10-31 | No | 2021-02-17 | 2021-02-17 | 100
b3307 | PJM WEST | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69 kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12 kV 30 MVA transformer, replace 12 kV CB A and D. Retire existing Fleming substation. | Baseline | 138/69 | 21.1 | 2025-12-01 | 5/9/2024 | AEP |  | Appendix A | AEP:100 |  | KY | Fleming subtation | Substation | Rebuild | UC | 21.1 | TO Criteria Violation | 2026-06-25 |  | No | 2021-01-15 | 2021-01-15 | 75
b3288.1 | PJM WEST | Construct ~ 2.75 mi Orinoco - Stone 69 kV transmission line in the clear between Orinoco station and Stone station. | Baseline | 69 | 9.23 | 2025-12-01 | 2027-05-27 | AEP |  | Appendix A | AEP:100 |  | KY | Orinoco - Stone | Transmission Line | Build | UC | 9.23 | TO Criteria Violation | 2027-05-27 |  | No | 2021-01-15 | 2021-01-15 | 75
b3288.3 | PJM WEST | At Stone substation, circuit breaker A to remain in place and be utilized as T1 low side breaker, circuit breaker B to remain in place and be utilized as new Hatfield (via Orinoco and New Camp) 69 kV line breaker. Add new 69 kV circuit breaker E for Coleman Line exit. | Baseline | 69 | 0.66 | 2025-12-01 | 2027-05-27 | AEP |  | Appendix A | AEP:100 |  | KY | Stone | Circuit Breaker | Install | UC | 0.66 | TO Criteria Violation | 2027-05-27 |  | No | 2021-01-15 | 2021-01-15 | 75
b3847.1 | PJM WEST | Add a 765 kV breaker at Baker station for the reactor on the Broadford 765 kV line. | Baseline | 765 | 23.36 | 2024-06-01 | 2027-02-12 | AEP | Immediate Need | Appendix A | AEP:70.68,EKPC:8.12,PEPCO:21.20 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41 | KY | Baker | Circuit Breaker | Install | EP | 23.36 | Operational Performance | 2027-06-25 |  | Yes | 2024-06-05 | 2024-06-05 | 15
b3288.2 | PJM WEST | Construct ~ 3.25 mi Orinoco – New Camp 69 kV transmission line in the clear between Orinoco station and New Camp station. | Baseline | 69 | 9.95 | 2025-12-01 | 2027-11-08 | AEP |  | Appendix A | AEP:100 |  | KY | Orinoco – New Camp | Transmission Line | Build | UC | 9.95 | TO Criteria Violation | 2027-11-08 |  | No | 2021-01-15 | 2021-01-15 | 75
b3288.5 | PJM WEST | At New Camp substation, rebuild the 69 kV bus, add 69 kV MOAB W and replace the 69 kV ground switch Z1 with a 69 kV circuit switcher on the New Camp transformer. | Baseline | 69 | 1.18 | 2025-12-01 | 2027-11-08 | AEP |  | Appendix A | AEP:100 |  | KY | New Camp | Substation | Modify | UC | 1.18 | TO Criteria Violation | 2027-11-08 |  | No | 2021-01-15 | 2021-01-15 | 75
b3288.4 | PJM WEST | Reconfigure the New Camp 69 kV tap which includes access road improvements/installation, temporary wire and permanent wire work along with dead end structures installation. | Baseline | 69 | 0.45 | 2025-12-01 | 2027-11-12 | AEP |  | Appendix A | AEP:100 |  | KY | New Camp | Substation | Modify | UC | 0.45 | TO Criteria Violation | 2027-11-12 |  | No | 2021-01-15 | 2021-01-15 | 75
b3349 | PJM WEST | Replace Bellefonte 69 kV risers on the section between Bellefonte TR #3 and 69 kV Bus #2. | Baseline | 69 | 0.54 | 6/1/2026 | 2027-06-10 | AEP |  | Appendix A | AEP:100 |  | KY | Bellefonte | Relay | Replace | UC | 0.54 | TO Criteria Violation | 6/10/2027 |  | No | 11/19/2021 | 11/19/2021 | 25
b3352 | PJM WEST | Replace MOAB W, MOAB Y, line and bus side jumpers of both W and Y at 47th Street 69 kV station. Upgrade the 69 kV strain bus between MOABs W and Y to 795 KCM AAC. Change the connectors on the tap to MOAB X1 to accommodate the larger 795 KCM AAC. | Baseline | 69 | 0 | 6/1/2026 | 2025-04-15 | AEP |  | Appendix A | AEP:100 |  | KY | 47th 69kV station | Disconnect Switch | Replace | IS | 0 | TO Criteria Violation | 12/1/2025 | 4/15/2025 | No | 11/19/2021 | 11/19/2021 | 100
b3353.1 | PJM WEST | Allen substation: Rebuild Allen station to the northwest of its current footprint utilizing a standard air-insulated substation with equipment raised by 7’ concrete platforms and control house raised by a 10’ platform to mitigate flooding concerns. Install five 69 kV 3000A 40 kA circuit breakers in a ring bus (operated at 46 kV) configuration with a 13.2 MVAR capacitor bank. Existing Allen station will be retired (does not include the distribution cost). Distribution scope of work: Install 69/46 kV-12 kV 20 MVA transformer along with 2-12 kV breakers on 7’ concrete platforms (conversion of S2405.1). | Baseline | 46 | 10.55 | 12/1/2026 | 2028-06-05 | AEP |  | Appendix A | AEP:100 |  | KY | Allen | Substation | Rebuild | EP | 10.55 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.2 | PJM WEST | Allen-East Prestonsburg: A 0.20 mile segment of this 46 kV line will be relocated to the new station (SN/SE/WN/WE: 53/61/67/73MVA). (Conversion of S2405.2) | Baseline | 46 | 0.33 | 12/1/2026 | 2028-06-05 | AEP |  | Appendix A | AEP:100 |  | KY | Allen – East Prestonsburg | Transmission Line | Modify | EP | 0.33 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.3 | PJM WEST | McKinney-Allen: The new line extension will walk around the south and east sides of the existing Allen station to the new Allen station being built in the clear. A short segment of new single circuit 69 kV line and a short segment of new double circuit 69 kV line (both operated at 46 kV) will be added to the line to tie into the new Allen station bays. (Conversion of S2405.3) | Baseline | 46 | 1.95 | 12/1/2026 | 2028-06-05 | AEP |  | Appendix A | AEP:100 |  | KY | McKinney – Allen | Transmission Line | Install | EP | 1.95 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.4 | PJM WEST | Stanville-Allen: A segment of this line will have to be relocated to the new station (SN/SE/WN/WE: 50/50/63/63MVA). (Conversion of S2405.4) | Baseline | 46 | 0.17 | 12/1/2026 | 2028-06-05 | AEP |  | Appendix A | AEP:100 |  | KY | Stanville – Allen | Transmission Line | Modify | EP | 0.17 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.5 | PJM WEST | Allen-Prestonsburg: 0.25 mile segment of this existing single circuit will be relocated. The relocated line segment will require construction of one custom self-supporting double circuit dead-end structure and single circuit suspension structure. A short segment of new double circuit 69 kV line (energized at 46 kV) will be added to tie into the new Allen station bays, which will carry Allen-Prestonsburg 46 kV and Allen-East Prestonsburg 46 kV lines. A temporary 0.15 mile section double circuit line will be constructed to keep Allen-Prestonsburg and Allen-East Prestonsburg 46 kV lines energized during construction. (Conversion of S2405.5) | Baseline | 46 | 2.66 | 12/1/2026 | 2028-06-05 | AEP |  | Appendix A | AEP:100 |  | KY | Allen – Prestonsburg | Transmission Line | Modify | EP | 2.66 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3353.6 | PJM WEST | Remote end work will be required at Prestonsburg, Stanville and McKinney stations. (Conversion of S2405.6) | Baseline | 46 | 0.34 | 12/1/2026 | 2028-06-05 | AEP |  | Appendix A | AEP:100 |  | KY | Prestonsburg, Stanville, McKinney | Substation | Modify | EP | 0.34 | TO Criteria Violation | 6/5/2028 |  | No | 11/19/2021 | 11/19/2021 | 0
b3360 | PJM WEST | Replace Thelma Transformer #1 with a 138/69/46 kV 130/130/90 MVA transformer and replace 46 kV risers and relaying toward Kenwood substation. Existing TR#1 to be used as spare. | Baseline | 69 | 3.54 | 12/1/2026 | 2026-11-20 | AEP |  | Appendix A | AEP:100 |  | KY | Thelma | Transformer | Replace | EP | 3.54 | TO Criteria Violation | 11/20/2026 |  | No | 11/19/2021 | 11/19/2021 | 15
b3361 | PJM WEST | Rebuild Prestonsburg - Thelma 46kV circuit connecting though Kenwood station, approximately 12.7 miles. Retire Jenny Wiley SS and Van Lear SS. | Baseline | 46 | 63.6 | 12/1/2026 | 2028-10-10 | AEP |  | Appendix A | AEP:100 |  | KY | Prestonsburg - Thelma | Transmission Line | Rebuild | EP | 63.6 | TO Criteria Violation | 12/16/2027 |  | No | 11/19/2021 | 5/16/2025 | 15 |  | 12/16/2027