## Sheet1
Unplanned Boil Water Advisories for Kentucky since 2/27/23
System | Cause category | BWA Cause description provided by Operator | DateCreated/ issued | Affected area of system | number of connections affected | Duration of Boil water Advisory (Days)
KY - Center Ridge - Water District 2 | Mechanical Failure - Well | Well pump sucked up sand damaging the pump | 2026-02-02 22:29 | all | 135 | 3
KY - Center Ridge - Water District 1 | Mechanical Failure - Well | Well 1 had a electrical issue | 2026-01-24 09:55 | all | 99 | 4
KY - Center Ridge - Water District 2 | Mechanical Failure - Well | Well 2A tripped well pump breaker and lost water pressure from failure on capacitors | 2025-12-20 14:13 | all | 135 | 3
KY - Center Ridge - Water District 3 | Outside Contractor Damage | Line break at well house Dr lot 1-3. Crew onsite to make repair. Entire location affected. PWSID: KY0180502. | 2025-11-17 12:17 | all | 68 | 2
KY - Center Ridge - Water District 3 | Infrastructure Failure - Production Site | Ground fault outlet for chlorine pump at center ridge 3 tripped. System had low chlorine residual (0.02). Facility wide advisory needed. | 2025-11-11 17:18 | all | 68 | 2
KY - Center Ridge - Water District 2 | Infrastructure Failure - Production Site | Tank 2A isn't holding water pressure. CWS has changed a relay and changing a capacitor. | 2025-11-05 23:23 | all | 135 | 2
KY - Center Ridge - Water District 3 | Infrastructure Failure - Distribution System | Main line leak | 2025-08-12 20:31 | all | 68 | 3
KY - Center Ridge - Water District 4 | Mechanical Failure - Well | Well pump failed | 2025-07-14 17:23 | all | 51 | 4
KY - Center Ridge - Water District 1 | Power loss | Lost power and due to storms and system went to zero pressure | 2025-04-04 17:12 | all | 99 | 1
KY - Center Ridge - Water District 1 | Infrastructure Failure - Distribution System | Repair to leaking Tee on three inch main. Only one customer affected | 2025-03-10 12:30 | Partial | 1 | 3
KY - Center Ridge - Water District 3 | Infrastructure Failure - Distribution System | 3 inch main blew out, coupling split | 2024-12-02 20:13 | all | 68 | 2
KY - Center Ridge - Water District 4 | Infrastructure Failure - Distribution System | 3 inch water main blew out | 2024-12-02 20:10 | all | 51 | 2
KY - Center Ridge - Water District 4 | Mechanical Failure - Well | Well pump breaker failed, replaced breaker. | 2024-11-25 20:26 | all | 51 | 2
KY - Center Ridge - Water District 4 | Outside Contractor Damage | repair 3 inch Watermain damaged by fiber optic crew boring rig. | 2024-09-27 00:22 | all | 51 | 2
KY - Center Ridge - Water District 3 | Outside Contractor Damage | Contractor broke line, 258 Waterway Trail New Concord KY CR District 3 | 2024-07-25 13:21 | Partial | unknown | 1
KY - Center Ridge - Water District 1 | Power loss | Low pressure event caused by electric power failure, electric spike burnt the capacitor, replaced capacitor, system back online about about 1am. | 2024-05-08 13:49 | all | 99 | 2
KY - Center Ridge - Water District 4 | Outside Contractor Damage | Repair 4 inch waterline struck by utility company contractor running fiber-optic . | 2024-04-16 02:35 | Partial | 3 | 7
KY - Center Ridge - Water District 3 | Infrastructure Failure - Distribution System | Repaired 4 inch Watermain at 942waterway Trail | 2024-04-04 02:21 | Partial | 6 | 1
KY - Center Ridge - Water District 4 | Outside Contractor Damage | Contractor hit 3 inch PVC Watermain had to replace 4 feet of pipe. | 2024-02-27 00:30 | all | 66 | 3
KY - Center Ridge - Water District 4 | Outside Contractor Damage | Outside contractor damaged our main line | 2024-08-01 | all | 51 | 1
KY - Center Ridge - Water District 3 | Infrastructure Failure - Distribution System | Main break | 2024-07-08 | unknown | unknown | 1
KY - Center Ridge - Water District 4 | Infrastructure Failure - Distribution System | Main break | 2024-06-21 | Partial | 6 | 4
KY - Center Ridge - Water District 3 | Infrastructure Failure - Distribution System | Main break | 2024-02-01 | Partial | 10 | 1
KY - Center Ridge - Water District 3 | Infrastructure Failure - Distribution System | Main break | 2024-01-21 | all | 66 | 2
KY - Center Ridge - Water District 2 | Infrastructure Failure - Distribution System | Main break | 2023-12-28 | Partial | 50 | 1
KY - Center Ridge - Water District 4 | Infrastructure Failure - Distribution System | Main break | 2023-12-01 | Partial | 14 | 3
KY - Center Ridge - Water District 3 | Power loss | Power Loss | 2023-09-25 | all | 66 | 1