## Upgrades
AEP
Run Date: 6/12/2025
TOID | Revised TOID | Upgrade ID | Description | Driver | Deactivation Study | PJM Required In Service Date | Revised PJM In Service Date | TO Projected In Service Date | Revised TO Projected In Service Date | Actual In Service Date | Status Code | Revised Status Code | % Comp | Revised % Comp | Cost Est (Millions) | Revised Cost Est (Millions) | TEAC Cost (Millions) | TEAC Date | TO Project Manager | TO Project Manager | e Dart Ticket No | ImpactsTie | TO Notes
P15082C28 |  | b2597 | Rebuild approximately 1 mi. section of Dragoon-Virgil Street 34.5 kV line between Dragoon and Dodge Tap switch and replace Dodge switch MOAB to increase thermal capability of Dragoon-Dodge Tap branch | TO Criteria Violation |  | 2019-06-01 |  | 2026-12-18 | 2027-03-12 |  | EP |  | 50 |  | 2.15 |  | 2.154 | 2015-01-07 | Pm Cliff Vaughn/ Planner Joshua Smith |  |  | FALSE
P15082C10, P15082C05, P15082C07 |  | b2598 | Rebuild approximately 1 mile section of the Kline-Virgil Street 34.5 kV line between Kline and Virgil Street tap. Replace MOAB switches at Beiger, risers at Kline, switches and bus at Virgil Street. | TO Criteria Violation |  | 2019-06-01 |  | 2026-07-17 |  |  | EP |  | 50 |  | 1.69 |  | 1.689 | 2015-01-07 | Pm Cliff Vaughn/ Planner Joshua Smith |  |  | FALSE
P15095006 |  | b2604.1 | Remove approximately 11.32 miles of the 69 kV line between Millbrook Park and Franklin Furnace. | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 |  |  | EP |  | 50 |  | 1.13 |  | 1.13 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095017 |  | b2604.2 | At Millbrook Park station, add a new 138/69 kV transformer #2 (90 MVA) with 3000 A 40 kA breakers on the high and low side. Replace the 600 A MOAB Switch and add a 3000 A circuit switcher on the high side of transformer #1. | TO Criteria Violation |  | 2019-06-01 |  | 2028-05-08 |  |  | EP |  | 0 | 50 | 3.05 |  | 3.05 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095020 |  | b2604.3 | Replace Sciotoville 69 kV station with a new 138/12 kV in-out station (Cottrell) with 2000A line MOABs facing Millbrook Park and East Wheelersburg 138 kV. | TO Criteria Violation |  | 2019-06-01 |  | 2027-10-07 |  |  | EP |  | 0 | 75 | 1.4 |  | 1.4 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095022 |  | b2604.4 | Tie Cottrell switch into the Millbrook Park-East Wheelersburg 138 kV circuit by constructing 0.50 miles of line using 795 ACSR 26/7 Drake (SE 359 MVA). | TO Criteria Violation |  | 2019-06-01 |  | 2027-10-07 |  |  | EP |  | 0 | 75 | 1.96 |  | 1.96 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095028 |  | b2604.5 | Install a new 2000 A 3-way POP Switch outside of Texas Eastern 138 kV substation (Sadiq Switch). | TO Criteria Violation |  | 2019-06-01 |  | 2027-10-27 |  |  | EP |  | 0 | 50 | 1.08 |  | 1.08 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095027 |  | b2604.6 | Replace the Wheelersburg 69 kV station with a new 138/12 kV in-out station (Sweetgum) with a 3000 A 40 kA breaker facing Sadiq Switch and a 2000 A 138 kV MOAB facing Althea. | TO Criteria Violation |  | 2019-06-01 |  | 2027-12-09 |  |  | EP |  | 0 | 50 | 2.16 |  | 2.16 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095032 |  | b2604.7 | Build approximately 1.4 miles of new 138 kV line using 795 ACSR 26/7 Drake (SE 359 MVA) between the new Sadiq Switch and the new Sweetgum 138 kV stations. | TO Criteria Violation |  | 2019-06-01 |  | 2027-12-07 |  |  | EP |  | 0 | 50 | 3.41 |  | 3.41 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095007 |  | b2604.8 | Remove the existing 69 kV Hayport Road Switch. | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 |  |  | EP |  | 0 | 50 | 0.1 |  | 0.1 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095015 |  | b2604.9 | Rebuild approximately 2.3 miles along existing ROW from Sweetgum to the Hayport Rd switch 69 kV location as 138 kV single circuit and rebuild approximately 2.0 miles from the Hayport Road switch to Althea 69 kV with double circuit 138 kV construction, one side operated at 69 kV to continue service to K.O. Wheelersburg, using 795 ACSR 26/7 Drake (SE 359 MVA). | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 | 2028-06-02 |  | EP |  | 0 | 50 | 10.76 |  | 10.76 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095015 |  | b2604.10 | Build a new station (Althea) with a 138/69 kV, 90 MVA transformer. The 138 kV side will have a single 2000 A 40 kA circuit breaker and the 69 kV side will be a 2000 A 40 kA three breaker ring bus. | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 | 2028-06-02 |  | EP |  | 0 | 50 | 11.07 |  | 11.07 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P15095060 |  | b2604.11 | Remote end work at Hanging Rock, East Wheelersburg and North Haverhill 138 kV. | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 | 2028-06-02 |  | EP |  | 0 | 50 | 0.06 |  | 0.06 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  |  | FALSE
P16108002 |  | b2753.7 | Retire line sections (Dilles Bottom - Bellaire and Moundsville - Dilles Bottom 69 kV lines) south of First Energy 138 kV line corridor, near “Point A”. Tie George Washington - Moundsville 69 kV circuit to George Washington - West Bellaire 69 kV circuit. | Baseline Load Growth Deliverability & Reliability |  | 2020-05-31 |  | 2027-10-11 |  |  | EP |  | 50 |  | 5.52 |  | 5.52 | 2017-07-21 | PM Jon Starr/ Planner Christian Mitchell-Flores |  |  | TRUE
P24071001 |  | b2760 | Perform a Sag Study of the Saltville - Tazewell 138 kV line to increase the thermal rating of the line | Baseline Load Growth Deliverability & Reliability |  | 2021-06-01 |  | 2025-03-01 |  |  | EP |  | 5 |  | 0.1 |  | 0.1 | 2016-10-06 | PM Blair Burns / Bobby Valerio |  |  | FALSE
P21009002 |  | b2793 | Energize the spare Fremont Center 138/69 kV 130 MVA transformer #3. Reduces overloaded facilities to 46% loading. | TO Criteria Violation |  | 2021-06-01 |  | 2026-12-14 |  |  | UC |  | 26 |  | 1.3 |  | 0.081 | 2017-05-31 | PM Colton Caldwell/Brendan Fuller |  |  | FALSE
P19004001 |  | b2938 | Perform a sag mitigations on the Broadford – Wolf Hills 138kV circuit to allow the line to operate to a higher maximum temperature. | Generator Deactivation | BEAVER VALLEY 1¦BEAVER VALLEY 2¦DAVIS BESSE 1¦PERRY 1 | 2022-06-01 | 2021-06-01 | 2028-06-27 |  |  | EP |  | 15 |  | 2.6 |  | 2.6 | 2018-06-07 | PM Blair Burns Planner Robert Vaalerio |  |  | FALSE
P19269001 |  | b3037 | Upgrades at the Natrium substation | Baseline Load Growth Deliverability & Reliability |  | 2023-06-01 |  | 2025-06-02 |  |  | EP |  | 15 |  | 1.1 |  | 1.1 | 2018-09-28 | PM Wayne Cooper/Planner Christian Mitchell-Flores |  |  | FALSE
P21036002 |  | b3085 | Reconductor Kammer - George Washington 138 kV line (~0.08 miles). Replace the wave trap at Kammer 138 kV. | Generator Deactivation | MANSFIELD 1¦MANSFIELD 2¦MANSFIELD 3¦SAMMIS DIESEL¦SAMMIS 6¦SAMMIS 7¦SAMMIS 5¦KIMBERLY CLARK¦EASTLAKE 6 | 2022-06-01 | 2022-06-01 | 2025-06-02 |  |  | UC |  | 75 |  | 0.5 |  | 0.5 | 2020-07-07 | PM Andrew Garlick/Planner Christian Mitchell-Flores |  |  | FALSE
P19052004 |  | b3150 | Rebuild Ferguson 69/12 kV station in the clear as the 138/12 kV Bear station and connect it to a ~1 mile double circuit 138 kV extension from the Aviation – Ellison Rd 138 kV line to remove the load from the 69 kV line. | TO Criteria Violation |  | 2024-06-01 |  | 2027-12-15 |  |  | EP |  | 25 |  | 6.4 |  | 6.4 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  |  | FALSE
P16024021 |  | b3151.7 | Install a 69 kV Bobay switch at Woodland Station. | TO Criteria Violation |  | 2024-06-01 |  | 2025-09-18 |  |  | UC |  | 75 |  | 0.6 |  | 0.6 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  |  | FALSE
p16024029 |  | b3151.8 | Replace Carroll and Churubusco 34.5 kV stations with the 69 kV Snapper station. Snapper will have two (2) line circuit breakers, one (1) bus tie circuit breaker and a 14.4 MVAR cap bank | TO Criteria Violation |  | 2024-06-01 |  | 2025-06-10 |  |  | UC |  | 75 |  | 8.7 |  | 8.7 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  |  | FALSE
P16024031 |  | b3151.9 | Remove 34.5 kV circuit breaker "AD" at Wallen station. | TO Criteria Violation |  | 2024-06-01 |  | 2025-09-18 |  |  | EP |  | 25 |  | 0.3 |  | 0.3 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  |  | FALSE
P19096013 |  | b3151.15 | Rebuild the 0.6 mile double circuit section of the Rob Park – South Hicksville / Rob Park – Diebold Road as 69 kV | TO Criteria Violation |  | 2024-06-01 |  | 2027-01-28 |  |  | EP |  | 25 |  | 1 |  | 1 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  |  | FALSE
P19297001 |  | b3160.1 | Construct a ~2.4 mile double circuit 138 kV extension using 1033 ACSR to connect Lake Head to the 138 kV network. | TO Criteria Violation |  | 2024-06-01 |  | 2025-10-03 |  |  | UC |  | 75 |  | 6 |  | 6 | 2020-01-17 | Charles Linkous/ Bobby Valerio |  |  | FALSE
A15701239 |  | b3160.2 | Retire the ~2.5 mile 34.5 kV Niles – Simplicity Tap line. | TO Criteria Violation |  | 2024-06-01 |  | 2027-01-20 |  |  | EP |  | 10 |  | 1.2 |  | 1.2 | 2020-01-17 | PM Joseph Scott/Planner Joshua Smith |  |  | FALSE
P17078023 |  | b3160.3 | Retire the ~4.6 mile Lakehead 69 kV Tap | TO Criteria Violation |  | 2024-06-01 |  | 2025-11-24 |  |  | EP |  | 10 |  | 1.4 |  | 1.4 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  |  | FALSE
p19297011 |  | b3160.4 | Build new 138/69 kV drop down station to feed Lakehead with a 138 kV breaker, 138 kV switcher, 138/69 kV transformer and a 138 kV MOAB | TO Criteria Violation |  | 2024-06-01 |  | 2025-10-03 |  |  | UC |  | 50 |  | 4 |  | 4 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  |  | FALSE
P19298001 |  | b3160.5 | Rebuild the ~1.2 mile Buchanan South 69 kV Radial Tap using 795 ACSR | TO Criteria Violation |  | 2024-06-01 |  | 2028-01-05 |  |  | EP |  | 10 |  | 3 |  | 3 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  |  | FALSE
P19298001 |  | b3160.6 | Rebuild the ~8.4 mile 69 kV Pletcher – Buchanan Hydro line as the ~9 mile Pletcher – Buchanan South 69 kV line using 795 ACSR. | TO Criteria Violation |  | 2024-06-01 |  | 2028-01-05 |  |  | EP |  | 10 |  | 20 |  | 20 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  |  | FALSE
P19298020 |  | b3160.7 | Install a PoP switch at Buchanan South station with 2 line Moabs. | TO Criteria Violation |  | 2024-06-01 |  | 2028-01-05 |  |  | EP |  | 10 |  | 0.6 |  | 0.6 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  |  | FALSE
p17081018 |  | b3208 | Retire approximately 38 miles of the 44 mile Clifford-Scottsville 46 kV circuit. Build new 138 kV “in and out” to two new Distribution stations to serve the load formerly served by Phoenix, Shipman, Schuyler (AEP), and Rockfish stations. Construct new 138 kV lines from Joshua Falls-Riverville (~10 mi.) and Riverville-Gladstone (~5 mi.). Install required station upgrades at Joshua Falls, Riverville and Gladstone stations to accommodate the new 138 kV circuits. Rebuild Reusen – Monroe 69 kV (~4 mi.) | TO Criteria Violation |  | 2022-12-01 |  | 2027-05-04 |  |  | EP |  | 25 |  | 85 |  | 85 | 2019-05-20 | PM Scott Maxwell/Planner Robert Valerio |  |  | FALSE
P21296007 |  | b3243 | Replace risers at Bass 34.5kV station | TO Criteria Violation |  | 2025-06-01 |  | 2025-11-03 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-11-20 | PM Kyle Martin/Planner Valerie Watros |  |  | FALSE
P19096001 |  | b3244 | Rebuild approximately 9 miles of the Rob Park - Harlan 69 kV line | TO Criteria Violation |  | 2025-06-01 |  | 2025-07-24 |  |  | EP |  | 0 |  | 20.9 |  | 20.9 | 2020-11-20 | PM Dan Ballmer/Planner Valerie Watros |  |  | FALSE
P21005001 |  | b3248 | Install a low side 69 kV circuit breaker at Albion 138/69 kV transformer 1 | TO Criteria Violation |  | 2025-06-01 |  | 2028-10-02 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2020-11-20 | PM Kyle Martin/Planner Valerie Watros |  |  | FALSE
P20255001 |  | b3249 | Rebuild the Chatfield-Melmore 138kV line (~ 10 miles) to 1033 ACSR conductor. | Baseline Load Growth Deliverability & Reliability |  | 2025-06-01 |  | 2026-02-24 |  |  | EP |  | 0 |  | 27.2 |  | 27.2 | 2021-02-17 | PM Anthony Antronica/Planner Jaspm Lee |  |  | FALSE
P15095017 |  | b3253 | Install a 3000A 40 kA 138 kV breaker on high side of 138/69 kV transformer #5 at Millbrook Park station. The transformer and associated bus protection will be upgraded accordingly. | TO Criteria Violation |  | 2025-06-01 |  | 2028-03-14 |  |  | UC |  | 26 |  | 0.63 |  | 0.63 | 2020-11-20 | PM Cole Fehrman/Planner Michael Ritchey |  |  | FALSE
P21252005 |  | b3258 | Install a 3000A 63 kA 138 kV breaker on high side of 138/69 kV transformer #2 at Wagenhals station. The transformer and associated bus protection will be upgraded accordingly. | TO Criteria Violation |  | 2025-06-01 |  | 2027-06-04 |  |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2020-11-20 | PM Davide Roudebush/Planner Michael Ritchey |  |  | FALSE
P20009043 |  | b3259 | At West Millersburg station, replace the 138 kV MOAB on the West Millersburg - Wooster 138 kV line with a 3000A 40 kA breaker. | TO Criteria Violation |  | 2025-06-01 |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.68 |  | 0.68 | 2020-11-20 | PM David Roudebush/Planner Hunter Hutchison |  |  | FALSE
P21746001, P21746011 |  | b3269 | At West New Philadelphia station, add a high side 138 kV breaker on the 138/69 kV transformer #2 along with a 138 kV breaker on the line towards Newcomerstown. | TO Criteria Violation |  | 2025-06-01 |  | 2028-04-13 |  |  | EP |  | 0 |  | 2.02 |  | 2.02 | 2020-11-04 | Planner Hunter Hutcison |  |  | FALSE
p15082c31 |  | b3270 | Install 1.7 miles of 795 ASCR 138kV conductor along the other side of Dragoon Tap 138 kV line, which is currently double circuit tower with one position open. Additionally, install a 2nd 138/34.5 kV transformer at Dragoon, install a high side circuit switcher on the current transformer at Dragoon Station, and install 2-138 kV line breakers on the Dragoon-Jackson 138 kV and Dragoon-Twin Branch 138 kV lines. | TO Criteria Violation |  | 2025-06-01 |  | 2025-12-19 |  |  | UC |  | 75 |  | 4.89 |  | 4.89 | 2020-11-04 | PM Cliff Vaughn/Planner Joshua Smith |  |  | FALSE
P22094002 |  | b3270.1 | Replace Dragoon 34.5 kV Breakers "B", "C" and "D" with 40 kA breakers. | TO Criteria Violation |  | 2025-06-01 |  | 2025-01-01 |  |  | EP |  | 0 |  | 2 |  | 2 | 2020-11-04 | PM Cliff Vaughn/Planner Joshua Smith |  |  | FALSE
P20896002, P20896006 |  | b3271 | Install a 138 kV circuit breaker at Fremont station on line towards Fremont Center and install a 9.6 MVAR 69 kV capacitor bank at Bloom Road station. | TO Criteria Violation |  | 2025-06-01 |  | 2024-09-01 |  |  | EP |  | 25 |  | 1.76 |  | 1.76 | 2020-11-04 | PM Colton Caldwell/Planner Hunter Hutchison |  |  | FALSE
P23024001 |  | b3272 | Install two 138 kV circuit switchers on the high side of 138/34.5 kV transformers #1 & #2 at Rockhill station. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.47 |  | 1.47 | 2020-11-04 |  |  |  | FALSE
P20017004 |  | b3273.1 | Rebuild and convert the existing 17.6 miles East Leipsic-New Liberty 34.5 kV circuit to 138 kV using 795 ACSR | TO Criteria Violation |  | 2025-06-01 |  | 2027-11-17 |  |  | EP |  | 25 |  | 31.35 |  | 31.351 | 2020-12-01 | PM Benjamin Gilsdorf/Planner Jason Lee |  |  | FALSE
P20017002 |  | b3273.2 | Convert the existing 34.5 kV equipment to 138 kV and expanded the existing McComb station to the north and east to allow for new equipment to be installed. Install two new 138 kV box bays to allow for line positions and two new 138/12 kV transformers. | TO Criteria Violation |  | 2025-06-01 |  | 2027-02-02 |  |  | EP |  | 25 |  | 0.87 |  | 0.868 | 2020-12-01 | PM Benjamin Gilsdorf/Planner Jason Lee |  |  | FALSE
P20017004 |  | b3273.3 | Expand the existing East Leipsic 138 kV station to the north to allow for another 138 kV line exit to be installed. The new line exit will involve installing a new 138 kV circuit breaker, disconnect switches and new dead end structure along with extending existing 138 kV bus work. | TO Criteria Violation |  | 2025-06-01 |  | 2027-11-17 |  |  | EP |  | 25 |  | 1.3 |  | 1.3 | 2020-12-01 | PM Benjamin Gilsdorf/Planner Jason Lee |  |  | FALSE
P20017015 |  | b3273.4 | Add one 138 kV circuit breaker and disconnect switches in order to add an additional line position at New Liberty 138 kV station. Install line relaying potential devices and retire the 34.5 kV breaker F. | TO Criteria Violation |  | 2025-06-01 |  | 2027-08-19 |  |  | EP |  | 25 |  | 0.9 |  | 0.899 | 2020-12-01 | PM Benjamin Gilsdorf/Planner Jason Lee |  |  | FALSE
P21013015 |  | b3274 | Rebuild approximately 8.9 miles of 69 kV line between Newcomerstown and Salt Fork Switch with 556 ACSR conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 |  |  | EP |  | 0 |  | 15.89 |  | 15.89 | 2020-12-01 |  |  |  | FALSE
P21565006 |  | b3275.1 | Rebuild Kammer Station-Cresaps Switch 69 kV, approximately 0.5 miles. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | 2025-05-08 | EP | IS | 15 | 100 | 0.93 |  | 0.933 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  |  | FALSE
P21565007 |  | b3275.2 | Rebuild Cresaps Switch-McElroy Station 69 kV, approximately 0.67 miles. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  |  | EP |  | 15 |  | 1.25 |  | 1.25 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  |  | FALSE
P21565009 | P21565008 | b3275.3 | Replace a single span of 4/0 ACSR from Moundsville-Natrium str 93L to Carbon Tap switch 69kV located between Colombia Carbon and Conner Run stations. Remainder of line is 336 ACSR. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | 2025-03-06 | EP | IS | 15 | 100 | 0.01 |  | 0.012 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  |  | FALSE
P21565010 |  | b3275.4 | Rebuild from Colombia Carbon to Columbia Carbon Tap str 93N 69 kV, approximately 0.72 miles. The remainder of the line between Colombia Carbon Tap structure 93N and Natrium station is 336 ACSR and will remain. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | 2025-03-06 | EP | IS | 15 | 100 | 1.08 |  | 1.082 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  |  | FALSE
P21565001 |  | b3275.5 | Replace the Cresaps 69 kV 3-Way Phase-Over-Phase Switch and structure with a new 1200 A 3-Way Switch and Steel Pole. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | 2025-05-08 | EP | IS | 15 | 100 | 0.71 |  | 0.706 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  |  | FALSE
P21565004 |  | b3275.6 | Replace 477 MCM Alum bus and risers at McElroy 69 kV station. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  |  | EP |  | 15 |  | 0.33 |  | 0.325 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  |  | FALSE
P21565008 | P19269001 | b3275.7 | Replace Natrium 138 kV bus existing between CB-BT1 and along the 138 kV Main Bus # 1 dropping to CBH1 from the 500MCM conductors to a 1272 KCM AAC conductor. Replace the dead end clamp and strain insulators. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 | 2025-11-26 |  | EP |  | 15 | 75 | 0.29 |  | 0.291 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  |  | FALSE
P22062009 |  | b3276.1 | Rebuild the 2/0 Copper section of the Lancaster-South Lancaster 69 kV line, approximately 2.9 miles of the 3.2 mile total length with 556 ACSR conductor. The remaining section has 336 ACSR conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2027-10-19 | 2030-12-31 |  | EP |  | 0 |  | 5.37 |  | 5.37 | 2020-12-01 | PM Karmyn Wilford/Planner Christian Mitchell-Flores |  |  | FALSE
P22062009 |  | b3276.2 | Rebuild the 1/0 Copper section of the line between Lancaster Junction and Ralston station 69 kV, approximately 2.3 miles of the 3.1 mile total length. | TO Criteria Violation |  | 2025-06-01 |  | 2025-04-30 | 2030-12-31 |  | EP |  | 0 |  | 4.58 |  | 4.582 | 2020-12-01 | PM Karmyn Wilford/Planner Christian Mitchell-Flores |  |  | FALSE
P20252011 |  | b3276.3 | Rebuild the 2/0 Copper portion of the line between East Lancaster Tap and Lancaster 69 kV, approximately 0.81 miles. | TO Criteria Violation |  | 2025-06-01 |  | 2026-04-20 | 2026-07-16 |  | EP |  | 15 |  | 1.2 |  | 1.195 | 2020-12-01 |  |  |  | FALSE
P19004009 |  | b3278.1 | Saltville Station: Replace H.S. MOAB Switches on the high side of the 138/69/34.5 kV T1 with a H.S. Circuit Switcher. | TO Criteria Violation |  | 2025-12-01 |  | 2028-01-27 | 2031-06-23 |  | On Hold | EP | 0 | 25 | 0.72 |  | 0.72 | 2021-02-17 | PM Blair Burns/Planner Christian Mitchell-Flores |  |  | FALSE
P19004015 |  | b3278.2 | Meadowview Station: Replace existing 138/69/34.5 kV transformer T2 with a new 130 MVA 138/69/13 kV transformer. | TO Criteria Violation |  | 2025-12-01 |  | 2028-05-12 | 2032-10-19 |  | EP |  | 0 | 25 | 3.14 |  | 3.14 | 2021-02-17 | PM Blair Burns/Planner Christian Mitchell-Flores |  |  | FALSE
P19004009 |  | b3278.3 | Saltville Station: Install two 138 kV breakers and bus diff protection | TO Criteria Violation |  | 2025-12-01 |  | 2028-05-12 |  |  | EP |  | 0 | 25 | 0.36 |  | 0.36 | 2021-07-16 | PM Blair Burns/Planner Christian Mitchell-Flores |  |  | FALSE
P22908005 |  | b3279 | Install a new 138 kV, 21.6 MVAR cap bank and circuit switcher at Apple Grove Station. | TO Criteria Violation |  | 2025-06-01 |  | 2027-04-01 |  |  | EP |  | 0 | 10 | 1 |  | 1 | 2021-02-17 | PM Blair Burns/Planner Christian Mitchell-Flores |  |  | FALSE
P20228001, P20228002 |  | b3280 | Rebuild the existing Cabin Creek - Kelly Creek 46 kV line (to structure 366-44), approximately 4.4 miles. This section is double circuit with the existing Cabin Creek - London 46 kV line so a double circuit rebuild would be required. | TO Criteria Violation |  | 2025-06-01 |  | 2026-11-25 | 2026-10-15 |  | EP |  | 10 | 50 | 17.9 |  | 17.9 | 2021-01-15 | PM Wayne Cooper/Planner Michael Hassay |  |  | FALSE
P21753001 |  | b3281 | Install 138 kV circuit switcher on the 138/69 kV transformer #1 and 138/34.5 kV transformer #2 at Dewey. Install 138 kV 2000 A 40 kA breaker on Stanville line at Dewey 138 kV substation. | TO Criteria Violation |  | 2025-12-01 |  | 2025-12-01 | 2025-11-05 |  | EP | UC | 15 | 75 | 1.4 |  | 1.4 | 2021-02-17 | PM Jacob Arwood/Joshua Smith |  |  | FALSE
P19292001 |  | b3282.1 | Install a second 138 kV circuit utilizing 795 ACSR conductor on the open position of the existing double circuit towers from East Huntington-North Proctorville. Remove the existing 34.5 kV line from East Huntington-North Chesapeake and rebuild this section to 138 kV served from a new PoP switch off the new East Huntington-North Proctorville 138 kV #2 line. | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-22 | 2029-03-21 |  | EP |  | 0 | 10 | 7.1 |  | 7.1 | 2021-02-17 | PM Wayne Cooper/Planner Michael Hassay |  |  | FALSE
P19292012 |  | b3282.2 | Install a 138 kV 40 kA circuit breaker at North Proctorville. | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-22 | 2029-03-21 |  | EP |  | 0 | 10 | 1.4 |  | 1.4 | 2021-02-17 | PM Wayne Cooper/Planner Michael Hassay |  |  | FALSE
P19292011 |  | b3282.3 | Install a 138 kV 40 kA circuit breaker at East Huntington. | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-22 | 2029-03-21 |  | EP |  | 0 | 10 | 1.1 |  | 1.1 | 2021-02-17 | PM Wayne Cooper/Planner Michael Hassay |  |  | FALSE
P19292009 |  | b3282.4 | Convert the existing 34/12 kV North Chesapeake to a 138/12 kV station. | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-22 | 2029-03-21 |  | EP |  | 0 | 10 | 0.8 |  | 0.8 | 2021-02-17 | PM Wayne Cooper/Planner Michael Hassay |  |  | FALSE
P19303001 |  | b3284 | Rebuild ~5.44 miles of 69 kV line from Lock Lane to Point Pleasant. | TO Criteria Violation |  | 2025-06-01 |  | 2026-09-10 | 2027-09-10 |  | UC | EP | 15 | 50 | 13.5 |  | 13.5 | 2021-01-15 | PM Andrew Garlick/Planner Michael Hassay |  |  | FALSE
P18243002 |  | b3285 | Replace the Meigs 69 kV 4/0 Cu station riser towards Gavin and rebuild the section of the Meigs – Hemlock 69 kV circuit from Meigs to approximately structure #40 (~4 miles) replacing the line conductor 4/0 ACSR with the line conductor size 556.5 ACSR. | TO Criteria Violation |  | 2025-06-01 |  | 2026-05-28 | 2026-02-02 |  | UC |  | 50 | 75 | 12.14 |  | 12.14 | 2021-01-15 | PM James Albright/Planner Patrick Hodgson |  |  | FALSE
P19305001 |  | b3288.1 | Construct ~ 2.75 mi Orinoco - Stone 69 kV transmission line in the clear between Orinoco station and Stone station. | TO Criteria Violation |  | 2025-12-01 |  | 2025-05-29 | 2027-05-07 |  | EP | UC | 15 | 75 | 9.23 |  | 9.23 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  |  | FALSE
P19305016 |  | b3288.2 | Construct ~ 3.25 mi Orinoco – New Camp 69 kV transmission line in the clear between Orinoco station and New Camp station. | TO Criteria Violation |  | 2025-12-01 |  | 2025-11-13 | 2027-11-08 |  | EP | UC | 15 | 75 | 9.95 |  | 9.95 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  |  | FALSE
P19305010 |  | b3288.3 | At Stone substation, circuit breaker A to remain in place and be utilized as T1 low side breaker, circuit breaker B to remain in place and be utilized as new Hatfield (via Orinoco and New Camp) 69 kV line breaker. Add new 69 kV circuit breaker E for Coleman Line exit. | TO Criteria Violation |  | 2025-12-01 |  | 2025-05-29 | 2027-05-07 |  | EP | UC | 15 | 75 | 0.66 |  | 0.66 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  |  | FALSE
P19305018 |  | b3288.4 | Reconfigure the New Camp 69 kV tap which includes access road improvements/installation, temporary wire and permanent wire work along with dead end structures installation. | TO Criteria Violation |  | 2025-12-01 |  | 2025-11-13 | 2027-11-12 |  | EP | UC | 15 | 75 | 0.45 |  | 0.45 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  |  | FALSE
P19305022 |  | b3288.5 | At New Camp substation, rebuild the 69 kV bus, add 69 kV MOAB W and replace the 69 kV ground switch Z1 with a 69 kV circuit switcher on the New Camp transformer. | TO Criteria Violation |  | 2025-12-01 |  | 2025-11-13 | 2027-11-08 |  | EP | UC | 15 | 75 | 1.18 |  | 1.18 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  |  | FALSE
P19296003 |  | b3289.1 | Roanoke Station: Install high-side circuit switcher on 138/69/12 kV T5 | TO Criteria Violation |  | 2025-06-01 |  | 2026-12-10 | 2027-08-18 |  | EP | EP | 0 | 10 | 1.1 |  | 1.102 | 2021-01-15 | PM Jonathan Wood/Planner Robert Valerio |  |  | FALSE
P23013002 |  | b3289.2 | Huntington Court Station: Install high-side circuit switcher on 138/69/34.5 kV T1 | TO Criteria Violation |  | 2025-06-01 |  | 2026-05-21 |  |  | EP |  | 0 | 50 | 1.42 |  | 1.415 | 2021-01-15 | PM Myles Gunter/Planner Robert Valerio |  |  | FALSE
P19220001 |  | b3290.1 | Build 9.4 miles of single circuit 69 kV line from Roselms to near East Ottoville 69 kV Switch. | TO Criteria Violation |  | 2025-06-01 |  | 2026-04-07 | 2027-06-07 |  | EP |  | 15 | 50 | 13.7 |  | 13.7 | 2021-01-15 | PM Benjamin Gilsdorf/Planner |  |  | FALSE
P19220018 |  | b3290.2 | Rebuild 7.5 miles of double circuit 69kV line between East Ottoville Switch and Kalida Station (combining with the new Roselms to Kalida 69 kV circuit). | TO Criteria Violation |  | 2025-06-01 |  | 2026-03-05 | 2027-02-19 |  | EP |  | 15 | 50 | 23.6 |  | 23.6 | 2021-01-15 | PM Benjamin Gilsdorf/Planner Jason Lee |  |  | FALSE
P19220017 |  | b3290.3 | At Roselms Switch, install a new three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | TO Criteria Violation |  | 2025-06-01 |  | 2026-04-07 | 2027-06-07 |  | EP |  | 15 | 50 | 0.6 |  | 0.6 | 2021-01-15 | PM Benjamin Gilsdorf/Planner Jason Lee |  |  | FALSE
P19220021 |  | b3290.4 | At Kalida 69 kV station, terminate the new line from Roselms Switch. Move the CS XT2 from high side of T2 to the high side of T1. Remove existing T2 transformer. | TO Criteria Violation |  | 2025-06-01 |  | 2026-04-07 | 2027-06-18 |  | EP |  | 15 | 50 | 1 |  | 1 | 2021-01-15 | PM Benjamin Gilsdorf/Planner Jason Lee |  |  | FALSE
P15082C15 |  | b3291 | Replace the Russ St. 34.5 kV Switch | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-23 |  |  | EP |  | 15 | 50 | 1.5 |  | 1.5 | 2021-01-15 | PM Cliff Vaughn/Planner Joshua Smith |  |  | FALSE
P18100001 |  | b3292 | Replace existing 69 kV capacitor bank at Stuart Station with a 17.2 MVAr capacitor bank | TO Criteria Violation |  | 2025-12-01 |  | 2025-12-01 | 2028-12-13 |  | EP |  | 0 | 25 | 0 |  | 0 | 2021-01-15 |  |  |  | FALSE
P19296005 |  | b3294 | Replace existing 69 kV disconnect switches for circuit breaker "C" at Walnut Avenue station | TO Criteria Violation |  | 2025-06-01 |  | 2026-09-16 | 2027-08-05 |  | EP |  | 0 | 10 | 0 |  | 0 | 2021-01-15 | PM Jonathan Woods/Planner Robert Valerio |  |  | FALSE
P19281003, P19281024 |  | b3296 | Rebuild the overloaded portion of the Concord-Whitaker 34.5 kV line (1.13 miles). Rebuild is double circuit and will utilize 795 ACSR conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2026-06-30 | 2027-08-30 |  | EP |  | 0 | 25 | 2.8 |  | 2.8 | 2021-01-15 |  |  |  | FALSE
P20233002 |  | b3297.1 | Rebuild 4.23 miles of 69 kV line between Sawmill and Lazelle station, using 795 ACSR 26/7 conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2027-09-04 | 2026-07-22 |  | EP |  | 0 | 10 | 12 |  | 12 | 2021-01-15 | PM Andrew Nardella/Planner Huner Hutchinson |  |  | FALSE
P20233006 |  | b3297.2 | Rebuild 1.94 miles of 69 kV line between Westerville and Genoa stations, using 795 ACSR 26/7 conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2027-09-24 | 2027-05-08 |  | EP |  | 0 | 10 | 5.9 |  | 5.9 | 2021-01-15 |  |  |  | FALSE
P20233007 |  | b3297.3 | Replace risers and switchers at Lazelle, Westerville, and Genoa 69 kV stations. Upgrade associated relaying accordingly. | TO Criteria Violation |  | 2025-06-01 |  | 2027-09-24 | 2026-07-22 |  | EP |  | 0 | 10 | 1.9 |  | 1.9 | 2021-01-15 | PM Andrew Nardella/Planner Hunter Hutchison |  |  | FALSE
P21600005 |  | b3298 | Rebuild 0.8 miles of double circuit 69 kV line between South Toronto and West Toronto. Replace 219 kcmil ACSR with 556 ACSR. | TO Criteria Violation |  | 2025-06-01 |  | 2026-06-08 | 2028-04-10 |  | EP |  | 0 | 10 | 2.83 |  | 2.83 | 2021-02-17 | PM Jared Grzeskowiak/Planner Christian Mitchell-Flores |  |  | FALSE
P22734002 |  | b3298.1 | Replace the 69 kV breaker D at South Toronto station with 40 kA breaker. | TO Criteria Violation |  | 2025-06-01 |  | 2025-12-02 | 2026-05-19 |  | EP |  | 0 | 10 | 0.7 |  | 0.7 | 2021-02-17 | PM Jared Grzeskowiak/Planner Christian Mitchell-Flores |  |  | FALSE
P18221001 |  | b3307 | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69 kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12 kV 30 MVA transformer, replace 12 kV CB A and D. Retire existing Fleming substation. | TO Criteria Violation |  | 2025-12-01 |  | 2025-12-01 | 2025-11-21 |  | UC |  | 50 | 75 | 21.1 |  | 21.1 | 2021-01-15 | PM Wayne Cooper/Planner Michael Hassay |  |  | FALSE
P21600001 |  | b3308 | Reconductor and rebuild 1 span of T-line on the Fort Steuben-Sunset Blvd 69 kV branch with 556 ACSR. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 | 2028-04-10 |  | EP |  | 0 | 10 | 0.73 |  | 0.73 | 2021-01-15 | PM Cole Fehrman/Planner Christian Mitchell-Flores |  |  | FALSE
P20010021 |  | b3309 | Rebuild 1.75 miles of the Greenlawn - East Tiffin line section of the Carrothers - Greenlawn 69 kV circuit containing 133 ACSR conductor with 556 ACSR conductor. Upgrade relaying as required. | TO Criteria Violation |  | 2025-06-01 |  | 2029-03-21 |  |  | EP |  | 15 | 50 | 3.45 |  | 3.45 | 2021-01-15 | PM Benjamin Gilsdorf/Planner Hunter Hutchison |  |  | FALSE
P21033004 |  | b3310.1 | Rebuild 10.5 miles of the Howard-Willard 69 kV line utilizing 556 ACSR conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2025-05-30 |  | 2025-05-30 | UC | IS | 50 | 100 | 19 |  | 19 | 2021-02-17 | PM Danielle Hilliard/Planner Jason Lee |  |  | FALSE
P21033014 |  | b3310.2 | Upgrade relaying at Howard 69 kV station. | TO Criteria Violation |  | 2025-06-01 |  | 2025-10-31 |  | 2025-06-05 | EP | IS | 15 | 100 | 0.23 |  | 0.23 | 2021-02-17 | PM Danielle Hilliard/Planner Jason Lee |  |  | FALSE
P20889008 |  | b3312 | Rebuild approximately 4.0 miles of existing 69 kV line between West Mount Vernon and Mount Vernon stations. Replace the existing 138/69 kV transformer at West Mount Vernon with a larger 90 MVA unit along with existing 69 kV breaker 'C'. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 | 2026-01-21 |  | EP | UC | 15 | 75 | 12.93 |  | 12.926 | 2021-01-06 | PM Adam Clark/Planner Christian Mitchell-Flores |  |  | FALSE
P21030010 |  | b3313 | Add 40 kA circuit breakers on the low and high side of East Lima 138/69 kV Transformer | TO Criteria Violation |  | 2025-06-01 |  | 2026-12-30 | 2026-10-26 |  | EP |  | 15 | 50 | 1.2 |  | 1.2 | 2021-03-19 | PM Jon Starr/Planner Hunter Hutchison |  |  | FALSE
P19225006 |  | b3314.1 | Install a new 138/69 kV 130 MVA transformer and associated protection at Elliot station. | TO Criteria Violation |  | 2025-06-01 |  | 2029-09-20 |  |  | EP |  | 15 | 50 | 3 |  | 3 | 2021-03-19 | PM John Wright/Planner Christian Mitchell-Flores |  |  | FALSE
P19225022 |  | b3314.2 | Perform work at Strouds Run station to retire 138/69/13 kV 33.6 MVA transformer #1 and install a dedicated 138/13 KV distribution transformer. | TO Criteria Violation |  | 2025-06-01 |  | 2030-10-24 |  |  | EP |  | 15 | 50 | 0 |  | 0 | 2021-03-19 | PM John Wright/Planner Christian Mitchell-Flores |  |  | FALSE
P19178030 |  | b3315 | Upgrade Relaying on Mark Center-South Hicksville 69 kV line and replace Mark Center cap bank with a 7.7 MVAR unit. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 |  | 2025-03-20 | EP | IS | 0 | 100 | 1.25 |  | 1.25 | 2021-03-19 | PM Danille Hilliard/Planner Christian Mitchell-Flores |  |  | FALSE
P21751001 |  | b3337 | Replace the one (1) Hyatt 138 kV breaker “AB1(101N)” with 3000 A, 63 kA interrupting breaker. | Short Circuit |  | 2026-06-01 |  | 2025-05-23 | 2025-12-09 |  | EP |  | 15 | 50 | 0.48 |  | 0.48 | 2021-10-15 | PM Melinda Kemplin/Planner Christian Mitchell-Flores |  |  | FALSE
P20013001 |  | b3338 | Replace the two (2) Kenny 138 kV breakers, “102” (SC-3) and “106” (SC-4), each with a 3000 A, 63 kA interrupting breaker. | Short Circuit |  | 2026-06-01 |  | 2024-06-14 | 2026-06-01 |  | EP |  | 0 | 50 | 0.76 |  | 0.76 | 2021-10-05 |  |  |  | FALSE
P21751002 |  | b3339 | Replace the one (1) Canal 138 kV breaker “3” with 3000 A, 63 kA breaker. | Short Circuit |  | 2026-06-01 |  | 2025-04-30 | 2025-10-22 |  | EP |  | 15 | 50 | 0.48 |  | 0.48 | 2021-10-15 |  |  |  | FALSE
P23008001 |  | b3344.1 | Install two (2) 138 kV circuit breakers in the M and N strings in the breaker-and-a half configuration in West Kingsport station 138 kV yard to allow the Clinch River-Moreland Dr. 138 kV to cut in the West Kingsport station | TO Criteria Violation |  | 2026-11-01 |  | 2025-11-01 |  |  | EP |  | 0 | 50 | 1.85 |  | 1.846 | 2021-11-02 |  |  |  | FALSE
P23008004 |  | b3344.2 | Upgrade remote end relaying at Riverport 138 kV station due to the line cut in at West Kingsport station | TO Criteria Violation |  | 2026-11-01 |  | 2026-11-01 |  |  | EP |  | 15 | 50 | 0.25 |  | 0.251 | 2021-11-02 |  |  |  | FALSE
P21013019 |  | b3345.1 | Rebuild ~4.2 miles of overloaded sections of the 69 kV line between Salt Fork Switch and Leatherwood Switch with 556 ACSR. | TO Criteria Violation |  | 2026-06-01 |  | 2027-08-02 | 2027-10-05 |  | EP |  | 0 | 25 | 9.06 |  | 9.062 | 2021-11-02 |  |  |  | FALSE
P21013024 |  | b3345.2 | Update relay settings at Broom Road station. | TO Criteria Violation |  | 2026-06-01 |  | 2027-08-02 | 2027-10-05 |  | EP |  | 0 | 25 | 0.04 |  | 0.039 | 2021-11-02 |  |  |  | FALSE
P21590002, P21590003, P21590004, P21590005, P21590008, P21590009, P21590012, P21590014 |  | b3346.1 | Rebuild approximately 3.5 miles of overloaded 69 kV line between North Delphos-East Delphos-Elida Road switch. This includes approximately 1.1 miles of double circuit line that makes up a portion of the North Delphos-South Delphos 69 kV line and the North Delphos-East Delphos 69 kV line. Approximately 2.4 miles of single circuit line will also be rebuilt between the double circuit portion to East Delphos station and from East Delphos to Elida Road Switch. | TO Criteria Violation |  | 2026-06-01 |  | 2026-08-21 | 2026-10-19 |  | EP |  | 0 | 25 | 8.43 |  | 8.434 | 2021-11-30 |  |  |  | FALSE
P21590015, P21590017 |  | b3346.2 | Replace the line entrance spans at South Delphos to eliminate the overloaded 4/0 Copper and 4/0 ACSR conductor. | TO Criteria Violation |  | 2026-06-01 |  | 2027-04-20 | 2027-06-16 |  | EP |  | 0 | 25 | 0.44 |  | 0.437 | 2021-11-30 |  |  |  | FALSE
P21737001, P21737010, P21737011, P21737012, P21737013, P21737014 |  | b3347.1 | Rebuild approximately 20 miles of line between Bancroft and Milton stations with 556 ACSR conductor | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-14 | 2031-12-17 |  | EP |  | 0 | 10 | 56.55 |  | 56.553 | 2021-11-02 |  |  |  | FALSE
P21737023, A20001419 |  | b3347.2 | Replace the jumpers around Hurrican switch with 556 ACSR | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 | 2030-05-10 |  | EP |  | 0 | 10 | 0.01 |  | 0.014 | 2021-11-02 |  |  |  | FALSE
P21737024 |  | b3347.3 | Replace the jumpers around Teays switch with 556 ACSR | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 | 2030-11-22 |  | EP |  | 0 | 10 | 0.01 |  | 0.014 | 2021-11-02 |  |  |  | FALSE
P21737008 |  | b3347.4 | Winfield Station Relay Settings: Update relay settings to coordinate with remote ends on line rebuild | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 | 2031-06-11 |  | EP |  | 0 | 10 | 0.05 |  | 0.047 | 2021-11-02 |  |  |  | FALSE
P21737009 |  | b3347.5 | Bancroft Station Relay Settings: Update relay settings to coordinate with remote ends on line rebuild | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 | 2031-12-17 |  | EP |  | 0 | 10 | 0.03 |  | 0.027 | 2021-11-02 |  |  |  | FALSE
P21737004 |  | b3347.6 | Milton Station Relay Settings: Update relay settings to coordinate with remote ends on line rebuild. | TO Criteria Violation |  | 2026-11-01 |  | 2027-12-23 | 2029-12-19 |  | EP |  | 0 | 10 | 0.03 |  | 0.027 | 2021-11-02 |  |  |  | FALSE
P21737007 |  | b3347.7 | Putnam Village Station Relay Settings: Update relay settings to coordinate with remote ends on line rebuild | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 | 2031-06-11 |  | EP |  | 0 | 10 | 0.05 |  | 0.047 | 2021-11-02 |  |  |  | FALSE
P21259011, P21259040 |  | b3348.1 | Construct a 138 kV single bus station (Tin Branch) consisting of a 138 kV box bay with a distribution transformer and 12 kV distribution bay. Two 138 kV lines will feed this station (from Logan and Sprigg stations), and distribution will have one 12 kV feed. Install two 138 kV circuit breakers on the line exits. Install 138 kV circuit switcher for the new transformer. | TO Criteria Violation |  | 2026-11-01 |  | 2026-11-09 | 2028-02-03 |  | EP |  | 0 | 25 | 5.58 |  | 5.584 | 2021-11-30 |  |  |  | FALSE
P21259013 |  | b3348.2 | Construct a new 138/46/12 kV Argyle station to replace Dehue station. Install a 138 kV ring bus using a breaker-and-a-half configuration, with an autotransformer with a 46 kV feed and a distribution transformer with a 12 kV distribution bay. Two 138 kV lines will feed this station (from Logan and Wyoming stations). There will also be a 46 kV feed from this station to Becco station. Distribution will have two 12 kV feeds. Retire Dehue station in its entirety. | TO Criteria Violation |  | 2026-11-01 |  | 2026-07-17 | 2027-07-19 |  | EP |  | 0 | 25 | 10 |  | 9.996 | 2021-11-30 |  |  |  | FALSE
P21259036, P21259037 |  | b3348.3 | Bring the Logan-Sprigg #2 138 kV circuit in and out of Tin Branch station by constructing approximately 1.75 miles of new overhead double circuit 138 kV line. Double circuit T3 series lattice towers will be used along with 795,000 cm ACSR 26/7 conductor. One shield wire will be conventional 7 #8 ALUMOWELD, and one shield wire will be OPGW. | TO Criteria Violation |  | 2026-11-01 |  | 2027-03-22 | 2028-02-03 |  | EP |  | 0 | 25 | 8.58 |  | 8.578 | 2021-11-30 |  |  |  | FALSE
P21259034, P21259035 |  | b3348.4 | Logan-Wyoming No. 1 circuit in and out of the proposed Argyle station. Double circuit T3 series lattice towers will be used along with 795,000 cm ACSR 26/7 conductor. One shield wire will be conventional 7 #8 ALUMOWELD, and one shield wire will be OPGW. | TO Criteria Violation |  | 2026-11-01 |  | 2026-07-17 | 2027-04-26 |  | EP |  | 0 | 25 | 7.7 |  | 7.702 | 2021-11-30 |  |  |  | FALSE
P21259023, P21259024, P21259025 |  | b3348.5 | Rebuild approximately 10 miles of 46 kV line between Becco and the new Argyle substation. Retire approximately 16 miles of 46 kV line between the new Argyle substation and Chauncey station. | TO Criteria Violation |  | 2026-11-01 |  | 2026-08-20 | 2027-07-19 |  | EP |  | 0 | 25 | 33.71 |  | 33.705 | 2021-11-30 |  |  |  | FALSE
P21259028, P21259029, P21259030 P21259031 |  | b3348.6 | Adjust relay settings due to new line terminations and retirements at Logan, Wyoming, Sprigg, Becco and Chauncey stations. | TO Criteria Violation |  | 2026-11-01 |  | 2026-11-23 | 2028-02-13 |  | EP |  | 0 | 25 | 0.23 |  | 0.233 | 2021-11-30 |  |  |  | FALSE
P21720001 |  | b3349 | Replace Bellefonte 69 kV risers on the section between Bellefonte TR #3 and 69 kV Bus #2. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 | 2026-12-02 |  | EP | UC | 15 | 75 | 0.54 |  | 0.54 | 2021-11-19 |  |  |  | FALSE
P21720001 |  | b3350.1 | Replace overdutied 69 kV breakers C, G, I, Z, AB and JJ in place. The new 69 kV breakers to be rated at 3000 A 40 kA breakers. | TO Criteria Violation |  | 2023-06-01 |  | 2026-05-27 | 2026-12-02 |  | EP | UC | 15 | 75 | 2 |  | 2 | 2022-01-21 |  |  |  | FALSE
P21720005, P21720003, P21720007 |  | b3350.2 | Upgrade remote end relaying at Point Pleasant, Coalton and South Point 69 kV substations. | TO Criteria Violation |  | 2023-06-01 |  | 2026-06-04 | 2026-12-23 |  | EP |  | 15 | 50 | 0 |  | 0 | 2022-01-21 |  |  |  | FALSE
A20001430 | no project yet, please rmv BPID | b3351 | Replace the 69 kV in-line switches at Monterey 69 kV substation. | TO Criteria Violation |  | 2026-06-01 |  | 2029-08-31 |  |  | EP |  | 0 |  | 0 |  | 0 | 2021-11-19 |  |  |  | FALSE
P22005001 |  | b3352 | Replace MOAB W, MOAB Y, line and bus side jumpers of both W and Y at 47th Street 69 kV station. Upgrade the 69 kV strain bus between MOABs W and Y to 795 KCM AAC. Change the connectors on the tap to MOAB X1 to accommodate the larger 795 KCM AAC. | TO Criteria Violation |  | 2026-06-01 |  | 2025-12-01 |  | 2025-04-15 | EP | IS | 15 | 100 | 0 |  | 0 | 2021-11-19 |  |  |  | FALSE
P19092002 |  | b3353.1 | Allen substation: Rebuild Allen station to the northwest of its current footprint utilizing a standard air-insulated substation with equipment raised by 7’ concrete platforms and control house raised by a 10’ platform to mitigate flooding concerns. Install five 69 kV 3000A 40 kA circuit breakers in a ring bus (operated at 46 kV) configuration with a 13.2 MVAR capacitor bank. Existing Allen station will be retired (does not include the distribution cost). Distribution scope of work: Install 69/46 kV-12 kV 20 MVA transformer along with 2-12 kV breakers on 7’ concrete platforms (conversion of S2405.1). | TO Criteria Violation |  | 2026-12-01 |  | 2024-11-15 | 2027-12-31 |  | EP |  | 15 | 30 | 10.55 |  | 10.55 | 2021-11-19 |  |  |  | FALSE
P19092007 |  | b3353.2 | Allen-East Prestonsburg: A 0.20 mile segment of this 46 kV line will be relocated to the new station (SN/SE/WN/WE: 53/61/67/73MVA). (Conversion of S2405.2) | TO Criteria Violation |  | 2026-12-01 |  | 2024-04-25 | 2027-12-31 |  | EP |  | 15 | 30 | 0.33 |  | 0.33 | 2021-11-19 |  |  |  | FALSE
P19092011 |  | b3353.3 | McKinney-Allen: The new line extension will walk around the south and east sides of the existing Allen station to the new Allen station being built in the clear. A short segment of new single circuit 69 kV line and a short segment of new double circuit 69 kV line (both operated at 46 kV) will be added to the line to tie into the new Allen station bays. (Conversion of S2405.3) | TO Criteria Violation |  | 2026-12-01 |  | 2024-04-05 | 2027-12-31 |  | EP |  | 15 | 30 | 1.95 |  | 1.95 | 2021-11-19 |  |  |  | FALSE
P19092013 |  | b3353.4 | Stanville-Allen: A segment of this line will have to be relocated to the new station (SN/SE/WN/WE: 50/50/63/63MVA). (Conversion of S2405.4) | TO Criteria Violation |  | 2026-12-01 |  | 2024-11-15 | 2027-12-31 |  | EP |  | 15 | 30 | 0.17 |  | 0.17 | 2021-11-19 |  |  |  | FALSE
P19092013 |  | b3353.5 | Allen-Prestonsburg: 0.25 mile segment of this existing single circuit will be relocated. The relocated line segment will require construction of one custom self-supporting double circuit dead-end structure and single circuit suspension structure. A short segment of new double circuit 69 kV line (energized at 46 kV) will be added to tie into the new Allen station bays, which will carry Allen-Prestonsburg 46 kV and Allen-East Prestonsburg 46 kV lines. A temporary 0.15 mile section double circuit line will be constructed to keep Allen-Prestonsburg and Allen-East Prestonsburg 46 kV lines energized during construction. (Conversion of S2405.5) | TO Criteria Violation |  | 2026-12-01 |  | 2025-10-18 | 2027-12-31 |  | EP |  | 15 | 30 | 2.66 |  | 2.66 | 2021-11-19 |  |  |  | FALSE
P19092014 |  | b3353.6 | Remote end work will be required at Prestonsburg, Stanville and McKinney stations. (Conversion of S2405.6) | TO Criteria Violation |  | 2026-12-01 |  | 2024-11-15 | 2027-12-31 |  | EP |  | 15 | 30 | 0.34 |  | 0.34 | 2021-11-19 |  |  |  | FALSE
P22110020 |  | b3359 | Rebuild approximately 2.3 miles of the existing North Van Wert Sw-Van Wert 69 kV line utilizing 556 ACSR conductor. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 | 2027-01-06 |  | EP |  | 0 | 50 | 6.2 |  | 6.2 | 2021-11-19 |  |  |  | FALSE
P21043015 |  | b3360 | Replace Thelma Transformer #1 with a 138/69/46 kV 130/130/90 MVA transformer and replace 46 kV risers and relaying toward Kenwood substation. Existing TR#1 to be used as spare. | TO Criteria Violation |  | 2026-12-01 |  | 2027-12-16 | 2026-11-20 |  | EP |  | 15 | 50 | 3.54 |  | 3.54 | 2021-11-19 |  |  |  | FALSE
A20045015 |  | b3361 | Rebuild Prestonsburg - Thelma 46kV circuit connecting though Kenwood station, approximately 12.7 miles. Retire Jenny Wiley SS and Van Lear SS. | TO Criteria Violation |  | 2026-12-01 | 2027-12-16 | 2027-12-16 |  |  | EP |  | 0 | 50 | 63.6 |  | 63.6 | 2021-11-19 |  |  |  | FALSE
P21773002 |  | b3362 | Rebuild approximately 3.1 miles of the overloaded conductor on the existing Oertels Corner-North Portsmouth 69 kV line utilizing 556 ACSR. | TO Criteria Violation |  | 2026-06-01 |  | 2026-05-01 | 2026-10-20 |  | EP |  | 15 | 50 | 8 |  | 8 | 2021-11-19 |  |  |  | FALSE
P23027003 |  | b3722 | Rebuild the existing Darrah-Barnett 69 kV line, approximately 2.8 miles and replace a riser at Darrah station. | TO Criteria Violation |  | 2027-12-01 |  | 2027-12-01 | 2028-03-29 |  | EP |  | 0 | 10 | 6.98 |  | 6.98 | 2022-10-14 |  |  |  | FALSE
P21036003 |  | b3723 | Rebuild the George Washington – Kammer 138 kV circuit, except for 0.1-mile of previously-upgraded T-line outside each terminal station (6.7 miles of total upgrade scope). Remove the existing 6-wired steel lattice towers and supplement the right-of-way as needed. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2024-06-01 |  | 2025-04-14 | UC | IS | 50 | 100 | 18.3 |  | 18.3 | 2022-10-14 |  |  |  | FALSE
P19296003 |  | b3724 | Install 138 kV circuit switcher on the high-side of Transformer #2 at Roanoke station (previously proposed as a portion of s2469.7, posted in 2021 AEP local plan). | TO Criteria Violation |  | 2027-06-01 |  | 2025-03-20 | 2027-08-18 |  | EP |  | 0 | 10 | 0.1 |  | 0.1 | 2022-10-14 |  |  |  | FALSE
P17002006 |  | b3731 | Replace 40kV breaker J at McComb station with a new 3000A 40kA breaker | TO Criteria Violation |  | 2027-06-01 |  | 2025-06-01 | 2028-08-14 |  | EP |  | 0 | 25 | 0.5 |  | 0.5 | 2022-11-18 |  |  |  | FALSE
P22797001 |  | b3732 | Install a 6 MVAR, 34.5kV cap bank at Morgan Run station | TO Criteria Violation |  | 2027-06-01 |  | 2027-06-01 | 2026-05-15 |  | EP |  | 15 | 50 | 0.37 |  | 0.37 | 2022-11-18 |  |  |  | FALSE
P22968002 |  | b3733 | Rebuild the 1.8 mile 69kV T-line between Summerhill and Willow Grove Switch. Replace 4/0 ACSR conductor with 556 ACSR. | TO Criteria Violation |  | 2027-06-01 |  | 2026-06-23 | 2027-06-01 |  | EP |  | 0 | 10 | 5.1 |  | 5.1 | 2022-11-18 | Rachel Kosarko |  |  | FALSE
P18150035 |  | b3734 | Install a 7.7 MVAR, 69kV cap bank at both Otway station and Rosemount station | TO Criteria Violation |  | 2027-06-01 |  | 2026-06-15 | 2028-02-23 |  | EP |  | 0 | 25 | 1.73 |  | 1.73 | 2022-11-18 |  |  |  | FALSE
P19095004 |  | b3735 | Terminate the existing Broadford – Wolf Hills #1 138 kV line into Abingdon 138 kV Station. This line currently bypasses the existing Abingdon 138 kV Station; Install two new 138 kV circuit breakers on each new line exit towards Broadford and towards Wolf Hills #1; Install one new 138 kV circuit breaker on line exit towards South Abingdon for standard bus sectionalizing | TO Criteria Violation |  | 2027-06-01 |  | 2025-05-01 | 2025-12-10 |  | EP | UC | 15 | 75 | 8.48 |  | 8.48 | 2022-11-18 |  |  |  | FALSE
P19037013 |  | b3736.1 | Establish 69kV bus and new 69 kV line CB at Dorton substation. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-03-16 |  | EP |  | 0 | 50 | 1.13 |  | 1.13 | 2022-11-18 |  |  |  | FALSE
P19037014 |  | b3736.2 | At Breaks substation, reuse 72kV breaker A as the new 69kV line breaker. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-05-18 |  | EP |  | 0 | 50 | 0.71 |  | 0.71 | 2022-11-18 |  |  |  | FALSE
P19037004, P19037005 |  | b3736.3 | Rebuild ~16.7 mi Dorton – Breaks 46kV line to 69kV | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-03-16 |  | EP |  | 0 | 50 | 58.52 |  | 58.52 | 2022-11-18 |  |  |  | FALSE
P19037020 |  | b3736.4 | Retire ~17.2 mi Cedar Creek – Elwood 46kV circuit. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2030-08-01 |  | EP |  | 0 | 10 | 11.15 |  | 11.15 | 2022-11-18 |  |  |  | FALSE
P19037020 |  | b3736.5 | Retire ~ 6.2 mi Henry Clay – Elwood 46kV line section. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-11-08 |  | EP |  | 0 | 50 | 4.3 |  | 4.3 | 2022-11-18 |  |  |  | FALSE
P19037008 |  | b3736.6 | Retire Henry Clay 46 kV substation and replace with Poor Bottom 69 kV station. Install a new 0.7 mi double circuit extension to Poor Bottom 69kV. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-03-16 |  | EP |  | 0 | 50 | 3.42 |  | 3.42 | 2022-11-18 |  |  |  | FALSE
P19037015 |  | b3736.7 | Retire Draffin substation and replace with a new substation. Install a new 0.25 mi double circuit extension to New Draffin substation. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-09-01 |  | EP |  | 0 | 50 | 2.01 |  | 2.01 | 2022-11-18 |  |  |  | FALSE
P19037029 |  | b3736.8 | Remote End work at Jenkins substation | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-03-16 |  | EP |  | 0 | 50 | 0.03 |  | 0.03 | 2022-11-18 |  |  |  | FALSE
P19037023, P19037024, P19037028, P19037030 |  | b3736.9 | Provide Transition fiber to Dorton, Breaks, Poor Bottom, Jenkins and New Draffin substations | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-03-16 |  | EP |  | 0 | 50 | 0.41 |  | 0.41 | 2022-11-18 |  |  |  | FALSE
P19037001 |  | b3736.10 | Henry Clay S.S Retirement: | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-09-01 |  | EP |  | 0 | 50 | 0.3 |  | 0.3 | 2022-11-18 |  |  |  | FALSE
P19037018 |  | b3736.11 | Cedar Creek substation work | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2029-11-15 |  | EP |  | 0 | 10 | 0.44 |  | 0.44 | 2022-11-18 |  |  |  | FALSE
P19037014 |  | b3736.12 | Breaks substation retire 46kV equipment: | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-05-18 |  | EP |  | 0 | 50 | 0.25 |  | 0.25 | 2022-11-18 |  |  |  | FALSE
P19037019 |  | b3736.13 | Retire Pike 29 SS and Rob Fork SS | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2029-11-15 |  | EP |  | 0 | 10 | 0.42 |  | 0.42 | 2022-11-18 |  |  |  | FALSE
P19037022 |  | b3736.14 | Serve Pike 29 and Rob Fork customers from nearby 34kV Distribution sources. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2029-11-15 |  | EP |  | 0 | 10 | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
P19037008 |  | b3736.15 | Poor Bottom substation install | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-03-16 |  | EP |  | 0 | 50 | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
P19037008 |  | b3736.16 | Henry Clay 46kV substation retirement | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-03-16 |  | EP |  | 0 | 50 | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
P19037016 |  | b3736.17 | New Draffin 69kV substation install | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-03-23 |  | EP |  | 0 | 50 | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
P19037015 |  | b3736.18 | Draffin 46kV substation retirement | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 | 2028-09-01 |  | EP |  | 0 | 50 | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
P22055006 |  | b3763 | Replace the Jug Street 138kV breakers M, N, BC, BF, BD, BE, D, H, J, L, BG, BH, BJ, BK with 80KA breakers | Short Circuit |  | 2024-06-01 |  | 2024-06-01 |  | 2025-04-08 | EP | IS | 50 | 100 | 14 |  | 14 | 2022-12-16 |  |  |  | FALSE
P21751001 |  | b3764 | Replace the Hyatt 138kV breakers AB1 and AD1 with 63kA breakers | Short Circuit |  | 2024-06-01 |  | 2024-06-01 | 2025-12-09 |  | EP |  | 15 | 50 | 2 |  | 2 | 2022-12-16 |  |  |  | FALSE
P22052004, P22052005 |  | b3766.1 | Hayes – New Westville 138 kV line: Build ~0.19 miles of 138 kV line to the Indiana/ Ohio State line to connect to AES’s line portion of the Hayes – New Westville 138 kV line with the conductor size 795 ACSR26/7 Drake. The following cost includes the line construction and ROW. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2026-01-08 | 2027-06-17 |  | EP |  | 0 | 25 | 0.38 |  | 0.38 | 2022-12-06 |  |  |  | TRUE
P22052007, P22052008, P22052014 |  | b3766.2 | Hayes – Hodgin 138 kV line: Build ~0.05 miles of 138 kV line with the conductor size 795 ACSR26/7 Drake. The following cost includes the line construction, ROW, and fiber. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2026-01-08 | 2027-06-17 |  | EP |  | 0 | 25 | 1.22 |  | 1.22 | 2022-12-06 |  |  |  | TRUE
P22052001, P22052002, P22052003, P22052006 |  | b3766.3 | Hayes 138 kV: Build a new 4-138 kV circuit breaker ring bus. The following cost includes the new station construction, property purchase, metering, station fiber and the College Corner –Randolph 138 kV line connection. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2026-01-08 | 2027-06-17 |  | EP |  | 0 | 25 | 7.44 |  | 7.44 | 2022-12-06 |  |  |  | TRUE
P23010002 |  | b3775.6 | Perform sag study mitigation work on the Dumont-Stillwell 345 kV line (remove a center-pivot irrigation system from under the line, allowing for the normal and emergency ratings of the line to increase, replace two structures and modify a third structure). | Congestion Relief - Economic¦Baseline Load Growth Deliverability & Reliability |  | 2026-12-01 |  | 2026-11-20 |  |  | EP |  | 15 | 50 | 2.22 |  | 2.22 | 2023-04-11 |  |  |  | TRUE
P23010001, P23010004 |  | b3775.7 | Upgrade the limiting element at Dumont substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | Congestion Relief - Economic¦Baseline Load Growth Deliverability & Reliability |  | 2026-12-01 |  | 2026-12-01 |  |  | EP |  | 15 | 50 | 2 |  | 2 | 2023-04-11 |  |  |  | TRUE
P23018001, P23018002 |  | b3775.10 | Perform a sag study on the Olive – University Park 345kV line to increase the operating temperature to 225 F. Remediation work includes two tower replacements on the line. | Congestion Relief - Economic¦Baseline Load Growth Deliverability & Reliability |  | 2026-12-01 |  | 2026-12-01 |  |  | EP |  | 0 | 10 | 1.5 |  | 1.5 | 2023-01-10 |  |  |  | TRUE
P23010001 |  | b3775.11 | Upgrade the limiting element at Stillwell substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | Congestion Relief - Economic¦Baseline Load Growth Deliverability & Reliability |  | 2026-12-01 |  | 2026-12-01 |  |  | EP |  | 15 | 50 | 0.14 |  | 1.78 | 2023-04-11 |  |  |  | TRUE
P24141001 |  | b3784.1 | Replace 138kV breaker 5 at Canal St station with a new 3000A 63kA breaker | Short Circuit |  | 2028-06-01 |  | 2028-02-24 |  |  | EP |  | 0 | 10 | 0.5 |  | 0.5 | 2023-11-17 |  |  |  | FALSE
P24043001 |  | b3785.1 | Replace existing 3000A wave trap at Mountaineer 765 kV, on the Belmont-Mountaineer 765 kV line, with a new 5000 A wave trap. | Baseline Load Growth Deliverability & Reliability |  | 2028-06-01 |  | 2028-06-01 | 2026-10-07 |  | EP |  | 0 | 25 | 0.46 |  | 0.46 | 2023-12-05 |  |  |  | FALSE
P24081002 |  | b3786.1 | Rebuild ~4.5 miles of 69 kV line between Abert and Reusens substations. Update line settings at Reusens and Skimmer. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 | 2029-11-16 |  | EP |  | 0 | 10 | 14.4023 |  | 14.4023 | 2023-11-17 |  |  |  | FALSE
|  | b3787.1 | Install a CCVT on three-phase stand and remove the single phase existing CCVT on the 69 kV Coalton to Bellefonte line exit. The existing CCVT is mounted to lattice on a single-phase CCVT stand, which will be replaced with the three-phase CCVT stand. The line riser between line disconnect and line takeoff is being replaced. This remote end work changes the MLSE of the line section between Coalton-Princess 69 kV line section. | TO Criteria Violation |  | 2028-12-01 |  | 2028-12-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 |  |  |  | FALSE
P23837001 |  | b3788.1 | Replace AEP-owned station takeoff riser and breaker BB risers at OVEC-owned Kyger Creek station. | Baseline Load Growth Deliverability & Reliability |  | 2028-06-01 |  | 2028-06-01 | 2027-11-18 |  | EP |  | 0 | 10 | 0.41 |  | 0.41 | 2023-12-05 |  |  |  | TRUE
P24034001, P24034002 |  | b3790.0 | Replace the overdutied Olive 345 kV circuit breaker "D" with a 5000A 63 kA circuit breaker. Reuse existing cables and a splice box to support the circuit breaker install. | Short Circuit |  | 2028-06-01 |  | 2028-06-01 | 2026-11-19 |  | EP |  | 15 | 50 | 1.083 |  | 1.083 | 2023-12-05 |  |  |  | FALSE
P24059001, P24059002 |  | b3800.100 | Establish a new 500 kV breaker position for the low-side of the existing 765/500 kV transformer at Cloverdale Station. The new position will be between two new 500 kV circuit breakers located in a new breaker string, electrically converting the 500 kV yard to "double-bus double-breaker" configuration. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  |  | EP |  | 0 | 10 | 11.591 |  | 11.591 | 2023-12-05 |  |  |  | FALSE
P23878001 |  | b3800.121 | Kammer to 502 Junction 500 kV line: Conduct LIDAR Sag Study to assess SE rating and needed upgrades. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2023-12-05 |  |  |  | FALSE
P24014001 |  | b3836.1 | Rebuild approximately 1.7 miles of line on the Chemical-Washington Street 46 kV circuit. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  |  | EP |  | 0 | 10 | 7.6 |  | 7.6 | 2023-11-17 |  |  |  | FALSE
P23027013 |  | b3837.1 | Replace existing 34.5 kV, 25 kA circuit breaker B at West Huntington station with new 69 kV, 40 kA circuit breaker. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 | 2028-11-06 |  | EP |  | 0 | 10 | 0.3648 |  | 0.3648 | 2023-11-17 |  |  |  | FALSE
P24004001 |  | b3838.1 | Replace breaker A and B at Timken station with 40 kA breakers. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  |  | EP |  | 0 | 10 | 1.2 |  | 1.2 | 2023-11-17 |  |  |  | FALSE
P24063001 |  | b3839.1 | Replace 69 kV breaker C at Haviland station with a new 3000A 40 kA breaker. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2023-11-17 | Manager4 |  |  | FALSE
P23877002 |  | b3843.1 | Rebuild the underground portion of the Ohio University-West Clark 69 kV line, approximately 0.65 miles. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  |  | EP |  | 0 | 10 | 4.6 |  | 4.6 | 2023-11-17 |  |  |  | FALSE
P24051001 |  | b3847.1 | Add a 765 kV breaker at Baker station for the reactor on the Broadford 765 kV line. | Operational Performance |  | 2024-06-01 |  | 2027-06-25 |  |  | EP |  | 0 | 50 | 23.3564 |  | 23.36 | 2024-06-05 | PM Jacob Arwood |  |  | FALSE
P24052001 |  | b3847.2 | Add two 765 kV breakers to the reactors at Broadford station on the Baker and Jacksons Ferry 765 kV lines. | Operational Performance |  | 2024-06-01 |  | 2027-06-01 | 2028-06-19 |  | EP |  | 0 | 10 | 29.0472 |  | 29.05 | 2024-06-05 | PM Blair Burns |  |  | FALSE
P24049001 |  | b3847.3 | Add a 765 kV breaker to the reactor at Jefferson station on the Greentown 765 kV line. | Operational Performance |  | 2024-06-01 |  | 2027-04-15 |  |  | EP |  | 0 | 50 | 8.5319 |  | 8.53 | 2024-06-05 | PM Kyle Martin / Planner Sharlene Rivera Gonzalez |  |  | FALSE
P24084001 |  | b3851.1 | Rebuild Allen –R.P. Mone 345kV line (18.6 miles). | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  |  | EP |  | 0 | 10 | 49.875 |  | 49.875 | 2024-07-10 | PM Shawn Lynch / Planner Valerie Watros |  |  | FALSE
P24084002 |  | b3851.2 | Rebuild R.P. Mone – Maddox Creek 345kV line (9.4 miles). | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  |  | EP |  | 0 | 10 | 39.034 |  | 39.034 | 2024-07-09 | PM Shawn Lynch / Planner Valerie Watros |  |  | FALSE
P24092001 |  | b3851.3 | Replace breakers 'B1' and 'B' at Maddox Creek. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  |  | EP |  | 0 | 10 | 1.8 |  | 1.8 | 2024-07-09 | PM Shawn Lynch / Planner Valerie Watros |  |  | FALSE
P24092002 |  | b3851.4 | Replace two 345kV breakers 'M' and 'M2' at East Lima Station. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  |  | EP |  | 0 | 10 | 1.761 |  | 1.761 | 2024-07-09 | PM Shawn Lynch / Planner Valerie Watros |  |  | FALSE
P22915001 |  | b3852.1 | Connect and energize a second 765/345 kV bank at Vassell station. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2026-07-15 |  |  | EP | UC | 0 | 75 | 30.829 |  | 30.829 | 2024-07-09 |  |  |  | FALSE
|  | b3852.2 | Replace 765 kV breaker D at Maliszewski station. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  |  | EP |  | 0 |  | 2.9 |  | 2.9 | 2024-07-09 |  |  |  | FALSE
|  | b3872.1 | Adjust the tertiary tap on the Hartford 138/69/34.5 kV transformer 1 and on Hartford 138/69/12 kV transformer 4 to eliminate the high voltage issues and avoid circulating current. | TO Criteria Violation |  | 2029-04-15 |  | 2029-04-15 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2024-11-15 |  |  |  | FALSE
|  | b3873.1 | Install 12 MVAR 34.5 kV cap bank at Greenleaf | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 1.3139 |  | 1.3139 | 2024-11-15 |  |  |  | FALSE
|  | b3875.1 | Reconductor ~3.95 miles of ACSR 6/1 Penguin (4/0) on the Firebrick-Jefferson Switch 69 kV branch with ACSR 556.6 26/7. Remote End (Line setting) would need to be updated at Firebrick and Lick. Replace 600A Switches at Jefferson and replace 477 AA 19 sub conductor at Firebrick. | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 8.5 |  | 8.5 | 2024-11-15 |  |  |  | FALSE
|  | b3876.1 | Install a 69kV 11.5MVar capacitor bank at Richlands station with a circuit switcher. | TO Criteria Violation |  | 2029-12-01 |  | 2029-12-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2024-11-15 |  |  |  | FALSE
|  | b3877.1 | Project will replace station conductor and switches in the 345 kV yard at Beatty that are currently limiting the 345 kV lines to Adkins and Chenoweth | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2024-12-03 |  |  |  | FALSE
|  | b3877.2 | Project will upgrade 345 kV circuit breakers 'A' and 'A1' to 4000A 63 kA breakers at Adkins station along with some station conductor that is currently limiting the 345 kV line to Beatty. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 4.5 |  | 4.5 | 2024-12-03 |  |  |  | FALSE
|  | b3878.1 | Proposal will upgrade 765 kV circuit breakers 'B' and 'B2' 'to 5000A 50 kA breakers at Marysville station. In addition, the project will upgrade the existing wavetrap towards Sorenson. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 10 |  | 10 | 2025-01-07 |  |  |  | FALSE
|  | b3879.1 | Replace line conductor, ~0.11 miles of 4/0 ACSR 6/1 conductor with 556.5 26/7 between South Toronto and the South Toronto Tap. | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2024-11-15 |  |  |  | FALSE
|  | b3879.2 | Upgrade the wave trap, CCVTs, switches, and station conductor at South Toronto station currently limiting the line to South Toronto Tap. | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2024-11-15 |  |  |  | FALSE
|  | b3880.1 | At Beatty Road substation, install a 69 kV 23 MVAR capacitor bank along with the 69kV Cap bank breaker. | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 2.25 |  | 2.25 | 2024-11-15 |  |  |  | FALSE
|  | b3882.1 | Replace 138 kV circuit breaker BB with higher fault current capable counterpart. | Short Circuit |  | 2026-06-01 |  | 2026-06-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2024-11-15 |  |  |  | FALSE
|  | b3883.1 | 69 kV station equipment, including relays, conductor, and switches, will be replaced at Haviland station in order to address identified overloads on the lines to North Van Wert and Cavett. | TO Criteria Violation |  | 2029-12-01 |  | 2029-12-01 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2024-11-15 |  |  |  | FALSE
|  | b3884.1 | Replace the 69 kV circuit breaker D at Van Wert with a 40 kA breaker. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2024-11-15 |  |  |  | FALSE
|  | b3885.1 | Replace 69 kV circuit breakers N and M at Schroyer Avenue station with higher fault current capable counterparts. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  |  | EP |  | 0 |  | 2 |  | 2 | 2024-11-15 |  |  |  | FALSE
|  | b3886.1 | Replace 69 kV circuit breaker 'A' along with disconnect switches at Benwood substation with a 40 kA Circuit Breaker. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2024-11-15 |  |  |  | FALSE
|  | b3887.1 | Replace Greentown 138kV circuit switcher for Transformer #5 with a 138kV 63kA Circuit Breaker | Short Circuit |  | 2026-06-01 |  | 2026-06-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2024-11-15 |  |  |  | FALSE
|  | b3888.1 | Preform sag study and complete mitigations on the 138 kV line between East Leipsic and the AE2-072 tap (Lammer) to allow line's conductor to operate to its maximum operating temperature (MOT). | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 2.5 |  | 2.5 | 2024-11-15 |  |  |  | FALSE
|  | b3889.1 | Project will replace limiting station equipment at Tiltonsville station to increase the rating on the branch to Windsor | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2024-11-15 |  |  |  | TRUE
|  | b3890.1 | Replace station conductor at South Coshocton station currently limiting the branch to Ohio Central | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2024-11-15 |  |  |  | FALSE
|  | b3891.1 | Project will perform relay upgrades at Kenny 138 kV to raise the CT & Relay thermal limits that are currently limiting the line to Roberts. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2024-11-15 |  |  |  | FALSE
|  | b3892.1 | Replace 69 kV circuit breakers A and S at Mount Vernon station with 40 kA breakers. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  |  | EP |  | 0 |  | 2 |  | 2 | 2024-11-15 |  |  |  | FALSE
|  | b3894.1 | Replace limiting station conductor at Tidd on the line to Carnegie (FE). | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2024-11-15 |  |  |  | FALSE
|  | b3895.1 | Replace existing 138 kV, 40 kA Circuit Switcher L at Jacksons Ferry Station with new 138 kV, 63 kA Circuit Breaker | Short Circuit |  | 2026-06-01 |  | 2026-06-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2024-11-15 |  |  |  | FALSE
|  | b3896.1 | Adjust the capacitor bank voltage settings to allow the cap bank to operate as needed under N-1-1 scenarios. | TO Criteria Violation |  | 2029-12-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2024-11-15 |  |  |  | FALSE
|  | b3897.1 | Replace the 138 kV 40kA circuit switcher XT8 with a 63 kA circuit breaker. | Short Circuit |  | 2026-06-01 |  | 2026-06-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2024-11-15 |  |  |  | FALSE
|  | b3898.1 | Upgrade the CT thermal limit at Buchanan station on the Buchanan-Keen Mountain 138 kV line. | Baseline Load Growth Deliverability & Reliability |  | 2029-12-01 |  | 2025-12-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2024-11-15 |  |  |  | FALSE
|  | b3911.1 | Rebuild the existing 1.1 mile Canal - Gay 138 kV oil filled pipe-type underground line to address overloads on the existing cable utilizing 5000 MCM XLPE cable. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 15.595 |  | 15.595 | 2024-12-03 |  |  |  | FALSE
|  | b3912.1 | Rebuild the existing 2.2-mile Canal-Mound St 138 kV oil filled pipe-type underground line to address overloads on the existing cable utilizing 5000 MCM XLPE cable. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 31.09 |  | 31.09 | 2024-12-03 |  |  |  | FALSE
|  | b3913.1 | Rebuild 138 kV line section between Beatty and White Road stations (approximately 4.5 miles). Update remote end relay settings as needed. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 18.8 |  | 18.8 | 2024-12-03 |  |  |  | FALSE
|  | b3913.2 | Rebuild 138 kV line section between White Road and Cyprus stations (approximately 3.34 miles). Update remote end relay settings as needed. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 14.313 |  | 14.313 | 2024-12-03 |  |  |  | FALSE
|  | b3919.1 | Reconfigure Maliszewski 765 kV station from 2 breakers to a 6 breaker ring bus. Install a new 765/345 kV transformer. Establish new 345 kV breaker yard with 3 string breaker and a half to include a line exit to Hyatt and a line exit to Corridor. Loop the existing Hyatt - West Millersport 345 kV line into the new established 345 kV yard at the Maliszewski station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 79.736 |  | 79.736 | 2024-12-03 |  |  |  | FALSE
|  | b3919.2 | Establish a 0.18 mile double circuit 345 kV line extension to cut the existing Hyatt – West Millersport 345 kV line in and out of Corridor station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 3.101 |  | 3.101 | 2024-12-03 |  |  |  | FALSE
|  | b3919.3 | Install three new 345 kV breakers at Corridor station in order to accommodate the cut in of the Hyatt- West Millersport 345 kV line. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 5.521 |  | 5.521 | 2024-12-03 |  |  |  | FALSE
|  | b3919.4 | Reconductor 10.2-mile of Maliszewski-Corridor 345 kV line. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 18.301 |  | 18.301 | 2024-12-03 |  |  |  | FALSE
|  | b3919.5 | Reconductor 4.75-miles of the existing Bokes Creek-Marysville 345 kV circuit. Update the associated relay settings. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 6.668 |  | 6.668 | 2024-12-03 |  |  |  | FALSE
|  | b3919.6 | Rebuild 4.4-miles of the existing Marysville - Hyatt 345 kV double circuit line where it extends into Marysville station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 26.256 |  | 26.256 | 2024-12-03 |  |  |  | FALSE
|  | b3919.7 | Upgrade 345 kV breakers K & K1 along with associated switches and conductor to 5000A at Hyatt Station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 2.944 |  | 2.944 | 2024-12-03 |  |  |  | FALSE
|  | b3919.8 | Upgrade the relaying and associated equipment at West Millersport stationto coordinate with the cut in work to Corridor station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.41 |  | 0.41 | 2024-12-03 |  |  |  | FALSE
|  | b3919.9 | Upgrade 3000A 345 kV breaker 'L2' along with associated terminal elements to 5000A at Marysville. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 2.558 |  | 2.558 | 2024-12-03 |  |  |  | FALSE
|  | b3919.10 | Rebuild ~19.0 miles of Hyatt - Marysville 345 kV line using 4-bundled 795 ACSR conductor Bold construction (This is an EOL rebuild) | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2027-06-01 |  |  | EP |  | 0 |  | 116.7 |  | 116.7 | 2025-01-07 |  |  |  | FALSE
|  | b4000.1 | Add one 765 kV breaker at Amos Substation to expand the breaker and a half scheme to accommodate the new Amos-Welton Spring 765 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 30.87 |  | 30.87 | 2025-01-07 |  |  |  | TRUE
|  | b4000.200 | Broadford 765 kV Upgrade: Replace Jackson's Ferry CB Q2 | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 4.5 |  | 4.5 | 2025-01-07 |  |  |  | FALSE
|  | b4000.201 | Smith Mountain 138 kV Upgrade: Replace 795 KCM AAC, 37-Str. 795 KCM AAC, 37-Str. PH A B2S1 B2S2 BS1 BS2 | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2025-01-07 |  |  |  | FALSE
|  | b4000.202 | Rebuild 12.5 miles of Smith Mountain - Redeye 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 14.9 |  | 14.9 | 2025-01-07 |  |  |  | FALSE
|  | b4000.203 | Rebuild 17.5 miles of Redeye - Candler's Mountain 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 21 |  | 21 | 2025-01-07 |  |  |  | FALSE
|  | b4000.204 | Rebuild 4 miles of Candler's Mountain - Opossum Creek 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 4.9 |  | 4.9 | 2025-01-07 |  |  |  | FALSE
|  | b4000.205 | Candler's Mountain 138 kV: Replace 1590 KCM AAC, 61-Str. Replace MOAB "Y" SMITH MTN LINE | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2025-01-07 |  |  |  | FALSE
|  | b4000.206 | Opposum Creek 138 kV: Replace Opossum Creek Switch | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2025-01-07 |  |  |  | FALSE
|  | b4000.207 | Leesville Station Upgrade 138 kV: Replace 795 KCM AAC, 37-Str. IPS Sch. 40 1272 KCM AAC, 61-Str. 1272 KCM AAC, 61-Str. PH A,B,C ALTA VISTA CB-A BUS DISC ALTA VISTA CB-A LINE DISC Wavetrap (1200A) Relay Thermal Limit 1356 Amps | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2025-01-07 |  |  |  | TRUE
|  | b4000.208 | Otter 138 kV Station Upgrade: Replace 795 KCM AAC, 37-Str. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2025-01-07 |  |  |  | FALSE
|  | b4000.209 | Rebuild 0.9 miles of Altavista - Otter 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2025-01-07 |  |  |  | TRUE
|  | b4000.210 | Rebuild 7 miles of Otter - Johnson Mountain 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 8.4 |  | 8.4 | 2025-01-07 |  |  |  | FALSE
|  | b4000.211 | Rebuild 6.5 miles of Johnson Mountain - New London 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 7.68 |  | 7.68 | 2025-01-07 |  |  |  | FALSE
|  | b4000.251 | Replace the wave trap and upgrade the relay at Cloverdale 765kV substation | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2025-01-07 |  |  |  | FALSE
|  | b4000.252 | Replace the wave trap and upgrade the relay at Joshua Falls 765kV substation | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2025-01-07 |  |  |  | FALSE
|  | b4000.355 | Build a new 156 mile 765kV line from Joshua Falls – Yeat. (Roughly 69.3 miles in AEP section). | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 341.17 |  | 341.17 | 2025-01-07 |  |  |  | TRUE
|  | b4000.359 | Add (2) 765kV breakers at Joshua Falls substation. Substation expansion is required to add the additional breakers. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  |  | EP |  | 0 |  | 99.19 |  | 99.19 | 2025-01-07 |  |  |  | FALSE
P16123010 |  | s1297 | Valley Area Reinforcement project | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 | 2025-07-17 |  | UC |  | 50 |  | 143 |  | 143 | 2017-05-31 | Alvaro Rodriguez/ Joshua Smith |  |  | FALSE
P16123010 |  | s1297.5 | At Main Street station, rebuild the entire station on existing property at the site and install a 90 MVA transformer with 3000 A 40 kA breakers. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 | 2025-07-17 |  | UC |  | 50 |  | 0 |  | 0 | 2017-05-31 | Alvaro Rodriguez/ Joshua Smith |  |  | FALSE
P12059014 |  | s1377.3 | Lavalette: Install 138kV MOAB facing West Huntington. Replace high-speed ground switch/MOAB combo on XFR #1 with a circuit switcher. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-17 | 2026-05-22 |  | UC |  | 50 |  | 0.1 |  | 0.1 | 2017-12-18 | PM Aaron Crespin/Planner Michael Hassay |  |  | FALSE
P12059003 |  | s1377.4 | Stone Branch: Replace high-speed ground switch/MOAB combo on XFRs #1 and #2 with circuit switchers. Install 138kV MOABs facing Midkiff and Chapman. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-09-09 | 2026-02-19 |  | UC |  | 50 |  | 0.2 |  | 0.2 | 2017-12-18 | PM Alvaro Rodgriguez/planner Chintan Raval |  |  | FALSE
P12059004 |  | s1377.5 | Chapman: Retire Trace Fork S.S. and 4-way switch and replace with Chapman Switching Station located ~1 mile away. Install 4 138kV 3000 A 40 kA CB ring bus at new Chapman. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-08 | 2026-03-16 |  | UC |  | 50 |  | 5.7 |  | 5.7 | 2017-12-18 | PM Alvaro Rodgriguez/planner Chintan Raval |  |  | FALSE
P12059009 |  | s1377.7 | Construct an 8 mile 138kV double circuit line between Sheridan and Midkiff utilizing 1033.5 ACSR (375/464 MVA winter ratings) and OPGW. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-12-12 |  |  | UC |  | 50 |  | 25.7 |  | 25.7 | 2017-12-18 | PM Alvaro Rodgriguez/planner Chintan Raval |  |  | FALSE
P12059009 |  | s1377.8 | Construct a 17 mile 138kV line between Midkiff and Stone Branch utilizing 1033.5 ACSR (375/464 MVA winter ratings) and OPGW. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-12-12 |  |  | UC |  | 50 |  | 28.1 |  | 28.1 | 2017-12-18 | PM Alvaro Rodgriguez/planner Chintan Raval |  |  | FALSE
P12059011 |  | s1377.9 | Construct 138kV double circuit line from Chapman to existing 138kV Stone Branch – Trace Fork line utilizing 1033.5 ACSR (375/464 MVA winter ratings). Install OPGW on new line sections. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-08 | 2026-03-16 |  | UC |  | 50 |  | 5.5 |  | 5.5 | 2017-12-18 | PM Aaron Crespin/Planner Chintan Rival |  |  | FALSE
P12059011 |  | s1377.10 | Construct 138kV double circuit line from Chapman to existing 138kV Logan – Hopkins line utilizing 1590 ACSR (493/624 MVA winter ratings) to match the existing Logan-Hopkins line capabilities. Install OPGW on new line sections. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-02-13 | 2026-03-16 |  | UC |  | 50 |  | 5.7 |  | 5.7 | 2017-12-18 | PM Aaron Crespin/Planner Michael Hassay |  |  | FALSE
A15701002 |  | s1414 | Anaconda 34.5 kV Station Rebuild | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-18 | 2026-01-20 |  | UC |  | 31 |  | 1.49 |  | 1.49 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  |  | FALSE
A15701181 |  | s1414.1 | Anaconda : Retire the current Anaconda 34.5KV station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-31 |  |  | UC |  | 31 |  | 0.04 |  | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  |  | FALSE
A15701063 |  | s1414.2 | Anaconda Tap switch : Retire Anaconda Tap and reconnect Hummel Creek – Deer Creek circuit | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-18 | 2026-01-20 |  | UC |  | 31 |  | 0.01 |  | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  |  | FALSE
A15701200 |  | s1414.3 | Wire Mill: Install a 4kV bus with a CB protecting the Anaconda load; Install a 34.5kV bus; Install a 6.25MVA 69/34.5/4kV non-LTC transformer to connect the 4kV and 34.5kV busses; Install a circuit switcher on the high side of the transformer | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-22 | 2025-10-21 |  | UC |  | 50 |  | 0.02 |  | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  |  | FALSE
A15041032 |  | s1414.4 | Shunk Street Switch: Install a new 1200A 3 way PoP ground operated switching structure | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-22 | 2025-10-21 |  | UC |  | 31 |  | 0 |  | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  |  | FALSE
A15041032 |  | s1414.5 | Fifth Street Extension: Install roughly .5 miles of 556.5 ACSR (WE: 80MVA) from Shunk Street Switch to the new station location. This line will be built to 69kV but operated at 34.5kV | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-22 | 2025-10-21 |  | UC |  | 50 |  | 0 |  | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  |  | FALSE
A15701063 |  | s1414.6 | Anaconda Tap: Retire the Anaconda - Anaconda Tap 34.5kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-18 | 2026-01-20 |  | UC |  | 31 |  | 0 |  | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  |  | FALSE
A16803026 |  | s1431 | Rebuild ~11 miles of the Hopkins – Sharples circuit including ~2.6 miles of the Hopkins – Bim line that is double circuited with Hopkins – Sharples. Replace switches at Hewett station with 1200A 3-way Phase Over Phase switch. On all lines, install OPGW. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-20 |  |  | UC |  | 50 |  | 23.7 |  | 61.73 | 2020-11-20 | PM Chance Strausbough/planner Michael Hassay |  |  | FALSE
A16801111 |  | s1432.1 | Rebuild from Ross to Heppner Sw (formerly Coalton Sw). Single Circuit 138kV Rebuild (Energized at 69kV) with 1033 ACSR Curlew Conductor (148 MVA SN rating) | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-25 |  |  | UC |  | 50 |  | 46.2 |  | 46.2 | 2018-01-08 | PM Robert Howard/ planner Peter Jones |  |  | FALSE
A16801096 |  | s1493.2 | Rebuild single circuit 69kV line from Harrison to Madison with 795 ACSR (129 MVA rating), mostly in existing ROW | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-08-09 | 2027-04-29 |  | EP |  | 35 |  | 23.4 |  | 23.4 | 2018-02-14 | planner Nathen Roberts |  |  | FALSE
A16801130 |  | s1493.3 | Rebuild tap to Darbyville as double circuit 795 ACSR (129 MVA rating) | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-16 | 2027-01-07 |  | On Hold | EP | 50 |  | 0.9 |  | 0.9 | 2018-02-14 | Brooks Arbogast/ Nathen Roberts |  |  | FALSE
P19015021 |  | s1590 | At Butler station, replace 69 kV breaker “A”, replace 69 kV MOABs “X” and “Y” with 69 kV breakers, replace 69 kV cap switchers “AA” and “BB” (S&C Mark V) with 3000 A, 40 kA circuit breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-01-16 |  |  | EP |  | 25 |  | 2.5 |  | 2.5 | 2018-04-17 | Tom Newlon/ Michael Van Schaik |  |  | FALSE
P17002006 |  | s1606.3 | At McComb station, replace 2-138kV 1600A 40kA CB’s 101C & 101E and disconnect switches with 3,000A 40kA CB’s. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-06-25 | 2028-08-14 |  | EP |  | 10 |  | 1.3 |  | 1.3 | 2018-04-17 | PM Crystal Wood-Hython/planner Nathen Roberts |  |  | FALSE
P15082C34 |  | s1611.3 | At Twin Branch Station, upgrade risers towards South Bend. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-01-01 | 2025-12-19 |  | UC |  | 50 |  | 1.8 |  | 1.8 | 2018-05-03 | PM Dan Ballmer/planner Joshua Smith |  |  | FALSE
P16123034 |  | s1622.1 | Rebuild the roughly 43 miles from the Twin Branch to Riverside station with double circuit 138kV 1033.5 ACSR (296 MVA rating). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | 2025-02-21 | UC | IS | 50 | 100 | 94.3 |  | 94.3 | 2018-05-21 | Alvaro Rodriguez/ Joshua Smith |  |  | FALSE
P19031001 |  | s1622.3 | Rebuild the 5 mile double circuit Hickory Creek 138kV Extension with double circuit 138kV 1033.5 ACSR. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-09-13 | 2026-09-18 |  | EP |  | 15 |  | 16.5 |  | 16.5 | 2018-05-21 | PM Warren Peterson/Planner Michael Van Schaik |  |  | FALSE
P17225003 |  | s1687.2 | Construct a 2.7 mile 138 kV line extension between Moore Hollow and Kentucky Electric Steel. At this time the existing KES metering structure will be retired due to the announced closure of the KES plant. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-06-23 |  |  | EP |  | 15 |  | 8.4 |  | 8.4 | 2018-08-31 | M. Shawn Smith/ Chintan Raval |  |  | FALSE
P17225027 |  | s1687.3 | At Chadwick Station, remote end relaying work will be required. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-06-23 |  |  | EP |  | 15 |  | 0.4 |  | 0.4 | 2018-08-31 | M. Shawn Smith/ Chintan Raval |  |  | FALSE
P17225006 |  | s1687.4 | Construct a new greenfield 138/19 kV station, named Ramey, tapping the Bellefonte - Grangston 138 kV circuit. Four 138 kV CBs (3000 A 40 kA) will be installed as well as a 138/19 kV transformer (25 MVA). AEP already owns the land at the proposed Ramey station site. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-06-23 |  |  | EP |  | 5 |  | 0 |  | 0 | 2018-08-31 | M. Shawn Smith/ Chintan Raval |  |  | FALSE
P17225013 |  | s1687.5 | Construct a new 2.8 mile 138 kV extension from Ramey to the existing Bellefonte - Coalton line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-12-08 |  |  | EP |  | 15 |  | 10.5 |  | 10.5 | 2018-08-31 | PM M. Shawn Smith/planner Chintan Raval |  |  | FALSE
P17225017 |  | s1687.6 | Convert the existing Bellefonte to Coalton 69 kV line between Bellefonte and Princess to 138 kV (line is built to 138 kV standards). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-12-08 |  |  | EP |  | 15 |  | 3.8 |  | 3.8 | 2018-08-31 | PM M. Shawn Smith/planner Chintan Raval |  |  | FALSE
P17225010 |  | s1687.8 | Convert Hoods Creek station to 138 kV by rebuilding the station in the adjacent lot with a 138/12 kV XF. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-12-08 |  |  | EP |  | 15 |  | 0 |  | 0 | 2018-08-31 | PM M. Shawn Smith/planner Chintan Raval |  |  | FALSE
P17225015 |  | s1687.10 | Construct 3.4 mile 138 kV line between Princess and Moore Hollow stations. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-06-23 |  |  | EP |  | 15 |  | 11.5 |  | 11.5 | 2018-08-31 | M. Shawn Smith mssmith@aep.com (540)759-5581/ Chintan Raval craval@aep.com (614)933-2219 |  |  | FALSE
P16121002 |  | s1692.1 | Build a new 8.5 mile 69 kV line from Friendship Station to Central Portsmouth Station, using 556 ACSR (102 MVA) and remove the old Central Portsmouth-Sugar Hill Line. Rebuild the remaining 13.9 miles of the Friendship Loop from North Portsmouth to Rosemount, from Rosemount to Sugar Hill and from Sugar Hill to Friendship using 556 ACSR (102 MVA) and ADSS. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-12-21 | 2031-01-23 |  | UC | EP | 50 |  | 41.8 |  | 41.8 | 2018-08-31 | PM Michael Deskin/planner Peter Jones |  |  | FALSE
P16121012 |  | s1692.2 | At Friendship station, install a 69 kV line CB & line MOAB. At Sugar Hill station, upgrade bus though-path and replace switches to accommodate the line reconfigurations. At North Portsmouth, replace 138-69 kV transformer with a 90 MVA unit with a 138 kV circuit switcher, replace 138 kV CB C and 69 kV CB A. Remove bus tie 138 kV CB D and install a new 138 kV CB to isolate Millbrook Park line. Install a new 69 kV CB on low side of the transformer. At Millbrook Park, replace relay & install a CCVT on North Portsmouth Line. At Central Portsmouth, replace 138 kV CBs G & H. At Rosemount, install two line MOAB switches inside substation and replace the ground switch MOAB with a 69 kV circuit switcher. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-21 | 2030-10-22 |  | UC | EP | 50 |  | 12.6 |  | 12.6 | 2018-08-31 | PM Michael Deskin/planner Peter Jones |  |  | FALSE
A16922004 |  | s1851 | Construct a new 69 kV line (approximately 14.25 miles) from Jubal Early Station to Point Lookout Station. Install a 69 kV circuit breaker at Jubal Early Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-22 | 2027-11-17 |  | UC | EP | 50 |  | 32.5 |  | 42.7 | 2021-05-21 | PM Charles Linkous/planner Bobby Valerio |  |  | FALSE
P22060001 |  | s1851.1 | Relocate Independence Station to a new property and rebuilt as Point Lookout Station. Point Lookout Station will consist of a 69 kV bus, a 11.5 MVAR cap bank, two 69 kV circuit breakers. The station will also include a 69/34.5 kV 30 MVA transformer with two 34.5 kV distribution circuit breakers and a 69/12 kV 20 MVA transformer with one 12 kV distribution circuit breaker. The new cap bank at Point Lookout Station is replacing the existing cap bank at Fries Station due to the space limitations at Fries Station associated with remote end work. The cap bank at Fries Station can not be retired due to a voltage violation scenario and the new cap bank will maintain the voltages above our criteria thresholds. Estimated Transmission Cost: $0 (station is considered Distribution) | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-22 | 2028-03-15 |  | EP |  | 0 | 10 | 0 |  | 32.5 | 2021-05-17 |  |  |  | FALSE
P21593001 |  | s1854.3 | Rebuild the 34.5 kV voltage class 23rd Street substation as a six (6) breaker ring bus with five (5) new 69 kV-rated breakers. Install three (3) 138 kV breakers to form a ring bus on the high side. Retire the cap banks. Rebuild the underground line exits as overhead. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-08-16 | 2027-11-30 |  | EP |  | 25 | 50 | 0 |  | 11.9 | 2019-08-28 | PM Gray Adam/planner Sharlene Rivera-Gonzalez |  |  | FALSE
P17081003 |  | s2000.2 | Rebuild Esmont-Scottsville 46 kV line section (~6.0 mi.) | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 |  | 2025-06-03 | UC | IS | 50 | 100 | 17 |  | 17 | 2019-05-20 | PM Mark Scotwinterll/planner Bobby Valerio |  |  | FALSE
P18144010 |  | s2012.1 | Retire the ~10.5 mile South Summitville – Jonesboro 34.5 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-24 |  | 2023-10-27 | EP | IS | 15 | 100 | 1.6 |  | 1.6 | 2019-04-23 | PM Tom Newlon/planner Sharlene Rivera-Gonzalez |  |  | FALSE
P18241012 |  | s2013.2 | Retire the Deer Creek – Miller Ave 34.5 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-30 | 2025-09-22 |  | UC |  | 50 |  | 0.6 |  | 0.6 | 2019-05-20 | PM Jarrod Combs/planner Michael Van Schaik |  |  | FALSE
P18241021 |  | s2013.5 | Re-route the Atlas Tap 34.5kV line into West End station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-07-02 | 2025-10-20 |  | UC |  | 50 |  | 0.5 |  | 0.5 | 2019-05-20 | Jarrod Combs/ Michael Van Schaik |  |  | FALSE
P18244005, P18244006, P18244007, P18244008, P18244009, P18244010, P18244011, P18244012 |  | s2014 | Rebuild the 62 mile College Corner – Jay 138 kV line as single circuit 138 kV. New conductor will be 795 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-31 |  | 2024-05-02 | EP | IS | 1 | 100 | 113.5 |  | 113.5 | 2019-05-20 | PM Kent Hice/planner Sharlene Rivera-Gonzalez |  |  | FALSE
P20236005, P20236012 |  | s2017.1 | Replace both 34.5 kV breakers “L” and “M” at Hummel Creek station with system spares. Install a high side circuit switcher on transformer 1. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-31 | 2025-11-21 |  | EP |  | 15 |  | 2.6 |  | 2.6 | 2019-06-17 | Jarrod Combs/ Michael Van Schaik |  |  | FALSE
P20236006 |  | s2017.2 | Remove the existing 34.5 kV breaker at Gas City station and re-use the existing switch as a MOAB. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-16 |  |  | EP |  | 25 |  | 0 |  | 0 | 2019-06-17 | Jarrod Combs/ Michael Van Schaik |  |  | FALSE
P18141023 |  | s2060.11 | Install 69 kV 1200 A phase over phase switch (Fliprock Switch) at National Lime & Stone hard tap. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-04-08 |  |  | EP |  | 25 |  | 2.4 |  | 2.4 | 2019-09-25 | Michael Fackler/ Patrick Hodgson |  |  | FALSE
P17002028 |  | s2062.1 | Extend the Wilson - Hess 138 kV line to the new 138 kV bus at Fifth Avenue station and install fiber between Fifth Ave and Hess. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-07-31 | 2028-08-14 |  | EP |  | 10 |  | 1.1 |  | 1.1 | 2019-09-25 | Denise Binford/ Nathen Roberts |  |  | FALSE
DP19C09Z0 |  | s2062.2 | At Fifth Avenue substation, install new 138 kV bus work in ring bus configuration. Install two (2) 138 kV breakers and associated switches on new bus work rated at 3000 A/63 kA. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-04-25 | 2026-06-05 |  | EP |  | 10 |  | 2.9 |  | 2.9 | 2019-09-25 | PM Denise Binford/planner Nathen Roberts |  |  | FALSE
DP19C09D1 |  | s2062.3 | Remote end work at Wilson Road station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-02-14 | 2026-02-12 |  | EP |  | 10 |  | 0.5 |  | 0.5 | 2019-09-25 | PM Denise Binford/planner Nathen Roberts |  |  | FALSE
DP19C09D2 |  | s2062.4 | Remote end work at Hess station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-12-10 | 2025-12-03 |  | EP |  | 15 |  | 0.6 |  | 0.6 | 2019-09-25 | PM Denise Binford/planner Nathen Roberts |  |  | FALSE
P19031003 |  | s2090.1 | Rebuild 6.7 miles of the 34.5 kV circuit Main Street-Hickory Creek circuit using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-09-13 | 2026-09-18 |  | EP |  | 15 |  | 19.5 |  | 19.5 | 2019-12-05 | PM Warren Peterson/Planner Michael Van Schaik |  |  | FALSE
P19031006 |  | s2090.2 | Rebuild the 0.5 miles of the Langley-Main Street 34.5 kV branch starting from the Langley station using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 | 2026-11-13 |  | EP |  | 15 |  | 3 |  | 3 | 2019-12-05 | PM Warren Peterson/Planner Michael Van Schaik |  |  | FALSE
P19015026 |  | s2098.4 | Build a 0.04 mile long greenfield line with 556 ACSR to eliminate the hard tap on the Butler - Hicksville Junction 138 kV Line. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 | 2026-02-27 |  | EP |  | 25 |  | 0.4 |  | 0.4 | 2019-12-05 | PM Tom Newlon/planner Michael Van Schaik |  |  | FALSE
P19015021 |  | s2098.6 | At Butler 69kV station, install three (3) 69 kV breakers and two (2) Cap Banks to accommodate the line loops. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 | 2026-04-24 |  | EP |  | 25 |  | 5.5 |  | 5.5 | 2019-12-05 | PM Tom Newlon/planner Michael Van Schaik |  |  | FALSE
P19015006 |  | s2098.11 | Remove Metcalf tap from the Butler-North Hicksville 69kV line and reconnect the through path. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 | 2026-04-24 |  | UC |  | 50 |  | 1 |  | 1 | 2019-12-05 | Tom Newlon/ Michael Van Schaik |  |  | FALSE
P19198004 |  | s2098.12 | Remote end relay upgrades at North Hicksville 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-31 | 2028-07-18 |  | EP |  | 15 |  | 1 |  | 1 | 2019-12-05 |  |  |  | FALSE
P19008001, P19008003, P19008005, P19008013 |  | s2145.1 | Rebuild the Amos – Hopkins 138 kV circuit from structure 124-8A to Hopkins station as single circuit (~19.6 miles), including structure work near Saint Albans Tap and Angel Branch Tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-16 |  |  | UC |  | 50 |  | 61.3 |  | 61.3 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19140004 |  | s2146.1 | Rebuild the ~3 miles of overhead between Delaware and Bethel 34.5 kV stations. ~2.5 miles will be rebuilt as overhead and ~.5 miles will be rebuilt as underground. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-02 | 2026-07-13 |  | UC |  | 35 |  | 16.8 |  | 16.8 | 2019-11-22 |  |  |  | FALSE
P19140001 |  | s2146.2 | Rebuild the ~1 mile of underground between Kenmore and Bethel 34.5 kV stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-02 | 2025-10-06 |  | UC |  | 75 |  | 12.8 |  | 12.8 | 2019-11-22 |  |  |  | FALSE
P19024005 |  | s2147.3 | At Highland Terrace, install a three-way 1200 A, 69 kV switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-25 |  |  | UC |  | 35 |  | 0.7 |  | 0.7 | 2019-11-22 | David Sanchez |  |  | FALSE
P19082002 |  | s2149.1 | Ravin: Build a greenfield station at 69 kV 2000 A 40 kA in a 3-breaker ring configuration next to Jelloway (L.R. Co-op). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-06-13 | 2027-11-29 |  | EP |  | 25 |  | 8.6 |  | 8.6 | 2019-11-22 | Isaac Rhodes |  |  | FALSE
J19082007, K19082008 |  | s2149.2 | Jelloway Co-op – Ravin 69 kV: Build ~0.01 miles of greenfield 69 kV line to connect Ravin to Jelloway Co-op. Under emergency conditions Jelloway can be fed radially from North Liberty Switch. North Liberty Switch will be normally open towards Jelloway Co-op. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-05-01 |  |  | UC |  | 35 |  | 0.7 |  | 0.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19082019 |  | s2149.3 | Stillwell Switch: Install a greenfield 69 kV 1200 A 3-way POP switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-08-01 |  |  | EP |  | 25 |  | 0.8 |  | 0.8 | 2019-11-22 | Shaun Lopez |  |  | FALSE
J19082002 |  | s2149.4 | Stillwell Switch – Ravin 69 kV: Build ~11.4 miles of greenfield 69 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-05-01 |  |  | EP |  | 25 |  | 26.4 |  | 26.4 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19082022 |  | s2149.5 | Hanover Switch: Install a greenfield 69 kV 1200 A 3-way POP switch (near existing Loudonville). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-08-01 |  |  | EP |  | 25 |  | 0.8 |  | 0.8 | 2019-11-22 | Shaun Lopez |  |  | FALSE
J19082004 |  | s2149.6 | Hanover Switch – Ravin 69 kV: Build ~5.17 miles of greenfield 69 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-05-01 |  |  | EP |  | 25 |  | 12.9 |  | 12.9 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19082022 |  | s2149.7 | Loudonville (L.R. Co-op) Station – Hanover Switch: Reconnect the Loudonville (L.R. Co-op) Station to the new Hanover 69 kV Switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-05-01 |  |  | EP |  | 25 |  | 0.7 |  | 0.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193067 |  | s2149.8 | Fort Fizzle (Replaces Glenmont Junction Sw): Build a new greenfield 69 kV station in an in/out configuration with 1200 A switches to replace Glenmont Junction Switch. Remove existing Glenmont station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | EP |  | 25 |  | 1.1 |  | 1.1 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193029 |  | s2149.9 | Fort Fizzle – Stillwell 69 kV: Rebuild ~7.07 miles of the existing Glenmont Junction -Stillwell 34.5 kV line at 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | EP |  | 25 |  | 16.7 |  | 16.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193028 |  | s2149.10 | Fort Fizzle – Killbuck 69 kV: Rebuild ~5.51 miles of the existing Killbuck to Glenmont (Fort Fizzle) 34.5 kV line at 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | EP |  | 25 |  | 12.9 |  | 12.9 | 2019-11-22 | Isaac Rhodes |  |  | FALSE
P19193063 |  | s2149.11 | Black Diamond (Replaces South Millersburg): Build a greenfield station at 138 kV 3000 A 40 kA in 4-breaker ring configuration. Replace the 138/34.5 kV 25 MVA transformer with a 138/69 kV 90 MVA transformer. Remove the 34.5 kV circuit breaker “C” and install a new 69 kV 2000 A 40 kA circuit breaker towards Killbuck. Remove the 34.5 kV 3000 A kVAR Cap bank “AA”. The Buckhorn (H.WN. Co-op) 138 kV delivery point will now connect to Black Diamond station. Remove South Millersburg station and Buckhorn switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 10.2 |  | 10.2 | 2019-11-22 | Isaac Rhodes |  |  | FALSE
P19193027 |  | s2149.12 | Black Diamond – Killbuck 69 kV: Rebuild ~4.12 miles of the existing South Millersburg (Black Diamond) to Killbuck 69 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 6.4 |  | 6.4 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193061 |  | s2149.13 | Black Diamond 138 kV Line Extension: Build ~0.56 miles of greenfield 138 kV line (556 ACSR) to connect Black Diamond 138 kV to the existing West Millersburg 138 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 1.7 |  | 1.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193023 |  | s2149.14 | Ohio Central – West Millersburg 138 kV circuit: Remove ~.9 miles of the Ohio Central – West Millersburg 138 kV circuit and reroute into Black Diamond station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 0.7 |  | 0.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193050 |  | s2149.15 | Buckhorn (H.WN Co-op) – South Millersburg 138 kV line: Build a new 138 kV line (~.8 miles) to reconnect the existing Buckhorn (H.WN Coop) into Black Diamond 138 kV station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 2 |  | 2 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193033 |  | s2149.16 | Millersburg: Cut the Berlin – West Millersburg 69 kV line into Millersburg station with an in/out configuration with 1200 A line switches. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 2.8 |  | 2.8 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193068 |  | s2149.17 | Schlegel (Replaces Ripley Switch): Build a greenfield station at 69 kV 40 kA 2000 A in a 4-breaker ring configuration next to Ripley (H.WN. Co-op)’s station. Remove the existing Ripley and Paint Valley switches and reconnect the lines into the new Schlegel station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 9.5 |  | 9.5 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193021 |  | s2149.18 | Shreve – Schlegel 69 kV: Relocate the existing Shreve to Ripley 69 kV line to Schlegel station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 0.6 |  | 0.6 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193022 |  | s2149.19 | West Millersburg – Schlegel 69 kV: Relocate the existing West Millersburg to Paint Valley 69 kV line to Schlegel station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 0.6 |  | 0.6 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193069 |  | s2149.20 | West Nashville: Install a 69 kV 1200 A 3-way POP switch (near existing Drake Valley (H.WN. Co-op)). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 0.7 |  | 0.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193008 |  | s2149.21 | Millersburg – West Millersburg 34 kV: Retire ~1.24 miles of the existing Millersburg to West Millersburg 34 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | UC |  | 35 |  | 0.1 |  | 0.1 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19193007 |  | s2149.22 | Millersburg - South Millersburg 34 kV: Retire ~2.93 miles of the existing Millersburg to South Millersburg 34 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2028-10-19 |  | EP |  | 25 |  | 0.9 |  | 0.9 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194001 |  | s2149.23 | South Killbuck Switch: Replace 2-way POP with a 3-way 69 kV 1200 A POP switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2029-04-27 |  | EP |  | 25 |  | 0.6 |  | 0.6 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194027 |  | s2149.24 | South Killbuck – Killbuck H.WN. Co-op 69 kV: Rebuild ~0.05 miles of the South Killbuck to Killbuck Holmes Wayne Co-op 34 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2029-04-27 |  | EP |  | 25 |  | 0.7 |  | 0.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194003 |  | s2149.25 | Metham Switch: Replace 2-way POP with a 3-way 69 kV 1200 A POP switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2029-04-27 |  | EP |  | 25 |  | 0.6 |  | 0.6 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194040 |  | s2149.26 | Metham – Jefferson (F.P. Co-op) 69 kV: Rebuild ~0.38 miles of the Metham to Jefferson (F.P. Co-op) 34.5 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 | 2029-04-27 |  | EP |  | 25 |  | 1.2 |  | 1.2 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194036 |  | s2149.27 | Simmons Run – Killbuck 69kV: Rebuild ~10.4 miles of the South Coshocton to Killbuck34.5 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2029-05-17 |  | EP |  | 25 |  | 31.1 |  | 31.1 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194062 |  | s2149.28 | Simmons Run (Replaces Warsaw Switch): Build a greenfield station at 69 kV 2000 A 40 kA in 3-breaker ring configuration. Remove existing Warsaw switching. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2029-04-06 |  | EP |  | 25 |  | 8.7 |  | 8.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194039 |  | s2149.29 | South Warsaw – Tunnel Hill (F.P. Co-op) 69 kV: Rebuild ~3.73 miles of the existing South Warsaw to Tunnel Hill (F.P. Co-op) 34.5 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-01-15 | 2029-03-22 |  | EP |  | 25 |  | 9.3 |  | 9.3 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194005 |  | s2149.30 | Moscow Switch: Replace 2-way POP with a 3-way 69 kV 1200 A POP switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2029-02-23 |  | EP |  | 25 |  | 0.6 |  | 0.6 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194023 |  | s2149.31 | Moscow – Jackson (F.P Co-op) 69 kV: Rebuild ~1.24 miles of the existing Moscow to Jackson (F.P. Co-op) 34.5 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2029-02-23 |  | EP |  | 25 |  | 3.5 |  | 3.5 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194020 |  | s2149.32 | South Coshocton - Simmons Run 69 kV: Rebuild ~14.4 miles of the existing South Coshocton to Killbuck 34 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2029-02-23 |  | EP |  | 25 |  | 31.7 |  | 31.7 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19194012 |  | s2149.33 | South Coshocton: Build a 138 kV 3000 A 40 kA 5-breaker ring bus and install a 138/69 kV 130 MVA transformer. Install 3 new 69 kV 1200A 40 kA circuit breakers on the line towards Simmons Run, towards Coshocton, and on the low side of the transformer. Retire and remove the 138/69 kV 75 MVA transformer #2, as well as the 69/34.5 kV 35 MVA transformer #3. Leave the 138/34.5 kV 30 MVA transformer #1 to serve San Cast customer. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 | 2027-01-20 |  | EP |  | 25 |  | 10.9 |  | 10.9 | 2019-11-22 | Shaun Lopez |  |  | FALSE
P19052027 |  | s2153.1 | Rebuild the ~9.5 miles of the Kingsland – Bluffton – Adams circuit as 6-wired 138 kV design structures. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2031-12-01 |  | UC | EP | 35 | 25 | 28.5 |  | 28.5 | 2019-12-18 | Robert Renner |  |  | FALSE
P19052025 |  | s2153.2 | Build ~4.5 mile greenfield from Uniondale station to Ossian station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2029-11-05 |  | EP |  | 10 |  | 8 |  | 8 | 2019-12-18 | Robert Renner |  |  | FALSE
P19052002 |  | s2153.3 | Rebuild the Bluffton – Hillcrest 69 kV line as the ~26 mile Bluffton to Pleasant circuit as 6-wired 138 kV design structures. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2031-03-28 |  | EP |  | 10 |  | 67.1 |  | 67.1 | 2019-12-18 | Tom Newlon |  |  | FALSE
P19052001 |  | s2153.4 | Build the ~3.3 mile Pleasant to Kinnerk circuit as 6-wired 138 kV design structures. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2028-07-26 |  | EP |  | 10 |  | 9.6 |  | 9.6 | 2019-12-18 | Robert Renner |  |  | FALSE
P19052011 |  | s2153.5 | Install one 138 kV rated POP switch to feed Kinnerk’s load. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2029-08-17 |  | EP |  | 10 |  | 0.4 |  | 0.4 | 2019-12-18 | Robert Renner |  |  | FALSE
P19052010 |  | s2153.6 | Replace 2 69 kV CB’s toward Bluffton and Pleasant at Kingsland. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2029-11-15 |  | EP |  | 10 |  | 1.6 |  | 1.6 | 2019-12-18 | Robert Renner |  |  | FALSE
P19052011 |  | s2153.7 | Install the new 69 kV switch called Skips Place to feed the Uniondale load. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2029-08-17 |  | EP |  | 10 |  | 0.3 |  | 0.3 | 2019-12-18 | Robert Renner |  |  | FALSE
P19052008 |  | s2153.8 | Install 69 kV switch called Thiele to feed Kinnerk load. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2028-03-23 |  | EP |  | 10 |  | 0.6 |  | 0.6 | 2019-12-18 | Robert Renner |  |  | FALSE
P19052007 |  | s2153.9 | Remove CB “F” at Hillcrest station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 | 2028-08-18 |  | EP |  | 10 |  | 0.1 |  | 0.1 | 2019-12-18 | Robert Renner |  |  | FALSE
P19248004 |  | s2154.3 | Relocate the Firebrick – Lick 69 kV circuit associated with station work at Lick. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-03-05 | 2026-07-06 |  | UC |  | 35 | 50 | 0.8 |  | 0.8 | 2019-12-18 | Michael Trauntvein |  |  | FALSE
A15043156 |  | s2159 | South Point Sporn | Operational Flexibility and Efficiency |  |  |  | 2024-11-21 | 2026-05-29 |  | EP |  | 0 | 50 | 0 |  | 0 | 2019-12-18 |  |  |  | FALSE
A15043156 |  | s2159.1 | Install 3-way 138 kV (2000 A) MOAB’s at Mercerville hard tap, including dead end structures to connect to new switch pole location. | Operational Flexibility and Efficiency |  |  |  | 2024-11-21 | 2026-05-29 |  | EP |  | 0 | 50 | 2.2 |  | 2.2 | 2019-12-18 | Elmann Cabotage |  |  | FALSE
A15043157 |  | s2159.2 | Install 3-way 138 kV (2000 A) MOAB’s at Windsor hard tap. | Operational Flexibility and Efficiency |  |  |  | 2025-05-12 | 2026-02-24 |  | UC | EP | 50 |  | 1.3 |  | 1.3 | 2019-12-18 | Elmann Cabotage |  |  | FALSE
P19310001 |  | s2159.3 | Install 3-way 138 kV (2000 A) MOAB’s at Fayette hard tap. Extend the existing line 0.25 miles to the new switch location. | Operational Flexibility and Efficiency |  |  |  | 2024-11-18 | 2025-11-21 |  | UC |  | 50 | 75 | 3.5 |  | 3.5 | 2019-12-18 | Justin Robb |  |  | FALSE
P19150009 |  | s2160 | Rebuild the existing 31.6-mile Crooksville - North Newark 138 kV line using 795 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-16 | 2026-03-31 |  | UC |  | 35 | 75 | 55.6 |  | 55.6 | 2019-12-18 | Michael Deskin |  |  | FALSE
P18255001 |  | s2165.1 | Rebuild the existing Bancroft – Nitro 69kV line (~8.1 miles) to 69 kV standards. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-14 | 2027-12-16 |  | UC |  | 35 | 75 | 27.3 |  | 27.3 | 2019-12-18 | Shaun Lopez |  |  | FALSE
P17078055 |  | s2167 | Niles Area Improvements | Equipment Material Condition, Performance and Risk |  |  |  | 2028-08-09 | 2025-12-05 |  | EP | UC | 0 | 75 | 0 |  | 0 | 2019-12-18 |  |  |  | FALSE
P17078003 |  | s2167.1 | At Kenzie Creek station, install a 138/69 kV XFR, 3 138 kV breakers, 5 69 kV breakers and a 14.4 Mvar cap bank to allow for the retirement of Pokagon’s 69 kV transmission yard. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-02 | 2025-09-01 |  | EP | UC | 0 | 75 | 12 |  | 12 | 2019-12-18 | Scott Joseph |  |  | FALSE
P17078060 |  | s2167.2 | At Pokagon station, retire the 69 kV voltage class and re-organize this station as a 138/12 kV station only. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-05 |  |  | UC |  | 35 |  | 2 |  | 2 | 2019-12-18 | Scott Joseph |  |  | FALSE
P17078006 |  | s2167.3 | At Lake Street station, install a new 69/12 kV load delivery point, replace XFR 1 with a 50 MVA bank, and replace 34.5 kV CB “H” and 69kV Breaker “A” | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-29 | 2027-01-18 |  | UC | EP | 35 |  | 7.8 |  | 7.8 | 2019-12-18 | Scott Joseph |  |  | FALSE
P19159008 |  | s2167.4 | At Niles station, replace 69 kV breakers “B” and “A”. Replace XFR 2 and the breaker toward the City of Niles | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-15 |  |  | EP |  | 0 |  | 6.2 |  | 6.2 | 2019-12-18 | Michael Fisher |  |  | FALSE
P19142001 |  | s2167.5 | Route the Dailey, Barret and Lake St 69 kV lines into Kenzie Creek station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-03 | 2028-06-05 |  | EP |  | 0 |  | 2.8 |  | 2.8 | 2019-12-18 | Scott Joseph/Joshua Smith |  |  | FALSE
P17078005 |  | s2167.6 | Build the new 138/69/34 kV Boundary station to serve the new 34.5 kV distribution load and to separate the Swanson and University Park load form the network. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-05 |  |  | EP |  | 0 |  | 13.6 |  | 13.6 | 2019-12-18 | Scott Joseph |  |  | FALSE
P17078034 |  | s2167.7 | Build the ~2 mile 138 kV double ckt Boundary Extension | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-30 |  |  | EP |  | 0 |  | 4.4 |  | 4.4 | 2019-12-18 | Scott Joseph |  |  | FALSE
P19142002 |  | s2167.8 | Rebuild the Pokagon – Niles 69 kV line as the ~9.3 mile Kenzie – Niles 69 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-03 | 2028-06-05 |  | EP |  | 0 |  | 22.8 |  | 22.8 | 2019-12-18 | Scott Joseph/Joshua Smith |  |  | FALSE
P19159010 |  | s2167.9 | Rebuild the ~11.8 mile South Bend – Niles 69 kV line as the South Bend – Boundary – Niles 69 kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-15 | 2029-10-16 |  | EP |  | 0 |  | 26.6 |  | 26.6 | 2019-12-18 | Michael Fisher |  |  | FALSE
P19159005 |  | s2167.10 | Install a 69 kV bus tie CB at Swanson station to separate the 4 Moabs in series. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-15 |  |  | EP |  | 0 |  | 2.1 |  | 2.1 | 2019-12-18 | Michael Fisher |  |  | FALSE
P19159006 |  | s2167.11 | Replace the switch pole for University Park 69 kV. The new PoP Switch pole will be called “Peppermint Switch”. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-22 | 2029-10-16 |  | EP |  | 0 |  | 1 |  | 1 | 2019-12-18 | Michael Fisher |  |  | FALSE
P19073001 |  | s2177.1 | Rebuild the Carbondale – Kincaid 46 kV lines as a single circuit 46 kV line (~16.3 miles). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-03 |  |  | UC |  | 50 |  | 50.7 |  | 50.7 | 2020-01-17 | Scott Joseph/Joshua Smith |  |  | FALSE
P19073006 |  | s2177.2 | Retire the Carbondale – Kincaid #1/#2 double circuit 46 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-19 | 2026-05-04 |  | UC |  | 35 |  | 9.1 |  | 9.1 | 2020-01-17 | Roger Whitt/Michael Hassay |  |  | FALSE
P19073002 |  | s2177.3 | Alloy Station: Install a 2-way switch to address hard tap. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-09-09 |  |  | UC |  | 50 |  | 0.9 |  | 0.9 | 2020-01-17 | Roger Whitt/Michael Hassay |  |  | FALSE
P19073012 |  | s2177.5 | Raynes Meter Station: Remove/retire station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-16 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2020-01-17 | Roger Whitt/Michael Hassay |  |  | FALSE
P19073009 |  | s2177.6 | Boomer Station: Remove/retire station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-19 | 2026-02-10 |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-01-17 | Roger Whitt/Michael Hassay |  |  | FALSE
DP19H05W0 |  | s2178.2 | Construct a new 138 kV line (~10 mi.) from Kenna to the existing Sisson 138 kV station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-11-05 |  |  | UC |  | 75 |  | 25.5 |  | 25.5 | 2020-01-17 | Frank Jenkins |  |  | FALSE
P18100051 |  | s2179.1 | Construct ~12.5 miles 138 kV line from Alum Ridge - Claytor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-11-01 | 2032-12-14 |  | UC | EP | 35 | 25 | 40.78 |  | 40.78 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100040 |  | s2179.2 | Construct ~6.5 miles 138 kV line from Alum Ridge - Floyd. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-02 | 2031-06-27 |  | UC |  | 35 |  | 23.85 |  | 23.85 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100048 |  | s2179.4 | Construct ~1.25 miles of double circuit 138 kV line to connect Stanleytown. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-16 | 2029-11-15 |  | UC |  | 35 |  | 2.35 |  | 2.35 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100038 |  | s2179.6 | Construct ~1.2 miles of 138 kV line from Philpott Dam - Fairystone. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 | 2030-06-20 |  | UC |  | 35 |  | 6.86 |  | 6.86 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100008 |  | s2179.7 | Construct ~22 miles of 138 kV line from Salem Highway - Willis Gap. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-01 | 2027-12-09 |  | UC |  | 35 |  | 42.39 |  | 42.39 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100031 |  | s2179.9 | Construct ~11 miles of 138 kV line from Floyd - Woolwine. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 | 2029-12-21 |  | UC |  | 35 |  | 33.44 |  | 33.44 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100013 |  | s2179.10 | Construct ~10 miles of 138 kV line from Salem Highway - Woolwine. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 | 2026-12-18 |  | UC |  | 35 |  | 34.75 |  | 34.75 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100031 |  | s2179.11 | Remove ~11 miles of 69 kV line from Floyd - Woolwine. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-02 | 2029-12-21 |  | UC |  | 35 |  | 1.55 |  | 1.55 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100020 |  | s2179.12 | Remove ~10 miles of 69 kV line from Stuart - Woolwine. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 | 2028-03-10 |  | UC |  | 35 |  | 5.02 |  | 5.02 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100041 |  | s2179.13 | Remove ~12.2 miles of 138 kV line from Alum Ridge - Claytor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-11-01 | 2032-12-17 |  | UC |  | 35 |  | 1.49 |  | 1.49 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100040 |  | s2179.14 | Remove ~6.25 miles of 138 kV line from Alum Ridge - Floyd. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-02 | 2031-06-27 |  | UC |  | 35 |  | 0.94 |  | 0.94 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100022 |  | s2179.15 | Remove ~19 miles of 138 kV line from Floyd - West Bassett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-08-14 | 2029-12-27 |  | UC |  | 35 |  | 16.61 |  | 16.61 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100022 |  | s2179.16 | Remove ~6.4 miles of 138 kV line from Fieldale - West Bassett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-15 | 2029-12-27 |  | UC |  | 35 |  | 3.77 |  | 3.77 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100043 |  | s2179.17 | Remove ~0.34 miles of 138 kV line from Philpott SS - Philpott. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-16 |  |  | UC |  | 35 |  | 0.13 |  | 0.13 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100021 |  | s2179.18 | Remove ~19 miles of 69 kV line from Fieldale - Stuart. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-08-14 | 2028-12-15 |  | UC |  | 35 |  | 8.26 |  | 8.26 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100023 |  | s2179.19 | Remove ~7.1 miles of 69 kV line from Fieldale - West Bassett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-15 | 2030-02-15 |  | UC |  | 35 |  | 11.56 |  | 11.56 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100042 |  | s2179.20 | Remove ~6.8 miles of 69 kV line from Fieldale - West Bassett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-15 | 2029-12-19 |  | UC |  | 35 |  | 10.77 |  | 10.77 | 2023-02-17 | Scott Markwell |  |  | FALSE
P18100054 |  | s2179.21 | At Floyd station, install 2-138 kV circuit breakers (3000 A, 40 kA). Install high-side circuit switcher on T2 (3000A, 40 kA). Station expansion to accommodate new equipment and DICM. Install 138 kV line relaying, CCVT’s, breaker controls, bus differential protection, transformer #2 protection. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-09-01 | 2030-06-12 |  | UC |  | 35 |  | 10.75 |  | 10.75 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100006 |  | s2179.22 | At Fieldale station, retire 69 kV CB G, D and C. Install CCVTs and arresters on 138 kV West Bassett Line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-13 | 2029-12-19 |  | UC |  | 35 |  | 0.7 |  | 0.7 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100004 |  | s2179.24 | At Bassett station, convert station from 69 kV to 138 kV. Install 138/12 kV transformer with high-side circuit switcher, transclosure and associated distribution feeders. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 | 2029-11-15 |  | UC |  | 35 |  | 0 |  | 0 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100055 |  | s2179.25 | At Claytor 138 kV station, install line relaying. Remove wavetrap, replace 1590 AAC risers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-11-01 | 2032-12-14 |  | UC |  | 35 |  | 0.55 |  | 0.55 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100043 |  | s2179.26 | Retire Philpott 138 kV switch structure. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-16 |  |  | UC |  | 35 |  | 0.4 |  | 0.4 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100002 |  | s2179.27 | At Willis Gap station, install 2-138 kV MOABs. Terminate new Salem Highway - Willis Gap 138 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-12-12 |  |  | UC |  | 35 |  | 0 |  | 0 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100003 |  | s2179.28 | At Woolwine station, convert station from 69 kV to 138 kV. Retire/remove 69 kV switch structure, 69 kV MOABs, 69/34.5 kV transformer. Install 138 kV 3-way switch structure with MOABs, 138/34.5 kV transformer with high-side circuit switcher. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 | 2029-12-18 |  | UC |  | 35 |  | 0 |  | 0 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100061 |  | s2179.29 | At Salem Highway station, establish new 138 kV station replacing Stuart Station. Install 138 kV 5-breaker ring bus, 138/34.5 kV & 138/12 kV transformers with high-side circuit switchers. Terminate Huffman, Floyd and Fairystone 138 kV circuits. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-09-02 | 2027-12-09 |  | UC |  | 35 |  | 0 |  | 0 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100001 |  | s2179.30 | At Stuart 69 kV station, retire and remove all existing equipment and control house. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-02 | 2028-12-13 |  | UC |  | 35 |  | 0 |  | 0 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100005 |  | s2179.31 | At Stanleytown station, convert station from 69 kV to 138 kV. Retire/remove 69 kV switch structure, 69 kV MOABs, 69/12 kV transformer. Install 138 kV 3-way switch structure with MOABs, 138/12 kV transformer with high-side circuit switcher. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-13 | 2029-11-29 |  | UC |  | 35 |  | 0 |  | 0 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100064 |  | s2179.32 | At Fairystone station, establish new 138 kV station replacing West Bassett. Install 138 kV 4-breaker ring bus, 138/34.5 kV transformer with high-side circuit switcher and associated distribution feeders. Terminate Salem Highway, Fieldale and Philpott Dam 138 kV circuits. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 |  |  | EP |  | 5 |  | 0 |  | 0 | 2020-01-17 | Scott Markwell |  |  | FALSE
DR19R07L0 |  | s2179.33 | At Claudville station, establish new 138/34.5 kV distribution station with 2-138 kV CBs, 138/34.5 kV transformer and 3-34.5 kV feeders. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 | 2029-03-01 |  | EP |  | 0 |  | 0 |  | 0 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100010 |  | s2179.34 | Provide transition, entry and termination for OPGW connectivity at Willis Gap, Claytor, Alum Ridge, Floyd, Woolwine, Stuart, Fairystone, Philpott Dam, Bassett, Stanleytown, Fieldale, and Salem Highway to support fiber relaying. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-01 | 2027-11-11 |  | UC |  | 35 |  | 0.83 |  | 0.83 | 2020-01-17 | Scott Markwell |  |  | FALSE
P18100046 |  | s2179.35 | Construct ~11.4 miles of 138 kV line from Claudville to Mayo River. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 | 2027-12-10 |  | EP |  | 0 |  | 38.87 |  | 38.87 | 2023-02-17 |  |  |  | FALSE
P18100044 |  | s2179.36 | Remove ~0.4 miles of 69 kV line from Woolwine “in and out” loop. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 | 2029-12-21 |  | EP |  | 0 |  | 0.09 |  | 0.09 | 2023-02-17 |  |  |  | FALSE
P18100025 |  | s2179.37 | Construct ~9.5 miles 138 kV from Stoneleigh Station Site to Proposed Patrick Henry Site . | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 | 2030-11-13 |  | EP |  | 0 |  | 28.87 |  | 28.87 | 2023-02-17 |  |  |  | FALSE
P18100027 |  | s2179.38 | Construct ~4.1 miles of double circuit 138 kV from Stoneleigh Station Site to Smith River . | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 | 2030-11-14 |  | EP |  | 0 |  | 11.89 |  | 11.89 | 2023-02-17 |  |  |  | FALSE
P18100029 |  | s2179.39 | Construct ~1.8 miles of 138 kV from Fieldale to Stoneleigh tap structure . | Equipment Material Condition, Performance and Risk |  |  |  | 2029-12-31 | 2030-06-20 |  | EP |  | 0 |  | 6.92 |  | 6.92 | 2023-02-17 |  |  |  | FALSE
P18100015 |  | s2179.40 | Construct ~11 miles 138 kV from Mayo River to Proposed Patrick Henry Site . | Equipment Material Condition, Performance and Risk |  |  |  | 2029-12-31 | 2028-12-13 |  | EP |  | 0 |  | 34.98 |  | 34.98 | 2023-02-17 |  |  |  | FALSE
P18100007 |  | s2179.41 | At Huffman station remove CB “C” bypass switch and Install CCVT with Wavetrap on Willis Gap line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 | 2031-01-13 |  | EP |  | 0 |  | 0 |  | 0 | 2023-02-17 |  |  |  | FALSE
P18100053 |  | s2179.42 | Retire West Bassett station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 | 2029-12-20 |  | EP |  | 0 |  | 0 |  | 0 | 2023-02-17 |  |  |  | FALSE
P18100068 |  | s2179.43 | At Stoneleigh station establish new 138 kV tap station, install 3-way MOAB switch, install 138/12 kV transformer and associated feeders . | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 | 2029-12-28 |  | EP |  | 0 |  | 0 |  | 0 | 2023-02-17 |  |  |  | FALSE
P19006001 |  | s2184.1 | Rebuild 22.0 miles of the existing 28.5 mile Stuart-Seaman 69kV circuit with 795 ACSR. Retire approximately 3 miles of the line between West Union and structure 86. 32 of the line’s 170 structure were replaced since 2012 and will not be replaced as part of the rebuild | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 48.5 |  | 48.5 | 2020-02-21 |  |  |  | FALSE
P19006001 |  | s2184.2 | Construct approximately 2.5 miles of new line from structure 86 on the Stuart – Seaman 69 kV line to Copeland station utilizing 795 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 5 |  | 5 | 2020-02-21 |  |  |  | FALSE
P19316010 |  | s2184.3 | Rebuild the 2.0 mile West Union – Copeland 69 kV line utilizing 795 ACSR. The line is part of the Stuart – Seaman 69 kV circuit and is currently radial fed from West Union switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 | 2025-07-30 |  | EP | UC | 0 | 75 | 4 |  | 4 | 2020-02-21 |  |  |  | FALSE
P19316003 |  | s2184.4 | Establish a four breaker 69 kV ring (3000A, 40kA) at the existing Copeland station to serve the Adams Co-op and AEP Ohio customers currently served from a hard tap at the end of the radial. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 | 2025-07-30 |  | UC |  | 50 | 75 | 5 |  | 5 | 2020-02-21 |  |  |  | FALSE
P19006007 |  | s2184.5 | Retire existing West Union Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-02-21 |  |  |  | FALSE
P19316005 |  | s2184.6 | Install new 2000A 3-way phase over phase switch at Panhandle. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 | 2025-12-11 |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2020-02-21 |  |  |  | FALSE
P19120006 |  | s2185 | Rebuild the 4-mile Sunnyside-Torrey 138kV circuit. Supplement the existing right-of-way as needed, to resolve encroachments and other constraints. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-09 | 2029-07-03 |  | EP |  | 0 |  | 12.7 |  | 12.7 | 2020-02-21 |  |  |  | FALSE
P17083002 |  | s2188.1 | Construct 10.3 miles of single circuit 138kV from Soft Shell to Garrett picking up Salt Lick Co-op via Snag Fork along the way. Complete associated remote end relaying. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-05-12 |  | EP |  | 0 |  | 35.3 |  | 35.3 | 2020-02-21 |  |  |  | FALSE
P17083007 |  | s2188.2 | Construct ~3 miles of single circuit 138kV from the Eastern station to Garrett station. A short extension will be required from the new station to the existing Hays Branch metering point. Construct short extension to existing Morgan Fork – Hays Branch 138 kV circuit from Eastern station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-05-12 |  | EP |  | 0 |  | 11.5 |  | 11.5 | 2020-02-21 |  |  |  | FALSE
P17083008 |  | s2188.3 | Double circuit cut into existing Hays Branch - Morgan Fork line to tie into new Eastern Station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-10-13 |  | EP |  | 0 |  | 1.3 |  | 1.3 | 2020-02-21 |  |  |  | FALSE
P17083032 |  | s2188.4 | Construct ~1.4 mi of double circuit 138kV line between Eastern and the tap point on the Morgan Fork-Hays Branch line. The proposed line will establish a direct feed to Hays Branch from Eastern and establishing a through path line between Eastern and Morgan Fork.. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-09-17 |  | EP |  | 0 |  | 1.6 |  | 1.6 | 2020-02-21 |  |  |  | FALSE
P17083005 |  | s2188.5 | New relaying at Hays Branch to accommodate new line from Eastern station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-10-13 |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2020-02-21 |  |  |  | FALSE
P17083033 |  | s2188.6 | Expand the Garrett station,Install a straight bus arrangement with two 138kV breakers and a circuit switcher on the high side of the transformer, 138/12kV 30MVA transformer | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-05-12 |  | EP |  | 0 |  | 0 |  | 5.8 | 2020-02-21 |  |  |  | FALSE
P17083041 |  | s2188.7 | Establish a new 138 kV substation Eastern south of the existing Hays Branch station. Install three 138kV breakers (3000A 40kA) at the new Eastern station in a ring bus arrangement. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-05-12 |  | EP |  | 0 |  | 6 |  | 6 | 2020-02-21 |  |  |  | FALSE
P17083038 |  | s2188.8 | Establish Snag Fork S.S. Install a 3 way phase over phase motorized (automated) switching structure near Saltlick to serve the EKPC co-op. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-06-24 |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2020-02-21 |  |  |  | FALSE
P17083016 |  | s2188.9 | Move the existing 69kV rated CB G to the Beaver Creek – McKinney #2 circuit exit at McKinney substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-11-12 |  | EP |  | 0 |  | 0 |  | 0 | 2020-02-21 |  |  |  | FALSE
P17083019 |  | s2188.11 | Retire the ~25 miles of the 46kV Beaver Creek – McKinney #1 46 KV circuit. Retire Spring Fork Tap. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 | 2027-09-23 |  | EP |  | 0 |  | 17.3 |  | 17.3 | 2020-02-21 |  |  |  | FALSE
P19058001 |  | s2189 | Rebuild ~27.8 miles of the existing Baileysville – Hales Branch 138kV circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-08-01 | 2028-06-16 |  | EP |  | 0 |  | 98.5 |  | 98.5 | 2020-02-21 |  |  |  | FALSE
P19014002 |  | s2190 | Rebuild approximately 15 miles of the AEP-owned portion of the 138 kV line between Fieldale and Dan River stations (AEP/Duke ownership changes at the VA/NC border). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-28 | 2026-12-10 |  | EP |  | 0 |  | 32.2 |  | 32.2 | 2020-02-21 |  |  |  | TRUE
P15082C01 |  | s2197 | At Dragoon Station, replace the 34.5KV breaker A. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-01-01 | 2025-12-19 |  | UC |  | 75 |  | 2 |  | 0.66 | 2020-02-21 |  |  |  | FALSE
P19253014 |  | s2199.1 | Rebuild approximately 3.0 miles of New Liberty – North Baltimore 34kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-03 | 2029-03-21 |  | EP |  | 0 |  | 9.3 |  | 9.3 | 2020-02-21 |  |  |  | FALSE
P19091011 |  | s2200.1 | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Install a 2MW BESS at Middle Creek substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-28 |  |  | On Hold |  | 0 |  | 9.7 |  | 9.7 | 2020-01-17 |  |  |  | FALSE
P19091003 |  | s2200.2 | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Rebuild ~8.5 miles of 46 kV line between Prestonsburg and Middle Creek station. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 |  |  | On Hold |  | 0 |  | 25.5 |  | 25.5 | 2020-01-17 |  |  |  | FALSE
A20705035 |  | s2200.3 | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Retire ~14.5 miles of 46 kV line between Falcon and Middle Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 |  |  | On Hold |  | 0 |  | 6.1 |  | 6.1 | 2020-01-17 |  |  |  | FALSE
P19105003 |  | s2201.1 | Rebuild 43.4 miles single circuit line between Hillsboro – South Lucasville with 1033 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-16 |  |  | UC |  | 75 |  | 92.5 |  | 92.5 | 2020-02-21 |  |  |  | FALSE
P19105003 |  | s2201.2 | Rebuild 8.5 miles double circuit between Millbrook Park – South Lucasville with 1033 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-16 |  |  | UC |  | 75 |  | 33.6 |  | 33.6 | 2020-02-21 |  |  |  | FALSE
P18147020 |  | s2213.4 | Construct two independent lines to serve the X-555 substation (DP #1). The lines will be ~0.4 miles long each. | Customer Service |  |  |  | 2025-10-06 | 2028-01-04 |  | EP |  | 0 |  | 1.7 |  | 1.7 | 2020-03-10 | Oliver Duncan/? |  |  | TRUE
P18147022 |  | s2213.5 | Construct two independent lines to serve the X-5001 substation (DP #2). The lines will be ~0.8 miles long each. | Customer Service |  |  |  | 2025-10-06 | 2028-01-04 |  | EP |  | 0 |  | 3.5 |  | 3.5 | 2020-03-10 | Oliver Duncan/? |  |  | TRUE
P18147006 |  | s2213.6 | At Don Marquis 345 kV, install 3-345kV 4000A 63kA circuit breakers to terminate the OVEC lines from Pierce and Kyger Creek. Install intertie metering. (AEP work) | Customer Service |  |  |  | 2026-08-20 | 2028-05-05 |  | EP |  | 0 |  | 8.8 |  | 8.8 | 2020-03-10 | Oliver Duncan/Patrick Hodgson |  |  | TRUE
J19220002 |  | s2215.1 | Rebuild 16 miles of 69 kV single circuit line from North Continental Switch (existing switch to be retired) to Roselms Switch (located next to the existing Roselms- PP Co-op Station). | Equipment Material Condition, Performance and Risk |  |  |  | 2026-05-01 | 2027-06-07 |  | EP |  | 0 |  | 38.4 |  | 38.4 | 2020-03-19 |  |  |  | FALSE
J19220001 |  | s2215.2 | Build 9.4 miles of single circuit 69 kV line from Roselms to near East Ottoville 69 kV Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-06-07 |  | EP |  | 0 |  | 13.7 |  | 13.7 | 2020-03-19 |  |  |  | FALSE
P19220012 |  | s2215.3 | Rebuild 7.5 miles of double circuit 69kV line between East Ottoville Switch and Kalida Station (combining with the new Roselms to Kalida 69 kV circuit). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-02-19 |  | EP |  | 0 |  | 23.6 |  | 23.6 | 2020-03-19 |  |  |  | FALSE
P19220021 |  | s2215.4 | Rebuild 5.1 miles of single circuit 69 kV line from East Ottoville to North Delphos. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-06-18 |  | EP |  | 0 |  | 9.4 |  | 9.4 | 2020-03-19 |  |  |  | FALSE
P19220024 |  | s2215.5 | At North Continental, remove normally open bypass switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2028-07-31 |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-03-19 |  |  |  | FALSE
P19220014 |  | s2215.6 | At Fort Brown Switch, install a three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2028-03-10 |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2020-03-19 |  |  |  | FALSE
P19220016 |  | s2215.7 | At West Oakwood Switch, install a three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-08-05 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-03-19 |  |  |  | FALSE
P19220017 |  | s2215.8 | At Roselms Switch, install a new three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-06-07 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-03-19 |  |  |  | FALSE
P19220018 |  | s2215.9 | At Kalida station, move CB J from low side of Transformer 2 to terminate the new line from Roselms Switch. Move the CS XT2 from high side of T2 to the high side of T1. Remove existing T2 transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-02-19 |  | EP |  | 0 |  | 1 |  | 1 | 2020-03-19 |  |  |  | FALSE
P19220040 |  | s2215.10 | Remote end work at North Delphos station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-06-18 |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2020-03-19 |  |  |  | FALSE
P19220026 |  | s2215.11 | At East Ottoville, install a three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2026-07-27 |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2020-03-19 |  |  |  | FALSE
P19220028 |  | s2215.12 | At Ottoville station, install 2- three way 69 kV, 1200 A, phase over phase Switches, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-01-07 |  | EP |  | 0 |  | 1.9 |  | 1.9 | 2020-03-19 |  |  |  | FALSE
P19220029 |  | s2215.13 | At Fort Jennings, replace hard tap with a three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 | 2027-07-16 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-03-19 |  |  |  | FALSE
P19216001 |  | s2216.1 | At Lamping station, install a 138kV breaker string with 2 breakers, a 90 MVA 138-69kV transformer, and 1- 69kV breaker. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 | 2028-09-22 |  | EP |  | 0 |  | 4.8 |  | 4.8 | 2020-03-19 |  |  |  | FALSE
J19216001 |  | s2216.2 | Construct a 10-mile 69kV transmission line between Lamping and the Woodsfield area. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 | 2029-08-15 |  | EP |  | 0 |  | 19.9 |  | 19.9 | 2020-03-19 |  |  |  | FALSE
P19216005 |  | s2216.3 | At the existing Woodsfield Co-op station, install a 3-way 69kV switch with SCADA functionality (Cranes Nest Switch). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 | 2028-09-29 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-03-19 |  |  |  | FALSE
P19216005 |  | s2216.4 | At the existing hard tap to Woodsfield Municipal, install a 3-way 69kV switch with SCADA functionality (Standingstone Switch). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 | 2028-09-29 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-03-19 |  |  |  | FALSE
P19216006 |  | s2216.5 | Remove the existing Cameron 2-way switch and install a new 3-way 69kV switch with SCADA functionality. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 | 2028-09-29 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-03-19 |  |  |  | FALSE
P19216002 |  | s2216.6 | At Switzer station, install 2- 138kV line breakers (toward Herlan & Natrium). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 | 2028-09-29 |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2020-03-19 |  |  |  | FALSE
P19216010 |  | s2216.7 | At the 138kV remote-end of Natrium, replace the line protection relays to coordinate with the upgrade at Switzer. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 | 2028-09-29 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-03-19 |  |  |  | FALSE
P19216007 |  | s2216.8 | Modify the existing Switzer-Woodsfield 69kV transmission line on each side of the switches due to the switch installation. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 | 2028-09-29 |  | EP |  | 0 |  | 1.9 |  | 1.9 | 2020-03-19 |  |  |  | FALSE
P18221001 |  | s2219 | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12kV 30 MVA transformer, Replace 12 kV CB A and D. Retire existing Fleming substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-29 | 2025-11-21 |  | EP | UC | 25 | 75 | 21.1 |  | 21.1 | 2020-03-19 | Wayne Cooper/Chintan Raval |  |  | FALSE
P19209001 |  | s2221.1 | Remove ~3.3 miles of the Derwent – Summerfield 69 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-03 | 2028-04-14 |  | EP |  | 10 |  | 2 |  | 2 | 2020-03-19 | Shawn ynch/Jerod Marker |  |  | FALSE
J19209001 |  | s2221.2 | Build a new 69 kV line (~2.42 miles) from Lashley to the existing Summerfield line to loop the customers served from the existing radial. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-03 | 2028-04-14 |  | EP |  | 10 |  | 6.1 |  | 6.1 | 2020-03-19 | Shawn ynch/Jerod Marker |  |  | FALSE
P19209004 |  | s2221.3 | Install a new 69kV 1200A 3-way POP switch (Lashley) with auto-sectionalizing MOABs to serve the Senecaville GM co-op. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-03 | 2028-04-14 |  | EP |  | 10 |  | 1.1 |  | 1.1 | 2020-03-19 | Shawn ynch/Jerod Marker |  |  | FALSE
P19209005 |  | s2221.6 | At Derwent station, remove the Summerfield line exit and associated equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 | 2028-04-14 |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2020-03-19 |  |  |  | FALSE
P19225029 |  | s2222.1 | Build a new single circuit 138 kV line (~1.5 mi) to connect the new IIesboro delivery point to the Lemaster - Ross 138kV circuit using 336.4 ACSR. | Customer Service |  |  |  | 2025-01-06 | 2029-08-28 |  | EP |  | 0 |  | 4.3 |  | 4.3 | 2020-03-19 |  |  |  | FALSE
P19260004 |  | s2222.2 | Install a new 3-way phase over phase 138 kV 2000 A switch (Fiddlestix) with MOABs on the Lemaster – Ross 138kV circuit. Update remote end work at Lemaster. | Customer Service |  |  |  | 2025-07-18 | 2025-09-30 |  | UC |  | 75 |  | 0.9 |  | 0.9 | 2020-03-19 |  |  |  | FALSE
P19225013, P19225004 |  | s2224.1 | Rebuild the existing ~8 mile Elliott – Lee 69kV line to 138 kV and retire the existing 69 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 | 2029-09-18 |  | EP |  | 0 |  | 20.7 |  | 20.7 | 2020-03-19 |  |  |  | FALSE
P19225009 |  | s2224.2 | Retire approximately 11.5 miles of the Philo – Rutland 138kV line asset from Lee station north, including the de-energized portion of the line that runs through the Plains community. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 | 2030-10-31 |  | EP |  | 0 |  | 3.5 |  | 3.5 | 2020-03-19 |  |  |  | FALSE
P19225020 |  | s2224.6 | Rebuild ~3.68 miles of single circuit line from the Poston - Strouds Run line as double circuit 138kV transmission line to eliminate the hard tap on the line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 | 2029-12-20 |  | EP |  | 0 |  | 16 |  | 16 | 2020-03-19 |  |  |  | FALSE
P19225017 |  | s2224.8 | At Lemaster station, install a 138kV breaker (3000A 40kA) to accommodate the new circuit. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 | 2029-08-28 |  | EP |  | 0 |  | 1 |  | 1 | 2020-03-19 |  |  |  | FALSE
P19225008 |  | s2224.9 | Remove Rosewood switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 | 2029-06-20 |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-03-19 |  |  |  | FALSE
P18039002 |  | s2225.1 | Retire the existing 7.5-mile long Belle-Cabin Creek #1 and #2 circuits from Belle to Cabin Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-02 | 2025-11-20 |  | UC |  | 75 |  | 10 |  | 10 | 2020-03-19 | Wayne Cooper/Michael Hassay |  |  | FALSE
P18039107 |  | s2225.2 | Construct new double circuit 46kV line (designed to 138 kV) from Belle to Hernshaw (~4 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-01 | 2025-11-20 |  | UC |  | 75 |  | 13.5 |  | 13.5 | 2020-03-19 | Wayne Cooper/Michael Hassay |  |  | FALSE
P18039001 |  | s2225.4 | Remote end work and retire circuit breakers AA and AB at Cabin Creek station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-02 | 2025-11-20 |  | UC |  | 75 |  | 0.8 |  | 0.8 | 2020-03-19 | Wayne Cooper/Michael Hassay |  |  | FALSE
P22081002 |  | s2225.7 | Marmet Hydro Hard Tap will be relocated to be positioned between 46 kV circuit breaker G at Belle and the new switches at Marmet Station. Remote end work required at Marmet Hydro Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-01 | 2030-10-01 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-03-19 | Wayne Cooper/Michael Hassay |  |  | FALSE
P18250001, P18250002, P18250003, P18250004, P18250007, P18250009 |  | s2226.1 | Construct approximately 10 miles of new 138kV line between Glen Lyn and Speedway. New ROW will be required for the new Glen Lyn – Speedway 138kV line. Retire the existing section of line from Glen Lyn to Hatcher Switch (~ 8 miles), including Hatcher Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-06-21 | 2031-02-13 |  | EP |  | 0 |  | 32 |  | 32 | 2020-03-19 | Charles Linkous/Robert Valerio |  |  | FALSE
P18250005, P18250014 |  | s2226.2 | Retire Hatcher Switch. Install MOABs at Speedway on new line to Glen Lyn and existing line towards South Princeton. Install a circuit switcher on the Speedway transformer. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-06-21 | 2031-02-13 |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2020-03-19 | Charles Linkous/Robert Valerio |  |  | FALSE
P18250001 |  | s2226.3 | Rebuild ~7.3 miles of the Glen Lyn – South Princeton 138 KV circuit between Speedway station and the previous Hatcher Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 21.9 |  | 21.9 | 2020-03-19 |  |  |  | FALSE
P19304011 |  | s2250 | Rebuild the existing Broadford - Wolf Hills/Clinch River - Saltville #2 138kV double circuit line (~26 miles) section between Saltville and Wolf Hills stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2035-06-25 | 2036-09-02 |  | EP |  | 0 |  | 107.1 |  | 107.1 | 2020-04-20 |  |  |  | FALSE
DP16K03B1 |  | s2251.2 | Retire Siloam Station. | Customer Service |  |  |  | 2025-06-05 |  | 2025-07-03 | UC | IS | 75 | 100 | 0 |  | 0 | 2020-04-20 | Wayne Cooper/Shaheed Khan |  |  | FALSE
P15095040 |  | s2251.3 | Remote end relaying at Millbrook Park to coordinate with new breakers. | Customer Service |  |  |  | 2028-04-03 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2020-04-20 |  |  |  | FALSE
P15095024 |  | s2251.4 | Tap the 69kV Central Portsmouth – Millbrook Park line and install 3 custom T-line structures due to proximity to the Railroad. | Customer Service |  |  |  | 2027-08-11 | 2027-10-07 |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2020-04-20 |  |  |  | FALSE
P21082004 |  | s2270.8 | Cut into the George Washington-Natrium 138kV circuit and extend an 8.6- mile double-circuit 138kV loop east to Nauvoo Ridge. | Customer Service |  |  |  | 2026-08-20 | 2026-05-12 |  | EP | UC | 0 | 75 | 23.13 |  | 23.13 | 2022-03-08 |  |  |  | FALSE
P21082004 |  | s2270.9 | Modify the George Washington-Natrium 138kV line, which is part of a double-circuit lattice tower line. | Customer Service |  |  |  | 2027-04-28 | 2026-05-12 |  | EP | UC | 0 | 75 | 0.65 |  | 0.65 | 2022-03-08 |  |  |  | FALSE
P22964008 |  | s2270.10 | Rebuild the Kammer-Natrium 138kV double-circuit line (9.3 miles). The circuit’s limiting ratings are currently set by the T-Line conductor (556 ACSR). The rebuilt circuit will utilize 795 ACSS high-temperature conductor, to optimize the new structure sizing and cost | Customer Service |  |  |  | 2025-12-01 | 2028-12-20 |  | EP |  | 0 |  | 22.86 |  | 22.86 | 2022-09-16 |  |  |  | FALSE
P19104001 |  | s2272.1 | Rebuild the 35-miles of the South Point- Portsmouth double circuit 138 kV line between Millbrook Park – South Point; with 795 ACSR (257MVA) or equivalent conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-15 | 2028-05-17 |  | EP |  | 0 |  | 128 |  | 128 | 2020-05-22 |  |  |  | FALSE
P19104013 |  | s2272.3 | Remote end work at South Point 138 kV station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-15 | 2030-10-24 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-05-22 |  |  |  | FALSE
P19290021, P19290022, P19290003, P19290026 |  | s2273.1 | Rebuild the 1.25 mile long Anchor Hocking-Winchester 69 kV circuit. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-08-16 |  |  | EP |  | 0 |  | 5.9 |  | 5.9 | 2020-05-22 |  |  |  | FALSE
P19290023, P19290024 |  | s2273.2 | Expand and upgrade Anchor Hocking 69 kV station to a 5 breaker ring bus to accommodate 5 elements (2 transmission lines and 3 distribution transformers). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-02-23 |  |  | EP |  | 0 |  | 6.7 |  | 6.7 | 2020-05-22 |  |  |  | FALSE
P19290009, P19290010 |  | s2273.3 | Replace circuit breakers A & B at Winchester 69 kV station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-09-07 |  |  | EP |  | 0 |  | 3 |  | 3 | 2020-05-22 |  |  |  | FALSE
P19290004, P19290005, P19290006, P19290007 |  | s2273.5 | At Randolph station, replace 138/69/12 kV Transformer #1 with a 138/69kV 90MVA unit, move the distribution load to a new 138/12kV transformer, and install a 138kV bus tie circuit breaker. Replace cap switcher AA. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-07-03 |  |  | EP |  | 0 |  | 6.8 |  | 6.8 | 2020-05-22 |  |  |  | FALSE
|  | s2273.10 | Retire Lobdell station. Moved the load from 69kV to 12kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2020-05-22 |  |  |  | FALSE
P19311007 |  | s2274.1 | Rebuild a 4.17 mile portion of the Madison – Pendleton 138kV single circuit line with DRAKE 795 ACSR 26/7. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-01 | 2028-12-07 |  | EP |  | 0 |  | 7.7 |  | 7.7 | 2020-05-22 | Seth Jacobson/Sharlene Rivera-Gonzalez |  |  | FALSE
P19311009 |  | s2274.2 | At Meadowbrook station, install 2 138kV circuit breakers to eliminate the 3 terminal line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-01 | 2028-07-31 |  | EP |  | 0 |  | 2.8 |  | 2.8 | 2020-05-22 | Seth Jacobson/Sharlene Rivera-Gonzalez |  |  | FALSE
P19017002 |  | s2282.1 | Rebuild ~5.0 miles of 138 kV line between Astor - Shannon. The existing Refugee Switch will be retired. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 | 2027-09-01 |  | EP | UC | 0 | 75 | 21.8 |  | 21.8 | 2020-06-19 |  |  |  | FALSE
P19017008 |  | s2282.2 | Rebuild ~0.5 miles and construct ~4.6 miles of greenfield 138 kV line between Groves - Shannon to eliminate the three terminal line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 | 2027-08-05 |  | EP |  | 0 |  | 22 |  | 22 | 2020-06-19 |  |  |  | FALSE
P19017010 |  | s2282.3 | Rebuild ~4.3 miles of 138 kV line between Bixby – Shannon. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | 2025-07-13 | EP | IS | 0 | 100 | 15.1 |  | 15.1 | 2020-06-19 |  |  |  | FALSE
P19017013 |  | s2282.4 | Reconfigure lines at Shannon to accommodate the new 138 kV circuit from Groves. Install two new 138 kV 3000A 40 kA circuit breakers on circuits towards Brice and Bixby to prevent dissimilar zones of protection when bringing the 3rd 138 kV circuit to the station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 | 2027-12-15 |  | EP | UC | 0 | 75 | 1.9 |  | 1.9 | 2020-06-19 |  |  |  | FALSE
P19211005 |  | s2283.1 | Build ~ 3.75 miles of single circuit 138kV transmission line from new Condit 3-way MOAB Switch (tapping the Centerburg – Trent 138kV circuit) to Lott station (Consolidated Co-op). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-04-28 | 2028-11-20 |  | EP |  | 0 |  | 9.86 |  | 9.86 | 2020-06-19 |  |  |  | FALSE
P19211002 |  | s2283.2 | Build Condit 3-way MOAB 138kV switch | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-11-20 | 2028-11-20 |  | EP |  | 0 |  | 0.78 |  | 0.78 | 2020-06-19 |  |  |  | FALSE
P21573020 |  | s2342.1 | Marion – Parsons 40kV: Retire ~5.2 miles of double circuit 40kV line between Marion and Parsons. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-23 |  |  | UC |  | 75 |  | 2.97 |  | 2.97 | 2020-10-16 | Crystal Wood-Hython/Nathen Robers |  |  | FALSE
P19278009 |  | s2344.2 | Add a 69kV bus tie CB to Hadley station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-17 | 2028-04-03 |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2020-07-17 | Teresa Rogers/Michael Hassay |  |  | FALSE
P19238016 |  | s2345.2 | Riverside Station: Replace (2) 138kV breakers and (2) 34.5kV breakers at Riverside. While at the station and taking advantage of the outage AEP will install a new 34.5kV breaker to bring Whirlpool customer, whose delivery point is currently one tower outside of the station, into Riverside station. Install high side circuit switcher to 138/69-34.5kV transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-04-07 | 2027-06-14 |  | EP |  | 0 |  | 3.3 |  | 3.3 | 2020-07-17 | Joseph Smith/Joshua Smith |  |  | FALSE
P18180007 |  | s2346 | Replace existing 138 kV CBs G, H, I, K, L and N with six new 138 kV 40 kA circuit breakers. Replace existing 138 kV cap bank BB and install a new 138 kV breaker on the new cap bank. Replace existing 46 kV cap bank switcher with a new cap bank switcher. Install a high side circuit switcher on the existing 138/46 kV transformer. Upgrades will be made to the existing road into the station to improve access and space constraints. A flood wall will be installed to mitigate flooding concerns. *Note: 138 kV CS CC failed and has been replaced. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-19 |  |  | EP | UC | 0 | 75 | 10.1 |  | 10.1 | 2020-07-17 |  |  |  | FALSE
P19163001 |  | s2348.4 | Rebuild the Chemical – South Charleston #1 and Chemical – South Charleston #2 46 kV lines with a new double circuit 46 kV line (69 kV standards) from Chemical – Criel Mound. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-17 | 2025-10-09 |  | UC |  | 75 |  | 5.4 |  | 5.4 | 2020-07-17 | Shively, John / Hassay, Michael |  |  | FALSE
P19163007 |  | s2348.5 | At South Charleston, retire the existing circuit breakers A and B and install four new 46 kV 40 kA circuit breakers in a ring at a new station (Criel Mound) adjacent to the existing South Charleston Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-18 | 2025-10-09 |  | UC |  | 75 |  | 11 |  | 11 | 2020-07-17 |  |  |  | FALSE
P19277009, P19277010 |  | s2392.2 | Add a 3000A bus tie CB at 138kV Trier station to separate the 4 MOAB’s in series. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-05-01 |  |  | UC |  | 50 |  | 1.2 |  | 1.2 | 2020-09-11 | Anthony Antronica/Michael Van Schaik |  |  | FALSE
P19198002 |  | s2393.1 | On the South Hicksville – Rob Park 69 kV line. Rebuild the 21.6 miles as currently constructed, including ~2.4 miles of 69 kV double circuit and ~19.2 miles of 69 kV single circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-08-05 | 2028-10-24 |  | EP |  | 0 |  | 50.8 |  | 50.8 | 2020-09-11 | Danielle Hilliard/Brendan Fuller |  |  | FALSE
P19096004 |  | s2393.2 | Rebuild the through path of St Joe 69 kV station. Install a breaker on the Harlan line exit to eliminate four MOABs in series. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-07-23 | 2027-10-14 |  | EP |  | 0 |  | 1.3 |  | 1.3 | 2020-09-11 | Wayne Cooper/Michael Hassay |  |  | FALSE
P19096020 |  | s2393.3 | At Harlan 69 kV (FERC-Distribution) station, replace a switch and line riser in order to accommodate the new line entrance. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-30 | 2027-04-08 |  | EP |  | 0 |  | 0 |  | 0 | 2020-09-11 | Wayne Cooper/Michael Hassay |  |  | FALSE
P19096038 |  | s2393.4 | Replace the West Hicksville 69 kV PoP switch to accommodate the new line height, route and structure/conductor type. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-23 | 2028-09-12 |  | EP |  | 0 |  | 1 |  | 1 | 2020-09-11 | Wayne Cooper/ |  |  | FALSE
P19096012 |  | s2393.5 | In order to rebuild the line, the in-line switch at Vulcraft 69 kV needs to be replaced. The switch replacement will be a 3-way switch with a MOAB toward West Hicksville 69 kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-29 | 2026-03-10 |  | EP |  | 0 |  | 1 |  | 1 | 2020-09-11 | Wayne Cooper/Michael Hassay |  |  | FALSE
P20015002 |  | s2394.1 | Rebuild ~14.3 mi of the Payne - South Hicksville 69 kV circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 | 2028-12-27 |  | EP |  | 0 |  | 30.6 |  | 30.6 | 2020-09-11 |  |  |  | FALSE
P20015011 |  | s2394.3 | Install Seiberi switch as a new 69 kV, 1200A, 3-way Phase-over-Phase switch with sectionalizing capability to eliminate the hard tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 | 2027-05-26 |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2020-09-11 |  |  |  | FALSE
P20015012 |  | s2394.4 | Replace Antwerp Sw with 69 kV, 1200A, 3-way Phase-over-Phase switches with sectionalizing capability, including 4.3 miles of fiber buildout to allow for sectionalizing. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 | 2027-07-30 |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2020-09-11 |  |  |  | FALSE
P20015015 |  | s2394.5 | Replace North Antwerp Sw with 69 kV, 1200A, 3-way Phase-over-Phase switches with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 | 2027-01-29 |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-09-11 |  |  |  | FALSE
P19143001 |  | s2395.1 | Rebuild existing double circuit portion of the Dunkirk – Forest line asset from existing Str 194 to the greenfield Rangeline station (1.35 miles). Rebuild existing ~6.5 mi Arlington – Dunkirk 34.5 kV as Rangeline – East Arlington single 69 circuit from Str 194 to the greenfield East Arlington (formerly Arlington). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  |  | UC |  | 75 |  | 21 |  | 21 | 2020-09-11 |  |  |  | FALSE
P19143007 |  | s2395.5 | Rebuild ~5.75 mi 69 kV line section between greenfield West Crawford Station and Buckrun Switch (outside of Blanchard Station) as single circuit 69 kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2026-06-04 |  | EP |  | 25 |  | 13 |  | 13 | 2020-09-11 |  |  |  | FALSE
P19143059 |  | s2395.6 | Rebuild ~0.22 mi South Vanlue Extension to tie into East Arlington – West Crawford 69 kV ckt. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2026-06-04 |  | EP |  | 25 |  | 0.1 |  | 0.1 | 2020-09-11 |  |  |  | FALSE
P19143009 |  | s2395.7 | Rebuild ~11.5 mi 69 kV line between West Crawford and South Berwick Stations. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2025-12-18 |  | UC |  | 50 |  | 28.9 |  | 28.9 | 2020-09-11 |  |  |  | FALSE
P19143005 |  | s2395.8 | Remove/retire ~10 mi of 69 kV line from Forest to North Wharton Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2026-06-04 |  | EP |  | 25 |  | 8.3 |  | 8.3 | 2020-09-11 |  |  |  | FALSE
P19143018 |  | s2395.9 | Reconfigure North Upper Sandusky – South Berwick 69 kV line to tie into Hurd Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2025-12-18 |  | EP |  | 25 |  | 0.1 |  | 0.1 | 2020-09-11 |  |  |  | FALSE
P19143019 |  | s2395.10 | Remove/Retire ~2.58 mi South Carey – Hurd Switch 69 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2026-02-03 |  | UC |  | 75 |  | 1.9 |  | 1.9 | 2020-09-11 |  |  |  | FALSE
P19143023 |  | s2395.11 | Carey 69kV: Install 69 kV Box Bay with 2000A, 40 kA MOABs with sectionalizing capability. Remove existing Carey Sw. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | 2025-05-29 | UC | IS | 75 | 100 | 1.5 |  | 1.5 | 2020-09-11 |  |  |  | FALSE
P19143024 |  | s2395.12 | West Crawford 69kV (Rebuild): Install a new 69 kV ring bus with three 3000A, 40 kA circuit breakers to replace West Crawford Sw. Replace Cap switcher “AA” and relocate Cap bank from Carey Sw to West Crawford 69 kV bus. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2025-12-18 |  | UC |  | 75 |  | 5.6 |  | 5.6 | 2020-09-11 |  |  |  | FALSE
P19143041 |  | s2395.13 | South Carey Sw 69 kV: Remove South Carey Sw 69 kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | 2025-05-19 | UC | IS | 75 | 100 | 0.1 |  | 0.1 | 2020-09-11 |  |  |  | FALSE
P19143042 |  | s2395.14 | North Wharton Sw 69 kV: Remove North Wharton Sw 69 kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2026-06-09 |  | EP |  | 25 |  | 0.1 |  | 0.1 | 2020-09-11 |  |  |  | FALSE
P19143043 |  | s2395.15 | South Vanlue 69 kV: Replace 69 kV bus and existing switches with 2000A, 40 kA line MOABs with sectionalizing capability. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2027-03-08 |  | EP |  | 25 |  | 0.5 |  | 0.5 | 2020-09-11 |  |  |  | FALSE
P19143040 |  | s2395.21 | Forest 69 kV: Remove 69 kV CB-H towards South Berwick. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2026-12-09 |  | EP |  | 25 |  | 0.1 |  | 0.1 | 2020-09-11 |  |  |  | FALSE
P19143038 |  | s2395.22 | Dunkirk 69 kV: Retire Dunkirk 69kV station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 | 2025-09-02 |  | EP |  | 25 |  | 1 |  | 1 | 2020-09-11 |  |  |  | FALSE
P19066007, P19066008 |  | s2397.1 | Rebuild approximately 1.2 miles of line on the West Huntington – South Point 34.5 kV line between Kenova station and South Point station. Cost drivers on this line section include Ohio River crossing, urban line route through Huntington, WV, and encroachments along the line. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-02-27 |  |  | EP |  | 25 |  | 8.9 |  | 8.9 | 2020-09-11 | Jonathan Wood/Michael Hassay |  |  | FALSE
P19066006 |  | s2397.2 | Rebuild approximately 5.5 miles of line on the West Huntington – South Point 34.5 kV line between Kenova station and West Huntington station. This segment of line is classified as Distribution and thus has no transmission cost. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-02-27 |  |  | EP |  | 25 |  | 0 |  | 0 | 2020-09-11 | Jonathan Wood/Michael Hassay |  |  | FALSE
P19066015 |  | s2397.3 | Install 3-way Phase over Phase GOAB switch at Ceredo Switch Station addressing hard tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-02-13 |  |  | EP |  | 25 |  | 0.6 |  | 0.6 | 2020-09-11 | Jonathan Wood/Michael Hassay |  |  | FALSE
P19066017 |  | s2397.4 | Install 3-way Phase over Phase GOAB switch at Sanitary Board Station addressing hard tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-02-13 |  |  | EP |  | 25 |  | 0.6 |  | 0.6 | 2020-09-11 | Jonathan Wood/Michael Hassay |  |  | FALSE
P19066019 |  | s2397.5 | Install 3-way Phase over Phase GOAB switch at Four Pole Creek Station addressing hard tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-02-13 |  |  | EP |  | 25 |  | 0.6 |  | 0.6 | 2020-09-11 | Jonathan Wood/Michael Hassay |  |  | FALSE
P18009026 |  | s2398.7 | AEP will also install a pole outside of West Moulton Substation and a single span of line to connect the West Moulton-Amsterdam 138kV circuit. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2028-08-31 |  |  | EP |  | 25 |  | 0.25 |  | 0.25 | 2020-10-16 |  |  |  | TRUE
DR20C02B0 |  | s2401.1 | Install a a two breaker (3000A, 40 kA) 69kV straight bus station called Grace along the proposed South Rokeby – West Watertown 69 kV circuit (s2791) to serve the requested delivery point | Customer Service |  |  |  | 2026-04-02 |  |  | EP |  | 25 |  | 1.8 |  | 1.8 | 2023-02-17 |  |  |  | FALSE
DR20C02W0 |  | s2401.2 | Install approximately 0.2 miles of 69kV line to tie the greenfield Grace station in-and-out to the Muskingum River – South Rokeby 69kV circuit. | Customer Service |  |  |  | 2024-11-21 |  |  | EP |  | 25 |  | 2.1 |  | 2.1 | 2020-10-16 | Luz Cohmer |  |  | FALSE
DR20C02C0 |  | s2401.3 | Remove/Relocate approximately 0.05 miles of line on the Muskingum River – South Rokeby 69kV Line asset between structures 75 and 74A to accommodate the cut in to the new station. | Customer Service |  |  |  | 2026-04-02 |  |  | EP |  | 25 |  | 0.1 |  | 0.1 | 2020-10-16 |  |  |  | FALSE
DR20C02D0 |  | s2401.4 | Remote end work at South Rokeby Switch. | Customer Service |  |  |  | 2026-04-02 |  |  | EP |  | 25 |  | 0.9 |  | 0.9 | 2020-10-16 |  |  |  | FALSE
DR20C02D1 |  | s2401.5 | Remove the South Stockport Switch | Customer Service |  |  |  | 2026-04-02 |  |  | EP |  | 25 |  | 0.07 |  | 0.07 | 2023-02-17 |  |  |  | FALSE
P19293006 |  | s2408.3 | At Hill station, replace existing 69 KV circuit breaker H with new 40 KA 3000A circuit breaker. Replace existing 69 KV circuit breaker E with new 40 KA 3000A circuit breaker for constructability flexibility, existing breaker E can be used as a capital spare. Replace existing 69 KV cap bank circuit switcher AA with new circuit breaker. Replace existing 138/69 KV 40 MVA transformer # 1 with new 138/69 KV 40 MVA transformer #1, add H.S. circuit switcher to the new transformer. Replace existing 138KV line MOABs W & Y with new 138 kV circuit breakers. Replace ground MOAB switches on 138/12 KV T2 with circuit switcher. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-05-15 |  |  | EP |  | 25 |  | 6.7 |  | 6.7 | 2020-10-16 |  |  |  | FALSE
P19293019 |  | s2408.4 | Remote end relaying work at Clinch River, Wolf Hills, Lovedale, Holston, West Kingsport. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-05-15 |  |  | EP |  | 0 |  | 2 |  | 2 | 2020-10-16 |  |  |  | FALSE
DX21C03Z0 |  | s2426.1 | Rarden: The existing station will be rebuilt to 69 kV with a new 69kV breaker (3000A, 40kA) facing Adams and a MOAB switch (2000A) facing Otway. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-10-12 |  |  | EP |  | 0 |  | 2.24 |  | 2.24 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
P18150004 |  | s2426.2 | Adams – Rarden 69kV: Reroute the line to the rebuilt Rarden station with 795 ACSR 26/7 (SE 179MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-10-05 |  |  | EP |  | 0 |  | 0.12 |  | 0.12 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
J18150002 |  | s2426.3 | Rarden – Otway 69kV: Install ~8.5 miles of greenfield 69 kV line between Rarden & Otway stations; using 556.5 ACSR 26/7 conductor (SE 142 MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-10-23 |  |  | EP |  | 0 |  | 12.49 |  | 12.49 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
P18150011 |  | s2426.4 | Otway: Construct a new 69kV Station with 4-CBs (3000 Amp, 40kA) in a ring bus configuration. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-11-11 |  |  | EP |  | 0 |  | 5.23 |  | 5.23 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
P18150002 |  | s2426.5 | Tick Ridge Extension: Install ~0.1 miles of greenfield line between Otway and Tick Ridge (Adams) stations using 556.5 ACSR 26/7 conductor (SE 142 MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-09-21 |  |  | EP |  | 0 |  | 0.29 |  | 0.29 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
J18150003 |  | s2426.6 | Otway – McDermott 69kV: Install ~7.3 miles of greenfield 69 kV line between Otway & McDermott stations; using 556.5 ACSR 26/7 conductor (SE 142 MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-09-21 |  |  | EP |  | 0 |  | 17.59 |  | 17.59 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
DX21C03B2 |  | s2426.7 | McDermott: Rebuild the existing station with a 69kV box bay and 2 MOAB switches (2000A) on the line connections. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-12-23 |  |  | EP |  | 0 |  | 2.15 |  | 2.15 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
J18150004 |  | s2426.8 | McDermott – Rosemount 69kV: Install ~6.3 miles of greenfield line between McDermott & Rosemount stations; using 556.5 ACSR 26/7 conductor (SE 142 MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-12-23 |  |  | EP |  | 0 |  | 12.49 |  | 12.49 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
P18150029 |  | s2426.9 | Rosemount: Expand the existing station footprint. Install 5-CBs (3000 Amp, 40kA) in a ring configuration. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-10-15 |  |  | EP |  | 0 |  | 3.88 |  | 3.88 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
P18150028 |  | s2426.10 | Rosemount Extension: Reroute the line into the Rosemount 69kV ring bus with 795 ACSR 26/7 (SE 179MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-10-05 |  |  | EP |  | 0 |  | 0.95 |  | 0.95 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  |  | FALSE
P13064009, P13064010, P13064011, P13064012, P13064014 |  | s2428.4 | Rebuild approximately ~40 miles of Wooton – Pineville 161kV line to address the identified asset condition needs. This work also includes line removal work as well as access road construction. Majority of proposed line rebuild is to be constructed on existing center line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-30 |  |  | EP |  | 0 |  | 115 |  | 115 | 2020-11-20 |  |  |  | FALSE
P13064009, P13064010, P13064011, P13064012, P13064014 |  | s2428.5 | Expand existing ROW for the Wooton – Pineville 161kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-30 |  |  | EP |  | 0 |  | 8.5 |  | 8.5 | 2020-11-20 |  |  |  | FALSE
P14030009 |  | s2428.7 | At Stinnett station, upgrade relaying to accommodate new OPGW fiber protection. Provide transition, entry and termination for OPGW connectivity to the Hazard-Pineville fiber route. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-30 |  |  | EP |  | 25 |  | 0.7 |  | 0.7 | 2020-11-20 |  |  |  | FALSE
P19267003 |  | s2430.2 | Construct ~3.9 miles of new 69kV line from Whitewater station to Fayetteville 69 kV station. Rebuild the line section between Fayetteville and Elmo SS 69kV (~1.7 miles). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-27 |  |  | UC |  | 50 |  | 16.5 |  | 16.5 | 2020-11-20 | Roger Whitt/Michael Hassay |  |  | FALSE
P19267021 |  | s2430.3 | Construct ~1.5 miles of new 69 kV double circuit line from the Carbondale – Tower 117 69 kV circuit to serve the new Victor Station in/out. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-05-19 |  |  | EP |  | 0 |  | 5.8 |  | 5.8 | 2020-11-20 | Roger Whitt/Michael Hassay |  |  | FALSE
P19267021 |  | s2430.5 | Reconfigure a line section between Tower 117 – Carbondale to connect in the new Chestnutburg Station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-07 |  |  | UC |  | 50 |  | 0.6 |  | 0.6 | 2020-11-20 | Roger Whitt/Michael Hassay |  |  | FALSE
DR21H63W0 |  | s2430.7 | Victor Station: Retire/remove Gauley Mountain 69 kV Station. Establish a 69 kV bus and install two new 69 kV 3000 A 40 kA circuit breakers at the new site to be called Victor Station to serve requested Distribution delivery point. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-10-22 |  |  | EP |  | 0 |  | 2.3 |  | 2.3 | 2020-11-20 | Roger Whitt/Michael Hassay |  |  | FALSE
P19267012 |  | s2430.8 | Fayetteville Station: Install a new 69kV 3-way PoP switch outside of the station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-27 |  |  | UC |  | 75 |  | 0.4 |  | 0.4 | 2020-11-20 | Roger Whitt/Michael Hassay |  |  | FALSE
P19267013 |  | s2430.9 | Chestnutburg SS: Const.ruct a new three breaker ring utilizing three new 69kV 3000A 40kA circuit breakers to eliminate a three terminal line connection. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-05-01 |  |  | UC |  | 50 |  | 3.2 |  | 3.2 | 2020-11-20 | Roger Whitt/Michael Hassay |  |  | FALSE
DP19F03B1, DP19F03L1, DP19F03W2, DP19F03Y2 |  | s2431.1 | Rebuild North Kendallville 69/12kV station as Henderson 138/12kV station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2020-11-20 |  |  |  | FALSE
DP19F03B0, DP19F03Y0, DP19F03D1, |  | s2431.2 | Expand Bixler 138/12kV station with a second transformer. Rebuild the through path to accommodate the expansion with a bus tie breaker and line MOAB’s. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  |  | EP |  | 0 |  | 2.5 |  | 2.5 | 2020-11-20 |  |  |  | FALSE
DP19F03D0, DP19F03Z0 |  | s2431.3 | Add a 138kV CB to Kendallville station on the line exit to Henderson. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2020-11-20 |  |  |  | FALSE
DP19F03C0, DP19F03W1, DP19F03W3, DP19F03T0 |  | s2431.4 | Rebuild the ~1.8 mile North Kendallville 69kV tap as the 138kV Henderson – Kendallville line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  |  | EP |  | 0 |  | 5.5 |  | 5.5 | 2020-11-20 |  |  |  | FALSE
DP19F03W0, DP19F03X0 |  | s2431.5 | Build the new ~2.6 mile Henderson – Bixler 138kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  |  | EP |  | 0 |  | 6.9 |  | 6.9 | 2020-11-20 |  |  |  | FALSE
DP19F03B3, DP19F03C2 |  | s2431.6 | Retire the 138kV Bixler Sw, and the ~.6 mile between Bixler SW and Kendallville station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2020-11-20 |  |  |  | FALSE
DR19F07B1 |  | s2432.1 | Retire Harvest Park 34.5kV station and move distribution load source to Lincoln station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0 |  | 0 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19274006 |  | s2432.2 | Retire ~.6 miles of the Storm Water - Lincoln line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19157013 |  | s2432.3 | Retire the ~2.5 mile Anthony – Harvest Park line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19274010 |  | s2432.4 | Retire Filtration Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
A19036056 |  | s2432.5 | Retire the ~1.1 mile Anthony – Lincoln 34.5kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
A19036057 |  | s2432.6 | Retire the ~2.9 mile Anthony – Lincoln 138kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P20213007 |  | s2432.7 | At Lincoln station, move the Storm Water CB to the 69kV bus. Install 138/12kV transformer with new 12kV distribution bay to replace Harvest Park. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 5.7 |  | 5.7 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19157015 |  | s2432.8 | Rebuild the Lincoln – Inca line. Line will connect to the new Lincoln 69/34.5kV extension at Maumee switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-09-19 |  |  | EP |  | 0 |  | 6.3 |  | 6.3 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19274007 |  | s2432.9 | Build a ~0.9 mile 69/34.5kV double circuit line out of Lincoln station to connect to the Lincoln – Maumee 34.5kV line and the Lincoln – Stormwater 69kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 3.4 |  | 3.4 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19157003 |  | s2432.10 | Install a 34.5kV POP Switch to feed Inca station called Maumee switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19274001 |  | s2432.11 | Build a greenfield ~1.7 mile Anthony – Melita 69kV line | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 6.2 |  | 6.2 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P22730001 |  | s2432.12 | At Storm Water station, replace Transformer 1 with a 69/12kV unit and re-energize station at 69kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-08-27 |  |  | EP |  | 0 |  | 0 |  | 0 | 2020-11-20 |  |  |  | FALSE
P19274012 |  | s2432.13 | At Water Pollution station, re-energize station at 69kV. Station was previously built to take either 34.5 or 69 kV service. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0 |  | 0 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19274014 |  | s2432.14 | At Omnisource station, replace Transformer 1 with a 69/4kV unit and re-energize station at 69kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19274009 |  | s2432.15 | At Melita station, install a 3000A 40kA 69kV CB for the Anthony line entrance. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19157006 |  | s2432.16 | At Anthony station, replace both 34.5/12kV transformers with 69/12kV 25MVA units. Replace 2 CB’s with 3000A 40kA 69kV CB’s for the Water Pollution line exit and bus tie positions. Re-use the existing Water Pollution breaker for the new Melita line entrance. Install a 21.6Mvar Cap bank. Retire the 138/34.5kV transformer, the 34.5kV CB’s Q and A, and the existing buswork. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  |  | EP |  | 0 |  | 8.7 |  | 8.7 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P20090003 |  | s2433.3 | Install approximately 0.1 mile radial line extension connecting Towhee Switch to the structure outside SCP’s Paint Creek Substation. | Customer Service |  |  |  | 2025-05-20 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-12-18 |  |  |  | FALSE
P20091006 |  | s2434.1 | Install a greenfield 3-way 69 kV 1200 A phase over phase switch (Bryson Switch) with Auto-Sectionalizing, MOABs, and SCADA to serve the new requested delivery point. Install metering at the proposed customer station. | Customer Service |  |  |  | 2025-05-20 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2020-12-18 |  |  |  | FALSE
P20091001 |  | s2434.2 | Build a ~4.3 miles of greenfield single circuit 69kV transmission line between Hemlock – Bryson Switch with 556 ACSR conductor. | Customer Service |  |  |  | 2025-05-21 |  |  | EP |  | 0 |  | 9.4 |  | 9.4 | 2020-12-18 |  |  |  | FALSE
P20091005 |  | s2434.3 | At Hemlock station, install a new 69kV 3000 A 40kA circuit breaker towards Bryson Switch. | Customer Service |  |  |  | 2025-05-22 |  |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2020-12-18 |  |  |  | FALSE
P19293011 | P17115001, P18220006 | s2435.1 | West Kingsport Station Work: Install five 138 kV 40 kA 3000A CBs and reconfigure existing Bus #2 to a breaker and a half arrangement. Note that the replacement of breaker E was accelerated due to a customer request and constrained outages and is currently in service to feed Industry Drive. Replace existing 34.5 kV CBs A, C and F with three new 69 kV-rated 3000A 40 kA breaker — to be energized at 34.5kV. Replace existing 34.5kV bus structures with new box bays built to 69kV. Remove existing 34.5 KV 14.4 MVAR Cap bank and Cap Bank Switcher. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 |  | 2024-07-18 | EP | IS | 0 | 100 | 9.2 |  | 9.2 | 2020-12-18 |  |  |  | FALSE
DR23R18Y0 |  | s2435.2 | Line work and ROW required to relocate the North Bristol and Industry Drive 138KV lines at West Kingsport Station into the new configuration. This includes installing 3 structures (2 tower structures and 1 custom Steel Pole) to bring North Bristol Circuit in and relocate the Industrial Drive Circuit to final string of breakers. This also includes re-terminating the Ft. Robinson-West Kingsport 34kV line, Cumberland- West Kingsport 34.5kV Line and the Waste Water- West Kingsport 34kV Line into new station bays. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-26 |  |  | EP |  | 0 |  | 4.2 |  | 4.2 | 2020-12-18 |  |  |  | FALSE
P17084055 |  | s2436.2 | Construct a greenfield 138KV Myra Station to replace Elwood Station. Install 138KV double box bay with two 138kV circuit breakers and line exits to Fremont & Beaver Creek. Install 138/34.5 kV transformer with high-side circuit switcher and associated 34.5kV breakers. Install fiber connectivity for upgraded relaying. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 0 |  | 3.43 |  | 3.43 | 2020-12-18 |  |  |  | FALSE
P17084053 |  | s2436.3 | Remote end relaying work at Beaver Creek substation. Remove 46KV Elwood Line 46kV circuit breaker "G“ and associated equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 0 |  | 0.17 |  | 0.17 | 2020-12-18 |  |  |  | FALSE
P17084050 |  | s2436.4 | Remote end relaying work at Fremont substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 0 |  | 0.42 |  | 0.42 | 2020-12-18 |  |  |  | FALSE
P19036002 |  | s2436.5 | At Burton station, retire and remove all existing equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 25 |  | 0 |  | 0 | 2020-12-18 |  |  |  | FALSE
P17084025 |  | s2436.6 | At Elwood station, retire and remove all existing equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 0 |  | 0 |  | 0 | 2020-12-18 |  |  |  | FALSE
P17084007 |  | s2436.9 | Construct a new ~2 mi double circuit 138 kV line to the proposed Myra substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 0 |  | 8.8 |  | 8.8 | 2020-12-18 |  |  |  | FALSE
P17084017 |  | s2436.10 | Reconfigure the existing Beaver Creek - Fremont 138kV circuit to facilitate the construction of the new double circuit Myra Extension 138kV Line to feed the proposed Myra Substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 0 |  | 1 |  | 1 | 2020-12-18 |  |  |  | FALSE
P17084020 |  | s2436.11 | Install two replacement structures in order to bypass Elwood station. Transfer wires from old structure to new structure. Tie new structure to Cedar Creek-Henry Clay 46kV Line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 0 |  | 1.35 |  | 1.35 | 2020-12-18 |  |  |  | FALSE
P17084018 |  | s2436.12 | Retire ~10.48 mi Beaver Creek – Elwood 46kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  |  | EP |  | 0 |  | 6.47 |  | 6.47 | 2020-12-18 |  |  |  | FALSE
P17081001 |  | s2438 | Clifford Station: Replace the existing 138/69-46 kV, 50 MVA transformer #1 and 138/46 kV, 20 MVA transformer #3 with two 138/46 kV, 30 MVA transformers. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-16 |  |  | UC |  | 75 |  | 5.9 |  | 5.9 | 2020-12-18 |  |  |  | FALSE
P17081002 |  | s2439 | At Scottsville station, replace the existing 138/46 kV, 20 MVA transformer #1 & #2 (connected in parallel) and 138/46 kV, 20 MVA transformer #5 with two 138/46 kV, 30 MVA transformers; replace 46/12 kV, 5 MVA transformer #3 with 46/12 kV, 20 MVA transformer; replace 46 kV circuit breaker E; add 12 kV circuit breaker & feeder. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-16 |  |  | EP |  | 0 |  | 7 |  | 7 | 2020-12-18 |  |  |  | FALSE
P19298001 |  | s2440.1 | Rebuild the 7.7 mile long Bridgman-Pletcher line with 556 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-07 |  |  | EP |  | 0 |  | 18.8 |  | 18.8 | 2020-12-18 | Mitchell Rice/Joshua Smith |  |  | FALSE
P19298015, P19298026, P19298027, P19298037 |  | s2440.2 | Install new 69/34.5kV Bucktown station to replace Buchanan Hydro station. Install new 69/34.5kV transformer with (2) 34.5kV line breakers and a (4) 69kV breaker ring bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-07 |  |  | EP |  | 0 |  | 10.4 |  | 10.4 | 2020-12-18 | Mitchell Rice/Joshua Smith |  |  | FALSE
P19298009 , P192980010, P192980011 |  | s2440.3 | Retire 1 mile of 4/0 copper conductor from Buchanan Hydro to Clark Equipment and Jack’s Post customer. Construct 0.1 miles of 34.5 kV line from Jack’s Post to new Bucktown station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-07 |  |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2020-12-18 | Mitchell Rice/Joshua Smith |  |  | FALSE
P19298019, P19298022 |  | s2440.4 | At Buchanan Hydro station, retire the Transmission and Distribution equipment. Install one new 34.5kV breaker for line protection to Bucktown to continue service to the hydro plant. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-07 |  |  | EP |  | 0 |  | 1.3 |  | 1.3 | 2020-12-18 | Mitchell Rice/Joshua Smith |  |  | FALSE
P19095012 |  | s2444.1 | At Meadowview station, replace 69KV circuit breakers F&G with new 69kV 3000A 40kA breakers. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-01 |  |  | UC |  | 50 |  | 1.86 |  | 1.86 | 2020-12-18 |  |  |  | FALSE
P19095003 |  | s2444.2 | At South Abingdon, install a new 90 MVA 138/ 69KV transformer bank. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-01 |  | 2025-05-22 | UC | IS | 50 | 100 | 3.4 |  | 3.4 | 2020-12-18 |  |  |  | FALSE
P19095001 |  | s2444.3 | Construct a new 69kV line from South Abingdon to Arrowhead (~6.6 miles) (SN:129 MVA, SE: 180 MVA, WN: 162 MVA, WE: 202 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-01 |  | 2025-05-22 | UC | IS | 50 | 100 | 20.2 |  | 20.2 | 2020-12-18 |  |  |  | FALSE
P19095008 |  | s2444.4 | At Arrowhead station, install three 69kV 3000A 40kA breakers towards Damascus, Hillman Highway, and South Abingdon. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-12 |  | 2025-05-22 | UC | IS | 50 | 100 | 2.2 |  | 2.2 | 2020-12-18 |  |  |  | FALSE
P19095016 |  | s2444.5 | Retire the 69kV section of line from Abingdon to Hillman Highway (~5 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-05 |  |  | UC |  | 50 |  | 6.2 |  | 6.2 | 2020-12-18 |  |  |  | FALSE
P20039001 |  | s2444.6 | Rebuild ~23 miles of the Hillman Highway – Saltville 69 kV line (SN:129 MVA, SE: 180 MVA, WN: 162 MVA, WE: 202 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-08 |  |  | UC |  | 50 |  | 57.5 |  | 57.5 | 2020-12-18 |  |  |  | FALSE
P20039001 |  | s2444.7 | Retire ~23 miles of the Hillman Highway – Saltville 69 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-08 |  |  | UC |  | 50 |  | 6.9 |  | 6.9 | 2020-12-18 |  |  |  | FALSE
P20039007 |  | s2444.8 | Hillman Highway Remote End Work. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-08 |  |  | UC |  | 50 |  | 0.1 |  | 0.1 | 2020-12-18 |  |  |  | FALSE
P19095004 |  | s2444.9 | At Abingdon station, retire 138/69-12kV transformer bank #1 and associated equipment. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-01 |  |  | UC |  | 50 |  | 0.3 |  | 0.3 | 2020-12-18 |  |  |  | FALSE
P19305008 |  | s2446.1 | Replace Belfry substation with Orinoco substation by installing a 69KV box bay and 12KV rural bay to be built in the clear southwest of existing Belfry station. Install 69/12kV 20 MVA transformer and two 12kV breakers. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 0.65 |  | 0.65 | 2021-01-15 |  |  |  | FALSE
P19305008 |  | s2446.2 | Retire Belfry 46kV substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 0 |  | 0 | 2021-01-15 |  |  |  | FALSE
P19305010 |  | s2446.3 | Retire 46kV equipment from Stone substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 0.07 |  | 0.07 | 2021-01-15 |  |  |  | FALSE
P19305009 |  | s2446.4 | At Hatfield substation, replace MOAB Y with a 69KV Circuit Breaker towards Stone 69kV line via New Camp and Orinoco. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 0.85 |  | 0.85 | 2021-01-15 |  |  |  | FALSE
P19305012 |  | s2446.5 | Retire the 46kV equipment at Sprigg station towards Stone (via Belfry). | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 0.05 |  | 0.05 | 2021-01-15 |  |  |  | FALSE
P19305014 |  | s2446.6 | Retire Turkey Creek Tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 0.76 |  | 0.76 | 2021-01-15 |  |  |  | FALSE
P19305005, P19305006 |  | s2446.7 | Retire the ~8.23 miles of the 46kV Sprigg – Stone 46 KV circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 6.73 |  | 6.73 | 2021-01-15 |  |  |  | FALSE
P15095041 |  | s2464 | Rebuild ~2 miles of 138kV line between East Wheelersburg and Texas Eastern using 795 ACSR 26/7 Drake (SE 359 MVA). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-04-15 |  |  | EP |  | 0 |  | 3.41 |  | 3.41 | 2021-02-17 |  |  |  | FALSE
P20004001 |  | s2465.1 | Retire ~3 miles of the Philo- Canton 138kV line, between Philo and East New Concord. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 6.18 |  | 6.18 | 2021-02-17 |  |  |  | FALSE
P20004003 |  | s2465.2 | Retire ~18 miles of the Philo-Torrey 138kV line, north of Bethel Church/Bloomfield and stopping at Newcomerstown. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 6.01 |  | 6.01 | 2021-02-17 |  |  |  | FALSE
P20004004 |  | s2465.3 | Rebuild from Philo to Str 62 a ~13.07 mile section of the Philo – Torrey 138kV line as double circuit, using 795 KCMIL 26/7 ACSR "Drake" conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 32.65 |  | 32.65 | 2021-02-17 |  |  |  | FALSE
P20004006 |  | s2465.4 | Build a greenfield ~4.76 mile double circuit line between Str. 62 on the Philo – Torrey line to the greenfield East New Concord Switch, using 795 KCMIL 26/7 ACSR "Drake" conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 13.27 |  | 13.27 | 2021-02-17 |  |  |  | FALSE
P20004002 |  | s2465.5 | Rebuild from the greenfield East New Concord Switch to Newcomerstown station a ~19.72 mile section of the Philo – Canton 138kV line as double circuit, using 795 KCMIL 26/7 ACSR "Drake" conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 49.26 |  | 49.26 | 2021-02-17 |  |  |  | FALSE
P20004008 |  | s2465.6 | Install a 3 Way Phase Over Phase Switch, 1200A, 138 KV Full SCADA Functionality (Rustic Switch) to replace the hard tap to Bridgeville. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.63 |  | 0.63 | 2021-02-17 |  |  |  | FALSE
P20004011 |  | s2465.7 | Rebuild the 1.9-mile radial T-line tap to Bridgeville as a double-circuit in-and-out loop up to the new 3-way switch, Rustic Switch. The new line will use 556.5 KCMIL ACSR 26/7 "Dove”. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 4.62 |  | 4.62 | 2021-02-17 |  |  |  | FALSE
P20004007 |  | s2465.8 | Install a 3 Way Phase Over Phase Switch, 1200A, 138 KV Full SCADA Functionality (Chandlersville Switch) to replace the hard tap to Chandlersville. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.63 |  | 0.63 | 2021-02-17 |  |  |  | FALSE
P20004013 |  | s2465.9 | A new 0.12-mile double circuit 138kV loop line is to be constructed to replace the existing tap to GM Co-op Chandlerville station, to supply a loop line circuit to a new switch structure. The new line will use 556.5 KCMIL ACSR 26/7 "Dove”. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 1.3 |  | 1.3 | 2021-02-17 |  |  |  | FALSE
P20004018 |  | s2465.10 | Install a 3 Way Phase Over Phase Switch, 1200A, 138 KV Full SCADA Functionality (Norfield Switch) to replace the hard tap to Bethel Church. Remove the existing Bloomfield 1-way switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.65 |  | 0.65 | 2021-02-17 |  |  |  | FALSE
P20004014 |  | s2465.11 | A new 0.5-mile double circuit 138kV line is to be constructed to replace a portion of the Philo- Torrey 138kV line, to supply a loop line circuit to a new two pole dead-end with one of the poles of the two pole dead-end supporting a new switch structure. From the switch structure, it will connect to an existing structure of the existing tap line to supply the Bloomfield – GM Co-op tap. The new line will use 556.5 KCMIL ACSR 26/7 "Dove". | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.96 |  | 0.96 | 2021-02-17 |  |  |  | FALSE
P20004010 |  | s2465.12 | Install a 3 Way Phase Over Phase Switch, 1200A, 138 KV Full SCADA Functionality (East New Concord Switch) to replace the hard tap to East New Concord. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.63 |  | 0.63 | 2021-02-17 |  |  |  | FALSE
P20004021 |  | s2465.13 | Upgrade the line protection relays at Philo, replacing the electromechanical relays with modern microprocessor-based relays. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.16 |  | 0.16 | 2021-02-17 |  |  |  | FALSE
P20004028 |  | s2465.14 | Connect OPGW fiber to stations and switches along the route, for telecom network connectivity. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.47 |  | 0.47 | 2021-02-17 |  |  |  | FALSE
P19296008 |  | s2469.1 | Rebuild ~43 miles of double circuit 138 kV line between Reusens and Roanoke substations. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-01-23 |  |  | EP |  | 0 |  | 142 |  | 142 | 2021-03-19 |  |  |  | FALSE
P19296002, P19296021, P19296024, P19296025, P19296027, P19296029, P19296031 |  | s2469.2 | Acquire additional Reusens-Roanoke 138 kV ROW as needed for the rebuild. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 13.7 |  | 13.7 | 2021-03-19 |  |  |  | FALSE
P19296007 |  | s2469.3 | Reconductor ~0.1 mile span into Ivy Hill Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2021-03-19 |  |  |  | FALSE
P19296008 |  | s2469.4 | Tie into the existing Roanoke-Cloverdale 138 kV Line via a new ~0.3 mile extension. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2021-03-19 |  |  |  | FALSE
P19296009 |  | s2469.5 | Install new wire as underbuild on the Reusens-Roanoke 138kV line and re-route the existing Campbell Avenue-Roanoke 34.5 kV line due to Roanoke substation reconfiguration. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2021-03-19 |  |  |  | FALSE
P19296018 |  | s2469.6 | Re-route the existing Roanoke-Walnut 69kV line due to Roanoke substation reconfiguration. Three (3) replacement structures are expected to shift the alignment and follow the western part of the substation fence to terminate into the new box bay at Reusens Substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2021-03-19 |  |  |  | FALSE
P19296003 |  | s2469.7 | At Roanoke station, replace 138 kV capacitor bank switcher “BB” with a 3000 A, 40 kA circuit breaker. Replace 138 kV capacitor bank switcher “CC” with a 3000 A, 40 kA circuit breaker. Replace 138 kV capacitor bank “CC” with a new 57.6 MVAr capacitor bank. Install high-side circuit switchers on Transformers #2 (138/34.5 kV) and #5 (138/69 kV). Replace transformer #5 (138/69/12 kV) with a 130 MVA, 138/69/12 kV transformer. Replace 69 kV circuit breakers “U” and “V” with 2000 A, 40 kA circuit breakers. Replace pilot wire relaying with fiber relaying associated with 69 kV CBs “U” and “V”, and 34.5 kV CB “L”. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 10.1 |  | 10.1 | 2021-03-19 |  |  |  | FALSE
P19296006 |  | s2469.8 | At Centerville station, reconfigure existing 138 kV with two (2) new 138 kV circuit breakers on each line exit towards Cloverdale and Reusens substations rated at 3000 A, 40 kA to eliminate the three terminal line. Replace MOAB ground switch with circuit switcher on high-side of the Transformer #1 (138/69/34.5 kV). Replace 69 kV circuit breaker “B”, associated disconnect switches and foundations with 3000 A, 40 kA circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 6.7 |  | 6.7 | 2021-03-19 |  |  |  | FALSE
P19296004 |  | s2469.9 | At Campbell Avenue station, replace pilot wire relaying with fiber relaying associated with 34.5 kV CB-B and 69 kV CB-C. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2021-03-19 |  |  |  | FALSE
P19296005 |  | s2469.10 | At Walnut Avenue station, replace pilot wire relaying with fiber relaying associated with 69 kV CB-C. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2021-03-19 |  |  |  | FALSE
P19296010, P19296011, P19296012 |  | s2469.11 | Install fiber extensions and telecom to support SCADA connectivity along the line and at Vinton, Ivy Hill, Coffee, and Moseley stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2021-03-19 |  |  |  | FALSE
DP20C21Z0 |  | s2472 | Fifth Avenue 138 kV: Upgrade the existing 138 kV partial ring bus to a complete 138 kV ring bus and provide a high side connection for a new Distribution transformer. Complete the 138 kV ring bus by adding 2-138 kV circuit breakers along with associated bus work and relaying equipment. | Customer Service |  |  |  | 2025-04-25 |  |  | EP |  | 0 |  | 1 |  | 1 | 2021-03-19 | Adam Forshey/Brian Hatt |  |  | FALSE
P20151001, P20151002, P20151003, P20151004 |  | s2510 | Rebuild 0.96 miles of the AM General #2 – Twin Branch 34.5 kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-02-23 |  |  | EP |  | 0 |  | 4.3 |  | 4.3 | 2021-04-16 |  |  |  | FALSE
P19303004 |  | s2522.1 | Rebuild the existing 5.36 mile Lakin – Lock Lane 69 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-17 |  |  | EP |  | 0 |  | 11.9 |  | 11.9 | 2021-05-21 |  |  |  | FALSE
P19302008 |  | s2522.2 | Point Pleasant Station: replace existing 69 kV circuit breakers G and H with two new 69 kV 3000 A 40 kA circuit breakers. Replace existing cap switcher AA with a new 69 kV cap switcher. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-31 |  |  | EP |  | 0 |  | 2.1 |  | 2.1 | 2021-05-21 |  |  |  | FALSE
P20186005 |  | s2523.1 | West Malta: Replace circuit breaker “A” with a 69kV 3000A 40kA circuit breaker. Replace MOAB “X” with a 69kV SCADA controlled switch. Remove Capacitor bank “AA” and the circuit switcher | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-22 |  |  | EP |  | 0 |  | 1.87 |  | 1.87 | 2021-05-21 |  |  |  | FALSE
P20186006 |  | s2523.2 | South Rokeby: Remote end upgrades to coordinate with new relaying at West Malta will require a transclosure at South Rokeby and an upgrade to the existing station service. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-23 |  |  | EP |  | 0 |  | 0.69 |  | 0.69 | 2021-05-21 | Karmyn Wilford/Sophia Halter |  |  | FALSE
P20249003 |  | s2524.1 | Rebuild from Howard to Ohio Central as 138kV double-circuit (64 miles), using 795 ACSR conductor. Note that the approx. 0.5 mile 138kV line segments outside Ohio Central station will not be rebuilt, as they are newer and in better condition; connect these existing T-line segments to the rebuilt Philo-Howard line asset. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-01 |  |  | EP |  | 0 |  | 142.26 |  | 142.26 | 2021-05-21 |  |  |  | FALSE
P20250003 |  | s2524.2 | Rebuild from Ohio Central to Philo as 138kV single-circuit (19 miles), using 795 ACSR conductor. The existing Ohio Central-Philo #2 138kV circuit will be retired. Update both terminal stations to account for the retired circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-01 |  |  | EP |  | 0 |  | 43.45 |  | 43.45 | 2021-05-21 |  |  |  | FALSE
P20014015 |  | s2524.4 | At West Trinway station, replace 138kV through-path risers & bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-22 |  | 2025-05-29 | UC | IS | 75 | 100 | 0.12 |  | 0.12 | 2021-05-21 |  |  |  | FALSE
P20249007 |  | s2524.5 | Modify 138kV protective relay settings at Philo, Culbertson, Ohio Central, Academia, North Bellville, North Lexington, and Howard stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-01 |  |  | EP |  | 0 |  | 0.69 |  | 0.69 | 2021-05-21 |  |  |  | FALSE
P20024001 |  | s2525.1 | Rebuild of the Astor – East Broad 138 KV circuit, approximately 2.75 miles in length; with 477KCM ACSS. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 9.5 |  | 9.5 | 2021-05-21 |  |  |  | FALSE
P20024002 |  | s2525.2 | Astor 138 kV Station: Remote end work including replacing the line surge arresters, relay settings, and line termination. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2021-05-21 |  |  |  | FALSE
|  | s2525.3 | East Broad 138 kV Station: Remote end work including relay settings and line termination. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 0.02 |  | 0.02 | 2021-05-21 |  |  |  | FALSE
P20005019 |  | s2526.2 | Cyprus – Cyprus (Customer) 138 kV #1: Build ~0.3miles of double circuit 138kV line using 795 ACSR conductor. Extend fiber cable & install redundant fiber cable for relaying and communication to the customer station. One circuit will serve customer’s first building, second circuit will be partially constructed to be utilized for future second building to customer’s redundancy requirements. | Customer Service |  |  |  | 2025-02-28 |  | 2022-11-18 | EP | IS | 0 | 100 | 0.96 |  | 0.96 | 2021-05-21 |  |  |  | FALSE
P20005002 |  | s2526.3 | Cyprus – Cyprus (Customer) 138 kV #2: Build ~0.3miles of double circuit 138kV line using 795 ACSR conductor. Extend fiber cable & install redundant fiber cable for relaying and communication to Customer Station. One circuit will serve customer’s first building, second circuit will be partially constructed to be utilized for future second building due to customer’s redundancy requirements. | Customer Service |  |  |  | 2025-02-28 |  |  | EP |  | 0 |  | 0 |  | 0 | 2021-05-21 |  |  |  | FALSE
P21580002 |  | s2527.7 | West Millersport – West Lancaster 138 kV Sag Study Mitigation: The new customer will increase loading on the existing West Millersport – West Lancaster 138 kV circuit. Multiple structure and distribution crossing issues will be mitigated on the line in order to allow the line to operate to its conductor’s designed maximum operating temperature. | Customer Service |  |  |  | 2024-12-17 |  |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2021-05-21 |  |  |  | FALSE
P20009040 |  | s2534.1 | Construct ~ 5.1 miles of new 69 kV line between the existing Trail and Alpine delivery points using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 18.5 |  | 18.5 | 2020-11-20 |  |  |  | FALSE
P20009007 |  | s2534.4 | Retire West Wilmont Jct Sw. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.04 |  | 0.04 | 2020-11-20 |  |  |  | FALSE
P20009010 |  | s2534.5 | West Wilmont- Holmes Wayne Co-op line work for Alpine station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-11-20 |  |  |  | FALSE
P20009018 |  | s2534.6 | Biliar – West Wilmont 69kV line work for Alpine station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2020-11-20 |  |  |  | FALSE
P20009019 |  | s2534.7 | Beartown – West Wilmont 69kV line work for Alpine station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2020-11-20 |  |  |  | FALSE
P20009002 |  | s2534.8 | Build a new station (called Alpine), replacing West Wilmont Junction Switch. This station will be a 4 breaker 69kV ring bus utilizing 3000A 40kA breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-06-16 |  |  | EP |  | 0 |  | 6.8 |  | 6.8 | 2020-11-20 | David Roudebush/Brendan Fuller |  |  | FALSE
P20009021 |  | s2534.9 | Remote end relay work at Beartown station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.03 |  | 0.03 | 2020-11-20 |  |  |  | FALSE
P20009022 |  | s2534.10 | Remote end relay work at Moreland Sw. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.03 |  | 0.03 | 2020-11-20 |  |  |  | FALSE
P20009008 |  | s2534.11 | Retire Shie Hill Sw. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 0.04 |  | 0.04 | 2020-11-20 |  |  |  | FALSE
P20009003 |  | s2534.12 | Build a new station replacing Shie Hill Sw named Shie Hill. This station will be a 3 breaker 69kV ring bus utilizing 3000A 40kA breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 6.4 |  | 6.4 | 2020-11-20 | David Roudebush/Brendan Fuller |  |  | FALSE
P20009011 |  | s2534.13 | Sugar Creek – Millersburg 34.5kV line work for Shie Hill station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-04-20 |  |  | EP |  | 0 |  | 1.6 |  | 1.6 | 2020-11-20 |  |  |  | FALSE
P20009049 |  | s2534.14 | Shie Hill- Holmes Wayne Co-op line work for Shie Hill station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2020-11-20 |  |  |  | FALSE
P20009028 |  | s2534.15 | Remote end relay work at Sugarcreek Terminal station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2020-11-20 |  |  |  | FALSE
P20009029 |  | s2534.16 | Remote end relay work at Berlin station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2020-11-20 |  |  |  | FALSE
P20009043 |  | s2534.17 | Install a new 138 kV 3000A 40kA breaker at West Millersburg Station on the line towards Wooster to reduce contingency impacts and potential low voltage concerns resulting from the new load. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2020-11-20 |  |  |  | FALSE
P20009027 |  | s2534.18 | Replace the 2-way POP Switch at North Fredericksburg with a new 1200A 69 kV POP with new MOAB’s. The switch currently in place is not capable of supporting the necessary new equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 1 |  | 1 | 2020-11-20 |  |  |  | FALSE
P20009033 |  | s2534.19 | Moreland Sw- Biliar line work for North Fredricksburg Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2020-11-20 |  |  |  | FALSE
P20236001, P20236002, P20236004 |  | s2570.1 | Deer Creek – Hartford City 69 kV: Rebuild ~17.67 miles of 69 kV line with the conductor size 556.5 ACSR 26/7 Dove. The following cost includes the line rebuild, line removal and right of way. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-21 |  |  | EP |  | 0 |  | 40.69 |  | 40.69 | 2021-07-16 |  |  |  | FALSE
P20236003 |  | s2570.2 | Hummel Creek – Deer Creek 34.5 kV: Retire ~4.6 miles of 34.5 kV 1940s wood line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-01-10 |  |  | EP |  | 0 |  | 1.01 |  | 1.01 | 2021-07-16 |  |  |  | FALSE
P20236009 |  | s2570.3 | Jonesboro – Gas City 34.5 kV : Retire ~0.99 miles of 34.5 kV 1969 wood line. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-09-03 |  |  | EP |  | 0 |  | 0.42 |  | 0.42 | 2021-07-16 |  |  |  | FALSE
P20236011 |  | s2570.4 | Deer Creek – Alexandria 34.5 kV : Retire ~2.2 miles of 34.5 kV 1968 wood line. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-08-15 |  |  | EP |  | 0 |  | 1.23 |  | 1.23 | 2021-07-16 |  |  |  | FALSE
P20236005, P20236012 |  | s2570.5 | Hummel Creek 34.5 kV Station: Remove the 34.5 kV circuit breaker “M”. Replace 34.5 kV circuit breaker “L” with a system spare circuit breaker. Rebuild the 34.5 kV bus to a 69 kV standards. Install a 138 kV high side circuit switcher on the 138/34.5 kV transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-06-11 |  |  | EP |  | 0 |  | 1.74 |  | 1.74 | 2021-07-16 |  |  |  | FALSE
P20244001, P20244002, P20244003, P20244004 |  | s2571.1 | Riverside – Hartford 138kV: Rebuild the ~14.7 miles of 1950’s wood H Frame line with 795 Drake ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-06 |  |  | EP |  | 0 |  | 26.9 |  | 26.9 | 2021-07-16 |  |  |  | FALSE
P20244026, P20244005, P20244006, P20244007 |  | s2571.2 | South Haven – Hartford 69kV: Rebuild the ~18.7 miles of 1960’s wood pole line with 795 Drake ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-03-17 | 2025-12-19 |  | EP | UC | 0 | 75 | 37.1 |  | 37.1 | 2021-07-16 |  |  |  | FALSE
P20244012, P20244013 |  | s2571.3 | Phoenix Switch 69kV: Replace the switch with a new POP Switch with line MOAB’s. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-18 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2021-07-16 |  |  |  | FALSE
P19304003 |  | s2572.1 | Rebuild and reconfigure the Saltville 138 KV station in a 3 string breaker-and-a-half bus arrangement to allow replacement of 138 KV CBs A, B, C, V, L, and U with new 3000A 40 KA circuit breakers. Replace existing 69 KV circuit breaker J with a new 3000A 40 KA circuit breaker. Replace existing Transformer #1 with a new 138/69-34.5 KV 50 MVA transformer. Replace existing high side MOAB switches with high side circuit switchers on T2&T5. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-01 |  |  | EP |  | 0 |  | 13.54 |  | 13.54 | 2021-07-16 |  |  |  | FALSE
P19304011 |  | s2572.2 | Line work and ROW required to relocate the Broadford – Saltville #1 138KV, Broadford – Saltville #2 138KV, Clinch River – Saltville 138KV lines to terminate into Saltville Station’s new configuration. This work includes installing 2 structures (steel tower structures) and total of ~0.24 new wire and old wire replacement. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-01 |  |  | EP |  | 0 |  | 1.87 |  | 1.87 | 2021-07-16 |  |  |  | FALSE
P19304001 |  | s2572.3 | Rebuild ~21 miles of the 138KV line between Saltville and Tazewell stations (SN/SE/WN/WE: 296/413/375/464 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-01 |  |  | EP |  | 0 |  | 59.5 |  | 59.5 | 2021-07-16 |  |  |  | FALSE
P19304004 |  | s2572.4 | Remote End Work Costs Tazewell, Meadowview, Broadford and Clinch River Stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-01 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2021-07-16 |  |  |  | FALSE
P20235001 |  | s2574 | Once the Jubal Early to Point Lookout line is built, rebuild the existing ~11.4 mile 69kV Fries – Point Lookout line on the current center line. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-12-19 |  |  | EP |  | 0 |  | 33 |  | 33 | 2021-07-16 |  |  |  | FALSE
P20010027 |  | s2575.1 | Install a new 3-way POP Switch (Mousey Sw) and 69 kV metering to serve North Central’s Sycamore station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 0.68 |  | 0.68 | 2021-07-16 |  |  |  | FALSE
P20010043 |  | s2575.2 | Construct ~ 13 miles of new 69 kV line between Bucyrus Center and the new Mousey Switch delivery point using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 29.3 |  | 29.3 | 2021-07-16 |  |  |  | FALSE
P20010034 |  | s2575.3 | Install a new 69 kV 3000A 40kA breaker and associated terminal equipment at Bucyrus Center on the line towards Mousey switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 1.02 |  | 1.02 | 2021-07-16 |  |  |  | FALSE
P20010007 |  | s2575.4 | Remove the existing West Rockaway 69 kV switch currently used to radially serve the Sycamore delivery point. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 0.08 |  | 0.075 | 2021-07-16 |  |  |  | FALSE
P20010003 |  | s2575.5 | Construct ~ 0.8 miles of new 69 kV line between the existing Sycamore radial line and East Tiffin delivery points using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 2.54 |  | 2.54 | 2021-07-16 |  |  |  | FALSE
P20010036 |  | s2575.6 | Reconfigure East Tiffin station to add in a box bay, a breaker, and terminal equipment towards Mousey switch and a new line MOAB toward South Tiffin. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 2.5 |  | 2.5 | 2021-07-16 |  |  |  | FALSE
P20010016 |  | s2575.7 | Rebuild ~ 2.3 miles of new 69 kV line between the existing Bucyrus and East Bucyrus delivery points using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 5.9 |  | 5.9 | 2021-07-16 |  |  |  | FALSE
P20010012 |  | s2575.8 | Remove ~ 16 miles of existing 69 kV line between the existing East Bucyrus and Howard delivery points. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 5.94 |  | 5.94 | 2021-07-16 |  |  |  | FALSE
P20010019 |  | s2575.9 | Retire the existing ~1.4 miles of the Howard- Bucyrus #2 line between Bucyrus station and structure 366. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 0.32 |  | 0.32 | 2021-07-16 |  |  |  | FALSE
P20010009 |  | s2575.10 | Construct ~ 1.3 miles of new 69 kV line between the existing East Bucyrus delivery point and structure 336 on the Howard- East Bucyrus #2 line. This construction will be coordinated with rebuild project S2156. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  |  | EP |  | 0 |  | 3.3 |  | 3.3 | 2021-07-16 |  |  |  | FALSE
P19248004 |  | s2576.1 | Lick-Jefferson 69kV: Rebuild ~8.3 miles of the 69kV line from Structure 29 to Jefferson switch station with 556.5 ACSR. Install shield wire from Structure 29 to Lick Station, approximately 4 miles. This work requires tree clearing and access road construction in order to add the shield wire to existing structures. Total access road construction is 5.5 miles. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-03-05 |  |  | EP |  | 15 |  | 25 |  | 25 | 2021-07-16 | Pravi Goplan/Andrew Garlick |  |  | FALSE
P19248002 |  | s2576.2 | Echo Valley: Replace existing switch with a 3-way phase over phase 69kV 1200A Switch with SCADA. There will be auto-sectionalizing enabled toward Firebrick. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-04-13 |  |  | EP |  | 0 |  | 1.39 |  | 1.39 | 2021-07-16 | Pravi Goplan/Andrew Garlick |  |  | FALSE
P19248008 |  | s2576.3 | Remote end work associate with the line rebuild at Lick & Firebrick. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-15 |  |  | EP |  | 0 |  | 0.31 |  | 0.31 | 2021-07-16 | Pravi Goplan/Andrew Garlick |  |  | FALSE
P19119005 |  | s2577.1 | Rebuild the South Lancaster – East Logan 69 KV circuit, approximately 16.6 miles in length, with 556.5 ACSR Dove conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-29 |  |  | EP |  | 0 |  | 40 |  | 52 | 2021-07-16 |  |  |  | FALSE
P19119009 |  | s2577.2 | Rebuild the Enterprise Switch - Enterprise Metering Structure, approximately 200’ in length; with 556.5 ACSR Dove conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-27 |  |  | EP |  | 0 |  | 0.51 |  | 0.51 | 2021-07-16 |  |  |  | FALSE
P19119012 |  | s2577.3 | Enterprise Switch: Replace the two way phase over phase switch with a new 1200A three way phase over phase switch with auto sectionalizing and SCADA functionality. Replace the CTs, PTs, and metering. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-27 |  |  | EP |  | 0 |  | 0.93 |  | 0.93 | 2021-07-16 |  |  |  | FALSE
P19119011 |  | s2577.4 | West Logan: Replace the three way phase over phase switch with a new 1200A three way phase over phase switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-21 |  |  | EP |  | 0 |  | 0.77 |  | 0.77 | 2021-07-16 |  |  |  | FALSE
P19119016 |  | s2577.5 | South Lancaster: Remote end work. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-07 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2021-07-16 |  |  |  | FALSE
P20225007 |  | s2578.2 | Innovation Extension 138kV: Tap the existing Babbitt-Kirk 138kV circuit creating the Babbitt-Innovation and Kirk-Innovation 138kV circuits and construct approximately 2.2 miles of double circuit line to serve the new station. Extend the telecom fiber into Innovation station for relaying/communication. | Customer Service |  |  |  | 2025-05-22 |  | 2023-07-26 | EP | IS | 0 | 100 | 13.33 |  | 13.334 | 2021-07-16 |  |  |  | FALSE
P20225016 |  | s2578.4 | Babbitt 138 kV Station: Update remote end relay settings and telecom electronics. | Customer Service |  |  |  | 2025-05-22 |  | 2023-07-26 | EP | IS | 0 | 100 | 0.07 |  | 0.074 | 2021-07-16 |  |  |  | FALSE
P20225017 |  | s2578.5 | Kirk 138 kV Station: Update remote end relay settings and telecom electronics. | Customer Service |  |  |  | 2025-05-22 |  | 2023-07-26 | EP | IS | 0 | 100 | 0.06 |  | 0.062 | 2021-07-16 |  |  |  | FALSE
P22024001, P22024002, P22024007, P20179011, |  | s2584.1 | East Elkhart – Mottville Hydro 138kV: Rebuild the ~10 miles of 1950’s wood on the East Elkhart – Mottville Hydro 138kV line using 795 Drake ACSR | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-08-18 |  |  | EP |  | 0 |  | 31 |  | 31 | 2021-08-16 |  |  |  | FALSE
P20179012, P20179013, P20179025, P20179030 |  | s2584.2 | Mottville Hydro – Corey 138kV: Retire the ~9 mile 138kV line | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-02-12 |  |  | EP |  | 0 |  | 4.25 |  | 4.25 | 2021-08-16 |  |  |  | FALSE
P20179009 |  | s2584.6 | Sturgis 69kV Station: Retire Sturgis 69kV station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-03-25 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2021-08-16 |  |  |  | FALSE
P20179004, P20179005, P20179043, P20179023 |  | s2584.7 | Stubey Rd 138/69kV Station: Expand station to include (6) 69kV CB’s in a ring , (4) 138kV CB’s in a ring, (2) 138/69kV 130MVA XFR’s and (2) 17.6Mvar 69kV Cap Banks. Reterminate the Sturgis IP line into Stubey Road. Reterminate the Corey line into Stubey Road to energize the line at 138 kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-12-20 |  | 2025-02-26 | EP | IS | 0 | 100 | 18.9 |  | 18.9 | 2021-08-16 |  |  |  | FALSE
P20179026 |  | s2584.8 | Howe (Nipsco) – Sturgis 69kV: Retire the ~2.9 mile 69kV line | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-03-25 |  |  | EP |  | 0 |  | 1.9 |  | 1.9 | 2021-08-16 |  |  |  | TRUE
P20179014, P20179015, P20179016 P20179017 |  | s2584.9 | Mottville Hydro – Stubey Rd 138kV: Re-energize the existing line from Mottville – Pigeon River to 138kV and construct a new ~8.9 mile 138kV line between Pigeon River and Stubey Road to re-establish the 138 kV through path to Corey station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-15 |  | 2024-11-14 | EP | IS | 0 | 100 | 23.7 |  | 23.7 | 2021-08-16 |  |  |  | FALSE
P20179031 |  | s2584.10 | Pigeon River 69kV Station: Remove 69kV CB “K” from Pigeon River to re-use at Stubey Rd. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-15 |  | 2024-11-15 | EP | IS | 0 | 100 | 0.4 |  | 0.4 | 2021-08-16 |  |  |  | FALSE
P20179010 |  | s2584.11 | Mottville Hydro 138/69kV Station: Remove 69kV CB “D” from Mottville Hydro to re-use at Stubey Rd. E | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-15 |  | 2024-11-14 | EP | IS | 0 | 100 | 0.4 |  | 0.4 | 2021-08-16 |  |  |  | FALSE
P20179001 |  | s2584.12 | Corey 138/69kV Station: Remove 69kV CB “C” from Corey to re-use at Stubey Rd. E | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-15 |  | 2024-12-20 | EP | IS | 0 | 100 | 0.4 |  | 0.4 | 2021-08-16 |  |  |  | FALSE
P20179018, P20179019 |  | s2584.13 | White Pigeon 69kV Ext: Build new 69kV .2 mile extension from Corey – Pigeon River to the existing White Pigeon Station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-12-17 |  | 2024-11-14 | EP | IS | 0 | 100 | 1.7 |  | 1.7 | 2021-08-16 |  |  |  | FALSE
P20213015 |  | s2632.1 | Lincoln – Tillman 34.5kV line: Retire approximately ~11 miles of the Lincoln – Tillman 34.5kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  |  | EP |  | 0 |  | 2.8 |  | 2.8 | 2021-09-17 |  |  |  | FALSE
P20213007 |  | s2632.2 | Lincoln 138/69/34.5kV substation : Remove Lincoln CB “P”. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2021-09-17 |  |  |  | FALSE
P20213008, P20213009 |  | s2632.3 | Tillman 138/34.5kV substation: Remove CB “A” and “B” as well as the 138/34.5kV transformer and all 34.5kV equipment | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2021-09-17 |  |  |  | FALSE
P20213006 |  | s2632.4 | St Rd 14 Sw: Remove St Rd 14 34.5kV Sw | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2021-09-17 |  |  |  | FALSE
P20213010, P20213011 |  | s2632.5 | Huguenard 138kV extension: Rebuild a portion of the Lincoln-Tillman line as a new ~2.5 mile 138kV double circuit extension from the Allen – Milan 138kV line to Huguenard 138/34.5kV substation | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  |  | EP |  | 0 |  | 7.9 |  | 7.9 | 2021-09-17 |  |  |  | FALSE
P20213001, P20213002, P20213003, P20213016 |  | s2632.6 | Huguenard 138/34.5kV station: Build the new 138/34.5kV substation to feed the St Rd 14 load. This station will have 2 138kV CB’s, 1 138kV Circuit switcher, 1 34.5kV CB and a 138/34.5kV 30MVA XFR. The XFR, 34.5kV CB and high side switcher will be reused from Tillman substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  |  | EP |  | 0 |  | 5.1 |  | 5.1 | 2021-09-17 |  |  |  | FALSE
P20213010, P20213011 |  | s2632.7 | Huguenard – ST Rd 14 34.5kV: Rebuild the radial 34.5kV line to connect to the new Huguenard substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2021-09-17 |  |  |  | FALSE
P19268001 |  | s2634.1 | Construct approximately 3 miles of new 46 kV line from Kincaid to Westerly. Rebuild 5.4 miles of the existing Westerly – Pax Branch 46 kV line. New line to be constructed at 69 kV, operated at 46 kV. Install fiber on the new line construction for upgraded relaying communication. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 23.1 |  | 23.1 | 2021-09-17 |  |  |  | FALSE
P19268004 |  | s2634.2 | Retire Toms Fork – Westerly 46 kV and Toms Fork – Str. 364-13 46 kV (approximately 24 miles total) | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-07 |  |  | EP |  | 0 |  | 8.9 |  | 8.9 | 2021-09-17 |  |  |  | FALSE
P19268005 |  | s2634.3 | 6 wire the existing double circuit 46 kV line from Cabin Creek to Str. 364-13 to maintain the feed to Rhoda station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2021-09-17 |  |  |  | FALSE
p19268007 |  | s2634.4 | Construct a new 138 kV double circuit in/out (approx. 2 miles) from Kanawha – Sundial #1 138 kV circuit to Toms Fork Station. Because of the very rugged terrain in the area, large angles and long span construction is required. These heavy angles and long spans mean minimal tangent structures could be utilized and required dead end towers for nearly every structure instead. These dead end towers are very heavy, resulting in larger equipment and steel costs, and require large foundations resulting in higher costs | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 9.1 |  | 9.1 | 2021-09-17 |  |  |  | FALSE
P19268009 |  | s2634.5 | Convert Toms Fork Station to 138 kV by installing a new 138/12 kV XFR, circuit switcher and two 138 kV line switches. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2021-09-17 |  |  |  | FALSE
P19268012 |  | s2634.6 | Replace existing switches at Westerly Station with two new 1200 A switches. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2021-09-17 |  |  |  | FALSE
P1919268015 |  | s2634.7 | Replace existing switches at Fork Ridge/Mossy Creek with two new 1200 A switches, renamed Haystack Station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2021-09-17 |  |  |  | FALSE
P19268016 |  | s2634.8 | Kincaid remote end work. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2021-09-17 |  |  |  | FALSE
P19268017 |  | s2634.9 | Pax Branch remote end work. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2021-09-17 |  |  |  | FALSE
P21016002 |  | s2635.1 | Replace existing hard tap at SCSM with a new 1200 A three way SCADA controlled MOAB switch | Operational Flexibility and Efficiency |  |  |  | 2025-04-18 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2021-09-17 | Jared/Frye/Michael Hassay |  |  | FALSE
P21016005 |  | s2635.2 | Replace existing hard tap at CMS with a new 1200 A three way switch | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-04-18 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2021-09-17 | Jared/Frye/Michael Hassay |  |  | FALSE
P21016001 |  | s2635.3 | Reconfigure 0.13 mile of the Chemical – Ward Hollow line to accommodate the new switches being installed | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-04-18 |  |  | EP |  | 0 |  | 1.8 |  | 1.8 | 2021-09-17 | Jared/Frye/Michael Hassay |  |  | FALSE
P20011027 |  | s2637.1 | Install a new 69 kV 3-way POP Switch (Kilbourne Sw) and 69 kV metering to serve North Central’s Republic Station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.64 |  | 0.64 | 2021-09-17 |  |  |  | FALSE
P20011005 |  | s2637.2 | Construct a new 3- breaker 69kV Station in a ring configuration named Founders | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 5.1 |  | 5.1 | 2021-09-17 |  |  |  | FALSE
J20011001 |  | s2637.3 | Construct ~ 8 miles of new 69 kV line between Tiffin Center and the new Kilbourne Switch delivery point using 556 ACSR conductor. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 11.99 |  | 11.99 | 2021-09-17 |  |  |  | FALSE
P20011025 |  | s2637.4 | Install a new 69 kV 3000A 40kA breaker and associated terminal equipment at Tiffin Center on the line towards Kilbourne switch | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2021-09-17 |  |  |  | FALSE
P20011001 |  | s2637.5 | Remove the existing Honey Creek 69 kV switch currently used to radially serve the Republic delivery point | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2021-09-17 |  |  |  | FALSE
P20011007 |  | s2637.6 | Construct ~ 0.83 miles of new 69 kV double circuit line between structure 103 on the Carrothers- Greenlawn circuit to the new Founders delivery point using 556 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 2.4 |  | 2.4 | 2021-09-17 |  |  |  | FALSE
DX20A02A0 |  | s2638.1 | Construct a new 69-12kV station (“Ruby”) 0.2-mile to the east of Robyville, on new property. The station will have a 4-breaker 69kV ring bus, with 3- 69kV circuit connections and serving one AEP Ohio distribution transformer | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-11-30 |  |  | EP |  | 0 |  | 6.2 |  | 6.2 | 2021-09-17 | luz Cohmer/Jerod Marker |  |  | FALSE
P17125009 |  | s2638.2 | At the 69kV remote-end of South Cadiz: Replace 69kV circuit breaker D, line relays to Ruby, and 69kV bus protection; expand control building | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-01-23 |  |  | EP |  | 0 |  | 1.3 |  | 1.3 | 2021-09-17 | luz Cohmer/Jerod Marker |  |  | FALSE
DX20A02B1 |  | s2638.3 | At the 69kV remote-end of Dillonvale: Replace 69kV circuit breaker B, line relays to Ruby, and 69kV bus protection | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-11-30 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2021-09-17 | luz Cohmer/Jerod Marker |  |  | FALSE
P17125013 |  | s2638.4 | Re-route the three 69kV transmission lines near Robyville to extend to the new Ruby station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-02-18 |  |  | EP |  | 0 |  | 1.8 |  | 1.8 | 2021-09-17 | luz Cohmer/Jerod Marker |  |  | FALSE
P17125011 |  | s2638.5 | Remove the former DTE Coal 69kV switch just south of South Cadiz station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-01-23 |  |  | EP |  | 0 |  | 0.04 |  | 0.04 | 2021-09-17 | luz Cohmer/Jerod Marker |  |  | FALSE
P17125020 |  | s2638.6 | Retire the existing Robyville station and remove all equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-02-18 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2021-09-17 | luz Cohmer/Jerod Marker |  |  | FALSE
DP21C05Z0 |  | s2639.1 | Poth 138 kV Station: Construct a greenfield station 138kV ring bus with (4) 3000A 63kA 138kV breakers and two 138/13 kV transformers to replace the existing 40 kV station. | Customer Service |  |  |  | 2024-08-09 |  | 2025-04-01 | EP | IS | 0 | 100 | 4.19 |  | 4.19 | 2021-09-17 | Hannah ing/Robert Richardson |  |  | FALSE
DP21C05D4 |  | s2639.2 | East Broad 138 kV Station: Replace CB 3 & CB 7 and 4 disconnect switches with 3000A 63kA 138kV breakers and 4-3000A disconnect switches and install new relaying to coordinate with the new relays at Poth station | Customer Service |  |  |  | 2024-08-13 |  | 2025-04-01 | EP | IS | 0 | 100 | 0.79 |  | 0.793 | 2021-09-17 | Hannah ing/Robert Richardson |  |  | FALSE
DP21C05Z0 |  | s2639.3 | Yearling 138 kV Station: Remote end relay settings | Customer Service |  |  |  | 2024-08-13 |  | 2025-04-01 | EP | IS | 0 | 100 | 0.06 |  | 0.064 | 2021-09-17 | Hannah ing/Robert Richardson |  |  | FALSE
DP21C05W2 |  | s2639.4 | Poth Extension 138 kV: Tap the existing East Broad-Bexley 138kV line into Poth station by constructing approximately 0.5 miles of greenfield lines from the line taps. Extend telecom ADSS for relaying and communication from Bexley to Poth & East Broad to Poth. | Customer Service |  |  |  | 2024-08-13 |  | 2025-04-01 | EP | IS | 0 | 100 | 3.06 |  | 3.06 | 2021-09-17 | Hannah ing/Robert Richardson |  |  | FALSE
P20210002 |  | s2640.1 | At West Dover station, install 4- 138kV breakers in a ring bus arrangement. Install 1- 69kV breaker on the low-side of the 138-69kV transformer. Remove the existing control building and install a new prefabricated drop-in-control-module (DICM). Upgrade the 69kV circuit protection to Sugarcreek, replacing electromechanical relays with new fiber-based protection. Various improvements to the station site, including new fencing, grading, and station service | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-12 |  | 2024-12-30 | UC | IS | 31 | 100 | 7.03 |  | 7.03 | 2021-09-17 | Todd Sides/Jerod Marker |  |  | FALSE
P20210004 |  | s2640.2 | Re-terminate the 3- 138kV transmission lines at West Dover to connect to the new ring bus layout. The Sugarcreek 138kV tap will be re-routed slightly. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-12 |  | 2024-12-19 | UC | IS | 31 | 100 | 0.77 |  | 0.77 | 2021-09-17 | Todd Sides/Jerod Marker |  |  | FALSE
P20210005 |  | s2640.3 | Remote-end 69kV protection upgrades at Sugarcreek station, to coordinate with the West Dover upgrades | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 |  | 2024-12-19 | UC | IS | 31 | 100 | 0.51 |  | 0.51 | 2021-09-17 | Todd Sides/Jerod Marker |  |  | FALSE
P19178030 |  | s2650.1 | Rebuild Mark Center station in the clear as Platter Creek station. Install 4 new 3000A, 40kA, 69 kV breakers at the new Platter Creek ring bus and add a DICM. Upgrade NW Coop 69 kV metering. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  |  | UC |  | 31 |  | 6.37 |  | 6.37 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  |  | FALSE
P19178013 |  | s2650.2 | Retire existing Mark Center station. Relocate circuit switcher AA to Platter Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  |  | UC |  | 31 |  | 0.76 |  | 0.76 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  |  | FALSE
P19178018 |  | s2650.3 | Remote end work at South Hicksville station | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  |  | UC |  | 31 |  | 0.57 |  | 0.57 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  |  | FALSE
P19178030 |  | s2650.4 | Relocate Mark Center – Continental to terminate at Platter Creek | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  |  | UC |  | 31 |  | 0.37 |  | 0.37 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  |  | FALSE
P19178008 |  | s2650.5 | Relocate Mark Center – Paulding to terminate at Platter Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | 2025-03-20 | UC | IS | 31 | 100 | 0.51 |  | 0.51 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  |  | FALSE
P19178006 |  | s2650.6 | Relocate Mark Center – South Hicksville to terminate at Platter Creek | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  |  | UC |  | 31 |  | 0.4 |  | 0.4 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  |  | FALSE
P19178010 |  | s2650.7 | Relocate Mark Center- NW Co-op to terminate at Platter Creek | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | 2025-03-20 | UC | IS | 31 | 100 | 0.02 |  | 0.02 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  |  | FALSE
P20224003 |  | s2651.1 | Rebuild the Philo-Torrey 138kV transmission line between South Canton and Torrey (3.5 miles). The circuits affected are South Canton-Timken Richville and Timken Richville-Timken 138kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-01 |  |  | EP |  | 0 |  | 7.64 |  | 7.64 | 2021-10-15 |  |  |  | FALSE
P20224001 |  | s2651.2 | Rebuild the Philo-Canton 138kV transmission line between South Canton and Sunnyside (5.5 miles). The circuits affected are South Canton-Southeast Canton and Southeast Canton-Sunnyside 138kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-01 |  |  | EP |  | 0 |  | 14.22 |  | 14.22 | 2021-10-15 |  |  |  | FALSE
P20224010 |  | s2651.3 | Replace the 138kV switches at Faircrest Street station to accommodate the new line structures. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-01 |  |  | EP |  | 0 |  | 0.12 |  | 0.12 | 2021-10-15 |  |  |  | FALSE
P19099014 |  | s2651.4 | At Sunnyside, upgrade the relays on the 138kV circuit to Southeast Canton. The control building needs expanded to accommodate the new relay panels. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-01 |  |  | EP |  | 0 |  | 0.73 |  | 0.73 | 2021-10-15 |  |  |  | FALSE
P21033014 |  | s2652 | Install a new 69kV 3000A 40kA breaker to replace breaker K at Howard station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2021-10-15 |  |  |  | FALSE
P20245001, P20245002, P20245003, P20245007 |  | s2654.1 | New Carlisle - Maple 138 kV: Rebuild ~0.95 miles of 138 kV single circuit line with 1590 ACSR 45/7 Lapwing to match the NIPSCO owned conductor size. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  |  | EP |  | 0 |  | 1.76 |  | 1.76 | 2021-10-15 |  |  |  | FALSE
P20245004, P20245008 |  | s2654.2 | New Carlisle - Bosserman 138 kV: Rebuild ~0.95 miles of 138 kV double circuit line with 1590 ACSR 45/7 Lapwing to match the NIPSCO owned conductor size and transition fiber installation for NIPSCO connectivity. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  |  | EP |  | 0 |  | 1.86 |  | 1.86 | 2021-10-15 |  |  |  | FALSE
P20245005, P20245006 |  | s2654.3 | New Carlisle – South Bend 138 kV: Remove ~0.86 mile of the existing 138 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  |  | EP |  | 0 |  | 0.17 |  | 0.17 | 2021-10-15 |  |  |  | FALSE
P20245009 |  | s2654.4 | Bosserman 138 kV Station: Relay settings changes. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  |  | EP |  | 0 |  | 0.08 |  | 0.08 | 2021-10-15 |  |  |  | FALSE
P20245010 |  | s2654.5 | New Carlisle 138 kV station: Remote end relaying upgrades and settings changes. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  |  | EP |  | 0 |  | 0.82 |  | 0.82 | 2021-10-15 |  |  |  | FALSE
A19036089, P21010001 |  | s2655.1 | Retire the ~3.65 mile 138kV Lincoln extension and reconnect the existing line between Robison Park and Allen. The extension can be retired due to previous upgrades strengthening the underlying sub-transmission system through connections to other sources and a rebuild of the existing Robison Park-Allen and Lincoln-Robison Park lines which increased the 138 kV capacity. This extension does not impact the larger 138 kV network as Lincoln station will keep three 138 kV sources to serve the Fort Wayne area. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-09-22 |  |  | EP |  | 0 |  | 2.8 |  | 2.8 | 2021-09-17 |  |  |  | FALSE
A19036084 |  | s2655.2 | At Lincoln station, retire 138kV CB “B” and “C”, Replace 138kV CB “I” and relocate 138kV CB “A” to the old CB “C” position. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-09-22 |  |  | EP |  | 0 |  | 2 |  | 2 | 2021-09-17 |  |  |  | FALSE
A19036104, P21022002, P21022003, P21022004 |  | s2656.1 | On the Colony Bay – Illinois Rd 69kV line, rebuild approximately 2.7 miles and re-conductor approximately 3.6 miles with 556.5 ACSR. The 3.6 miles to be reconductored has newer structures that do not need replaced due to various INDOT and Fort Wayne road widening projects that have replaced structures more recently but kept the original conductor in place. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-03-19 |  |  | EP |  | 0 |  | 10.7 |  | 10.7 | 2021-10-15 |  |  |  | FALSE
P21022001, P21022007, P21022009 |  | s2656.2 | Aboite 69kV Switch: Replace Aboite 69kV Switch due to the line structure replacements. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-03-19 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2021-10-15 |  |  |  | FALSE
P19056020, P19056011 |  | s2657.1 | Blossom Trail – Colby 34.5kV: Retire the ~10.2 miles of 34.5kV line between Blossom Trail – Dowagiac Tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 3 |  | 3 | 2021-10-15 |  |  |  | FALSE
P19056005, P19056006, P19056023 |  | s2657.2 | Rudy Tap 34.5kV: Replace the failed Rudy Tap Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2021-10-15 |  |  |  | FALSE
P19056007 |  | s2657.3 | Colby North Ext 138kV: Reterminate the Valley 138kV line into Colby with a .1 mile new extension | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2021-10-15 |  |  |  | FALSE
P19056004, P19056016 |  | s2657.4 | Colby South Ext 138kV: Reterminate the Kenzie Creek 138kV line into Colby with a .25 mile new extension | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2021-10-15 |  |  |  | FALSE
P19056003 |  | s2657.5 | Colby – Rothedew 34.5kV line: Reterminate the Rothedew 34.5kV line into Colby | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2021-10-15 |  |  |  | FALSE
P19056008 |  | s2657.6 | Colby - Dowagiac 34.5kV : Reterminate the Dowagiac 34.5kV feed back into Colby station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 1 |  | 1 | 2021-10-15 |  |  |  | FALSE
P19056014 |  | s2657.7 | Colby – Rudy Tap 34.5kV : Reterminate the Rudy Tap 34.5kV feed back into Colby station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 1 |  | 1 | 2021-10-15 |  |  |  | FALSE
P19056018 |  | s2657.8 | Colby – Kenzie Creek 69kV : Reterminate the Kenzie Creek 69kV feed back into Colby station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2021-10-15 |  |  |  | FALSE
P19056017 |  | s2657.9 | Colby 138kV Switch: Retire the Colby 138kV Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2021-10-15 |  |  |  | FALSE
A19036083, P19056001, P19056002, P19056024 |  | s2657.10 | Colby 138/69/34.5kV: On the existing property, build a new 138kV yard with 4 CB’s built in a ring configuration. Install a new 138/34.5 50MVA XFR with a low side CB protecting the single line exit toward Rudy Tap to replace the source previously served by the retired line to Blossom Trail. Install 3 34.5kV CB’s on a new 34.5kV bus that will be connected to the existing 138/69/34.5kV XFR, and the Rothedew and Dowagiac exits. Install a new 69kV CB toward Kenzie Creek. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 11.9 |  | 11.9 | 2021-10-15 |  |  |  | FALSE
P19056020, P19056011 |  | s2657.11 | Blossom Trail 138/69/34.5kV: Remove CB “M” and reuse it at Colby station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2021-10-15 |  |  |  | FALSE
A19036097, A19036098, A19036099, P21080001 |  | s2658 | New Buffalo – Bridgman 69kV line: Rebuild the 22.1 mile New Buffalo – Bridgman 69kV line with 556.5 ACSR Dove. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-24 |  |  | EP |  | 0 |  | 55.5 |  | 55.5 | 2021-10-15 |  |  |  | FALSE
DP20R09C1 |  | s2663.1 | Extend a 0.37 mile double circuit 69 kV line to the new station location by tapping the existing Hancock-Walnut Ave 69 kV Circuit using 556 ACSR 26/7 overhead conductor | Customer Service |  |  |  | 2025-11-03 |  | 2025-01-16 | EP | IS | 0 | 100 | 2.8 |  | 2.8 | 2021-11-19 | Jonathan Wood/Robert Valerio |  |  | FALSE
DP20R09B0 |  | s2663.2 | Establish new 69 kV station (Winston Avenue) in a straight bus configuration with 2-69 kV circuit breakers, 69/12 kV, 25 MVA transformer with high-side circuit switcher and three 12 kV feeder breakers | Customer Service |  |  |  | 2024-10-14 |  | 2025-01-16 | EP | IS | 0 | 100 | 0 |  | 0 | 2021-11-19 | Jonathan Wood/Robert Valerio |  |  | FALSE
DP20R09B1 |  | s2663.3 | Update relay settings at Walnut Ave and Hancock stations. | Customer Service |  |  |  | 2024-10-25 |  |  | UC |  | 31 |  | 0.03 |  | 0.03 | 2021-11-19 | Jonathan Wood/Robert Valerio |  |  | FALSE
DP20R09B0 |  | s2663.4 | At Winston Ave install a second 69/12 kV, 25 MVA transformer with high-side circuit switcher and 12 kV feeders | Customer Service |  |  |  | 2026-12-01 |  | 2025-01-16 | EP | IS | 0 | 100 | 0 |  | 0 | 2021-11-19 |  |  |  | FALSE
|  | s2663.5 | At Roanoke install a second 138/12 kV Distribution transformer with high-side circuit switcher and 12 kV feeders. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 2 |  | 2 | 2021-11-19 |  |  |  | FALSE
DP20R09B1 |  | s2663.6 | Retire Distribution from Walnut Ave. Station. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2021-11-19 |  |  |  | FALSE
A19036106, P21235001, P21235002 |  | s2664 | Hummel Creek – Marion 34.5 kV: Rebuild ~4.5 miles of 34.5 kV line with the conductor size 556.5 ACSR 26/7 Dove to 69 kV standards. The following cost includes the line rebuild, line removal and ROW. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-15 |  |  | EP |  | 0 |  | 11.3 |  | 11.3 | 2021-11-19 |  |  |  | FALSE
P19273001 |  | s2682.1 | Spy Run-Melita 69kV: Rebuild the Spy Run – McKinley 34.5kV line as the ~2.2 mile Spy Run – Melita 69kV line and retire the remaining 2.8 miles. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-08-01 |  |  | EP |  | 0 |  | 24.8 |  | 24.8 | 2022-01-21 | Katherine Vecchiarelli/Michael Van Schaik |  |  | FALSE
P19273007 |  | s2682.2 | Melita Station: Add a 69kV CB to Melita station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-08-01 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2022-01-21 | Joseph Smith/Michael Van Schaik |  |  | FALSE
A21111072 |  | s2682.3 | Fulton Station: Rebuild the through-path of Fulton 34.5/12kV station at 69kV and replace the transformer with a 69/12kV unit. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  |  | FALSE
P20230005 |  | s2682.4 | Spy Run Station: Replace transformer #3 with a 138/69/34.5kV unit. Move the Fulton exit from 34.5kV to 69kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-04-22 |  |  | UC |  | 31 |  | 2.6 |  | 2.6 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  |  | FALSE
P19273008 |  | s2682.5 | McKinley Station: Retire CB “G” at McKinley station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-05 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  |  | FALSE
P16024031 |  | s2682.6 | Wallen Station: Retire the 34.5kV voltage class equipment at Wallen station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-09-09 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  |  | FALSE
P19153009 |  | s2682.7 | Industrial Park: Retire the entire 34.5kV voltage class, install a new 138/12kV load delivery to replace the 34.5/12kV delivery. Replace 69kV CB “G”, Replace the 138/69kV XFR 1 and add a high side switcher to XFR 1. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 11.1 |  | 11.1 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  |  | FALSE
P19273005 |  | s2682.8 | Wallen-Industrial Park 34.5kV: Retire the ~3.3 mile Wallen – Industrial Park 34.5kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 2.9 |  | 2.9 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  |  | FALSE
P20230006 |  | s2682.9 | Glenbrook Station: Retire Glenbrook 34.5/12kV substation | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-05 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-01-21 | Joseph Smith/Michael Van Schaik |  |  | FALSE
A20045021 |  | s2684 | North Blacksburg Station : Replace existing Transformer #1 with a 130 MVA 138/69-12 kV transformer. Replace existing Transformer #2 with a 25 MVA 138/12 kV transformer and add bus regulators. Add a 69kV circuit breaker on the low side of Transformer #1 | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-21 |  |  | EP |  | 0 |  | 4.06 |  | 4.06 | 2022-01-21 |  |  |  | FALSE
A19036102, P21238003, P21238004, P21238005 |  | s2685.1 | Robison Park – Sowers 138kV line: Rebuild the 13.6 miles of wood construction with double circuit capable 138kV with one side strung. Reconductor 4.3 miles of the steel lattice section with 795 Drake ACSR. This 4.3 mile section is already constructed as double circuit capable. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-05-04 |  |  | EP |  | 0 |  | 42.3 |  | 42.3 | 2022-01-21 |  |  |  | FALSE
P21238001, P21238002 |  | s2685.2 | Replace switches and risers at Grabill switch to accommodate the line rebuild. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-01-22 |  |  | EP |  | 0 |  | 1 |  | 1 | 2022-01-21 |  |  |  | FALSE
A19036075, P21086001, P21086002 |  | s2686 | Kenzie Creek 345/138/69kV station: Replace 138kV CB’s “F”, “F1”, “F2”, “G” and “G1” with 40 kA circuit breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-01-31 |  | 2025-01-16 | EP | IS | 0 | 100 | 1.8 |  | 1.8 | 2022-01-21 |  |  |  | FALSE
DP21A09D0 |  | s2688.1 | Install a new distribution station (“Pumpkin”) adjacent to the 69kV transmission through-path south of Barnesville. Retire Barnesville station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-08-27 |  |  | EP |  | 0 |  | 0.83 |  | 0.83 | 2022-01-21 | David Roudebush/antonio Lampkins |  |  | FALSE
DP21A09C0 |  | s2688.2 | Retire the 0.4-mile 69kV transmission line tap into Barnesville station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-08-28 |  |  | EP |  | 0 |  | 0.46 |  | 0.46 | 2022-01-21 | David Roudebush/antonio Lampkins |  |  | FALSE
DP21A09W0 |  | s2688.3 | Loop the Speidel-Summerfield 69kV transmission line into Pumpkin station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-08-27 |  |  | EP |  | 0 |  | 1.38 |  | 1.38 | 2022-01-21 | David Roudebush/antonio Lampkins |  |  | FALSE
A20705032 |  | s2693.1 | Rebuild approximately 4.5 miles of 46 kV line on the Cabin Creek – London 46 kV circuit (total length approximately 8 miles) in an area where there’s larger than standard ROW requirements due to long spans from ridge-ridge and more angle/dead ends required to mitigate landslide risk in rugged terrain. Long access roads due to terrain | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 17.7 |  | 17.7 | 2022-02-28 |  |  |  | FALSE
P20228007 |  | s2693.2 | Remove/retire existing Cabin Creek – London (4.5 miles). Helicopter removal will be utilized for existing line to avoid avoiding landslide prone areas | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 2.3 |  | 2.3 | 2022-02-28 |  |  |  | FALSE
P20228009 |  | s2693.3 | Retire the existing Hugheston Station | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-02-28 |  |  |  | FALSE
P20228020 |  | s2693.4 | Rebuild London Station in the clear due to space constraints and access concerns. Install four 46 kV circuit breakers in a single bus configuration, DICM and appropriate metering equipment for the adjacent Hydro Plant. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 8.3 |  | 8.3 | 2022-02-28 |  |  |  | FALSE
P20228010 |  | s2693.5 | Rebuild approximately 1 mile of double circuit line from the existing London Hydro Station to the new London Station. Due to terrain dead-end structures will be used to construct this section of line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 5.4 |  | 5.4 | 2022-02-28 |  |  |  | FALSE
P20228012 |  | s2693.6 | Rebuild approximately 1 mile of single circuit line on the Carbondale – London 46 kV to accommodate the new London Station location | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 3.5 |  | 3.5 | 2022-02-28 |  |  |  | FALSE
A20045011 |  | s2694 | Cloverdale station: Replace 345/138 kV Transformer 11A & 11B with new 345/138 kV, 675 MVA Transformer 11 and reconnect to the 138 kV structure via a new 138 kV tie-line with 3 custom single-pole structures outside of the station in order to keep storage/driving space within the station. Install two new 345 kV 5000A 63 kA breakers to connect the new transformer and existing transformer 3 into a string position in the 345 kV yard. Replace all 69 kV hook-stick switches new 2000 A GOAB switches. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-31 |  | 2024-12-19 | EP | IS | 0 | 100 | 12.33 |  | 12.33 | 2022-02-09 |  |  |  | FALSE
P20019001 |  | s2748.1 | Install a new 3-way POP Switch (Boughtonville Sw) and 69 kV metering to address the hard tap to Firelands’ Boughtonville station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  |  | EP |  | 0 |  | 0.75 |  | 0.75 | 2022-03-18 |  |  |  | FALSE
P20019002 |  | s2748.2 | Install a new 3-way POP Switch (Lake Park Sw) and 69 kV metering to address the hard tap to Lake Park Industries. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  |  | EP |  | 0 |  | 0.76 |  | 0.76 | 2022-03-18 |  |  |  | FALSE
P20019003 |  | s2748.3 | Install a new 3-way POP Switch (Greenwich Sw) to address the hard tap to the Village of Greenwich’s Greenwich station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2022-03-18 |  |  |  | FALSE
P20019005 |  | s2748.4 | Remove North Greenwich Switch. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  |  | EP |  | 0 |  | 0.07 |  | 0.07 | 2022-03-18 |  |  |  | FALSE
J20019002 |  | s2748.5 | Construct ~ 10.4 miles of new 69 kV line between South Greenwich and ATSI’s New London delivery point using 556 ACSR conductor to give the existing radial line looped transmission service | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  |  | EP |  | 0 |  | 18 |  | 18 | 2022-03-18 |  |  |  | TRUE
P20019019 |  | s2748.6 | Install a box bay and two new 69 kV 3000A 40kA breaker at South Greenwich to accommodate the new line to New London (ATSI) | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  |  | EP |  | 0 |  | 3 |  | 3 | 2022-03-18 |  |  |  | TRUE
P20019022 |  | s2748.7 | Remove the existing 69kV bypass line at Willard station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  |  | EP |  | 0 |  | 0.32 |  | 0.32 | 2022-03-18 |  |  |  | FALSE
P20233007 |  | s2770.1 | Lazelle 69 kV Station: Replace 69kV circuit breakers 61 and 62 with 3000A 40kA breakers and associated equipment and relaying. | Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.62 |  | 0.62 | 2022-04-22 |  |  |  | FALSE
P20233014 |  | s2770.2 | Sawmill 138kV Station: Replace 69kV circuit breaker B with 3000A 40kA breaker and associated controls | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2022-04-22 |  |  |  | FALSE
P20233015 |  | s2770.3 | Westerville 69kV Station: Replace 69kV circuit breakers 62 and 63 with 3000A 40kA breakers and associated equipment and relaying | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.44 |  | 0.44 | 2022-04-22 |  |  |  | FALSE
P20233016 |  | s2770.4 | Genoa 138kV Station: Replace 69kV circuit breaker 64 with 3000A 40kA breaker | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.28 |  | 0.28 | 2022-04-22 |  |  |  | FALSE
P20233019 |  | s2770.5 | Hyatt Telecom Site: Install Telecom site with CES SFP to communicate with Lazelle station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.04 |  | 0.04 | 2022-04-22 |  |  |  | FALSE
A20705039 |  | s2771.1 | Retire the existing Bradley – Layland 69 kV line (approx. 14.3 miles) T | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 9.7 |  | 9.7 | 2022-04-22 |  |  |  | FALSE
|  | s2771.2 | Construct a new double circuit 138 kV in/out line from the existing Bradley – Grandview 138 kV line (approx. 2.6 miles) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 8.3 |  | 8.3 | 2022-04-22 |  |  |  | FALSE
P20229008 |  | s2771.3 | Prince Station: Retire existing station | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-04-22 |  |  |  | FALSE
P20229003, P20229004 |  | s2771.4 | Chessie Station: Install new 138 kV station including two 138 kV switches, circuit switcher and 138/12 kV 20 MVA XFR | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2022-04-22 |  |  |  | FALSE
P20229006 |  | s2771.5 | Grandview Station: Install a new 138/12 kV transformer to accommodate the retirement of Prince Station | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 2.2 |  | 2.2 | 2022-04-22 |  |  |  | FALSE
P20229005 |  | s2771.6 | Bradley Station: Remove existing 69 kV breaker due to line retirement | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2022-04-22 |  |  |  | FALSE
P20229009 |  | s2771.7 | Layland Station: Remove existing 69 kV breaker due to line retirement | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2022-04-22 |  |  |  | FALSE
A19036079, P20177001, P20177002, P20177003 |  | s2772 | Rebuild the Pettit Ave – Melita 69kV 1.84 mile section on centerline utilizing 556.5 ACSR. Construction includes a high percentage of custom self-supporting running corners and dead ends due to line angles created by route adjustments. Constrained corridors are not suitable for guy wire installation. There are also an increased number of structures per mile due to configuration of existing underbuild and existing distribution service connections to residential and commercial customers along the existing line route. The line also passes through a heavily developed urban area of Fort Wayne, requiring new easements along the route and short span construction which all lead to higher than normal costs. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-13 |  |  | EP |  | 0 |  | 12 |  | 12 | 2022-04-22 |  |  |  | FALSE
P20231008 |  | s2773.1 | East Lima – Columbus Grove Line: Rebuild 9.3 miles of the East Lima - Columbus Grove line between Columbus Grove and structure 38. Construct ~1 mile of greenfield 69 kV line between structure 38 and the existing Bluelick Sw. Rebuild 1.65 miles of the 34.5 kV line section between Bluelick and East Lima to 69 kV to provide looped service to the new 69 kV delivery at Bluelick. Retire 1.7 miles of the Columbus Grove – East Lima line from structure 38 into East Lima. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-08-27 |  |  | EP |  | 0 |  | 25.55 |  | 25.547 | 2022-04-22 |  |  |  | FALSE
P20231017 |  | s2773.2 | Slabtown Switch: Install Slabtown SW with 1200A POP switches. Install Auto-sectionalizing on the through path. Upgrade Bluelick delivery point metering. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-12-14 |  |  | EP |  | 0 |  | 0.89 |  | 0.885 | 2022-04-22 |  |  |  | FALSE
P20231007 |  | s2773.3 | Bluelick Switch: Retire 34.5 kV Bluelick SW | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-09-23 |  |  | EP |  | 0 |  | 0.05 |  | 0.054 | 2022-04-22 |  |  |  | FALSE
P20231019 |  | s2773.4 | Cairo Switch: Replace Cairo switch with 1200A POP switches. Install SCADA control on the through-path | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-08-27 |  |  | EP |  | 0 |  | 0.71 |  | 0.706 | 2022-04-22 |  |  |  | FALSE
P20231005 |  | s2773.5 | East Lima Station: Upgrade telecom equipment at East Lima station | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-11-01 |  |  | EP |  | 0 |  | 0.02 |  | 0.021 | 2022-04-22 |  |  |  | FALSE
P20231020 |  | s2773.6 | Columbus Grove Station: In order to accommodate the line rebuild, work will be performed on the existing Columbus Grove switch. Install a box bay with two 69 kV, 1200A line witch automated MOABs, at Columbus Gove station | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-08-27 |  |  | EP |  | 0 |  | 1.14 |  | 1.141 | 2022-04-22 |  |  |  | FALSE
DP21R01B0 |  | s2774.1 | Construct a greenfield station (Salmon) with a 138/12 kV 25 MVA transformer with high side circuit switcher. There will be two 12 kV feeders from the station. The 138 kV side will be a straight bus with two 138kV circuit breakers. | Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-04-22 |  |  |  | FALSE
DP21R01B2 |  | s2774.2 | Tap the Broadford – Claypool Hill 138kV line and construct an in and out line to the greenfield Salmon station by building 2.3 miles of greenfield double circuit 138kV line. The higher estimated cost is due to environmental surveying and a large amount of new access roads required for this greenfield line that is in hilly terrain | Customer Service |  |  |  | 2026-06-30 |  |  | EP |  | 0 |  | 8.5 |  | 8.5 | 2022-04-22 |  |  |  | FALSE
DP21R01C1 |  | s2774.3 | Build 4.1 miles of 96 ADSS Telecom underbuilt cable to connect Salmon station to the existing fiber network. | Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2022-04-22 |  |  |  | FALSE
P21209009 |  | s2775.1 | Rebuild the existing Belva – Clendenin 46 kV line to 138 kV standards (approximately 27 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-05 |  |  | EP |  | 0 |  | 85.6 |  | 85.6 | 2022-04-22 |  |  |  | FALSE
P21209006 |  | s2775.2 | Belva Station: Replace existing Gr. Sw. MOAB with a new 138 kV 3000 A 40 kA CB. Install a new 138 kV 3000 A 40 kA CB on the Belva – Gilboa 138 kV line at Belva Station. Install 9.6 MVAR cap bank. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-09-01 |  |  | EP |  | 0 |  | 2.9 |  | 2.9 | 2022-04-22 |  |  |  | FALSE
P21209007 |  | s2775.3 | Hartland Station: Replace existing MOABs W and Y with two new switches. Retire/Remove existing circuit switcher AA and cap bank. E | Equipment Material Condition, Performance and Risk |  |  |  | 2026-09-01 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2022-04-22 |  |  |  | FALSE
A19036103, P21296003, P21296004, P21296005 |  | s2776 | Industrial Park – McKinley 138kV line: Rebuild the ~1 mile section that is double circuit with McKinley – Melita 69kV and rebuild the ~0.9 mile section that is double circuit with Melita – Hadley 69kV in place. The remaining ~1.3 miles will be rebuilt as single circuit. All new line conductor will be 795 Drake ACSR. The total rebuild length is 1.9 miles double circuit and 1.3 miles single circuit for a total of 3.2 miles. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-03 |  |  | EP |  | 0 |  | 9.3 |  | 9.3 | 2022-04-22 |  |  |  | FALSE
A19036107, P21282001, P21282002 |  | s2777 | Robison Park – Wallen 69kV line: Reconductor the ~2.96 miles of 300,000 CU with 556.5 ACSR and replace 21 structures outlined in the need with steel monopole structures. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-13 |  |  | EP |  | 0 |  | 6.3 |  | 6.3 | 2022-04-22 |  |  |  | FALSE
P21013006 |  | s2778.1 | Rebuild approximately 4.6 mile of the Newcomerstown- Cambridge 69kV line that wasn’t addressed under b3274 and b3345 utilizing 556 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 8.97 |  | 8.97 | 2022-04-22 |  |  |  | FALSE
P21013010 |  | s2778.2 | Rebuild the 0.6 mile Leatherwood Sw- North Cambridge with double circuit 556 ACSR conductor to provide loop service to North Cambridge station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.45 |  | 1.45 | 2022-04-22 |  |  |  | FALSE
P21013018 |  | s2778.3 | Add line MOABs for each of the double circuit lines coming into North Cambridge station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.28 |  | 0.28 | 2022-04-22 |  |  |  | FALSE
P21013013 |  | s2778.4 | Remove the Leatherwood Switch that currently radially serves North Cambridge station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.08 |  | 0.08 | 2022-04-22 |  |  |  | FALSE
P21013019 |  | s2778.5 | Replace Salt Fork Switch with a new 1200A POP Switch | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.13 |  | 1.13 | 2022-04-22 |  |  |  | FALSE
P21009012 |  | s2779 | Fremont Center: Rebuild the existing 69 kV yard to a breaker and a half arrangement. Install 11 new 3000A 40kA 69kV breakers and relocate one existing breaker into the new strings | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-15 |  |  | EP |  | 0 |  | 10.35 |  | 10.35 | 2022-04-22 |  |  |  | FALSE
P20255004 |  | s2780.1 | Rebuild the 15.7 mile 138kV line between Howard and Chatfield stations with new 1033 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 39.96 |  | 39.96 | 2022-04-22 |  |  |  | FALSE
P20255011 |  | s2780.2 | Rebuild the 6.1 mile 138kV line between Melmore and South Tiffin stations with new 1033 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 14.97 |  | 14.97 | 2022-04-22 |  |  |  | FALSE
P20255014 |  | s2780.3 | Rebuild the 11.7 mile 138kV line between South Tiffin and West End Fostoria stations with new 1033 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 30.19 |  | 30.19 | 2022-04-22 |  |  |  | FALSE
P21088002 |  | s2781.3 | Brie 138kV Station: Establish the greenfield 138kV Brie station. Two full breaker and a half strings and 2 partial strings will be initially installed; total of ten (10) 138 kV breakers. | Customer Service |  |  |  | 2024-09-14 |  |  | UC |  | 75 |  | 11.04 |  | 11.04 | 2022-04-22 | Sydney Hunter/Nathen Roberts |  |  | FALSE
P21088003 |  | s2781.5 | Brie – Customer: Construct approximately 2 miles of two double circuit 138kV tie lines #1-4 to the customer's facility | Customer Service |  |  |  | 2025-02-11 |  | 2025-02-05 | EP | IS | 0 | 100 | 0.11 |  | 4.11 | 2023-08-18 | Sydney Hunter/Nathen Roberts |  |  | FALSE
P21237001 |  | s2784.1 | Merrick Switch – Atwood Switch: Rebuild the existing 8.8 mile 69kV line section between Merrick Switch and Atwood Switch, using 477 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 19.92 |  | 19.92 | 2022-05-19 |  |  |  | FALSE
P21237006 |  | s2784.2 | Zoarville – Merrick Switch: Build 7.0 mile greenfield 69kV line between Merrick Switch and Zoarville, using 477 ACSR conductor | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 16.47 |  | 16.47 | 2022-05-19 |  |  |  | FALSE
P21237002 |  | s2784.3 | Merrick Switch – East Dover: Retire 6.5 miles of 69 kV line between Merrick Switch and East Dover | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 1.84 |  | 1.84 | 2022-05-19 |  |  |  | FALSE
P21237004 |  | s2784.4 | East Dover: Remove 69kV breaker K and associated equipment. Connect the modified Carrollton 69kV circuit to breaker H; upgrade a small amount of risers at East Dover. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 0.34 |  | 0.34 | 2022-05-19 |  |  |  | FALSE
P21237008 |  | s2784.5 | Zoarville: Install 69kV switch and conductor to connect to new T-line entrance. Relay settings updates at Carrollton. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 0.14 |  | 0.14 | 2022-05-19 |  |  |  | FALSE
P21029001 |  | s2785.1 | Invision Switch: Install a new switch on the Ebersole – Findlay center 138 kV line to serve the new Buckeye Co-Op Cass Substation. | Customer Service |  |  |  | 2026-02-20 |  |  | UC |  | 50 |  | 1.49 |  | 1.49 | 2022-05-19 |  |  |  | FALSE
P21029006 |  | s2785.2 | Invision – Cass: Install approximately 0.1 miles of new 138 kV line from Invision Switch to the Buckeye Co-op Cass Substation. | Customer Service |  |  |  | 2026-02-20 |  |  | UC |  | 50 |  | 0.6 |  | 0.595 | 2022-05-19 |  |  |  | FALSE
P22024006 |  | s2787.1 | RV Capital 138 kV - Install a new 138kV straight bus with a (2) 138kV MOAB switches, fiber and relaying. | Customer Service |  |  |  | 2025-01-03 |  |  | EP |  | 0 |  | 1.96 |  | 1.96 | 2022-04-22 | Matthew Van Volkenburg/Joshua Smith |  |  | FALSE
DP21C23D2 |  | s2789.1 | Scherers Switch 138kV: Install a new 2000 A three-way Phase Over Phase switch with SCADA automation on the Huntley – Greif through path and install a bypass for maintenance. | Customer Service |  |  |  | 2024-11-08 |  | 2024-11-15 | UC | IS | 75 | 100 | 0.8 |  | 0.8 | 2022-04-22 |  |  |  | FALSE
DP21C23D4 |  | s2789.2 | Greif – Huntley 138kV line: Tap the existing Greif-Huntley 138kV circuit by installing structures to carry the 69 kV underbuild Lazelle-Busch circuit and maintain separation from the new Scherers Switch as well as install dead end poles and centerline poles on each direction of the new switch | Customer Service |  |  |  | 2024-11-03 |  | 2024-11-15 | UC | IS | 75 | 100 | 1.11 |  | 1.113 | 2022-04-22 |  |  |  | FALSE
DP21C23C0 |  | s2789.3 | Cologix Extension 138kV: Construct ~0.24 miles of single circuit 138kV radial transmission line from Scherers Switch to the new Cologix Customer Station. | Customer Service |  |  |  | 2024-11-08 |  | 2024-11-15 | UC | IS | 75 | 100 | 0.8 |  | 0.795 | 2022-04-22 |  |  |  | FALSE
P20022001 |  | s2791.1 | West Watertown Station, 138 kV: Construct a greenfield 138/69 kV West Watertown station off the existing Corner – Wolf Creek 138 kV circuit. Install four-138 kV 3000 A 40 kA breakers configured in a ring arrangement. Install 90 MVA 138/69/13.09 kV transformer along with a 3000A 40 kA 69 kV low side breaker towards WEC’s Bartlett delivery. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 8.8 |  | 8.8 | 2022-06-15 |  |  |  | FALSE
P20022008 |  | s2791.2 | Wolf Creek – Corner 138 kV Line cut-in: Cut-in on the line to install the new West Watertown station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.55 |  | 0.55 | 2022-06-15 |  |  |  | FALSE
P20022011 |  | s2791.3 | West Watertown – Watertown (WEC) 138 kV circuit: Construct approximately 4.3 miles of single circuit 138 kV line between the newly proposed West Watertown station and WEC’s new 138 kV delivery at Watertown. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 9.32 |  | 9.32 | 2022-06-15 |  |  |  | FALSE
P20022013 |  | s2791.4 | West Watertown – Patten Mills 69 kV circuit : Construct approximately 5.8 miles of single circuit 69 kV line between the newly proposed West Watertown station and a proposed phase over phase switch (Patten Mills Switch) near WEC’s delivery at Bartlett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 11.81 |  | 11.81 | 2022-06-15 |  |  |  | FALSE
P20022002 |  | s2791.5 | Patten Mills Switch, 69 kV: Install a new 69 kV 2000A phase over phase (Patten Mills switch) to serve the Bartlett delivery point. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2022-06-15 |  |  |  | FALSE
P20022014 |  | s2791.6 | South Stockport - Washington Co-op 69 kV Line cut-in : Cut-in on the line to install the new Patten Mills Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.65 |  | 0.65 | 2022-06-15 |  |  |  | FALSE
P20022016 |  | s2791.7 | Muskingum River - South Rokeby 69 kV Line Removal : Retire ~9 miles of existing 69 kV line between Grace and Muskingum River stations. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 4.1 |  | 4.1 | 2022-06-15 |  |  |  | FALSE
P20022005 |  | s2791.8 | Muskingum River Removals: At Muskingum River 138 kV yard, retire the 138/69 kV XF #C, CB-HM & HW. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.63 |  | 0.63 | 2022-06-15 |  |  |  | FALSE
P20022019 |  | s2791.9 | Grace Station, 69 kV: Retire Grace - Muskingum River circuit, upgrade protection and fiber work at Grace Station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.91 |  | 0.91 | 2022-06-15 |  |  |  | FALSE
P20022017 |  | s2791.10 | Grace – Watertown Fiber: Install fiber between Grace and Watertown stations. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.55 |  | 0.55 | 2022-06-15 |  |  |  | FALSE
P20022007 |  | s2791.11 | Wolf Creek & Corner Stations Protection upgrades: Remote end protection upgrade | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.65 |  | 0.65 | 2022-06-15 |  |  |  | FALSE
P20022003 |  | s2791.12 | Watertown (WEC) Metering: Install 12 kV revenue metering at WEC’s new Watertown station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  |  | EP |  | 0 |  | 0.03 |  | 0.026 | 2022-06-15 |  |  |  | FALSE
P21710001 |  | s2792.1 | Eliminate the Moreland area 69kV hard tap and install a new 3-way, motor-operated switch with SCADA functionality (“Rufener Switch”). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-07-25 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2022-06-15 | Parker Joyner/? |  |  | FALSE
P21710003 |  | s2792.2 | Modify the Beartown-Moreland 69kV through-path T-line and ROW, in order to install the new switch structure. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-07-25 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2022-06-15 |  |  |  | FALSE
P21710005 |  | s2792.3 | Modify the Rufener – Co-op 69kV radial T-line and ROW, in order to install the new switch structure. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-07-25 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2022-06-15 |  |  |  | FALSE
P20168022 |  | s2793.1 | West Van Wert – Ohio City: Rebuild the 8.9 mile West Van Wert – Ohio City 34.5 kV circuit to operate at 69 kV utilizing 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 12.27 |  | 12.271 | 2022-06-15 |  |  |  | FALSE
P20168012 |  | s2793.2 | West Van Wert 69kV: In order to address the three terminal point created by closing in the interconnection at Rockford and address existing dissimilar zones of protection, 4 new 3000A, 40kA breakers will be installed at West Van Wert station in a ring configuration. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | 2024-12-10 | EP | IS | 0 | 100 | 5.5 |  | 5.503 | 2022-06-15 |  |  |  | FALSE
P20168023 |  | s2793.3 | Haviland – West Van Wert: Relocate Haviland – West Van Wert 69kV to accommodate work at West Van Wert station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.04 |  | 1.035 | 2022-06-15 |  |  |  | FALSE
P20168023 |  | s2793.4 | West Van Wert – South Van Wert: Relocate West Van Wert –South Van Wert to accommodate work at West Van Wert station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.17 |  | 1.174 | 2022-06-15 |  |  |  | FALSE
P20168020 |  | s2793.5 | Roller Creek 69kV: Install new 69/12 kV Roller Creek station to replace Ohio City 34.5/12 kV station. Install a box bay with a 1200A 69kV auto-sectionalizing MOAB and a 3000A,40kA 69kV breaker on the West Van Wert- Rockford through path. Install 69kV metering | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.64 |  | 1.641 | 2022-06-15 |  |  |  | FALSE
P20168011 |  | s2793.6 | West Ohio City Switch 34kV: Retire Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.04 |  | 0.039 | 2022-06-15 |  |  |  | FALSE
P20168010 |  | s2793.7 | Southwest Van Wert Switch 34kV: Retire Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | 2025-06-09 | EP | IS | 0 | 100 | 0.09 |  | 0.088 | 2022-06-15 |  |  |  | FALSE
P21304001 |  | s2794.1 | Mount Perry Switch, 138 kV: Install a new 3-way POP MOAB switch (Mount Perry Switch) tapping the Crooksville – North Newark 138kV circuit to SCP’s new Mount Perry Station. | Customer Service |  |  |  | 2024-07-19 |  | 2025-03-12 | EP | IS | 0 | 100 | 0.97 |  | 0.966 | 2022-06-15 |  |  |  | FALSE
P21304008 |  | s2794.2 | Mount Perry Extension, 138 kV: Construct approximately 0.08 miles of greenfield 138kV transmission line from the greenfield 3-way POP MOAB switch to SCP’s new Mount Perry Station. | Customer Service |  |  |  | 2024-07-19 |  |  | EP |  | 0 |  | 0.74 |  | 0.737 | 2022-06-15 |  |  |  | FALSE
P21304002 |  | s2794.3 | Mount Perry Meter, 12 kV: Install 12 kV metering at SCP’s new Mount Perry Station. | Customer Service |  |  |  | 2024-07-19 |  |  | EP |  | 0 |  | 0.02 |  | 0.023 | 2022-06-15 |  |  |  | FALSE
P21304006 |  | s2794.4 | Crooksville – North Newark 138 kV line: Perform work to cut-in the Crooksville – North Newark 138 kV line to install the new POP MOAB switch. | Customer Service |  |  |  | 2024-07-19 |  | 2025-03-12 | EP | IS | 0 | 100 | 0.16 |  | 0.162 | 2022-06-15 |  |  |  | FALSE
P21304004 |  | s2794.5 | Crooksville Protection upgrades: Remote end protection upgrade | Customer Service |  |  |  | 2024-07-19 |  |  | EP |  | 0 |  | 0.55 |  | 0.551 | 2022-06-15 |  |  |  | FALSE
P21075001 |  | s2795.1 | Rebuild approximately 4 miles of line from Layland – Mollys Creek (Str. 1183-229) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  |  | EP |  | 0 |  | 13.8 |  | 13.8 | 2022-06-15 |  |  |  | FALSE
P21075012 |  | s2795.2 | Install a new 138 kV PoP switch on the Bradley – Mollys Creek 138 kV line and associated line work on the existing Bradley – Mollys Creek 138 kV line to accommodate switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  |  | EP |  | 0 |  | 1.9 |  | 1.9 | 2022-06-15 |  |  |  | FALSE
P21075009 |  | s2795.3 | Construct a new 138 kV extension from the new 138 kV PoP Switch to the existing Claremont Station (to be renamed Dun Glen) approximately 0.6 mi | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  |  | EP |  | 0 |  | 2 |  | 2 | 2022-06-15 |  |  |  | FALSE
P21075013 |  | s2795.4 | Convert existing Claremont Station from 69 kV to 138 kV. Station to be renamed Dun Glen. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-06-15 |  |  |  | FALSE
A20705041 |  | s2795.5 | Retire existing Claremont – Mollys Creek 69 kV line (approximately 3.1 miles) Retire existing Thurmond S.S. – Brooklyn S.S. 69 kV line (approx. 3.2 miles) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  |  | EP |  | 0 |  | 7.6 |  | 7.6 | 2022-06-15 |  |  |  | FALSE
P21075008 |  | s2795.6 | Install two new 138 kV breakers at Mollys Creek Station | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2022-06-15 |  |  |  | FALSE
A19036105, P21236012, P21236013, P21236024 |  | s2796.1 | Derby – Hickory Creek 69kV Line:Rebuild the remaining ~6.2 miles of the Derby – Hickory Creek 69kV line utilizing 795 ACSR which will match the ~2.5 miles built in 2013 | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 14.7 |  | 14.7 | 2022-06-15 |  |  |  | FALSE
A19036109 |  | s2796.2 | Derby – Hickory Creek 34.5kV Line: Retire the ~6.16 mile Derby – Hickory Creek 34.5kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2022-06-15 |  |  |  | FALSE
A19036111 |  | s2796.3 | Bendix Lakeshore 34.5kV Tap: Retire the ~1.73 mile Bendix Lakeshore 34.5kV Tap | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2022-06-15 |  |  |  | FALSE
P21236006, P21236020 |  | s2796.4 | Hawthorne SS 69kV /Bendix Sw 34.5kV: Remove the switch from Bendix Sw and re-use it at Hawthorne SS | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2022-06-15 |  |  |  | FALSE
P21236004, P21236005 |  | s2796.5 | Stevensville 69kV: Rework the through-path to accommodate the new line entrances. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2022-06-15 |  |  |  | FALSE
P21236001, P21236002, P21236003 |  | s2796.6 | Trafalgar 69/34kV: Install Trafalgar station to serve the Bendix 34.5kV customer. This station will include a new 69kV switcher and a new 69/34.5kV XFR. Two CB’s will be reused from Derby and Hickory Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 4.7 |  | 4.7 | 2022-06-15 |  |  |  | FALSE
P21236008 |  | s2796.7 | Scottdale 69kV: Re-energize to 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-06-15 |  |  |  | FALSE
P21236019 |  | s2796.8 | Derby 138/69/34.5kV: Retire the 34.5kV voltage class | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2022-06-15 |  |  |  | FALSE
P21236016 |  | s2796.9 | Boxer – Blossom Trail 34.5: Re-energize at 34.5kV | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2022-06-15 |  |  |  | FALSE
P21236017 |  | s2796.10 | Boxer – Hickory Cr 69kV: Re-energize at 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2022-06-15 |  |  |  | FALSE
P21236018 |  | s2796.11 | Trafalgar – Bendix 34.5kV: Build a 0.15 mile radial line from Trafalgar to Bendix Lakeshore | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2022-06-15 |  |  |  | FALSE
A19036113, P21728001, P21728002, P21728008 |  | s2797.1 | Pendleton – Makahoy 138 kV: Rebuild ~15 miles of 138 kV line with the conductor size 795 ACSR. The following cost includes the line rebuild, line removal and ROW. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-04-09 |  |  | EP |  | 0 |  | 27.2 |  | 27.2 | 2022-06-15 |  |  |  | FALSE
P21728003, P21728004 |  | s2797.2 | Pendelton: Replace the Pendleton 138/34.5 kV transformer with a 138/34.5 kV 75 MVA transformer. The following cost includes the transformer install and removal. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-28 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2022-06-15 |  |  |  | FALSE
P20241001, P20241002, P20241003 |  | s2798 | McGalliard Road replace 34.5 kV Moab switches “A” and “B” with 2000 A switches and install a 2000 A bus tie switch for operational and transformer maintenance flexibility | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-14 |  | 2024-11-07 | EP | IS | 0 | 100 | 0.4 |  | 0.4 | 2022-06-15 |  |  |  | FALSE
P20269005 |  | s2801.1 | Lockwood Rd 138kV:Retire the existing box bay and breaker bypass switch. Install two 138 kV 40 kA breakers in coordination with an active IPP AF1-063 project that will be installing an additional two breakers in a ring bus arrangement at the station. Install a DICM. Install a new 23MVAR capacitor bank with breaker. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-11-15 |  |  | EP |  | 0 |  | 3.71 |  | 3.713 | 2022-07-22 | Aaron Fahey/Jerod Marker |  |  | FALSE
P20269014 |  | s2801.2 | Sowers – Lockwood Rd – Richlands 138 kV: Relocate Lockwood Road – Sowers and Lockwood Road – Richland lines line to accommodate work at Lockwood Road station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-11-15 |  |  | EP |  | 0 |  | 1.18 |  | 1.178 | 2022-07-22 | Karmyn Wilford/Jerod Marker |  |  | FALSE
P20269012 |  | s2801.3 | Lockwood Rd – City of Bryan 138 kV: Relocate Lockwood Road- City of Bryan line to accommodate work at Lockwood Road station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-11-15 |  |  | EP |  | 0 |  | 0.69 |  | 0.693 | 2022-07-22 | Aaron Fahey/Jerod Marker |  |  | FALSE
P21309001 |  | s2802.1 | Crooksville Station, 69 kV: Replace 69 kV oil filled FK type breaker CB-W with a 3000A, 40 kA breaker . | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  |  | EP |  | 0 |  | 0.67 |  | 0.67 | 2022-07-22 |  |  |  | FALSE
P21309002 |  | s2802.2 | South Fultonham, 69 kV: Retire CB-B. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  |  | EP |  | 0 |  | 0.09 |  | 0.09 | 2022-07-22 |  |  |  | FALSE
P21309003 |  | s2802.3 | Saltillo Switch, 69 kV: Retire Saltillo Switch | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  |  | EP |  | 0 |  | 0.05 |  | 0.05 | 2022-07-22 |  |  |  | FALSE
P21309005 |  | s2802.4 | Crooksville – South Fultonham 69 kV line: Rebuild approximately 7.4 miles of single circuit 69 kV line between the Crooksville and South Fultonham stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  |  | EP |  | 0 |  | 12.47 |  | 12.47 | 2022-07-22 |  |  |  | FALSE
P21309007 |  | s2802.5 | Crooksville – Somerset 69 kV line: Rebuild approximately 8.8 miles of single circuit and 1.6 miles of double circuit 69 kV line between the Crooksville and Somerset stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  |  | EP |  | 0 |  | 19.92 |  | 19.92 | 2022-07-22 |  |  |  | FALSE
P21309009 |  | s2802.6 | South Fultonham – Mount Sterling 69 kV line: Rebuild approximately 7.2 miles of single circuit 69 kV line between the South Fultonham and Mount Sterling stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  |  | EP |  | 0 |  | 13.88 |  | 13.88 | 2022-07-22 |  |  |  | FALSE
P21309013 |  | s2802.7 | South Fultonham – Saltillo 69 kV line: Retire approximately 5.9 miles of single circuit 69 kV line between the South Fultonham station and Saltillo Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  |  | EP |  | 0 |  | 3.22 |  | 3.22 | 2022-07-22 |  |  |  | FALSE
P21761004 |  | s2807.2 | Modify AEP’s proposed Alpine 69 kV ring bus station (s2534.8) by adding an additional 69 kV circuit position to Brewster. Install one (1) 69 kV circuit breaker, protective relaying, and tie-line metering. Construct a 0.1 mile segment of 69 kV transmission line using 795 ACSR 26/7 conductor leaving Alpine station to connect to AMPT’s transmission line toward Brewster. | Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.81 |  | 1.81 | 2022-08-19 |  |  |  | TRUE
P22026001, P22026002 |  | s2810 | Replace 138kV circuit breakers A, B, and C with 3000A 40kA breakers at Edison station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  |  | EP |  | 0 |  | 1.18 |  | 1.18 | 2022-08-19 |  |  |  | FALSE
P20896004 |  | s2811 | Fremont: Install a new 69 kV 3000A 40kA breaker to replace breaker C and associated terminal equipment at Fremont on the line towards the City of Clyde. Install a new 138kV 1200A MOAB switch to replace MOAB W toward West Fremont. Install new DICM. Station will need to be expanded to accomplish work. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 3.48 |  | 3.48 | 2022-08-19 |  |  |  | FALSE
P21273003 |  | s2812.1 | Fostoria - East Lima 138: The 41.3 mile long line will be rebuilt using double circuit 795 ACSR Drake conductor. OPGW shield wire will be installed. Approximately one mile of line is being considered for greenfield construction to avoid encroachments and ROW challenges. The Boutwell, Flag City and Ebersole stations were installed recently, these line cut-ins will not be rebuilt. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-09-15 |  |  | EP |  | 0 |  | 95.9 |  | 95.9 | 2022-08-19 |  |  |  | FALSE
P21273031 |  | s2812.2 | North Findlay - N Main & North Findlay - Findlay 69kV lines: The North Findlay - N Main and North Findlay - Findlay 69kV lines will be modified for the Fostoria - East Lima 138kV line crossing | Equipment Material Condition, Performance and Risk |  |  |  | 2026-09-15 |  |  | EP |  | 0 |  | 0.08 |  | 0.08 | 2022-08-19 |  |  |  | FALSE
P21753002 |  | s2813.1 | At Dewey substation: Replace 138kV CB B towards Thelma with new 138kV 40kA circuit breaker. Provide new DICM with new relays for all equipment at station so that existing control house can be removed. Upgrade station service. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 2.4 |  | 2.4 | 2022-08-19 |  |  |  | FALSE
P21753006 |  | s2813.2 | At Dewey substation: Provide Transition fiber via underground from the existing Control House to the new DICM at Dewey Station. Retire existing fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 0.18 |  | 0.18 | 2022-08-19 |  |  |  | FALSE
P21753004 |  | s2813.3 | At Thelma substation, Remote end relaying to replace line protection for Breaker A towards (Dewey) to match upgrade at Dewey Station. Provide MOS on existing 138kV HS of transformer XF #1 & #3 to provide additional control to stability system | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2022-08-19 |  |  |  | FALSE
A20705082 |  | s2814.1 | Bellefonte: Replace XFR #2 with a 200MVA Auto unit and retire XFR #1 & #5. The U/G feeder for XFR #3 69kV riser is getting reconductored under B3349. Reconductor sections of 138kV Bus #1 and 138kV Bus #2. Replace remaining oil PTs connected to Bus #1 and Bus #2. Upgrade Primary and back up station service. Replace 69kV bus tie breaker H. Replace the hook stick disconnects switches for the tie breaker H and 69kV tie breaker location will be relocated one bay south of the existing location and 69kV buses will be reconfigured. Replace the hook stick disconnects switches for Raceland breaker D. Relocate the Raceland feeder to bus #1 after extending the 69kV bus #1. The cap bank switcher/moab Mark 5 combo unit will get replaced with 69kV breaker and set of breaker disconnects and relocated to bus #1. 69kV breaker is needed instead of circuit switcher due to the high fault current. Relocate the cap bank to bus #1 after extending the 69kV bus #1. 69kV Air Products line MOABs will be replaced with 2000A SW. Replace hook-stick switches for Oil CB – AB, JJ, I, G, Z, T and C. These Breakers are replaced as part of B3350. Install 16'x48' DICM for 69kV Yard and a 16'x48' DICM for the 138kV Yard. Replace cable trench, single phase AC system & cable work, entire fence replacement and ground grid extension for 100'X10' expansion toward the Northwest of the 69kV yard. Both 138kV and 69kV control house will be retired. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 12.59 |  | 12.59 | 2022-08-19 |  |  |  | FALSE
A20705083 |  | s2814.2 | The customer served out of 34.5 kV Yard has plans for demolition of their facilities. Retire entire 34kV Yard, contingent on the timing of the customer being removed from service. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 2.67 |  | 2.67 | 2022-08-19 |  |  |  | FALSE
P21720006 |  | s2814.3 | Retirement of the Bellefonte 34.5kV Bus Tie Line that connects the Bellefonte 138kV Station to the Bellefonte 34kV Station. This removal involves removing 3- Double Circuit Lattice Towers, 1-Triple Circuit Lattice Towers, and 1 Single Wood Pole Structure. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 0.46 |  | 0.46 | 2022-08-19 |  |  |  | FALSE
P21720008 |  | s2814.4 | Retire the existing Bellefonte – Armco 34.5kV operated line. The major removal work involves removing 4 lattice steel towers, 1 H-Frame wood structure, and 2 single wood poles. The line being removed is approximately 0.55 miles long. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | 2025-06-19 | EP | IS | 0 | 100 | 1 |  | 1 | 2022-08-19 |  |  |  | FALSE
P21720007 |  | s2814.5 | Remote end relaying at Raceland substation to install 2 new CCVTs on a custom two-phase single column stand for the Bellefonte 69kV line exit. The existing CCVT mounted on a single phase CCVT stand will be reused and will remain as it is. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 0.37 |  | 0.37 | 2022-08-19 |  |  |  | FALSE
A20705082 |  | s2814.6 | Provide 0.2 miles of fiber from Distribution structures outside the station to the new DICMs. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  |  | EP |  | 0 |  | 0.49 |  | 0.49 | 2022-08-19 |  |  |  | FALSE
P21205002 |  | s2815.1 | At Hatfield Substation, expand the substation yard. Relocate 138/69/46kV XF#1. Replace 138/69/46kV XF#1 Bushings, 138kV 3 phase Bus CCVTs, MOAB X1 and GND Switch Z1 with a new 138kV Circuit Switcher. Replace 138KV Sprigg Line metering, Line Switch "11" with a 138kV Circuit Breaker. Replace and relocate 69kV CB-B to standard Bay position. Replace 69KV CB-A and add 3 phase CCVTs to John's Creek 69kV line. Add 138kV Backup and 69kV Primary Station Service transformers and Station Service. Expand yard and install a 16' X 27' base DICM. Remove 111MVA 46/7.2KV Transformer #2 and associated equipment and 7.2KV 3 phase station service. Remove the control building. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-08-01 |  |  | EP |  | 0 |  | 4.95 |  | 4.95 | 2022-08-19 |  |  |  | FALSE
P21205003 |  | s2815.2 | On the Leslie No.1 – Hatfield 69kV circuit, remove existing guyed dead-end structure K357-29 and install a new single pole, single circuit, custom dead-end to remove the guy wires conflicting with station footprint plans. The existing guy anchors would conflict with station expansion plans, and it is not feasible to span guy over top of proposed control house as the anchors would land in the proposed station drive path. The proposed custom dead-end structure will be placed 20' downhill from existing structure K357-29. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-30 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2022-08-19 |  |  |  | FALSE
DP21H07B1 |  | s2816.1 | Construct a new greenfield station (Holden) with a 138/12 kV 25 MVA transformer and high side circuit switcher. There will be two 12 kV feeders from the station. The 138 kV side will be a straight bus with one 138kV circuit breaker facing Ragland and one 138kV MOAB switch facing Tin Branch. The intent of the greenfield station is to support the business ready site and the 138kV circuit breaker will provide added protection for sensitive industrial customers. The existing Pine Creek station will be retired. | Customer Service |  |  |  | 2026-10-06 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-08-19 |  |  |  | FALSE
DP21H07C0 |  | s2816.2 | Tap the Logan – Sprigg #2 138kV line and build 3.5 miles of greenfield double circuit 138kV line to serve Holden station. The higher estimated cost is due to a large amount of new access roads and environmental studies that are required for this greenfield line that will be built through mountainous terrain. | Customer Service |  |  |  | 2026-10-06 |  |  | EP |  | 0 |  | 12.18 |  | 12.18 | 2022-08-19 |  |  |  | FALSE
DP21H07C4 |  | s2816.3 | Build 0.6 miles of 96 ADSS Telecom underbuilt cable to connect Holden station to the existing fiber network. | Customer Service |  |  |  | 2026-10-06 |  |  | EP |  | 0 |  | 0.18 |  | 0.18 | 2022-08-19 |  |  |  | FALSE
DP21H07C3 |  | s2816.4 | Remove 1.85 mile long Pine Creek 138kV Tap | Customer Service |  |  |  | 2026-10-06 |  |  | EP |  | 0 |  | 1.74 |  | 1.74 | 2022-08-19 |  |  |  | FALSE
P21574006 |  | s2817.1 | Rebuild the Midway – South Christiansburg 69kV line from Midway station to Str. 466-9 (0.45 miles). Rebuild the Midway – South Christiansburg 69kV line from Str. 466-28B to Str. 466-98 (3.8 miles). At Str. 466-98 build new 69kV line to the existing Tech Drive station (0.35 miles). The cost per mile is due to the need for matted access roads to minimize property damage in the urban environment. 50 permanent encroachments have been identified within the existing ROW and require a greater number of line structures than normal to reroute the line. Also, due to numerous encroachments on the existing centerline, the rebuild will consist of 1.8 miles rebuilt on existing centerline and 2.8 miles near centerline or greenfield. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 21.33 |  | 21.33 | 2022-08-19 |  |  |  | FALSE
P21574010 |  | s2817.2 | Remove the Midway – South Christiansburg 69kV circuit from Midway station to Str. 466-9 (0.45 miles). Remove the Midway – South Christiansburg 69kV circuit from Str. 466-28B to Str. 466-98 (3.4 miles). Retire the Midway – South Christiansburg 69kV circuit from South Christiansburg station to Str. 466-98 (0.7 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 2.7 |  | 2.7 | 2022-08-19 |  |  |  | FALSE
A20045072 |  | s2817.3 | At South Christiansburg station, remove the existing 138/69kV transformer and 69kV circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 1.29 |  | 1.29 | 2022-08-19 |  |  |  | FALSE
P21574009 |  | s2817.4 | Build 4 fiber station transitions using OPGW at Midway, Hans Meadow, Tech Drive and South Christiansburg. Retire 4.3 miles of ADSS fiber currently on the Midway – South Christiansburg 69kV circuit. Build 4.6 miles of OPGW on the new Midway - Tech Drive 69kV Line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 1.03 |  | 1.03 | 2022-08-19 |  |  |  | FALSE
P21574001 |  | s2817.5 | At Hans Meadow station, replace the MOAB switch facing Cambria station with a 69kV circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-08-19 |  |  |  | FALSE
P21574002 |  | s2817.6 | At Cambria station, replace existing 69kV line CCVTs, bus conductors, and pass-through riser connectors on both line exits to match the 69kV line capacity. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-08-19 |  |  |  | FALSE
P21574003 |  | s2817.7 | At Midway station, replace existing risers to support the 69kV line rebuild. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-08-19 |  |  |  | FALSE
P21574004 |  | s2817.8 | At Tech Drive station, replace the manual switch facing South Christiansburg station with a 138kV circuit breaker and remove the 138kV bus tie switch. Install a 138kV circuit switcher and a 90 MVA 138/69 kV transformer. Add a 69kV circuit breaker to the 69kV side of the transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-08-19 |  |  |  | FALSE
P22725002 |  | s2818.1 | Add two additional 138kV circuit breakers to the already proposed and approved Tin Branch station (b3348), transforming the designed station from a 138kV two-breaker straight station to a four-breaker ring bus station. | Operational Flexibility and Efficiency |  |  |  | 2027-03-01 |  |  | EP |  | 0 |  | 1.9 |  | 1.9 | 2022-08-19 |  |  |  | FALSE
P22725012 |  | s2818.2 | Disconnect the Chauncey hard tap from the Logan – Sprigg circuit and build 1.5 miles of greenfield 138kV line to connect the Chauncey 138kV Tap into the new Tin Branch station. The higher estimated cost is due to the difficult mountainous terrain, expensive access roads and required environmental studies. | Operational Flexibility and Efficiency |  |  |  | 2027-03-01 |  |  | EP |  | 0 |  | 5.6 |  | 5.6 | 2022-08-19 |  |  |  | FALSE
P19302001 |  | s2819.1 | Rebuild existing Apple Grove – Point Pleasant 69 kV line to 138 kV standards. (approx. 17.3 miles) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-04-01 |  |  | EP |  | 0 |  | 50.3 |  | 50.3 | 2022-09-16 |  |  |  | FALSE
P19302006 |  | s2819.2 | Apple Grove Station: Replace existing 69 kV CB-L with a new 69 kV 3000 A 40 kA CB. Replace existing 138/69 kV XFR #1 with a new 138/69 kV 90 MVA XFR and install new high side circuit switcher. Add 138 kV CB on 138 kV bus increasing sectionalizing, by separating existing customer facilities from AEP facilities. Upgrade metering at station. Install new DICM. Replace existing 69/12 kV XFR #2 with a new 138/12 kV XFR. E | Equipment Material Condition, Performance and Risk |  |  |  | 2025-04-01 |  |  | EP |  | 0 |  | 6.7 |  | 6.7 | 2022-09-16 |  |  |  | FALSE
P21572003 |  | s2820.1 | Rebuild the “Philo-Torrey” 138kV transmission line between West Dover and South Canton stations (18.0 miles). The circuit affected is South Canton-West Dover 138kV. Remove the existing lattice towers and supplement the right-of-way as needed. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 46.74 |  | 46.74 | 2022-09-16 |  |  |  | FALSE
P21572007 |  | s2820.2 | Rebuild the “Philo-Canton” 138kV transmission line between North Intertie and South Canton (14.6 miles). The circuit affected is North Intertie-South Canton 138kV. Remove the existing lattice towers and supplemental the right-of-way as needed. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 42.84 |  | 42.84 | 2022-09-16 |  |  |  | FALSE
A19036082, P21730001, P21730002, P21730003 |  | s2821 | Kalamazoo – Vicksburg 69kV line: Rebuild the 4.72 Kalamazoo – Vicksburg #1 69kV line with 336 30/7 ACSR Oriole and eliminate line crossings with Kalamazoo – Vicksburg #2 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-11-02 |  |  | EP |  | 0 |  | 8.45 |  | 8.45 | 2022-09-16 |  |  |  | FALSE
P21558002 |  | s2822.1 | Rebuild Gambrinus station as Nolan station approximately 0.2 miles away as a 4-breaker 69kV ring bus. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 7.07 |  | 7.07 | 2022-09-16 |  |  |  | FALSE
P21558001 |  | s2822.2 | Retire Gambrinus station and remove all equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 1.04 |  | 1.04 | 2022-09-16 |  |  |  | FALSE
P21558006 |  | s2822.3 | Extend the Gambrinus-Reedurban and Gambrinus-Torrey 69kV transmission lines 0.2 mile northward, to connect to Nolan station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 1.36 |  | 1.36 | 2022-09-16 |  |  |  | FALSE
P21558012 |  | s2822.4 | From Nolan station, construct a span of 69kV transmission line and a structure, for each of the two feeds to the customer. This will connect to the customer’s 69kV loop. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 0.67 |  | 0.67 | 2022-09-16 |  |  |  | FALSE
P21558009 |  | s2822.5 | At the 69kV remote-end of Torrey, upgrade line relays to coordinate with Nolan station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 0.47 |  | 0.47 | 2022-09-16 |  |  |  | FALSE
P21558008 |  | s2822.6 | At the 69kV remote-end of Reedurban, upgrade line relays to coordinate with Nolan and also replace the 69kV oil-filled breaker “R”. Convert the 69kV pilot wire system to fiber. Eliminate the 138kV 3-terminal configuration by installing 2- 138kV breakers on the incoming 138kV circuits. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 3.61 |  | 3.61 | 2022-09-16 |  |  |  | FALSE
P21558011 |  | s2822.7 | At Reedurban station, reconfigure the South Canton-Reedurban-Miles Avenue 138kV transmission line going into the station, to connect to the new breakers and bus. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  |  | EP |  | 0 |  | 0.66 |  | 0.66 | 2022-09-16 |  |  |  | FALSE
P21558021 |  | s2822.8 | At Reedurban station, replace and relocate a structure on the Nolan 69kV transmission line, to accommodate the station improvements and distribution scope. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  | 2024-08-05 | EP | IS | 0 | 100 | 0.33 |  | 0.33 | 2022-09-16 |  |  |  | FALSE
P22038005 |  | s2827.2 | At AEP’s East Leipsic station extend the 69kV bus and install a new 69kV breaker. Install 69kV To/To Metering. The station will need expanded to accommodate the work. Construct a new greenfield 0.55 miles long 69kV single circuit line using 556 ACSR Dove from the new East Leipsic 69kV breaker to the AEP / AMPT POI. Modify the East Leipsic Extension line. Modify the Yellow Creek - East Leipsic 69kV line. | Customer Service |  |  |  | 2025-08-01 |  |  | EP |  | 0 |  | 8.01 |  | 8.01 | 2022-10-14 |  |  |  | FALSE
P21252001 |  | s2829.1 | Wagenhals Station: Construct a new Wagenhals 138-69kV station on greenfield property owned by AEP to the south of the existing station. The 138kV portion will be a breaker-and-a-half design, with a total of 17 breakers. The 69kV will be a 5-breaker ring bus. The existing 138-69kV transformer #3 and 138kV cap bank will be transferred, while the 138-69-23kV transformer #2 will be retired. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 27.45 |  | 27.45 | 2022-10-14 |  |  |  | FALSE
P21252006 |  | s2829.2 | Retire the existing 138-69-23kV station, including structures and control house. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 3.71 |  | 3.71 | 2022-10-14 |  |  |  | FALSE
P21252007 |  | s2829.3 | Relocate 8- 138kV transmission lines and 4- 69kV transmission lines to connect to the new station location. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 10.48 |  | 10.48 | 2022-10-14 |  |  |  | FALSE
P21252028 |  | s2829.4 | Required environmental remediation at the existing station property. Dispose of PCB-contaminated soils, drainage tile, legacy oil piping and storage tanks, and synchronous condenser system. Final abatement plan to be determined with EPA. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 23.51 |  | 23.51 | 2022-10-14 |  |  |  | FALSE
P21252021 |  | s2829.5 | Wayview: Remote-end 138kV relay upgrades. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.36 |  | 0.36 | 2022-10-14 |  |  |  | FALSE
P21252022 |  | s2829.6 | Sunnyside: Remote-end 69kV relay upgrades. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.02 |  | 1.02 | 2022-10-14 |  |  |  | FALSE
P21252023 |  | s2829.7 | Stanley Court: Remote-end 69kV relay upgrades. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.49 |  | 0.49 | 2022-10-14 |  |  |  | FALSE
A19036120, P21005009, P21005010, P21005020 |  | s2830.1 | Richland – Ummel/Tri Lakes 69kV line: Rebuild the ~8.7 mile line using double circuit 138kV construction and 795 ACSR Drake construction but energize only one side at 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-03 |  |  | EP |  | 0 |  | 17.1 |  | 17.1 | 2022-10-14 |  |  |  | FALSE
P21005015, P21005016, A19036114 |  | s2830.2 | Rebuild the Albion – Kendallville 138kV: Rebuild the ~8.5 mile Albion – Kendallville 138kV circuit using 795 ACSR Drake | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  |  | EP |  | 0 |  | 15.8 |  | 15.8 | 2022-10-14 |  |  |  | FALSE
P21005011, P21005012 |  | s2830.3 | Wolf Lake 69kV Tap: Rebuild the ~5.5 mile Wolf Lake tap as double circuit 138kV using 795 ACSR Drake. This line will be energized at 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  |  | EP |  | 0 |  | 13.6 |  | 13.6 | 2022-10-14 |  |  |  | FALSE
A19036068, P21005001, P21005002 |  | s2830.4 | Albion 138/69kV: Replace 138kV CB “F” and cap switcher “BB”. In addition to this, this station had significant ancillary work needed including foundation repairs, new control cable runs and DICM installation. Construction at this station will be aligned with B3248 | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-30 |  |  | EP |  | 0 |  | 4.6 |  | 4.6 | 2022-10-14 |  |  |  | FALSE
P21005005, P21005018 |  | s2830.5 | Kuhns / Albion REMC 69kV: Reconnect Kuhns Sw to serve the currently hard tapped Albion REMC load | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2022-10-14 |  |  |  | FALSE
P21005014 |  | s2830.6 | Albion REMC 69kV Radial Tap: Reterminate the line into Kuhns Sw 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2022-10-14 |  |  |  | FALSE
A19036114, P21005013, P21005015, P21005016 |  | s2830.7 | Albion – Kendallville 69kV Line: Reterminate the line into Kuhns Sw 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2022-10-14 |  |  |  | FALSE
P21005007, P21005008, A19036065 |  | s2830.8 | Kendallville 138/69kV: Replace the 138/69kV transformer with a 90MVA unit. This work will be aligned with S2431. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  |  | EP |  | 0 |  | 2.2 |  | 2.2 | 2022-10-14 |  |  |  | FALSE
P21005003, P21005004 |  | s2830.9 | Onion Bottom Bog Sw/Wolf Lake 69kV: Install a 69kV POP “Onion Bottom Bog” Switch to serve Wolf Lake station. This switch will be re-used from the “Whitford Sw” that was removed with S2431 | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2022-10-14 |  |  |  | FALSE
|  | s2830.10 | Rebuild ~21 miles of the circuit from Sorenson to north of Columbia. Retire the remaining 44.1 miles of the line. | Equipment Material Condition, Performance and Risk |  |  |  | 2032-12-01 |  |  | EP |  | 0 |  | 65.7 |  | 65.7 | 2022-10-14 |  |  |  | FALSE
|  | s2830.11 | Build a new ~7.5 mile double circuit extension from the Twin Branch – Guardian line to connect the existing Northeast station. | Equipment Material Condition, Performance and Risk |  |  |  | 2032-12-01 |  |  | EP |  | 0 |  | 21 |  | 21 | 2022-10-14 |  |  |  | TRUE
P23509004, P23509005 |  | s2830.12 | Build a new ~11.7 mile double circuit 138/69kV line from Tri Lakes – Onion Bottom Bog Sw and reenergize the 138kV circuit from Columbia – Albion | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-01 |  |  | EP |  | 0 |  | 32.8 |  | 32.8 | 2022-10-14 |  |  |  | FALSE
P23509006 |  | s2830.13 | Retire the ~7.8 mile Tri Lakes – Gateway 69kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-01 |  |  | EP |  | 0 |  | 2.3 |  | 2.3 | 2022-10-14 |  |  |  | FALSE
P23509001, P21005001 |  | s2830.14 | Install a new 138kV CB and a new 69kV CB to connect the new lines at Albion station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-01 |  |  | EP |  | 0 |  | 2 |  | 2 | 2022-10-14 |  |  |  | FALSE
|  | s2830.15 | Reconnect Kline station to the Twin Branch – Jackson Rd 138kV line and install a new 138kV breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2032-12-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2022-10-14 |  |  |  | FALSE
DR22F04B0, DR22F04B1, DR22F04L0, DR22F04W2 |  | s2831.1 | Retire 69kV Noble station. Re-terminate 69kV Auburn-Kendallville 69kV line outside of Noble station. | Customer Service |  |  |  | 2026-04-08 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2024-02-16 |  |  |  | FALSE
DR22F04C0, DR22F04T0, DR22F04W2 |  | s2831.2 | Install 138kV bus, 15.4MVAR Capacitor with 138kV circuit breaker, 2x 138kV MOAB to serve new distribution station. Install Telecom at Virtue station and remote ends. | Customer Service |  |  |  | 2026-04-27 |  |  | EP |  | 0 |  | 2.9 |  | 2.9 | 2024-02-16 |  |  |  | FALSE
P21030003 |  | s2832.2 | East Lima 138kV: Replace 1000MCM, 1590 AAC bus and riser conductors on the ‘B’ string and Bus 2 with 2-2000 MCM AAC | Operational Flexibility and Efficiency |  |  |  | 2025-02-28 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2022-10-04 |  |  |  | FALSE
|  | s2832.4 | Marysville 345kV station: Replace (2) 345 kV 5000A 63kA circuit breakers and associated sub conductor and switches on the H string to eliminate the lower-rated equipment. | Operational Flexibility and Efficiency |  |  |  | 2024-12-20 |  |  | UC |  | 50 |  | 3.01 |  | 3.01 | 2022-10-04 |  |  |  | FALSE
DR21R37B0 |  | s2848 | Patrick Henry Station: Establish new Distribution station which will be designed at 138 kV and operated at 69 kV until the area conversion project converts the high-side to 138 kV as part of s2179 (Stuart Area Improvements). The new station will consist of two 138 kV Motor Operated Air-Break Switches (MOABs), high-side circuit switcher, 138 (69) kV/34.5 kV 30 MVA transformer, 34.5 kV low-side circuit breaker and 2-34.5 kV distribution feeder circuit breakers. | Customer Service |  |  |  | 2025-12-02 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
P20245010 |  | s2851 | New Carlisle 138 kV station: Replace 138kV circuit breaker A with a new 3000A 63kA circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-28 |  |  | EP |  | 0 |  | 0.35 |  | 0.35 | 2022-11-18 |  |  |  | FALSE
A19036095, P21604001, P21604002 |  | s2854.1 | Twenty Third Street – Blaine Street 34.5 kV: Rebuild ~1.20 miles of 34.5 kV line with 556.5 ACSR 26/7 Dove. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-01 |  |  | EP |  | 0 |  | 7 |  | 7 | 2022-12-16 |  |  |  | FALSE
A19036063, P21593001 |  | s2854.2 | Twenty Third Street station: Replace the Twenty Third Street 138/34.5 kV transformer #1 and transformer #2 with two 138/69/34.5 kV 90 MVA transformers. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-22 |  |  | EP |  | 0 |  | 5.36 |  | 5.36 | 2022-12-16 |  |  |  | FALSE
P21582001 |  | s2856 | Rebuild the West Coshocton 138-69kV station, with a 138kV 3-breaker ring bus, a new 138-69kV transformer (90 MVA nameplate), and a single 69kV breaker. A new control building will also be installed. Remove the existing station facilities. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-16 |  |  | EP |  | 0 |  | 10.17 |  | 10.17 | 2022-12-16 |  |  |  | FALSE
DP22C10Z1 |  | s2857.1 | Green Chapel 138 kV: Construct a greenfield station with 19 - 138kV, 90 kA, 4000 A circuit breakers in breaker and half bus configuration. | Customer Service |  |  |  | 2025-02-26 |  |  | UC |  | 31 |  | 27.57 |  | 27.57 | 2022-12-16 |  |  |  | FALSE
DP22C10Z0 |  | s2857.2 | Innovation 138 kV: Build out the remaining 2 breaker & half strings at the station and install 4 - 138 kV 4000A 80kA circuit breakers | Customer Service |  |  |  | 2025-02-26 |  | 2025-03-13 | UC | IS | 31 | 100 | 3.91 |  | 3.91 | 2022-12-16 |  |  |  | FALSE
DP22C10W2 |  | s2857.3 | Green Chapel – Innovation 138 kV: Construct ~2.1 miles of double circuit 138kV transmission line from Innovation Station to Green Chapel Station utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor SE rating 1123 MVA. | Customer Service |  |  |  | 2025-02-26 |  | 2025-03-13 | UC | IS | 31 | 100 | 12.6 |  | 12.6 | 2022-12-16 |  |  |  | FALSE
DP22C10W3 |  | s2857.4 | Green Chapel Extension 138 kV: Construct ~2.6 miles of double circuit 138kV transmission line extending from Jug - Corridor 138 kV line to Green Chapel station utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor SE rating 1118 MVA to match the existing conductor on the Corridor-Jug line | Customer Service |  |  |  | 2025-03-04 |  |  | UC |  | 31 |  | 15.6 |  | 15.6 | 2022-12-16 |  |  |  | FALSE
DP22C10W0 |  | s2857.5 | Jug – Corridor 138/345 kV: Additional structures and dead ends will be required on the existing Jug – Corridor double circuit line to accommodate the extension eastward to Green Chapel as the 138 kV circuit is on the west side of the structures. E | Customer Service |  |  |  | 2025-02-26 |  |  | UC |  | 31 |  | 3.6 |  | 3.6 | 2022-12-16 |  |  |  | FALSE
DP22C10C0 |  | s2857.6 | Conesville - Corridor 345kV: Modify the existing 345kV line structures to enable appropriate height for the new line to Green Chapel Station | Customer Service |  |  |  | 2025-03-04 |  |  | UC |  | 31 |  | 1.97 |  | 1.97 | 2022-12-16 |  |  |  | FALSE
P22799001 |  | s2857.7 | Babbitt 345/138 kV: Install a second 675 MVA, 345/138 kV transformer to address overloading Jug Street 345/138 kV transformer under N-1-1 contingencies as a result of this customer load interconnection. Cost | Customer Service |  |  |  | 2026-07-10 |  |  | EP |  | 0 |  | 16 |  | 16 | 2022-12-16 |  |  |  | FALSE
P22799002 |  | s2857.8 | Corridor 138 kV: Replace 3000A breakers CB-104C & 104S with 4000 A breakers. This addresses N-1-1 overloading on those breakers as a result of this customer load interconnection. | Customer Service |  |  |  | 2027-04-20 |  |  | EP |  | 0 |  | 2 |  | 2 | 2022-12-16 |  |  |  | FALSE
P20252007 |  | s2857.9 | West Lancaster 138 kV: Install high and low side sectionalizing on the two 138/69 kV transformers. This addresses, due to lack of sectionalizing, N-1-1 overloading on 69 kV lines as a result of this customer load interconnection. | Customer Service |  |  |  | 2029-05-02 |  |  | EP |  | 0 |  | 3.5 |  | 3.5 | 2022-12-16 |  |  |  | FALSE
DP22C11Z0 |  | s2858 | Jug station 138 kV: Install 1 - 138kV 80kA 4000A circuit breaker in the open F position on the ring bus to accommodate a new distribution transformer at the station. | Customer Service |  |  |  | 2025-11-20 |  |  | EP |  | 0 |  | 0.678 |  | 0.678 | 2022-12-16 |  |  |  | FALSE
P17002002 |  | s2882.1 | Install a new seven breaker 138 kV ring bus utilizing 3000A 63kA breakers to replace the existing Wilson Rd ring bus. Retire the 40kV equipment at Wilson Rd. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 8 |  | 8 | 2023-01-20 |  |  |  | FALSE
P17002031 |  | s2882.2 | Rebuild the existing 0.7 miles triple circuit line between structure 47 and Wilson Rd as double circuit using 1033 ACSR conductor. The third circuit that creates a three terminal point between Hall, Fisher, and Wilson will be permanently retired. The Hall Road – Fisher 138 kV circuit will remain. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 2.1 |  | 2.1 | 2023-01-20 |  |  |  | FALSE
P17002022 |  | s2882.3 | Convert Phillipi station to 138kV service to allow for the elimination of the 40kV system between McComb and Wilson Rd. stations. Majority of the station was originally built to 138kV standards. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 0.51 |  | 0.51 | 2023-01-20 |  |  |  | FALSE
P17002033 |  | s2882.4 | Build a new 0.7 mile 138kV double circuit line to serve Phillipi at 138 kV off the Beatty – Wilson circuit. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 1.4 |  | 1.4 | 2023-01-20 |  |  |  | FALSE
P17002019 |  | s2882.5 | Retire the 5.45 mile 40kV circuit between Wilson and McComb. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2023-01-20 |  |  |  | FALSE
P17002006 |  | s2882.6 | The 40kV breakers at McComb station are no longer needed once Phillipi is converted to 138kV and will be retired. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  |  | EP |  | 0 |  | 0.59 |  | 0.59 | 2023-01-20 |  |  |  | FALSE
P19269004 |  | s2883.1 | Upgrade the Natrium 138-69kV station by completing the breaker-and-a-half design in the 138kV and 69kV portions of the station. Install a new control house in the 69kV yard and expand the newer 138kV control house. Remove the older control house and various 138kV & 69kV station structures. Install a 2nd 138kV capacitor bank (46 MVAR). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 18.22 |  | 18.22 | 2023-01-20 |  |  |  | FALSE
P19269005 |  | s2883.2 | Construct a new 138kV transmission line from Natrium to a customer station (0.5 mile), providing a 2nd source to the customer | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 2.59 |  | 2.59 | 2023-01-20 |  |  |  | FALSE
P19269009 |  | s2883.3 | Remote-end upgrades at Mobay 69kV station, to coordinate with the new fiber-based line relays at Natrium (2- 69kV circuits). A new transclosure will be installed to house the relays, RTU, and metering equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 1.26 |  | 1.26 | 2023-01-20 |  |  |  | FALSE
P21598001 |  | s2884.1 | Morse – Gahanna 138kV Line (Gahanna-Hap Cremean & Hap Cremean-Morse Road circuits): Rebuild the ~5.04 miles single circuit line with 795 kCM ACSR & install OPGW fiber on new line rebuild. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 13.62 |  | 13.62 | 2023-01-20 |  |  |  | FALSE
P21598007 |  | s2884.2 | Gahanna – Blacklick 138kV Line: Rebuild the ~3.32 miles single circuit line with 795 kCM ACSR & install OPGW fiber on new line rebuild. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 11.68 |  | 11.68 | 2023-01-20 |  |  |  | FALSE
P21598012 |  | s2884.3 | Blacklick Extension 138kV line: Partially rebuild the line from Blacklick to structure No. 11 ~0.71 mile single circuit line with 795 kCM ACSR & install OPGW fiber on new line rebuild | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 2.19 |  | 2.19 | 2023-01-20 |  |  |  | FALSE
P21598013 |  | s2884.4 | Morse Road 138kV station: Telecom upgrades. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0.025 |  | 0.025 | 2023-01-20 |  |  |  | FALSE
P21598008 |  | s2884.5 | Hap Cremean 138kV station: Install remote end relay upgrades, CCVTs, telecom multiplexer, & remove wave trap. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0.508 |  | 0.508 | 2023-01-20 |  |  |  | FALSE
P21598009 |  | s2884.6 | Gahanna 138kV station: Install remote end relay upgrades, telecom multiplexer, & remove wave trap. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0.497 |  | 0.497 | 2023-01-20 |  |  |  | FALSE
P21598010 |  | s2884.7 | Blacklick 138kV station: Install remote end relay upgrades, CCVTs, Telecom Multiplexer, & remove wave trap. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0.681 |  | 0.681 | 2023-01-20 |  |  |  | FALSE
P21598011 |  | s2884.8 | East Broad Street 138kV station: Install remote end relay upgrades, telecom upgrades, CCVTs, & remove wave trap. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 0.482 |  | 0.482 | 2023-01-20 |  |  |  | FALSE
P18171001 |  | s2887.1 | Construct a new brownfield, breaker and a half Glen Lyn station next to the existing station. The new station will contain eleven 138kV breakers with seven 138kV line exits creating four breaker and half strings. Two 138kV capacitor banks with circuit switchers. One 138/34.5kV Distribution bank with high side circuit switcher and four 34.5kV breakers. The high station cost is due to the need to raise the new station nearly 10 feet to relieve the flooding concern. Environmental cost is anticipated to be high to remove station equipment, asbestos abatement, building demolition, disposal of soils/TCI conduit/concrete/underground piping/underground transformer vaults. Remove the existing 138 and 34.5 kV yards. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 37.8 |  | 37.8 | 2023-01-20 |  |  |  | FALSE
P18171004 |  | s2887.2 | At Hinton station, remove the line trap. Install bus CCVTs and line arresters on the 138kV line to Glen Lyn. Upgrade relaying to coordinate to the new breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 0.67 |  | 0.67 | 2023-01-20 |  |  |  | FALSE
P18171006 |  | s2887.3 | Extend the Glen Lyn – Progress Park circuit ~0.4 miles of install to reconnect the circuit to the new Glen Lyn station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 2.5 |  | 2.5 | 2023-01-20 |  |  |  | FALSE
P18171007 |  | s2887.4 | Extend the Glen Lyn – Morgans Cut and Glen Lyn – Hazel Hollow lines (double circuit construction) ~0.15 miles to reconnect the lines to the new Glen Lyn station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2029-04-03 |  |  | EP |  | 0 |  | 2.6 |  | 2.6 | 2023-01-20 |  |  |  | FALSE
P18171009 |  | s2887.5 | Extend the Glen Lyn – Kimballton and Glen Lyn – Peters Mountain lines (double circuit construction) ~0.25 miles to reconnect the lines to the new Glen Lyn station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2029-03-06 |  |  | EP |  | 0 |  | 2.1 |  | 2.1 | 2023-01-20 |  |  |  | FALSE
P18171010 |  | s2887.6 | Extend the Glen Lyn – Hinton circuit ~0.1 miles to reconnect the line to the new Glen Lyn station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 1.8 |  | 1.8 | 2023-01-20 |  |  |  | FALSE
P18171017 |  | s2887.7 | Required work to connect the New Glen Lyn station to the existing fiber network. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 0.71 |  | 0.71 | 2023-01-20 |  |  |  | FALSE
A19036118, P21736001, P21736002, P21736003, P21736004 |  | s2888 | Adams – Berne 69 kV: Replace ~4.9 miles of 69 kV line structures. The following cost includes the structure replacements, structure removals, ROW acquisitions, and station connections. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-28 |  |  | EP |  | 0 |  | 12.8 |  | 12.8 | 2023-01-20 |  |  |  | FALSE
DX21C02D0 |  | s2911.1 | Guysville 69 kV: Install a in-out station with an 2000A auto sectionalizing MOAB switch towards Coolville and a 3000A 40kA circuit breaker towards Bryson. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 1.73 |  | 1.73 | 2023-02-17 |  |  |  | FALSE
P20092001 |  | s2911.2 | Bryson - Guysville 69 kV: Construct a greenfield ~12.5-mile single circuit line using 556.5 ACSR (Dove) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 28.26 |  | 28.26 | 2023-02-17 |  |  |  | FALSE
P20092003 |  | s2911.3 | Coolville – Guysville 69 kV: Constructing a greenfield ~10.5-mile single circuit line using 556.5 ACSR (Dove) conductor (SE 142 MVA) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 29.22 |  | 29.22 | 2023-02-17 |  |  |  | FALSE
P20092010 |  | s2911.4 | Coolville 69 kV: Upgrade to a in-out station with two 3000A 40kA circuit breakers on the through path. Existing wood structures will be replaced with a new steel box bay to accommodate new breakers | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 3.08 |  | 3.08 | 2023-02-17 |  |  |  | FALSE
P20092005 |  | s2911.5 | Coolville – East Bashan 69 kV: Rebuild the existing single circuit ~12.6-mile line using 556.5 ACSR (Dove) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 29.61 |  | 29.61 | 2023-02-17 |  |  |  | FALSE
P20092011 |  | s2911.6 | West Bashan 69 kV: Remove switch going to Hemlock | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.02 |  | 0.02 | 2023-02-17 |  |  |  | FALSE
P20092014 |  | s2911.7 | Hemlock – West Bashan 69kV: Remove ~7.7 miles of single circuit line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 2.09 |  | 2.09 | 2023-02-17 |  |  |  | FALSE
P20092012 |  | s2911.8 | Hemlock 69 kV: Remove the circuit breaker going to West Bashan (CB C). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 0.14 |  | 0.14 | 2023-02-17 |  |  |  | FALSE
P21733001 |  | s2913.1 | Retire existing Kyle Hill Station | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-02-17 |  |  |  | FALSE
P21733001 |  | s2913.2 | Kyle Hill Extension : New 0.07 miles double circuit in/out line from the Fort Robinson-Hill 69kV line to the new Kyle Hill 69kV Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  |  | EP |  | 0 |  | 1.22 |  | 1.22 | 2023-02-17 |  |  |  | FALSE
P21733004 |  | s2913.3 | Build a new Kyle Hill Station behind the existing station. Establish a 69KV bus to allow a 69KV in/out from Fort Robinson – Hill 69KV line. Install one (1) 1200A 69KV rated line MOAB switches towards Hill station. Install one (1) 1200A 69KV rated line switches towards Fort Robinson station. Replace Ground MOAB with a high-side circuit switcher. Replace existing 34.5/12KV transformer #1 with 69/12KV transformer. Install new 12KV bus. Reuse existing Kyle Hill 12kV Breakers. Install 16x19 DICM. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-07-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-02-17 |  |  |  | FALSE
P21733005 |  | s2913.4 | Retire approximately 3.41 miles of the Fort Robinson-Lovedale 34.5kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  |  | EP |  | 0 |  | 2.69 |  | 2.69 | 2023-02-17 |  |  |  | FALSE
P21733006 |  | s2913.5 | Remote end and Removal of Circuit Breaker J at Fort Robinson substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  |  | EP |  | 0 |  | 0.197 |  | 0.197 | 2023-02-17 |  |  |  | FALSE
P21733007 |  | s2913.6 | Remote end and Removal of Circuit Breaker G at Lovedale substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-07-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-02-17 |  |  |  | FALSE
P21733010 |  | s2913.7 | Retire 34.5 kV Echo Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  |  | EP |  | 0 |  | 0.095 |  | 0.095 | 2023-02-17 |  |  |  | FALSE
P21733011 |  | s2913.8 | Provide Transition Fiber for Kyle Hill Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  |  | EP |  | 0 |  | 0.106 |  | 0.106 | 2023-02-17 |  |  |  | FALSE
P21597001 |  | s2915.1 | Grace - South Rokeby 69 kV Line: Rebuild ~12.3 mi of line asset, the section between Grace – South Rokeby using 556 ACSR conductor & install telecom fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  |  | EP |  | 0 |  | 29.62 |  | 29.62 | 2023-02-17 |  |  |  | FALSE
P21597003 |  | s2915.2 | West Malta - North Muskingum 69 kV Line: Rebuild the whole ~8.4 mi line asset using 556 ACSR conductor & install telecom fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  |  | EP |  | 0 |  | 18.28 |  | 18.28 | 2023-02-17 |  |  |  | FALSE
P21597005 |  | s2915.3 | West Malta - North McConnelsville 69 kV Line: Rebuild the whole ~2.1 mi line asset using 556 ACSR conductor & install telecom fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  |  | EP |  | 0 |  | 6.08 |  | 6.08 | 2023-02-17 |  |  |  | FALSE
P21597015 |  | s2915.4 | South Rokeby – Gould No.1 & No. 2 69 kV Line: Rebuild both ~0.05 mi (each) line assets using 556 ACSR conductor & install telecom fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  |  | EP |  | 0 |  | 0.78 |  | 0.78 | 2023-02-17 |  |  |  | FALSE
P21597031 |  | s2915.5 | South Rokeby - North McConnelsville 69kV Line: ~0.25 miles rebuild on the South Rokeby – West Malta 69 kV Circuit & install telecom fiber | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  |  | EP |  | 0 |  | 0.92 |  | 0.92 | 2023-02-17 |  |  |  | FALSE
P21597023 |  | s2915.6 | Buttermilk Hill Switch 69 kV: Install a new 69 kV, 1200A, 3-way POP switch outside the fence of North McConnelsville station and install auto-sectionalizing. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  |  | EP |  | 0 |  | 0.73 |  | 0.73 | 2023-02-17 |  |  |  | FALSE
P21597017 |  | s2915.7 | Pennsville 69 kV POP Switch: Replace existing switch with 1200A, 3-way switch & install auto-sectionalizing. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  |  | EP |  | 0 |  | 0.73 |  | 0.73 | 2023-02-17 |  |  |  | FALSE
P21716011 |  | s2917.1 | Reconfigure the existing East Cambridge- West Cambridge 69kV circuit to add in a replacement switch pole for Cassell Junction Sw that is capable of adding MOAB operation on the throughpath. This replacement structure will be one span down from the existing switch in order to comply with current ROW standards. | Customer Service |  |  |  | 2025-12-31 |  |  | EP |  | 0 |  | 0.89 |  | 0.89 | 2023-02-17 |  |  |  | FALSE
P21716002 |  | s2917.2 | Install a new 138kV three- way phase over phase switch named Cassell Junction Switch to serve the Cassell Junction Co-op station. | Customer Service |  |  |  | 2025-12-31 |  |  | EP |  | 0 |  | 0.68 |  | 0.68 | 2023-02-17 |  |  |  | FALSE
P21716003 |  | s2917.3 | Construct ~ 0.12 miles of new 69 kV line between the new Cassell Junction Switch and the Cassell Junction Co-op station using 556 ACSR conductor. | Customer Service |  |  |  | 2025-12-31 |  |  | EP |  | 0 |  | 0.66 |  | 0.66 | 2023-02-17 |  |  |  | FALSE
P21716001 |  | s2917.4 | Install new customer metering at Cassell Junction for Guernsey Muskingum Electric Cooperative. | Customer Service |  |  |  | 2025-12-31 |  |  | EP |  | 0 |  | 0.004 |  | 0.004 | 2023-02-17 |  |  |  | FALSE
P19256001 |  | s2920.1 | At East Lima 69kV breakers U and V will be replaced with 3000A 40kA breakers. The 69kV disconnect switches and sub-conductors will be upgraded. A DICM will be installed to replace the old control structure. Relay and breaker control voltages will be standardized. Environmental remediation at the station will be completed per federal requirements. Remediation will include the disposal of PCB-impacted soils, concrete, and a legacy oil processing facility including associated oil piping and equipment. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 11.1 |  | 11.1 | 2023-03-17 |  |  |  | FALSE
P19256004 |  | s2920.2 | Upgrade relays at West Lima, Ford Lima, Yellow Creek and Woodlawn to coordinate with the new protection and communication scheme tied out of East Lima | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 1 |  | 1 | 2023-03-17 |  |  |  | FALSE
P21599001 |  | s2921 | Conesville-Bixby 345kV Line ( Bixby-Ohio Central & Ohio Central-Conesville Circuits ): Rebuild ~46.1 miles of the ~51.1 miles of line using 954 kCM ACSR bundled conductor & install OPGW fiber on new line rebuild. Newer steel poles on the line will not be replaced | Equipment Material Condition, Performance and Risk |  |  |  | 2032-12-31 |  |  | EP |  | 0 |  | 154.53 |  | 154.53 | 2023-02-07 |  |  |  | FALSE
P21076018 |  | s2941 | Install one new 138/12 kV XFR and one new 138 kV CB at the existing Coco Station. | Customer Service |  |  |  | 2025-02-28 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2023-04-21 |  |  |  | FALSE
P21748001, P21748002, P21748012, P21748003 |  | s2942.1 | Main Street – Hickory Creek 138kV Line Asset: Rebuild ~3.47 miles of the Derby – Main Street 138kV circuit up to structure 125. Of that ~3.47 miles, the Main Street – Napier – Hickory Creek 34.5kV circuit is double circuited with Derby – Main Street 138kV circuit for ~2.84 miles, which will also be rebuilt and then energized to 69kV. Both lines will utilize the 795 ACSR 26/7 Drake conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  |  | EP |  | 0 |  | 16.2 |  | 16.2 | 2023-04-21 |  |  |  | FALSE
P21748016 |  | s2942.2 | Main Street – Hickory Creek 34.5kV (via Pearl Street): Energize at 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-04-21 |  |  |  | FALSE
P21748013 |  | s2942.3 | Main Street: Energize circuit breakers J, K, and L to 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  |  | EP |  | 0 |  | 0.91 |  | 0.91 | 2023-04-21 |  |  |  | FALSE
P21748016 |  | s2942.4 | Hickory Creek: Retire 34.5kV circuit breaker BG and remaining 34.5kV equipment. Energize circuit breakers AQ, BE, and BH to 69kV. Breaker BH will be used as a bus tie breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  |  | EP |  | 0 |  | 1.18 |  | 1.18 | 2023-04-21 |  |  |  | FALSE
P21748017, P21748014, P21748015, P21748021 |  | s2942.5 | Pearl Street, Langley, and Napier: Energize to 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  |  | EP |  | 0 |  | 0.41 |  | 0.41 | 2023-04-21 |  |  |  | FALSE
P21748019, P21748020 |  | s2942.6 | Ausco Radial 34.5kV: Retire the 34.5kV Ausco radial | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2023-04-21 |  |  |  | FALSE
A19036115, P22047001, P22047002, P22047003 |  | s2943 | Rebuild 5.88 miles of the 6.36 mile circuit from Magley-Decatur with 795 ACSR. The rebuild will consist of all 1957 and 1966 vintage poles, towers with failed strength requirements, as well as the 4/0 and 336 ACSR conductor | Equipment Material Condition, Performance and Risk |  |  |  | 2030-02-19 |  |  | EP |  | 0 |  | 12.48 |  | 12.48 | 2023-04-21 |  |  |  | FALSE
P16078006 |  | s2944 | Warwood: Replace the 3- 69kV oil circuit breakers with new SF6 gas breakers. Replace the electromechanical 69kV line relays and bus differential relays with microprocessor-based relays. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  |  | EP |  | 0 |  | 1.49 |  | 1.49 | 2023-04-21 |  |  |  | FALSE
P16078018 |  | s2970 | Remove the 69kV cap bank and cap switcher at Scio. A new RTU will be added along with standard SCADA functionality for transmission & distribution equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-08-04 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2023-06-16 |  |  |  | FALSE
P19303004 |  | s2981.1 | Cut in/out of the existing Lakin – Lock Lane 69 kV line and construct a new double circuit 69 kV line in/out to the new Mason County Industrial Park Station (approx. 0.25 mi) | Customer Service |  |  |  | 2025-11-17 |  |  | EP |  | 0 |  | 2.1 |  | 2.1 | 2023-07-21 |  |  |  | FALSE
P19303012 |  | s2981.2 | Install two 69 kV circuit breakers and a 69/12 kV 25 MVA transformer at the new Mason County Industrial Park Station (York Station) | Customer Service |  |  |  | 2025-11-17 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-07-21 |  |  |  | FALSE
P21591001 |  | s2982.1 | South Kenton. Rebuild the 138kV bay as a four breaker ring bus using 3000A 40kA breakers. Replace transformers two and three with a single 90MVA unit. Install a DICM and replace the EM relays. Replace the 69kV bus and breakers C and E. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  |  | EP |  | 0 |  | 12.7 |  | 12.7 | 2023-07-21 |  |  |  | FALSE
P21591010 |  | s2982.2 | Re-terminate the East Lima - South Kenton 138 kV and South Kenton - Larue 138kV circuits into the new South Kenton ring bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  |  | EP |  | 0 |  | 3.64 |  | 3.64 | 2023-07-21 |  |  |  | FALSE
P21591007 |  | s2982.3 | Re-terminate the South Kenton - Kenton #1 69kV and South Kenton - Kenton #2 69kV circuits into the station. Install fiber between South Kenton and Kenton, retire the pilot wire scheme E | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  |  | EP |  | 0 |  | 1.45 |  | 1.45 | 2023-07-21 |  |  |  | FALSE
P21591002 |  | s2982.4 | At Kenton station, replace MOABS X,Z with 69kV 3000A 40kA breakers. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  |  | EP |  | 0 |  | 3.8 |  | 3.8 | 2023-07-21 |  |  |  | FALSE
|  | s2982.5 | Upgrade telecom equipment at Rangeline and Gunn Road stations | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  |  | EP |  | 0 |  | 0.094 |  | 0.094 | 2023-07-21 |  |  |  | FALSE
P21590001 |  | s2983.1 | North Delphos: Replace 69kV circuit breakers A & C and Install DICM. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 3.3 |  | 3.3 | 2023-07-21 |  |  |  | FALSE
P21590013 |  | s2983.2 | Van Wert: Upgrade line relays. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2023-07-21 |  |  |  | FALSE
P21590006 |  | s2983.3 | South Delphos – Delphos: Rebuild 2.7 miles of 69kV with 556 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 7.8 |  | 7.8 | 2023-07-21 |  |  |  | FALSE
P21590010 |  | s2983.4 | North Delphos - South Delphos: Rebuild 4.33 miles of 69kV with dove 556 ACSR. 1.1 miles will be double circuit (part of the in and out to North Delphos not covered under b3346) and 3.2 miles will be single circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-06-01 |  |  | EP |  | 0 |  | 11.7 |  | 11.7 | 2023-07-21 |  |  |  | FALSE
P22110013 |  | s2984.1 | Haviland - Paulding 69kV: Rebuild the existing 10.73 mile-long line using 795 ACSR Drake conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-01 |  |  | EP |  | 0 |  | 18.74 |  | 18.74 | 2023-07-21 |  |  |  | FALSE
P22110007 |  | s2984.2 | Paulding: Perform remote end work | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-01 |  |  | EP |  | 0 |  | 1.4 |  | 1.4 | 2023-07-21 |  |  |  | FALSE
P22110008 |  | s2984.3 | Haviland: Perform remote end work | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-01 |  |  | EP |  | 0 |  | 1.03 |  | 1.03 | 2023-07-21 |  |  |  | FALSE
P21244004 |  | s2985.1 | Elgin – North Spencerville: Construct approximately 5 miles of 69kv single circuit. Install ADSS. | Customer Service |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 12.13 |  | 12.13 | 2023-07-21 |  |  |  | FALSE
P21244001 |  | s2985.2 | North Spencerville: Install a DCIM expansion and new 69kv circuit breaker. Install bypass switch called West Spencerville | Customer Service |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2023-07-21 |  |  |  | FALSE
P21244007 |  | s2985.3 | Kossuth-E Delphos: Install ~0.05 miles of 69kv single circuit. | Customer Service |  |  |  | 2024-12-01 |  |  | EP |  | 0 |  | 0.31 |  | 0.31 | 2023-07-21 |  |  |  | FALSE
P21077001, P21077002 |  | s2986.1 | East Elkhart 138kV: Install a new 138kV breaker string with 3 3000A 40kA circuit breakers to accommodate two new feeds to the NIPSCO station. Relocate the 345/138kV transformer #2 feed to the new string. Install metering on both exits out of East Elkhart towards NIPSCO’S Menges Ditch station. | Customer Service |  |  |  | 2026-07-22 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-05-19 |  |  |  | TRUE
P21077003, P21077004, P21077005, P21077007 |  | s2986.2 | East Elkhart – Menges Ditch 138kV #1 and #2: Install the first span and structure outside of East Elkhart, one exiting to the north and the other to the south, utilizing 2 bundle 795 ACSR 26/7 DRAKE conductor creating a new AEP-NIPSCO interconnection and PJM-MISO seam. | Customer Service |  |  |  | 2026-07-22 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-05-19 |  |  |  | TRUE
P20252035 |  | s3133.1 | Ralston - North Logan 69 kV Line : Retire the line section between North Logan – Geneva Switch (~9.0 miles) between Str. 70 – 147 and rebuild a portion as double circuit from Geneva Sw up to Str. 70/71 (~1.15 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2026-04-16 |  |  | EP |  | 15 |  | 9.67 |  | 9.67 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252024 |  | s3133.2 | East Logan – Shawnee 69 kV Line : Six-wire the 69 kV line between N. Logan – E. Logan (Str. 2-43) and terminate the E. Logan – New Lexington 69 kV circuit into the now vacated Ralston – N. Logan 69 kV line position at N. Logan station at/near structure 44 to form the new N. Logan – New Lex. 69 kV circuit. Remove sections between Str. 43 – 44 and Str. 2 – E. Logan (CB-L). | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-20 |  |  | EP |  | 15 |  | 1.28 |  | 1.28 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252029, P20252030 |  | s3133.3 | Clouse - West Lancaster 138 kV: Rebuild ~23 miles of 138 kV line between West Lancaster and Clouse stations. The existing double circuit line will be rebuilt as double circuit between West Lancaster and just east of South Lancaster station along with the section between structure 96 and Clouse station. The remaining ~5.6 miles of the line will be rebuilt as single circuit. The section between structure 96 and Clouse will have one circuit of the double circuit operated at 69 kV to form the South Lancaster – Clouse circuit to allow for the retirement of the Ralston – North Logan line south. 69 kV and 138 kV line extensions will be installed into Clouse station, using 795 ACSR conductor SE 360 MVA. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-02-12 |  |  | EP |  | 15 |  | 65.81 |  | 65.81 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252049 |  | s3133.4 | East Logan – South Lancaster 69 kV Line : Re-terminate this line at East Logan to utilize CB-P, which is a newer vintage breaker in better health than existing breaker M. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-03-27 |  |  | EP |  | 15 |  | 0.72 |  | 0.72 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252008 |  | s3133.5 | East Logan 69 kV: Retire 69 kV CB-M and repurpose CB-P for re-terminating the South Lancaster circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-20 |  |  | EP |  | 15 |  | 0.77 |  | 0.77 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252046 |  | s3133.6 | Clouse 138 kV & 69 kV: Add a 138 kV, 3000 A, 63 kA breaker to accommodate the new 138 kV line from Crooksville. Add a 69 kV, 3000 A, 40 kA breaker to accommodate the new 69 kV line from South Lancaster (thru Geneva Sw). Install all associated attachment facilities. DICM expansion will likely be required. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-08-08 |  |  | EP |  | 15 |  | 1.67 |  | 1.67 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252047 |  | s3133.7 | Geneva Sw 69 kV: Replace & relocate the existing PoP Switch with a 3-way 1200A PoP Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-08-08 |  |  | EP |  | 15 |  | 0.95 |  | 0.95 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252006 |  | s3133.8 | Junction City 138 kV: Replace the existing 2-way POP with a 3-way 2000A POP. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-09-07 |  |  | EP |  | 15 |  | 1.15 |  | 1.15 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252007 |  | s3133.9 | West Lancaster 138 kV & 69 kV: Replace T2 with a 90MVA bank. Replace 138 kV CB-D with 1 - 138 kV, 3000 A, 40 kA circuit breaker, 69 kV CB-C & CB-J with 2 – 69kV 3000 A, 40 kA circuit breakers, 69 kV CS-BB with 1 – 69 kV 2000A 31.5 kA circuit breaker and, the control building with DICM & new relays. Retire 138 kV CB-E. Replace 69 kV Bus 1 PT’s. Note: Work will be coordinated with previously proposed upgrades at station captured under S2857.9. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-09-11 |  |  | EP |  | 15 |  | 10.83 |  | 10.83 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252036 |  | s3133.10 | South Lancaster 138 kV & 69 kV: Add 2 - 69 kV, 3000 A, 40 kA and 2- 138 kV, 3000 A, 40 kA circuit breakers to the low and high sides of T1 and T2. Upgrade transformers’ protection. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-09-05 |  |  | EP |  | 15 |  | 3.22 |  | 3.22 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252022 |  | s3133.11 | Lancaster – E. Lancaster – S. Lancaster 69 kV: In order to mitigate the 3-terminal line, 0.2 miles of 69 kV double circuit line, including several dead end and turning structures, will be constructed to loop the circuit into East Lancaster station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-20 |  |  | EP |  | 15 |  | 2.39 |  | 2.39 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252004 |  | s3133.12 | East Lancaster 69 kV: Extend the bus to accommodate a new line. Install one new 69 kV, 3000 A, 40 kA breaker and all associated attachment facilities (relays, bus work, risers, and switches). Retire the 69 kV cap bank. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-21 |  |  | EP |  | 15 |  | 1.04 |  | 1.04 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252037 |  | s3133.13 | Lancaster Jct – E. Lancaster – Ralson 69 kV : In order to mitigate the 3-terminal line, 0.2 miles of 69 kV double circuit line will be constructed to loop the circuit into Lancaster Junction station. There will be associated telecom work performed as well. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-27 |  |  | EP |  | 15 |  | 1.65 |  | 1.65 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252001 |  | s3133.14 | Lancaster Junction 69 kV: Add three 69 kV, 3000 A, 40 kA line breakers at Lancaster Junction and all associated attachment facilities (relays, bus work, risers, and switches). Expand the Station to include two box bays. Retire 69 kV Line & Bus tie switches. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-02-20 |  |  | EP |  | 15 |  | 5.03 |  | 5.03 | 2023-11-17 | PM Robert Howard |  |  | FALSE
P20252045 |  | s3133.15 | Anchor Hocking, Lancaster, North Logan, New Lexington 69 kV: Remote end PCE work will be performed to accommodate project in area. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-28 |  |  | EP |  | 15 |  | 0.69 |  | 0.69 | 2023-11-17 | PM Robert Howard |  |  | FALSE
DP21R02B0 |  | s3134.1 | Construct a 138 kV straight bus with 2 MOABs that are SCADA controlled. Install a 138/34.5 kV, 30 MVA Distribution transformer with two 34.5kV circuit breakers | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-24 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 |  |  |  | FALSE
DP21R02C0 |  | s3134.2 | Install a new 138kV 3 pole custom tap structure on the Jacksons Ferry – Huffman 138 kV circuit. Construct approximately 4.0 miles of new double circuit 138 kV line with OPGW from the tap location to the new Wildwood substation. The higher cost is due to access road and restoration costs in the state of Virginia. The right of way for this 138kV extension travels in different directions due to hard to obtain easements causing higher line cost. Install ADSS fiber along existing Huffman-Jacksons Ferry line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-24 |  |  | EP |  | 0 |  | 20.8 |  | 20.8 | 2023-11-17 |  |  |  | FALSE
A16927002 |  | s3135.1 | Rebuild ~2.6 mi portion of the existing Garden Creek - Richlands - Skeggs Branch 69kV Line from the existing Permac station to the existing tap structure 340-28 on the Garden Creek – Skeggs Branch - Richlands. Rebuild ~4.6 mi of the existing Garden Creek - Richlands - Skeggs Branch 69kV Line from the existing Coal Creek to Richlands substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  |  | EP |  | 0 |  | 27.2 |  | 27.2 | 2023-11-17 |  |  |  | FALSE
A16927023 |  | s3135.2 | At Whetstone Branch Station, replace circuit switcher "AA" with a new, standard, 69kV circuit switcher, replace all metering CTs and PTs with CT/PT combo metering units, and replace the existing single phase CCVT with a new standard three phase CCVT. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  |  | EP |  | 0 |  | 1.55 |  | 1.55 | 2023-11-17 |  |  |  | FALSE
|  | s3135.3 | At Coal Creek substation, reconductor the 69kV bus, replace 600A Switchers with new MOAB switches on new steel structures. Switch "33" towards the customer will be replaced to allow for the new structure to fit into the existing station footprint. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 |  |  |  | FALSE
|  | s3135.4 | Remote end work at Richlands substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  |  | EP |  | 0 |  | 0.05 |  | 0.05 | 2023-11-17 |  |  |  | FALSE
|  | s3135.5 | Provide transition fiber on the Garden Creek - Richlands - Skeggs Branch 69kV Line for connectivity at Mount Heron Station and at Whetstone Branch Station to support CES networking and SCADA connectivity. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2023-11-17 |  |  |  | FALSE
P22091001 |  | s3136.1 | Hartford Station: Install a 69kV breaker and remove the 34.5kV equipment. Station Service will be relocated closer to the transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-14 |  |  | EP |  | 15 |  | 0.59 |  | 0.59 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  |  | FALSE
P22091003 |  | s3136.2 | Sister Lakes: Replace both transformers with 9.375MVA 69/12kV units and install a high side switcher on transformer 1. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-02-10 |  |  | EP |  | 15 |  | 0 |  | 0 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  |  | FALSE
P22091004 |  | s3136.3 | Dewey Lake Street: Install a new 7.5 MVA 69/34.5kV transformer with low side breaker and high side fuse. This will be located close to Gearcon Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-07-07 |  |  | EP |  | 15 |  | 1.72 |  | 1.72 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  |  | FALSE
P22091006 |  | s3136.4 | Valley: Install a 69/34.5kV 12.5MVA transformer and retermniate the Rothadew line to the 69kV bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-12-07 |  |  | EP |  | 15 |  | 3.63 |  | 3.63 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  |  | FALSE
P22091007 |  | s3136.5 | Colby: Move the Rothadew line to the 69kV bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-12-04 |  |  | EP |  | 15 |  | 0.11 |  | 0.11 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  |  | FALSE
P22091016 |  | s3136.6 | Twin Lakes Sw.: Replace Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-16 |  |  | EP |  | 15 |  | 0.83 |  | 0.83 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  |  | FALSE
P22091008 |  | s3136.7 | Keelette, Sister Lakes, Gearcon Sw., Rothadew,: Energize to 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-14 |  |  | EP |  | 15 |  | 1.01 |  | 1.01 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  |  | FALSE
P23221002 |  | s3137.1 | Cut in/out of the existing Yellow Bush – Polymer 138 kV line, install a new double circuit 138 kV 0.1 mile line to the new 138 kV station (Kera Lakes). | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-13 |  |  | UC |  | 75 |  | 0 |  | 0 | 2023-11-17 | PM Roger Whitt / Planner Michael Hassay |  |  | FALSE
P23321003 |  | s3137.2 | Construct a new 138 kV station (Kera Lakes) with 4 – 3000A, 40 kA circuit breakers in a ring bus configuration with two feeds to the customer. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-13 |  | 2024-12-12 | UC | IS | 75 | 100 | 0 |  | 0 | 2023-11-17 | PM Roger Whitt / Planner Michael Hassay |  |  | FALSE
P23321008 |  | s3137.3 | Network fiber support work at Cottageville Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-13 |  | 2024-12-12 | UC | IS | 75 | 100 | 0 |  | 0 | 2023-11-17 | PM Roger Whitt / Planner Michael Hassay |  |  | FALSE
DR23C08D0 |  | s3138.1 | At Taylor station, install 1-138 kV 40 kA 3000 A bus tie circuit breaker and 1-138 kV 3000 A 40 kA GOAB beaker disconnect switch to accommodate a new distribution transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  |  | EP |  | 0 |  | 1.26 |  | 1.26 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21724009 |  | s3139.1 | Construct a new double circuit 138 kV line (approx. 1 miles) by tapping the existing Cherry Creek – Pemberton 138 kV and building in/out to a new 138 kV station near Coal City. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 5.4 |  | 5.4 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
A20045035 |  | s3139.2 | Retire existing 46 kV line from Sophia – Maben Energy. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 11.5 |  | 11.5 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
A20045036 |  | s3139.3 | Retire existing Sophia – Tams Mountain 46 kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 4.7 |  | 4.7 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21724004 |  | s3139.4 | Retire existing Pemberton – Sophia 46 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 3.3 |  | 3.3 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21724001 |  | s3139.5 | New Coal City Station: Install two 138 kV line MOABs, one 138/12 kV 20 MVA XFR with high side circuit switcher and two 12 kV feeders | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 1 |  | 1 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
A20045062 |  | s3139.6 | Retire Sophia 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 1.4 |  | 1.4 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21724003, P21724015, P21722016, P21723013 |  | s3139.7 | Pemberton Station: Install a new 138/46 kV XFR with a high side circuit switcher and new metering. This will feed the customer currently served out of Sophia Station. Construct a new 1 mile 46 kV line from Pemberton to the customer. Install two new 138 kV circuit breakers . Retire 138/46 kV XFR, 46 kV CB-A, 46 kV CB-C and 4 kV distribution equipment. Install one new 138 kV circuit breaker. Retire 46 kV CB-B | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 10.7 |  | 10.7 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21724005 |  | s3139.8 | Stotesbury: Replace existing hard tap with a new 3-way phase over phase switch | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 1.8 |  | 1.8 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21724006 |  | s3139.9 | Retire Killarney 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21724007 |  | s3139.10 | Retire Bowyer 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723017 |  | s3139.11 | Tams Mountain: Remove 46 kV CB-N2 and 46 kV CB M | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723007 |  | s3139.12 | Construct a new double circuit 138 kV line in/out (approx. 1 mile) to the existing Sweeneysburg Switch Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 3.8 |  | 3.8 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723001, P21723016 |  | s3139.13 | Construct a new 138 kV double circuit line (approx. 2 miles) by tapping the existing North Beckley – Tams Mountain 138 kV line and building in/out to a new 138 kV station (Lester Square Station) | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 9.9 |  | 9.9 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723004 |  | s3139.14 | Construct a new 138 kV single circuit line (approx. 1.2 miles) from the new Lester Square Station to the existing Pemberton 138 kV station. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 6.6 |  | 6.6 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723014 |  | s3139.15 | Retire Glen White Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723019 |  | s3139.16 | Retire Shockley Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
A20001421 |  | s3139.17 | Retire Bradley – Tams Mountain 46 kV line: | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 20.3 |  | 20.3 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723012 |  | s3139.18 | Sweeneysburg Switch: Convert to 138 kV | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723010, P21723011, P21723025 |  | s3139.19 | Lester Square: Install five 138 kV CBs in a ring configuration, install one 23 MVAR capacitor bank with a circuit switcher, install a new 138/12 kV 20 MVA XFR with two 12 kV feeders. Install a new 138/46 kV XFR to feed the customer previously served from Shockley Station. Construct a new 46 kV line from Lester Square to the customer previously served at Shockley Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 5.9 |  | 5.9 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723021 |  | s3139.20 | North Beckley Station: Remote End work required due to the new line cut in to Lester Square Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0.6 |  | 0.6 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21723015 |  | s3139.21 | Bradley Station: Remove 46 kV CB-F, Retire 46 kV CB-J | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722003 |  | s3139.22 | Construct a new 138 kV double circuit line (approx. 1.5 miles) tapping the existing Bradley – North Beckley 138 kV line and building in/out to a new 138 kV station (Cranberry Creek) | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 7.9 |  | 7.9 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722001 |  | s3139.23 | Construct a new single circuit 138 kV line (approx. 5.1 miles) from Pemberton to a new 138 kV station (East Beckley) | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 15.7 |  | 15.7 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722002 |  | s3139.24 | Construct a new single circuit 138 kV line (approx. 1.7 mile) from the new East Beckley 138 kV Station to a new 138 kV station (Armory Station) | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 8 |  | 8 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722025 |  | s3139.25 | Construct a new double circuit 138 kV line (approx. 1.0 miles) by tapping the Raleigh County 138 kV Extension line and building in/out to the new Armory 138 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 4.5 |  | 4.5 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
A20045034 |  | s3139.26 | Retire Bradley – Beckley 46 kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 9.6 |  | 9.6 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
A20045032 |  | s3139.27 | Retire Beckley – Pemberton 46 kV line and Crab Orchard 46 kV tap line | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 7 |  | 7 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722020 |  | s3139.28 | Retire Whitestick 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
A20045059 |  | s3139.29 | Retire Beckley 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722021 |  | s3139.30 | Retire Crab Orchard 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722032, P21722027 |  | s3139.31 | Armory Station: Install three 138 kV circuit breakers, 23 MVAR capacitor bank with circuit switcher, install one new 138/12 kV 25 MVA XFR with high side circuit switcher and three 12 kV feeders | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 4.2 |  | 4.2 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722010, P21722011 |  | s3139.32 | East Beckley: Install two 138 kV MOABs, install one new 138/12 kV 25 MVA XFR with a high side circuit switcher and three 12 kV feeders | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722012, P21722013 |  | s3139.33 | Cranberry Creek: Install one 138 kV circuit breaker, one 138 kV line MOAB, one 138/12 kV 25 MVA XFR with a high side circuit switcher and three 12 kV feeders | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 2.2 |  | 2.2 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
|  | s3139.34 | Cherry Creek Station: Remote end work due to the the Armory Extension cut-in | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21722019, P21722022, P21722031 |  | s3139.35 | North Beckley Station: Install one 138/12 kV 25 MVA XFR with three 12 kV feeders. Install one new 138 kV circuit breaker, replace existing ground switch MOAB on XFR #1 with a new 138 kV circuit switcher. Replace existing ground switch MOAB on 138/34.5 kV XFR #2 and replace existing 34.5 kV circuit breakers G and H. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  |  | EP |  | 0 |  | 1.6 |  | 1.6 | 2023-11-17 | PM Roger Whitt |  |  | FALSE
P21577003, P21577012, P21577006 |  | s3140.1 | Wooster – South Coshocton: The 37.7-mile line will be rebuilt using 795 ACSR DRAKE to alleviate identified asset renewal conditions. This includes the 15.2-mile West Millersburg – Wooster 138kV circuit as well a portion of the 30.9-mile single circuit Ohio Central – West Millersburg 138kV circuit up to structure 13 outside Ohio Central station. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  |  | EP |  | 0 |  | 96.5 |  | 96.5 | 2023-10-20 | PM Pleau, Cayla / Marker, Jerod |  |  | FALSE
P21577017 |  | s3140.2 | Perform remote end work at Wooster | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  |  | EP |  | 0 |  | 0.501 |  | 0.501 | 2023-10-20 | PM Pleau, Cayla / Marker, Jerod |  |  | FALSE
P21577018 |  | s3140.3 | Perform remote end work at West Millersburg | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  |  | EP |  | 0 |  | 0.503 |  | 0.503 | 2023-10-20 | PM Pleau, Cayla / Marker, Jerod |  |  | FALSE
DR23R04B0 |  | s3141.1 | Snowville Station: The greenfield station will contain a 138/34.5 kV 30 MVA transformer with high side circuit switcher. There will be two 34.5 kV feeders from the station. The 138 kV side will be a straight bus with two 138 kV MOABs. | Customer Service |  |  |  | 2025-10-25 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-10-20 | Kay, Brian |  |  | FALSE
DR23R04C0 |  | s3141.2 | Snowville 138kV Line Extension: The line extension will tap the Claytor – Wurno - Pulaski 138kV line and bring the line in and out of the greenfield Snowville station by building 0.1 miles of greenfield double circuit 138kV line. | Customer Service |  |  |  | 2025-10-25 |  |  | EP |  | 0 |  | 1.48 |  | 1.48 | 2023-10-20 | Kay, Brian |  |  | FALSE
DR23R04C1 |  | s3141.3 | Snowville Fiber Line Extension: Build 2.0 miles of 144 ADSS Telecom underbuilt cable to connect Snowville station to Claytor station. | Customer Service |  |  |  | 2025-10-25 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2023-10-20 | Kay, Brian |  |  | FALSE
P22110005 |  | s3142.1 | Haviland - Van Wert: Rebuild the line to double circuit 138kV design using 1033 Curlew ACSR conductor. The line will be six wired and operated at 69kV. The rebuild will include a 2.6-mile greenfield section to route the line near several new industrial sites. The overall line length will be 10.8 miles. Newer installed poles will be re-used elsewhere. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  |  | EP |  | 0 |  | 27.8 |  | 27.8 | 2023-10-20 | Simon, Devin |  |  | FALSE
P22110012 |  | s3142.2 | Modify the b3359 scope from single circuit 69kV construction to double circuit 1033 Curlew at 138kV design | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  |  | EP |  | 0 |  | 2.89 |  | 2.89 | 2023-10-20 | Simon, Devin |  |  | FALSE
P22110008 |  | s3142.3 | Perform remote end work at Haviland | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  |  | EP |  | 0 |  | 1.03 |  | 1.03 | 2023-10-20 | Simon, Devin |  |  | FALSE
P22110009 |  | s3142.4 | Perform remote end work at Van Wert | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  |  | EP |  | 0 |  | 0.635 |  | 0.635 | 2023-10-20 | Simon, Devin |  |  | FALSE
PCE deemed work not needed. Do we need to submit a redline just for telecom? |  | s3142.5 | Upgrade telecom equipment at South Van Wert, Logtown, Maddox Creek, Timber Switch and North Delphos stations | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  |  | EP |  | 0 |  | 0.194 |  | 0.194 | 2023-10-20 | Simon, Devin |  |  | FALSE
P22744003, P22744005 |  | s3143.1 | Cut in/out of the existing Sporn – Tri-State 345 kV line and construct two single circuit 345 kV line extensions to a new 345 kV Station (Mercers Bottom) | Customer Service |  |  |  | 2024-10-03 |  |  | UC |  | 50 |  | 19.7 |  | 19.7 | 2023-10-03 | Jenkins, Frank |  |  | FALSE
P22744001 |  | s3143.2 | Construct a new 345 kV Station (Mercers Bottom) with 8 - 5000 A, 63 kA circuit breakers | Customer Service |  |  |  | 2024-10-03 |  |  | UC |  | 50 |  | 30.8 |  | 30.8 | 2023-10-03 | Jenkins, Frank |  |  | FALSE
P22744009 |  | s3143.3 | Remote end station work required at Sporn 345 kV | Customer Service |  |  |  | 2024-10-03 |  |  | EP |  | 15 |  | 0.8 |  | 0.8 | 2023-10-03 | Jenkins, Frank |  |  | FALSE
P22744041, P22744043 |  | s3143.4 | Construct two single circuit 345 kV feeds, approximately 0.75 miles each from Mercers Bottom 345 kV Station to the customer’s 345 kV Station. | Customer Service |  |  |  | 2024-10-03 |  |  | UC |  | 50 |  | 12.4 |  | 12.4 | 2023-10-03 | Jenkins, Frank |  |  | FALSE
P22744011 |  | s3143.5 | Cut into the existing Apple Grove – South Point 138 kV line and install a new 3-way Phase over Phase switch. Install a single circuit 0.1 mi 138 kV extension to the customer station. Install 138 kV metering at the new switch | Customer Service |  |  |  | 2024-10-03 |  | 2024-12-16 | UC | IS | 50 | 100 | 4.1 |  | 4.1 | 2023-10-03 | Jenkins, Frank |  |  | FALSE
P22744006, P22744034 |  | s3143.6 | construct a new 345 kV line from Sporn 345 kV Station to Mercers Bottom 345 kV Station, approximately 26 miles. | Customer Service |  |  |  | 2024-10-03 |  |  | EP |  | 15 |  | 143 |  | 143 | 2023-10-03 | Jenkins, Frank |  |  | FALSE
P22744022 |  | s3143.7 | Install a new 345 kV circuit breaker at Sporn to accommodate the new 345 kV line. | Customer Service |  |  |  | 2024-10-03 |  |  | EP |  | 15 |  | 2 |  | 2 | 2023-10-03 | Jenkins, Frank |  |  | FALSE
DP23F01B0 |  | s3144.1 | Install a 138kV/12kV distribution station named Kekionga on the MckinleyEllison Road 138kV line. Install 138kV line extension from Mckinley-Ellison 138kV line with fiber (~0.15 miles from the 138kV line), install 138kV bus with 2-138kV switches and 138kV MOAB. | Customer Service |  |  |  | 2025-11-12 |  |  | EP |  | 0 |  | 4.4 |  | 4.4 | 2023-08-18 | Jacobson, Seth |  |  | FALSE
DP21A01B0, DP21A01D0 |  | s3145.1 | At East Liverpool station, replace the 138kV MOAB/ground switch system with a circuit breaker and new relays. Install a 69kV breaker on the low side of the 138-69kV transformer. Upgrade tie-line metering, relays, and expand SCADA functionality at the station. Replace the control house with a new prefabricated control building. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 3 |  | 3 | 2023-08-18 | Sides, Todd |  |  | FALSE
DP21A01D1, DP21A01D0 |  | s3145.2 | At the 69kV remote end station of Second Street, replace the electromechanical relays and pilot wire communications with microprocessor-based relays, to coordinate with East Liverpool. Install new 69kV CCVT’s. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-05-01 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2023-08-18 | Sides, Todd |  |  | FALSE
P22012052, A20705029 |  | s3147.1 | Coleman - Peter Creek 69kV line - Install new 69kV line with OPGW from Coleman station to Peter Creek Station. Total line length 5.8 miles. Rebuilding within the existing ROW, but some new ROW will be required to get from Coleman station to Peter Creek station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 19.2 |  | 19.2 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012057 |  | s3147.2 | Peter Creek - Wharncliffe 69kV line - Install new 69kV line with OPGW from the KY/WV State Line to Peter Creek Station. Total line length 0.1 miles. New ROW will be required to get from the WV/KY state line to Peter Creek station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012049, P22012048 |  | s3147.3 | Peter Creek - Wharncliffe 69kV line - Install new 69kV line with OPGW from the KY/WV State Line to Wharncliffe Station. Intermediate station includes Bear Creek. Includes switching structures Devil Anse and Briar Mt. for Transmission customers and their delineation poles. Total line length 12.7 miles. Rebuilding within the existing ROW, but some new ROW will be required to get from the WV/KY state line to Devil Anse S.S. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 44.7 |  | 44.7 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012004, P22012029 |  | s3147.4 | Devi Anse S.S. Metering - One 69kV meter for the Transmission customer and one 69kV meter facing the WV/KY state line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.5 |  | 0.5 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012014 |  | s3147.5 | Briar Mt. S.S. Metering - One 69kV metering structure for the Transmission customer. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012056 |  | s3147.6 | Huff Creek - Wharncliffe 46kV line - The remove the span into the takeoff and the first structure 556-109 then reterminate the line into the new station takeoff structure on the Huff Creek – Wharncliffe 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.25 |  | 0.25 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012031 |  | s3147.7 | Tug Fork - Wharncliffe 69kV line - Install a new single circuit 69kV with OPGW line from existing Wharncliffe station to Tug Fork station totaling 5.9 miles long. Also reusing 2.3 miles of the Jim Branch – Wharncliffe line asset at 69kV that was rebuilt in 2007. Create 2.2 miles of greenfield ROW and reuse 3.7 miles of existing ROW from Tug Fork to Wharncliffe stations. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 24.3 |  | 24.3 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012026, P22012028 |  | s3147.8 | Lester Fork - Tug Fork 69kV line - Install a new single circuit 69kV with OPGW line from Lester Fork to Tug Fork stations crossing the VA/WV state border totaling 8.0 miles long. Create greenfield ROW from Lester Fork to Tug Fork stations crossing the VA/WV state border. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 33.9 |  | 33.9 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012059 |  | s3147.9 | Looney Creek - Lester Fork 69kV line - Install new 69kV line with OPGW from structure 343-1A to the new Lester Fork Station at 0.25 miles. Remove structure 343-1 and the span into the Hurley Station at 0.1 miles. Create greenfield ROW from structure 343-1A to Lester Fork station at 0.25 miles. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 2.51 |  | 2.51 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012054 |  | s3147.10 | Rapoca 69kV Customer - Replace the Rapoca Station hard tap from the Hurley - Looney 69kV circuit with a Phase over Phase switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012010 |  | s3147.11 | Bear Creek Station - Two 69kV MOABs that are automatic, and SCADA controlled for the Bear Creek 69kV work. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012035 |  | s3147.12 | Wharncliffe Station - Upgrade the existing Wharncliffe station to 69kV. One 69kV Capacitor bank that is 11.5 MVAR and circuit switcher. One 69/46kV 50 MVA transformer and one 46kV circuit breaker facing Gilbert on the low side of the transformer. Reusing the existing three Transmission circuit breaker for the high side of the transformer and lines facing Tug Fork and Briar Mt. S.S. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 5.9 |  | 5.9 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
DR22H03B0, DR22H03Y0 |  | s3147.13 | Tug Fork Station - Two 69kV circuit breakers with one facing Wharncliffe and the other facing Lester Fork stations. Includes 69kV bus work. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 2.1 |  | 2.1 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012025 |  | s3147.14 | Lester Creek Station - One 69kV meter facing Tug Fork for the state line crossing. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.3 |  | 0.3 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012027 |  | s3147.15 | Looney Creek Station - Replace the existing 69kV MOAB facing Lester Fork with a 69kV circuit breaker. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 1.2 |  | 1.2 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
A20705028 |  | s3147.16 | Sprigg - Barrenshe 69kV line - Remove approximately 6.9 miles of Sprigg - Barrenshe 69kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.024 |  | 0.024 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
A20705029 |  | s3147.17 | Barrenshe – Coleman 69kV line - Remove approximately 6.2 miles of Barrenshe - Coleman 69kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.024 |  | 0.024 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012011, A20705030 | P22012011 | s3147.18 | Sprigg - Wharncliffe 46kV line - Remove approximately 1.29 miles of Sprigg - Wharncliffe 46kV line in KY. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 1.1 |  | 1.1 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
A20705030 |  | s3147.19 | Sprigg - Wharncliffe 46kV line - Remove approximately 18.3 miles of Sprigg - Wharncliffe 46kV line in WV and remove the Grapevine Switching Structure. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 14.2 |  | 14.2 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012006, A20705048, P22012005 |  | s3147.20 | Jim Branch - Wharncliffe 46kV line - Remove approximately 19.7 miles of Jim Branch - Wharncliffe 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 15.3 |  | 15.3 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012021, A20705050 |  | s3147.21 | Hardy Tap 46kV line - Remove approximately 2.0 miles of the Hardy Tap 46kV line and remove the Hardy Switching Structure. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 1.9 |  | 1.9 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
A20705051 |  | s3147.22 | Panther Tap 46kV line - Remove approximately 0.7 miles of the Panther Tap 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.69 |  | 0.69 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012040 |  | s3147.23 | Briar Mt. Tap 46kV line - Remove approximately 0.1 miles of the Briar Mt. Tap 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.12 |  | 0.12 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012050 |  | s3147.24 | Grapevine Tap 46kV line - Remove approximately 0.1 miles of the Grapevine Tap 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.45 |  | 0.45 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012017 |  | s3147.25 | Jim Branch station Removal - Remove the 46kV Circuit Breaker P facing Panther and the Grounding Bank. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.087 |  | 0.087 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012037, where is rebuild BPID? |  | s3147.26 | Sprigg Station: Remove all the 46kV bus and attached equipment. Remove the 138/69 – 46kV transformer and the 46/7.2KV GND Bank. Remove the 69kV bus and attached equipment. Remove the 138kV equipment. Rebuild the station as a four 138kV circuit breaker ring bus station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 5 |  | 5 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012001 |  | s3147.27 | Coleman Station - Replace 69kV circuit breaker H towards Peter Creek and risers. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
A20705033 |  | s3147.28 | Barrenshe Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012002 |  | s3147.29 | Peter Creek Station - A new Distribution station that is replacing Barrenshe station that has a MOAB that is Scada controlled facing Coleman and a 69kV circuit breaker facing Devil Anse S.S. One 69kV circuit switcher and a 20 MVA 69/12kV Transformer and 4 Distribution feeders. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012053, A20705024 |  | s3147.30 | Grapevine Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012010, P22012008 |  | s3147.31 | Bear Creek Station - A new Distribution station that is replacing Grapevine station that has one 69kV circuit switcher and a 20 MVA 69/34kV Transformer and two Distribution feeder. Also helping to break up a large Distribution circuit out of Pigeon Creek station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012041 |  | s3147.32 | Briar Mt. Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012042 |  | s3147.33 | Bens Creek Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012043 |  | s3147.34 | Wharncliffe Station - Add one 69kV circuit switcher and a 20 MVA 69/12kV transformer and one Distribution feeder to pick up the load from the retired Bens Creek and Briar Mt. stations. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
DR22H03B0 |  | s3147.35 | Tug Fork Station - A new Distribution station that is replacing Hardy and Panther stations that has one 69kV circuit switcher and a 20 MVA 69/12kV Transformer and three Distribution feeder. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
DR22H03B1, DR22H03B2 |  | s3147.36 | Hardy and Panther Stations - Removal of the Distribution stations and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012022 |  | s3147.37 | Lester Fork Station - A new Distribution station that is replacing Hurley station that has two MOABs that are Scada controlled, one 69kV circuit switcher and a 20 MVA 69/12kV Transformer and three Distribution feeder. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012063, A20001431 |  | s3147.38 | Hurley Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22012039 |  | s3147.39 | Build 2 fiber station transitions using OPGW at Coleman and Peter Creek stations. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.2 |  | 0.2 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
|  | s3147.40 | Build 4 fiber station transitions using OPGW at Devil Anse S.S. Bear Creek, Briar Mt. S.S. and Wharncliffe. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 0.7 |  | 0.7 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
|  | s3147.41 | Lester Fork – Wharncliffe Fiber - Build 3 fiber station transitions using OPGW at Tug Fork, Wharncliffe and Lester Fork. Remove one of the existing shield wires and replace it with an OPGW at 2.3 miles on the Jim Branch – Wharncliffe line asset that is being reused from 2007 | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  |  | EP |  | 0 |  | 5.1 |  | 5.1 | 2023-08-18 | Smith, M Shawn |  |  | FALSE
P22045003 |  | s3148.1 | Sorenson - Desoto 345kV: Rebuild the ~51.5 mile line as is using double circuit 345kV construction. Replace jumpers at Sorenson and Desoto to accommodate the new structure entrances at the stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-10 |  |  | EP |  | 0 |  | 202.4 |  | 202.4 | 2023-08-08 |  |  |  | FALSE
TP2021264 |  | s3211.1 | Construct a new 69 kV line from the existing Looney Creek station to the greenfield Conaway station, approximately 6.1 miles long. New right of way is needed from Looney Creek to Conaway station. The line cost is driven by very steep terrain and the miles of access roads required and access road restoration cost, which is a requirement in Virginia. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  |  | EP |  | 0 |  | 30.2 |  | 30.2 | 2022-11-18 |  |  |  | FALSE
TP2021264 |  | s3211.2 | Construct a greenfield station (Conaway) to replace Big Rock and Thomas stations. Conaway will contain a 69/12 kV 20 MVA transformer with high side circuit switcher. There will be two 12 kV feeders from the station. The 69 kV side will be a straight bus with 69 kV MOABs. Distribution work is required to reconnect the Distribution system to the new Conaway station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
TP2021264 |  | s3211.3 | At the existing Looney Creek station, a new 69 kV circuit breaker will be installed to connect the Conaway – Looney Creek 69 kV line. Replace the high side 138kV MOAB ground switch with a 138 kV circuit breaker due to protection and control at the station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  |  | EP |  | 0 |  | 2.44 |  | 2.44 | 2022-11-18 |  |  |  | FALSE
TP2021264 |  | s3211.4 | Remove the ~6.4 mile long Big Rock – Grundy 34.5 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  |  | EP |  | 0 |  | 5.08 |  | 5.08 | 2022-11-18 |  |  |  | FALSE
TP2021264 |  | s3211.5 | Remove 34.5 kV circuit breaker “D” and 34.5 KV circuit breaker “C” at Grundy station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  |  | EP |  | 0 |  | 0.4 |  | 0.4 | 2022-11-18 |  |  |  | FALSE
TP2021264 |  | s3211.6 | Remove the Big Rock station and equipment. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
TP2021264 |  | s3211.7 | Remove the Thomas station and equipment. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-11-18 |  |  |  | FALSE
DP25C03B0 |  | s3212.1 | A new 69/12 kV distribution station (Vision) will be constructed. The station will be an in and out design utilizing in line MOAB's | Customer Service |  |  |  | 2024-12-31 |  |  | EP |  | 25 |  | 1.12 |  | 1.12 | 2023-03-17 | Waite, Karmyn |  |  | FALSE
DP25C03W0 |  | s3212.2 | Work will be performed on the West Van Wert – Cavett 69 kV circuit to cut in the newly proposed Vision station . | Customer Service |  |  |  | 2024-12-31 |  |  | EP |  | 25 |  | 2.99 |  | 2.99 | 2023-03-17 | Waite, Karmyn |  |  | FALSE
DP22C23B0 |  | s3213.1 | Construct a greenfield station “Milepost”, utilizing three 138kV 63kA 3000A circuit breakers configured in a ring to serve new customer loads. | Customer Service |  |  |  | 2024-04-15 |  |  | EP |  | 25 |  | 4.54 |  | 4.54 | 2023-03-17 | Caldwell, Colton |  |  | FALSE
DP22C23C0 |  | s3213.2 | Cut into the Roberts - Trabue 138 kV circuit and construct a new 0.14-mile double circuit 138kV in and out line to the new Milepost station utilizing 795 ACSR conductor SE: 360 MVA. | Customer Service |  |  |  | 2024-04-15 |  |  | EP |  | 25 |  | 2.79 |  | 2.79 | 2023-03-17 | Caldwell, Colton |  |  | FALSE
DP22C23D2, DP22C23Z1, DP22C23Z2 |  | s3213.3 | Remote end work to accommodate the above work at Cole, Roberts, & Trabue. | Customer Service |  |  |  | 2024-04-15 |  |  | EP |  | 25 |  | 0.17 |  | 0.17 | 2023-03-17 | Caldwell, Colton |  |  | FALSE
P24003008 |  | s3213.4 | Retire 3.3 miles of the Bethel Rd – Hilliard 69 kV line from Bethel Rd to the structure adjacent to Davidson 69 kV. Build a 0.3-mile extension connecting the line from Hilliard to Davidson using 795 ACSR conductor creating the Hilliard – Davidson 69 kV circuit. | Customer Service |  |  |  | 2024-04-15 |  |  | EP |  | 0 |  | 2.92 |  | 2.92 | 2023-03-17 | Pleau, Cayla |  |  | FALSE
P24003001 |  | s3213.5 | Retire Bethel Road 138/69/13.8 kV Transformer #3 and associated breakers. Install a new 138/69 kV transformer at Davidson station with a high side MOAB and a single 69kV 3000A 40kA breaker on the low side connecting to the reconfigured Davidson - Hilliard 69 kV circuit. | Customer Service |  |  |  | 2024-04-15 |  |  | EP |  | 0 |  | 1.58 |  | 1.58 | 2023-03-17 | Pleau, Cayla |  |  | FALSE
|  | s3213.6 | Upgrade Sub Cond 477 AAC 19 Str. at Blaire 69 kV. | Customer Service |  |  |  | 2024-04-15 |  |  | EP |  | 0 |  | 0.05 |  | 0.05 | 2023-03-17 |  |  |  | FALSE
P22768001 |  | s3214.1 | Install new 138kV phase-over-phase switch on the Corwin-Lick 138kV circuit. Install metering towards Veterans. | Customer Service |  |  |  | 2024-12-31 |  |  | EP |  | 25 |  | 0.67 |  | 0.67 | 2023-07-21 | Bachtel, Cole |  |  | FALSE
P22768004 |  | s3214.2 | Install ~0.3 miles of line from Pattonsville Switch to Veterans. | Customer Service |  |  |  | 2024-12-31 |  |  | EP |  | 25 |  | 0.45 |  | 0.45 | 2023-07-21 | Bachtel, Cole |  |  | FALSE
P22768005 |  | s3214.3 | Modify existing line to accommodate switch installation. | Customer Service |  |  |  | 2024-12-31 |  |  | EP |  | 25 |  | 0.32 |  | 0.32 | 2023-07-21 | Bachtel, Cole |  |  | FALSE
P22768007 |  | s3214.4 | Heppner-Lick 138 kV: Remove span of line from City of Jackson’s Lick station toward Veterans. | Customer Service |  |  |  | 2024-12-31 |  |  | EP |  | 25 |  | 0.1 |  | 0.1 | 2023-07-21 | Bachtel, Cole |  |  | FALSE
P22036004 |  | s3215.1 | A new 138 kV double circuit line extension will be built from the existing Jim Branch – Switchback line between Gary and Thorpe stations to the greenfield Coalfields stations, approximately 2.0 miles, creating an in and out. New right of way is needed from the new tap structure to Coalfields station. The line cost is driven by very steep terrain and the miles of access roads required. The line will require marker balls and helicopter installation due to the valleys and terrain. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  |  | EP |  | 0 |  | 13 |  | 13 | 2022-04-20 | Cooper, Wayne |  |  | FALSE
P22036001, P22036008 |  | s3215.2 | The 138kV high side of Coalfields station will be a 138kV straight bus with two automatic MOAB switches. The greenfield station will contain a 138/12 kV 20 MVA transformer with high side circuit switcher. There will be three 12 kV feeders from the station. Distribution work will be required to reconnect the Distribution system to the new Coalfields station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  |  | EP |  | 0 |  | 1.65 |  | 1.65 | 2022-04-20 | Cooper, Wayne |  |  | FALSE
P22036003 |  | s3215.3 | Work required to tap the existing Jim Branch – Switchback 138kV line asset. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  |  | EP |  | 0 |  | 1.8 |  | 1.8 | 2022-04-20 | Cooper, Wayne |  |  | FALSE
P22036010, P22036011, P22036012, P22036013 |  | s3215.4 | Remote end work required at Trail Fork, Tazewell, Clark Branch and Baileysville stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  |  | EP |  | 0 |  | 0.38 |  | 0.38 | 2022-04-20 | Cooper, Wayne |  |  | FALSE
A20045017 |  | s3215.5 | Remove the Transmission station and equipment at Carswell station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  |  | EP |  | 0 |  | 2.86 |  | 2.86 | 2022-04-20 | Cooper, Wayne |  |  | FALSE
A20045013, A20045014 |  | s3215.6 | Remove the Carswell 138kV Loop at ~1.4 miles and the Carswell – Gary 88kV Line at ~2.5 miles. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  |  | EP |  | 0 |  | 5.15 |  | 5.15 | 2022-04-20 | Cooper, Wayne |  |  | FALSE
A20045018 |  | s3215.7 | Remove the Distribution station and equipment at Belcher Mountain station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2022-04-20 | Cooper, Wayne |  |  | FALSE
DP24C09Z0 |  | s3301.1 | At Mink station, install 2 – 138kV, 3000 A, 63 kA breakers in the breaker and half configuration and associated work to terminate two new distribution transformers. | Customer Service |  |  |  | 2025-05-20 |  |  | UC |  | 26 |  | 2.7 |  | 2.7 | 2023-07-21 | PM Colton Caldwell |  |  | FALSE
DP24F01Y0 |  | s3302.1 | Install a 69 kV 23 MVAR capacitor bank at Price station and a 69 kV circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | 2025-04-24 | EP | IS | 15 | 100 | 1.5 |  | 1.5 | 2024-02-16 | PM Ijeoma Gilbert / Planner Andrew Morchik |  |  | FALSE
DP24F01D0 |  | s3302.2 | Install a temporary, mobile 69 kV 14.4 MVAR capacitor bank at Winchester station to mitigate low voltage violations in the Winchester area. The mobile capacitor bank at Winchester will be removed when project s2273 Randolph upgrades are completed. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | 2025-04-24 | EP | IS | 15 | 100 | 0.02 |  | 0.02 | 2024-02-16 | PM Ijeoma Gilbert / Planner Andrew Morchik |  |  | FALSE
DP23F04B0 |  | s3302.3 | Install a 69/4 kV 12.5 MVA transformer and a 69 kV high side circuit switcher. |  |  |  |  | 2026-03-23 |  |  | EP |  | 15 |  | 0 |  | 0 | 2024-02-16 | PM Ijeoma Gilbert / Planner Andrew Morchik |  |  | FALSE
|  | s3303.1 | At Gund Metering Point, install new revenue metering for a 20 MW customer load connection. Install a new 69kV manual switch on the customer side of the hard tap. | Customer Service¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  |  | EP |  | 0 |  | 1.15 |  | 1.15 | 2024-03-15 |  |  |  | FALSE
|  | s3303.2 | At Bevins Metering Point, motorize the existing switch at Bevins towards Gund to facilitate the connection of a 7 MW customer load to existing delivery point. | Customer Service¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  |  | EP |  | 0 |  | 0.59 |  | 0.59 | 2024-03-15 |  |  |  | FALSE
P23705001, P23705003, P23705007 |  | s3304.1 | Install a 3-way phase over phase switch on the Sorenson-Van Buren 138kV circuit. From the new switch, install a ~2.5 mile 138kV line to the customer delivery point. Low-side metering will be installed in the customer owned station. | Customer Service |  |  |  | 2026-10-01 |  |  | EP |  | 15 |  | 9.4 |  | 9.4 | 2024-03-15 | Felt, Tyler |  |  | FALSE
P23127001 |  | s3305.1 | Sifford Station: Sifford station will be built out to accomodate two new 138 kV feeds to the customer. This will include the installation of 4-3000A 40kA 138 kV circuit breakers and associated equipment. | Customer Service |  |  |  | 2024-09-30 |  | 2025-02-28 | EP | IS | 15 | 100 | 6.373 |  | 6.373 | 2024-03-15 | Rhoades, Isaac |  |  | FALSE
P23127004 |  | s3305.2 | Sifford – Ruble #2 138 kV Feed A: Install 138 kV line extension from AEP’s Sifford station to serve the customer’s station located just south of the Sifford station. | Customer Service |  |  |  | 2024-09-30 |  | 2025-02-28 | EP | IS | 15 | 100 | 2.948 |  | 2.948 | 2024-03-15 | Rhoades, Isaac |  |  | FALSE
P23127004 |  | s3305.3 | Sifford – Ruble #2 138 kV Feed B: Install a second 138 kV line from AEP’s Sifford station to serve the customer’s station located just south of the Sifford station to meet customer’s redundancy requirements at the site. | Customer Service |  |  |  | 2024-09-30 |  | 2025-02-28 | EP | IS | 15 | 100 | 0 |  | 0 | 2024-03-15 | Rhoades, Isaac |  |  | FALSE
P23013002 |  | s3306.1 | Huntington Court Station: Replace 69 kV circuit breakers “E”, “H”, and “M” and previously identified electromechanical and legacy microprocessor relaying. Install high-side circuit switcher on 138/12 kV T2 and low-side breaker on 138/34.5 kV T4 | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-30 |  |  | EP |  | 15 |  | 0 |  | 0 | 2024-03-15 | Jackson, Paul |  |  | FALSE
|  | s3307.1 | Replace existing 69 kV MOABs “W” and “Y” with new 69 kV circuit breakers, new 69 kV box bay and transclosure to house the new relaying. Estimated Cost: $0 (Distribution) | Customer Service |  |  |  | 2025-06-17 |  |  | EP |  | 0 |  | 0 |  | 0 | 2024-03-15 |  |  |  | FALSE
|  | s3307.2 | The existing 69 kV MOAB switch is located on the opposite side of the street from the station requiring a new 69 kV “in and out” line extension (two spans, separate structures) from the existing line to the new 69 kV box bay. | Customer Service |  |  |  | 2025-06-17 |  |  | EP |  | 15 |  | 1.4 |  | 1.4 | 2024-03-15 |  |  |  | FALSE
P22923005, P22923009 |  | s3308.1 | West Lancaster – South Baltimore – West Millersport 138 kV : Rebuild ~14.4 miles of the line between West Lancaster and West Millersport stations using 1033 ACSS 54/7 conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  |  | EP |  | 15 |  | 38.7 |  | 38.7 | 2024-03-15 | Howard, Robert |  |  | FALSE
P22923001 |  | s3308.2 | West Lancaster Station: Replace existing bus and line risers at the station, upgrade line relays. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  |  | EP |  | 15 |  | 1 |  | 1 | 2024-03-15 | Howard, Robert |  |  | FALSE
P22923002 |  | s3308.3 | South Baltimore Station: Replace existing bus and line risers at the station, upgrade line relays. While at the station some additional site concerns such as the existing fence will be addressed. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  |  | EP |  | 15 |  | 0.7 |  | 0.7 | 2024-03-15 | Howard, Robert |  |  | FALSE
P23130018, P23130011, P23130012 |  | s3309.4 | Rebuild 3.2 miles of 69kV from AEP-Marathon to Trinity with 954ACSS/TW, AEP to build Burr Oak 3 terminal 69kV ring. This tie will provide improved reliability for WVPA’s Trinity and Mt Zion stations as well as to AES-Marathon that is currently served on a long radial. Conductor rating: 196MVA/212MVA SN/SE | Customer Service |  |  |  | 2027-12-31 |  |  | EP |  | 15 |  | 6.5 |  | 6.5 | 2024-03-15 | Glover, Grant |  |  | TRUE
P23130001, P23130007, P23130006 |  | s3309.5 | To help facilitate a new network connection from AEP to WVPA to Dayton, build a new 4-69 kV circuit breaker ring bus. The following cost includes the new station construction, property purchase, metering, remote end relay upgrades, the Portland – Marathon 69 kV line connection, Marathon – Berne 69 kV line connection and Trinity radial line AEP removal. | Customer Service |  |  |  | 2027-12-31 |  |  | EP |  | 15 |  | 8.7 |  | 8.7 | 2024-03-15 | Glover, Grant |  |  | TRUE
A20045027 |  | s3387.1 | Replace existing 138 kV circuit breakers A, B, C, and D with four new 138 kV 3000 A 40 kA circuit breakers and install a new a new 138 kV 3000 A 40 kA circuit breaker between Wolf Hills 138 kV Bus #1 and Wolf Hills 138 kV Bus #2. Upgrade control house and install primary and backup station service. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-09-10 |  |  | EP |  | 15 |  | 5.3 |  | 5.3 | 2024-05-17 | Burns, Blair |  |  | FALSE
| P23029005 | s3388.1 | Remove an existing wood pole structure on the Raikes Branch customer delivery line and install a new pole that will have the new metering equipment. This cost is reimbursable from the customer; the previous delivery point switches are still in good condition and do not need replaced. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-03 |  | 2024-11-04 | EP | IS | 0 | 100 | 0 |  | 0 | 2024-05-17 |  |  |  | FALSE
P23828001, P23828003 |  | s3389.1 | Install a 3-way switch, with SCADA, on Albion-Robison Park 138kV circuit. From the new switch, install a ~0.01 mile 138kV line radial to customer station at 138kV. Low-side metering will be installed in the customer owned station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-19 |  |  | EP |  | 15 |  | 3.2 |  | 3.2 | 2024-07-19 | Felt, Tyler |  |  | FALSE
P23836001, P23836003 |  | s3390.1 | Install a 3-way switch, with SCADA, on Albion- Robison Park 138kV circuit. From the new switch install a ~0.2 mile 138kV line radial to customer delivery 138kV. Low-side metering will be installed in the customer owned station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  |  | EP |  | 15 |  | 4.5 |  | 4.5 | 2024-07-19 | Vecchiarelli, Katherine |  |  | FALSE
AEP-2022-OH071 |  | s3440.1 | Cyprus 345/138 kV: Cyprus is the station that was originally developed (s2526) to serve 675 MW of demand with room for 345 kV expansion based on LOA with the customer. Cut into the Beatty – Bixby 345 kV circuit and construct ~1.6 miles of double circuit line, utilizing 2-bundled ACSR Bittern 1272 conductor, SE rating 2278 MVA, to a new 345 kV ring bus at Cyprus station with (4) 5000 A, 63kA circuit breakers, (2) 345/138/34.5 kV, 675 MVA transformers, (12) 4000 A, 63kA, 138 kV circuit breakers, (1) 69.1 MVAR 138 kV Cap bank. Construct (2) 138 kV single circuit, ~0.4 miles, & (2) double circuit, ~0.9 miles, tie lines to the customers dead end structures utilizing ACSR Drake 795 (26/7) conductor SE 360 MVA. Modify the existing Cyprus 138kV Extension & Parsons 138kV circuits #1 & 2 structures to accommodate a fence relocation. Remote end relay upgrades are required at Beatty & Bixby 345 kV stations. | Customer Service |  |  |  | 2024-11-13 |  |  | EP |  | 0 |  | 46.9 |  | 46.9 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH071 |  | s3440.2 | Parsons 138 kV: Install (1) 69.1 MVAR cap bank to resolve N-1-1 voltage issues | Customer Service |  |  |  | 2025-07-24 |  |  | EP |  | 0 |  | 2 |  | 2 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH071 |  | s3440.3 | Beatty – Canal 138 kV line Sag Re-rate: The Beatty – Canal 138 kV line flagged as overloading under N-1-1 scenarios after the addition of the new load at Cyprus. The line will be flown to address sag issues that are limiting its current rating. It is anticipated that several structures will need to be replaced in order to rase the rating of the line. | Customer Service |  |  |  | 2025-07-24 |  |  | EP |  | 0 |  | 5.5 |  | 5.5 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH071 |  | s3440.4 | Waverly Reactor 138 kV: Install a 4% series reactor towards Rozelle at Waverly station to address a N-1-0 scenario related to the loss of a nearby 345 kV line. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 3 |  | 3 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH071 |  | s3440.5 | Saint Clair Avenue Reactor 138 kV: Adjust tap settings on reactors towards Mound and Clinton stations to 3%. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 0 |  | 0 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH071 |  | s3440.6 | Marion Station: Replace switch and line riser at Marion station towards Obetz to address loading concern under certain N-1-1 scenario related to customer interconnections in the area | Customer Service |  |  |  | 2027-12-01 |  |  | EP |  | 0 |  | 0.1 |  | 0.1 | 2023-12-05 |  |  |  | FALSE
AEP-2021-OH049 |  | s3441.1 | Construct a greenfield Jerome station with (10) 138kV 63kA 4000A circuit breakers in breaker and half bus configuration. Construct ~ 2.5 miles of double circuit 138kV transmission line extending from Kileville station to Jerome utilizing 2-bundled ACSS Cardinal 954 (45/7) conductor, SE rating 1061 MVA. Construct (4) 138 kV tie lines to the customers dead end structures ~0.05 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. Customers will be directly connected at this station | Customer Service |  |  |  | 2025-01-30 |  |  | EP |  | 0 |  | 30 |  | 29.78 | 2024-12-13 |  |  |  | FALSE
AEP-2022-OH024 |  | s3441.2 | Beacon 345 kV: Construct a greenfield station with (8) 5000 A, 345 kV, 63 kA circuit breakers & & (1) 158.4 MVAR 345 kV Cap bank in a breaker and a half configuration. Cut into the 345 kV Hayden – Roberts No. 2 circuit with two single circuit 345 kV lines ~0.2 miles terminating into Beacon station; utilizing 2-bundle ACSR Rail 954 (45/7) conductor SE 1887 MVA. A structure will need be installed to raise the Hayden – Roberts No 1 circuit. Construct three single circuit lines ~0.1 miles, between Beacon and the customer; utilizing 2-bundle ACSR Drake 795 (26/7) conductor SE 1800 MVA. | Customer Service |  |  |  | 2024-11-21 |  |  | EP |  | 0 |  | 40 |  | 40 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH035 |  | s3441.3 | Cosgray 345 kV: Expand the existing Cosgray ring bus (originally proposed under s2653) station by installing (2) 5000 A, 63 kA, 345 kV circuit breakers. Construct two ~0.06 miles single circuit lines to connect the new customer deliveries to Cosgray. | Customer Service |  |  |  | 2024-06-14 |  |  | EP |  | 0 |  | 5.1 |  | 5.1 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH041 |  | s3441.4 | Originally, Kileville is the station that was envisioned (s2855) to serve 461 MW of demand with room for 345 kV expansion based on LOAs with the customer. However, land in the area of the proposed Kileville station was not available for expansion to install 345/138 kV transformation. Therefore, a new station site called Celtic is being proposed to serve as the 345 kV source for the 461 MW of load to be served in this area. Cut into the Hayden – Hyatt 345 kV circuit, reroute ~0.8 miles of the circuit and extend ~1.1 miles of new double circuit line, utilizing 2-bundled ACSR Pheasant 1272 (54/19) conductor, SE rating 2413 MVA, to the greenfield Celtic 345/138 kV station with (4) 345 kV, 63 kA, 5000 A breakers laid out as ring bus configuration on high side. Install two 675MVA-345/138 kV power transformers. Install (8 6) 138kV, 63 kA, 4000 A breakers & (2) 69.1 MVAR 138 kV Cap bank on low side configured as breaker-and-a-half bus with provisions for future expansion . The proposed Kileville – Jerome 138 kV line will be brought in and out of the station creating two 138 kV Celtic – Jerome circuits and a single Celtic – Kileville 138 kV circuit. | Customer Service |  |  |  | 2025-11-13 |  |  | EP |  | 0 |  | 60 |  | 70.31 | 2024-12-13 |  |  |  | FALSE
AEP-2023-OH041 |  | s3441.5 | Kileville 138 kV: Expand Kileville station (originally proposed under s2855) with (4) additional 63 kA, 4000A circuit breakers in breaker and half bus configuration. Construct (2) 138 kV tie lines to the customers dead end structures ~0.05 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. Customers will be directly connected at this station. | Customer Service |  |  |  | 2024-04-01 |  |  | EP |  | 0 |  | 4.1 |  | 4.1 | 2023-12-05 |  |  |  | FALSE
AEP-2021-OH049, AEP-2022-OH024, AEP-2022-OH035, AEP-2023-OH041 |  | s3441.6 | Beatty – Wilson 138 kV line Sag Re-rate: Due to new customer interconnections in the area the Beatty – Wilson, Beatty – Bolton, Bolton – Hall and Hall - Wilson 138 kV circuits will overload for certain N-1-1 scenarios. Structures will be replaced on the line to address distribution clearance issue in order to allow the lines to operate to their conductor’s designed maximum operating temperature. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2023-12-05 |  |  |  | FALSE
AEP-2021-OH049, AEP-2022-OH024, AEP-2022-OH035, AEP-2023-OH041 |  | s3441.7 | Dublin Reactor 138 kV: Install a 4% series reactor towards Sawmill at Dublin station to address a N-1-1 scenario as a result of the new load interconnections in the area. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 3 |  | 3 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023 |  | s3442.1 | Badger 138 kV: Cut into the Green Chapel – Jug 138 kV circuit and extend ~ 0.1 miles of new double circuit line, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 1118 MVA , to the greenfield Badger station with (10) 80 kA, 4000 A breakers & (1) 69.1 MVAR 138 kV Cap bank, laid out as breaker and a half for future expansion to 6 strings. Construct 4 - 138 kV tie lines to the customers dead end structures ~.05 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA | Customer Service |  |  |  | 2024-11-24 |  |  | EP |  | 0 |  | 18.43 |  | 18.43 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH034 |  | s3442.2 | QTS North 138 kV: Construct ~0.3 miles of double circuit & a single circuit radial 138 kV tie lines from Anguin station to QTS Customer’s site dead-end structures serving transformers #1, #2 # 3, each utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. | Customer Service |  |  |  | 2024-03-25 |  |  | EP |  | 0 |  | 1.8 |  | 1.8 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH036 |  | s3442.3 | Innovation 345/138 kV: Cut into the Corridor - Conesville 345 kV circuit and construct ~0.1 miles of double circuit line, utilizing 2-bundled ACSR Bittern 1272 conductor, SE rating 2278 MVA, to a new 345 kV ring bus at Innovation station (s2578) with (4) 5000 A, 63kA circuit breakers, (2) 345/138/34.5 kV, 675 MVA transformers, (15) 4000 A, 80, kA, 138 kV circuit breakers, (2) 69.1 MVAR, 138 kV Cap banks. Upgrade the line protection relays at Conesville & Corridor 345 kV. Construct (2) 138 kV tie lines to the customers dead end structures ~0.04 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. | Customer Service |  |  |  | 2026-06-24 |  |  | EP |  | 0 |  | 53.7 |  | 53.7 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH045 |  | s3442.4 | Horizon 138 kV: Construct a greenfield station with (8) 80 kA, 4000 A circuit breakers in breaker and half bus configuration. Construct ~ 0.05 miles of double circuit 138kV transmission line extending from the Jug St.- Green Chapel 138 kV circuit to Horizon station utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 1118 MVA. | Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 10.81 |  | 10.81 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH046 |  | s3442.5 | Jorden 138 kV: Cut into the Innovation – Kirk 138 kV circuit with two single circuit 138 kV lines ~0.35 miles terminating into Jorden station, utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor, SE rating 1123 MVA, to Construct a greenfield 138 kV 4-CB ring bus station, configurable to 4-strings breaker and half station in future, with (4) 4000 A, 80 kA circuit breakers. Construct two single circuit 138kV lines ~0.1 miles, between Jorden and the customer. | Customer Service |  |  |  | 2026-07-10 |  |  | EP |  | 0 |  | 12.5 |  | 12.5 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH075 |  | s3442.6 | QTS South 138 kV: Cut into one of the circuits of Anguin – Brie 138 kV line and extend ~0.1 miles of two single circuit lines, utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor, SE rating 1123 MVA , to the greenfield Macy station with (4) 80 kA, 4000 A breakers laid out as 4-CB ring bus. Construct (2) 138 kV tie lines to the customers dead end structures ~0.04 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. | Customer Service |  |  |  | 2024-07-31 |  |  | EP |  | 0 |  | 9.54 |  | 9.54 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH075 |  | s3442.7 | Brie – Innovation 138 kV Tie: Construct a greenfield ~1.75 mile of double circuit line, utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor, connecting Brie and Innovation stations as well as re-establish the Babbitt - Kirk 138 kV circuit. At Brie 138 kV station will install four 138 kV circuit breakers in two partial strings breaker and half configuration along with a 69.1 MVAR capacitor. Perform remote end work at Innovation, Babbitt, and Kirk 138 kV stations. This project addresses a consequential (for a N-1-1 contingency) load drop event of more than 300 MW for the loads served out of AEP’s Anguin and Brie stations while also addressing an overload on the Babbitt – Innovation 138 kV circuit in relation to new customer interconnections in the area | Customer Service |  |  |  | 2025-07-31 |  |  | EP |  | 0 |  | 10.8 |  | 10.8 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH077 |  | s3442.8 | Curleys 345 kV: Cut into the rerouted Corridor – Innovation 345 kV circuit, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 2278 MVA, to a new 345 kV Curleys station with (14) 5000 A, 63kA circuit breakers & (2 1) 158.4 MVAR 345 kV Cap bank, laid out as breaker and a half for future expansion to 3 strings with future configurations to build up to total (10) breaker and half strings. Construct four single circuit lines ~0.1 miles, between Curleys station and the customer; utilizing 2-bundle ACSR Drake 795 (26/7) conductor SE 1800 MVA. The rerouted line, built as double circuit, will establish two 345 kV ties between Bermuda and Curleys stations. Reason For Update: As part of further engineering reviews it was determined that the previously proposed capacitor bank at Bermuda would be more efficiently accommodated at Curleys station. The scope update adds the 2nd capacitor at Curleys and removes it from the scope at Bermuda | Customer Service |  |  |  | 2027-12-01 |  |  | EP |  | 0 |  | 57.2 |  | 57.2 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH016 |  | s3442.9 | Souder 138 kV: Cut into the Corridor – Green Chapel 138 kV circuit and extend ~1.0 mile of new double circuit line, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 1118 MVA , to the greenfield Souder station with (5) 80 kA, 4000 A breakers laid out as 5-CB ring bus for future expansion to 6-CB ring. | Customer Service |  |  |  | 2025-10-22 |  |  | EP |  | 0 |  | 14.31 |  | 14.31 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH019 |  | s3442.10 | Bermuda 345 kV: Reroute the Corridor – Innovation 345 kV circuit across the customer’s site utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, built with double circuit structures, SE rating 2278 MVA, to a new 345 kV Bermuda station with (11) 5000 A, 63kA circuit breakers & (1) 158.4 MVAR 345 kV Cap bank, laid out as breaker and a half configuration. Construct four single circuit lines ~0.1 miles, between Bermuda station and the customer; utilizing 2-bundle ACSR Drake 795 (26/7) conductor SE 1800 MVA. Reason For Update: As part of further engineering reviews it was determined that the previously proposed capacitor bank at Bermuda would be more efficiently accommodated at Curleys station. The scope update adds the 2nd capacitor at Curleys and removes it from the scope at Bermuda. | Customer Service |  |  |  | 2025-09-12 |  |  | EP |  | 0 |  | 58.3 |  | 58.3 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH032 |  | s3442.11 | Fiesta 138 kV: Cut into the Corridor – Green Chapel 138 kV circuit and extend ~ 0.75 miles of new double circuit line, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 1118 MVA , to the greenfield Fiesta station with (10) 80 kA, 4000 A breakers laid out as breaker and a half for future expansion to 6 strings. Construct 4 - 138 kV tie lines to the customers dead end structures ~0.05 miles utilizing ACSR Drake 795 (26/7) conductor SE 360 MVA. | Customer Service |  |  |  | 2026-01-02 |  |  | EP |  | 0 |  | 22.3 |  | 22.3 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH040 |  | s3442.12 | Anguin – Rockhopper 138 kV: Reconfigure existing Anguin station and install (10) 138 kV, 4000A, 80 kA circuit breakers to feed customer stations at Penguin and QTS North. Build out strings G & H and construct a new greenfield ~0.6 miles double circuit line to customer’s Rockhopper station. Install (2) 69.1 MVAR cap banks at Anguin station | Customer Service |  |  |  | 2024-02-20 |  |  | EP |  | 0 |  | 13.2 |  | 13.2 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH044 |  | s3442.13 | Tasjan 138 kV: Cut into the Innovation – Green Chapel 138 kV circuit #1 and extend ~ 0.75 miles of new double circuit line, utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor, SE rating 1123 MVA, to the greenfield Tasjan station with (4) 80 kA, 4000 A breakers laid out 4-CB ring bus. Construct (2) 138 kV tie lines to the customers dead end structures ~0.05 miles utilizing ACSR Drake 795 (26/7) conductor SE 360 MVA. | Customer Service |  |  |  | 2025-11-19 |  |  | EP |  | 0 |  | 18.95 |  | 18.95 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH052 |  | s3442.14 | Anguin – Chinstrap 138 kV: Extend the 138 kV double circuit line to Rockhopper by ~0.22 miles to the new Chinstrap (customer) station. | Customer Service |  |  |  | 2024-04-04 |  |  | EP |  | 0 |  | 1.01 |  | 1.01 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH063 |  | s3442.15 | Anguin – NBY-6A 138 kV: Install (3) 138 kV, 4000A, 80 kA circuit breakers and construct a new greenfield ~0.9 miles double circuit line to customer’s new NBY-6A station. | Customer Service |  |  |  | 2025-01-31 |  |  | EP |  | 0 |  | 6.92 |  | 6.92 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.16 | Corridor – Vassell 345 kV #1 & #2 Circuits Sag Re-rate: Replace two structures to mitigate sag issues on the line in order to allow the line to operate to its conductor’s designed maximum operating temperature. | Customer Service |  |  |  | 2025-10-14 |  |  | EP |  | 0 |  | 1.88 |  | 1.88 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.17 | Kiber Station 138 kV: Cut-into Green Chapel – Corridor 138 kV circuit to a new Kiber station with (8 3) 80 kA 138 kV circuit breakers laid out in a breaker and a half arrangement to install a 300 2x150 MVAR STATCOM to support the significant amount of load added to the area. Reason For Update: As part of further engineering analysis it was determined that in order to be able to physically accommodate the line exits along with two feeds to the STATCOM when taking into account future needs at the station that a total of 8 138 kV breakers would need to be installed initially. | Customer Service |  |  |  | 2027-10-05 |  |  | EP |  | 0 |  | 35 |  | 35 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.18 | Green Chapel Cap Banks 138 kV: Upgrade proposed cap banks at Green Chapel station from (2) 69.1 MVAR to (2) 115.2 MVAR. | Customer Service |  |  |  | 2026-10-02 |  |  | EP |  | 0 |  | 3.6 |  | 3.6 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.19 | Corridor 138 kV: Replace (12) 63 kA circuit breakers & cap breakers with 80 kA circuit breakers to improve interrupting capabilities as a result of the new sources in the area. | Customer Service |  |  |  | 2025-06-01 |  |  | EP |  | 0 |  | 12.6 |  | 12.6 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.20 | Babbitt 138 kV: Replace (2) 63 kA bus-tie circuit breakers with 80 kA circuit breakers to improve interrupting capabilities as a result of the new sources in the area. | Customer Service |  |  |  | 2026-02-17 |  |  | EP |  | 0 |  | 2.15 |  | 2.15 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.21 | Jug Street: Replace CB-C which is an existing 40 kA breaker with a 4000A 80kA 138 kV breaker to address interrupting capability concerns related to the introduction of the new 345 kV source at Innovation. | Customer Service |  |  |  | 2025-04-08 |  |  | EP |  | 0 |  | 0.8 |  | 0.8 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.22 | Anchor Hocking – Lancaster 69 kV line Rebuild: Rebuild ~1.16 miles of 69 kV line utilizing ACSR Dove 556.5 (26/7) conductor, SE 142 MVA. As a result of the new customer interconnections in the area, this line will overload under certain N-1-1 scenarios. | Customer Service |  |  |  | 2026-06-29 |  |  | EP |  | 0 |  | 2.5 |  | 2.5 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.23 | Newark Center 138 kV: Install high and low side sectionalizing on the 138/69 kV transformer to address overloading of 69 kV lines in the area related to the new customer interconnections under certain N-1-1 scenarios. | Customer Service |  |  |  | 2027-05-03 |  |  | EP |  | 0 |  | 2.5 |  | 2.5 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.24 | Fremont – West Fremont Sag re-rate 138 kV: Sag re-rate the 138 kV circuit & upgrade 1200 A switches at Fremont to address a Generation deliverability violation related to the new customer interconnections in the area. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 2 |  | 2 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.25 | Fremont – Fremont Center Sag re-rate 138 kV: Sag re-rate the 138 kV circuit to address a Generation deliverability violation related to the new customer interconnections in the area. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 1.5 |  | 1.5 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.26 | Dumont 765 kV: Replace 3000 A circuit breaker at Dumont to address a generation deliverability violation on the Dumont – Sorenson 765 kV branch related to the new customer interconnections in the area. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 4 |  | 4 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.27 | Vassell – Green Chapel 345 kV line: Install approximately 12.5-mile long 345 kV transmission between Vassell and Green Chapel stations to mitigate overloading on multiple transmission facilities including other 345 kV transmission lines and 345-138 kV transformers. | Customer Service |  |  |  | 2026-04-01 |  |  | EP |  | 0 |  | 75 |  | 75 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.28 | Vassell – Curleys 345 kV line: Install approximately 12.5-mile long 345 kV transmission between Vassell and Curleys stations to mitigate overloading on multiple transmission facilities including other 345 kV transmission lines and 345-138 kV transformers. | Customer Service |  |  |  | 2026-12-01 |  |  | EP |  | 0 |  | 75 |  | 75 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.29 | Vassell 765 & 345 kV stations: Add 3-345 kV breakers to connect new lines to Curleys and Green Chapel. | Customer Service |  |  |  | 2026-04-01 |  |  | EP |  | 0 |  | 10 |  | 10 | 2023-12-05 |  |  |  | FALSE
AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 |  | s3442.30 | Green Chapel 345/138 kV station: Install two 675 MVA, 345/138 kV transformers to connect the new Vassell – Green Chapel 345 kV line to 138 kV system and to mitigate overloading on the other 345/138 kV transformers in the system. | Customer Service |  |  |  | 2026-04-01 |  |  | EP |  | 0 |  | 39.2 |  | 39.2 | 2023-12-05 |  |  |  | FALSE
AEP-2023-OH048 |  | s3445.1 | Giles station 138kV: Establish a new three breaker ring bus station named Giles using 3000A 40kA circuit breakers. | Customer Service |  |  |  | 2025-10-01 |  |  | EP |  | 0 |  | 3.88 |  | 3.88 | 2024-02-16 |  |  |  | FALSE
AEP-2023-OH048 |  | s3445.2 | Clinton- Huntley- Karl 138kV Circuit: Cut into the existing Clinton - Huntley - Karl 138kV for the Giles Extension line to tap into. | Customer Service |  |  |  | 2025-10-01 |  |  | EP |  | 0 |  | 0.79 |  | 0.79 | 2024-02-16 |  |  |  | FALSE
AEP-2023-OH048 |  | s3445.3 | Giles 138kV Extension: Construct a new 0.1 mile double circuit in and out line from the Clinton- Huntley- Karl 138kV Circuit to the new Giles station. | Customer Service |  |  |  | 2025-10-01 |  |  | EP |  | 0 |  | 0.56 |  | 0.56 | 2024-02-16 |  |  |  | FALSE
AEP-2023-OH048 |  | s3445.4 | Giles 138kV Extension: Remote end relay upgrades at Scherers Switch, Huntley and Blendon stations. | Customer Service |  |  |  | 2025-10-01 |  |  | EP |  | 0 |  | 0.07 |  | 0.07 | 2024-02-16 |  |  |  | FALSE
AEP-2021-OH050 |  | s3446.1 | Rebuild on the existing site with 9- 138kV 63kA 3000A breakers and utilizing one of the original breakers that is in good health to create a ten-breaker ring bus. Add a 28.8 MVAR 138kV Cap Bank. Construct a greenfield 40kV yard with two new 50MVA 138/40kV transformers to support the three 40kV customers served from the station. Use existing breaker 16 and 22 on the low-side of the transformers. Replace breakers 17 and 10 with existing breakers 15 and 21 which are in good health. Install a new DICM and remove the existing control house. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  |  | EP |  | 0 |  | 35.38 |  | 35.38 | 2024-01-19 |  |  |  | FALSE
AEP-2021-OH050 |  | s3446.2 | As part of the station reconfiguration the double circuit 138 kV line from Marion to LSII and Harrison will be rerouted into the new 138kV yard with a new 0.15-mile extension using ACSR Drake 795 (26/7) conductor (SE 360 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  |  | EP |  | 0 |  | 1.14 |  | 1.14 | 2024-01-19 |  |  |  | FALSE
AEP-2021-OH050 |  | s3446.3 | reroute the existing 40 kV service (Royal Building Products) T-line into the new 40 kV yard with a new 0.24 miles extension using ACSR Dove 556.5 (26/7) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  |  | EP |  | 0 |  | 0.9 |  | 0.9 | 2024-01-19 |  |  |  | FALSE
AEP-2021-OH050 |  | s3446.4 | reroute the existing 40 kV service (ITC Manufacturing) T line into the new 40 kV yard with a new 0.19-mile extension using ACSR Dove 556.5 (26/7) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  |  | EP |  | 0 |  | 0.93 |  | 0.93 | 2024-01-19 |  |  |  | FALSE
AEP-2021-OH050 |  | s3446.5 | Construct a greenfield ~0.15-mile single circuit line to Columbus Auto Shredding POI using ACSR Dove 556.5 (26/7) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  |  | EP |  | 0 |  | 0.92 |  | 0.92 | 2024-01-19 |  |  |  | FALSE
AEP-2021-OH050 |  | s3446.6 | Remote end work will be performed at Mound, Harrison, and LSII stations to coordinate with the work at Marion Road. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  |  | EP |  | 0 |  | 0.89 |  | 0.89 | 2024-01-19 |  |  |  | FALSE

## Dropdowns (hidden)
Status
EP
UC
On Hold
IS

## output (hidden)
Upgrade ID | TO ID Number | Projected In Service Date | Actual In Service Date | Status | Percent Complete (%) | Cost Estimate ($M) | TO Project Manager | eDart Ticket No | IC Notes
b2597 |  | 2027-03-12
b2598
b2604.1
b2604.2 |  |  |  |  | 50
b2604.3 |  |  |  |  | 75
b2604.4 |  |  |  |  | 75
b2604.5 |  |  |  |  | 50
b2604.6 |  |  |  |  | 50
b2604.7 |  |  |  |  | 50
b2604.8 |  |  |  |  | 50
b2604.9 |  | 2028-06-02 |  |  | 50
b2604.10 |  | 2028-06-02 |  |  | 50
b2604.11 |  | 2028-06-02 |  |  | 50
b2753.7
b2760
b2793
b2938
b3037
b3085
b3150
b3151.7
b3151.8
b3151.9
b3151.15
b3160.1
b3160.2
b3160.3
b3160.4
b3160.5
b3160.6
b3160.7
b3208
b3243
b3244
b3248
b3249
b3253
b3258
b3259
b3269
b3270
b3270.1
b3271
b3272
b3273.1
b3273.2
b3273.3
b3273.4
b3274
b3275.1 |  |  | 2025-05-08 | IS | 100
b3275.2
b3275.3 | P21565008 |  | 2025-03-06 | IS | 100
b3275.4 |  |  | 2025-03-06 | IS | 100
b3275.5 |  |  | 2025-05-08 | IS | 100
b3275.6
b3275.7 | P19269001 | 2025-11-26 |  |  | 75
b3276.1 |  | 2030-12-31
b3276.2 |  | 2030-12-31
b3276.3 |  | 2026-07-16
b3278.1 |  | 2031-06-23 |  | EP | 25
b3278.2 |  | 2032-10-19 |  |  | 25
b3278.3 |  |  |  |  | 25
b3279 |  |  |  |  | 10
b3280 |  | 2026-10-15 |  |  | 50
b3281 |  | 2025-11-05 |  | UC | 75
b3282.1 |  | 2029-03-21 |  |  | 10
b3282.2 |  | 2029-03-21 |  |  | 10
b3282.3 |  | 2029-03-21 |  |  | 10
b3282.4 |  | 2029-03-21 |  |  | 10
b3284 |  | 2027-09-10 |  | EP | 50
b3285 |  | 2026-02-02 |  |  | 75
b3288.1 |  | 2027-05-07 |  | UC | 75
b3288.2 |  | 2027-11-08 |  | UC | 75
b3288.3 |  | 2027-05-07 |  | UC | 75
b3288.4 |  | 2027-11-12 |  | UC | 75
b3288.5 |  | 2027-11-08 |  | UC | 75
b3289.1 |  | 2027-08-18 |  | EP | 10
b3289.2 |  |  |  |  | 50
b3290.1 |  | 2027-06-07 |  |  | 50
b3290.2 |  | 2027-02-19 |  |  | 50
b3290.3 |  | 2027-06-07 |  |  | 50
b3290.4 |  | 2027-06-18 |  |  | 50
b3291 |  |  |  |  | 50
b3292 |  | 2028-12-13 |  |  | 25
b3294 |  | 2027-08-05 |  |  | 10
b3296 |  | 2027-08-30 |  |  | 25
b3297.1 |  | 2026-07-22 |  |  | 10
b3297.2 |  | 2027-05-08 |  |  | 10
b3297.3 |  | 2026-07-22 |  |  | 10
b3298 |  | 2028-04-10 |  |  | 10
b3298.1 |  | 2026-05-19 |  |  | 10
b3307 |  | 2025-11-21 |  |  | 75
b3308 |  | 2028-04-10 |  |  | 10
b3309 |  |  |  |  | 50
b3310.1 |  |  | 2025-05-30 | IS | 100
b3310.2 |  |  | 2025-06-05 | IS | 100
b3312 |  | 2026-01-21 |  | UC | 75
b3313 |  | 2026-10-26 |  |  | 50
b3314.1 |  |  |  |  | 50
b3314.2 |  |  |  |  | 50
b3315 |  |  | 2025-03-20 | IS | 100
b3337 |  | 2025-12-09 |  |  | 50
b3338 |  | 2026-06-01 |  |  | 50
b3339 |  | 2025-10-22 |  |  | 50
b3344.1 |  |  |  |  | 50
b3344.2 |  |  |  |  | 50
b3345.1 |  | 2027-10-05 |  |  | 25
b3345.2 |  | 2027-10-05 |  |  | 25
b3346.1 |  | 2026-10-19 |  |  | 25
b3346.2 |  | 2027-06-16 |  |  | 25
b3347.1 |  | 2031-12-17 |  |  | 10
b3347.2 |  | 2030-05-10 |  |  | 10
b3347.3 |  | 2030-11-22 |  |  | 10
b3347.4 |  | 2031-06-11 |  |  | 10
b3347.5 |  | 2031-12-17 |  |  | 10
b3347.6 |  | 2029-12-19 |  |  | 10
b3347.7 |  | 2031-06-11 |  |  | 10
b3348.1 |  | 2028-02-03 |  |  | 25
b3348.2 |  | 2027-07-19 |  |  | 25
b3348.3 |  | 2028-02-03 |  |  | 25
b3348.4 |  | 2027-04-26 |  |  | 25
b3348.5 |  | 2027-07-19 |  |  | 25
b3348.6 |  | 2028-02-13 |  |  | 25
b3349 |  | 2026-12-02 |  | UC | 75
b3350.1 |  | 2026-12-02 |  | UC | 75
b3350.2 |  | 2026-12-23 |  |  | 50
b3351 | no project yet, please rmv BPID
b3352 |  |  | 2025-04-15 | IS | 100
b3353.1 |  | 2027-12-31 |  |  | 30
b3353.2 |  | 2027-12-31 |  |  | 30
b3353.3 |  | 2027-12-31 |  |  | 30
b3353.4 |  | 2027-12-31 |  |  | 30
b3353.5 |  | 2027-12-31 |  |  | 30
b3353.6 |  | 2027-12-31 |  |  | 30
b3359 |  | 2027-01-06 |  |  | 50
b3360 |  | 2026-11-20 |  |  | 50
b3361 |  |  |  |  | 50
b3362 |  | 2026-10-20 |  |  | 50
b3722 |  | 2028-03-29 |  |  | 10
b3723 |  |  | 2025-04-14 | IS | 100
b3724 |  | 2027-08-18 |  |  | 10
b3731 |  | 2028-08-14 |  |  | 25
b3732 |  | 2026-05-15 |  |  | 50
b3733 |  | 2027-06-01 |  |  | 10
b3734 |  | 2028-02-23 |  |  | 25
b3735 |  | 2025-12-10 |  | UC | 75
b3736.1 |  | 2028-03-16 |  |  | 50
b3736.2 |  | 2028-05-18 |  |  | 50
b3736.3 |  | 2028-03-16 |  |  | 50
b3736.4 |  | 2030-08-01 |  |  | 10
b3736.5 |  | 2028-11-08 |  |  | 50
b3736.6 |  | 2028-03-16 |  |  | 50
b3736.7 |  | 2028-09-01 |  |  | 50
b3736.8 |  | 2028-03-16 |  |  | 50
b3736.9 |  | 2028-03-16 |  |  | 50
b3736.10 |  | 2028-09-01 |  |  | 50
b3736.11 |  | 2029-11-15 |  |  | 10
b3736.12 |  | 2028-05-18 |  |  | 50
b3736.13 |  | 2029-11-15 |  |  | 10
b3736.14 |  | 2029-11-15 |  |  | 10
b3736.15 |  | 2028-03-16 |  |  | 50
b3736.16 |  | 2028-03-16 |  |  | 50
b3736.17 |  | 2028-03-23 |  |  | 50
b3736.18 |  | 2028-09-01 |  |  | 50
b3763 |  |  | 2025-04-08 | IS | 100
b3764 |  | 2025-12-09 |  |  | 50
b3766.1 |  | 2027-06-17 |  |  | 25
b3766.2 |  | 2027-06-17 |  |  | 25
b3766.3 |  | 2027-06-17 |  |  | 25
b3775.6 |  |  |  |  | 50
b3775.7 |  |  |  |  | 50
b3775.10 |  |  |  |  | 10
b3775.11 |  |  |  |  | 50
b3784.1 |  |  |  |  | 10
b3785.1 |  | 2026-10-07 |  |  | 25
b3786.1 |  | 2029-11-16 |  |  | 10
b3787.1
b3788.1 |  | 2027-11-18 |  |  | 10
b3790.0 |  | 2026-11-19 |  |  | 50
b3800.100 |  |  |  |  | 10
b3800.121
b3836.1 |  |  |  |  | 10
b3837.1 |  | 2028-11-06 |  |  | 10
b3838.1 |  |  |  |  | 10
b3839.1
b3843.1 |  |  |  |  | 10
b3847.1 |  |  |  |  | 50
b3847.2 |  | 2028-06-19 |  |  | 10
b3847.3 |  |  |  |  | 50
b3851.1 |  |  |  |  | 10
b3851.2 |  |  |  |  | 10
b3851.3 |  |  |  |  | 10
b3851.4 |  |  |  |  | 10
b3852.1 |  |  |  | UC | 75
b3852.2
b3872.1
b3873.1
b3875.1
b3876.1
b3877.1
b3877.2
b3878.1
b3879.1
b3879.2
b3880.1
b3882.1
b3883.1
b3884.1
b3885.1
b3886.1
b3887.1
b3888.1
b3889.1
b3890.1
b3891.1
b3892.1
b3894.1
b3895.1
b3896.1
b3897.1
b3898.1
b3911.1
b3912.1
b3913.1
b3913.2
b3919.1
b3919.2
b3919.3
b3919.4
b3919.5
b3919.6
b3919.7
b3919.8
b3919.9
b3919.10
b4000.1
b4000.200
b4000.201
b4000.202
b4000.203
b4000.204
b4000.205
b4000.206
b4000.207
b4000.208
b4000.209
b4000.210
b4000.211
b4000.251
b4000.252
b4000.355
b4000.359
s1297 |  | 2025-07-17
s1297.5 |  | 2025-07-17
s1377.3 |  | 2026-05-22
s1377.4 |  | 2026-02-19
s1377.5 |  | 2026-03-16
s1377.7
s1377.8
s1377.9 |  | 2026-03-16
s1377.10 |  | 2026-03-16
s1414 |  | 2026-01-20
s1414.1
s1414.2 |  | 2026-01-20
s1414.3 |  | 2025-10-21
s1414.4 |  | 2025-10-21
s1414.5 |  | 2025-10-21
s1414.6 |  | 2026-01-20
s1431
s1432.1
s1493.2 |  | 2027-04-29
s1493.3 |  | 2027-01-07 |  | EP
s1590
s1606.3 |  | 2028-08-14
s1611.3 |  | 2025-12-19
s1622.1 |  |  | 2025-02-21 | IS | 100
s1622.3 |  | 2026-09-18
s1687.2
s1687.3
s1687.4
s1687.5
s1687.6
s1687.8
s1687.10
s1692.1 |  | 2031-01-23 |  | EP
s1692.2 |  | 2030-10-22 |  | EP
s1851 |  | 2027-11-17 |  | EP
s1851.1 |  | 2028-03-15 |  |  | 10
s1854.3 |  | 2027-11-30 |  |  | 50
s2000.2 |  |  | 2025-06-03 | IS | 100
s2012.1 |  |  | 2023-10-27 | IS | 100
s2013.2 |  | 2025-09-22
s2013.5 |  | 2025-10-20
s2014 |  |  | 2024-05-02 | IS | 100
s2017.1 |  | 2025-11-21
s2017.2
s2060.11
s2062.1 |  | 2028-08-14
s2062.2 |  | 2026-06-05
s2062.3 |  | 2026-02-12
s2062.4 |  | 2025-12-03
s2090.1 |  | 2026-09-18
s2090.2 |  | 2026-11-13
s2098.4 |  | 2026-02-27
s2098.6 |  | 2026-04-24
s2098.11 |  | 2026-04-24
s2098.12 |  | 2028-07-18
s2145.1
s2146.1 |  | 2026-07-13
s2146.2 |  | 2025-10-06
s2147.3
s2149.1 |  | 2027-11-29
s2149.2
s2149.3
s2149.4
s2149.5
s2149.6
s2149.7
s2149.8 |  | 2028-10-19
s2149.9 |  | 2028-10-19
s2149.10 |  | 2028-10-19
s2149.11 |  | 2028-10-19
s2149.12 |  | 2028-10-19
s2149.13 |  | 2028-10-19
s2149.14 |  | 2028-10-19
s2149.15 |  | 2028-10-19
s2149.16 |  | 2028-10-19
s2149.17 |  | 2028-10-19
s2149.18 |  | 2028-10-19
s2149.19 |  | 2028-10-19
s2149.20 |  | 2028-10-19
s2149.21 |  | 2028-10-19
s2149.22 |  | 2028-10-19
s2149.23 |  | 2029-04-27
s2149.24 |  | 2029-04-27
s2149.25 |  | 2029-04-27
s2149.26 |  | 2029-04-27
s2149.27 |  | 2029-05-17
s2149.28 |  | 2029-04-06
s2149.29 |  | 2029-03-22
s2149.30 |  | 2029-02-23
s2149.31 |  | 2029-02-23
s2149.32 |  | 2029-02-23
s2149.33 |  | 2027-01-20
s2153.1 |  | 2031-12-01 |  | EP | 25
s2153.2 |  | 2029-11-05
s2153.3 |  | 2031-03-28
s2153.4 |  | 2028-07-26
s2153.5 |  | 2029-08-17
s2153.6 |  | 2029-11-15
s2153.7 |  | 2029-08-17
s2153.8 |  | 2028-03-23
s2153.9 |  | 2028-08-18
s2154.3 |  | 2026-07-06 |  |  | 50
s2159 |  | 2026-05-29 |  |  | 50
s2159.1 |  | 2026-05-29 |  |  | 50
s2159.2 |  | 2026-02-24 |  | EP
s2159.3 |  | 2025-11-21 |  |  | 75
s2160 |  | 2026-03-31 |  |  | 75
s2165.1 |  | 2027-12-16 |  |  | 75
s2167 |  | 2025-12-05 |  | UC | 75
s2167.1 |  | 2025-09-01 |  | UC | 75
s2167.2
s2167.3 |  | 2027-01-18 |  | EP
s2167.4
s2167.5 |  | 2028-06-05
s2167.6
s2167.7
s2167.8 |  | 2028-06-05
s2167.9 |  | 2029-10-16
s2167.10
s2167.11 |  | 2029-10-16
s2177.1
s2177.2 |  | 2026-05-04
s2177.3
s2177.5
s2177.6 |  | 2026-02-10
s2178.2
s2179.1 |  | 2032-12-14 |  | EP | 25
s2179.2 |  | 2031-06-27
s2179.4 |  | 2029-11-15
s2179.6 |  | 2030-06-20
s2179.7 |  | 2027-12-09
s2179.9 |  | 2029-12-21
s2179.10 |  | 2026-12-18
s2179.11 |  | 2029-12-21
s2179.12 |  | 2028-03-10
s2179.13 |  | 2032-12-17
s2179.14 |  | 2031-06-27
s2179.15 |  | 2029-12-27
s2179.16 |  | 2029-12-27
s2179.17
s2179.18 |  | 2028-12-15
s2179.19 |  | 2030-02-15
s2179.20 |  | 2029-12-19
s2179.21 |  | 2030-06-12
s2179.22 |  | 2029-12-19
s2179.24 |  | 2029-11-15
s2179.25 |  | 2032-12-14
s2179.26
s2179.27
s2179.28 |  | 2029-12-18
s2179.29 |  | 2027-12-09
s2179.30 |  | 2028-12-13
s2179.31 |  | 2029-11-29
s2179.32
s2179.33 |  | 2029-03-01
s2179.34 |  | 2027-11-11
s2179.35 |  | 2027-12-10
s2179.36 |  | 2029-12-21
s2179.37 |  | 2030-11-13
s2179.38 |  | 2030-11-14
s2179.39 |  | 2030-06-20
s2179.40 |  | 2028-12-13
s2179.41 |  | 2031-01-13
s2179.42 |  | 2029-12-20
s2179.43 |  | 2029-12-28
s2184.1
s2184.2
s2184.3 |  | 2025-07-30 |  | UC | 75
s2184.4 |  | 2025-07-30 |  |  | 75
s2184.5
s2184.6 |  | 2025-12-11
s2185 |  | 2029-07-03
s2188.1 |  | 2027-05-12
s2188.2 |  | 2027-05-12
s2188.3 |  | 2027-10-13
s2188.4 |  | 2027-09-17
s2188.5 |  | 2027-10-13
s2188.6 |  | 2027-05-12
s2188.7 |  | 2027-05-12
s2188.8 |  | 2027-06-24
s2188.9 |  | 2027-11-12
s2188.11 |  | 2027-09-23
s2189 |  | 2028-06-16
s2190 |  | 2026-12-10
s2197 |  | 2025-12-19
s2199.1 |  | 2029-03-21
s2200.1
s2200.2
s2200.3
s2201.1
s2201.2
s2213.4 |  | 2028-01-04
s2213.5 |  | 2028-01-04
s2213.6 |  | 2028-05-05
s2215.1 |  | 2027-06-07
s2215.2 |  | 2027-06-07
s2215.3 |  | 2027-02-19
s2215.4 |  | 2027-06-18
s2215.5 |  | 2028-07-31
s2215.6 |  | 2028-03-10
s2215.7 |  | 2027-08-05
s2215.8 |  | 2027-06-07
s2215.9 |  | 2027-02-19
s2215.10 |  | 2027-06-18
s2215.11 |  | 2026-07-27
s2215.12 |  | 2027-01-07
s2215.13 |  | 2027-07-16
s2216.1 |  | 2028-09-22
s2216.2 |  | 2029-08-15
s2216.3 |  | 2028-09-29
s2216.4 |  | 2028-09-29
s2216.5 |  | 2028-09-29
s2216.6 |  | 2028-09-29
s2216.7 |  | 2028-09-29
s2216.8 |  | 2028-09-29
s2219 |  | 2025-11-21 |  | UC | 75
s2221.1 |  | 2028-04-14
s2221.2 |  | 2028-04-14
s2221.3 |  | 2028-04-14
s2221.6 |  | 2028-04-14
s2222.1 |  | 2029-08-28
s2222.2 |  | 2025-09-30
s2224.1 |  | 2029-09-18
s2224.2 |  | 2030-10-31
s2224.6 |  | 2029-12-20
s2224.8 |  | 2029-08-28
s2224.9 |  | 2029-06-20
s2225.1 |  | 2025-11-20
s2225.2 |  | 2025-11-20
s2225.4 |  | 2025-11-20
s2225.7 |  | 2030-10-01
s2226.1 |  | 2031-02-13
s2226.2 |  | 2031-02-13
s2226.3
s2250 |  | 2036-09-02
s2251.2 |  |  | 2025-07-03 | IS | 100
s2251.3
s2251.4 |  | 2027-10-07
s2270.8 |  | 2026-05-12 |  | UC | 75
s2270.9 |  | 2026-05-12 |  | UC | 75
s2270.10 |  | 2028-12-20
s2272.1 |  | 2028-05-17
s2272.3 |  | 2030-10-24
s2273.1
s2273.2
s2273.3
s2273.5
s2273.10
s2274.1 |  | 2028-12-07
s2274.2 |  | 2028-07-31
s2282.1 |  | 2027-09-01 |  | UC | 75
s2282.2 |  | 2027-08-05
s2282.3 |  |  | 2025-07-13 | IS | 100
s2282.4 |  | 2027-12-15 |  | UC | 75
s2283.1 |  | 2028-11-20
s2283.2 |  | 2028-11-20
s2342.1
s2344.2 |  | 2028-04-03
s2345.2 |  | 2027-06-14
s2346 |  |  |  | UC | 75
s2348.4 |  | 2025-10-09
s2348.5 |  | 2025-10-09
s2392.2
s2393.1 |  | 2028-10-24
s2393.2 |  | 2027-10-14
s2393.3 |  | 2027-04-08
s2393.4 |  | 2028-09-12
s2393.5 |  | 2026-03-10
s2394.1 |  | 2028-12-27
s2394.3 |  | 2027-05-26
s2394.4 |  | 2027-07-30
s2394.5 |  | 2027-01-29
s2395.1
s2395.5 |  | 2026-06-04
s2395.6 |  | 2026-06-04
s2395.7 |  | 2025-12-18
s2395.8 |  | 2026-06-04
s2395.9 |  | 2025-12-18
s2395.10 |  | 2026-02-03
s2395.11 |  |  | 2025-05-29 | IS | 100
s2395.12 |  | 2025-12-18
s2395.13 |  |  | 2025-05-19 | IS | 100
s2395.14 |  | 2026-06-09
s2395.15 |  | 2027-03-08
s2395.21 |  | 2026-12-09
s2395.22 |  | 2025-09-02
s2397.1
s2397.2
s2397.3
s2397.4
s2397.5
s2398.7
s2401.1
s2401.2
s2401.3
s2401.4
s2401.5
s2408.3
s2408.4
s2426.1
s2426.2
s2426.3
s2426.4
s2426.5
s2426.6
s2426.7
s2426.8
s2426.9
s2426.10
s2428.4
s2428.5
s2428.7
s2430.2
s2430.3
s2430.5
s2430.7
s2430.8
s2430.9
s2431.1
s2431.2
s2431.3
s2431.4
s2431.5
s2431.6
s2432.1
s2432.2
s2432.3
s2432.4
s2432.5
s2432.6
s2432.7
s2432.8
s2432.9
s2432.10
s2432.11
s2432.12
s2432.13
s2432.14
s2432.15
s2432.16
s2433.3
s2434.1
s2434.2
s2434.3
s2435.1 | P17115001, P18220006 |  | 2024-07-18 | IS | 100
s2435.2
s2436.2
s2436.3
s2436.4
s2436.5
s2436.6
s2436.9
s2436.10
s2436.11
s2436.12
s2438
s2439
s2440.1
s2440.2
s2440.3
s2440.4
s2444.1
s2444.2 |  |  | 2025-05-22 | IS | 100
s2444.3 |  |  | 2025-05-22 | IS | 100
s2444.4 |  |  | 2025-05-22 | IS | 100
s2444.5
s2444.6
s2444.7
s2444.8
s2444.9
s2446.1
s2446.2
s2446.3
s2446.4
s2446.5
s2446.6
s2446.7
s2464
s2465.1
s2465.2
s2465.3
s2465.4
s2465.5
s2465.6
s2465.7
s2465.8
s2465.9
s2465.10
s2465.11
s2465.12
s2465.13
s2465.14
s2469.1
s2469.2
s2469.3
s2469.4
s2469.5
s2469.6
s2469.7
s2469.8
s2469.9
s2469.10
s2469.11
s2472
s2510
s2522.1
s2522.2
s2523.1
s2523.2
s2524.1
s2524.2
s2524.4 |  |  | 2025-05-29 | IS | 100
s2524.5
s2525.1
s2525.2
s2525.3
s2526.2 |  |  | 2022-11-18 | IS | 100
s2526.3
s2527.7
s2534.1
s2534.4
s2534.5
s2534.6
s2534.7
s2534.8
s2534.9
s2534.10
s2534.11
s2534.12
s2534.13
s2534.14
s2534.15
s2534.16
s2534.17
s2534.18
s2534.19
s2570.1
s2570.2
s2570.3
s2570.4
s2570.5
s2571.1
s2571.2 |  | 2025-12-19 |  | UC | 75
s2571.3
s2572.1
s2572.2
s2572.3
s2572.4
s2574
s2575.1
s2575.2
s2575.3
s2575.4
s2575.5
s2575.6
s2575.7
s2575.8
s2575.9
s2575.10
s2576.1
s2576.2
s2576.3
s2577.1
s2577.2
s2577.3
s2577.4
s2577.5
s2578.2 |  |  | 2023-07-26 | IS | 100
s2578.4 |  |  | 2023-07-26 | IS | 100
s2578.5 |  |  | 2023-07-26 | IS | 100
s2584.1
s2584.2
s2584.6
s2584.7 |  |  | 2025-02-26 | IS | 100
s2584.8
s2584.9 |  |  | 2024-11-14 | IS | 100
s2584.10 |  |  | 2024-11-15 | IS | 100
s2584.11 |  |  | 2024-11-14 | IS | 100
s2584.12 |  |  | 2024-12-20 | IS | 100
s2584.13 |  |  | 2024-11-14 | IS | 100
s2632.1
s2632.2
s2632.3
s2632.4
s2632.5
s2632.6
s2632.7
s2634.1
s2634.2
s2634.3
s2634.4
s2634.5
s2634.6
s2634.7
s2634.8
s2634.9
s2635.1
s2635.2
s2635.3
s2637.1
s2637.2
s2637.3
s2637.4
s2637.5
s2637.6
s2638.1
s2638.2
s2638.3
s2638.4
s2638.5
s2638.6
s2639.1 |  |  | 2025-04-01 | IS | 100
s2639.2 |  |  | 2025-04-01 | IS | 100
s2639.3 |  |  | 2025-04-01 | IS | 100
s2639.4 |  |  | 2025-04-01 | IS | 100
s2640.1 |  |  | 2024-12-30 | IS | 100
s2640.2 |  |  | 2024-12-19 | IS | 100
s2640.3 |  |  | 2024-12-19 | IS | 100
s2650.1
s2650.2
s2650.3
s2650.4
s2650.5 |  |  | 2025-03-20 | IS | 100
s2650.6
s2650.7 |  |  | 2025-03-20 | IS | 100
s2651.1
s2651.2
s2651.3
s2651.4
s2652
s2654.1
s2654.2
s2654.3
s2654.4
s2654.5
s2655.1
s2655.2
s2656.1
s2656.2
s2657.1
s2657.2
s2657.3
s2657.4
s2657.5
s2657.6
s2657.7
s2657.8
s2657.9
s2657.10
s2657.11
s2658
s2663.1 |  |  | 2025-01-16 | IS | 100
s2663.2 |  |  | 2025-01-16 | IS | 100
s2663.3
s2663.4 |  |  | 2025-01-16 | IS | 100
s2663.5
s2663.6
s2664
s2682.1
s2682.2
s2682.3
s2682.4
s2682.5
s2682.6
s2682.7
s2682.8
s2682.9
s2684
s2685.1
s2685.2
s2686 |  |  | 2025-01-16 | IS | 100
s2688.1
s2688.2
s2688.3
s2693.1
s2693.2
s2693.3
s2693.4
s2693.5
s2693.6
s2694 |  |  | 2024-12-19 | IS | 100
s2748.1
s2748.2
s2748.3
s2748.4
s2748.5
s2748.6
s2748.7
s2770.1
s2770.2
s2770.3
s2770.4
s2770.5
s2771.1
s2771.2
s2771.3
s2771.4
s2771.5
s2771.6
s2771.7
s2772
s2773.1
s2773.2
s2773.3
s2773.4
s2773.5
s2773.6
s2774.1
s2774.2
s2774.3
s2775.1
s2775.2
s2775.3
s2776
s2777
s2778.1
s2778.2
s2778.3
s2778.4
s2778.5
s2779
s2780.1
s2780.2
s2780.3
s2781.3
s2781.5 |  |  | 2025-02-05 | IS | 100
s2784.1
s2784.2
s2784.3
s2784.4
s2784.5
s2785.1
s2785.2
s2787.1
s2789.1 |  |  | 2024-11-15 | IS | 100
s2789.2 |  |  | 2024-11-15 | IS | 100
s2789.3 |  |  | 2024-11-15 | IS | 100
s2791.1
s2791.2
s2791.3
s2791.4
s2791.5
s2791.6
s2791.7
s2791.8
s2791.9
s2791.10
s2791.11
s2791.12
s2792.1
s2792.2
s2792.3
s2793.1
s2793.2 |  |  | 2024-12-10 | IS | 100
s2793.3
s2793.4
s2793.5
s2793.6
s2793.7 |  |  | 2025-06-09 | IS | 100
s2794.1 |  |  | 2025-03-12 | IS | 100
s2794.2
s2794.3
s2794.4 |  |  | 2025-03-12 | IS | 100
s2794.5
s2795.1
s2795.2
s2795.3
s2795.4
s2795.5
s2795.6
s2796.1
s2796.2
s2796.3
s2796.4
s2796.5
s2796.6
s2796.7
s2796.8
s2796.9
s2796.10
s2796.11
s2797.1
s2797.2
s2798 |  |  | 2024-11-07 | IS | 100
s2801.1
s2801.2
s2801.3
s2802.1
s2802.2
s2802.3
s2802.4
s2802.5
s2802.6
s2802.7
s2807.2
s2810
s2811
s2812.1
s2812.2
s2813.1
s2813.2
s2813.3
s2814.1
s2814.2
s2814.3
s2814.4 |  |  | 2025-06-19 | IS | 100
s2814.5
s2814.6
s2815.1
s2815.2
s2816.1
s2816.2
s2816.3
s2816.4
s2817.1
s2817.2
s2817.3
s2817.4
s2817.5
s2817.6
s2817.7
s2817.8
s2818.1
s2818.2
s2819.1
s2819.2
s2820.1
s2820.2
s2821
s2822.1
s2822.2
s2822.3
s2822.4
s2822.5
s2822.6
s2822.7
s2822.8 |  |  | 2024-08-05 | IS | 100
s2827.2
s2829.1
s2829.2
s2829.3
s2829.4
s2829.5
s2829.6
s2829.7
s2830.1
s2830.2
s2830.3
s2830.4
s2830.5
s2830.6
s2830.7
s2830.8
s2830.9
s2830.10
s2830.11
s2830.12
s2830.13
s2830.14
s2830.15
s2831.1
s2831.2
s2832.2
s2832.4
s2848
s2851
s2854.1
s2854.2
s2856
s2857.1
s2857.2 |  |  | 2025-03-13 | IS | 100
s2857.3 |  |  | 2025-03-13 | IS | 100
s2857.4
s2857.5
s2857.6
s2857.7
s2857.8
s2857.9
s2858
s2882.1
s2882.2
s2882.3
s2882.4
s2882.5
s2882.6
s2883.1
s2883.2
s2883.3
s2884.1
s2884.2
s2884.3
s2884.4
s2884.5
s2884.6
s2884.7
s2884.8
s2887.1
s2887.2
s2887.3
s2887.4
s2887.5
s2887.6
s2887.7
s2888
s2911.1
s2911.2
s2911.3
s2911.4
s2911.5
s2911.6
s2911.7
s2911.8
s2913.1
s2913.2
s2913.3
s2913.4
s2913.5
s2913.6
s2913.7
s2913.8
s2915.1
s2915.2
s2915.3
s2915.4
s2915.5
s2915.6
s2915.7
s2917.1
s2917.2
s2917.3
s2917.4
s2920.1
s2920.2
s2921
s2941
s2942.1
s2942.2
s2942.3
s2942.4
s2942.5
s2942.6
s2943
s2944
s2970
s2981.1
s2981.2
s2982.1
s2982.2
s2982.3
s2982.4
s2982.5
s2983.1
s2983.2
s2983.3
s2983.4
s2984.1
s2984.2
s2984.3
s2985.1
s2985.2
s2985.3
s2986.1
s2986.2
s3133.1
s3133.2
s3133.3
s3133.4
s3133.5
s3133.6
s3133.7
s3133.8
s3133.9
s3133.10
s3133.11
s3133.12
s3133.13
s3133.14
s3133.15
s3134.1
s3134.2
s3135.1
s3135.2
s3135.3
s3135.4
s3135.5
s3136.1
s3136.2
s3136.3
s3136.4
s3136.5
s3136.6
s3136.7
s3137.1
s3137.2 |  |  | 2024-12-12 | IS | 100
s3137.3 |  |  | 2024-12-12 | IS | 100
s3138.1
s3139.1
s3139.2
s3139.3
s3139.4
s3139.5
s3139.6
s3139.7
s3139.8
s3139.9
s3139.10
s3139.11
s3139.12
s3139.13
s3139.14
s3139.15
s3139.16
s3139.17
s3139.18
s3139.19
s3139.20
s3139.21
s3139.22
s3139.23
s3139.24
s3139.25
s3139.26
s3139.27
s3139.28
s3139.29
s3139.30
s3139.31
s3139.32
s3139.33
s3139.34
s3139.35
s3140.1
s3140.2
s3140.3
s3141.1
s3141.2
s3141.3
s3142.1
s3142.2
s3142.3
s3142.4
s3142.5
s3143.1
s3143.2
s3143.3
s3143.4
s3143.5 |  |  | 2024-12-16 | IS | 100
s3143.6
s3143.7
s3144.1
s3145.1
s3145.2
s3147.1
s3147.2
s3147.3
s3147.4
s3147.5
s3147.6
s3147.7
s3147.8
s3147.9
s3147.10
s3147.11
s3147.12
s3147.13
s3147.14
s3147.15
s3147.16
s3147.17
s3147.18 | P22012011
s3147.19
s3147.20
s3147.21
s3147.22
s3147.23
s3147.24
s3147.25
s3147.26
s3147.27
s3147.28
s3147.29
s3147.30
s3147.31
s3147.32
s3147.33
s3147.34
s3147.35
s3147.36
s3147.37
s3147.38
s3147.39
s3147.40
s3147.41
s3148.1
s3211.1
s3211.2
s3211.3
s3211.4
s3211.5
s3211.6
s3211.7
s3212.1
s3212.2
s3213.1
s3213.2
s3213.3
s3213.4
s3213.5
s3213.6
s3214.1
s3214.2
s3214.3
s3214.4
s3215.1
s3215.2
s3215.3
s3215.4
s3215.5
s3215.6
s3215.7
s3301.1
s3302.1 |  |  | 2025-04-24 | IS | 100
s3302.2 |  |  | 2025-04-24 | IS | 100
s3302.3
s3303.1
s3303.2
s3304.1
s3305.1 |  |  | 2025-02-28 | IS | 100
s3305.2 |  |  | 2025-02-28 | IS | 100
s3305.3 |  |  | 2025-02-28 | IS | 100
s3306.1
s3307.1
s3307.2
s3308.1
s3308.2
s3308.3
s3309.4
s3309.5
s3387.1
s3388.1 | P23029005 |  | 2024-11-04 | IS | 100
s3389.1
s3390.1
s3440.1
s3440.2
s3440.3
s3440.4
s3440.5
s3440.6
s3441.1
s3441.2
s3441.3
s3441.4
s3441.5
s3441.6
s3441.7
s3442.1
s3442.2
s3442.3
s3442.4
s3442.5
s3442.6
s3442.7
s3442.8
s3442.9
s3442.10
s3442.11
s3442.12
s3442.13
s3442.14
s3442.15
s3442.16
s3442.17
s3442.18
s3442.19
s3442.20
s3442.21
s3442.22
s3442.23
s3442.24
s3442.25
s3442.26
s3442.27
s3442.28
s3442.29
s3442.30
s3445.1
s3445.2
s3445.3
s3445.4
s3446.1
s3446.2
s3446.3
s3446.4
s3446.5
s3446.6

## data (hidden)
Upgrade Type | Transmission Owner | TO ID Number | Upgrade Id | Description | Driver | Deactivation Study | Required In Service Date | Revised In Service Date | Projected In Service Date | Actual In Service Date | Status | Percent Complete (%) | Cost Estimate ($M) | TEAC Cost ($M) | TEAC Date | TO Project Manager | eDart Ticket No | Impact Tie Line | Breaker Name | Breaker Before Capacity | Breaker After Capacity | Line Rating Name | Line Rating Before Rating (SN/SE/WN/WE) | Line Rating After Rating (SN/SE/WN/WE) | Transformer Name | Transformer High Before Rating (SN/SE/WN/WE) | Transformer High After Rating (SN/SE/WN/WE) | Transformer Low Before Rating (SN/SE/WN/WE) | Transformer Low After Rating (SN/SE/WN/WE) | Transformer Tertiary Before Rating (SN/SE/WN/WE) | Transformer Tertiary After Rating (SN/SE/WN/WE) | Transmission Line Name | Transmission Line Before Rating (SN/SE/WN/WE) | Transmission Line After Rating (SN/SE/WN/WE)
Baseline | AEP | P15082C28 | b2597 | Rebuild approximately 1 mi. section of Dragoon-Virgil Street 34.5 kV line between Dragoon and Dodge Tap switch and replace Dodge switch MOAB to increase thermal capability of Dragoon-Dodge Tap branch | TO Criteria Violation |  | 2019-06-01 |  | 2026-12-18 |  | EP | 50 | 2.15 | 2.154 | 2015-01-07 | Pm Cliff Vaughn/ Planner Joshua Smith |  | FALSE
Baseline | AEP | P15082C10, P15082C05, P15082C07 | b2598 | Rebuild approximately 1 mile section of the Kline-Virgil Street 34.5 kV line between Kline and Virgil Street tap. Replace MOAB switches at Beiger, risers at Kline, switches and bus at Virgil Street. | TO Criteria Violation |  | 2019-06-01 |  | 2026-07-17 |  | EP | 50 | 1.69 | 1.689 | 2015-01-07 | Pm Cliff Vaughn/ Planner Joshua Smith |  | FALSE
Baseline | AEP | P15095006 | b2604.1 | Remove approximately 11.32 miles of the 69 kV line between Millbrook Park and Franklin Furnace. | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 |  | EP | 50 | 1.13 | 1.13 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095017 | b2604.2 | At Millbrook Park station, add a new 138/69 kV transformer #2 (90 MVA) with 3000 A 40 kA breakers on the high and low side. Replace the 600 A MOAB Switch and add a 3000 A circuit switcher on the high side of transformer #1. | TO Criteria Violation |  | 2019-06-01 |  | 2028-03-14 |  | EP | 0 | 3.05 | 3.05 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095020 | b2604.3 | Replace Sciotoville 69 kV station with a new 138/12 kV in-out station (Cottrell) with 2000A line MOABs facing Millbrook Park and East Wheelersburg 138 kV. | TO Criteria Violation |  | 2019-06-01 |  | 2027-10-07 |  | EP | 0 | 1.4 | 1.4 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095022 | b2604.4 | Tie Cottrell switch into the Millbrook Park-East Wheelersburg 138 kV circuit by constructing 0.50 miles of line using 795 ACSR 26/7 Drake (SE 359 MVA). | TO Criteria Violation |  | 2019-06-01 |  | 2027-10-07 |  | EP | 0 | 1.96 | 1.96 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095028 | b2604.5 | Install a new 2000 A 3-way POP Switch outside of Texas Eastern 138 kV substation (Sadiq Switch). | TO Criteria Violation |  | 2019-06-01 |  | 2027-10-27 |  | EP | 0 | 1.08 | 1.08 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095027 | b2604.6 | Replace the Wheelersburg 69 kV station with a new 138/12 kV in-out station (Sweetgum) with a 3000 A 40 kA breaker facing Sadiq Switch and a 2000 A 138 kV MOAB facing Althea. | TO Criteria Violation |  | 2019-06-01 |  | 2027-12-09 |  | EP | 0 | 2.16 | 2.16 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095032 | b2604.7 | Build approximately 1.4 miles of new 138 kV line using 795 ACSR 26/7 Drake (SE 359 MVA) between the new Sadiq Switch and the new Sweetgum 138 kV stations. | TO Criteria Violation |  | 2019-06-01 |  | 2027-12-07 |  | EP | 0 | 3.41 | 3.41 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095007 | b2604.8 | Remove the existing 69 kV Hayport Road Switch. | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 |  | EP | 0 | 0.1 | 0.1 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095015 | b2604.9 | Rebuild approximately 2.3 miles along existing ROW from Sweetgum to the Hayport Rd switch 69 kV location as 138 kV single circuit and rebuild approximately 2.0 miles from the Hayport Road switch to Althea 69 kV with double circuit 138 kV construction, one side operated at 69 kV to continue service to K.O. Wheelersburg, using 795 ACSR 26/7 Drake (SE 359 MVA). | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 |  | EP | 0 | 10.76 | 10.76 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095015 | b2604.10 | Build a new station (Althea) with a 138/69 kV, 90 MVA transformer. The 138 kV side will have a single 2000 A 40 kA circuit breaker and the 69 kV side will be a 2000 A 40 kA three breaker ring bus. | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 |  | EP | 0 | 11.07 | 11.07 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P15095060 | b2604.11 | Remote end work at Hanging Rock, East Wheelersburg and North Haverhill 138 kV. | TO Criteria Violation |  | 2019-06-01 |  | 2027-11-09 |  | EP | 0 | 0.06 | 0.06 | 2021-02-17 | PM Oliver Duncan/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P16108002 | b2753.7 | Retire line sections (Dilles Bottom - Bellaire and Moundsville - Dilles Bottom 69 kV lines) south of First Energy 138 kV line corridor, near “Point A”. Tie George Washington - Moundsville 69 kV circuit to George Washington - West Bellaire 69 kV circuit. | Baseline Load Growth Deliverability & Reliability |  | 2020-05-31 |  | 2027-10-11 |  | EP | 50 | 5.52 | 5.52 | 2017-07-21 | PM Jon Starr/ Planner Christian Mitchell-Flores | 16329 | TRUE
Baseline | AEP | P24071001 | b2760 | Perform a Sag Study of the Saltville - Tazewell 138 kV line to increase the thermal rating of the line | Baseline Load Growth Deliverability & Reliability |  | 2021-06-01 |  | 2025-03-01 |  | EP | 5 | 0.1 | 0.1 | 2016-10-06 | PM Blair Burns / Bobby Valerio |  | FALSE
Baseline | AEP | P21009002 | b2793 | Energize the spare Fremont Center 138/69 kV 130 MVA transformer #3. Reduces overloaded facilities to 46% loading. | TO Criteria Violation |  | 2021-06-01 |  | 2026-12-14 |  | UC | 26 | 1.3 | 0.081 | 2017-05-31 | PM Colton Caldwell/Brendan Fuller |  | FALSE
Baseline | AEP | P19004001 | b2938 | Perform a sag mitigations on the Broadford – Wolf Hills 138kV circuit to allow the line to operate to a higher maximum temperature. | Generator Deactivation | BEAVER VALLEY 1¦BEAVER VALLEY 2¦DAVIS BESSE 1¦PERRY 1 | 2022-06-01 | 2021-06-01 | 2028-06-27 |  | EP | 15 | 2.6 | 2.6 | 2018-06-07 | PM Blair Burns Planner Robert Vaalerio |  | FALSE
Baseline | AEP | P19269001 | b3037 | Upgrades at the Natrium substation | Baseline Load Growth Deliverability & Reliability |  | 2023-06-01 |  | 2025-06-02 |  | EP | 15 | 1.1 | 1.1 | 2018-09-28 | PM Wayne Cooper/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P21036002 | b3085 | Reconductor Kammer - George Washington 138 kV line (~0.08 miles). Replace the wave trap at Kammer 138 kV. | Generator Deactivation | MANSFIELD 1¦MANSFIELD 2¦MANSFIELD 3¦SAMMIS DIESEL¦SAMMIS 6¦SAMMIS 7¦SAMMIS 5¦KIMBERLY CLARK¦EASTLAKE 6 | 2022-06-01 | 2022-06-01 | 2025-06-02 |  | UC | 75 | 0.5 | 0.5 | 2020-07-07 | PM Andrew Garlick/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P19052004 | b3150 | Rebuild Ferguson 69/12 kV station in the clear as the 138/12 kV Bear station and connect it to a ~1 mile double circuit 138 kV extension from the Aviation – Ellison Rd 138 kV line to remove the load from the 69 kV line. | TO Criteria Violation |  | 2024-06-01 |  | 2027-12-15 |  | EP | 25 | 6.4 | 6.4 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  | FALSE
Baseline | AEP | P16024021 | b3151.7 | Install a 69 kV Bobay switch at Woodland Station. | TO Criteria Violation |  | 2024-06-01 |  | 2025-09-18 |  | UC | 75 | 0.6 | 0.6 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  | FALSE
Baseline | AEP | p16024029 | b3151.8 | Replace Carroll and Churubusco 34.5 kV stations with the 69 kV Snapper station. Snapper will have two (2) line circuit breakers, one (1) bus tie circuit breaker and a 14.4 MVAR cap bank | TO Criteria Violation |  | 2024-06-01 |  | 2025-06-10 |  | UC | 75 | 8.7 | 8.7 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  | FALSE
Baseline | AEP | P16024031 | b3151.9 | Remove 34.5 kV circuit breaker "AD" at Wallen station. | TO Criteria Violation |  | 2024-06-01 |  | 2025-09-18 |  | EP | 25 | 0.3 | 0.3 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  | FALSE
Baseline | AEP | P19096013 | b3151.15 | Rebuild the 0.6 mile double circuit section of the Rob Park – South Hicksville / Rob Park – Diebold Road as 69 kV | TO Criteria Violation |  | 2024-06-01 |  | 2027-01-28 |  | EP | 25 | 1 | 1 | 2019-12-18 | PM Katherine Vecchiarelli/Planner Valerie Watros |  | FALSE
Baseline | AEP | P19297001 | b3160.1 | Construct a ~2.4 mile double circuit 138 kV extension using 1033 ACSR to connect Lake Head to the 138 kV network. | TO Criteria Violation |  | 2024-06-01 |  | 2025-10-03 |  | UC | 75 | 6 | 6 | 2020-01-17 | Charles Linkous/ Bobby Valerio |  | FALSE
Baseline | AEP | A15701239 | b3160.2 | Retire the ~2.5 mile 34.5 kV Niles – Simplicity Tap line. | TO Criteria Violation |  | 2024-06-01 |  | 2027-01-20 |  | EP | 10 | 1.2 | 1.2 | 2020-01-17 | PM Joseph Scott/Planner Joshua Smith |  | FALSE
Baseline | AEP | P17078023 | b3160.3 | Retire the ~4.6 mile Lakehead 69 kV Tap | TO Criteria Violation |  | 2024-06-01 |  | 2025-11-24 |  | EP | 10 | 1.4 | 1.4 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  | FALSE
Baseline | AEP | p19297011 | b3160.4 | Build new 138/69 kV drop down station to feed Lakehead with a 138 kV breaker, 138 kV switcher, 138/69 kV transformer and a 138 kV MOAB | TO Criteria Violation |  | 2024-06-01 |  | 2025-10-03 |  | UC | 50 | 4 | 4 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  | FALSE
Baseline | AEP | P19298001 | b3160.5 | Rebuild the ~1.2 mile Buchanan South 69 kV Radial Tap using 795 ACSR | TO Criteria Violation |  | 2024-06-01 |  | 2028-01-05 |  | EP | 10 | 3 | 3 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  | FALSE
Baseline | AEP | P19298001 | b3160.6 | Rebuild the ~8.4 mile 69 kV Pletcher – Buchanan Hydro line as the ~9 mile Pletcher – Buchanan South 69 kV line using 795 ACSR. | TO Criteria Violation |  | 2024-06-01 |  | 2028-01-05 |  | EP | 10 | 20 | 20 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  | FALSE
Baseline | AEP | P19298020 | b3160.7 | Install a PoP switch at Buchanan South station with 2 line Moabs. | TO Criteria Violation |  | 2024-06-01 |  | 2028-01-05 |  | EP | 10 | 0.6 | 0.6 | 2020-01-17 | PM Mitchell Rice/Pl;anner Joshua Smith |  | FALSE
Baseline | AEP | p17081018 | b3208 | Retire approximately 38 miles of the 44 mile Clifford-Scottsville 46 kV circuit. Build new 138 kV “in and out” to two new Distribution stations to serve the load formerly served by Phoenix, Shipman, Schuyler (AEP), and Rockfish stations. Construct new 138 kV lines from Joshua Falls-Riverville (~10 mi.) and Riverville-Gladstone (~5 mi.). Install required station upgrades at Joshua Falls, Riverville and Gladstone stations to accommodate the new 138 kV circuits. Rebuild Reusen – Monroe 69 kV (~4 mi.) | TO Criteria Violation |  | 2022-12-01 |  | 2027-05-04 |  | EP | 25 | 85 | 85 | 2019-05-20 | PM Scott Maxwell/Planner Robert Valerio |  | FALSE
Baseline | AEP | P21296007 | b3243 | Replace risers at Bass 34.5kV station | TO Criteria Violation |  | 2025-06-01 |  | 2025-11-03 |  | EP | 0 | 0.1 | 0.1 | 2020-11-20 | PM Kyle Martin/Planner Valerie Watros |  | FALSE
Baseline | AEP | P19096001 | b3244 | Rebuild approximately 9 miles of the Rob Park - Harlan 69 kV line | TO Criteria Violation |  | 2025-06-01 |  | 2025-07-24 |  | EP | 0 | 20.9 | 20.9 | 2020-11-20 | PM Dan Ballmer/Planner Valerie Watros |  | FALSE
Baseline | AEP | P21005001 | b3248 | Install a low side 69 kV circuit breaker at Albion 138/69 kV transformer 1 | TO Criteria Violation |  | 2025-06-01 |  | 2028-10-02 |  | EP | 0 | 0.4 | 0.4 | 2020-11-20 | PM Kyle Martin/Planner Valerie Watros |  | FALSE
Baseline | AEP | P20255001 | b3249 | Rebuild the Chatfield-Melmore 138kV line (~ 10 miles) to 1033 ACSR conductor. | Baseline Load Growth Deliverability & Reliability |  | 2025-06-01 |  | 2026-02-24 |  | EP | 0 | 27.2 | 27.2 | 2021-02-17 | PM Anthony Antronica/Planner Jaspm Lee |  | FALSE
Baseline | AEP | P15095017 | b3253 | Install a 3000A 40 kA 138 kV breaker on high side of 138/69 kV transformer #5 at Millbrook Park station. The transformer and associated bus protection will be upgraded accordingly. | TO Criteria Violation |  | 2025-06-01 |  | 2028-03-14 |  | UC | 26 | 0.63 | 0.63 | 2020-11-20 | PM Cole Fehrman/Planner Michael Ritchey |  | FALSE
Baseline | AEP | P21252005 | b3258 | Install a 3000A 63 kA 138 kV breaker on high side of 138/69 kV transformer #2 at Wagenhals station. The transformer and associated bus protection will be upgraded accordingly. | TO Criteria Violation |  | 2025-06-01 |  | 2027-06-04 |  | EP | 0 | 1.1 | 1.1 | 2020-11-20 | PM Davide Roudebush/Planner Michael Ritchey |  | FALSE
Baseline | AEP | P20009043 | b3259 | At West Millersburg station, replace the 138 kV MOAB on the West Millersburg - Wooster 138 kV line with a 3000A 40 kA breaker. | TO Criteria Violation |  | 2025-06-01 |  | 2024-09-01 |  | EP | 0 | 0.68 | 0.68 | 2020-11-20 | PM David Roudebush/Planner Hunter Hutchison |  | FALSE
Baseline | AEP | P21746001, P21746011 | b3269 | At West New Philadelphia station, add a high side 138 kV breaker on the 138/69 kV transformer #2 along with a 138 kV breaker on the line towards Newcomerstown. | TO Criteria Violation |  | 2025-06-01 |  | 2028-04-13 |  | EP | 0 | 2.02 | 2.02 | 2020-11-04 | Planner Hunter Hutcison |  | FALSE
Baseline | AEP | p15082c31 | b3270 | Install 1.7 miles of 795 ASCR 138kV conductor along the other side of Dragoon Tap 138 kV line, which is currently double circuit tower with one position open. Additionally, install a 2nd 138/34.5 kV transformer at Dragoon, install a high side circuit switcher on the current transformer at Dragoon Station, and install 2-138 kV line breakers on the Dragoon-Jackson 138 kV and Dragoon-Twin Branch 138 kV lines. | TO Criteria Violation |  | 2025-06-01 |  | 2025-12-19 |  | UC | 75 | 4.89 | 4.89 | 2020-11-04 | PM Cliff Vaughn/Planner Joshua Smith |  | FALSE
Baseline | AEP | P22094002 | b3270.1 | Replace Dragoon 34.5 kV Breakers "B", "C" and "D" with 40 kA breakers. | TO Criteria Violation |  | 2025-06-01 |  | 2025-01-01 |  | EP | 0 | 2 | 2 | 2020-11-04 | PM Cliff Vaughn/Planner Joshua Smith |  | FALSE
Baseline | AEP | P20896002, P20896006 | b3271 | Install a 138 kV circuit breaker at Fremont station on line towards Fremont Center and install a 9.6 MVAR 69 kV capacitor bank at Bloom Road station. | TO Criteria Violation |  | 2025-06-01 |  | 2024-09-01 |  | EP | 25 | 1.76 | 1.76 | 2020-11-04 | PM Colton Caldwell/Planner Hunter Hutchison |  | FALSE
Baseline | AEP | P23024001 | b3272 | Install two 138 kV circuit switchers on the high side of 138/34.5 kV transformers #1 & #2 at Rockhill station. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 |  | EP | 0 | 1.47 | 1.47 | 2020-11-04 |  |  | FALSE
Baseline | AEP | P20017004 | b3273.1 | Rebuild and convert the existing 17.6 miles East Leipsic-New Liberty 34.5 kV circuit to 138 kV using 795 ACSR | TO Criteria Violation |  | 2025-06-01 |  | 2027-11-17 |  | EP | 25 | 31.35 | 31.351 | 2020-12-01 | PM Benjamin Gilsdorf/Planner Jason Lee |  | FALSE
Baseline | AEP | P20017002 | b3273.2 | Convert the existing 34.5 kV equipment to 138 kV and expanded the existing McComb station to the north and east to allow for new equipment to be installed. Install two new 138 kV box bays to allow for line positions and two new 138/12 kV transformers. | TO Criteria Violation |  | 2025-06-01 |  | 2027-02-02 |  | EP | 25 | 0.87 | 0.868 | 2020-12-01 | PM Benjamin Gilsdorf/Planner Jason Lee |  | FALSE
Baseline | AEP | P20017004 | b3273.3 | Expand the existing East Leipsic 138 kV station to the north to allow for another 138 kV line exit to be installed. The new line exit will involve installing a new 138 kV circuit breaker, disconnect switches and new dead end structure along with extending existing 138 kV bus work. | TO Criteria Violation |  | 2025-06-01 |  | 2027-11-17 |  | EP | 25 | 1.3 | 1.3 | 2020-12-01 | PM Benjamin Gilsdorf/Planner Jason Lee |  | FALSE
Baseline | AEP | P20017015 | b3273.4 | Add one 138 kV circuit breaker and disconnect switches in order to add an additional line position at New Liberty 138 kV station. Install line relaying potential devices and retire the 34.5 kV breaker F. | TO Criteria Violation |  | 2025-06-01 |  | 2027-08-19 |  | EP | 25 | 0.9 | 0.899 | 2020-12-01 | PM Benjamin Gilsdorf/Planner Jason Lee |  | FALSE
Baseline | AEP | P21013015 | b3274 | Rebuild approximately 8.9 miles of 69 kV line between Newcomerstown and Salt Fork Switch with 556 ACSR conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 |  | EP | 0 | 15.89 | 15.89 | 2020-12-01 |  |  | FALSE
Baseline | AEP | P21565006 | b3275.1 | Rebuild Kammer Station-Cresaps Switch 69 kV, approximately 0.5 miles. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | EP | 15 | 0.93 | 0.933 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  | FALSE
Baseline | AEP | P21565007 | b3275.2 | Rebuild Cresaps Switch-McElroy Station 69 kV, approximately 0.67 miles. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | EP | 15 | 1.25 | 1.25 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  | FALSE
Baseline | AEP | P21565009 | b3275.3 | Replace a single span of 4/0 ACSR from Moundsville-Natrium str 93L to Carbon Tap switch 69kV located between Colombia Carbon and Conner Run stations. Remainder of line is 336 ACSR. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | EP | 15 | 0.01 | 0.012 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  | FALSE
Baseline | AEP | P21565010 | b3275.4 | Rebuild from Colombia Carbon to Columbia Carbon Tap str 93N 69 kV, approximately 0.72 miles. The remainder of the line between Colombia Carbon Tap structure 93N and Natrium station is 336 ACSR and will remain. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | EP | 15 | 1.08 | 1.082 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  | FALSE
Baseline | AEP | P21565001 | b3275.5 | Replace the Cresaps 69 kV 3-Way Phase-Over-Phase Switch and structure with a new 1200 A 3-Way Switch and Steel Pole. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | EP | 15 | 0.71 | 0.706 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  | FALSE
Baseline | AEP | P21565004 | b3275.6 | Replace 477 MCM Alum bus and risers at McElroy 69 kV station. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | EP | 15 | 0.33 | 0.325 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  | FALSE
Baseline | AEP | P21565008 | b3275.7 | Replace Natrium 138 kV bus existing between CB-BT1 and along the 138 kV Main Bus # 1 dropping to CBH1 from the 500MCM conductors to a 1272 KCM AAC conductor. Replace the dead end clamp and strain insulators. | TO Criteria Violation |  | 2025-06-01 |  | 2025-09-04 |  | EP | 15 | 0.29 | 0.291 | 2020-12-01 | PM Andrew Garlick/Planner Patrick Hodgson |  | FALSE
Baseline | AEP | P22062009 | b3276.1 | Rebuild the 2/0 Copper section of the Lancaster-South Lancaster 69 kV line, approximately 2.9 miles of the 3.2 mile total length with 556 ACSR conductor. The remaining section has 336 ACSR conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2027-10-19 |  | EP | 0 | 5.37 | 5.37 | 2020-12-01 | PM Karmyn Wilford/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P22062009 | b3276.2 | Rebuild the 1/0 Copper section of the line between Lancaster Junction and Ralston station 69 kV, approximately 2.3 miles of the 3.1 mile total length. | TO Criteria Violation |  | 2025-06-01 |  | 2025-04-30 |  | EP | 0 | 4.58 | 4.582 | 2020-12-01 | PM Karmyn Wilford/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P20252011 | b3276.3 | Rebuild the 2/0 Copper portion of the line between East Lancaster Tap and Lancaster 69 kV, approximately 0.81 miles. | TO Criteria Violation |  | 2025-06-01 |  | 2026-04-20 |  | EP | 15 | 1.2 | 1.195 | 2020-12-01 |  |  | FALSE
Baseline | AEP | P19004009 | b3278.1 | Saltville Station: Replace H.S. MOAB Switches on the high side of the 138/69/34.5 kV T1 with a H.S. Circuit Switcher. | TO Criteria Violation |  | 2025-12-01 |  | 2028-01-27 |  | On Hold | 0 | 0.72 | 0.72 | 2021-02-17 | PM Blair Burns/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P19004015 | b3278.2 | Meadowview Station: Replace existing 138/69/34.5 kV transformer T2 with a new 130 MVA 138/69/13 kV transformer. | TO Criteria Violation |  | 2025-12-01 |  | 2028-05-12 |  | EP | 0 | 3.14 | 3.14 | 2021-02-17 | PM Blair Burns/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P19004009 | b3278.3 | Saltville Station: Install two 138 kV breakers and bus diff protection | TO Criteria Violation |  | 2025-12-01 |  | 2028-05-12 |  | EP | 0 | 0.36 | 0.36 | 2021-07-16 | PM Blair Burns/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P22908005 | b3279 | Install a new 138 kV, 21.6 MVAR cap bank and circuit switcher at Apple Grove Station. | TO Criteria Violation |  | 2025-06-01 |  | 2027-04-01 |  | EP | 0 | 1 | 1 | 2021-02-17 | PM Blair Burns/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P20228001, P20228002 | b3280 | Rebuild the existing Cabin Creek - Kelly Creek 46 kV line (to structure 366-44), approximately 4.4 miles. This section is double circuit with the existing Cabin Creek - London 46 kV line so a double circuit rebuild would be required. | TO Criteria Violation |  | 2025-06-01 |  | 2026-11-25 |  | EP | 10 | 17.9 | 17.9 | 2021-01-15 | PM Wayne Cooper/Planner Michael Hassay |  | FALSE
Baseline | AEP | P21753001 | b3281 | Install 138 kV circuit switcher on the 138/69 kV transformer #1 and 138/34.5 kV transformer #2 at Dewey. Install 138 kV 2000 A 40 kA breaker on Stanville line at Dewey 138 kV substation. | TO Criteria Violation |  | 2025-12-01 |  | 2025-12-01 |  | EP | 15 | 1.4 | 1.4 | 2021-02-17 | PM Jacob Arwood/Joshua Smith |  | FALSE
Baseline | AEP | P19292001 | b3282.1 | Install a second 138 kV circuit utilizing 795 ACSR conductor on the open position of the existing double circuit towers from East Huntington-North Proctorville. Remove the existing 34.5 kV line from East Huntington-North Chesapeake and rebuild this section to 138 kV served from a new PoP switch off the new East Huntington-North Proctorville 138 kV #2 line. | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-22 |  | EP | 0 | 7.1 | 7.1 | 2021-02-17 | PM Wayne Cooper/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19292012 | b3282.2 | Install a 138 kV 40 kA circuit breaker at North Proctorville. | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-22 |  | EP | 0 | 1.4 | 1.4 | 2021-02-17 | PM Wayne Cooper/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19292011 | b3282.3 | Install a 138 kV 40 kA circuit breaker at East Huntington. | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-22 |  | EP | 0 | 1.1 | 1.1 | 2021-02-17 | PM Wayne Cooper/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19292009 | b3282.4 | Convert the existing 34/12 kV North Chesapeake to a 138/12 kV station. | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-22 |  | EP | 0 | 0.8 | 0.8 | 2021-02-17 | PM Wayne Cooper/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19303001 | b3284 | Rebuild ~5.44 miles of 69 kV line from Lock Lane to Point Pleasant. | TO Criteria Violation |  | 2025-06-01 |  | 2026-09-10 |  | EP | 15 | 13.5 | 13.5 | 2021-01-15 | PM Andrew Garlick/Planner Michael Hassay |  | FALSE
Baseline | AEP | P18243002 | b3285 | Replace the Meigs 69 kV 4/0 Cu station riser towards Gavin and rebuild the section of the Meigs – Hemlock 69 kV circuit from Meigs to approximately structure #40 (~4 miles) replacing the line conductor 4/0 ACSR with the line conductor size 556.5 ACSR. | TO Criteria Violation |  | 2025-06-01 |  | 2026-05-28 |  | UC | 50 | 12.14 | 12.14 | 2021-01-15 | PM James Albright/Planner Patrick Hodgson |  | FALSE
Baseline | AEP | P19305001 | b3288.1 | Construct ~ 2.75 mi Orinoco - Stone 69 kV transmission line in the clear between Orinoco station and Stone station. | TO Criteria Violation |  | 2025-12-01 |  | 2025-05-29 |  | EP | 15 | 9.23 | 9.23 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19305016 | b3288.2 | Construct ~ 3.25 mi Orinoco – New Camp 69 kV transmission line in the clear between Orinoco station and New Camp station. | TO Criteria Violation |  | 2025-12-01 |  | 2025-11-13 |  | EP | 15 | 9.95 | 9.95 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19305010 | b3288.3 | At Stone substation, circuit breaker A to remain in place and be utilized as T1 low side breaker, circuit breaker B to remain in place and be utilized as new Hatfield (via Orinoco and New Camp) 69 kV line breaker. Add new 69 kV circuit breaker E for Coleman Line exit. | TO Criteria Violation |  | 2025-12-01 |  | 2025-05-29 |  | EP | 15 | 0.66 | 0.66 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19305018 | b3288.4 | Reconfigure the New Camp 69 kV tap which includes access road improvements/installation, temporary wire and permanent wire work along with dead end structures installation. | TO Criteria Violation |  | 2025-12-01 |  | 2025-11-13 |  | EP | 15 | 0.45 | 0.45 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19305022 | b3288.5 | At New Camp substation, rebuild the 69 kV bus, add 69 kV MOAB W and replace the 69 kV ground switch Z1 with a 69 kV circuit switcher on the New Camp transformer. | TO Criteria Violation |  | 2025-12-01 |  | 2025-11-13 |  | EP | 15 | 1.18 | 1.18 | 2021-01-15 | PM Lance Blackburn/Planner Michael Hassay |  | FALSE
Baseline | AEP | P19296003 | b3289.1 | Roanoke Station: Install high-side circuit switcher on 138/69/12 kV T5 | TO Criteria Violation |  | 2025-06-01 |  | 2026-12-10 |  | EP | 0 | 1.1 | 1.102 | 2021-01-15 | PM Jonathan Wood/Planner Robert Valerio |  | FALSE
Baseline | AEP | P23013002 | b3289.2 | Huntington Court Station: Install high-side circuit switcher on 138/69/34.5 kV T1 | TO Criteria Violation |  | 2025-06-01 |  | 2026-05-21 |  | EP | 0 | 1.42 | 1.415 | 2021-01-15 | PM Myles Gunter/Planner Robert Valerio |  | FALSE
Baseline | AEP | P19220001 | b3290.1 | Build 9.4 miles of single circuit 69 kV line from Roselms to near East Ottoville 69 kV Switch. | TO Criteria Violation |  | 2025-06-01 |  | 2026-04-07 |  | EP | 15 | 13.7 | 13.7 | 2021-01-15 | PM Benjamin Gilsdorf/Planner |  | FALSE
Baseline | AEP | P19220018 | b3290.2 | Rebuild 7.5 miles of double circuit 69kV line between East Ottoville Switch and Kalida Station (combining with the new Roselms to Kalida 69 kV circuit). | TO Criteria Violation |  | 2025-06-01 |  | 2026-03-05 |  | EP | 15 | 23.6 | 23.6 | 2021-01-15 | PM Benjamin Gilsdorf/Planner Jason Lee |  | FALSE
Baseline | AEP | P19220017 | b3290.3 | At Roselms Switch, install a new three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | TO Criteria Violation |  | 2025-06-01 |  | 2026-04-07 |  | EP | 15 | 0.6 | 0.6 | 2021-01-15 | PM Benjamin Gilsdorf/Planner Jason Lee |  | FALSE
Baseline | AEP | P19220021 | b3290.4 | At Kalida 69 kV station, terminate the new line from Roselms Switch. Move the CS XT2 from high side of T2 to the high side of T1. Remove existing T2 transformer. | TO Criteria Violation |  | 2025-06-01 |  | 2026-04-07 |  | EP | 15 | 1 | 1 | 2021-01-15 | PM Benjamin Gilsdorf/Planner Jason Lee |  | FALSE
Baseline | AEP | P15082C15 | b3291 | Replace the Russ St. 34.5 kV Switch | TO Criteria Violation |  | 2025-06-01 |  | 2026-10-23 |  | EP | 15 | 1.5 | 1.5 | 2021-01-15 | PM Cliff Vaughn/Planner Joshua Smith |  | FALSE
Baseline | AEP | P18100001 | b3292 | Replace existing 69 kV capacitor bank at Stuart Station with a 17.2 MVAr capacitor bank | TO Criteria Violation |  | 2025-12-01 |  | 2025-12-01 |  | EP | 0 | 0 | 0 | 2021-01-15 |  |  | FALSE
Baseline | AEP | P19296005 | b3294 | Replace existing 69 kV disconnect switches for circuit breaker "C" at Walnut Avenue station | TO Criteria Violation |  | 2025-06-01 |  | 2026-09-16 |  | EP | 0 | 0 | 0 | 2021-01-15 | PM Jonathan Woods/Planner Robert Valerio |  | FALSE
Baseline | AEP | P19281003, P19281024 | b3296 | Rebuild the overloaded portion of the Concord-Whitaker 34.5 kV line (1.13 miles). Rebuild is double circuit and will utilize 795 ACSR conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2026-06-30 |  | EP | 0 | 2.8 | 2.8 | 2021-01-15 |  |  | FALSE
Baseline | AEP | P20233002 | b3297.1 | Rebuild 4.23 miles of 69 kV line between Sawmill and Lazelle station, using 795 ACSR 26/7 conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2027-09-04 |  | EP | 0 | 12 | 12 | 2021-01-15 | PM Andrew Nardella/Planner Huner Hutchinson |  | FALSE
Baseline | AEP | P20233006 | b3297.2 | Rebuild 1.94 miles of 69 kV line between Westerville and Genoa stations, using 795 ACSR 26/7 conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2027-09-24 |  | EP | 0 | 5.9 | 5.9 | 2021-01-15 |  |  | FALSE
Baseline | AEP | P20233007 | b3297.3 | Replace risers and switchers at Lazelle, Westerville, and Genoa 69 kV stations. Upgrade associated relaying accordingly. | TO Criteria Violation |  | 2025-06-01 |  | 2027-09-24 |  | EP | 0 | 1.9 | 1.9 | 2021-01-15 | PM Andrew Nardella/Planner Hunter Hutchison |  | FALSE
Baseline | AEP | P21600005 | b3298 | Rebuild 0.8 miles of double circuit 69 kV line between South Toronto and West Toronto. Replace 219 kcmil ACSR with 556 ACSR. | TO Criteria Violation |  | 2025-06-01 |  | 2026-06-08 |  | EP | 0 | 2.83 | 2.83 | 2021-02-17 | PM Jared Grzeskowiak/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P22734002 | b3298.1 | Replace the 69 kV breaker D at South Toronto station with 40 kA breaker. | TO Criteria Violation |  | 2025-06-01 |  | 2025-12-02 |  | EP | 0 | 0.7 | 0.7 | 2021-02-17 | PM Jared Grzeskowiak/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P18221001 | b3307 | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69 kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12 kV 30 MVA transformer, replace 12 kV CB A and D. Retire existing Fleming substation. | TO Criteria Violation |  | 2025-12-01 |  | 2025-12-01 |  | UC | 50 | 21.1 | 21.1 | 2021-01-15 | PM Wayne Cooper/Planner Michael Hassay |  | FALSE
Baseline | AEP | P21600001 | b3308 | Reconductor and rebuild 1 span of T-line on the Fort Steuben-Sunset Blvd 69 kV branch with 556 ACSR. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 |  | EP | 0 | 0.73 | 0.73 | 2021-01-15 | PM Cole Fehrman/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P20010021 | b3309 | Rebuild 1.75 miles of the Greenlawn - East Tiffin line section of the Carrothers - Greenlawn 69 kV circuit containing 133 ACSR conductor with 556 ACSR conductor. Upgrade relaying as required. | TO Criteria Violation |  | 2025-06-01 |  | 2029-03-21 |  | EP | 15 | 3.45 | 3.45 | 2021-01-15 | PM Benjamin Gilsdorf/Planner Hunter Hutchison |  | FALSE
Baseline | AEP | P21033004 | b3310.1 | Rebuild 10.5 miles of the Howard-Willard 69 kV line utilizing 556 ACSR conductor. | TO Criteria Violation |  | 2025-06-01 |  | 2025-05-30 |  | UC | 50 | 19 | 19 | 2021-02-17 | PM Danielle Hilliard/Planner Jason Lee |  | FALSE
Baseline | AEP | P21033014 | b3310.2 | Upgrade relaying at Howard 69 kV station. | TO Criteria Violation |  | 2025-06-01 |  | 2025-10-31 |  | EP | 15 | 0.23 | 0.23 | 2021-02-17 | PM Danielle Hilliard/Planner Jason Lee |  | FALSE
Baseline | AEP | P20889008 | b3312 | Rebuild approximately 4.0 miles of existing 69 kV line between West Mount Vernon and Mount Vernon stations. Replace the existing 138/69 kV transformer at West Mount Vernon with a larger 90 MVA unit along with existing 69 kV breaker 'C'. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 |  | EP | 15 | 12.93 | 12.926 | 2021-01-06 | PM Adam Clark/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P21030010 | b3313 | Add 40 kA circuit breakers on the low and high side of East Lima 138/69 kV Transformer | TO Criteria Violation |  | 2025-06-01 |  | 2026-12-30 |  | EP | 15 | 1.2 | 1.2 | 2021-03-19 | PM Jon Starr/Planner Hunter Hutchison |  | FALSE
Baseline | AEP | P19225006 | b3314.1 | Install a new 138/69 kV 130 MVA transformer and associated protection at Elliot station. | TO Criteria Violation |  | 2025-06-01 |  | 2029-09-20 |  | EP | 15 | 3 | 3 | 2021-03-19 | PM John Wright/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P19225022 | b3314.2 | Perform work at Strouds Run station to retire 138/69/13 kV 33.6 MVA transformer #1 and install a dedicated 138/13 KV distribution transformer. | TO Criteria Violation |  | 2025-06-01 |  | 2030-10-24 |  | EP | 15 | 0 | 0 | 2021-03-19 | PM John Wright/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P19178030 | b3315 | Upgrade Relaying on Mark Center-South Hicksville 69 kV line and replace Mark Center cap bank with a 7.7 MVAR unit. | TO Criteria Violation |  | 2025-06-01 |  | 2025-06-01 |  | EP | 0 | 1.25 | 1.25 | 2021-03-19 | PM Danille Hilliard/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P21751001 | b3337 | Replace the one (1) Hyatt 138 kV breaker “AB1(101N)” with 3000 A, 63 kA interrupting breaker. | Short Circuit |  | 2026-06-01 |  | 2025-05-23 |  | EP | 15 | 0.48 | 0.48 | 2021-10-15 | PM Melinda Kemplin/Planner Christian Mitchell-Flores |  | FALSE
Baseline | AEP | P20013001 | b3338 | Replace the two (2) Kenny 138 kV breakers, “102” (SC-3) and “106” (SC-4), each with a 3000 A, 63 kA interrupting breaker. | Short Circuit |  | 2026-06-01 |  | 2024-06-14 |  | EP | 0 | 0.76 | 0.76 | 2021-10-05 |  |  | FALSE
Baseline | AEP | P21751002 | b3339 | Replace the one (1) Canal 138 kV breaker “3” with 3000 A, 63 kA breaker. | Short Circuit |  | 2026-06-01 |  | 2025-04-30 |  | EP | 15 | 0.48 | 0.48 | 2021-10-15 |  |  | FALSE
Baseline | AEP | P23008001 | b3344.1 | Install two (2) 138 kV circuit breakers in the M and N strings in the breaker-and-a half configuration in West Kingsport station 138 kV yard to allow the Clinch River-Moreland Dr. 138 kV to cut in the West Kingsport station | TO Criteria Violation |  | 2026-11-01 |  | 2025-11-01 |  | EP | 0 | 1.85 | 1.846 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P23008004 | b3344.2 | Upgrade remote end relaying at Riverport 138 kV station due to the line cut in at West Kingsport station | TO Criteria Violation |  | 2026-11-01 |  | 2026-11-01 |  | EP | 15 | 0.25 | 0.251 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21013019 | b3345.1 | Rebuild ~4.2 miles of overloaded sections of the 69 kV line between Salt Fork Switch and Leatherwood Switch with 556 ACSR. | TO Criteria Violation |  | 2026-06-01 |  | 2027-08-02 |  | EP | 0 | 9.06 | 9.062 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21013024 | b3345.2 | Update relay settings at Broom Road station. | TO Criteria Violation |  | 2026-06-01 |  | 2027-08-02 |  | EP | 0 | 0.04 | 0.039 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21590002, P21590003, P21590004, P21590005, P21590008, P21590009, P21590012, P21590014 | b3346.1 | Rebuild approximately 3.5 miles of overloaded 69 kV line between North Delphos-East Delphos-Elida Road switch. This includes approximately 1.1 miles of double circuit line that makes up a portion of the North Delphos-South Delphos 69 kV line and the North Delphos-East Delphos 69 kV line. Approximately 2.4 miles of single circuit line will also be rebuilt between the double circuit portion to East Delphos station and from East Delphos to Elida Road Switch. | TO Criteria Violation |  | 2026-06-01 |  | 2026-08-21 |  | EP | 0 | 8.43 | 8.434 | 2021-11-30 |  |  | FALSE
Baseline | AEP | P21590015, P21590017 | b3346.2 | Replace the line entrance spans at South Delphos to eliminate the overloaded 4/0 Copper and 4/0 ACSR conductor. | TO Criteria Violation |  | 2026-06-01 |  | 2027-04-20 |  | EP | 0 | 0.44 | 0.437 | 2021-11-30 |  |  | FALSE
Baseline | AEP | P21737001, P21737010, P21737011, P21737012, P21737013, P21737014 | b3347.1 | Rebuild approximately 20 miles of line between Bancroft and Milton stations with 556 ACSR conductor | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-14 |  | EP | 0 | 56.55 | 56.553 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21737023, A20001419 | b3347.2 | Replace the jumpers around Hurrican switch with 556 ACSR | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 |  | EP | 0 | 0.01 | 0.014 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21737024 | b3347.3 | Replace the jumpers around Teays switch with 556 ACSR | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 |  | EP | 0 | 0.01 | 0.014 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21737008 | b3347.4 | Winfield Station Relay Settings: Update relay settings to coordinate with remote ends on line rebuild | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 |  | EP | 0 | 0.05 | 0.047 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21737009 | b3347.5 | Bancroft Station Relay Settings: Update relay settings to coordinate with remote ends on line rebuild | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 |  | EP | 0 | 0.03 | 0.027 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21737004 | b3347.6 | Milton Station Relay Settings: Update relay settings to coordinate with remote ends on line rebuild. | TO Criteria Violation |  | 2026-11-01 |  | 2027-12-23 |  | EP | 0 | 0.03 | 0.027 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21737007 | b3347.7 | Putnam Village Station Relay Settings: Update relay settings to coordinate with remote ends on line rebuild | TO Criteria Violation |  | 2026-11-01 |  | 2029-08-03 |  | EP | 0 | 0.05 | 0.047 | 2021-11-02 |  |  | FALSE
Baseline | AEP | P21259011, P21259040 | b3348.1 | Construct a 138 kV single bus station (Tin Branch) consisting of a 138 kV box bay with a distribution transformer and 12 kV distribution bay. Two 138 kV lines will feed this station (from Logan and Sprigg stations), and distribution will have one 12 kV feed. Install two 138 kV circuit breakers on the line exits. Install 138 kV circuit switcher for the new transformer. | TO Criteria Violation |  | 2026-11-01 |  | 2026-11-09 |  | EP | 0 | 5.58 | 5.584 | 2021-11-30 |  |  | FALSE
Baseline | AEP | P21259013 | b3348.2 | Construct a new 138/46/12 kV Argyle station to replace Dehue station. Install a 138 kV ring bus using a breaker-and-a-half configuration, with an autotransformer with a 46 kV feed and a distribution transformer with a 12 kV distribution bay. Two 138 kV lines will feed this station (from Logan and Wyoming stations). There will also be a 46 kV feed from this station to Becco station. Distribution will have two 12 kV feeds. Retire Dehue station in its entirety. | TO Criteria Violation |  | 2026-11-01 |  | 2026-07-17 |  | EP | 0 | 10 | 9.996 | 2021-11-30 |  |  | FALSE
Baseline | AEP | P21259036, P21259037 | b3348.3 | Bring the Logan-Sprigg #2 138 kV circuit in and out of Tin Branch station by constructing approximately 1.75 miles of new overhead double circuit 138 kV line. Double circuit T3 series lattice towers will be used along with 795,000 cm ACSR 26/7 conductor. One shield wire will be conventional 7 #8 ALUMOWELD, and one shield wire will be OPGW. | TO Criteria Violation |  | 2026-11-01 |  | 2027-03-22 |  | EP | 0 | 8.58 | 8.578 | 2021-11-30 |  |  | FALSE
Baseline | AEP | P21259034, P21259035 | b3348.4 | Logan-Wyoming No. 1 circuit in and out of the proposed Argyle station. Double circuit T3 series lattice towers will be used along with 795,000 cm ACSR 26/7 conductor. One shield wire will be conventional 7 #8 ALUMOWELD, and one shield wire will be OPGW. | TO Criteria Violation |  | 2026-11-01 |  | 2026-07-17 |  | EP | 0 | 7.7 | 7.702 | 2021-11-30 |  |  | FALSE
Baseline | AEP | P21259023, P21259024, P21259025 | b3348.5 | Rebuild approximately 10 miles of 46 kV line between Becco and the new Argyle substation. Retire approximately 16 miles of 46 kV line between the new Argyle substation and Chauncey station. | TO Criteria Violation |  | 2026-11-01 |  | 2026-08-20 |  | EP | 0 | 33.71 | 33.705 | 2021-11-30 |  |  | FALSE
Baseline | AEP | P21259028, P21259029, P21259030 P21259031 | b3348.6 | Adjust relay settings due to new line terminations and retirements at Logan, Wyoming, Sprigg, Becco and Chauncey stations. | TO Criteria Violation |  | 2026-11-01 |  | 2026-11-23 |  | EP | 0 | 0.23 | 0.233 | 2021-11-30 |  |  | FALSE
Baseline | AEP | P21720001 | b3349 | Replace Bellefonte 69 kV risers on the section between Bellefonte TR #3 and 69 kV Bus #2. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  | EP | 15 | 0.54 | 0.54 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P21720001 | b3350.1 | Replace overdutied 69 kV breakers C, G, I, Z, AB and JJ in place. The new 69 kV breakers to be rated at 3000 A 40 kA breakers. | TO Criteria Violation |  | 2023-06-01 |  | 2026-05-27 |  | EP | 15 | 2 | 2 | 2022-01-21 |  |  | FALSE
Baseline | AEP | P21720005, P21720003, P21720007 | b3350.2 | Upgrade remote end relaying at Point Pleasant, Coalton and South Point 69 kV substations. | TO Criteria Violation |  | 2023-06-01 |  | 2026-06-04 |  | EP | 15 | 0 | 0 | 2022-01-21 |  |  | FALSE
Baseline | AEP | A20001430 | b3351 | Replace the 69 kV in-line switches at Monterey 69 kV substation. | TO Criteria Violation |  | 2026-06-01 |  | 2029-08-31 |  | EP | 0 | 0 | 0 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P22005001 | b3352 | Replace MOAB W, MOAB Y, line and bus side jumpers of both W and Y at 47th Street 69 kV station. Upgrade the 69 kV strain bus between MOABs W and Y to 795 KCM AAC. Change the connectors on the tap to MOAB X1 to accommodate the larger 795 KCM AAC. | TO Criteria Violation |  | 2026-06-01 |  | 2025-12-01 |  | EP | 15 | 0 | 0 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P19092002 | b3353.1 | Allen substation: Rebuild Allen station to the northwest of its current footprint utilizing a standard air-insulated substation with equipment raised by 7’ concrete platforms and control house raised by a 10’ platform to mitigate flooding concerns. Install five 69 kV 3000A 40 kA circuit breakers in a ring bus (operated at 46 kV) configuration with a 13.2 MVAR capacitor bank. Existing Allen station will be retired (does not include the distribution cost). Distribution scope of work: Install 69/46 kV-12 kV 20 MVA transformer along with 2-12 kV breakers on 7’ concrete platforms (conversion of S2405.1). | TO Criteria Violation |  | 2026-12-01 |  | 2024-11-15 |  | EP | 15 | 10.55 | 10.55 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P19092007 | b3353.2 | Allen-East Prestonsburg: A 0.20 mile segment of this 46 kV line will be relocated to the new station (SN/SE/WN/WE: 53/61/67/73MVA). (Conversion of S2405.2) | TO Criteria Violation |  | 2026-12-01 |  | 2024-04-25 |  | EP | 15 | 0.33 | 0.33 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P19092011 | b3353.3 | McKinney-Allen: The new line extension will walk around the south and east sides of the existing Allen station to the new Allen station being built in the clear. A short segment of new single circuit 69 kV line and a short segment of new double circuit 69 kV line (both operated at 46 kV) will be added to the line to tie into the new Allen station bays. (Conversion of S2405.3) | TO Criteria Violation |  | 2026-12-01 |  | 2024-04-05 |  | EP | 15 | 1.95 | 1.95 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P19092013 | b3353.4 | Stanville-Allen: A segment of this line will have to be relocated to the new station (SN/SE/WN/WE: 50/50/63/63MVA). (Conversion of S2405.4) | TO Criteria Violation |  | 2026-12-01 |  | 2024-11-15 |  | EP | 15 | 0.17 | 0.17 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P19092013 | b3353.5 | Allen-Prestonsburg: 0.25 mile segment of this existing single circuit will be relocated. The relocated line segment will require construction of one custom self-supporting double circuit dead-end structure and single circuit suspension structure. A short segment of new double circuit 69 kV line (energized at 46 kV) will be added to tie into the new Allen station bays, which will carry Allen-Prestonsburg 46 kV and Allen-East Prestonsburg 46 kV lines. A temporary 0.15 mile section double circuit line will be constructed to keep Allen-Prestonsburg and Allen-East Prestonsburg 46 kV lines energized during construction. (Conversion of S2405.5) | TO Criteria Violation |  | 2026-12-01 |  | 2025-10-18 |  | EP | 15 | 2.66 | 2.66 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P19092014 | b3353.6 | Remote end work will be required at Prestonsburg, Stanville and McKinney stations. (Conversion of S2405.6) | TO Criteria Violation |  | 2026-12-01 |  | 2024-11-15 |  | EP | 15 | 0.34 | 0.34 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P22110020 | b3359 | Rebuild approximately 2.3 miles of the existing North Van Wert Sw-Van Wert 69 kV line utilizing 556 ACSR conductor. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 6.2 | 6.2 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P21043015 | b3360 | Replace Thelma Transformer #1 with a 138/69/46 kV 130/130/90 MVA transformer and replace 46 kV risers and relaying toward Kenwood substation. Existing TR#1 to be used as spare. | TO Criteria Violation |  | 2026-12-01 |  | 2027-12-16 |  | EP | 15 | 3.54 | 3.54 | 2021-11-19 |  |  | FALSE
Baseline | AEP | A20045015 | b3361 | Rebuild Prestonsburg - Thelma 46kV circuit connecting though Kenwood station, approximately 12.7 miles. Retire Jenny Wiley SS and Van Lear SS. | TO Criteria Violation |  | 2026-12-01 | 2027-12-16 | 2027-12-16 |  | EP | 0 | 63.6 | 63.6 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P21773002 | b3362 | Rebuild approximately 3.1 miles of the overloaded conductor on the existing Oertels Corner-North Portsmouth 69 kV line utilizing 556 ACSR. | TO Criteria Violation |  | 2026-06-01 |  | 2026-05-01 |  | EP | 15 | 8 | 8 | 2021-11-19 |  |  | FALSE
Baseline | AEP | P23027003 | b3722 | Rebuild the existing Darrah-Barnett 69 kV line, approximately 2.8 miles and replace a riser at Darrah station. | TO Criteria Violation |  | 2027-12-01 |  | 2027-12-01 |  | EP | 0 | 6.98 | 6.98 | 2022-10-14 |  |  | FALSE
Baseline | AEP | P21036003 | b3723 | Rebuild the George Washington – Kammer 138 kV circuit, except for 0.1-mile of previously-upgraded T-line outside each terminal station (6.7 miles of total upgrade scope). Remove the existing 6-wired steel lattice towers and supplement the right-of-way as needed. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2024-06-01 |  | UC | 50 | 18.3 | 18.3 | 2022-10-14 |  |  | FALSE
Baseline | AEP | P19296003 | b3724 | Install 138 kV circuit switcher on the high-side of Transformer #2 at Roanoke station (previously proposed as a portion of s2469.7, posted in 2021 AEP local plan). | TO Criteria Violation |  | 2027-06-01 |  | 2025-03-20 |  | EP | 0 | 0.1 | 0.1 | 2022-10-14 |  |  | FALSE
Baseline | AEP | P17002006 | b3731 | Replace 40kV breaker J at McComb station with a new 3000A 40kA breaker | TO Criteria Violation |  | 2027-06-01 |  | 2025-06-01 |  | EP | 0 | 0.5 | 0.5 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P22797001 | b3732 | Install a 6 MVAR, 34.5kV cap bank at Morgan Run station | TO Criteria Violation |  | 2027-06-01 |  | 2027-06-01 |  | EP | 15 | 0.37 | 0.37 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P22968002 | b3733 | Rebuild the 1.8 mile 69kV T-line between Summerhill and Willow Grove Switch. Replace 4/0 ACSR conductor with 556 ACSR. | TO Criteria Violation |  | 2027-06-01 |  | 2026-06-23 |  | EP | 0 | 5.1 | 5.1 | 2022-11-18 | Rachel Kosarko |  | FALSE
Baseline | AEP | P18150035 | b3734 | Install a 7.7 MVAR, 69kV cap bank at both Otway station and Rosemount station | TO Criteria Violation |  | 2027-06-01 |  | 2026-06-15 |  | EP | 0 | 1.73 | 1.73 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19095004 | b3735 | Terminate the existing Broadford – Wolf Hills #1 138 kV line into Abingdon 138 kV Station. This line currently bypasses the existing Abingdon 138 kV Station; Install two new 138 kV circuit breakers on each new line exit towards Broadford and towards Wolf Hills #1; Install one new 138 kV circuit breaker on line exit towards South Abingdon for standard bus sectionalizing | TO Criteria Violation |  | 2027-06-01 |  | 2025-05-01 |  | EP | 15 | 8.48 | 8.48 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037013 | b3736.1 | Establish 69kV bus and new 69 kV line CB at Dorton substation. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 1.13 | 1.13 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037014 | b3736.2 | At Breaks substation, reuse 72kV breaker A as the new 69kV line breaker. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0.71 | 0.71 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037004, P19037005 | b3736.3 | Rebuild ~16.7 mi Dorton – Breaks 46kV line to 69kV | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 58.52 | 58.52 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037020 | b3736.4 | Retire ~17.2 mi Cedar Creek – Elwood 46kV circuit. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 11.15 | 11.15 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037020 | b3736.5 | Retire ~ 6.2 mi Henry Clay – Elwood 46kV line section. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 4.3 | 4.3 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037008 | b3736.6 | Retire Henry Clay 46 kV substation and replace with Poor Bottom 69 kV station. Install a new 0.7 mi double circuit extension to Poor Bottom 69kV. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 3.42 | 3.42 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037015 | b3736.7 | Retire Draffin substation and replace with a new substation. Install a new 0.25 mi double circuit extension to New Draffin substation. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 2.01 | 2.01 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037029 | b3736.8 | Remote End work at Jenkins substation | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0.03 | 0.03 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037023, P19037024, P19037028, P19037030 | b3736.9 | Provide Transition fiber to Dorton, Breaks, Poor Bottom, Jenkins and New Draffin substations | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0.41 | 0.41 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037001 | b3736.10 | Henry Clay S.S Retirement: | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0.3 | 0.3 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037018 | b3736.11 | Cedar Creek substation work | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0.44 | 0.44 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037014 | b3736.12 | Breaks substation retire 46kV equipment: | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0.25 | 0.25 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037019 | b3736.13 | Retire Pike 29 SS and Rob Fork SS | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0.42 | 0.42 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037022 | b3736.14 | Serve Pike 29 and Rob Fork customers from nearby 34kV Distribution sources. | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037008 | b3736.15 | Poor Bottom substation install | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037008 | b3736.16 | Henry Clay 46kV substation retirement | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037016 | b3736.17 | New Draffin 69kV substation install | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P19037015 | b3736.18 | Draffin 46kV substation retirement | TO Criteria Violation |  | 2027-12-01 |  | 2027-07-31 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Baseline | AEP | P22055006 | b3763 | Replace the Jug Street 138kV breakers M, N, BC, BF, BD, BE, D, H, J, L, BG, BH, BJ, BK with 80KA breakers | Short Circuit |  | 2024-06-01 |  | 2024-06-01 |  | EP | 50 | 14 | 14 | 2022-12-16 |  |  | FALSE
Baseline | AEP | P21751001 | b3764 | Replace the Hyatt 138kV breakers AB1 and AD1 with 63kA breakers | Short Circuit |  | 2024-06-01 |  | 2024-06-01 |  | EP | 15 | 2 | 2 | 2022-12-16 |  |  | FALSE
Baseline | AEP | P22052004, P22052005 | b3766.1 | Hayes – New Westville 138 kV line: Build ~0.19 miles of 138 kV line to the Indiana/ Ohio State line to connect to AES’s line portion of the Hayes – New Westville 138 kV line with the conductor size 795 ACSR26/7 Drake. The following cost includes the line construction and ROW. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2026-01-08 |  | EP | 0 | 0.38 | 0.38 | 2022-12-06 |  |  | TRUE
Baseline | AEP | P22052007, P22052008, P22052014 | b3766.2 | Hayes – Hodgin 138 kV line: Build ~0.05 miles of 138 kV line with the conductor size 795 ACSR26/7 Drake. The following cost includes the line construction, ROW, and fiber. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2026-01-08 |  | EP | 0 | 1.22 | 1.22 | 2022-12-06 |  |  | TRUE
Baseline | AEP | P22052001, P22052002, P22052003, P22052006 | b3766.3 | Hayes 138 kV: Build a new 4-138 kV circuit breaker ring bus. The following cost includes the new station construction, property purchase, metering, station fiber and the College Corner –Randolph 138 kV line connection. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2026-01-08 |  | EP | 0 | 7.44 | 7.44 | 2022-12-06 |  |  | TRUE
Baseline | AEP | P23010002 | b3775.6 | Perform sag study mitigation work on the Dumont-Stillwell 345 kV line (remove a center-pivot irrigation system from under the line, allowing for the normal and emergency ratings of the line to increase, replace two structures and modify a third structure). | Congestion Relief - Economic¦Baseline Load Growth Deliverability & Reliability |  | 2026-12-01 |  | 2026-11-20 |  | EP | 15 | 2.22 | 2.22 | 2023-04-11 |  |  | TRUE
Baseline | AEP | P23010001, P23010004 | b3775.7 | Upgrade the limiting element at Dumont substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | Congestion Relief - Economic¦Baseline Load Growth Deliverability & Reliability |  | 2026-12-01 |  | 2026-12-01 |  | EP | 15 | 2 | 2 | 2023-04-11 |  |  | TRUE
Baseline | AEP | P23018001, P23018002 | b3775.10 | Perform a sag study on the Olive – University Park 345kV line to increase the operating temperature to 225 F. Remediation work includes two tower replacements on the line. | Congestion Relief - Economic¦Baseline Load Growth Deliverability & Reliability |  | 2026-12-01 |  | 2026-12-01 |  | EP | 0 | 1.5 | 1.5 | 2023-01-10 |  |  | TRUE
Baseline | AEP | P23010001 | b3775.11 | Upgrade the limiting element at Stillwell substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | Congestion Relief - Economic¦Baseline Load Growth Deliverability & Reliability |  | 2026-12-01 |  | 2026-12-01 |  | EP | 15 | 0.14 | 1.78 | 2023-04-11 |  |  | TRUE
Baseline | AEP | P24141001 | b3784.1 | Replace 138kV breaker 5 at Canal St station with a new 3000A 63kA breaker | Short Circuit |  | 2028-06-01 |  | 2028-02-24 |  | EP | 0 | 0.5 | 0.5 | 2023-11-17 |  |  | FALSE
Baseline | AEP | P24043001 | b3785.1 | Replace existing 3000A wave trap at Mountaineer 765 kV, on the Belmont-Mountaineer 765 kV line, with a new 5000 A wave trap. | Baseline Load Growth Deliverability & Reliability |  | 2028-06-01 |  | 2028-06-01 |  | EP | 0 | 0.46 | 0.46 | 2023-12-05 |  |  | FALSE
Baseline | AEP | P24081002 | b3786.1 | Rebuild ~4.5 miles of 69 kV line between Abert and Reusens substations. Update line settings at Reusens and Skimmer. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  | EP | 0 | 14.4023 | 14.4023 | 2023-11-17 |  |  | FALSE
Baseline | AEP |  | b3787.1 | Install a CCVT on three-phase stand and remove the single phase existing CCVT on the 69 kV Coalton to Bellefonte line exit. The existing CCVT is mounted to lattice on a single-phase CCVT stand, which will be replaced with the three-phase CCVT stand. The line riser between line disconnect and line takeoff is being replaced. This remote end work changes the MLSE of the line section between Coalton-Princess 69 kV line section. | TO Criteria Violation |  | 2028-12-01 |  | 2028-12-01 |  | EP | 0 | 0 | 0 | 2023-11-17 |  |  | FALSE
Baseline | AEP | P23837001 | b3788.1 | Replace AEP-owned station takeoff riser and breaker BB risers at OVEC-owned Kyger Creek station. | Baseline Load Growth Deliverability & Reliability |  | 2028-06-01 |  | 2028-06-01 |  | EP | 0 | 0.41 | 0.41 | 2023-12-05 |  |  | TRUE
Baseline | AEP | P24034001, P24034002 | b3790.0 | Replace the overdutied Olive 345 kV circuit breaker "D" with a 5000A 63 kA circuit breaker. Reuse existing cables and a splice box to support the circuit breaker install. | Short Circuit |  | 2028-06-01 |  | 2028-06-01 |  | EP | 15 | 1.083 | 1.083 | 2023-12-05 |  |  | FALSE
Baseline | AEP | P24059001, P24059002 | b3800.100 | Establish a new 500 kV breaker position for the low-side of the existing 765/500 kV transformer at Cloverdale Station. The new position will be between two new 500 kV circuit breakers located in a new breaker string, electrically converting the 500 kV yard to "double-bus double-breaker" configuration. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  | EP | 0 | 11.591 | 11.591 | 2023-12-05 |  |  | FALSE
Baseline | AEP | P23878001 | b3800.121 | Kammer to 502 Junction 500 kV line: Conduct LIDAR Sag Study to assess SE rating and needed upgrades. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  | EP | 0 | 0.1 | 0.1 | 2023-12-05 |  |  | FALSE
Baseline | AEP | P24014001 | b3836.1 | Rebuild approximately 1.7 miles of line on the Chemical-Washington Street 46 kV circuit. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  | EP | 0 | 7.6 | 7.6 | 2023-11-17 |  |  | FALSE
Baseline | AEP | P23027013 | b3837.1 | Replace existing 34.5 kV, 25 kA circuit breaker B at West Huntington station with new 69 kV, 40 kA circuit breaker. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  | EP | 0 | 0.3648 | 0.3648 | 2023-11-17 |  |  | FALSE
Baseline | AEP | P24004001 | b3838.1 | Replace breaker A and B at Timken station with 40 kA breakers. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  | EP | 0 | 1.2 | 1.2 | 2023-11-17 |  |  | FALSE
Baseline | AEP | P24063001 | b3839.1 | Replace 69 kV breaker C at Haviland station with a new 3000A 40 kA breaker. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  | EP | 0 | 0.4 | 0.4 | 2023-11-17 | Manager4 | 4444 | FALSE
Baseline | AEP | P23877002 | b3843.1 | Rebuild the underground portion of the Ohio University-West Clark 69 kV line, approximately 0.65 miles. | TO Criteria Violation |  | 2028-06-01 |  | 2028-06-01 |  | EP | 0 | 4.6 | 4.6 | 2023-11-17 |  |  | FALSE
Baseline | AEP | P24051001 | b3847.1 | Add a 765 kV breaker at Baker station for the reactor on the Broadford 765 kV line. | Operational Performance |  | 2024-06-01 |  | 2027-06-25 |  | EP | 0 | 23.3564 | 23.36 | 2024-06-05 | PM Jacob Arwood |  | FALSE | RX | 0 | 0
Baseline | AEP | P24052001 | b3847.2 | Add two 765 kV breakers to the reactors at Broadford station on the Baker and Jacksons Ferry 765 kV lines. | Operational Performance |  | 2024-06-01 |  | 2027-06-01 |  | EP | 0 | 29.0472 | 29.05 | 2024-06-05 | PM Blair Burns |  | FALSE | RX | 0 | 0
Baseline | AEP | P24049001 | b3847.3 | Add a 765 kV breaker to the reactor at Jefferson station on the Greentown 765 kV line. | Operational Performance |  | 2024-06-01 |  | 2027-04-15 |  | EP | 0 | 8.5319 | 8.53 | 2024-06-05 | PM Kyle Martin / Planner Sharlene Rivera Gonzalez |  | FALSE | RA1 | 0 | 0
Baseline | AEP | P24084001 | b3851.1 | Rebuild Allen –R.P. Mone 345kV line (18.6 miles). | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  | EP | 0 | 49.875 | 49.875 | 2024-07-10 | PM Shawn Lynch / Planner Valerie Watros |  | FALSE
Baseline | AEP | P24084002 | b3851.2 | Rebuild R.P. Mone – Maddox Creek 345kV line (9.4 miles). | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  | EP | 0 | 39.034 | 39.034 | 2024-07-09 | PM Shawn Lynch / Planner Valerie Watros |  | FALSE
Baseline | AEP | P24092001 | b3851.3 | Replace breakers 'B1' and 'B' at Maddox Creek. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  | EP | 0 | 1.8 | 1.8 | 2024-07-09 | PM Shawn Lynch / Planner Valerie Watros |  | FALSE
Baseline | AEP | P24092002 | b3851.4 | Replace two 345kV breakers 'M' and 'M2' at East Lima Station. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  | EP | 0 | 1.761 | 1.761 | 2024-07-09 | PM Shawn Lynch / Planner Valerie Watros |  | FALSE
Baseline | AEP | P22915001 | b3852.1 | Connect and energize a second 765/345 kV bank at Vassell station. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2026-07-15 |  | EP | 0 | 30.829 | 30.829 | 2024-07-09 |  |  | FALSE
Baseline | AEP |  | b3852.2 | Replace 765 kV breaker D at Maliszewski station. | Baseline Load Growth Deliverability & Reliability |  | 2027-06-01 |  | 2027-06-01 |  | EP | 0 | 2.9 | 2.9 | 2024-07-09 |  |  | FALSE
Baseline | AEP |  | b3872.1 | Adjust the tertiary tap on the Hartford 138/69/34.5 kV transformer 1 and on Hartford 138/69/12 kV transformer 4 to eliminate the high voltage issues and avoid circulating current. | TO Criteria Violation |  | 2029-04-15 |  | 2029-04-15 |  | EP | 0 | 0.1 | 0.1 | 2024-11-15 |  |  | FALSE
Baseline | AEP |  | b3873.1 | Install 12 MVAR 34.5 kV cap bank at Greenleaf | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 1.3139 | 1.3139 | 2024-11-15 |  |  | FALSE | CAP BREAKER | 0 | 0
Baseline | AEP |  | b3875.1 | Reconductor ~3.95 miles of ACSR 6/1 Penguin (4/0) on the Firebrick-Jefferson Switch 69 kV branch with ACSR 556.6 26/7. Remote End (Line setting) would need to be updated at Firebrick and Lick. Replace 600A Switches at Jefferson and replace 477 AA 19 sub conductor at Firebrick. | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 8.5 | 8.5 | 2024-11-15 |  |  | FALSE | [13 empty] | Firebrick | 50/50/63/63 | 102/129/129/129
Baseline | AEP |  | b3876.1 | Install a 69kV 11.5MVar capacitor bank at Richlands station with a circuit switcher. | TO Criteria Violation |  | 2029-12-01 |  | 2029-12-01 |  | EP | 0 | 1 | 1 | 2024-11-15 |  |  | FALSE | EE | 0 | 0
Baseline | AEP |  | b3877.1 | Project will replace station conductor and switches in the 345 kV yard at Beatty that are currently limiting the 345 kV lines to Adkins and Chenoweth | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.5 | 0.5 | 2024-12-03 |  |  | FALSE |  |  |  | Beatty - Adkins 345 kV | 1096/1203/1423/1511 | 1269/1385/1604/1737
Baseline | AEP |  | b3877.2 | Project will upgrade 345 kV circuit breakers 'A' and 'A1' to 4000A 63 kA breakers at Adkins station along with some station conductor that is currently limiting the 345 kV line to Beatty. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 4.5 | 4.5 | 2024-12-03 |  |  | FALSE | A | 50 | 50 | Beatty - Adkins 345 kV | 1080/1203/1368/1511 | 1269/1385/1604/1737
Baseline | AEP |  | b3878.1 | Proposal will upgrade 765 kV circuit breakers 'B' and 'B2' 'to 5000A 50 kA breakers at Marysville station. In addition, the project will upgrade the existing wavetrap towards Sorenson. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 10 | 10 | 2025-01-07 |  |  | FALSE | B | 50 | 50 | Marysville - Sorenson (Shunt Reactor Branch at Marysville) 765 kV | 4047/4142/4484/4961 | 5496/6667/6938/8024
Baseline | AEP |  | b3879.1 | Replace line conductor, ~0.11 miles of 4/0 ACSR 6/1 conductor with 556.5 26/7 between South Toronto and the South Toronto Tap. | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.5 | 0.5 | 2024-11-15 |  |  | FALSE | [13 empty] | South Toronto | 50/50/63/63 | 151/151/196/151
Baseline | AEP |  | b3879.2 | Upgrade the wave trap, CCVTs, switches, and station conductor at South Toronto station currently limiting the line to South Toronto Tap. | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.6 | 0.6 | 2024-11-15 |  |  | FALSE |  |  |  | South Toronto-South Toronto Tap 69 kV | 50/50/63/63 | 151/151/196/196
Baseline | AEP |  | b3880.1 | At Beatty Road substation, install a 69 kV 23 MVAR capacitor bank along with the 69kV Cap bank breaker. | TO Criteria Violation |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 2.25 | 2.25 | 2024-11-15 |  |  | FALSE | AA | 0 | 0
Baseline | AEP |  | b3882.1 | Replace 138 kV circuit breaker BB with higher fault current capable counterpart. | Short Circuit |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 1 | 1 | 2024-11-15 |  |  | FALSE | BB | 0 | 0
Baseline | AEP |  | b3883.1 | 69 kV station equipment, including relays, conductor, and switches, will be replaced at Haviland station in order to address identified overloads on the lines to North Van Wert and Cavett. | TO Criteria Violation |  | 2029-12-01 |  | 2029-12-01 |  | EP | 0 | 0.8 | 0.8 | 2024-11-15 |  |  | FALSE |  |  |  | Cavett - Haviland 69 kV | 57/57/57/57 | 129/180/162/202
Baseline | AEP |  | b3884.1 | Replace the 69 kV circuit breaker D at Van Wert with a 40 kA breaker. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 1 | 1 | 2024-11-15 |  |  | FALSE | D | 0 | 0
Baseline | AEP |  | b3885.1 | Replace 69 kV circuit breakers N and M at Schroyer Avenue station with higher fault current capable counterparts. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 2 | 2 | 2024-11-15 |  |  | FALSE | M | 0 | 0
Baseline | AEP |  | b3886.1 | Replace 69 kV circuit breaker 'A' along with disconnect switches at Benwood substation with a 40 kA Circuit Breaker. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 1 | 1 | 2024-11-15 |  |  | FALSE | A | 0 | 0
Baseline | AEP |  | b3887.1 | Replace Greentown 138kV circuit switcher for Transformer #5 with a 138kV 63kA Circuit Breaker | Short Circuit |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 1 | 1 | 2024-11-15 |  |  | FALSE | XT5 | 40 | 40
Baseline | AEP |  | b3888.1 | Preform sag study and complete mitigations on the 138 kV line between East Leipsic and the AE2-072 tap (Lammer) to allow line's conductor to operate to its maximum operating temperature (MOT). | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 2.5 | 2.5 | 2024-11-15 |  |  | FALSE | [13 empty] | East Leipsic | 223/223/281/281 | 223/310/281/310
Baseline | AEP |  | b3889.1 | Project will replace limiting station equipment at Tiltonsville station to increase the rating on the branch to Windsor | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.8 | 0.8 | 2024-11-15 |  |  | TRUE |  |  |  | Tiltonsville - Windsor (FE) 138 kV | 329/361/419/421 | 329/413/419/421
Baseline | AEP |  | b3890.1 | Replace station conductor at South Coshocton station currently limiting the branch to Ohio Central | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.2 | 0.2 | 2024-11-15 |  |  | FALSE |  |  |  | Ohio Central - South Coshocton 138 kV | 136/167/173/200 | 185/223/281/281
Baseline | AEP |  | b3891.1 | Project will perform relay upgrades at Kenny 138 kV to raise the CT & Relay thermal limits that are currently limiting the line to Roberts. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.4 | 0.4 | 2024-11-15 |  |  | FALSE |  |  |  | Kenny - Roberts | 184/184/184/184 | 213/311/221/318
Baseline | AEP |  | b3892.1 | Replace 69 kV circuit breakers A and S at Mount Vernon station with 40 kA breakers. | TO Criteria Violation |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 2 | 2 | 2024-11-15 |  |  | FALSE | A | 0 | 0
Baseline | AEP |  | b3894.1 | Replace limiting station conductor at Tidd on the line to Carnegie (FE). | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.5 | 0.5 | 2024-11-15 |  |  | FALSE |  |  |  | Tidd - Carnegie 138 kV | 187/240/247/285 | 200/254/253/293
Baseline | AEP |  | b3895.1 | Replace existing 138 kV, 40 kA Circuit Switcher L at Jacksons Ferry Station with new 138 kV, 63 kA Circuit Breaker | Short Circuit |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 1 | 1 | 2024-11-15 |  |  | FALSE | L | 40 | 40
Baseline | AEP |  | b3896.1 | Adjust the capacitor bank voltage settings to allow the cap bank to operate as needed under N-1-1 scenarios. | TO Criteria Violation |  | 2029-12-01 |  | 2029-06-01 |  | EP | 0 | 0.1 | 0.1 | 2024-11-15 |  |  | FALSE
Baseline | AEP |  | b3897.1 | Replace the 138 kV 40kA circuit switcher XT8 with a 63 kA circuit breaker. | Short Circuit |  | 2026-06-01 |  | 2026-06-01 |  | EP | 0 | 1 | 1 | 2024-11-15 |  |  | FALSE | XT8 | 40 | 40
Baseline | AEP |  | b3898.1 | Upgrade the CT thermal limit at Buchanan station on the Buchanan-Keen Mountain 138 kV line. | Baseline Load Growth Deliverability & Reliability |  | 2029-12-01 |  | 2025-12-01 |  | EP | 0 | 0.1 | 0.1 | 2024-11-15 |  |  | FALSE |  |  |  | Buchanan-Keen Mountain 138 kV | 86/86/86/86 | 179/179/179/179
Baseline | AEP |  | b3911.1 | Rebuild the existing 1.1 mile Canal - Gay 138 kV oil filled pipe-type underground line to address overloads on the existing cable utilizing 5000 MCM XLPE cable. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 15.595 | 15.595 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3912.1 | Rebuild the existing 2.2-mile Canal-Mound St 138 kV oil filled pipe-type underground line to address overloads on the existing cable utilizing 5000 MCM XLPE cable. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 31.09 | 31.09 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3913.1 | Rebuild 138 kV line section between Beatty and White Road stations (approximately 4.5 miles). Update remote end relay settings as needed. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 18.8 | 18.8 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3913.2 | Rebuild 138 kV line section between White Road and Cyprus stations (approximately 3.34 miles). Update remote end relay settings as needed. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 14.313 | 14.313 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.1 | Reconfigure Maliszewski 765 kV station from 2 breakers to a 6 breaker ring bus. Install a new 765/345 kV transformer. Establish new 345 kV breaker yard with 3 string breaker and a half to include a line exit to Hyatt and a line exit to Corridor. Loop the existing Hyatt - West Millersport 345 kV line into the new established 345 kV yard at the Maliszewski station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 79.736 | 79.736 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.2 | Establish a 0.18 mile double circuit 345 kV line extension to cut the existing Hyatt – West Millersport 345 kV line in and out of Corridor station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 3.101 | 3.101 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.3 | Install three new 345 kV breakers at Corridor station in order to accommodate the cut in of the Hyatt- West Millersport 345 kV line. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 5.521 | 5.521 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.4 | Reconductor 10.2-mile of Maliszewski-Corridor 345 kV line. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 18.301 | 18.301 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.5 | Reconductor 4.75-miles of the existing Bokes Creek-Marysville 345 kV circuit. Update the associated relay settings. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 6.668 | 6.668 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.6 | Rebuild 4.4-miles of the existing Marysville - Hyatt 345 kV double circuit line where it extends into Marysville station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 26.256 | 26.256 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.7 | Upgrade 345 kV breakers K & K1 along with associated switches and conductor to 5000A at Hyatt Station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 2.944 | 2.944 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.8 | Upgrade the relaying and associated equipment at West Millersport stationto coordinate with the cut in work to Corridor station. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.41 | 0.41 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.9 | Upgrade 3000A 345 kV breaker 'L2' along with associated terminal elements to 5000A at Marysville. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 2.558 | 2.558 | 2024-12-03 |  |  | FALSE
Baseline | AEP |  | b3919.10 | Rebuild ~19.0 miles of Hyatt - Marysville 345 kV line using 4-bundled 795 ACSR conductor Bold construction (This is an EOL rebuild) | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2027-06-01 |  | EP | 0 | 116.7 | 116.7 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.1 | Add one 765 kV breaker at Amos Substation to expand the breaker and a half scheme to accommodate the new Amos-Welton Spring 765 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 30.87 | 30.87 | 2025-01-07 |  |  | TRUE
Baseline | AEP |  | b4000.200 | Broadford 765 kV Upgrade: Replace Jackson's Ferry CB Q2 | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 4.5 | 4.5 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.201 | Smith Mountain 138 kV Upgrade: Replace 795 KCM AAC, 37-Str. 795 KCM AAC, 37-Str. PH A B2S1 B2S2 BS1 BS2 | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.4 | 0.4 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.202 | Rebuild 12.5 miles of Smith Mountain - Redeye 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 14.9 | 14.9 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.203 | Rebuild 17.5 miles of Redeye - Candler's Mountain 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 21 | 21 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.204 | Rebuild 4 miles of Candler's Mountain - Opossum Creek 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 4.9 | 4.9 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.205 | Candler's Mountain 138 kV: Replace 1590 KCM AAC, 61-Str. Replace MOAB "Y" SMITH MTN LINE | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.2 | 0.2 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.206 | Opposum Creek 138 kV: Replace Opossum Creek Switch | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.1 | 0.1 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.207 | Leesville Station Upgrade 138 kV: Replace 795 KCM AAC, 37-Str. IPS Sch. 40 1272 KCM AAC, 61-Str. 1272 KCM AAC, 61-Str. PH A,B,C ALTA VISTA CB-A BUS DISC ALTA VISTA CB-A LINE DISC Wavetrap (1200A) Relay Thermal Limit 1356 Amps | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.6 | 0.6 | 2025-01-07 |  |  | TRUE
Baseline | AEP |  | b4000.208 | Otter 138 kV Station Upgrade: Replace 795 KCM AAC, 37-Str. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 0.1 | 0.1 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.209 | Rebuild 0.9 miles of Altavista - Otter 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 1.2 | 1.2 | 2025-01-07 |  |  | TRUE
Baseline | AEP |  | b4000.210 | Rebuild 7 miles of Otter - Johnson Mountain 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 8.4 | 8.4 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.211 | Rebuild 6.5 miles of Johnson Mountain - New London 138 kV line | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 7.68 | 7.68 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.251 | Replace the wave trap and upgrade the relay at Cloverdale 765kV substation | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 1 | 1 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.252 | Replace the wave trap and upgrade the relay at Joshua Falls 765kV substation | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 1 | 1 | 2025-01-07 |  |  | FALSE
Baseline | AEP |  | b4000.355 | Build a new 156 mile 765kV line from Joshua Falls – Yeat. (Roughly 69.3 miles in AEP section). | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 341.17 | 341.17 | 2025-01-07 |  |  | TRUE
Baseline | AEP |  | b4000.359 | Add (2) 765kV breakers at Joshua Falls substation. Substation expansion is required to add the additional breakers. | Baseline Load Growth Deliverability & Reliability |  | 2029-06-01 |  | 2029-06-01 |  | EP | 0 | 99.19 | 99.19 | 2025-01-07 |  |  | FALSE
Supplemental | AEP | P16123010 | s1297 | Valley Area Reinforcement project | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 |  | UC | 50 | 143 | 143 | 2017-05-31 | Alvaro Rodriguez/ Joshua Smith |  | FALSE
Supplemental | AEP | P16123010 | s1297.5 | At Main Street station, rebuild the entire station on existing property at the site and install a 90 MVA transformer with 3000 A 40 kA breakers. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 |  | UC | 50 | 0 | 0 | 2017-05-31 | Alvaro Rodriguez/ Joshua Smith | 17025 | FALSE
Supplemental | AEP | P12059014 | s1377.3 | Lavalette: Install 138kV MOAB facing West Huntington. Replace high-speed ground switch/MOAB combo on XFR #1 with a circuit switcher. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-17 |  | UC | 50 | 0.1 | 0.1 | 2017-12-18 | PM Aaron Crespin/Planner Michael Hassay | 18321 | FALSE
Supplemental | AEP | P12059003 | s1377.4 | Stone Branch: Replace high-speed ground switch/MOAB combo on XFRs #1 and #2 with circuit switchers. Install 138kV MOABs facing Midkiff and Chapman. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-09-09 |  | UC | 50 | 0.2 | 0.2 | 2017-12-18 | PM Alvaro Rodgriguez/planner Chintan Raval | 18563 | FALSE
Supplemental | AEP | P12059004 | s1377.5 | Chapman: Retire Trace Fork S.S. and 4-way switch and replace with Chapman Switching Station located ~1 mile away. Install 4 138kV 3000 A 40 kA CB ring bus at new Chapman. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-08 |  | UC | 50 | 5.7 | 5.7 | 2017-12-18 | PM Alvaro Rodgriguez/planner Chintan Raval | 18242 | FALSE
Supplemental | AEP | P12059009 | s1377.7 | Construct an 8 mile 138kV double circuit line between Sheridan and Midkiff utilizing 1033.5 ACSR (375/464 MVA winter ratings) and OPGW. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-12-12 |  | UC | 50 | 25.7 | 25.7 | 2017-12-18 | PM Alvaro Rodgriguez/planner Chintan Raval | 18242 | FALSE
Supplemental | AEP | P12059009 | s1377.8 | Construct a 17 mile 138kV line between Midkiff and Stone Branch utilizing 1033.5 ACSR (375/464 MVA winter ratings) and OPGW. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-12-12 |  | UC | 50 | 28.1 | 28.1 | 2017-12-18 | PM Alvaro Rodgriguez/planner Chintan Raval | 18242 | FALSE
Supplemental | AEP | P12059011 | s1377.9 | Construct 138kV double circuit line from Chapman to existing 138kV Stone Branch – Trace Fork line utilizing 1033.5 ACSR (375/464 MVA winter ratings). Install OPGW on new line sections. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-08 |  | UC | 50 | 5.5 | 5.5 | 2017-12-18 | PM Aaron Crespin/Planner Chintan Rival | 18242 | FALSE
Supplemental | AEP | P12059011 | s1377.10 | Construct 138kV double circuit line from Chapman to existing 138kV Logan – Hopkins line utilizing 1590 ACSR (493/624 MVA winter ratings) to match the existing Logan-Hopkins line capabilities. Install OPGW on new line sections. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-02-13 |  | UC | 50 | 5.7 | 5.7 | 2017-12-18 | PM Aaron Crespin/Planner Michael Hassay | 17929 | FALSE
Supplemental | AEP | A15701002 | s1414 | Anaconda 34.5 kV Station Rebuild | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-18 |  | UC | 31 | 1.49 | 1.49 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | A15701181 | s1414.1 | Anaconda : Retire the current Anaconda 34.5KV station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-31 |  | UC | 31 | 0.04 | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | A15701063 | s1414.2 | Anaconda Tap switch : Retire Anaconda Tap and reconnect Hummel Creek – Deer Creek circuit | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-18 |  | UC | 31 | 0.01 | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | A15701200 | s1414.3 | Wire Mill: Install a 4kV bus with a CB protecting the Anaconda load; Install a 34.5kV bus; Install a 6.25MVA 69/34.5/4kV non-LTC transformer to connect the 4kV and 34.5kV busses; Install a circuit switcher on the high side of the transformer | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-22 |  | UC | 50 | 0.02 | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | A15041032 | s1414.4 | Shunk Street Switch: Install a new 1200A 3 way PoP ground operated switching structure | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-22 |  | UC | 31 | 0 | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | A15041032 | s1414.5 | Fifth Street Extension: Install roughly .5 miles of 556.5 ACSR (WE: 80MVA) from Shunk Street Switch to the new station location. This line will be built to 69kV but operated at 34.5kV | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-22 |  | UC | 50 | 0 | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | A15701063 | s1414.6 | Anaconda Tap: Retire the Anaconda - Anaconda Tap 34.5kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-18 |  | UC | 31 | 0 | 0 | 2017-12-18 | PM Jarrod Combs/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | A16803026 | s1431 | Rebuild ~11 miles of the Hopkins – Sharples circuit including ~2.6 miles of the Hopkins – Bim line that is double circuited with Hopkins – Sharples. Replace switches at Hewett station with 1200A 3-way Phase Over Phase switch. On all lines, install OPGW. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-20 |  | UC | 50 | 23.7 | 61.73 | 2020-11-20 | PM Chance Strausbough/planner Michael Hassay |  | FALSE
Supplemental | AEP | A16801111 | s1432.1 | Rebuild from Ross to Heppner Sw (formerly Coalton Sw). Single Circuit 138kV Rebuild (Energized at 69kV) with 1033 ACSR Curlew Conductor (148 MVA SN rating) | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-25 |  | UC | 50 | 46.2 | 46.2 | 2018-01-08 | PM Robert Howard/ planner Peter Jones |  | FALSE
Supplemental | AEP | A16801096 | s1493.2 | Rebuild single circuit 69kV line from Harrison to Madison with 795 ACSR (129 MVA rating), mostly in existing ROW | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-08-09 |  | EP | 35 | 23.4 | 23.4 | 2018-02-14 | planner Nathen Roberts |  | FALSE
Supplemental | AEP | A16801130 | s1493.3 | Rebuild tap to Darbyville as double circuit 795 ACSR (129 MVA rating) | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-16 |  | On Hold | 50 | 0.9 | 0.9 | 2018-02-14 | Brooks Arbogast/ Nathen Roberts |  | FALSE
Supplemental | AEP | P19015021 | s1590 | At Butler station, replace 69 kV breaker “A”, replace 69 kV MOABs “X” and “Y” with 69 kV breakers, replace 69 kV cap switchers “AA” and “BB” (S&C Mark V) with 3000 A, 40 kA circuit breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-01-16 |  | EP | 25 | 2.5 | 2.5 | 2018-04-17 | Tom Newlon/ Michael Van Schaik |  | FALSE
Supplemental | AEP | P17002006 | s1606.3 | At McComb station, replace 2-138kV 1600A 40kA CB’s 101C & 101E and disconnect switches with 3,000A 40kA CB’s. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-06-25 |  | EP | 10 | 1.3 | 1.3 | 2018-04-17 | PM Crystal Wood-Hython/planner Nathen Roberts |  | FALSE
Supplemental | AEP | P15082C34 | s1611.3 | At Twin Branch Station, upgrade risers towards South Bend. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-01-01 |  | UC | 50 | 1.8 | 1.8 | 2018-05-03 | PM Dan Ballmer/planner Joshua Smith |  | FALSE
Supplemental | AEP | P16123034 | s1622.1 | Rebuild the roughly 43 miles from the Twin Branch to Riverside station with double circuit 138kV 1033.5 ACSR (296 MVA rating). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | UC | 50 | 94.3 | 94.3 | 2018-05-21 | Alvaro Rodriguez/ Joshua Smith |  | FALSE
Supplemental | AEP | P19031001 | s1622.3 | Rebuild the 5 mile double circuit Hickory Creek 138kV Extension with double circuit 138kV 1033.5 ACSR. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-09-13 |  | EP | 15 | 16.5 | 16.5 | 2018-05-21 | PM Warren Peterson/Planner Michael Van Schaik |  | FALSE
Supplemental | AEP | P17225003 | s1687.2 | Construct a 2.7 mile 138 kV line extension between Moore Hollow and Kentucky Electric Steel. At this time the existing KES metering structure will be retired due to the announced closure of the KES plant. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-06-23 |  | EP | 15 | 8.4 | 8.4 | 2018-08-31 | M. Shawn Smith/ Chintan Raval |  | FALSE
Supplemental | AEP | P17225027 | s1687.3 | At Chadwick Station, remote end relaying work will be required. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-06-23 |  | EP | 15 | 0.4 | 0.4 | 2018-08-31 | M. Shawn Smith/ Chintan Raval |  | FALSE
Supplemental | AEP | P17225006 | s1687.4 | Construct a new greenfield 138/19 kV station, named Ramey, tapping the Bellefonte - Grangston 138 kV circuit. Four 138 kV CBs (3000 A 40 kA) will be installed as well as a 138/19 kV transformer (25 MVA). AEP already owns the land at the proposed Ramey station site. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-06-23 |  | EP | 5 | 0 | 0 | 2018-08-31 | M. Shawn Smith/ Chintan Raval |  | FALSE
Supplemental | AEP | P17225013 | s1687.5 | Construct a new 2.8 mile 138 kV extension from Ramey to the existing Bellefonte - Coalton line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-12-08 |  | EP | 15 | 10.5 | 10.5 | 2018-08-31 | PM M. Shawn Smith/planner Chintan Raval |  | FALSE
Supplemental | AEP | P17225017 | s1687.6 | Convert the existing Bellefonte to Coalton 69 kV line between Bellefonte and Princess to 138 kV (line is built to 138 kV standards). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-12-08 |  | EP | 15 | 3.8 | 3.8 | 2018-08-31 | PM M. Shawn Smith/planner Chintan Raval |  | FALSE
Supplemental | AEP | P17225010 | s1687.8 | Convert Hoods Creek station to 138 kV by rebuilding the station in the adjacent lot with a 138/12 kV XF. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-12-08 |  | EP | 15 | 0 | 0 | 2018-08-31 | PM M. Shawn Smith/planner Chintan Raval |  | FALSE
Supplemental | AEP | P17225015 | s1687.10 | Construct 3.4 mile 138 kV line between Princess and Moore Hollow stations. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-06-23 |  | EP | 15 | 11.5 | 11.5 | 2018-08-31 | M. Shawn Smith mssmith@aep.com (540)759-5581/ Chintan Raval craval@aep.com (614)933-2219 |  | FALSE
Supplemental | AEP | P16121002 | s1692.1 | Build a new 8.5 mile 69 kV line from Friendship Station to Central Portsmouth Station, using 556 ACSR (102 MVA) and remove the old Central Portsmouth-Sugar Hill Line. Rebuild the remaining 13.9 miles of the Friendship Loop from North Portsmouth to Rosemount, from Rosemount to Sugar Hill and from Sugar Hill to Friendship using 556 ACSR (102 MVA) and ADSS. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-12-21 |  | UC | 50 | 41.8 | 41.8 | 2018-08-31 | PM Michael Deskin/planner Peter Jones |  | FALSE
Supplemental | AEP | P16121012 | s1692.2 | At Friendship station, install a 69 kV line CB & line MOAB. At Sugar Hill station, upgrade bus though-path and replace switches to accommodate the line reconfigurations. At North Portsmouth, replace 138-69 kV transformer with a 90 MVA unit with a 138 kV circuit switcher, replace 138 kV CB C and 69 kV CB A. Remove bus tie 138 kV CB D and install a new 138 kV CB to isolate Millbrook Park line. Install a new 69 kV CB on low side of the transformer. At Millbrook Park, replace relay & install a CCVT on North Portsmouth Line. At Central Portsmouth, replace 138 kV CBs G & H. At Rosemount, install two line MOAB switches inside substation and replace the ground switch MOAB with a 69 kV circuit switcher. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-21 |  | UC | 50 | 12.6 | 12.6 | 2018-08-31 | PM Michael Deskin/planner Peter Jones |  | FALSE
Supplemental | AEP | A16922004 | s1851 | Construct a new 69 kV line (approximately 14.25 miles) from Jubal Early Station to Point Lookout Station. Install a 69 kV circuit breaker at Jubal Early Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-22 |  | UC | 50 | 32.5 | 42.7 | 2021-05-21 | PM Charles Linkous/planner Bobby Valerio |  | FALSE
Supplemental | AEP | P22060001 | s1851.1 | Relocate Independence Station to a new property and rebuilt as Point Lookout Station. Point Lookout Station will consist of a 69 kV bus, a 11.5 MVAR cap bank, two 69 kV circuit breakers. The station will also include a 69/34.5 kV 30 MVA transformer with two 34.5 kV distribution circuit breakers and a 69/12 kV 20 MVA transformer with one 12 kV distribution circuit breaker. The new cap bank at Point Lookout Station is replacing the existing cap bank at Fries Station due to the space limitations at Fries Station associated with remote end work. The cap bank at Fries Station can not be retired due to a voltage violation scenario and the new cap bank will maintain the voltages above our criteria thresholds. Estimated Transmission Cost: $0 (station is considered Distribution) | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-22 |  | EP | 0 | 0 | 32.5 | 2021-05-17 |  |  | FALSE
Supplemental | AEP | P21593001 | s1854.3 | Rebuild the 34.5 kV voltage class 23rd Street substation as a six (6) breaker ring bus with five (5) new 69 kV-rated breakers. Install three (3) 138 kV breakers to form a ring bus on the high side. Retire the cap banks. Rebuild the underground line exits as overhead. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-08-16 |  | EP | 25 | 0 | 11.9 | 2019-08-28 | PM Gray Adam/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | P17081003 | s2000.2 | Rebuild Esmont-Scottsville 46 kV line section (~6.0 mi.) | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 |  | UC | 50 | 17 | 17 | 2019-05-20 | PM Mark Scotwinterll/planner Bobby Valerio |  | FALSE
Supplemental | AEP | P18144010 | s2012.1 | Retire the ~10.5 mile South Summitville – Jonesboro 34.5 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-24 |  | EP | 15 | 1.6 | 1.6 | 2019-04-23 | PM Tom Newlon/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | P18241012 | s2013.2 | Retire the Deer Creek – Miller Ave 34.5 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-30 |  | UC | 50 | 0.6 | 0.6 | 2019-05-20 | PM Jarrod Combs/planner Michael Van Schaik |  | FALSE
Supplemental | AEP | P18241021 | s2013.5 | Re-route the Atlas Tap 34.5kV line into West End station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-07-02 |  | UC | 50 | 0.5 | 0.5 | 2019-05-20 | Jarrod Combs/ Michael Van Schaik |  | FALSE
Supplemental | AEP | P18244005, P18244006, P18244007, P18244008, P18244009, P18244010, P18244011, P18244012 | s2014 | Rebuild the 62 mile College Corner – Jay 138 kV line as single circuit 138 kV. New conductor will be 795 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-31 |  | EP | 1 | 113.5 | 113.5 | 2019-05-20 | PM Kent Hice/planner Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | P20236005, P20236012 | s2017.1 | Replace both 34.5 kV breakers “L” and “M” at Hummel Creek station with system spares. Install a high side circuit switcher on transformer 1. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-31 |  | EP | 15 | 2.6 | 2.6 | 2019-06-17 | Jarrod Combs/ Michael Van Schaik |  | FALSE
Supplemental | AEP | P20236006 | s2017.2 | Remove the existing 34.5 kV breaker at Gas City station and re-use the existing switch as a MOAB. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-16 |  | EP | 25 | 0 | 0 | 2019-06-17 | Jarrod Combs/ Michael Van Schaik |  | FALSE
Supplemental | AEP | P18141023 | s2060.11 | Install 69 kV 1200 A phase over phase switch (Fliprock Switch) at National Lime & Stone hard tap. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-04-08 |  | EP | 25 | 2.4 | 2.4 | 2019-09-25 | Michael Fackler/ Patrick Hodgson |  | FALSE
Supplemental | AEP | P17002028 | s2062.1 | Extend the Wilson - Hess 138 kV line to the new 138 kV bus at Fifth Avenue station and install fiber between Fifth Ave and Hess. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-07-31 |  | EP | 10 | 1.1 | 1.1 | 2019-09-25 | Denise Binford/ Nathen Roberts |  | FALSE
Supplemental | AEP | DP19C09Z0 | s2062.2 | At Fifth Avenue substation, install new 138 kV bus work in ring bus configuration. Install two (2) 138 kV breakers and associated switches on new bus work rated at 3000 A/63 kA. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-04-25 |  | EP | 10 | 2.9 | 2.9 | 2019-09-25 | PM Denise Binford/planner Nathen Roberts |  | FALSE
Supplemental | AEP | DP19C09D1 | s2062.3 | Remote end work at Wilson Road station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-02-14 |  | EP | 10 | 0.5 | 0.5 | 2019-09-25 | PM Denise Binford/planner Nathen Roberts |  | FALSE
Supplemental | AEP | DP19C09D2 | s2062.4 | Remote end work at Hess station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-12-10 |  | EP | 15 | 0.6 | 0.6 | 2019-09-25 | PM Denise Binford/planner Nathen Roberts |  | FALSE
Supplemental | AEP | P19031003 | s2090.1 | Rebuild 6.7 miles of the 34.5 kV circuit Main Street-Hickory Creek circuit using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-09-13 |  | EP | 15 | 19.5 | 19.5 | 2019-12-05 | PM Warren Peterson/Planner Michael Van Schaik |  | FALSE
Supplemental | AEP | P19031006 | s2090.2 | Rebuild the 0.5 miles of the Langley-Main Street 34.5 kV branch starting from the Langley station using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 |  | EP | 15 | 3 | 3 | 2019-12-05 | PM Warren Peterson/Planner Michael Van Schaik |  | FALSE
Supplemental | AEP | P19015026 | s2098.4 | Build a 0.04 mile long greenfield line with 556 ACSR to eliminate the hard tap on the Butler - Hicksville Junction 138 kV Line. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 25 | 0.4 | 0.4 | 2019-12-05 | PM Tom Newlon/planner Michael Van Schaik |  | FALSE
Supplemental | AEP | P19015021 | s2098.6 | At Butler 69kV station, install three (3) 69 kV breakers and two (2) Cap Banks to accommodate the line loops. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 25 | 5.5 | 5.5 | 2019-12-05 | PM Tom Newlon/planner Michael Van Schaik |  | FALSE
Supplemental | AEP | P19015006 | s2098.11 | Remove Metcalf tap from the Butler-North Hicksville 69kV line and reconnect the through path. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | UC | 50 | 1 | 1 | 2019-12-05 | Tom Newlon/ Michael Van Schaik |  | FALSE
Supplemental | AEP | P19198004 | s2098.12 | Remote end relay upgrades at North Hicksville 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-31 |  | EP | 15 | 1 | 1 | 2019-12-05 |  |  | FALSE
Supplemental | AEP | P19008001, P19008003, P19008005, P19008013 | s2145.1 | Rebuild the Amos – Hopkins 138 kV circuit from structure 124-8A to Hopkins station as single circuit (~19.6 miles), including structure work near Saint Albans Tap and Angel Branch Tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-16 |  | UC | 50 | 61.3 | 61.3 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19140004 | s2146.1 | Rebuild the ~3 miles of overhead between Delaware and Bethel 34.5 kV stations. ~2.5 miles will be rebuilt as overhead and ~.5 miles will be rebuilt as underground. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-02 |  | UC | 35 | 16.8 | 16.8 | 2019-11-22 |  |  | FALSE
Supplemental | AEP | P19140001 | s2146.2 | Rebuild the ~1 mile of underground between Kenmore and Bethel 34.5 kV stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-02 |  | UC | 75 | 12.8 | 12.8 | 2019-11-22 |  |  | FALSE
Supplemental | AEP | P19024005 | s2147.3 | At Highland Terrace, install a three-way 1200 A, 69 kV switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-25 |  | UC | 35 | 0.7 | 0.7 | 2019-11-22 | David Sanchez |  | FALSE
Supplemental | AEP | P19082002 | s2149.1 | Ravin: Build a greenfield station at 69 kV 2000 A 40 kA in a 3-breaker ring configuration next to Jelloway (L.R. Co-op). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-06-13 |  | EP | 25 | 8.6 | 8.6 | 2019-11-22 | Isaac Rhodes |  | FALSE
Supplemental | AEP | J19082007, K19082008 | s2149.2 | Jelloway Co-op – Ravin 69 kV: Build ~0.01 miles of greenfield 69 kV line to connect Ravin to Jelloway Co-op. Under emergency conditions Jelloway can be fed radially from North Liberty Switch. North Liberty Switch will be normally open towards Jelloway Co-op. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-05-01 |  | UC | 35 | 0.7 | 0.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19082019 | s2149.3 | Stillwell Switch: Install a greenfield 69 kV 1200 A 3-way POP switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-08-01 |  | EP | 25 | 0.8 | 0.8 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | J19082002 | s2149.4 | Stillwell Switch – Ravin 69 kV: Build ~11.4 miles of greenfield 69 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-05-01 |  | EP | 25 | 26.4 | 26.4 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19082022 | s2149.5 | Hanover Switch: Install a greenfield 69 kV 1200 A 3-way POP switch (near existing Loudonville). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-08-01 |  | EP | 25 | 0.8 | 0.8 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | J19082004 | s2149.6 | Hanover Switch – Ravin 69 kV: Build ~5.17 miles of greenfield 69 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-05-01 |  | EP | 25 | 12.9 | 12.9 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19082022 | s2149.7 | Loudonville (L.R. Co-op) Station – Hanover Switch: Reconnect the Loudonville (L.R. Co-op) Station to the new Hanover 69 kV Switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-05-01 |  | EP | 25 | 0.7 | 0.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193067 | s2149.8 | Fort Fizzle (Replaces Glenmont Junction Sw): Build a new greenfield 69 kV station in an in/out configuration with 1200 A switches to replace Glenmont Junction Switch. Remove existing Glenmont station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | EP | 25 | 1.1 | 1.1 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193029 | s2149.9 | Fort Fizzle – Stillwell 69 kV: Rebuild ~7.07 miles of the existing Glenmont Junction -Stillwell 34.5 kV line at 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | EP | 25 | 16.7 | 16.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193028 | s2149.10 | Fort Fizzle – Killbuck 69 kV: Rebuild ~5.51 miles of the existing Killbuck to Glenmont (Fort Fizzle) 34.5 kV line at 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | EP | 25 | 12.9 | 12.9 | 2019-11-22 | Isaac Rhodes |  | FALSE
Supplemental | AEP | P19193063 | s2149.11 | Black Diamond (Replaces South Millersburg): Build a greenfield station at 138 kV 3000 A 40 kA in 4-breaker ring configuration. Replace the 138/34.5 kV 25 MVA transformer with a 138/69 kV 90 MVA transformer. Remove the 34.5 kV circuit breaker “C” and install a new 69 kV 2000 A 40 kA circuit breaker towards Killbuck. Remove the 34.5 kV 3000 A kVAR Cap bank “AA”. The Buckhorn (H.WN. Co-op) 138 kV delivery point will now connect to Black Diamond station. Remove South Millersburg station and Buckhorn switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 10.2 | 10.2 | 2019-11-22 | Isaac Rhodes |  | FALSE
Supplemental | AEP | P19193027 | s2149.12 | Black Diamond – Killbuck 69 kV: Rebuild ~4.12 miles of the existing South Millersburg (Black Diamond) to Killbuck 69 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 6.4 | 6.4 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193061 | s2149.13 | Black Diamond 138 kV Line Extension: Build ~0.56 miles of greenfield 138 kV line (556 ACSR) to connect Black Diamond 138 kV to the existing West Millersburg 138 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 1.7 | 1.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193023 | s2149.14 | Ohio Central – West Millersburg 138 kV circuit: Remove ~.9 miles of the Ohio Central – West Millersburg 138 kV circuit and reroute into Black Diamond station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 0.7 | 0.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193050 | s2149.15 | Buckhorn (H.WN Co-op) – South Millersburg 138 kV line: Build a new 138 kV line (~.8 miles) to reconnect the existing Buckhorn (H.WN Coop) into Black Diamond 138 kV station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 2 | 2 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193033 | s2149.16 | Millersburg: Cut the Berlin – West Millersburg 69 kV line into Millersburg station with an in/out configuration with 1200 A line switches. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 2.8 | 2.8 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193068 | s2149.17 | Schlegel (Replaces Ripley Switch): Build a greenfield station at 69 kV 40 kA 2000 A in a 4-breaker ring configuration next to Ripley (H.WN. Co-op)’s station. Remove the existing Ripley and Paint Valley switches and reconnect the lines into the new Schlegel station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 9.5 | 9.5 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193021 | s2149.18 | Shreve – Schlegel 69 kV: Relocate the existing Shreve to Ripley 69 kV line to Schlegel station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 0.6 | 0.6 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193022 | s2149.19 | West Millersburg – Schlegel 69 kV: Relocate the existing West Millersburg to Paint Valley 69 kV line to Schlegel station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 0.6 | 0.6 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193069 | s2149.20 | West Nashville: Install a 69 kV 1200 A 3-way POP switch (near existing Drake Valley (H.WN. Co-op)). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 0.7 | 0.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193008 | s2149.21 | Millersburg – West Millersburg 34 kV: Retire ~1.24 miles of the existing Millersburg to West Millersburg 34 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | UC | 35 | 0.1 | 0.1 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19193007 | s2149.22 | Millersburg - South Millersburg 34 kV: Retire ~2.93 miles of the existing Millersburg to South Millersburg 34 kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | EP | 25 | 0.9 | 0.9 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194001 | s2149.23 | South Killbuck Switch: Replace 2-way POP with a 3-way 69 kV 1200 A POP switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 0.6 | 0.6 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194027 | s2149.24 | South Killbuck – Killbuck H.WN. Co-op 69 kV: Rebuild ~0.05 miles of the South Killbuck to Killbuck Holmes Wayne Co-op 34 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 0.7 | 0.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194003 | s2149.25 | Metham Switch: Replace 2-way POP with a 3-way 69 kV 1200 A POP switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 0.6 | 0.6 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194040 | s2149.26 | Metham – Jefferson (F.P. Co-op) 69 kV: Rebuild ~0.38 miles of the Metham to Jefferson (F.P. Co-op) 34.5 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-25 |  | EP | 25 | 1.2 | 1.2 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194036 | s2149.27 | Simmons Run – Killbuck 69kV: Rebuild ~10.4 miles of the South Coshocton to Killbuck34.5 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 31.1 | 31.1 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194062 | s2149.28 | Simmons Run (Replaces Warsaw Switch): Build a greenfield station at 69 kV 2000 A 40 kA in 3-breaker ring configuration. Remove existing Warsaw switching. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 8.7 | 8.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194039 | s2149.29 | South Warsaw – Tunnel Hill (F.P. Co-op) 69 kV: Rebuild ~3.73 miles of the existing South Warsaw to Tunnel Hill (F.P. Co-op) 34.5 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-01-15 |  | EP | 25 | 9.3 | 9.3 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194005 | s2149.30 | Moscow Switch: Replace 2-way POP with a 3-way 69 kV 1200 A POP switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 0.6 | 0.6 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194023 | s2149.31 | Moscow – Jackson (F.P Co-op) 69 kV: Rebuild ~1.24 miles of the existing Moscow to Jackson (F.P. Co-op) 34.5 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 3.5 | 3.5 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194020 | s2149.32 | South Coshocton - Simmons Run 69 kV: Rebuild ~14.4 miles of the existing South Coshocton to Killbuck 34 kV line to 69 kV. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 31.7 | 31.7 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19194012 | s2149.33 | South Coshocton: Build a 138 kV 3000 A 40 kA 5-breaker ring bus and install a 138/69 kV 130 MVA transformer. Install 3 new 69 kV 1200A 40 kA circuit breakers on the line towards Simmons Run, towards Coshocton, and on the low side of the transformer. Retire and remove the 138/69 kV 75 MVA transformer #2, as well as the 69/34.5 kV 35 MVA transformer #3. Leave the 138/34.5 kV 30 MVA transformer #1 to serve San Cast customer. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-09-23 |  | EP | 25 | 10.9 | 10.9 | 2019-11-22 | Shaun Lopez |  | FALSE
Supplemental | AEP | P19052027 | s2153.1 | Rebuild the ~9.5 miles of the Kingsland – Bluffton – Adams circuit as 6-wired 138 kV design structures. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | UC | 35 | 28.5 | 28.5 | 2019-12-18 | Robert Renner |  | FALSE
Supplemental | AEP | P19052025 | s2153.2 | Build ~4.5 mile greenfield from Uniondale station to Ossian station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | EP | 10 | 8 | 8 | 2019-12-18 | Robert Renner |  | FALSE
Supplemental | AEP | P19052002 | s2153.3 | Rebuild the Bluffton – Hillcrest 69 kV line as the ~26 mile Bluffton to Pleasant circuit as 6-wired 138 kV design structures. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | EP | 10 | 67.1 | 67.1 | 2019-12-18 | Tom Newlon |  | FALSE
Supplemental | AEP | P19052001 | s2153.4 | Build the ~3.3 mile Pleasant to Kinnerk circuit as 6-wired 138 kV design structures. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | EP | 10 | 9.6 | 9.6 | 2019-12-18 | Robert Renner |  | FALSE
Supplemental | AEP | P19052011 | s2153.5 | Install one 138 kV rated POP switch to feed Kinnerk’s load. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | EP | 10 | 0.4 | 0.4 | 2019-12-18 | Robert Renner |  | FALSE
Supplemental | AEP | P19052010 | s2153.6 | Replace 2 69 kV CB’s toward Bluffton and Pleasant at Kingsland. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | EP | 10 | 1.6 | 1.6 | 2019-12-18 | Robert Renner |  | FALSE
Supplemental | AEP | P19052011 | s2153.7 | Install the new 69 kV switch called Skips Place to feed the Uniondale load. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | EP | 10 | 0.3 | 0.3 | 2019-12-18 | Robert Renner |  | FALSE
Supplemental | AEP | P19052008 | s2153.8 | Install 69 kV switch called Thiele to feed Kinnerk load. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | EP | 10 | 0.6 | 0.6 | 2019-12-18 | Robert Renner |  | FALSE
Supplemental | AEP | P19052007 | s2153.9 | Remove CB “F” at Hillcrest station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-19 |  | EP | 10 | 0.1 | 0.1 | 2019-12-18 | Robert Renner |  | FALSE
Supplemental | AEP | P19248004 | s2154.3 | Relocate the Firebrick – Lick 69 kV circuit associated with station work at Lick. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-03-05 |  | UC | 35 | 0.8 | 0.8 | 2019-12-18 | Michael Trauntvein |  | FALSE
Supplemental | AEP | A15043156 | s2159 | South Point Sporn | Operational Flexibility and Efficiency |  |  |  | 2024-11-21 |  | EP | 0 | 0 | 0 | 2019-12-18 |  |  | FALSE
Supplemental | AEP | A15043156 | s2159.1 | Install 3-way 138 kV (2000 A) MOAB’s at Mercerville hard tap, including dead end structures to connect to new switch pole location. | Operational Flexibility and Efficiency |  |  |  | 2024-11-21 |  | EP | 0 | 2.2 | 2.2 | 2019-12-18 | Elmann Cabotage |  | FALSE
Supplemental | AEP | A15043157 | s2159.2 | Install 3-way 138 kV (2000 A) MOAB’s at Windsor hard tap. | Operational Flexibility and Efficiency |  |  |  | 2025-05-12 |  | UC | 50 | 1.3 | 1.3 | 2019-12-18 | Elmann Cabotage |  | FALSE
Supplemental | AEP | P19310001 | s2159.3 | Install 3-way 138 kV (2000 A) MOAB’s at Fayette hard tap. Extend the existing line 0.25 miles to the new switch location. | Operational Flexibility and Efficiency |  |  |  | 2024-11-18 |  | UC | 50 | 3.5 | 3.5 | 2019-12-18 | Justin Robb | Winter 20 | FALSE
Supplemental | AEP | P19150009 | s2160 | Rebuild the existing 31.6-mile Crooksville - North Newark 138 kV line using 795 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-16 |  | UC | 35 | 55.6 | 55.6 | 2019-12-18 | Michael Deskin |  | FALSE
Supplemental | AEP | P18255001 | s2165.1 | Rebuild the existing Bancroft – Nitro 69kV line (~8.1 miles) to 69 kV standards. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-14 |  | UC | 35 | 27.3 | 27.3 | 2019-12-18 | Shaun Lopez |  | FALSE
Supplemental | AEP | P17078055 | s2167 | Niles Area Improvements | Equipment Material Condition, Performance and Risk |  |  |  | 2028-08-09 |  | EP | 0 | 0 | 0 | 2019-12-18 |  |  | FALSE
Supplemental | AEP | P17078003 | s2167.1 | At Kenzie Creek station, install a 138/69 kV XFR, 3 138 kV breakers, 5 69 kV breakers and a 14.4 Mvar cap bank to allow for the retirement of Pokagon’s 69 kV transmission yard. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-02 |  | EP | 0 | 12 | 12 | 2019-12-18 | Scott Joseph |  | FALSE
Supplemental | AEP | P17078060 | s2167.2 | At Pokagon station, retire the 69 kV voltage class and re-organize this station as a 138/12 kV station only. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-05 |  | UC | 35 | 2 | 2 | 2019-12-18 | Scott Joseph |  | FALSE
Supplemental | AEP | P17078006 | s2167.3 | At Lake Street station, install a new 69/12 kV load delivery point, replace XFR 1 with a 50 MVA bank, and replace 34.5 kV CB “H” and 69kV Breaker “A” | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-29 |  | UC | 35 | 7.8 | 7.8 | 2019-12-18 | Scott Joseph |  | FALSE
Supplemental | AEP | P19159008 | s2167.4 | At Niles station, replace 69 kV breakers “B” and “A”. Replace XFR 2 and the breaker toward the City of Niles | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-15 |  | EP | 0 | 6.2 | 6.2 | 2019-12-18 | Michael Fisher |  | FALSE
Supplemental | AEP | P19142001 | s2167.5 | Route the Dailey, Barret and Lake St 69 kV lines into Kenzie Creek station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-03 |  | EP | 0 | 2.8 | 2.8 | 2019-12-18 | Scott Joseph/Joshua Smith |  | FALSE
Supplemental | AEP | P17078005 | s2167.6 | Build the new 138/69/34 kV Boundary station to serve the new 34.5 kV distribution load and to separate the Swanson and University Park load form the network. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-05 |  | EP | 0 | 13.6 | 13.6 | 2019-12-18 | Scott Joseph |  | FALSE
Supplemental | AEP | P17078034 | s2167.7 | Build the ~2 mile 138 kV double ckt Boundary Extension | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-30 |  | EP | 0 | 4.4 | 4.4 | 2019-12-18 | Scott Joseph |  | FALSE
Supplemental | AEP | P19142002 | s2167.8 | Rebuild the Pokagon – Niles 69 kV line as the ~9.3 mile Kenzie – Niles 69 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-03 |  | EP | 0 | 22.8 | 22.8 | 2019-12-18 | Scott Joseph/Joshua Smith |  | FALSE
Supplemental | AEP | P19159010 | s2167.9 | Rebuild the ~11.8 mile South Bend – Niles 69 kV line as the South Bend – Boundary – Niles 69 kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-15 |  | EP | 0 | 26.6 | 26.6 | 2019-12-18 | Michael Fisher |  | FALSE
Supplemental | AEP | P19159005 | s2167.10 | Install a 69 kV bus tie CB at Swanson station to separate the 4 Moabs in series. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-15 |  | EP | 0 | 2.1 | 2.1 | 2019-12-18 | Michael Fisher |  | FALSE
Supplemental | AEP | P19159006 | s2167.11 | Replace the switch pole for University Park 69 kV. The new PoP Switch pole will be called “Peppermint Switch”. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-22 |  | EP | 0 | 1 | 1 | 2019-12-18 | Michael Fisher |  | FALSE
Supplemental | AEP | P19073001 | s2177.1 | Rebuild the Carbondale – Kincaid 46 kV lines as a single circuit 46 kV line (~16.3 miles). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-03 |  | UC | 50 | 50.7 | 50.7 | 2020-01-17 | Scott Joseph/Joshua Smith |  | FALSE
Supplemental | AEP | P19073006 | s2177.2 | Retire the Carbondale – Kincaid #1/#2 double circuit 46 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-19 |  | UC | 35 | 9.1 | 9.1 | 2020-01-17 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | P19073002 | s2177.3 | Alloy Station: Install a 2-way switch to address hard tap. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-09-09 |  | UC | 50 | 0.9 | 0.9 | 2020-01-17 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | P19073012 | s2177.5 | Raynes Meter Station: Remove/retire station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-16 |  | EP | 0 | 0.3 | 0.3 | 2020-01-17 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | P19073009 | s2177.6 | Boomer Station: Remove/retire station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-19 |  | EP | 0 | 0.1 | 0.1 | 2020-01-17 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | DP19H05W0 | s2178.2 | Construct a new 138 kV line (~10 mi.) from Kenna to the existing Sisson 138 kV station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-11-05 |  | UC | 75 | 25.5 | 25.5 | 2020-01-17 | Frank Jenkins |  | FALSE
Supplemental | AEP | P18100051 | s2179.1 | Construct ~12.5 miles 138 kV line from Alum Ridge - Claytor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-11-01 |  | UC | 35 | 40.78 | 40.78 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100040 | s2179.2 | Construct ~6.5 miles 138 kV line from Alum Ridge - Floyd. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-02 |  | UC | 35 | 23.85 | 23.85 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100048 | s2179.4 | Construct ~1.25 miles of double circuit 138 kV line to connect Stanleytown. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-16 |  | UC | 35 | 2.35 | 2.35 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100038 | s2179.6 | Construct ~1.2 miles of 138 kV line from Philpott Dam - Fairystone. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 |  | UC | 35 | 6.86 | 6.86 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100008 | s2179.7 | Construct ~22 miles of 138 kV line from Salem Highway - Willis Gap. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-01 |  | UC | 35 | 42.39 | 42.39 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100031 | s2179.9 | Construct ~11 miles of 138 kV line from Floyd - Woolwine. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 |  | UC | 35 | 33.44 | 33.44 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100013 | s2179.10 | Construct ~10 miles of 138 kV line from Salem Highway - Woolwine. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | UC | 35 | 34.75 | 34.75 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100031 | s2179.11 | Remove ~11 miles of 69 kV line from Floyd - Woolwine. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-02 |  | UC | 35 | 1.55 | 1.55 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100020 | s2179.12 | Remove ~10 miles of 69 kV line from Stuart - Woolwine. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 |  | UC | 35 | 5.02 | 5.02 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100041 | s2179.13 | Remove ~12.2 miles of 138 kV line from Alum Ridge - Claytor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-11-01 |  | UC | 35 | 1.49 | 1.49 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100040 | s2179.14 | Remove ~6.25 miles of 138 kV line from Alum Ridge - Floyd. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-02 |  | UC | 35 | 0.94 | 0.94 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100022 | s2179.15 | Remove ~19 miles of 138 kV line from Floyd - West Bassett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-08-14 |  | UC | 35 | 16.61 | 16.61 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100022 | s2179.16 | Remove ~6.4 miles of 138 kV line from Fieldale - West Bassett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-15 |  | UC | 35 | 3.77 | 3.77 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100043 | s2179.17 | Remove ~0.34 miles of 138 kV line from Philpott SS - Philpott. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-16 |  | UC | 35 | 0.13 | 0.13 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100021 | s2179.18 | Remove ~19 miles of 69 kV line from Fieldale - Stuart. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-08-14 |  | UC | 35 | 8.26 | 8.26 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100023 | s2179.19 | Remove ~7.1 miles of 69 kV line from Fieldale - West Bassett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-15 |  | UC | 35 | 11.56 | 11.56 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100042 | s2179.20 | Remove ~6.8 miles of 69 kV line from Fieldale - West Bassett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-15 |  | UC | 35 | 10.77 | 10.77 | 2023-02-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100054 | s2179.21 | At Floyd station, install 2-138 kV circuit breakers (3000 A, 40 kA). Install high-side circuit switcher on T2 (3000A, 40 kA). Station expansion to accommodate new equipment and DICM. Install 138 kV line relaying, CCVT’s, breaker controls, bus differential protection, transformer #2 protection. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-09-01 |  | UC | 35 | 10.75 | 10.75 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100006 | s2179.22 | At Fieldale station, retire 69 kV CB G, D and C. Install CCVTs and arresters on 138 kV West Bassett Line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-13 |  | UC | 35 | 0.7 | 0.7 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100004 | s2179.24 | At Bassett station, convert station from 69 kV to 138 kV. Install 138/12 kV transformer with high-side circuit switcher, transclosure and associated distribution feeders. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  | UC | 35 | 0 | 0 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100055 | s2179.25 | At Claytor 138 kV station, install line relaying. Remove wavetrap, replace 1590 AAC risers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-11-01 |  | UC | 35 | 0.55 | 0.55 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100043 | s2179.26 | Retire Philpott 138 kV switch structure. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-16 |  | UC | 35 | 0.4 | 0.4 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100002 | s2179.27 | At Willis Gap station, install 2-138 kV MOABs. Terminate new Salem Highway - Willis Gap 138 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-12-12 |  | UC | 35 | 0 | 0 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100003 | s2179.28 | At Woolwine station, convert station from 69 kV to 138 kV. Retire/remove 69 kV switch structure, 69 kV MOABs, 69/34.5 kV transformer. Install 138 kV 3-way switch structure with MOABs, 138/34.5 kV transformer with high-side circuit switcher. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | UC | 35 | 0 | 0 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100061 | s2179.29 | At Salem Highway station, establish new 138 kV station replacing Stuart Station. Install 138 kV 5-breaker ring bus, 138/34.5 kV & 138/12 kV transformers with high-side circuit switchers. Terminate Huffman, Floyd and Fairystone 138 kV circuits. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-09-02 |  | UC | 35 | 0 | 0 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100001 | s2179.30 | At Stuart 69 kV station, retire and remove all existing equipment and control house. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-02 |  | UC | 35 | 0 | 0 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100005 | s2179.31 | At Stanleytown station, convert station from 69 kV to 138 kV. Retire/remove 69 kV switch structure, 69 kV MOABs, 69/12 kV transformer. Install 138 kV 3-way switch structure with MOABs, 138/12 kV transformer with high-side circuit switcher. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-11-13 |  | UC | 35 | 0 | 0 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100064 | s2179.32 | At Fairystone station, establish new 138 kV station replacing West Bassett. Install 138 kV 4-breaker ring bus, 138/34.5 kV transformer with high-side circuit switcher and associated distribution feeders. Terminate Salem Highway, Fieldale and Philpott Dam 138 kV circuits. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 |  | EP | 5 | 0 | 0 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | DR19R07L0 | s2179.33 | At Claudville station, establish new 138/34.5 kV distribution station with 2-138 kV CBs, 138/34.5 kV transformer and 3-34.5 kV feeders. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-10-31 |  | EP | 0 | 0 | 0 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100010 | s2179.34 | Provide transition, entry and termination for OPGW connectivity at Willis Gap, Claytor, Alum Ridge, Floyd, Woolwine, Stuart, Fairystone, Philpott Dam, Bassett, Stanleytown, Fieldale, and Salem Highway to support fiber relaying. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-01 |  | UC | 35 | 0.83 | 0.83 | 2020-01-17 | Scott Markwell |  | FALSE
Supplemental | AEP | P18100046 | s2179.35 | Construct ~11.4 miles of 138 kV line from Claudville to Mayo River. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 |  | EP | 0 | 38.87 | 38.87 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P18100044 | s2179.36 | Remove ~0.4 miles of 69 kV line from Woolwine “in and out” loop. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 |  | EP | 0 | 0.09 | 0.09 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P18100025 | s2179.37 | Construct ~9.5 miles 138 kV from Stoneleigh Station Site to Proposed Patrick Henry Site . | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 |  | EP | 0 | 28.87 | 28.87 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P18100027 | s2179.38 | Construct ~4.1 miles of double circuit 138 kV from Stoneleigh Station Site to Smith River . | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 |  | EP | 0 | 11.89 | 11.89 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P18100029 | s2179.39 | Construct ~1.8 miles of 138 kV from Fieldale to Stoneleigh tap structure . | Equipment Material Condition, Performance and Risk |  |  |  | 2029-12-31 |  | EP | 0 | 6.92 | 6.92 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P18100015 | s2179.40 | Construct ~11 miles 138 kV from Mayo River to Proposed Patrick Henry Site . | Equipment Material Condition, Performance and Risk |  |  |  | 2029-12-31 |  | EP | 0 | 34.98 | 34.98 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P18100007 | s2179.41 | At Huffman station remove CB “C” bypass switch and Install CCVT with Wavetrap on Willis Gap line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 |  | EP | 0 | 0 | 0 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P18100053 | s2179.42 | Retire West Bassett station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 |  | EP | 0 | 0 | 0 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P18100068 | s2179.43 | At Stoneleigh station establish new 138 kV tap station, install 3-way MOAB switch, install 138/12 kV transformer and associated feeders . | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-01 |  | EP | 0 | 0 | 0 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P19006001 | s2184.1 | Rebuild 22.0 miles of the existing 28.5 mile Stuart-Seaman 69kV circuit with 795 ACSR. Retire approximately 3 miles of the line between West Union and structure 86. 32 of the line’s 170 structure were replaced since 2012 and will not be replaced as part of the rebuild | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  | EP | 0 | 48.5 | 48.5 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19006001 | s2184.2 | Construct approximately 2.5 miles of new line from structure 86 on the Stuart – Seaman 69 kV line to Copeland station utilizing 795 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  | EP | 0 | 5 | 5 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19316010 | s2184.3 | Rebuild the 2.0 mile West Union – Copeland 69 kV line utilizing 795 ACSR. The line is part of the Stuart – Seaman 69 kV circuit and is currently radial fed from West Union switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  | EP | 0 | 4 | 4 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19316003 | s2184.4 | Establish a four breaker 69 kV ring (3000A, 40kA) at the existing Copeland station to serve the Adams Co-op and AEP Ohio customers currently served from a hard tap at the end of the radial. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  | UC | 50 | 5 | 5 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19006007 | s2184.5 | Retire existing West Union Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  | EP | 0 | 0.1 | 0.1 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19316005 | s2184.6 | Install new 2000A 3-way phase over phase switch at Panhandle. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  | EP | 0 | 0.7 | 0.7 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19120006 | s2185 | Rebuild the 4-mile Sunnyside-Torrey 138kV circuit. Supplement the existing right-of-way as needed, to resolve encroachments and other constraints. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-09 |  | EP | 0 | 12.7 | 12.7 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083002 | s2188.1 | Construct 10.3 miles of single circuit 138kV from Soft Shell to Garrett picking up Salt Lick Co-op via Snag Fork along the way. Complete associated remote end relaying. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 35.3 | 35.3 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083007 | s2188.2 | Construct ~3 miles of single circuit 138kV from the Eastern station to Garrett station. A short extension will be required from the new station to the existing Hays Branch metering point. Construct short extension to existing Morgan Fork – Hays Branch 138 kV circuit from Eastern station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 11.5 | 11.5 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083008 | s2188.3 | Double circuit cut into existing Hays Branch - Morgan Fork line to tie into new Eastern Station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 1.3 | 1.3 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083032 | s2188.4 | Construct ~1.4 mi of double circuit 138kV line between Eastern and the tap point on the Morgan Fork-Hays Branch line. The proposed line will establish a direct feed to Hays Branch from Eastern and establishing a through path line between Eastern and Morgan Fork.. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 1.6 | 1.6 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083005 | s2188.5 | New relaying at Hays Branch to accommodate new line from Eastern station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 0.5 | 0.5 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083033 | s2188.6 | Expand the Garrett station,Install a straight bus arrangement with two 138kV breakers and a circuit switcher on the high side of the transformer, 138/12kV 30MVA transformer | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 0 | 5.8 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083041 | s2188.7 | Establish a new 138 kV substation Eastern south of the existing Hays Branch station. Install three 138kV breakers (3000A 40kA) at the new Eastern station in a ring bus arrangement. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 6 | 6 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083038 | s2188.8 | Establish Snag Fork S.S. Install a 3 way phase over phase motorized (automated) switching structure near Saltlick to serve the EKPC co-op. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 1.1 | 1.1 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083016 | s2188.9 | Move the existing 69kV rated CB G to the Beaver Creek – McKinney #2 circuit exit at McKinney substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 0 | 0 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P17083019 | s2188.11 | Retire the ~25 miles of the 46kV Beaver Creek – McKinney #1 46 KV circuit. Retire Spring Fork Tap. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 17.3 | 17.3 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19058001 | s2189 | Rebuild ~27.8 miles of the existing Baileysville – Hales Branch 138kV circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-08-01 |  | EP | 0 | 98.5 | 98.5 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19014002 | s2190 | Rebuild approximately 15 miles of the AEP-owned portion of the 138 kV line between Fieldale and Dan River stations (AEP/Duke ownership changes at the VA/NC border). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-28 |  | EP | 0 | 32.2 | 32.2 | 2020-02-21 |  |  | TRUE
Supplemental | AEP | P15082C01 | s2197 | At Dragoon Station, replace the 34.5KV breaker A. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-01-01 |  | UC | 75 | 2 | 0.66 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19253014 | s2199.1 | Rebuild approximately 3.0 miles of New Liberty – North Baltimore 34kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-03 |  | EP | 0 | 9.3 | 9.3 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19091011 | s2200.1 | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Install a 2MW BESS at Middle Creek substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-28 |  | On Hold | 0 | 9.7 | 9.7 | 2020-01-17 |  |  | FALSE
Supplemental | AEP | P19091003 | s2200.2 | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Rebuild ~8.5 miles of 46 kV line between Prestonsburg and Middle Creek station. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 |  | On Hold | 0 | 25.5 | 25.5 | 2020-01-17 |  |  | FALSE
Supplemental | AEP | A20705035 | s2200.3 | AEP is notifying PJM of our intention to suspend the project associated with S2200. Pending the sale, Liberty can decide on if they plan to move forward with the project as proposed or develop an alternate solution.Retire ~14.5 miles of 46 kV line between Falcon and Middle Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 |  | On Hold | 0 | 6.1 | 6.1 | 2020-01-17 |  |  | FALSE
Supplemental | AEP | P19105003 | s2201.1 | Rebuild 43.4 miles single circuit line between Hillsboro – South Lucasville with 1033 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-16 |  | UC | 75 | 92.5 | 92.5 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P19105003 | s2201.2 | Rebuild 8.5 miles double circuit between Millbrook Park – South Lucasville with 1033 ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-16 |  | UC | 75 | 33.6 | 33.6 | 2020-02-21 |  |  | FALSE
Supplemental | AEP | P18147020 | s2213.4 | Construct two independent lines to serve the X-555 substation (DP #1). The lines will be ~0.4 miles long each. | Customer Service |  |  |  | 2025-10-06 |  | EP | 0 | 1.7 | 1.7 | 2020-03-10 | Oliver Duncan/? |  | TRUE
Supplemental | AEP | P18147022 | s2213.5 | Construct two independent lines to serve the X-5001 substation (DP #2). The lines will be ~0.8 miles long each. | Customer Service |  |  |  | 2025-10-06 |  | EP | 0 | 3.5 | 3.5 | 2020-03-10 | Oliver Duncan/? |  | TRUE
Supplemental | AEP | P18147006 | s2213.6 | At Don Marquis 345 kV, install 3-345kV 4000A 63kA circuit breakers to terminate the OVEC lines from Pierce and Kyger Creek. Install intertie metering. (AEP work) | Customer Service |  |  |  | 2026-08-20 |  | EP | 0 | 8.8 | 8.8 | 2020-03-10 | Oliver Duncan/Patrick Hodgson |  | TRUE
Supplemental | AEP | J19220002 | s2215.1 | Rebuild 16 miles of 69 kV single circuit line from North Continental Switch (existing switch to be retired) to Roselms Switch (located next to the existing Roselms- PP Co-op Station). | Equipment Material Condition, Performance and Risk |  |  |  | 2026-05-01 |  | EP | 0 | 38.4 | 38.4 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | J19220001 | s2215.2 | Build 9.4 miles of single circuit 69 kV line from Roselms to near East Ottoville 69 kV Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 13.7 | 13.7 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220012 | s2215.3 | Rebuild 7.5 miles of double circuit 69kV line between East Ottoville Switch and Kalida Station (combining with the new Roselms to Kalida 69 kV circuit). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 23.6 | 23.6 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220021 | s2215.4 | Rebuild 5.1 miles of single circuit 69 kV line from East Ottoville to North Delphos. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 9.4 | 9.4 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220024 | s2215.5 | At North Continental, remove normally open bypass switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 0.1 | 0.1 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220014 | s2215.6 | At Fort Brown Switch, install a three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 0.7 | 0.7 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220016 | s2215.7 | At West Oakwood Switch, install a three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 0.6 | 0.6 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220017 | s2215.8 | At Roselms Switch, install a new three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 0.6 | 0.6 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220018 | s2215.9 | At Kalida station, move CB J from low side of Transformer 2 to terminate the new line from Roselms Switch. Move the CS XT2 from high side of T2 to the high side of T1. Remove existing T2 transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 1 | 1 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220040 | s2215.10 | Remote end work at North Delphos station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 0.8 | 0.8 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220026 | s2215.11 | At East Ottoville, install a three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 0.7 | 0.7 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220028 | s2215.12 | At Ottoville station, install 2- three way 69 kV, 1200 A, phase over phase Switches, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 1.9 | 1.9 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19220029 | s2215.13 | At Fort Jennings, replace hard tap with a three way 69kV, 1200 A phase-over-phase switch, with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-20 |  | EP | 0 | 0.6 | 0.6 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19216001 | s2216.1 | At Lamping station, install a 138kV breaker string with 2 breakers, a 90 MVA 138-69kV transformer, and 1- 69kV breaker. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 |  | EP | 0 | 4.8 | 4.8 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | J19216001 | s2216.2 | Construct a 10-mile 69kV transmission line between Lamping and the Woodsfield area. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 |  | EP | 0 | 19.9 | 19.9 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19216005 | s2216.3 | At the existing Woodsfield Co-op station, install a 3-way 69kV switch with SCADA functionality (Cranes Nest Switch). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 |  | EP | 0 | 0.6 | 0.6 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19216005 | s2216.4 | At the existing hard tap to Woodsfield Municipal, install a 3-way 69kV switch with SCADA functionality (Standingstone Switch). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 |  | EP | 0 | 0.6 | 0.6 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19216006 | s2216.5 | Remove the existing Cameron 2-way switch and install a new 3-way 69kV switch with SCADA functionality. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 |  | EP | 0 | 0.6 | 0.6 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19216002 | s2216.6 | At Switzer station, install 2- 138kV line breakers (toward Herlan & Natrium). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 |  | EP | 0 | 1.1 | 1.1 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19216010 | s2216.7 | At the 138kV remote-end of Natrium, replace the line protection relays to coordinate with the upgrade at Switzer. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 |  | EP | 0 | 0.6 | 0.6 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19216007 | s2216.8 | Modify the existing Switzer-Woodsfield 69kV transmission line on each side of the switches due to the switch installation. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-05 |  | EP | 0 | 1.9 | 1.9 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P18221001 | s2219 | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12kV 30 MVA transformer, Replace 12 kV CB A and D. Retire existing Fleming substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-29 |  | EP | 25 | 21.1 | 21.1 | 2020-03-19 | Wayne Cooper/Chintan Raval |  | FALSE
Supplemental | AEP | P19209001 | s2221.1 | Remove ~3.3 miles of the Derwent – Summerfield 69 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-03 |  | EP | 10 | 2 | 2 | 2020-03-19 | Shawn ynch/Jerod Marker |  | FALSE
Supplemental | AEP | J19209001 | s2221.2 | Build a new 69 kV line (~2.42 miles) from Lashley to the existing Summerfield line to loop the customers served from the existing radial. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-03 |  | EP | 10 | 6.1 | 6.1 | 2020-03-19 | Shawn ynch/Jerod Marker |  | FALSE
Supplemental | AEP | P19209004 | s2221.3 | Install a new 69kV 1200A 3-way POP switch (Lashley) with auto-sectionalizing MOABs to serve the Senecaville GM co-op. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-03 |  | EP | 10 | 1.1 | 1.1 | 2020-03-19 | Shawn ynch/Jerod Marker |  | FALSE
Supplemental | AEP | P19209005 | s2221.6 | At Derwent station, remove the Summerfield line exit and associated equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 0.4 | 0.4 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19225029 | s2222.1 | Build a new single circuit 138 kV line (~1.5 mi) to connect the new IIesboro delivery point to the Lemaster - Ross 138kV circuit using 336.4 ACSR. | Customer Service |  |  |  | 2025-01-06 |  | EP | 0 | 4.3 | 4.3 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19260004 | s2222.2 | Install a new 3-way phase over phase 138 kV 2000 A switch (Fiddlestix) with MOABs on the Lemaster – Ross 138kV circuit. Update remote end work at Lemaster. | Customer Service |  |  |  | 2025-07-18 |  | UC | 75 | 0.9 | 0.9 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19225013, P19225004 | s2224.1 | Rebuild the existing ~8 mile Elliott – Lee 69kV line to 138 kV and retire the existing 69 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 |  | EP | 0 | 20.7 | 20.7 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19225009 | s2224.2 | Retire approximately 11.5 miles of the Philo – Rutland 138kV line asset from Lee station north, including the de-energized portion of the line that runs through the Plains community. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 |  | EP | 0 | 3.5 | 3.5 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19225020 | s2224.6 | Rebuild ~3.68 miles of single circuit line from the Poston - Strouds Run line as double circuit 138kV transmission line to eliminate the hard tap on the line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 |  | EP | 0 | 16 | 16 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19225017 | s2224.8 | At Lemaster station, install a 138kV breaker (3000A 40kA) to accommodate the new circuit. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 |  | EP | 0 | 1 | 1 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19225008 | s2224.9 | Remove Rosewood switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 |  | EP | 0 | 0.1 | 0.1 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P18039002 | s2225.1 | Retire the existing 7.5-mile long Belle-Cabin Creek #1 and #2 circuits from Belle to Cabin Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-02 |  | UC | 75 | 10 | 10 | 2020-03-19 | Wayne Cooper/Michael Hassay |  | FALSE
Supplemental | AEP | P18039107 | s2225.2 | Construct new double circuit 46kV line (designed to 138 kV) from Belle to Hernshaw (~4 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-01 |  | UC | 75 | 13.5 | 13.5 | 2020-03-19 | Wayne Cooper/Michael Hassay |  | FALSE
Supplemental | AEP | P18039001 | s2225.4 | Remote end work and retire circuit breakers AA and AB at Cabin Creek station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-02 |  | UC | 75 | 0.8 | 0.8 | 2020-03-19 | Wayne Cooper/Michael Hassay |  | FALSE
Supplemental | AEP | P22081002 | s2225.7 | Marmet Hydro Hard Tap will be relocated to be positioned between 46 kV circuit breaker G at Belle and the new switches at Marmet Station. Remote end work required at Marmet Hydro Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-01 |  | EP | 0 | 0.6 | 0.6 | 2020-03-19 | Wayne Cooper/Michael Hassay |  | FALSE
Supplemental | AEP | P18250001, P18250002, P18250003, P18250004, P18250007, P18250009 | s2226.1 | Construct approximately 10 miles of new 138kV line between Glen Lyn and Speedway. New ROW will be required for the new Glen Lyn – Speedway 138kV line. Retire the existing section of line from Glen Lyn to Hatcher Switch (~ 8 miles), including Hatcher Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-06-21 |  | EP | 0 | 32 | 32 | 2020-03-19 | Charles Linkous/Robert Valerio |  | FALSE
Supplemental | AEP | P18250005, P18250014 | s2226.2 | Retire Hatcher Switch. Install MOABs at Speedway on new line to Glen Lyn and existing line towards South Princeton. Install a circuit switcher on the Speedway transformer. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-06-21 |  | EP | 0 | 1.5 | 1.5 | 2020-03-19 | Charles Linkous/Robert Valerio |  | FALSE
Supplemental | AEP | P18250001 | s2226.3 | Rebuild ~7.3 miles of the Glen Lyn – South Princeton 138 KV circuit between Speedway station and the previous Hatcher Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-12-01 |  | EP | 0 | 21.9 | 21.9 | 2020-03-19 |  |  | FALSE
Supplemental | AEP | P19304011 | s2250 | Rebuild the existing Broadford - Wolf Hills/Clinch River - Saltville #2 138kV double circuit line (~26 miles) section between Saltville and Wolf Hills stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2035-06-25 |  | EP | 0 | 107.1 | 107.1 | 2020-04-20 |  |  | FALSE
Supplemental | AEP | DP16K03B1 | s2251.2 | Retire Siloam Station. | Customer Service |  |  |  | 2025-06-05 |  | UC | 75 | 0 | 0 | 2020-04-20 | Wayne Cooper/Shaheed Khan |  | FALSE
Supplemental | AEP | P15095040 | s2251.3 | Remote end relaying at Millbrook Park to coordinate with new breakers. | Customer Service |  |  |  | 2028-04-03 |  | EP | 0 | 0.4 | 0.4 | 2020-04-20 |  |  | FALSE
Supplemental | AEP | P15095024 | s2251.4 | Tap the 69kV Central Portsmouth – Millbrook Park line and install 3 custom T-line structures due to proximity to the Railroad. | Customer Service |  |  |  | 2027-08-11 |  | EP | 0 | 0.9 | 0.9 | 2020-04-20 |  |  | FALSE
Supplemental | AEP | P21082004 | s2270.8 | Cut into the George Washington-Natrium 138kV circuit and extend an 8.6- mile double-circuit 138kV loop east to Nauvoo Ridge. | Customer Service |  |  |  | 2026-08-20 |  | EP | 0 | 23.13 | 23.13 | 2022-03-08 |  |  | FALSE
Supplemental | AEP | P21082004 | s2270.9 | Modify the George Washington-Natrium 138kV line, which is part of a double-circuit lattice tower line. | Customer Service |  |  |  | 2027-04-28 |  | EP | 0 | 0.65 | 0.65 | 2022-03-08 |  |  | FALSE
Supplemental | AEP | P22964008 | s2270.10 | Rebuild the Kammer-Natrium 138kV double-circuit line (9.3 miles). The circuit’s limiting ratings are currently set by the T-Line conductor (556 ACSR). The rebuilt circuit will utilize 795 ACSS high-temperature conductor, to optimize the new structure sizing and cost | Customer Service |  |  |  | 2025-12-01 |  | EP | 0 | 22.86 | 22.86 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P19104001 | s2272.1 | Rebuild the 35-miles of the South Point- Portsmouth double circuit 138 kV line between Millbrook Park – South Point; with 795 ACSR (257MVA) or equivalent conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-15 |  | EP | 0 | 128 | 128 | 2020-05-22 |  |  | FALSE
Supplemental | AEP | P19104013 | s2272.3 | Remote end work at South Point 138 kV station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-15 |  | EP | 0 | 0.6 | 0.6 | 2020-05-22 |  |  | FALSE
Supplemental | AEP | P19290021, P19290022, P19290003, P19290026 | s2273.1 | Rebuild the 1.25 mile long Anchor Hocking-Winchester 69 kV circuit. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-08-16 |  | EP | 0 | 5.9 | 5.9 | 2020-05-22 |  |  | FALSE
Supplemental | AEP | P19290023, P19290024 | s2273.2 | Expand and upgrade Anchor Hocking 69 kV station to a 5 breaker ring bus to accommodate 5 elements (2 transmission lines and 3 distribution transformers). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-02-23 |  | EP | 0 | 6.7 | 6.7 | 2020-05-22 |  |  | FALSE
Supplemental | AEP | P19290009, P19290010 | s2273.3 | Replace circuit breakers A & B at Winchester 69 kV station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-09-07 |  | EP | 0 | 3 | 3 | 2020-05-22 |  |  | FALSE
Supplemental | AEP | P19290004, P19290005, P19290006, P19290007 | s2273.5 | At Randolph station, replace 138/69/12 kV Transformer #1 with a 138/69kV 90MVA unit, move the distribution load to a new 138/12kV transformer, and install a 138kV bus tie circuit breaker. Replace cap switcher AA. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-07-03 |  | EP | 0 | 6.8 | 6.8 | 2020-05-22 |  |  | FALSE
Supplemental | AEP |  | s2273.10 | Retire Lobdell station. Moved the load from 69kV to 12kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-01 |  | EP | 0 | 0 | 0 | 2020-05-22 |  |  | FALSE
Supplemental | AEP | P19311007 | s2274.1 | Rebuild a 4.17 mile portion of the Madison – Pendleton 138kV single circuit line with DRAKE 795 ACSR 26/7. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-01 |  | EP | 0 | 7.7 | 7.7 | 2020-05-22 | Seth Jacobson/Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | P19311009 | s2274.2 | At Meadowbrook station, install 2 138kV circuit breakers to eliminate the 3 terminal line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-07-01 |  | EP | 0 | 2.8 | 2.8 | 2020-05-22 | Seth Jacobson/Sharlene Rivera-Gonzalez |  | FALSE
Supplemental | AEP | P19017002 | s2282.1 | Rebuild ~5.0 miles of 138 kV line between Astor - Shannon. The existing Refugee Switch will be retired. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | EP | 0 | 21.8 | 21.8 | 2020-06-19 |  |  | FALSE
Supplemental | AEP | P19017008 | s2282.2 | Rebuild ~0.5 miles and construct ~4.6 miles of greenfield 138 kV line between Groves - Shannon to eliminate the three terminal line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | EP | 0 | 22 | 22 | 2020-06-19 |  |  | FALSE
Supplemental | AEP | P19017010 | s2282.3 | Rebuild ~4.3 miles of 138 kV line between Bixby – Shannon. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | EP | 0 | 15.1 | 15.1 | 2020-06-19 |  |  | FALSE
Supplemental | AEP | P19017013 | s2282.4 | Reconfigure lines at Shannon to accommodate the new 138 kV circuit from Groves. Install two new 138 kV 3000A 40 kA circuit breakers on circuits towards Brice and Bixby to prevent dissimilar zones of protection when bringing the 3rd 138 kV circuit to the station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-01 |  | EP | 0 | 1.9 | 1.9 | 2020-06-19 |  |  | FALSE
Supplemental | AEP | P19211005 | s2283.1 | Build ~ 3.75 miles of single circuit 138kV transmission line from new Condit 3-way MOAB Switch (tapping the Centerburg – Trent 138kV circuit) to Lott station (Consolidated Co-op). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-04-28 |  | EP | 0 | 9.86 | 9.86 | 2020-06-19 |  |  | FALSE
Supplemental | AEP | P19211002 | s2283.2 | Build Condit 3-way MOAB 138kV switch | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-11-20 |  | EP | 0 | 0.78 | 0.78 | 2020-06-19 |  |  | FALSE
Supplemental | AEP | P21573020 | s2342.1 | Marion – Parsons 40kV: Retire ~5.2 miles of double circuit 40kV line between Marion and Parsons. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-23 |  | UC | 75 | 2.97 | 2.97 | 2020-10-16 | Crystal Wood-Hython/Nathen Robers |  | FALSE
Supplemental | AEP | P19278009 | s2344.2 | Add a 69kV bus tie CB to Hadley station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-17 |  | EP | 0 | 0.8 | 0.8 | 2020-07-17 | Teresa Rogers/Michael Hassay |  | FALSE
Supplemental | AEP | P19238016 | s2345.2 | Riverside Station: Replace (2) 138kV breakers and (2) 34.5kV breakers at Riverside. While at the station and taking advantage of the outage AEP will install a new 34.5kV breaker to bring Whirlpool customer, whose delivery point is currently one tower outside of the station, into Riverside station. Install high side circuit switcher to 138/69-34.5kV transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-04-07 |  | EP | 0 | 3.3 | 3.3 | 2020-07-17 | Joseph Smith/Joshua Smith |  | FALSE
Supplemental | AEP | P18180007 | s2346 | Replace existing 138 kV CBs G, H, I, K, L and N with six new 138 kV 40 kA circuit breakers. Replace existing 138 kV cap bank BB and install a new 138 kV breaker on the new cap bank. Replace existing 46 kV cap bank switcher with a new cap bank switcher. Install a high side circuit switcher on the existing 138/46 kV transformer. Upgrades will be made to the existing road into the station to improve access and space constraints. A flood wall will be installed to mitigate flooding concerns. *Note: 138 kV CS CC failed and has been replaced. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-19 |  | EP | 0 | 10.1 | 10.1 | 2020-07-17 |  |  | FALSE
Supplemental | AEP | P19163001 | s2348.4 | Rebuild the Chemical – South Charleston #1 and Chemical – South Charleston #2 46 kV lines with a new double circuit 46 kV line (69 kV standards) from Chemical – Criel Mound. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-17 |  | UC | 75 | 5.4 | 5.4 | 2020-07-17 | Shively, John / Hassay, Michael |  | FALSE
Supplemental | AEP | P19163007 | s2348.5 | At South Charleston, retire the existing circuit breakers A and B and install four new 46 kV 40 kA circuit breakers in a ring at a new station (Criel Mound) adjacent to the existing South Charleston Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-18 |  | UC | 75 | 11 | 11 | 2020-07-17 |  |  | FALSE
Supplemental | AEP | P19277009, P19277010 | s2392.2 | Add a 3000A bus tie CB at 138kV Trier station to separate the 4 MOAB’s in series. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-05-01 |  | UC | 50 | 1.2 | 1.2 | 2020-09-11 | Anthony Antronica/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19198002 | s2393.1 | On the South Hicksville – Rob Park 69 kV line. Rebuild the 21.6 miles as currently constructed, including ~2.4 miles of 69 kV double circuit and ~19.2 miles of 69 kV single circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-08-05 |  | EP | 0 | 50.8 | 50.8 | 2020-09-11 | Danielle Hilliard/Brendan Fuller |  | FALSE
Supplemental | AEP | P19096004 | s2393.2 | Rebuild the through path of St Joe 69 kV station. Install a breaker on the Harlan line exit to eliminate four MOABs in series. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-07-23 |  | EP | 0 | 1.3 | 1.3 | 2020-09-11 | Wayne Cooper/Michael Hassay |  | FALSE
Supplemental | AEP | P19096020 | s2393.3 | At Harlan 69 kV (FERC-Distribution) station, replace a switch and line riser in order to accommodate the new line entrance. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-30 |  | EP | 0 | 0 | 0 | 2020-09-11 | Wayne Cooper/Michael Hassay |  | FALSE
Supplemental | AEP | P19096038 | s2393.4 | Replace the West Hicksville 69 kV PoP switch to accommodate the new line height, route and structure/conductor type. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-23 |  | EP | 0 | 1 | 1 | 2020-09-11 | Wayne Cooper/ |  | FALSE
Supplemental | AEP | P19096012 | s2393.5 | In order to rebuild the line, the in-line switch at Vulcraft 69 kV needs to be replaced. The switch replacement will be a 3-way switch with a MOAB toward West Hicksville 69 kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-29 |  | EP | 0 | 1 | 1 | 2020-09-11 | Wayne Cooper/Michael Hassay |  | FALSE
Supplemental | AEP | P20015002 | s2394.1 | Rebuild ~14.3 mi of the Payne - South Hicksville 69 kV circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 |  | EP | 0 | 30.6 | 30.6 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P20015011 | s2394.3 | Install Seiberi switch as a new 69 kV, 1200A, 3-way Phase-over-Phase switch with sectionalizing capability to eliminate the hard tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 |  | EP | 0 | 0.5 | 0.5 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P20015012 | s2394.4 | Replace Antwerp Sw with 69 kV, 1200A, 3-way Phase-over-Phase switches with sectionalizing capability, including 4.3 miles of fiber buildout to allow for sectionalizing. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 |  | EP | 0 | 1.1 | 1.1 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P20015015 | s2394.5 | Replace North Antwerp Sw with 69 kV, 1200A, 3-way Phase-over-Phase switches with sectionalizing capability. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-15 |  | EP | 0 | 0.6 | 0.6 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143001 | s2395.1 | Rebuild existing double circuit portion of the Dunkirk – Forest line asset from existing Str 194 to the greenfield Rangeline station (1.35 miles). Rebuild existing ~6.5 mi Arlington – Dunkirk 34.5 kV as Rangeline – East Arlington single 69 circuit from Str 194 to the greenfield East Arlington (formerly Arlington). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | UC | 75 | 21 | 21 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143007 | s2395.5 | Rebuild ~5.75 mi 69 kV line section between greenfield West Crawford Station and Buckrun Switch (outside of Blanchard Station) as single circuit 69 kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 25 | 13 | 13 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143059 | s2395.6 | Rebuild ~0.22 mi South Vanlue Extension to tie into East Arlington – West Crawford 69 kV ckt. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 25 | 0.1 | 0.1 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143009 | s2395.7 | Rebuild ~11.5 mi 69 kV line between West Crawford and South Berwick Stations. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | UC | 50 | 28.9 | 28.9 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143005 | s2395.8 | Remove/retire ~10 mi of 69 kV line from Forest to North Wharton Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 25 | 8.3 | 8.3 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143018 | s2395.9 | Reconfigure North Upper Sandusky – South Berwick 69 kV line to tie into Hurd Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 25 | 0.1 | 0.1 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143019 | s2395.10 | Remove/Retire ~2.58 mi South Carey – Hurd Switch 69 kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | UC | 75 | 1.9 | 1.9 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143023 | s2395.11 | Carey 69kV: Install 69 kV Box Bay with 2000A, 40 kA MOABs with sectionalizing capability. Remove existing Carey Sw. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | UC | 75 | 1.5 | 1.5 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143024 | s2395.12 | West Crawford 69kV (Rebuild): Install a new 69 kV ring bus with three 3000A, 40 kA circuit breakers to replace West Crawford Sw. Replace Cap switcher “AA” and relocate Cap bank from Carey Sw to West Crawford 69 kV bus. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | UC | 75 | 5.6 | 5.6 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143041 | s2395.13 | South Carey Sw 69 kV: Remove South Carey Sw 69 kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | UC | 75 | 0.1 | 0.1 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143042 | s2395.14 | North Wharton Sw 69 kV: Remove North Wharton Sw 69 kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 25 | 0.1 | 0.1 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143043 | s2395.15 | South Vanlue 69 kV: Replace 69 kV bus and existing switches with 2000A, 40 kA line MOABs with sectionalizing capability. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 25 | 0.5 | 0.5 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143040 | s2395.21 | Forest 69 kV: Remove 69 kV CB-H towards South Berwick. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 25 | 0.1 | 0.1 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19143038 | s2395.22 | Dunkirk 69 kV: Retire Dunkirk 69kV station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 25 | 1 | 1 | 2020-09-11 |  |  | FALSE
Supplemental | AEP | P19066007, P19066008 | s2397.1 | Rebuild approximately 1.2 miles of line on the West Huntington – South Point 34.5 kV line between Kenova station and South Point station. Cost drivers on this line section include Ohio River crossing, urban line route through Huntington, WV, and encroachments along the line. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-02-27 |  | EP | 25 | 8.9 | 8.9 | 2020-09-11 | Jonathan Wood/Michael Hassay |  | FALSE
Supplemental | AEP | P19066006 | s2397.2 | Rebuild approximately 5.5 miles of line on the West Huntington – South Point 34.5 kV line between Kenova station and West Huntington station. This segment of line is classified as Distribution and thus has no transmission cost. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-02-27 |  | EP | 25 | 0 | 0 | 2020-09-11 | Jonathan Wood/Michael Hassay |  | FALSE
Supplemental | AEP | P19066015 | s2397.3 | Install 3-way Phase over Phase GOAB switch at Ceredo Switch Station addressing hard tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-02-13 |  | EP | 25 | 0.6 | 0.6 | 2020-09-11 | Jonathan Wood/Michael Hassay |  | FALSE
Supplemental | AEP | P19066017 | s2397.4 | Install 3-way Phase over Phase GOAB switch at Sanitary Board Station addressing hard tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-02-13 |  | EP | 25 | 0.6 | 0.6 | 2020-09-11 | Jonathan Wood/Michael Hassay |  | FALSE
Supplemental | AEP | P19066019 | s2397.5 | Install 3-way Phase over Phase GOAB switch at Four Pole Creek Station addressing hard tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-02-13 |  | EP | 25 | 0.6 | 0.6 | 2020-09-11 | Jonathan Wood/Michael Hassay |  | FALSE
Supplemental | AEP | P18009026 | s2398.7 | AEP will also install a pole outside of West Moulton Substation and a single span of line to connect the West Moulton-Amsterdam 138kV circuit. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2028-08-31 |  | EP | 25 | 0.25 | 0.25 | 2020-10-16 |  |  | TRUE
Supplemental | AEP | DR20C02B0 | s2401.1 | Install a a two breaker (3000A, 40 kA) 69kV straight bus station called Grace along the proposed South Rokeby – West Watertown 69 kV circuit (s2791) to serve the requested delivery point | Customer Service |  |  |  | 2026-04-02 |  | EP | 25 | 1.8 | 1.8 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | DR20C02W0 | s2401.2 | Install approximately 0.2 miles of 69kV line to tie the greenfield Grace station in-and-out to the Muskingum River – South Rokeby 69kV circuit. | Customer Service |  |  |  | 2024-11-21 |  | EP | 25 | 2.1 | 2.1 | 2020-10-16 | Luz Cohmer |  | FALSE
Supplemental | AEP | DR20C02C0 | s2401.3 | Remove/Relocate approximately 0.05 miles of line on the Muskingum River – South Rokeby 69kV Line asset between structures 75 and 74A to accommodate the cut in to the new station. | Customer Service |  |  |  | 2026-04-02 |  | EP | 25 | 0.1 | 0.1 | 2020-10-16 |  |  | FALSE
Supplemental | AEP | DR20C02D0 | s2401.4 | Remote end work at South Rokeby Switch. | Customer Service |  |  |  | 2026-04-02 |  | EP | 25 | 0.9 | 0.9 | 2020-10-16 |  |  | FALSE
Supplemental | AEP | DR20C02D1 | s2401.5 | Remove the South Stockport Switch | Customer Service |  |  |  | 2026-04-02 |  | EP | 25 | 0.07 | 0.07 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P19293006 | s2408.3 | At Hill station, replace existing 69 KV circuit breaker H with new 40 KA 3000A circuit breaker. Replace existing 69 KV circuit breaker E with new 40 KA 3000A circuit breaker for constructability flexibility, existing breaker E can be used as a capital spare. Replace existing 69 KV cap bank circuit switcher AA with new circuit breaker. Replace existing 138/69 KV 40 MVA transformer # 1 with new 138/69 KV 40 MVA transformer #1, add H.S. circuit switcher to the new transformer. Replace existing 138KV line MOABs W & Y with new 138 kV circuit breakers. Replace ground MOAB switches on 138/12 KV T2 with circuit switcher. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-05-15 |  | EP | 25 | 6.7 | 6.7 | 2020-10-16 |  |  | FALSE
Supplemental | AEP | P19293019 | s2408.4 | Remote end relaying work at Clinch River, Wolf Hills, Lovedale, Holston, West Kingsport. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-05-15 |  | EP | 0 | 2 | 2 | 2020-10-16 |  |  | FALSE
Supplemental | AEP | DX21C03Z0 | s2426.1 | Rarden: The existing station will be rebuilt to 69 kV with a new 69kV breaker (3000A, 40kA) facing Adams and a MOAB switch (2000A) facing Otway. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-10-12 |  | EP | 0 | 2.24 | 2.24 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | P18150004 | s2426.2 | Adams – Rarden 69kV: Reroute the line to the rebuilt Rarden station with 795 ACSR 26/7 (SE 179MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-10-05 |  | EP | 0 | 0.12 | 0.12 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | J18150002 | s2426.3 | Rarden – Otway 69kV: Install ~8.5 miles of greenfield 69 kV line between Rarden & Otway stations; using 556.5 ACSR 26/7 conductor (SE 142 MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-10-23 |  | EP | 0 | 12.49 | 12.49 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | P18150011 | s2426.4 | Otway: Construct a new 69kV Station with 4-CBs (3000 Amp, 40kA) in a ring bus configuration. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-11-11 |  | EP | 0 | 5.23 | 5.23 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | P18150002 | s2426.5 | Tick Ridge Extension: Install ~0.1 miles of greenfield line between Otway and Tick Ridge (Adams) stations using 556.5 ACSR 26/7 conductor (SE 142 MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-09-21 |  | EP | 0 | 0.29 | 0.29 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | J18150003 | s2426.6 | Otway – McDermott 69kV: Install ~7.3 miles of greenfield 69 kV line between Otway & McDermott stations; using 556.5 ACSR 26/7 conductor (SE 142 MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-09-21 |  | EP | 0 | 17.59 | 17.59 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | DX21C03B2 | s2426.7 | McDermott: Rebuild the existing station with a 69kV box bay and 2 MOAB switches (2000A) on the line connections. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-12-23 |  | EP | 0 | 2.15 | 2.15 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | J18150004 | s2426.8 | McDermott – Rosemount 69kV: Install ~6.3 miles of greenfield line between McDermott & Rosemount stations; using 556.5 ACSR 26/7 conductor (SE 142 MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-12-23 |  | EP | 0 | 12.49 | 12.49 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | P18150029 | s2426.9 | Rosemount: Expand the existing station footprint. Install 5-CBs (3000 Amp, 40kA) in a ring configuration. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-10-15 |  | EP | 0 | 3.88 | 3.88 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | P18150028 | s2426.10 | Rosemount Extension: Reroute the line into the Rosemount 69kV ring bus with 795 ACSR 26/7 (SE 179MVA). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-10-05 |  | EP | 0 | 0.95 | 0.95 | 2020-11-20 | Cole Bachtel/Patrick Hodgson |  | FALSE
Supplemental | AEP | P13064009, P13064010, P13064011, P13064012, P13064014 | s2428.4 | Rebuild approximately ~40 miles of Wooton – Pineville 161kV line to address the identified asset condition needs. This work also includes line removal work as well as access road construction. Majority of proposed line rebuild is to be constructed on existing center line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-30 |  | EP | 0 | 115 | 115 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P13064009, P13064010, P13064011, P13064012, P13064014 | s2428.5 | Expand existing ROW for the Wooton – Pineville 161kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-30 |  | EP | 0 | 8.5 | 8.5 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P14030009 | s2428.7 | At Stinnett station, upgrade relaying to accommodate new OPGW fiber protection. Provide transition, entry and termination for OPGW connectivity to the Hazard-Pineville fiber route. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-30 |  | EP | 25 | 0.7 | 0.7 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P19267003 | s2430.2 | Construct ~3.9 miles of new 69kV line from Whitewater station to Fayetteville 69 kV station. Rebuild the line section between Fayetteville and Elmo SS 69kV (~1.7 miles). | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-27 |  | UC | 50 | 16.5 | 16.5 | 2020-11-20 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | P19267021 | s2430.3 | Construct ~1.5 miles of new 69 kV double circuit line from the Carbondale – Tower 117 69 kV circuit to serve the new Victor Station in/out. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-05-19 |  | EP | 0 | 5.8 | 5.8 | 2020-11-20 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | P19267021 | s2430.5 | Reconfigure a line section between Tower 117 – Carbondale to connect in the new Chestnutburg Station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-07 |  | UC | 50 | 0.6 | 0.6 | 2020-11-20 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | DR21H63W0 | s2430.7 | Victor Station: Retire/remove Gauley Mountain 69 kV Station. Establish a 69 kV bus and install two new 69 kV 3000 A 40 kA circuit breakers at the new site to be called Victor Station to serve requested Distribution delivery point. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-10-22 |  | EP | 0 | 2.3 | 2.3 | 2020-11-20 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | P19267012 | s2430.8 | Fayetteville Station: Install a new 69kV 3-way PoP switch outside of the station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-06-27 |  | UC | 75 | 0.4 | 0.4 | 2020-11-20 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | P19267013 | s2430.9 | Chestnutburg SS: Const.ruct a new three breaker ring utilizing three new 69kV 3000A 40kA circuit breakers to eliminate a three terminal line connection. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2025-05-01 |  | UC | 50 | 3.2 | 3.2 | 2020-11-20 | Roger Whitt/Michael Hassay |  | FALSE
Supplemental | AEP | DP19F03B1, DP19F03L1, DP19F03W2, DP19F03Y2 | s2431.1 | Rebuild North Kendallville 69/12kV station as Henderson 138/12kV station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  | EP | 0 | 0.7 | 0.7 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | DP19F03B0, DP19F03Y0, DP19F03D1, | s2431.2 | Expand Bixler 138/12kV station with a second transformer. Rebuild the through path to accommodate the expansion with a bus tie breaker and line MOAB’s. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  | EP | 0 | 2.5 | 2.5 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | DP19F03D0, DP19F03Z0 | s2431.3 | Add a 138kV CB to Kendallville station on the line exit to Henderson. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  | EP | 0 | 1.5 | 1.5 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | DP19F03C0, DP19F03W1, DP19F03W3, DP19F03T0 | s2431.4 | Rebuild the ~1.8 mile North Kendallville 69kV tap as the 138kV Henderson – Kendallville line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  | EP | 0 | 5.5 | 5.5 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | DP19F03W0, DP19F03X0 | s2431.5 | Build the new ~2.6 mile Henderson – Bixler 138kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  | EP | 0 | 6.9 | 6.9 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | DP19F03B3, DP19F03C2 | s2431.6 | Retire the 138kV Bixler Sw, and the ~.6 mile between Bixler SW and Kendallville station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2029-07-02 |  | EP | 0 | 0.7 | 0.7 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | DR19F07B1 | s2432.1 | Retire Harvest Park 34.5kV station and move distribution load source to Lincoln station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0 | 0 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19274006 | s2432.2 | Retire ~.6 miles of the Storm Water - Lincoln line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0.1 | 0.1 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19157013 | s2432.3 | Retire the ~2.5 mile Anthony – Harvest Park line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0.5 | 0.5 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19274010 | s2432.4 | Retire Filtration Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0.1 | 0.1 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | A19036056 | s2432.5 | Retire the ~1.1 mile Anthony – Lincoln 34.5kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0.2 | 0.2 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | A19036057 | s2432.6 | Retire the ~2.9 mile Anthony – Lincoln 138kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0.6 | 0.6 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P20213007 | s2432.7 | At Lincoln station, move the Storm Water CB to the 69kV bus. Install 138/12kV transformer with new 12kV distribution bay to replace Harvest Park. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-05-01 |  | EP | 0 | 5.7 | 5.7 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19157015 | s2432.8 | Rebuild the Lincoln – Inca line. Line will connect to the new Lincoln 69/34.5kV extension at Maumee switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2023-09-19 |  | EP | 0 | 6.3 | 6.3 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19274007 | s2432.9 | Build a ~0.9 mile 69/34.5kV double circuit line out of Lincoln station to connect to the Lincoln – Maumee 34.5kV line and the Lincoln – Stormwater 69kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 3.4 | 3.4 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19157003 | s2432.10 | Install a 34.5kV POP Switch to feed Inca station called Maumee switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0.6 | 0.6 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19274001 | s2432.11 | Build a greenfield ~1.7 mile Anthony – Melita 69kV line | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 6.2 | 6.2 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P22730001 | s2432.12 | At Storm Water station, replace Transformer 1 with a 69/12kV unit and re-energize station at 69kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-08-27 |  | EP | 0 | 0 | 0 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P19274012 | s2432.13 | At Water Pollution station, re-energize station at 69kV. Station was previously built to take either 34.5 or 69 kV service. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0 | 0 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19274014 | s2432.14 | At Omnisource station, replace Transformer 1 with a 69/4kV unit and re-energize station at 69kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 1.2 | 1.2 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19274009 | s2432.15 | At Melita station, install a 3000A 40kA 69kV CB for the Anthony line entrance. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 0.9 | 0.9 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19157006 | s2432.16 | At Anthony station, replace both 34.5/12kV transformers with 69/12kV 25MVA units. Replace 2 CB’s with 3000A 40kA 69kV CB’s for the Water Pollution line exit and bus tie positions. Re-use the existing Water Pollution breaker for the new Melita line entrance. Install a 21.6Mvar Cap bank. Retire the 138/34.5kV transformer, the 34.5kV CB’s Q and A, and the existing buswork. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-02-15 |  | EP | 0 | 8.7 | 8.7 | 2020-11-20 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P20090003 | s2433.3 | Install approximately 0.1 mile radial line extension connecting Towhee Switch to the structure outside SCP’s Paint Creek Substation. | Customer Service |  |  |  | 2025-05-20 |  | EP | 0 | 0.1 | 0.1 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P20091006 | s2434.1 | Install a greenfield 3-way 69 kV 1200 A phase over phase switch (Bryson Switch) with Auto-Sectionalizing, MOABs, and SCADA to serve the new requested delivery point. Install metering at the proposed customer station. | Customer Service |  |  |  | 2025-05-20 |  | EP | 0 | 0.7 | 0.7 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P20091001 | s2434.2 | Build a ~4.3 miles of greenfield single circuit 69kV transmission line between Hemlock – Bryson Switch with 556 ACSR conductor. | Customer Service |  |  |  | 2025-05-21 |  | EP | 0 | 9.4 | 9.4 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P20091005 | s2434.3 | At Hemlock station, install a new 69kV 3000 A 40kA circuit breaker towards Bryson Switch. | Customer Service |  |  |  | 2025-05-22 |  | EP | 0 | 1.1 | 1.1 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19293011 | s2435.1 | West Kingsport Station Work: Install five 138 kV 40 kA 3000A CBs and reconfigure existing Bus #2 to a breaker and a half arrangement. Note that the replacement of breaker E was accelerated due to a customer request and constrained outages and is currently in service to feed Industry Drive. Replace existing 34.5 kV CBs A, C and F with three new 69 kV-rated 3000A 40 kA breaker — to be energized at 34.5kV. Replace existing 34.5kV bus structures with new box bays built to 69kV. Remove existing 34.5 KV 14.4 MVAR Cap bank and Cap Bank Switcher. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-01 |  | EP | 0 | 9.2 | 9.2 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | DR23R18Y0 | s2435.2 | Line work and ROW required to relocate the North Bristol and Industry Drive 138KV lines at West Kingsport Station into the new configuration. This includes installing 3 structures (2 tower structures and 1 custom Steel Pole) to bring North Bristol Circuit in and relocate the Industrial Drive Circuit to final string of breakers. This also includes re-terminating the Ft. Robinson-West Kingsport 34kV line, Cumberland- West Kingsport 34.5kV Line and the Waste Water- West Kingsport 34kV Line into new station bays. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-26 |  | EP | 0 | 4.2 | 4.2 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17084055 | s2436.2 | Construct a greenfield 138KV Myra Station to replace Elwood Station. Install 138KV double box bay with two 138kV circuit breakers and line exits to Fremont & Beaver Creek. Install 138/34.5 kV transformer with high-side circuit switcher and associated 34.5kV breakers. Install fiber connectivity for upgraded relaying. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 0 | 3.43 | 3.43 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17084053 | s2436.3 | Remote end relaying work at Beaver Creek substation. Remove 46KV Elwood Line 46kV circuit breaker "G“ and associated equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 0 | 0.17 | 0.17 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17084050 | s2436.4 | Remote end relaying work at Fremont substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 0 | 0.42 | 0.42 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19036002 | s2436.5 | At Burton station, retire and remove all existing equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 25 | 0 | 0 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17084025 | s2436.6 | At Elwood station, retire and remove all existing equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 0 | 0 | 0 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17084007 | s2436.9 | Construct a new ~2 mi double circuit 138 kV line to the proposed Myra substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 0 | 8.8 | 8.8 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17084017 | s2436.10 | Reconfigure the existing Beaver Creek - Fremont 138kV circuit to facilitate the construction of the new double circuit Myra Extension 138kV Line to feed the proposed Myra Substation. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 0 | 1 | 1 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17084020 | s2436.11 | Install two replacement structures in order to bypass Elwood station. Transfer wires from old structure to new structure. Tie new structure to Cedar Creek-Henry Clay 46kV Line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 0 | 1.35 | 1.35 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17084018 | s2436.12 | Retire ~10.48 mi Beaver Creek – Elwood 46kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-30 |  | EP | 0 | 6.47 | 6.47 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17081001 | s2438 | Clifford Station: Replace the existing 138/69-46 kV, 50 MVA transformer #1 and 138/46 kV, 20 MVA transformer #3 with two 138/46 kV, 30 MVA transformers. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-16 |  | UC | 75 | 5.9 | 5.9 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P17081002 | s2439 | At Scottsville station, replace the existing 138/46 kV, 20 MVA transformer #1 & #2 (connected in parallel) and 138/46 kV, 20 MVA transformer #5 with two 138/46 kV, 30 MVA transformers; replace 46/12 kV, 5 MVA transformer #3 with 46/12 kV, 20 MVA transformer; replace 46 kV circuit breaker E; add 12 kV circuit breaker & feeder. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-16 |  | EP | 0 | 7 | 7 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19298001 | s2440.1 | Rebuild the 7.7 mile long Bridgman-Pletcher line with 556 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-07 |  | EP | 0 | 18.8 | 18.8 | 2020-12-18 | Mitchell Rice/Joshua Smith |  | FALSE
Supplemental | AEP | P19298015, P19298026, P19298027, P19298037 | s2440.2 | Install new 69/34.5kV Bucktown station to replace Buchanan Hydro station. Install new 69/34.5kV transformer with (2) 34.5kV line breakers and a (4) 69kV breaker ring bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-07 |  | EP | 0 | 10.4 | 10.4 | 2020-12-18 | Mitchell Rice/Joshua Smith |  | FALSE
Supplemental | AEP | P19298009 , P192980010, P192980011 | s2440.3 | Retire 1 mile of 4/0 copper conductor from Buchanan Hydro to Clark Equipment and Jack’s Post customer. Construct 0.1 miles of 34.5 kV line from Jack’s Post to new Bucktown station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-07 |  | EP | 0 | 1.5 | 1.5 | 2020-12-18 | Mitchell Rice/Joshua Smith |  | FALSE
Supplemental | AEP | P19298019, P19298022 | s2440.4 | At Buchanan Hydro station, retire the Transmission and Distribution equipment. Install one new 34.5kV breaker for line protection to Bucktown to continue service to the hydro plant. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-07 |  | EP | 0 | 1.3 | 1.3 | 2020-12-18 | Mitchell Rice/Joshua Smith |  | FALSE
Supplemental | AEP | P19095012 | s2444.1 | At Meadowview station, replace 69KV circuit breakers F&G with new 69kV 3000A 40kA breakers. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-01 |  | UC | 50 | 1.86 | 1.86 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19095003 | s2444.2 | At South Abingdon, install a new 90 MVA 138/ 69KV transformer bank. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-01 |  | UC | 50 | 3.4 | 3.4 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19095001 | s2444.3 | Construct a new 69kV line from South Abingdon to Arrowhead (~6.6 miles) (SN:129 MVA, SE: 180 MVA, WN: 162 MVA, WE: 202 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-01 |  | UC | 50 | 20.2 | 20.2 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19095008 | s2444.4 | At Arrowhead station, install three 69kV 3000A 40kA breakers towards Damascus, Hillman Highway, and South Abingdon. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-12 |  | UC | 50 | 2.2 | 2.2 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19095016 | s2444.5 | Retire the 69kV section of line from Abingdon to Hillman Highway (~5 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-08-05 |  | UC | 50 | 6.2 | 6.2 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P20039001 | s2444.6 | Rebuild ~23 miles of the Hillman Highway – Saltville 69 kV line (SN:129 MVA, SE: 180 MVA, WN: 162 MVA, WE: 202 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-08 |  | UC | 50 | 57.5 | 57.5 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P20039001 | s2444.7 | Retire ~23 miles of the Hillman Highway – Saltville 69 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-08 |  | UC | 50 | 6.9 | 6.9 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P20039007 | s2444.8 | Hillman Highway Remote End Work. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-08 |  | UC | 50 | 0.1 | 0.1 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19095004 | s2444.9 | At Abingdon station, retire 138/69-12kV transformer bank #1 and associated equipment. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-07-01 |  | UC | 50 | 0.3 | 0.3 | 2020-12-18 |  |  | FALSE
Supplemental | AEP | P19305008 | s2446.1 | Replace Belfry substation with Orinoco substation by installing a 69KV box bay and 12KV rural bay to be built in the clear southwest of existing Belfry station. Install 69/12kV 20 MVA transformer and two 12kV breakers. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 0 | 0.65 | 0.65 | 2021-01-15 |  |  | FALSE
Supplemental | AEP | P19305008 | s2446.2 | Retire Belfry 46kV substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 0 | 0 | 0 | 2021-01-15 |  |  | FALSE
Supplemental | AEP | P19305010 | s2446.3 | Retire 46kV equipment from Stone substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 0 | 0.07 | 0.07 | 2021-01-15 |  |  | FALSE
Supplemental | AEP | P19305009 | s2446.4 | At Hatfield substation, replace MOAB Y with a 69KV Circuit Breaker towards Stone 69kV line via New Camp and Orinoco. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 0 | 0.85 | 0.85 | 2021-01-15 |  |  | FALSE
Supplemental | AEP | P19305012 | s2446.5 | Retire the 46kV equipment at Sprigg station towards Stone (via Belfry). | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 0 | 0.05 | 0.05 | 2021-01-15 |  |  | FALSE
Supplemental | AEP | P19305014 | s2446.6 | Retire Turkey Creek Tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 0 | 0.76 | 0.76 | 2021-01-15 |  |  | FALSE
Supplemental | AEP | P19305005, P19305006 | s2446.7 | Retire the ~8.23 miles of the 46kV Sprigg – Stone 46 KV circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 0 | 6.73 | 6.73 | 2021-01-15 |  |  | FALSE
Supplemental | AEP | P15095041 | s2464 | Rebuild ~2 miles of 138kV line between East Wheelersburg and Texas Eastern using 795 ACSR 26/7 Drake (SE 359 MVA). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-04-15 |  | EP | 0 | 3.41 | 3.41 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004001 | s2465.1 | Retire ~3 miles of the Philo- Canton 138kV line, between Philo and East New Concord. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 6.18 | 6.18 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004003 | s2465.2 | Retire ~18 miles of the Philo-Torrey 138kV line, north of Bethel Church/Bloomfield and stopping at Newcomerstown. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 6.01 | 6.01 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004004 | s2465.3 | Rebuild from Philo to Str 62 a ~13.07 mile section of the Philo – Torrey 138kV line as double circuit, using 795 KCMIL 26/7 ACSR "Drake" conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 32.65 | 32.65 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004006 | s2465.4 | Build a greenfield ~4.76 mile double circuit line between Str. 62 on the Philo – Torrey line to the greenfield East New Concord Switch, using 795 KCMIL 26/7 ACSR "Drake" conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 13.27 | 13.27 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004002 | s2465.5 | Rebuild from the greenfield East New Concord Switch to Newcomerstown station a ~19.72 mile section of the Philo – Canton 138kV line as double circuit, using 795 KCMIL 26/7 ACSR "Drake" conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 49.26 | 49.26 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004008 | s2465.6 | Install a 3 Way Phase Over Phase Switch, 1200A, 138 KV Full SCADA Functionality (Rustic Switch) to replace the hard tap to Bridgeville. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 0.63 | 0.63 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004011 | s2465.7 | Rebuild the 1.9-mile radial T-line tap to Bridgeville as a double-circuit in-and-out loop up to the new 3-way switch, Rustic Switch. The new line will use 556.5 KCMIL ACSR 26/7 "Dove”. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 4.62 | 4.62 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004007 | s2465.8 | Install a 3 Way Phase Over Phase Switch, 1200A, 138 KV Full SCADA Functionality (Chandlersville Switch) to replace the hard tap to Chandlersville. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 0.63 | 0.63 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004013 | s2465.9 | A new 0.12-mile double circuit 138kV loop line is to be constructed to replace the existing tap to GM Co-op Chandlerville station, to supply a loop line circuit to a new switch structure. The new line will use 556.5 KCMIL ACSR 26/7 "Dove”. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 1.3 | 1.3 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004018 | s2465.10 | Install a 3 Way Phase Over Phase Switch, 1200A, 138 KV Full SCADA Functionality (Norfield Switch) to replace the hard tap to Bethel Church. Remove the existing Bloomfield 1-way switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 0.65 | 0.65 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004014 | s2465.11 | A new 0.5-mile double circuit 138kV line is to be constructed to replace a portion of the Philo- Torrey 138kV line, to supply a loop line circuit to a new two pole dead-end with one of the poles of the two pole dead-end supporting a new switch structure. From the switch structure, it will connect to an existing structure of the existing tap line to supply the Bloomfield – GM Co-op tap. The new line will use 556.5 KCMIL ACSR 26/7 "Dove". | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 0.96 | 0.96 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004010 | s2465.12 | Install a 3 Way Phase Over Phase Switch, 1200A, 138 KV Full SCADA Functionality (East New Concord Switch) to replace the hard tap to East New Concord. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 0.63 | 0.63 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004021 | s2465.13 | Upgrade the line protection relays at Philo, replacing the electromechanical relays with modern microprocessor-based relays. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 0.16 | 0.16 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P20004028 | s2465.14 | Connect OPGW fiber to stations and switches along the route, for telecom network connectivity. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 0.47 | 0.47 | 2021-02-17 |  |  | FALSE
Supplemental | AEP | P19296008 | s2469.1 | Rebuild ~43 miles of double circuit 138 kV line between Reusens and Roanoke substations. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-01-23 |  | EP | 0 | 142 | 142 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296002, P19296021, P19296024, P19296025, P19296027, P19296029, P19296031 | s2469.2 | Acquire additional Reusens-Roanoke 138 kV ROW as needed for the rebuild. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 13.7 | 13.7 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296007 | s2469.3 | Reconductor ~0.1 mile span into Ivy Hill Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 0.2 | 0.2 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296008 | s2469.4 | Tie into the existing Roanoke-Cloverdale 138 kV Line via a new ~0.3 mile extension. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 0.7 | 0.7 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296009 | s2469.5 | Install new wire as underbuild on the Reusens-Roanoke 138kV line and re-route the existing Campbell Avenue-Roanoke 34.5 kV line due to Roanoke substation reconfiguration. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 0.5 | 0.5 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296018 | s2469.6 | Re-route the existing Roanoke-Walnut 69kV line due to Roanoke substation reconfiguration. Three (3) replacement structures are expected to shift the alignment and follow the western part of the substation fence to terminate into the new box bay at Reusens Substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 1.1 | 1.1 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296003 | s2469.7 | At Roanoke station, replace 138 kV capacitor bank switcher “BB” with a 3000 A, 40 kA circuit breaker. Replace 138 kV capacitor bank switcher “CC” with a 3000 A, 40 kA circuit breaker. Replace 138 kV capacitor bank “CC” with a new 57.6 MVAr capacitor bank. Install high-side circuit switchers on Transformers #2 (138/34.5 kV) and #5 (138/69 kV). Replace transformer #5 (138/69/12 kV) with a 130 MVA, 138/69/12 kV transformer. Replace 69 kV circuit breakers “U” and “V” with 2000 A, 40 kA circuit breakers. Replace pilot wire relaying with fiber relaying associated with 69 kV CBs “U” and “V”, and 34.5 kV CB “L”. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 10.1 | 10.1 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296006 | s2469.8 | At Centerville station, reconfigure existing 138 kV with two (2) new 138 kV circuit breakers on each line exit towards Cloverdale and Reusens substations rated at 3000 A, 40 kA to eliminate the three terminal line. Replace MOAB ground switch with circuit switcher on high-side of the Transformer #1 (138/69/34.5 kV). Replace 69 kV circuit breaker “B”, associated disconnect switches and foundations with 3000 A, 40 kA circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 6.7 | 6.7 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296004 | s2469.9 | At Campbell Avenue station, replace pilot wire relaying with fiber relaying associated with 34.5 kV CB-B and 69 kV CB-C. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 0.9 | 0.9 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296005 | s2469.10 | At Walnut Avenue station, replace pilot wire relaying with fiber relaying associated with 69 kV CB-C. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 0.5 | 0.5 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | P19296010, P19296011, P19296012 | s2469.11 | Install fiber extensions and telecom to support SCADA connectivity along the line and at Vinton, Ivy Hill, Coffee, and Moseley stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-31 |  | EP | 0 | 1.2 | 1.2 | 2021-03-19 |  |  | FALSE
Supplemental | AEP | DP20C21Z0 | s2472 | Fifth Avenue 138 kV: Upgrade the existing 138 kV partial ring bus to a complete 138 kV ring bus and provide a high side connection for a new Distribution transformer. Complete the 138 kV ring bus by adding 2-138 kV circuit breakers along with associated bus work and relaying equipment. | Customer Service |  |  |  | 2025-04-25 |  | EP | 0 | 1 | 1 | 2021-03-19 | Adam Forshey/Brian Hatt |  | FALSE
Supplemental | AEP | P20151001, P20151002, P20151003, P20151004 | s2510 | Rebuild 0.96 miles of the AM General #2 – Twin Branch 34.5 kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-02-23 |  | EP | 0 | 4.3 | 4.3 | 2021-04-16 |  |  | FALSE
Supplemental | AEP | P19303004 | s2522.1 | Rebuild the existing 5.36 mile Lakin – Lock Lane 69 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-17 |  | EP | 0 | 11.9 | 11.9 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P19302008 | s2522.2 | Point Pleasant Station: replace existing 69 kV circuit breakers G and H with two new 69 kV 3000 A 40 kA circuit breakers. Replace existing cap switcher AA with a new 69 kV cap switcher. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-31 |  | EP | 0 | 2.1 | 2.1 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20186005 | s2523.1 | West Malta: Replace circuit breaker “A” with a 69kV 3000A 40kA circuit breaker. Replace MOAB “X” with a 69kV SCADA controlled switch. Remove Capacitor bank “AA” and the circuit switcher | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-22 |  | EP | 0 | 1.87 | 1.87 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20186006 | s2523.2 | South Rokeby: Remote end upgrades to coordinate with new relaying at West Malta will require a transclosure at South Rokeby and an upgrade to the existing station service. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-23 |  | EP | 0 | 0.69 | 0.69 | 2021-05-21 | Karmyn Wilford/Sophia Halter |  | FALSE
Supplemental | AEP | P20249003 | s2524.1 | Rebuild from Howard to Ohio Central as 138kV double-circuit (64 miles), using 795 ACSR conductor. Note that the approx. 0.5 mile 138kV line segments outside Ohio Central station will not be rebuilt, as they are newer and in better condition; connect these existing T-line segments to the rebuilt Philo-Howard line asset. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-01 |  | EP | 0 | 142.26 | 142.26 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20250003 | s2524.2 | Rebuild from Ohio Central to Philo as 138kV single-circuit (19 miles), using 795 ACSR conductor. The existing Ohio Central-Philo #2 138kV circuit will be retired. Update both terminal stations to account for the retired circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-01 |  | EP | 0 | 43.45 | 43.45 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20014015 | s2524.4 | At West Trinway station, replace 138kV through-path risers & bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-22 |  | UC | 75 | 0.12 | 0.12 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20249007 | s2524.5 | Modify 138kV protective relay settings at Philo, Culbertson, Ohio Central, Academia, North Bellville, North Lexington, and Howard stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-01 |  | EP | 0 | 0.69 | 0.69 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20024001 | s2525.1 | Rebuild of the Astor – East Broad 138 KV circuit, approximately 2.75 miles in length; with 477KCM ACSS. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-30 |  | EP | 0 | 9.5 | 9.5 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20024002 | s2525.2 | Astor 138 kV Station: Remote end work including replacing the line surge arresters, relay settings, and line termination. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-30 |  | EP | 0 | 0.1 | 0.1 | 2021-05-21 |  |  | FALSE
Supplemental | AEP |  | s2525.3 | East Broad 138 kV Station: Remote end work including relay settings and line termination. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-30 |  | EP | 0 | 0.02 | 0.02 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20005019 | s2526.2 | Cyprus – Cyprus (Customer) 138 kV #1: Build ~0.3miles of double circuit 138kV line using 795 ACSR conductor. Extend fiber cable & install redundant fiber cable for relaying and communication to the customer station. One circuit will serve customer’s first building, second circuit will be partially constructed to be utilized for future second building to customer’s redundancy requirements. | Customer Service |  |  |  | 2025-02-28 |  | EP | 0 | 0.96 | 0.96 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20005002 | s2526.3 | Cyprus – Cyprus (Customer) 138 kV #2: Build ~0.3miles of double circuit 138kV line using 795 ACSR conductor. Extend fiber cable & install redundant fiber cable for relaying and communication to Customer Station. One circuit will serve customer’s first building, second circuit will be partially constructed to be utilized for future second building due to customer’s redundancy requirements. | Customer Service |  |  |  | 2025-02-28 |  | EP | 0 | 0 | 0 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P21580002 | s2527.7 | West Millersport – West Lancaster 138 kV Sag Study Mitigation: The new customer will increase loading on the existing West Millersport – West Lancaster 138 kV circuit. Multiple structure and distribution crossing issues will be mitigated on the line in order to allow the line to operate to its conductor’s designed maximum operating temperature. | Customer Service |  |  |  | 2024-12-17 |  | EP | 0 | 1.5 | 1.5 | 2021-05-21 |  |  | FALSE
Supplemental | AEP | P20009040 | s2534.1 | Construct ~ 5.1 miles of new 69 kV line between the existing Trail and Alpine delivery points using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 18.5 | 18.5 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009007 | s2534.4 | Retire West Wilmont Jct Sw. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.04 | 0.04 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009010 | s2534.5 | West Wilmont- Holmes Wayne Co-op line work for Alpine station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.1 | 0.1 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009018 | s2534.6 | Biliar – West Wilmont 69kV line work for Alpine station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 1.2 | 1.2 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009019 | s2534.7 | Beartown – West Wilmont 69kV line work for Alpine station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.5 | 0.5 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009002 | s2534.8 | Build a new station (called Alpine), replacing West Wilmont Junction Switch. This station will be a 4 breaker 69kV ring bus utilizing 3000A 40kA breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-06-16 |  | EP | 0 | 6.8 | 6.8 | 2020-11-20 | David Roudebush/Brendan Fuller |  | FALSE
Supplemental | AEP | P20009021 | s2534.9 | Remote end relay work at Beartown station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.03 | 0.03 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009022 | s2534.10 | Remote end relay work at Moreland Sw. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.03 | 0.03 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009008 | s2534.11 | Retire Shie Hill Sw. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-07 |  | EP | 0 | 0.04 | 0.04 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009003 | s2534.12 | Build a new station replacing Shie Hill Sw named Shie Hill. This station will be a 3 breaker 69kV ring bus utilizing 3000A 40kA breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-07 |  | EP | 0 | 6.4 | 6.4 | 2020-11-20 | David Roudebush/Brendan Fuller |  | FALSE
Supplemental | AEP | P20009011 | s2534.13 | Sugar Creek – Millersburg 34.5kV line work for Shie Hill station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2026-04-20 |  | EP | 0 | 1.6 | 1.6 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009049 | s2534.14 | Shie Hill- Holmes Wayne Co-op line work for Shie Hill station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-10-07 |  | EP | 0 | 0.1 | 0.1 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009028 | s2534.15 | Remote end relay work at Sugarcreek Terminal station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.4 | 0.4 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009029 | s2534.16 | Remote end relay work at Berlin station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.3 | 0.3 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009043 | s2534.17 | Install a new 138 kV 3000A 40kA breaker at West Millersburg Station on the line towards Wooster to reduce contingency impacts and potential low voltage concerns resulting from the new load. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.8 | 0.8 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009027 | s2534.18 | Replace the 2-way POP Switch at North Fredericksburg with a new 1200A 69 kV POP with new MOAB’s. The switch currently in place is not capable of supporting the necessary new equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 1 | 1 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20009033 | s2534.19 | Moreland Sw- Biliar line work for North Fredricksburg Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 0.9 | 0.9 | 2020-11-20 |  |  | FALSE
Supplemental | AEP | P20236001, P20236002, P20236004 | s2570.1 | Deer Creek – Hartford City 69 kV: Rebuild ~17.67 miles of 69 kV line with the conductor size 556.5 ACSR 26/7 Dove. The following cost includes the line rebuild, line removal and right of way. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-21 |  | EP | 0 | 40.69 | 40.69 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20236003 | s2570.2 | Hummel Creek – Deer Creek 34.5 kV: Retire ~4.6 miles of 34.5 kV 1940s wood line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-01-10 |  | EP | 0 | 1.01 | 1.01 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20236009 | s2570.3 | Jonesboro – Gas City 34.5 kV : Retire ~0.99 miles of 34.5 kV 1969 wood line. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-09-03 |  | EP | 0 | 0.42 | 0.42 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20236011 | s2570.4 | Deer Creek – Alexandria 34.5 kV : Retire ~2.2 miles of 34.5 kV 1968 wood line. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-08-15 |  | EP | 0 | 1.23 | 1.23 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20236005, P20236012 | s2570.5 | Hummel Creek 34.5 kV Station: Remove the 34.5 kV circuit breaker “M”. Replace 34.5 kV circuit breaker “L” with a system spare circuit breaker. Rebuild the 34.5 kV bus to a 69 kV standards. Install a 138 kV high side circuit switcher on the 138/34.5 kV transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-06-11 |  | EP | 0 | 1.74 | 1.74 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20244001, P20244002, P20244003, P20244004 | s2571.1 | Riverside – Hartford 138kV: Rebuild the ~14.7 miles of 1950’s wood H Frame line with 795 Drake ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-06 |  | EP | 0 | 26.9 | 26.9 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20244026, P20244005, P20244006, P20244007 | s2571.2 | South Haven – Hartford 69kV: Rebuild the ~18.7 miles of 1960’s wood pole line with 795 Drake ACSR. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-03-17 |  | EP | 0 | 37.1 | 37.1 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20244012, P20244013 | s2571.3 | Phoenix Switch 69kV: Replace the switch with a new POP Switch with line MOAB’s. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-18 |  | EP | 0 | 0.6 | 0.6 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19304003 | s2572.1 | Rebuild and reconfigure the Saltville 138 KV station in a 3 string breaker-and-a-half bus arrangement to allow replacement of 138 KV CBs A, B, C, V, L, and U with new 3000A 40 KA circuit breakers. Replace existing 69 KV circuit breaker J with a new 3000A 40 KA circuit breaker. Replace existing Transformer #1 with a new 138/69-34.5 KV 50 MVA transformer. Replace existing high side MOAB switches with high side circuit switchers on T2&T5. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-01 |  | EP | 0 | 13.54 | 13.54 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19304011 | s2572.2 | Line work and ROW required to relocate the Broadford – Saltville #1 138KV, Broadford – Saltville #2 138KV, Clinch River – Saltville 138KV lines to terminate into Saltville Station’s new configuration. This work includes installing 2 structures (steel tower structures) and total of ~0.24 new wire and old wire replacement. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-01 |  | EP | 0 | 1.87 | 1.87 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19304001 | s2572.3 | Rebuild ~21 miles of the 138KV line between Saltville and Tazewell stations (SN/SE/WN/WE: 296/413/375/464 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-01 |  | EP | 0 | 59.5 | 59.5 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19304004 | s2572.4 | Remote End Work Costs Tazewell, Meadowview, Broadford and Clinch River Stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-01 |  | EP | 0 | 0.7 | 0.7 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20235001 | s2574 | Once the Jubal Early to Point Lookout line is built, rebuild the existing ~11.4 mile 69kV Fries – Point Lookout line on the current center line. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-12-19 |  | EP | 0 | 33 | 33 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010027 | s2575.1 | Install a new 3-way POP Switch (Mousey Sw) and 69 kV metering to serve North Central’s Sycamore station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 0.68 | 0.68 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010043 | s2575.2 | Construct ~ 13 miles of new 69 kV line between Bucyrus Center and the new Mousey Switch delivery point using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 29.3 | 29.3 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010034 | s2575.3 | Install a new 69 kV 3000A 40kA breaker and associated terminal equipment at Bucyrus Center on the line towards Mousey switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 1.02 | 1.02 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010007 | s2575.4 | Remove the existing West Rockaway 69 kV switch currently used to radially serve the Sycamore delivery point. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 0.08 | 0.075 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010003 | s2575.5 | Construct ~ 0.8 miles of new 69 kV line between the existing Sycamore radial line and East Tiffin delivery points using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 2.54 | 2.54 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010036 | s2575.6 | Reconfigure East Tiffin station to add in a box bay, a breaker, and terminal equipment towards Mousey switch and a new line MOAB toward South Tiffin. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 2.5 | 2.5 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010016 | s2575.7 | Rebuild ~ 2.3 miles of new 69 kV line between the existing Bucyrus and East Bucyrus delivery points using 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 5.9 | 5.9 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010012 | s2575.8 | Remove ~ 16 miles of existing 69 kV line between the existing East Bucyrus and Howard delivery points. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 5.94 | 5.94 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010019 | s2575.9 | Retire the existing ~1.4 miles of the Howard- Bucyrus #2 line between Bucyrus station and structure 366. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 0.32 | 0.32 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20010009 | s2575.10 | Construct ~ 1.3 miles of new 69 kV line between the existing East Bucyrus delivery point and structure 336 on the Howard- East Bucyrus #2 line. This construction will be coordinated with rebuild project S2156. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-01 |  | EP | 0 | 3.3 | 3.3 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19248004 | s2576.1 | Lick-Jefferson 69kV: Rebuild ~8.3 miles of the 69kV line from Structure 29 to Jefferson switch station with 556.5 ACSR. Install shield wire from Structure 29 to Lick Station, approximately 4 miles. This work requires tree clearing and access road construction in order to add the shield wire to existing structures. Total access road construction is 5.5 miles. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-03-05 |  | EP | 15 | 25 | 25 | 2021-07-16 | Pravi Goplan/Andrew Garlick |  | FALSE
Supplemental | AEP | P19248002 | s2576.2 | Echo Valley: Replace existing switch with a 3-way phase over phase 69kV 1200A Switch with SCADA. There will be auto-sectionalizing enabled toward Firebrick. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-04-13 |  | EP | 0 | 1.39 | 1.39 | 2021-07-16 | Pravi Goplan/Andrew Garlick |  | FALSE
Supplemental | AEP | P19248008 | s2576.3 | Remote end work associate with the line rebuild at Lick & Firebrick. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-07-15 |  | EP | 0 | 0.31 | 0.31 | 2021-07-16 | Pravi Goplan/Andrew Garlick |  | FALSE
Supplemental | AEP | P19119005 | s2577.1 | Rebuild the South Lancaster – East Logan 69 KV circuit, approximately 16.6 miles in length, with 556.5 ACSR Dove conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-29 |  | EP | 0 | 40 | 52 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19119009 | s2577.2 | Rebuild the Enterprise Switch - Enterprise Metering Structure, approximately 200’ in length; with 556.5 ACSR Dove conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-27 |  | EP | 0 | 0.51 | 0.51 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19119012 | s2577.3 | Enterprise Switch: Replace the two way phase over phase switch with a new 1200A three way phase over phase switch with auto sectionalizing and SCADA functionality. Replace the CTs, PTs, and metering. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-27 |  | EP | 0 | 0.93 | 0.93 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19119011 | s2577.4 | West Logan: Replace the three way phase over phase switch with a new 1200A three way phase over phase switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-21 |  | EP | 0 | 0.77 | 0.77 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P19119016 | s2577.5 | South Lancaster: Remote end work. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-07 |  | EP | 0 | 0.1 | 0.1 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20225007 | s2578.2 | Innovation Extension 138kV: Tap the existing Babbitt-Kirk 138kV circuit creating the Babbitt-Innovation and Kirk-Innovation 138kV circuits and construct approximately 2.2 miles of double circuit line to serve the new station. Extend the telecom fiber into Innovation station for relaying/communication. | Customer Service |  |  |  | 2025-05-22 |  | EP | 0 | 13.33 | 13.334 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20225016 | s2578.4 | Babbitt 138 kV Station: Update remote end relay settings and telecom electronics. | Customer Service |  |  |  | 2025-05-22 |  | EP | 0 | 0.07 | 0.074 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P20225017 | s2578.5 | Kirk 138 kV Station: Update remote end relay settings and telecom electronics. | Customer Service |  |  |  | 2025-05-22 |  | EP | 0 | 0.06 | 0.062 | 2021-07-16 |  |  | FALSE
Supplemental | AEP | P22024001, P22024002, P22024007, P20179011, | s2584.1 | East Elkhart – Mottville Hydro 138kV: Rebuild the ~10 miles of 1950’s wood on the East Elkhart – Mottville Hydro 138kV line using 795 Drake ACSR | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-08-18 |  | EP | 0 | 31 | 31 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20179012, P20179013, P20179025, P20179030 | s2584.2 | Mottville Hydro – Corey 138kV: Retire the ~9 mile 138kV line | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-02-12 |  | EP | 0 | 4.25 | 4.25 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20179009 | s2584.6 | Sturgis 69kV Station: Retire Sturgis 69kV station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-03-25 |  | EP | 0 | 0.9 | 0.9 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20179004, P20179005, P20179043, P20179023 | s2584.7 | Stubey Rd 138/69kV Station: Expand station to include (6) 69kV CB’s in a ring , (4) 138kV CB’s in a ring, (2) 138/69kV 130MVA XFR’s and (2) 17.6Mvar 69kV Cap Banks. Reterminate the Sturgis IP line into Stubey Road. Reterminate the Corey line into Stubey Road to energize the line at 138 kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-12-20 |  | EP | 0 | 18.9 | 18.9 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20179026 | s2584.8 | Howe (Nipsco) – Sturgis 69kV: Retire the ~2.9 mile 69kV line | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-03-25 |  | EP | 0 | 1.9 | 1.9 | 2021-08-16 |  |  | TRUE
Supplemental | AEP | P20179014, P20179015, P20179016 P20179017 | s2584.9 | Mottville Hydro – Stubey Rd 138kV: Re-energize the existing line from Mottville – Pigeon River to 138kV and construct a new ~8.9 mile 138kV line between Pigeon River and Stubey Road to re-establish the 138 kV through path to Corey station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-15 |  | EP | 0 | 23.7 | 23.7 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20179031 | s2584.10 | Pigeon River 69kV Station: Remove 69kV CB “K” from Pigeon River to re-use at Stubey Rd. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-15 |  | EP | 0 | 0.4 | 0.4 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20179010 | s2584.11 | Mottville Hydro 138/69kV Station: Remove 69kV CB “D” from Mottville Hydro to re-use at Stubey Rd. E | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-15 |  | EP | 0 | 0.4 | 0.4 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20179001 | s2584.12 | Corey 138/69kV Station: Remove 69kV CB “C” from Corey to re-use at Stubey Rd. E | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-11-15 |  | EP | 0 | 0.4 | 0.4 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20179018, P20179019 | s2584.13 | White Pigeon 69kV Ext: Build new 69kV .2 mile extension from Corey – Pigeon River to the existing White Pigeon Station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-12-17 |  | EP | 0 | 1.7 | 1.7 | 2021-08-16 |  |  | FALSE
Supplemental | AEP | P20213015 | s2632.1 | Lincoln – Tillman 34.5kV line: Retire approximately ~11 miles of the Lincoln – Tillman 34.5kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  | EP | 0 | 2.8 | 2.8 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20213007 | s2632.2 | Lincoln 138/69/34.5kV substation : Remove Lincoln CB “P”. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  | EP | 0 | 0.1 | 0.1 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20213008, P20213009 | s2632.3 | Tillman 138/34.5kV substation: Remove CB “A” and “B” as well as the 138/34.5kV transformer and all 34.5kV equipment | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  | EP | 0 | 0.4 | 0.4 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20213006 | s2632.4 | St Rd 14 Sw: Remove St Rd 14 34.5kV Sw | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  | EP | 0 | 0.1 | 0.1 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20213010, P20213011 | s2632.5 | Huguenard 138kV extension: Rebuild a portion of the Lincoln-Tillman line as a new ~2.5 mile 138kV double circuit extension from the Allen – Milan 138kV line to Huguenard 138/34.5kV substation | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  | EP | 0 | 7.9 | 7.9 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20213001, P20213002, P20213003, P20213016 | s2632.6 | Huguenard 138/34.5kV station: Build the new 138/34.5kV substation to feed the St Rd 14 load. This station will have 2 138kV CB’s, 1 138kV Circuit switcher, 1 34.5kV CB and a 138/34.5kV 30MVA XFR. The XFR, 34.5kV CB and high side switcher will be reused from Tillman substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  | EP | 0 | 5.1 | 5.1 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20213010, P20213011 | s2632.7 | Huguenard – ST Rd 14 34.5kV: Rebuild the radial 34.5kV line to connect to the new Huguenard substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-06-01 |  | EP | 0 | 0.9 | 0.9 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P19268001 | s2634.1 | Construct approximately 3 miles of new 46 kV line from Kincaid to Westerly. Rebuild 5.4 miles of the existing Westerly – Pax Branch 46 kV line. New line to be constructed at 69 kV, operated at 46 kV. Install fiber on the new line construction for upgraded relaying communication. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-07 |  | EP | 0 | 23.1 | 23.1 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P19268004 | s2634.2 | Retire Toms Fork – Westerly 46 kV and Toms Fork – Str. 364-13 46 kV (approximately 24 miles total) | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-07 |  | EP | 0 | 8.9 | 8.9 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P19268005 | s2634.3 | 6 wire the existing double circuit 46 kV line from Cabin Creek to Str. 364-13 to maintain the feed to Rhoda station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  | EP | 0 | 0.2 | 0.2 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | p19268007 | s2634.4 | Construct a new 138 kV double circuit in/out (approx. 2 miles) from Kanawha – Sundial #1 138 kV circuit to Toms Fork Station. Because of the very rugged terrain in the area, large angles and long span construction is required. These heavy angles and long spans mean minimal tangent structures could be utilized and required dead end towers for nearly every structure instead. These dead end towers are very heavy, resulting in larger equipment and steel costs, and require large foundations resulting in higher costs | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  | EP | 0 | 9.1 | 9.1 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P19268009 | s2634.5 | Convert Toms Fork Station to 138 kV by installing a new 138/12 kV XFR, circuit switcher and two 138 kV line switches. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  | EP | 0 | 1.5 | 1.5 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P19268012 | s2634.6 | Replace existing switches at Westerly Station with two new 1200 A switches. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  | EP | 0 | 0.5 | 0.5 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P1919268015 | s2634.7 | Replace existing switches at Fork Ridge/Mossy Creek with two new 1200 A switches, renamed Haystack Station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  | EP | 0 | 0.7 | 0.7 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P19268016 | s2634.8 | Kincaid remote end work. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  | EP | 0 | 0.4 | 0.4 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P19268017 | s2634.9 | Pax Branch remote end work. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-10-07 |  | EP | 0 | 0.4 | 0.4 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P21016002 | s2635.1 | Replace existing hard tap at SCSM with a new 1200 A three way SCADA controlled MOAB switch | Operational Flexibility and Efficiency |  |  |  | 2025-04-18 |  | EP | 0 | 0.7 | 0.7 | 2021-09-17 | Jared/Frye/Michael Hassay |  | FALSE
Supplemental | AEP | P21016005 | s2635.2 | Replace existing hard tap at CMS with a new 1200 A three way switch | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-04-18 |  | EP | 0 | 0.4 | 0.4 | 2021-09-17 | Jared/Frye/Michael Hassay |  | FALSE
Supplemental | AEP | P21016001 | s2635.3 | Reconfigure 0.13 mile of the Chemical – Ward Hollow line to accommodate the new switches being installed | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-04-18 |  | EP | 0 | 1.8 | 1.8 | 2021-09-17 | Jared/Frye/Michael Hassay |  | FALSE
Supplemental | AEP | P20011027 | s2637.1 | Install a new 69 kV 3-way POP Switch (Kilbourne Sw) and 69 kV metering to serve North Central’s Republic Station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.64 | 0.64 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20011005 | s2637.2 | Construct a new 3- breaker 69kV Station in a ring configuration named Founders | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 5.1 | 5.1 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | J20011001 | s2637.3 | Construct ~ 8 miles of new 69 kV line between Tiffin Center and the new Kilbourne Switch delivery point using 556 ACSR conductor. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 11.99 | 11.99 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20011025 | s2637.4 | Install a new 69 kV 3000A 40kA breaker and associated terminal equipment at Tiffin Center on the line towards Kilbourne switch | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.7 | 0.7 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20011001 | s2637.5 | Remove the existing Honey Creek 69 kV switch currently used to radially serve the Republic delivery point | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.1 | 0.1 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | P20011007 | s2637.6 | Construct ~ 0.83 miles of new 69 kV double circuit line between structure 103 on the Carrothers- Greenlawn circuit to the new Founders delivery point using 556 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 2.4 | 2.4 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | DX20A02A0 | s2638.1 | Construct a new 69-12kV station (“Ruby”) 0.2-mile to the east of Robyville, on new property. The station will have a 4-breaker 69kV ring bus, with 3- 69kV circuit connections and serving one AEP Ohio distribution transformer | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-11-30 |  | EP | 0 | 6.2 | 6.2 | 2021-09-17 | luz Cohmer/Jerod Marker |  | FALSE
Supplemental | AEP | P17125009 | s2638.2 | At the 69kV remote-end of South Cadiz: Replace 69kV circuit breaker D, line relays to Ruby, and 69kV bus protection; expand control building | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-01-23 |  | EP | 0 | 1.3 | 1.3 | 2021-09-17 | luz Cohmer/Jerod Marker |  | FALSE
Supplemental | AEP | DX20A02B1 | s2638.3 | At the 69kV remote-end of Dillonvale: Replace 69kV circuit breaker B, line relays to Ruby, and 69kV bus protection | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-11-30 |  | EP | 0 | 0.8 | 0.8 | 2021-09-17 | luz Cohmer/Jerod Marker |  | FALSE
Supplemental | AEP | P17125013 | s2638.4 | Re-route the three 69kV transmission lines near Robyville to extend to the new Ruby station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-02-18 |  | EP | 0 | 1.8 | 1.8 | 2021-09-17 | luz Cohmer/Jerod Marker |  | FALSE
Supplemental | AEP | P17125011 | s2638.5 | Remove the former DTE Coal 69kV switch just south of South Cadiz station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-01-23 |  | EP | 0 | 0.04 | 0.04 | 2021-09-17 | luz Cohmer/Jerod Marker |  | FALSE
Supplemental | AEP | P17125020 | s2638.6 | Retire the existing Robyville station and remove all equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-02-18 |  | EP | 0 | 0.4 | 0.4 | 2021-09-17 | luz Cohmer/Jerod Marker |  | FALSE
Supplemental | AEP | DP21C05Z0 | s2639.1 | Poth 138 kV Station: Construct a greenfield station 138kV ring bus with (4) 3000A 63kA 138kV breakers and two 138/13 kV transformers to replace the existing 40 kV station. | Customer Service |  |  |  | 2024-08-09 |  | EP | 0 | 4.19 | 4.19 | 2021-09-17 | Hannah ing/Robert Richardson |  | FALSE
Supplemental | AEP | DP21C05D4 | s2639.2 | East Broad 138 kV Station: Replace CB 3 & CB 7 and 4 disconnect switches with 3000A 63kA 138kV breakers and 4-3000A disconnect switches and install new relaying to coordinate with the new relays at Poth station | Customer Service |  |  |  | 2024-08-13 |  | EP | 0 | 0.79 | 0.793 | 2021-09-17 | Hannah ing/Robert Richardson |  | FALSE
Supplemental | AEP | DP21C05Z0 | s2639.3 | Yearling 138 kV Station: Remote end relay settings | Customer Service |  |  |  | 2024-08-13 |  | EP | 0 | 0.06 | 0.064 | 2021-09-17 | Hannah ing/Robert Richardson |  | FALSE
Supplemental | AEP | DP21C05W2 | s2639.4 | Poth Extension 138 kV: Tap the existing East Broad-Bexley 138kV line into Poth station by constructing approximately 0.5 miles of greenfield lines from the line taps. Extend telecom ADSS for relaying and communication from Bexley to Poth & East Broad to Poth. | Customer Service |  |  |  | 2024-08-13 |  | EP | 0 | 3.06 | 3.06 | 2021-09-17 | Hannah ing/Robert Richardson |  | FALSE
Supplemental | AEP | P20210002 | s2640.1 | At West Dover station, install 4- 138kV breakers in a ring bus arrangement. Install 1- 69kV breaker on the low-side of the 138-69kV transformer. Remove the existing control building and install a new prefabricated drop-in-control-module (DICM). Upgrade the 69kV circuit protection to Sugarcreek, replacing electromechanical relays with new fiber-based protection. Various improvements to the station site, including new fencing, grading, and station service | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-12 |  | UC | 31 | 7.03 | 7.03 | 2021-09-17 | Todd Sides/Jerod Marker |  | FALSE
Supplemental | AEP | P20210004 | s2640.2 | Re-terminate the 3- 138kV transmission lines at West Dover to connect to the new ring bus layout. The Sugarcreek 138kV tap will be re-routed slightly. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-12 |  | UC | 31 | 0.77 | 0.77 | 2021-09-17 | Todd Sides/Jerod Marker |  | FALSE
Supplemental | AEP | P20210005 | s2640.3 | Remote-end 69kV protection upgrades at Sugarcreek station, to coordinate with the West Dover upgrades | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-10-01 |  | UC | 31 | 0.51 | 0.51 | 2021-09-17 | Todd Sides/Jerod Marker |  | FALSE
Supplemental | AEP | P19178030 | s2650.1 | Rebuild Mark Center station in the clear as Platter Creek station. Install 4 new 3000A, 40kA, 69 kV breakers at the new Platter Creek ring bus and add a DICM. Upgrade NW Coop 69 kV metering. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | UC | 31 | 6.37 | 6.37 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  | FALSE
Supplemental | AEP | P19178013 | s2650.2 | Retire existing Mark Center station. Relocate circuit switcher AA to Platter Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | UC | 31 | 0.76 | 0.76 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  | FALSE
Supplemental | AEP | P19178018 | s2650.3 | Remote end work at South Hicksville station | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | UC | 31 | 0.57 | 0.57 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  | FALSE
Supplemental | AEP | P19178030 | s2650.4 | Relocate Mark Center – Continental to terminate at Platter Creek | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | UC | 31 | 0.37 | 0.37 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  | FALSE
Supplemental | AEP | P19178008 | s2650.5 | Relocate Mark Center – Paulding to terminate at Platter Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | UC | 31 | 0.51 | 0.51 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  | FALSE
Supplemental | AEP | P19178006 | s2650.6 | Relocate Mark Center – South Hicksville to terminate at Platter Creek | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | UC | 31 | 0.4 | 0.4 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  | FALSE
Supplemental | AEP | P19178010 | s2650.7 | Relocate Mark Center- NW Co-op to terminate at Platter Creek | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-31 |  | UC | 31 | 0.02 | 0.02 | 2021-10-15 | Danielle Hilliard/Brendan Fuller |  | FALSE
Supplemental | AEP | P20224003 | s2651.1 | Rebuild the Philo-Torrey 138kV transmission line between South Canton and Torrey (3.5 miles). The circuits affected are South Canton-Timken Richville and Timken Richville-Timken 138kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-01 |  | EP | 0 | 7.64 | 7.64 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P20224001 | s2651.2 | Rebuild the Philo-Canton 138kV transmission line between South Canton and Sunnyside (5.5 miles). The circuits affected are South Canton-Southeast Canton and Southeast Canton-Sunnyside 138kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-01 |  | EP | 0 | 14.22 | 14.22 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P20224010 | s2651.3 | Replace the 138kV switches at Faircrest Street station to accommodate the new line structures. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-01 |  | EP | 0 | 0.12 | 0.12 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19099014 | s2651.4 | At Sunnyside, upgrade the relays on the 138kV circuit to Southeast Canton. The control building needs expanded to accommodate the new relay panels. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-11-01 |  | EP | 0 | 0.73 | 0.73 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P21033014 | s2652 | Install a new 69kV 3000A 40kA breaker to replace breaker K at Howard station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 1.1 | 1.1 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P20245001, P20245002, P20245003, P20245007 | s2654.1 | New Carlisle - Maple 138 kV: Rebuild ~0.95 miles of 138 kV single circuit line with 1590 ACSR 45/7 Lapwing to match the NIPSCO owned conductor size. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  | EP | 0 | 1.76 | 1.76 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P20245004, P20245008 | s2654.2 | New Carlisle - Bosserman 138 kV: Rebuild ~0.95 miles of 138 kV double circuit line with 1590 ACSR 45/7 Lapwing to match the NIPSCO owned conductor size and transition fiber installation for NIPSCO connectivity. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  | EP | 0 | 1.86 | 1.86 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P20245005, P20245006 | s2654.3 | New Carlisle – South Bend 138 kV: Remove ~0.86 mile of the existing 138 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  | EP | 0 | 0.17 | 0.17 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P20245009 | s2654.4 | Bosserman 138 kV Station: Relay settings changes. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  | EP | 0 | 0.08 | 0.08 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P20245010 | s2654.5 | New Carlisle 138 kV station: Remote end relaying upgrades and settings changes. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-05-02 |  | EP | 0 | 0.82 | 0.82 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | A19036089, P21010001 | s2655.1 | Retire the ~3.65 mile 138kV Lincoln extension and reconnect the existing line between Robison Park and Allen. The extension can be retired due to previous upgrades strengthening the underlying sub-transmission system through connections to other sources and a rebuild of the existing Robison Park-Allen and Lincoln-Robison Park lines which increased the 138 kV capacity. This extension does not impact the larger 138 kV network as Lincoln station will keep three 138 kV sources to serve the Fort Wayne area. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-09-22 |  | EP | 0 | 2.8 | 2.8 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | A19036084 | s2655.2 | At Lincoln station, retire 138kV CB “B” and “C”, Replace 138kV CB “I” and relocate 138kV CB “A” to the old CB “C” position. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-09-22 |  | EP | 0 | 2 | 2 | 2021-09-17 |  |  | FALSE
Supplemental | AEP | A19036104, P21022002, P21022003, P21022004 | s2656.1 | On the Colony Bay – Illinois Rd 69kV line, rebuild approximately 2.7 miles and re-conductor approximately 3.6 miles with 556.5 ACSR. The 3.6 miles to be reconductored has newer structures that do not need replaced due to various INDOT and Fort Wayne road widening projects that have replaced structures more recently but kept the original conductor in place. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-03-19 |  | EP | 0 | 10.7 | 10.7 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P21022001, P21022007, P21022009 | s2656.2 | Aboite 69kV Switch: Replace Aboite 69kV Switch due to the line structure replacements. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-03-19 |  | EP | 0 | 0.8 | 0.8 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056020, P19056011 | s2657.1 | Blossom Trail – Colby 34.5kV: Retire the ~10.2 miles of 34.5kV line between Blossom Trail – Dowagiac Tap. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-04-16 |  | EP | 0 | 3 | 3 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056005, P19056006, P19056023 | s2657.2 | Rudy Tap 34.5kV: Replace the failed Rudy Tap Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 0.7 | 0.7 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056007 | s2657.3 | Colby North Ext 138kV: Reterminate the Valley 138kV line into Colby with a .1 mile new extension | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 1.1 | 1.1 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056004, P19056016 | s2657.4 | Colby South Ext 138kV: Reterminate the Kenzie Creek 138kV line into Colby with a .25 mile new extension | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 1.5 | 1.5 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056003 | s2657.5 | Colby – Rothedew 34.5kV line: Reterminate the Rothedew 34.5kV line into Colby | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 0.3 | 0.3 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056008 | s2657.6 | Colby - Dowagiac 34.5kV : Reterminate the Dowagiac 34.5kV feed back into Colby station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 1 | 1 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056014 | s2657.7 | Colby – Rudy Tap 34.5kV : Reterminate the Rudy Tap 34.5kV feed back into Colby station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 1 | 1 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056018 | s2657.8 | Colby – Kenzie Creek 69kV : Reterminate the Kenzie Creek 69kV feed back into Colby station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 0.7 | 0.7 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056017 | s2657.9 | Colby 138kV Switch: Retire the Colby 138kV Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 0.2 | 0.2 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | A19036083, P19056001, P19056002, P19056024 | s2657.10 | Colby 138/69/34.5kV: On the existing property, build a new 138kV yard with 4 CB’s built in a ring configuration. Install a new 138/34.5 50MVA XFR with a low side CB protecting the single line exit toward Rudy Tap to replace the source previously served by the retired line to Blossom Trail. Install 3 34.5kV CB’s on a new 34.5kV bus that will be connected to the existing 138/69/34.5kV XFR, and the Rothedew and Dowagiac exits. Install a new 69kV CB toward Kenzie Creek. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 11.9 | 11.9 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | P19056020, P19056011 | s2657.11 | Blossom Trail 138/69/34.5kV: Remove CB “M” and reuse it at Colby station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2030-04-16 |  | EP | 0 | 0.2 | 0.2 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | A19036097, A19036098, A19036099, P21080001 | s2658 | New Buffalo – Bridgman 69kV line: Rebuild the 22.1 mile New Buffalo – Bridgman 69kV line with 556.5 ACSR Dove. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-11-24 |  | EP | 0 | 55.5 | 55.5 | 2021-10-15 |  |  | FALSE
Supplemental | AEP | DP20R09C1 | s2663.1 | Extend a 0.37 mile double circuit 69 kV line to the new station location by tapping the existing Hancock-Walnut Ave 69 kV Circuit using 556 ACSR 26/7 overhead conductor | Customer Service |  |  |  | 2025-11-03 |  | EP | 0 | 2.8 | 2.8 | 2021-11-19 | Jonathan Wood/Robert Valerio |  | FALSE
Supplemental | AEP | DP20R09B0 | s2663.2 | Establish new 69 kV station (Winston Avenue) in a straight bus configuration with 2-69 kV circuit breakers, 69/12 kV, 25 MVA transformer with high-side circuit switcher and three 12 kV feeder breakers | Customer Service |  |  |  | 2024-10-14 |  | EP | 0 | 0 | 0 | 2021-11-19 | Jonathan Wood/Robert Valerio |  | FALSE
Supplemental | AEP | DP20R09B1 | s2663.3 | Update relay settings at Walnut Ave and Hancock stations. | Customer Service |  |  |  | 2024-10-25 |  | UC | 31 | 0.03 | 0.03 | 2021-11-19 | Jonathan Wood/Robert Valerio |  | FALSE
Supplemental | AEP | DP20R09B0 | s2663.4 | At Winston Ave install a second 69/12 kV, 25 MVA transformer with high-side circuit switcher and 12 kV feeders | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 0 | 0 | 2021-11-19 |  |  | FALSE
Supplemental | AEP |  | s2663.5 | At Roanoke install a second 138/12 kV Distribution transformer with high-side circuit switcher and 12 kV feeders. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 2 | 2 | 2021-11-19 |  |  | FALSE
Supplemental | AEP | DP20R09B1 | s2663.6 | Retire Distribution from Walnut Ave. Station. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 0 | 0 | 2021-11-19 |  |  | FALSE
Supplemental | AEP | A19036106, P21235001, P21235002 | s2664 | Hummel Creek – Marion 34.5 kV: Rebuild ~4.5 miles of 34.5 kV line with the conductor size 556.5 ACSR 26/7 Dove to 69 kV standards. The following cost includes the line rebuild, line removal and ROW. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-15 |  | EP | 0 | 11.3 | 11.3 | 2021-11-19 |  |  | FALSE
Supplemental | AEP | P19273001 | s2682.1 | Spy Run-Melita 69kV: Rebuild the Spy Run – McKinley 34.5kV line as the ~2.2 mile Spy Run – Melita 69kV line and retire the remaining 2.8 miles. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-08-01 |  | EP | 0 | 24.8 | 24.8 | 2022-01-21 | Katherine Vecchiarelli/Michael Van Schaik |  | FALSE
Supplemental | AEP | P19273007 | s2682.2 | Melita Station: Add a 69kV CB to Melita station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-08-01 |  | EP | 0 | 1.2 | 1.2 | 2022-01-21 | Joseph Smith/Michael Van Schaik |  | FALSE
Supplemental | AEP | A21111072 | s2682.3 | Fulton Station: Rebuild the through-path of Fulton 34.5/12kV station at 69kV and replace the transformer with a 69/12kV unit. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-31 |  | EP | 0 | 0.6 | 0.6 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  | FALSE
Supplemental | AEP | P20230005 | s2682.4 | Spy Run Station: Replace transformer #3 with a 138/69/34.5kV unit. Move the Fulton exit from 34.5kV to 69kV. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-04-22 |  | UC | 31 | 2.6 | 2.6 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  | FALSE
Supplemental | AEP | P19273008 | s2682.5 | McKinley Station: Retire CB “G” at McKinley station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-05 |  | EP | 0 | 0.2 | 0.2 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  | FALSE
Supplemental | AEP | P16024031 | s2682.6 | Wallen Station: Retire the 34.5kV voltage class equipment at Wallen station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-09-09 |  | EP | 0 | 0.2 | 0.2 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  | FALSE
Supplemental | AEP | P19153009 | s2682.7 | Industrial Park: Retire the entire 34.5kV voltage class, install a new 138/12kV load delivery to replace the 34.5/12kV delivery. Replace 69kV CB “G”, Replace the 138/69kV XFR 1 and add a high side switcher to XFR 1. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-31 |  | EP | 0 | 11.1 | 11.1 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  | FALSE
Supplemental | AEP | P19273005 | s2682.8 | Wallen-Industrial Park 34.5kV: Retire the ~3.3 mile Wallen – Industrial Park 34.5kV line. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-31 |  | EP | 0 | 2.9 | 2.9 | 2022-01-21 | Cole Fehrman/Sharlene Rivera-Gomez |  | FALSE
Supplemental | AEP | P20230006 | s2682.9 | Glenbrook Station: Retire Glenbrook 34.5/12kV substation | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-08-05 |  | EP | 0 | 0 | 0 | 2022-01-21 | Joseph Smith/Michael Van Schaik |  | FALSE
Supplemental | AEP | A20045021 | s2684 | North Blacksburg Station : Replace existing Transformer #1 with a 130 MVA 138/69-12 kV transformer. Replace existing Transformer #2 with a 25 MVA 138/12 kV transformer and add bus regulators. Add a 69kV circuit breaker on the low side of Transformer #1 | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-11-21 |  | EP | 0 | 4.06 | 4.06 | 2022-01-21 |  |  | FALSE
Supplemental | AEP | A19036102, P21238003, P21238004, P21238005 | s2685.1 | Robison Park – Sowers 138kV line: Rebuild the 13.6 miles of wood construction with double circuit capable 138kV with one side strung. Reconductor 4.3 miles of the steel lattice section with 795 Drake ACSR. This 4.3 mile section is already constructed as double circuit capable. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2028-05-04 |  | EP | 0 | 42.3 | 42.3 | 2022-01-21 |  |  | FALSE
Supplemental | AEP | P21238001, P21238002 | s2685.2 | Replace switches and risers at Grabill switch to accommodate the line rebuild. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2027-01-22 |  | EP | 0 | 1 | 1 | 2022-01-21 |  |  | FALSE
Supplemental | AEP | A19036075, P21086001, P21086002 | s2686 | Kenzie Creek 345/138/69kV station: Replace 138kV CB’s “F”, “F1”, “F2”, “G” and “G1” with 40 kA circuit breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-01-31 |  | EP | 0 | 1.8 | 1.8 | 2022-01-21 |  |  | FALSE
Supplemental | AEP | DP21A09D0 | s2688.1 | Install a new distribution station (“Pumpkin”) adjacent to the 69kV transmission through-path south of Barnesville. Retire Barnesville station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-08-27 |  | EP | 0 | 0.83 | 0.83 | 2022-01-21 | David Roudebush/antonio Lampkins |  | FALSE
Supplemental | AEP | DP21A09C0 | s2688.2 | Retire the 0.4-mile 69kV transmission line tap into Barnesville station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-08-28 |  | EP | 0 | 0.46 | 0.46 | 2022-01-21 | David Roudebush/antonio Lampkins |  | FALSE
Supplemental | AEP | DP21A09W0 | s2688.3 | Loop the Speidel-Summerfield 69kV transmission line into Pumpkin station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-08-27 |  | EP | 0 | 1.38 | 1.38 | 2022-01-21 | David Roudebush/antonio Lampkins |  | FALSE
Supplemental | AEP | A20705032 | s2693.1 | Rebuild approximately 4.5 miles of 46 kV line on the Cabin Creek – London 46 kV circuit (total length approximately 8 miles) in an area where there’s larger than standard ROW requirements due to long spans from ridge-ridge and more angle/dead ends required to mitigate landslide risk in rugged terrain. Long access roads due to terrain | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 17.7 | 17.7 | 2022-02-28 |  |  | FALSE
Supplemental | AEP | P20228007 | s2693.2 | Remove/retire existing Cabin Creek – London (4.5 miles). Helicopter removal will be utilized for existing line to avoid avoiding landslide prone areas | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 2.3 | 2.3 | 2022-02-28 |  |  | FALSE
Supplemental | AEP | P20228009 | s2693.3 | Retire the existing Hugheston Station | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 0 | 0 | 2022-02-28 |  |  | FALSE
Supplemental | AEP | P20228020 | s2693.4 | Rebuild London Station in the clear due to space constraints and access concerns. Install four 46 kV circuit breakers in a single bus configuration, DICM and appropriate metering equipment for the adjacent Hydro Plant. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 8.3 | 8.3 | 2022-02-28 |  |  | FALSE
Supplemental | AEP | P20228010 | s2693.5 | Rebuild approximately 1 mile of double circuit line from the existing London Hydro Station to the new London Station. Due to terrain dead-end structures will be used to construct this section of line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 5.4 | 5.4 | 2022-02-28 |  |  | FALSE
Supplemental | AEP | P20228012 | s2693.6 | Rebuild approximately 1 mile of single circuit line on the Carbondale – London 46 kV to accommodate the new London Station location | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 3.5 | 3.5 | 2022-02-28 |  |  | FALSE
Supplemental | AEP | A20045011 | s2694 | Cloverdale station: Replace 345/138 kV Transformer 11A & 11B with new 345/138 kV, 675 MVA Transformer 11 and reconnect to the 138 kV structure via a new 138 kV tie-line with 3 custom single-pole structures outside of the station in order to keep storage/driving space within the station. Install two new 345 kV 5000A 63 kA breakers to connect the new transformer and existing transformer 3 into a string position in the 345 kV yard. Replace all 69 kV hook-stick switches new 2000 A GOAB switches. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-31 |  | EP | 0 | 12.33 | 12.33 | 2022-02-09 |  |  | FALSE
Supplemental | AEP | P20019001 | s2748.1 | Install a new 3-way POP Switch (Boughtonville Sw) and 69 kV metering to address the hard tap to Firelands’ Boughtonville station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  | EP | 0 | 0.75 | 0.75 | 2022-03-18 |  |  | FALSE
Supplemental | AEP | P20019002 | s2748.2 | Install a new 3-way POP Switch (Lake Park Sw) and 69 kV metering to address the hard tap to Lake Park Industries. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  | EP | 0 | 0.76 | 0.76 | 2022-03-18 |  |  | FALSE
Supplemental | AEP | P20019003 | s2748.3 | Install a new 3-way POP Switch (Greenwich Sw) to address the hard tap to the Village of Greenwich’s Greenwich station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  | EP | 0 | 0.6 | 0.6 | 2022-03-18 |  |  | FALSE
Supplemental | AEP | P20019005 | s2748.4 | Remove North Greenwich Switch. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  | EP | 0 | 0.07 | 0.07 | 2022-03-18 |  |  | FALSE
Supplemental | AEP | J20019002 | s2748.5 | Construct ~ 10.4 miles of new 69 kV line between South Greenwich and ATSI’s New London delivery point using 556 ACSR conductor to give the existing radial line looped transmission service | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  | EP | 0 | 18 | 18 | 2022-03-18 |  |  | TRUE
Supplemental | AEP | P20019019 | s2748.6 | Install a box bay and two new 69 kV 3000A 40kA breaker at South Greenwich to accommodate the new line to New London (ATSI) | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  | EP | 0 | 3 | 3 | 2022-03-18 |  |  | TRUE
Supplemental | AEP | P20019022 | s2748.7 | Remove the existing 69kV bypass line at Willard station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-09-03 |  | EP | 0 | 0.32 | 0.32 | 2022-03-18 |  |  | FALSE
Supplemental | AEP | P20233007 | s2770.1 | Lazelle 69 kV Station: Replace 69kV circuit breakers 61 and 62 with 3000A 40kA breakers and associated equipment and relaying. | Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 0.62 | 0.62 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20233014 | s2770.2 | Sawmill 138kV Station: Replace 69kV circuit breaker B with 3000A 40kA breaker and associated controls | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 0.4 | 0.4 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20233015 | s2770.3 | Westerville 69kV Station: Replace 69kV circuit breakers 62 and 63 with 3000A 40kA breakers and associated equipment and relaying | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 0.44 | 0.44 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20233016 | s2770.4 | Genoa 138kV Station: Replace 69kV circuit breaker 64 with 3000A 40kA breaker | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 0.28 | 0.28 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20233019 | s2770.5 | Hyatt Telecom Site: Install Telecom site with CES SFP to communicate with Lazelle station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 0.04 | 0.04 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | A20705039 | s2771.1 | Retire the existing Bradley – Layland 69 kV line (approx. 14.3 miles) T | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 9.7 | 9.7 | 2022-04-22 |  |  | FALSE
Supplemental | AEP |  | s2771.2 | Construct a new double circuit 138 kV in/out line from the existing Bradley – Grandview 138 kV line (approx. 2.6 miles) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 8.3 | 8.3 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20229008 | s2771.3 | Prince Station: Retire existing station | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 0 | 0 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20229003, P20229004 | s2771.4 | Chessie Station: Install new 138 kV station including two 138 kV switches, circuit switcher and 138/12 kV 20 MVA XFR | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 0.3 | 0.3 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20229006 | s2771.5 | Grandview Station: Install a new 138/12 kV transformer to accommodate the retirement of Prince Station | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 2.2 | 2.2 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20229005 | s2771.6 | Bradley Station: Remove existing 69 kV breaker due to line retirement | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 0.1 | 0.1 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20229009 | s2771.7 | Layland Station: Remove existing 69 kV breaker due to line retirement | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 0.1 | 0.1 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | A19036079, P20177001, P20177002, P20177003 | s2772 | Rebuild the Pettit Ave – Melita 69kV 1.84 mile section on centerline utilizing 556.5 ACSR. Construction includes a high percentage of custom self-supporting running corners and dead ends due to line angles created by route adjustments. Constrained corridors are not suitable for guy wire installation. There are also an increased number of structures per mile due to configuration of existing underbuild and existing distribution service connections to residential and commercial customers along the existing line route. The line also passes through a heavily developed urban area of Fort Wayne, requiring new easements along the route and short span construction which all lead to higher than normal costs. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-13 |  | EP | 0 | 12 | 12 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20231008 | s2773.1 | East Lima – Columbus Grove Line: Rebuild 9.3 miles of the East Lima - Columbus Grove line between Columbus Grove and structure 38. Construct ~1 mile of greenfield 69 kV line between structure 38 and the existing Bluelick Sw. Rebuild 1.65 miles of the 34.5 kV line section between Bluelick and East Lima to 69 kV to provide looped service to the new 69 kV delivery at Bluelick. Retire 1.7 miles of the Columbus Grove – East Lima line from structure 38 into East Lima. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-08-27 |  | EP | 0 | 25.55 | 25.547 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20231017 | s2773.2 | Slabtown Switch: Install Slabtown SW with 1200A POP switches. Install Auto-sectionalizing on the through path. Upgrade Bluelick delivery point metering. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2028-12-14 |  | EP | 0 | 0.89 | 0.885 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20231007 | s2773.3 | Bluelick Switch: Retire 34.5 kV Bluelick SW | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-09-23 |  | EP | 0 | 0.05 | 0.054 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20231019 | s2773.4 | Cairo Switch: Replace Cairo switch with 1200A POP switches. Install SCADA control on the through-path | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-08-27 |  | EP | 0 | 0.71 | 0.706 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20231005 | s2773.5 | East Lima Station: Upgrade telecom equipment at East Lima station | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-11-01 |  | EP | 0 | 0.02 | 0.021 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20231020 | s2773.6 | Columbus Grove Station: In order to accommodate the line rebuild, work will be performed on the existing Columbus Grove switch. Install a box bay with two 69 kV, 1200A line witch automated MOABs, at Columbus Gove station | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2027-08-27 |  | EP | 0 | 1.14 | 1.141 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | DP21R01B0 | s2774.1 | Construct a greenfield station (Salmon) with a 138/12 kV 25 MVA transformer with high side circuit switcher. There will be two 12 kV feeders from the station. The 138 kV side will be a straight bus with two 138kV circuit breakers. | Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0 | 0 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | DP21R01B2 | s2774.2 | Tap the Broadford – Claypool Hill 138kV line and construct an in and out line to the greenfield Salmon station by building 2.3 miles of greenfield double circuit 138kV line. The higher estimated cost is due to environmental surveying and a large amount of new access roads required for this greenfield line that is in hilly terrain | Customer Service |  |  |  | 2026-06-30 |  | EP | 0 | 8.5 | 8.5 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | DP21R01C1 | s2774.3 | Build 4.1 miles of 96 ADSS Telecom underbuilt cable to connect Salmon station to the existing fiber network. | Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.8 | 0.8 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21209009 | s2775.1 | Rebuild the existing Belva – Clendenin 46 kV line to 138 kV standards (approximately 27 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-05 |  | EP | 0 | 85.6 | 85.6 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21209006 | s2775.2 | Belva Station: Replace existing Gr. Sw. MOAB with a new 138 kV 3000 A 40 kA CB. Install a new 138 kV 3000 A 40 kA CB on the Belva – Gilboa 138 kV line at Belva Station. Install 9.6 MVAR cap bank. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-09-01 |  | EP | 0 | 2.9 | 2.9 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21209007 | s2775.3 | Hartland Station: Replace existing MOABs W and Y with two new switches. Retire/Remove existing circuit switcher AA and cap bank. E | Equipment Material Condition, Performance and Risk |  |  |  | 2026-09-01 |  | EP | 0 | 0.7 | 0.7 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | A19036103, P21296003, P21296004, P21296005 | s2776 | Industrial Park – McKinley 138kV line: Rebuild the ~1 mile section that is double circuit with McKinley – Melita 69kV and rebuild the ~0.9 mile section that is double circuit with Melita – Hadley 69kV in place. The remaining ~1.3 miles will be rebuilt as single circuit. All new line conductor will be 795 Drake ACSR. The total rebuild length is 1.9 miles double circuit and 1.3 miles single circuit for a total of 3.2 miles. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-03 |  | EP | 0 | 9.3 | 9.3 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | A19036107, P21282001, P21282002 | s2777 | Robison Park – Wallen 69kV line: Reconductor the ~2.96 miles of 300,000 CU with 556.5 ACSR and replace 21 structures outlined in the need with steel monopole structures. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-13 |  | EP | 0 | 6.3 | 6.3 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21013006 | s2778.1 | Rebuild approximately 4.6 mile of the Newcomerstown- Cambridge 69kV line that wasn’t addressed under b3274 and b3345 utilizing 556 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 8.97 | 8.97 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21013010 | s2778.2 | Rebuild the 0.6 mile Leatherwood Sw- North Cambridge with double circuit 556 ACSR conductor to provide loop service to North Cambridge station. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 1.45 | 1.45 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21013018 | s2778.3 | Add line MOABs for each of the double circuit lines coming into North Cambridge station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 0.28 | 0.28 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21013013 | s2778.4 | Remove the Leatherwood Switch that currently radially serves North Cambridge station | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 0.08 | 0.08 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21013019 | s2778.5 | Replace Salt Fork Switch with a new 1200A POP Switch | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 1.13 | 1.13 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21009012 | s2779 | Fremont Center: Rebuild the existing 69 kV yard to a breaker and a half arrangement. Install 11 new 3000A 40kA 69kV breakers and relocate one existing breaker into the new strings | Equipment Material Condition, Performance and Risk |  |  |  | 2026-12-15 |  | EP | 0 | 10.35 | 10.35 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20255004 | s2780.1 | Rebuild the 15.7 mile 138kV line between Howard and Chatfield stations with new 1033 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-05-01 |  | EP | 0 | 39.96 | 39.96 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20255011 | s2780.2 | Rebuild the 6.1 mile 138kV line between Melmore and South Tiffin stations with new 1033 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-05-01 |  | EP | 0 | 14.97 | 14.97 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20255014 | s2780.3 | Rebuild the 11.7 mile 138kV line between South Tiffin and West End Fostoria stations with new 1033 ACSR conductor | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-05-01 |  | EP | 0 | 30.19 | 30.19 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P21088002 | s2781.3 | Brie 138kV Station: Establish the greenfield 138kV Brie station. Two full breaker and a half strings and 2 partial strings will be initially installed; total of ten (10) 138 kV breakers. | Customer Service |  |  |  | 2024-09-14 |  | UC | 75 | 11.04 | 11.04 | 2022-04-22 | Sydney Hunter/Nathen Roberts |  | FALSE
Supplemental | AEP | P21088003 | s2781.5 | Brie – Customer: Construct approximately 2 miles of two double circuit 138kV tie lines #1-4 to the customer's facility | Customer Service |  |  |  | 2025-02-11 |  | EP | 0 | 0.11 | 4.11 | 2023-08-18 | Sydney Hunter/Nathen Roberts |  | FALSE
Supplemental | AEP | P21237001 | s2784.1 | Merrick Switch – Atwood Switch: Rebuild the existing 8.8 mile 69kV line section between Merrick Switch and Atwood Switch, using 477 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 19.92 | 19.92 | 2022-05-19 |  |  | FALSE
Supplemental | AEP | P21237006 | s2784.2 | Zoarville – Merrick Switch: Build 7.0 mile greenfield 69kV line between Merrick Switch and Zoarville, using 477 ACSR conductor | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 16.47 | 16.47 | 2022-05-19 |  |  | FALSE
Supplemental | AEP | P21237002 | s2784.3 | Merrick Switch – East Dover: Retire 6.5 miles of 69 kV line between Merrick Switch and East Dover | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 1.84 | 1.84 | 2022-05-19 |  |  | FALSE
Supplemental | AEP | P21237004 | s2784.4 | East Dover: Remove 69kV breaker K and associated equipment. Connect the modified Carrollton 69kV circuit to breaker H; upgrade a small amount of risers at East Dover. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 0.34 | 0.34 | 2022-05-19 |  |  | FALSE
Supplemental | AEP | P21237008 | s2784.5 | Zoarville: Install 69kV switch and conductor to connect to new T-line entrance. Relay settings updates at Carrollton. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 0 | 0.14 | 0.14 | 2022-05-19 |  |  | FALSE
Supplemental | AEP | P21029001 | s2785.1 | Invision Switch: Install a new switch on the Ebersole – Findlay center 138 kV line to serve the new Buckeye Co-Op Cass Substation. | Customer Service |  |  |  | 2026-02-20 |  | UC | 50 | 1.49 | 1.49 | 2022-05-19 |  |  | FALSE
Supplemental | AEP | P21029006 | s2785.2 | Invision – Cass: Install approximately 0.1 miles of new 138 kV line from Invision Switch to the Buckeye Co-op Cass Substation. | Customer Service |  |  |  | 2026-02-20 |  | UC | 50 | 0.6 | 0.595 | 2022-05-19 |  |  | FALSE
Supplemental | AEP | P22024006 | s2787.1 | RV Capital 138 kV - Install a new 138kV straight bus with a (2) 138kV MOAB switches, fiber and relaying. | Customer Service |  |  |  | 2025-01-03 |  | EP | 0 | 1.96 | 1.96 | 2022-04-22 | Matthew Van Volkenburg/Joshua Smith |  | FALSE
Supplemental | AEP | DP21C23D2 | s2789.1 | Scherers Switch 138kV: Install a new 2000 A three-way Phase Over Phase switch with SCADA automation on the Huntley – Greif through path and install a bypass for maintenance. | Customer Service |  |  |  | 2024-11-08 |  | UC | 75 | 0.8 | 0.8 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | DP21C23D4 | s2789.2 | Greif – Huntley 138kV line: Tap the existing Greif-Huntley 138kV circuit by installing structures to carry the 69 kV underbuild Lazelle-Busch circuit and maintain separation from the new Scherers Switch as well as install dead end poles and centerline poles on each direction of the new switch | Customer Service |  |  |  | 2024-11-03 |  | UC | 75 | 1.11 | 1.113 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | DP21C23C0 | s2789.3 | Cologix Extension 138kV: Construct ~0.24 miles of single circuit 138kV radial transmission line from Scherers Switch to the new Cologix Customer Station. | Customer Service |  |  |  | 2024-11-08 |  | UC | 75 | 0.8 | 0.795 | 2022-04-22 |  |  | FALSE
Supplemental | AEP | P20022001 | s2791.1 | West Watertown Station, 138 kV: Construct a greenfield 138/69 kV West Watertown station off the existing Corner – Wolf Creek 138 kV circuit. Install four-138 kV 3000 A 40 kA breakers configured in a ring arrangement. Install 90 MVA 138/69/13.09 kV transformer along with a 3000A 40 kA 69 kV low side breaker towards WEC’s Bartlett delivery. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 8.8 | 8.8 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022008 | s2791.2 | Wolf Creek – Corner 138 kV Line cut-in: Cut-in on the line to install the new West Watertown station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.55 | 0.55 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022011 | s2791.3 | West Watertown – Watertown (WEC) 138 kV circuit: Construct approximately 4.3 miles of single circuit 138 kV line between the newly proposed West Watertown station and WEC’s new 138 kV delivery at Watertown. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 9.32 | 9.32 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022013 | s2791.4 | West Watertown – Patten Mills 69 kV circuit : Construct approximately 5.8 miles of single circuit 69 kV line between the newly proposed West Watertown station and a proposed phase over phase switch (Patten Mills Switch) near WEC’s delivery at Bartlett. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 11.81 | 11.81 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022002 | s2791.5 | Patten Mills Switch, 69 kV: Install a new 69 kV 2000A phase over phase (Patten Mills switch) to serve the Bartlett delivery point. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.9 | 0.9 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022014 | s2791.6 | South Stockport - Washington Co-op 69 kV Line cut-in : Cut-in on the line to install the new Patten Mills Switch. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.65 | 0.65 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022016 | s2791.7 | Muskingum River - South Rokeby 69 kV Line Removal : Retire ~9 miles of existing 69 kV line between Grace and Muskingum River stations. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 4.1 | 4.1 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022005 | s2791.8 | Muskingum River Removals: At Muskingum River 138 kV yard, retire the 138/69 kV XF #C, CB-HM & HW. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.63 | 0.63 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022019 | s2791.9 | Grace Station, 69 kV: Retire Grace - Muskingum River circuit, upgrade protection and fiber work at Grace Station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.91 | 0.91 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022017 | s2791.10 | Grace – Watertown Fiber: Install fiber between Grace and Watertown stations. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.55 | 0.55 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022007 | s2791.11 | Wolf Creek & Corner Stations Protection upgrades: Remote end protection upgrade | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.65 | 0.65 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20022003 | s2791.12 | Watertown (WEC) Metering: Install 12 kV revenue metering at WEC’s new Watertown station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-09-01 |  | EP | 0 | 0.03 | 0.026 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21710001 | s2792.1 | Eliminate the Moreland area 69kV hard tap and install a new 3-way, motor-operated switch with SCADA functionality (“Rufener Switch”). | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-07-25 |  | EP | 0 | 0.6 | 0.6 | 2022-06-15 | Parker Joyner/? |  | FALSE
Supplemental | AEP | P21710003 | s2792.2 | Modify the Beartown-Moreland 69kV through-path T-line and ROW, in order to install the new switch structure. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-07-25 |  | EP | 0 | 0.6 | 0.6 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21710005 | s2792.3 | Modify the Rufener – Co-op 69kV radial T-line and ROW, in order to install the new switch structure. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2024-07-25 |  | EP | 0 | 0.3 | 0.3 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20168022 | s2793.1 | West Van Wert – Ohio City: Rebuild the 8.9 mile West Van Wert – Ohio City 34.5 kV circuit to operate at 69 kV utilizing 556 ACSR conductor. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 12.27 | 12.271 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20168012 | s2793.2 | West Van Wert 69kV: In order to address the three terminal point created by closing in the interconnection at Rockford and address existing dissimilar zones of protection, 4 new 3000A, 40kA breakers will be installed at West Van Wert station in a ring configuration. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 5.5 | 5.503 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20168023 | s2793.3 | Haviland – West Van Wert: Relocate Haviland – West Van Wert 69kV to accommodate work at West Van Wert station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 1.04 | 1.035 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20168023 | s2793.4 | West Van Wert – South Van Wert: Relocate West Van Wert –South Van Wert to accommodate work at West Van Wert station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 1.17 | 1.174 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20168020 | s2793.5 | Roller Creek 69kV: Install new 69/12 kV Roller Creek station to replace Ohio City 34.5/12 kV station. Install a box bay with a 1200A 69kV auto-sectionalizing MOAB and a 3000A,40kA 69kV breaker on the West Van Wert- Rockford through path. Install 69kV metering | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 1.64 | 1.641 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20168011 | s2793.6 | West Ohio City Switch 34kV: Retire Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 0.04 | 0.039 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20168010 | s2793.7 | Southwest Van Wert Switch 34kV: Retire Switch | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 0.09 | 0.088 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21304001 | s2794.1 | Mount Perry Switch, 138 kV: Install a new 3-way POP MOAB switch (Mount Perry Switch) tapping the Crooksville – North Newark 138kV circuit to SCP’s new Mount Perry Station. | Customer Service |  |  |  | 2024-07-19 |  | EP | 0 | 0.97 | 0.966 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21304008 | s2794.2 | Mount Perry Extension, 138 kV: Construct approximately 0.08 miles of greenfield 138kV transmission line from the greenfield 3-way POP MOAB switch to SCP’s new Mount Perry Station. | Customer Service |  |  |  | 2024-07-19 |  | EP | 0 | 0.74 | 0.737 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21304002 | s2794.3 | Mount Perry Meter, 12 kV: Install 12 kV metering at SCP’s new Mount Perry Station. | Customer Service |  |  |  | 2024-07-19 |  | EP | 0 | 0.02 | 0.023 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21304006 | s2794.4 | Crooksville – North Newark 138 kV line: Perform work to cut-in the Crooksville – North Newark 138 kV line to install the new POP MOAB switch. | Customer Service |  |  |  | 2024-07-19 |  | EP | 0 | 0.16 | 0.162 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21304004 | s2794.5 | Crooksville Protection upgrades: Remote end protection upgrade | Customer Service |  |  |  | 2024-07-19 |  | EP | 0 | 0.55 | 0.551 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21075001 | s2795.1 | Rebuild approximately 4 miles of line from Layland – Mollys Creek (Str. 1183-229) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  | EP | 0 | 13.8 | 13.8 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21075012 | s2795.2 | Install a new 138 kV PoP switch on the Bradley – Mollys Creek 138 kV line and associated line work on the existing Bradley – Mollys Creek 138 kV line to accommodate switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  | EP | 0 | 1.9 | 1.9 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21075009 | s2795.3 | Construct a new 138 kV extension from the new 138 kV PoP Switch to the existing Claremont Station (to be renamed Dun Glen) approximately 0.6 mi | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  | EP | 0 | 2 | 2 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21075013 | s2795.4 | Convert existing Claremont Station from 69 kV to 138 kV. Station to be renamed Dun Glen. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  | EP | 0 | 0 | 0 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | A20705041 | s2795.5 | Retire existing Claremont – Mollys Creek 69 kV line (approximately 3.1 miles) Retire existing Thurmond S.S. – Brooklyn S.S. 69 kV line (approx. 3.2 miles) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  | EP | 0 | 7.6 | 7.6 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21075008 | s2795.6 | Install two new 138 kV breakers at Mollys Creek Station | Equipment Material Condition, Performance and Risk |  |  |  | 2025-09-01 |  | EP | 0 | 1.5 | 1.5 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | A19036105, P21236012, P21236013, P21236024 | s2796.1 | Derby – Hickory Creek 69kV Line:Rebuild the remaining ~6.2 miles of the Derby – Hickory Creek 69kV line utilizing 795 ACSR which will match the ~2.5 miles built in 2013 | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 14.7 | 14.7 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | A19036109 | s2796.2 | Derby – Hickory Creek 34.5kV Line: Retire the ~6.16 mile Derby – Hickory Creek 34.5kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 1.2 | 1.2 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | A19036111 | s2796.3 | Bendix Lakeshore 34.5kV Tap: Retire the ~1.73 mile Bendix Lakeshore 34.5kV Tap | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 0.6 | 0.6 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21236006, P21236020 | s2796.4 | Hawthorne SS 69kV /Bendix Sw 34.5kV: Remove the switch from Bendix Sw and re-use it at Hawthorne SS | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 0.7 | 0.7 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21236004, P21236005 | s2796.5 | Stevensville 69kV: Rework the through-path to accommodate the new line entrances. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 0.6 | 0.6 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21236001, P21236002, P21236003 | s2796.6 | Trafalgar 69/34kV: Install Trafalgar station to serve the Bendix 34.5kV customer. This station will include a new 69kV switcher and a new 69/34.5kV XFR. Two CB’s will be reused from Derby and Hickory Creek. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 4.7 | 4.7 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21236008 | s2796.7 | Scottdale 69kV: Re-energize to 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 0 | 0 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21236019 | s2796.8 | Derby 138/69/34.5kV: Retire the 34.5kV voltage class | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 0.1 | 0.1 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21236016 | s2796.9 | Boxer – Blossom Trail 34.5: Re-energize at 34.5kV | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 0.2 | 0.2 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21236017 | s2796.10 | Boxer – Hickory Cr 69kV: Re-energize at 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 0.8 | 0.8 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21236018 | s2796.11 | Trafalgar – Bendix 34.5kV: Build a 0.15 mile radial line from Trafalgar to Bendix Lakeshore | Equipment Material Condition, Performance and Risk |  |  |  | 2029-04-11 |  | EP | 0 | 0.5 | 0.5 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | A19036113, P21728001, P21728002, P21728008 | s2797.1 | Pendleton – Makahoy 138 kV: Rebuild ~15 miles of 138 kV line with the conductor size 795 ACSR. The following cost includes the line rebuild, line removal and ROW. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-04-09 |  | EP | 0 | 27.2 | 27.2 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P21728003, P21728004 | s2797.2 | Pendelton: Replace the Pendleton 138/34.5 kV transformer with a 138/34.5 kV 75 MVA transformer. The following cost includes the transformer install and removal. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-28 |  | EP | 0 | 1.2 | 1.2 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20241001, P20241002, P20241003 | s2798 | McGalliard Road replace 34.5 kV Moab switches “A” and “B” with 2000 A switches and install a 2000 A bus tie switch for operational and transformer maintenance flexibility | Equipment Material Condition, Performance and Risk |  |  |  | 2024-11-14 |  | EP | 0 | 0.4 | 0.4 | 2022-06-15 |  |  | FALSE
Supplemental | AEP | P20269005 | s2801.1 | Lockwood Rd 138kV:Retire the existing box bay and breaker bypass switch. Install two 138 kV 40 kA breakers in coordination with an active IPP AF1-063 project that will be installing an additional two breakers in a ring bus arrangement at the station. Install a DICM. Install a new 23MVAR capacitor bank with breaker. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-11-15 |  | EP | 0 | 3.71 | 3.713 | 2022-07-22 | Aaron Fahey/Jerod Marker |  | FALSE
Supplemental | AEP | P20269014 | s2801.2 | Sowers – Lockwood Rd – Richlands 138 kV: Relocate Lockwood Road – Sowers and Lockwood Road – Richland lines line to accommodate work at Lockwood Road station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-11-15 |  | EP | 0 | 1.18 | 1.178 | 2022-07-22 | Karmyn Wilford/Jerod Marker |  | FALSE
Supplemental | AEP | P20269012 | s2801.3 | Lockwood Rd – City of Bryan 138 kV: Relocate Lockwood Road- City of Bryan line to accommodate work at Lockwood Road station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2027-11-15 |  | EP | 0 | 0.69 | 0.693 | 2022-07-22 | Aaron Fahey/Jerod Marker |  | FALSE
Supplemental | AEP | P21309001 | s2802.1 | Crooksville Station, 69 kV: Replace 69 kV oil filled FK type breaker CB-W with a 3000A, 40 kA breaker . | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  | EP | 0 | 0.67 | 0.67 | 2022-07-22 |  |  | FALSE
Supplemental | AEP | P21309002 | s2802.2 | South Fultonham, 69 kV: Retire CB-B. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  | EP | 0 | 0.09 | 0.09 | 2022-07-22 |  |  | FALSE
Supplemental | AEP | P21309003 | s2802.3 | Saltillo Switch, 69 kV: Retire Saltillo Switch | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  | EP | 0 | 0.05 | 0.05 | 2022-07-22 |  |  | FALSE
Supplemental | AEP | P21309005 | s2802.4 | Crooksville – South Fultonham 69 kV line: Rebuild approximately 7.4 miles of single circuit 69 kV line between the Crooksville and South Fultonham stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  | EP | 0 | 12.47 | 12.47 | 2022-07-22 |  |  | FALSE
Supplemental | AEP | P21309007 | s2802.5 | Crooksville – Somerset 69 kV line: Rebuild approximately 8.8 miles of single circuit and 1.6 miles of double circuit 69 kV line between the Crooksville and Somerset stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  | EP | 0 | 19.92 | 19.92 | 2022-07-22 |  |  | FALSE
Supplemental | AEP | P21309009 | s2802.6 | South Fultonham – Mount Sterling 69 kV line: Rebuild approximately 7.2 miles of single circuit 69 kV line between the South Fultonham and Mount Sterling stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  | EP | 0 | 13.88 | 13.88 | 2022-07-22 |  |  | FALSE
Supplemental | AEP | P21309013 | s2802.7 | South Fultonham – Saltillo 69 kV line: Retire approximately 5.9 miles of single circuit 69 kV line between the South Fultonham station and Saltillo Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-02 |  | EP | 0 | 3.22 | 3.22 | 2022-07-22 |  |  | FALSE
Supplemental | AEP | P21761004 | s2807.2 | Modify AEP’s proposed Alpine 69 kV ring bus station (s2534.8) by adding an additional 69 kV circuit position to Brewster. Install one (1) 69 kV circuit breaker, protective relaying, and tie-line metering. Construct a 0.1 mile segment of 69 kV transmission line using 795 ACSR 26/7 conductor leaving Alpine station to connect to AMPT’s transmission line toward Brewster. | Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 1.81 | 1.81 | 2022-08-19 |  |  | TRUE
Supplemental | AEP | P22026001, P22026002 | s2810 | Replace 138kV circuit breakers A, B, and C with 3000A 40kA breakers at Edison station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  | EP | 0 | 1.18 | 1.18 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P20896004 | s2811 | Fremont: Install a new 69 kV 3000A 40kA breaker to replace breaker C and associated terminal equipment at Fremont on the line towards the City of Clyde. Install a new 138kV 1200A MOAB switch to replace MOAB W toward West Fremont. Install new DICM. Station will need to be expanded to accomplish work. | Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 3.48 | 3.48 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21273003 | s2812.1 | Fostoria - East Lima 138: The 41.3 mile long line will be rebuilt using double circuit 795 ACSR Drake conductor. OPGW shield wire will be installed. Approximately one mile of line is being considered for greenfield construction to avoid encroachments and ROW challenges. The Boutwell, Flag City and Ebersole stations were installed recently, these line cut-ins will not be rebuilt. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-09-15 |  | EP | 0 | 95.9 | 95.9 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21273031 | s2812.2 | North Findlay - N Main & North Findlay - Findlay 69kV lines: The North Findlay - N Main and North Findlay - Findlay 69kV lines will be modified for the Fostoria - East Lima 138kV line crossing | Equipment Material Condition, Performance and Risk |  |  |  | 2026-09-15 |  | EP | 0 | 0.08 | 0.08 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21753002 | s2813.1 | At Dewey substation: Replace 138kV CB B towards Thelma with new 138kV 40kA circuit breaker. Provide new DICM with new relays for all equipment at station so that existing control house can be removed. Upgrade station service. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  | EP | 0 | 2.4 | 2.4 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21753006 | s2813.2 | At Dewey substation: Provide Transition fiber via underground from the existing Control House to the new DICM at Dewey Station. Retire existing fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  | EP | 0 | 0.18 | 0.18 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21753004 | s2813.3 | At Thelma substation, Remote end relaying to replace line protection for Breaker A towards (Dewey) to match upgrade at Dewey Station. Provide MOS on existing 138kV HS of transformer XF #1 & #3 to provide additional control to stability system | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  | EP | 0 | 0.4 | 0.4 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | A20705082 | s2814.1 | Bellefonte: Replace XFR #2 with a 200MVA Auto unit and retire XFR #1 & #5. The U/G feeder for XFR #3 69kV riser is getting reconductored under B3349. Reconductor sections of 138kV Bus #1 and 138kV Bus #2. Replace remaining oil PTs connected to Bus #1 and Bus #2. Upgrade Primary and back up station service. Replace 69kV bus tie breaker H. Replace the hook stick disconnects switches for the tie breaker H and 69kV tie breaker location will be relocated one bay south of the existing location and 69kV buses will be reconfigured. Replace the hook stick disconnects switches for Raceland breaker D. Relocate the Raceland feeder to bus #1 after extending the 69kV bus #1. The cap bank switcher/moab Mark 5 combo unit will get replaced with 69kV breaker and set of breaker disconnects and relocated to bus #1. 69kV breaker is needed instead of circuit switcher due to the high fault current. Relocate the cap bank to bus #1 after extending the 69kV bus #1. 69kV Air Products line MOABs will be replaced with 2000A SW. Replace hook-stick switches for Oil CB – AB, JJ, I, G, Z, T and C. These Breakers are replaced as part of B3350. Install 16'x48' DICM for 69kV Yard and a 16'x48' DICM for the 138kV Yard. Replace cable trench, single phase AC system & cable work, entire fence replacement and ground grid extension for 100'X10' expansion toward the Northwest of the 69kV yard. Both 138kV and 69kV control house will be retired. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  | EP | 0 | 12.59 | 12.59 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | A20705083 | s2814.2 | The customer served out of 34.5 kV Yard has plans for demolition of their facilities. Retire entire 34kV Yard, contingent on the timing of the customer being removed from service. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  | EP | 0 | 2.67 | 2.67 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21720006 | s2814.3 | Retirement of the Bellefonte 34.5kV Bus Tie Line that connects the Bellefonte 138kV Station to the Bellefonte 34kV Station. This removal involves removing 3- Double Circuit Lattice Towers, 1-Triple Circuit Lattice Towers, and 1 Single Wood Pole Structure. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  | EP | 0 | 0.46 | 0.46 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21720008 | s2814.4 | Retire the existing Bellefonte – Armco 34.5kV operated line. The major removal work involves removing 4 lattice steel towers, 1 H-Frame wood structure, and 2 single wood poles. The line being removed is approximately 0.55 miles long. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 1 | 1 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21720007 | s2814.5 | Remote end relaying at Raceland substation to install 2 new CCVTs on a custom two-phase single column stand for the Bellefonte 69kV line exit. The existing CCVT mounted on a single phase CCVT stand will be reused and will remain as it is. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-12-01 |  | EP | 0 | 0.37 | 0.37 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | A20705082 | s2814.6 | Provide 0.2 miles of fiber from Distribution structures outside the station to the new DICMs. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 0.49 | 0.49 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21205002 | s2815.1 | At Hatfield Substation, expand the substation yard. Relocate 138/69/46kV XF#1. Replace 138/69/46kV XF#1 Bushings, 138kV 3 phase Bus CCVTs, MOAB X1 and GND Switch Z1 with a new 138kV Circuit Switcher. Replace 138KV Sprigg Line metering, Line Switch "11" with a 138kV Circuit Breaker. Replace and relocate 69kV CB-B to standard Bay position. Replace 69KV CB-A and add 3 phase CCVTs to John's Creek 69kV line. Add 138kV Backup and 69kV Primary Station Service transformers and Station Service. Expand yard and install a 16' X 27' base DICM. Remove 111MVA 46/7.2KV Transformer #2 and associated equipment and 7.2KV 3 phase station service. Remove the control building. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-08-01 |  | EP | 0 | 4.95 | 4.95 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21205003 | s2815.2 | On the Leslie No.1 – Hatfield 69kV circuit, remove existing guyed dead-end structure K357-29 and install a new single pole, single circuit, custom dead-end to remove the guy wires conflicting with station footprint plans. The existing guy anchors would conflict with station expansion plans, and it is not feasible to span guy over top of proposed control house as the anchors would land in the proposed station drive path. The proposed custom dead-end structure will be placed 20' downhill from existing structure K357-29. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-30 |  | EP | 0 | 0.5 | 0.5 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | DP21H07B1 | s2816.1 | Construct a new greenfield station (Holden) with a 138/12 kV 25 MVA transformer and high side circuit switcher. There will be two 12 kV feeders from the station. The 138 kV side will be a straight bus with one 138kV circuit breaker facing Ragland and one 138kV MOAB switch facing Tin Branch. The intent of the greenfield station is to support the business ready site and the 138kV circuit breaker will provide added protection for sensitive industrial customers. The existing Pine Creek station will be retired. | Customer Service |  |  |  | 2026-10-06 |  | EP | 0 | 0 | 0 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | DP21H07C0 | s2816.2 | Tap the Logan – Sprigg #2 138kV line and build 3.5 miles of greenfield double circuit 138kV line to serve Holden station. The higher estimated cost is due to a large amount of new access roads and environmental studies that are required for this greenfield line that will be built through mountainous terrain. | Customer Service |  |  |  | 2026-10-06 |  | EP | 0 | 12.18 | 12.18 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | DP21H07C4 | s2816.3 | Build 0.6 miles of 96 ADSS Telecom underbuilt cable to connect Holden station to the existing fiber network. | Customer Service |  |  |  | 2026-10-06 |  | EP | 0 | 0.18 | 0.18 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | DP21H07C3 | s2816.4 | Remove 1.85 mile long Pine Creek 138kV Tap | Customer Service |  |  |  | 2026-10-06 |  | EP | 0 | 1.74 | 1.74 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21574006 | s2817.1 | Rebuild the Midway – South Christiansburg 69kV line from Midway station to Str. 466-9 (0.45 miles). Rebuild the Midway – South Christiansburg 69kV line from Str. 466-28B to Str. 466-98 (3.8 miles). At Str. 466-98 build new 69kV line to the existing Tech Drive station (0.35 miles). The cost per mile is due to the need for matted access roads to minimize property damage in the urban environment. 50 permanent encroachments have been identified within the existing ROW and require a greater number of line structures than normal to reroute the line. Also, due to numerous encroachments on the existing centerline, the rebuild will consist of 1.8 miles rebuilt on existing centerline and 2.8 miles near centerline or greenfield. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 21.33 | 21.33 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21574010 | s2817.2 | Remove the Midway – South Christiansburg 69kV circuit from Midway station to Str. 466-9 (0.45 miles). Remove the Midway – South Christiansburg 69kV circuit from Str. 466-28B to Str. 466-98 (3.4 miles). Retire the Midway – South Christiansburg 69kV circuit from South Christiansburg station to Str. 466-98 (0.7 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 2.7 | 2.7 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | A20045072 | s2817.3 | At South Christiansburg station, remove the existing 138/69kV transformer and 69kV circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 1.29 | 1.29 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21574009 | s2817.4 | Build 4 fiber station transitions using OPGW at Midway, Hans Meadow, Tech Drive and South Christiansburg. Retire 4.3 miles of ADSS fiber currently on the Midway – South Christiansburg 69kV circuit. Build 4.6 miles of OPGW on the new Midway - Tech Drive 69kV Line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 1.03 | 1.03 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21574001 | s2817.5 | At Hans Meadow station, replace the MOAB switch facing Cambria station with a 69kV circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0 | 0 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21574002 | s2817.6 | At Cambria station, replace existing 69kV line CCVTs, bus conductors, and pass-through riser connectors on both line exits to match the 69kV line capacity. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0 | 0 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21574003 | s2817.7 | At Midway station, replace existing risers to support the 69kV line rebuild. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0 | 0 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P21574004 | s2817.8 | At Tech Drive station, replace the manual switch facing South Christiansburg station with a 138kV circuit breaker and remove the 138kV bus tie switch. Install a 138kV circuit switcher and a 90 MVA 138/69 kV transformer. Add a 69kV circuit breaker to the 69kV side of the transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0 | 0 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P22725002 | s2818.1 | Add two additional 138kV circuit breakers to the already proposed and approved Tin Branch station (b3348), transforming the designed station from a 138kV two-breaker straight station to a four-breaker ring bus station. | Operational Flexibility and Efficiency |  |  |  | 2027-03-01 |  | EP | 0 | 1.9 | 1.9 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P22725012 | s2818.2 | Disconnect the Chauncey hard tap from the Logan – Sprigg circuit and build 1.5 miles of greenfield 138kV line to connect the Chauncey 138kV Tap into the new Tin Branch station. The higher estimated cost is due to the difficult mountainous terrain, expensive access roads and required environmental studies. | Operational Flexibility and Efficiency |  |  |  | 2027-03-01 |  | EP | 0 | 5.6 | 5.6 | 2022-08-19 |  |  | FALSE
Supplemental | AEP | P19302001 | s2819.1 | Rebuild existing Apple Grove – Point Pleasant 69 kV line to 138 kV standards. (approx. 17.3 miles) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-04-01 |  | EP | 0 | 50.3 | 50.3 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P19302006 | s2819.2 | Apple Grove Station: Replace existing 69 kV CB-L with a new 69 kV 3000 A 40 kA CB. Replace existing 138/69 kV XFR #1 with a new 138/69 kV 90 MVA XFR and install new high side circuit switcher. Add 138 kV CB on 138 kV bus increasing sectionalizing, by separating existing customer facilities from AEP facilities. Upgrade metering at station. Install new DICM. Replace existing 69/12 kV XFR #2 with a new 138/12 kV XFR. E | Equipment Material Condition, Performance and Risk |  |  |  | 2025-04-01 |  | EP | 0 | 6.7 | 6.7 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21572003 | s2820.1 | Rebuild the “Philo-Torrey” 138kV transmission line between West Dover and South Canton stations (18.0 miles). The circuit affected is South Canton-West Dover 138kV. Remove the existing lattice towers and supplement the right-of-way as needed. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-12-01 |  | EP | 0 | 46.74 | 46.74 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21572007 | s2820.2 | Rebuild the “Philo-Canton” 138kV transmission line between North Intertie and South Canton (14.6 miles). The circuit affected is North Intertie-South Canton 138kV. Remove the existing lattice towers and supplemental the right-of-way as needed. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-12-01 |  | EP | 0 | 42.84 | 42.84 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | A19036082, P21730001, P21730002, P21730003 | s2821 | Kalamazoo – Vicksburg 69kV line: Rebuild the 4.72 Kalamazoo – Vicksburg #1 69kV line with 336 30/7 ACSR Oriole and eliminate line crossings with Kalamazoo – Vicksburg #2 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-11-02 |  | EP | 0 | 8.45 | 8.45 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21558002 | s2822.1 | Rebuild Gambrinus station as Nolan station approximately 0.2 miles away as a 4-breaker 69kV ring bus. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-12-01 |  | EP | 0 | 7.07 | 7.07 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21558001 | s2822.2 | Retire Gambrinus station and remove all equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  | EP | 0 | 1.04 | 1.04 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21558006 | s2822.3 | Extend the Gambrinus-Reedurban and Gambrinus-Torrey 69kV transmission lines 0.2 mile northward, to connect to Nolan station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  | EP | 0 | 1.36 | 1.36 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21558012 | s2822.4 | From Nolan station, construct a span of 69kV transmission line and a structure, for each of the two feeds to the customer. This will connect to the customer’s 69kV loop. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  | EP | 0 | 0.67 | 0.67 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21558009 | s2822.5 | At the 69kV remote-end of Torrey, upgrade line relays to coordinate with Nolan station | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  | EP | 0 | 0.47 | 0.47 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21558008 | s2822.6 | At the 69kV remote-end of Reedurban, upgrade line relays to coordinate with Nolan and also replace the 69kV oil-filled breaker “R”. Convert the 69kV pilot wire system to fiber. Eliminate the 138kV 3-terminal configuration by installing 2- 138kV breakers on the incoming 138kV circuits. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  | EP | 0 | 3.61 | 3.61 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21558011 | s2822.7 | At Reedurban station, reconfigure the South Canton-Reedurban-Miles Avenue 138kV transmission line going into the station, to connect to the new breakers and bus. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  | EP | 0 | 0.66 | 0.66 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P21558021 | s2822.8 | At Reedurban station, replace and relocate a structure on the Nolan 69kV transmission line, to accommodate the station improvements and distribution scope. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-12-01 |  | EP | 0 | 0.33 | 0.33 | 2022-09-16 |  |  | FALSE
Supplemental | AEP | P22038005 | s2827.2 | At AEP’s East Leipsic station extend the 69kV bus and install a new 69kV breaker. Install 69kV To/To Metering. The station will need expanded to accommodate the work. Construct a new greenfield 0.55 miles long 69kV single circuit line using 556 ACSR Dove from the new East Leipsic 69kV breaker to the AEP / AMPT POI. Modify the East Leipsic Extension line. Modify the Yellow Creek - East Leipsic 69kV line. | Customer Service |  |  |  | 2025-08-01 |  | EP | 0 | 8.01 | 8.01 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21252001 | s2829.1 | Wagenhals Station: Construct a new Wagenhals 138-69kV station on greenfield property owned by AEP to the south of the existing station. The 138kV portion will be a breaker-and-a-half design, with a total of 17 breakers. The 69kV will be a 5-breaker ring bus. The existing 138-69kV transformer #3 and 138kV cap bank will be transferred, while the 138-69-23kV transformer #2 will be retired. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 27.45 | 27.45 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21252006 | s2829.2 | Retire the existing 138-69-23kV station, including structures and control house. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 3.71 | 3.71 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21252007 | s2829.3 | Relocate 8- 138kV transmission lines and 4- 69kV transmission lines to connect to the new station location. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 10.48 | 10.48 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21252028 | s2829.4 | Required environmental remediation at the existing station property. Dispose of PCB-contaminated soils, drainage tile, legacy oil piping and storage tanks, and synchronous condenser system. Final abatement plan to be determined with EPA. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 23.51 | 23.51 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21252021 | s2829.5 | Wayview: Remote-end 138kV relay upgrades. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 0.36 | 0.36 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21252022 | s2829.6 | Sunnyside: Remote-end 69kV relay upgrades. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 1.02 | 1.02 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21252023 | s2829.7 | Stanley Court: Remote-end 69kV relay upgrades. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-06-01 |  | EP | 0 | 0.49 | 0.49 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | A19036120, P21005009, P21005010, P21005020 | s2830.1 | Richland – Ummel/Tri Lakes 69kV line: Rebuild the ~8.7 mile line using double circuit 138kV construction and 795 ACSR Drake construction but energize only one side at 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-03 |  | EP | 0 | 17.1 | 17.1 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21005015, P21005016, A19036114 | s2830.2 | Rebuild the Albion – Kendallville 138kV: Rebuild the ~8.5 mile Albion – Kendallville 138kV circuit using 795 ACSR Drake | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  | EP | 0 | 15.8 | 15.8 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21005011, P21005012 | s2830.3 | Wolf Lake 69kV Tap: Rebuild the ~5.5 mile Wolf Lake tap as double circuit 138kV using 795 ACSR Drake. This line will be energized at 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  | EP | 0 | 13.6 | 13.6 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | A19036068, P21005001, P21005002 | s2830.4 | Albion 138/69kV: Replace 138kV CB “F” and cap switcher “BB”. In addition to this, this station had significant ancillary work needed including foundation repairs, new control cable runs and DICM installation. Construction at this station will be aligned with B3248 | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-30 |  | EP | 0 | 4.6 | 4.6 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21005005, P21005018 | s2830.5 | Kuhns / Albion REMC 69kV: Reconnect Kuhns Sw to serve the currently hard tapped Albion REMC load | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  | EP | 0 | 0.6 | 0.6 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21005014 | s2830.6 | Albion REMC 69kV Radial Tap: Reterminate the line into Kuhns Sw 69kV | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  | EP | 0 | 0.2 | 0.2 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | A19036114, P21005013, P21005015, P21005016 | s2830.7 | Albion – Kendallville 69kV Line: Reterminate the line into Kuhns Sw 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  | EP | 0 | 0.8 | 0.8 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21005007, P21005008, A19036065 | s2830.8 | Kendallville 138/69kV: Replace the 138/69kV transformer with a 90MVA unit. This work will be aligned with S2431. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  | EP | 0 | 2.2 | 2.2 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P21005003, P21005004 | s2830.9 | Onion Bottom Bog Sw/Wolf Lake 69kV: Install a 69kV POP “Onion Bottom Bog” Switch to serve Wolf Lake station. This switch will be re-used from the “Whitford Sw” that was removed with S2431 | Equipment Material Condition, Performance and Risk |  |  |  | 2028-04-26 |  | EP | 0 | 0.4 | 0.4 | 2022-10-14 |  |  | FALSE
Supplemental | AEP |  | s2830.10 | Rebuild ~21 miles of the circuit from Sorenson to north of Columbia. Retire the remaining 44.1 miles of the line. | Equipment Material Condition, Performance and Risk |  |  |  | 2032-12-01 |  | EP | 0 | 65.7 | 65.7 | 2022-10-14 |  |  | FALSE
Supplemental | AEP |  | s2830.11 | Build a new ~7.5 mile double circuit extension from the Twin Branch – Guardian line to connect the existing Northeast station. | Equipment Material Condition, Performance and Risk |  |  |  | 2032-12-01 |  | EP | 0 | 21 | 21 | 2022-10-14 |  |  | TRUE
Supplemental | AEP | P23509004, P23509005 | s2830.12 | Build a new ~11.7 mile double circuit 138/69kV line from Tri Lakes – Onion Bottom Bog Sw and reenergize the 138kV circuit from Columbia – Albion | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-01 |  | EP | 0 | 32.8 | 32.8 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P23509006 | s2830.13 | Retire the ~7.8 mile Tri Lakes – Gateway 69kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-01 |  | EP | 0 | 2.3 | 2.3 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | P23509001, P21005001 | s2830.14 | Install a new 138kV CB and a new 69kV CB to connect the new lines at Albion station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-10-01 |  | EP | 0 | 2 | 2 | 2022-10-14 |  |  | FALSE
Supplemental | AEP |  | s2830.15 | Reconnect Kline station to the Twin Branch – Jackson Rd 138kV line and install a new 138kV breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2032-12-01 |  | EP | 0 | 1 | 1 | 2022-10-14 |  |  | FALSE
Supplemental | AEP | DR22F04B0, DR22F04B1, DR22F04L0, DR22F04W2 | s2831.1 | Retire 69kV Noble station. Re-terminate 69kV Auburn-Kendallville 69kV line outside of Noble station. | Customer Service |  |  |  | 2026-04-08 |  | EP | 0 | 0.4 | 0.4 | 2024-02-16 |  |  | FALSE
Supplemental | AEP | DR22F04C0, DR22F04T0, DR22F04W2 | s2831.2 | Install 138kV bus, 15.4MVAR Capacitor with 138kV circuit breaker, 2x 138kV MOAB to serve new distribution station. Install Telecom at Virtue station and remote ends. | Customer Service |  |  |  | 2026-04-27 |  | EP | 0 | 2.9 | 2.9 | 2024-02-16 |  |  | FALSE
Supplemental | AEP | P21030003 | s2832.2 | East Lima 138kV: Replace 1000MCM, 1590 AAC bus and riser conductors on the ‘B’ string and Bus 2 with 2-2000 MCM AAC | Operational Flexibility and Efficiency |  |  |  | 2025-02-28 |  | EP | 0 | 0.3 | 0.3 | 2022-10-04 |  |  | FALSE
Supplemental | AEP |  | s2832.4 | Marysville 345kV station: Replace (2) 345 kV 5000A 63kA circuit breakers and associated sub conductor and switches on the H string to eliminate the lower-rated equipment. | Operational Flexibility and Efficiency |  |  |  | 2024-12-20 |  | UC | 50 | 3.01 | 3.01 | 2022-10-04 |  |  | FALSE
Supplemental | AEP | DR21R37B0 | s2848 | Patrick Henry Station: Establish new Distribution station which will be designed at 138 kV and operated at 69 kV until the area conversion project converts the high-side to 138 kV as part of s2179 (Stuart Area Improvements). The new station will consist of two 138 kV Motor Operated Air-Break Switches (MOABs), high-side circuit switcher, 138 (69) kV/34.5 kV 30 MVA transformer, 34.5 kV low-side circuit breaker and 2-34.5 kV distribution feeder circuit breakers. | Customer Service |  |  |  | 2025-12-02 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | P20245010 | s2851 | New Carlisle 138 kV station: Replace 138kV circuit breaker A with a new 3000A 63kA circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-28 |  | EP | 0 | 0.35 | 0.35 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | A19036095, P21604001, P21604002 | s2854.1 | Twenty Third Street – Blaine Street 34.5 kV: Rebuild ~1.20 miles of 34.5 kV line with 556.5 ACSR 26/7 Dove. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-01 |  | EP | 0 | 7 | 7 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | A19036063, P21593001 | s2854.2 | Twenty Third Street station: Replace the Twenty Third Street 138/34.5 kV transformer #1 and transformer #2 with two 138/69/34.5 kV 90 MVA transformers. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-22 |  | EP | 0 | 5.36 | 5.36 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | P21582001 | s2856 | Rebuild the West Coshocton 138-69kV station, with a 138kV 3-breaker ring bus, a new 138-69kV transformer (90 MVA nameplate), and a single 69kV breaker. A new control building will also be installed. Remove the existing station facilities. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-16 |  | EP | 0 | 10.17 | 10.17 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | DP22C10Z1 | s2857.1 | Green Chapel 138 kV: Construct a greenfield station with 19 - 138kV, 90 kA, 4000 A circuit breakers in breaker and half bus configuration. | Customer Service |  |  |  | 2025-02-26 |  | UC | 31 | 27.57 | 27.57 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | DP22C10Z0 | s2857.2 | Innovation 138 kV: Build out the remaining 2 breaker & half strings at the station and install 4 - 138 kV 4000A 80kA circuit breakers | Customer Service |  |  |  | 2025-02-26 |  | UC | 31 | 3.91 | 3.91 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | DP22C10W2 | s2857.3 | Green Chapel – Innovation 138 kV: Construct ~2.1 miles of double circuit 138kV transmission line from Innovation Station to Green Chapel Station utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor SE rating 1123 MVA. | Customer Service |  |  |  | 2025-02-26 |  | UC | 31 | 12.6 | 12.6 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | DP22C10W3 | s2857.4 | Green Chapel Extension 138 kV: Construct ~2.6 miles of double circuit 138kV transmission line extending from Jug - Corridor 138 kV line to Green Chapel station utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor SE rating 1118 MVA to match the existing conductor on the Corridor-Jug line | Customer Service |  |  |  | 2025-03-04 |  | UC | 31 | 15.6 | 15.6 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | DP22C10W0 | s2857.5 | Jug – Corridor 138/345 kV: Additional structures and dead ends will be required on the existing Jug – Corridor double circuit line to accommodate the extension eastward to Green Chapel as the 138 kV circuit is on the west side of the structures. E | Customer Service |  |  |  | 2025-02-26 |  | UC | 31 | 3.6 | 3.6 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | DP22C10C0 | s2857.6 | Conesville - Corridor 345kV: Modify the existing 345kV line structures to enable appropriate height for the new line to Green Chapel Station | Customer Service |  |  |  | 2025-03-04 |  | UC | 31 | 1.97 | 1.97 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | P22799001 | s2857.7 | Babbitt 345/138 kV: Install a second 675 MVA, 345/138 kV transformer to address overloading Jug Street 345/138 kV transformer under N-1-1 contingencies as a result of this customer load interconnection. Cost | Customer Service |  |  |  | 2026-07-10 |  | EP | 0 | 16 | 16 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | P22799002 | s2857.8 | Corridor 138 kV: Replace 3000A breakers CB-104C & 104S with 4000 A breakers. This addresses N-1-1 overloading on those breakers as a result of this customer load interconnection. | Customer Service |  |  |  | 2027-04-20 |  | EP | 0 | 2 | 2 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | P20252007 | s2857.9 | West Lancaster 138 kV: Install high and low side sectionalizing on the two 138/69 kV transformers. This addresses, due to lack of sectionalizing, N-1-1 overloading on 69 kV lines as a result of this customer load interconnection. | Customer Service |  |  |  | 2029-05-02 |  | EP | 0 | 3.5 | 3.5 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | DP22C11Z0 | s2858 | Jug station 138 kV: Install 1 - 138kV 80kA 4000A circuit breaker in the open F position on the ring bus to accommodate a new distribution transformer at the station. | Customer Service |  |  |  | 2025-11-20 |  | EP | 0 | 0.678 | 0.678 | 2022-12-16 |  |  | FALSE
Supplemental | AEP | P17002002 | s2882.1 | Install a new seven breaker 138 kV ring bus utilizing 3000A 63kA breakers to replace the existing Wilson Rd ring bus. Retire the 40kV equipment at Wilson Rd. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  | EP | 0 | 8 | 8 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P17002031 | s2882.2 | Rebuild the existing 0.7 miles triple circuit line between structure 47 and Wilson Rd as double circuit using 1033 ACSR conductor. The third circuit that creates a three terminal point between Hall, Fisher, and Wilson will be permanently retired. The Hall Road – Fisher 138 kV circuit will remain. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  | EP | 0 | 2.1 | 2.1 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P17002022 | s2882.3 | Convert Phillipi station to 138kV service to allow for the elimination of the 40kV system between McComb and Wilson Rd. stations. Majority of the station was originally built to 138kV standards. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  | EP | 0 | 0.51 | 0.51 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P17002033 | s2882.4 | Build a new 0.7 mile 138kV double circuit line to serve Phillipi at 138 kV off the Beatty – Wilson circuit. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  | EP | 0 | 1.4 | 1.4 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P17002019 | s2882.5 | Retire the 5.45 mile 40kV circuit between Wilson and McComb. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  | EP | 0 | 1.1 | 1.1 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P17002006 | s2882.6 | The 40kV breakers at McComb station are no longer needed once Phillipi is converted to 138kV and will be retired. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency¦Customer Service |  |  |  | 2025-06-30 |  | EP | 0 | 0.59 | 0.59 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P19269004 | s2883.1 | Upgrade the Natrium 138-69kV station by completing the breaker-and-a-half design in the 138kV and 69kV portions of the station. Install a new control house in the 69kV yard and expand the newer 138kV control house. Remove the older control house and various 138kV & 69kV station structures. Install a 2nd 138kV capacitor bank (46 MVAR). | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 18.22 | 18.22 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P19269005 | s2883.2 | Construct a new 138kV transmission line from Natrium to a customer station (0.5 mile), providing a 2nd source to the customer | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 2.59 | 2.59 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P19269009 | s2883.3 | Remote-end upgrades at Mobay 69kV station, to coordinate with the new fiber-based line relays at Natrium (2- 69kV circuits). A new transclosure will be installed to house the relays, RTU, and metering equipment. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2024-12-01 |  | EP | 0 | 1.26 | 1.26 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P21598001 | s2884.1 | Morse – Gahanna 138kV Line (Gahanna-Hap Cremean & Hap Cremean-Morse Road circuits): Rebuild the ~5.04 miles single circuit line with 795 kCM ACSR & install OPGW fiber on new line rebuild. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 13.62 | 13.62 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P21598007 | s2884.2 | Gahanna – Blacklick 138kV Line: Rebuild the ~3.32 miles single circuit line with 795 kCM ACSR & install OPGW fiber on new line rebuild. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 11.68 | 11.68 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P21598012 | s2884.3 | Blacklick Extension 138kV line: Partially rebuild the line from Blacklick to structure No. 11 ~0.71 mile single circuit line with 795 kCM ACSR & install OPGW fiber on new line rebuild | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 2.19 | 2.19 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P21598013 | s2884.4 | Morse Road 138kV station: Telecom upgrades. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0.025 | 0.025 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P21598008 | s2884.5 | Hap Cremean 138kV station: Install remote end relay upgrades, CCVTs, telecom multiplexer, & remove wave trap. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0.508 | 0.508 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P21598009 | s2884.6 | Gahanna 138kV station: Install remote end relay upgrades, telecom multiplexer, & remove wave trap. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0.497 | 0.497 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P21598010 | s2884.7 | Blacklick 138kV station: Install remote end relay upgrades, CCVTs, Telecom Multiplexer, & remove wave trap. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0.681 | 0.681 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P21598011 | s2884.8 | East Broad Street 138kV station: Install remote end relay upgrades, telecom upgrades, CCVTs, & remove wave trap. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 0.482 | 0.482 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P18171001 | s2887.1 | Construct a new brownfield, breaker and a half Glen Lyn station next to the existing station. The new station will contain eleven 138kV breakers with seven 138kV line exits creating four breaker and half strings. Two 138kV capacitor banks with circuit switchers. One 138/34.5kV Distribution bank with high side circuit switcher and four 34.5kV breakers. The high station cost is due to the need to raise the new station nearly 10 feet to relieve the flooding concern. Environmental cost is anticipated to be high to remove station equipment, asbestos abatement, building demolition, disposal of soils/TCI conduit/concrete/underground piping/underground transformer vaults. Remove the existing 138 and 34.5 kV yards. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  | EP | 0 | 37.8 | 37.8 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P18171004 | s2887.2 | At Hinton station, remove the line trap. Install bus CCVTs and line arresters on the 138kV line to Glen Lyn. Upgrade relaying to coordinate to the new breakers. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  | EP | 0 | 0.67 | 0.67 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P18171006 | s2887.3 | Extend the Glen Lyn – Progress Park circuit ~0.4 miles of install to reconnect the circuit to the new Glen Lyn station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  | EP | 0 | 2.5 | 2.5 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P18171007 | s2887.4 | Extend the Glen Lyn – Morgans Cut and Glen Lyn – Hazel Hollow lines (double circuit construction) ~0.15 miles to reconnect the lines to the new Glen Lyn station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2029-04-03 |  | EP | 0 | 2.6 | 2.6 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P18171009 | s2887.5 | Extend the Glen Lyn – Kimballton and Glen Lyn – Peters Mountain lines (double circuit construction) ~0.25 miles to reconnect the lines to the new Glen Lyn station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2029-03-06 |  | EP | 0 | 2.1 | 2.1 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P18171010 | s2887.6 | Extend the Glen Lyn – Hinton circuit ~0.1 miles to reconnect the line to the new Glen Lyn station. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  | EP | 0 | 1.8 | 1.8 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | P18171017 | s2887.7 | Required work to connect the New Glen Lyn station to the existing fiber network. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2026-06-01 |  | EP | 0 | 0.71 | 0.71 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | A19036118, P21736001, P21736002, P21736003, P21736004 | s2888 | Adams – Berne 69 kV: Replace ~4.9 miles of 69 kV line structures. The following cost includes the structure replacements, structure removals, ROW acquisitions, and station connections. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-28 |  | EP | 0 | 12.8 | 12.8 | 2023-01-20 |  |  | FALSE
Supplemental | AEP | DX21C02D0 | s2911.1 | Guysville 69 kV: Install a in-out station with an 2000A auto sectionalizing MOAB switch towards Coolville and a 3000A 40kA circuit breaker towards Bryson. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 1.73 | 1.73 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P20092001 | s2911.2 | Bryson - Guysville 69 kV: Construct a greenfield ~12.5-mile single circuit line using 556.5 ACSR (Dove) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 28.26 | 28.26 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P20092003 | s2911.3 | Coolville – Guysville 69 kV: Constructing a greenfield ~10.5-mile single circuit line using 556.5 ACSR (Dove) conductor (SE 142 MVA) | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 29.22 | 29.22 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P20092010 | s2911.4 | Coolville 69 kV: Upgrade to a in-out station with two 3000A 40kA circuit breakers on the through path. Existing wood structures will be replaced with a new steel box bay to accommodate new breakers | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 3.08 | 3.08 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P20092005 | s2911.5 | Coolville – East Bashan 69 kV: Rebuild the existing single circuit ~12.6-mile line using 556.5 ACSR (Dove) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 29.61 | 29.61 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P20092011 | s2911.6 | West Bashan 69 kV: Remove switch going to Hemlock | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 0.02 | 0.02 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P20092014 | s2911.7 | Hemlock – West Bashan 69kV: Remove ~7.7 miles of single circuit line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 2.09 | 2.09 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P20092012 | s2911.8 | Hemlock 69 kV: Remove the circuit breaker going to West Bashan (CB C). | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-01 |  | EP | 0 | 0.14 | 0.14 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21733001 | s2913.1 | Retire existing Kyle Hill Station | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  | EP | 0 | 0 | 0 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21733001 | s2913.2 | Kyle Hill Extension : New 0.07 miles double circuit in/out line from the Fort Robinson-Hill 69kV line to the new Kyle Hill 69kV Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  | EP | 0 | 1.22 | 1.22 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21733004 | s2913.3 | Build a new Kyle Hill Station behind the existing station. Establish a 69KV bus to allow a 69KV in/out from Fort Robinson – Hill 69KV line. Install one (1) 1200A 69KV rated line MOAB switches towards Hill station. Install one (1) 1200A 69KV rated line switches towards Fort Robinson station. Replace Ground MOAB with a high-side circuit switcher. Replace existing 34.5/12KV transformer #1 with 69/12KV transformer. Install new 12KV bus. Reuse existing Kyle Hill 12kV Breakers. Install 16x19 DICM. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-07-01 |  | EP | 0 | 0 | 0 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21733005 | s2913.4 | Retire approximately 3.41 miles of the Fort Robinson-Lovedale 34.5kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  | EP | 0 | 2.69 | 2.69 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21733006 | s2913.5 | Remote end and Removal of Circuit Breaker J at Fort Robinson substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  | EP | 0 | 0.197 | 0.197 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21733007 | s2913.6 | Remote end and Removal of Circuit Breaker G at Lovedale substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-07-01 |  | EP | 0 | 0 | 0 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21733010 | s2913.7 | Retire 34.5 kV Echo Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  | EP | 0 | 0.095 | 0.095 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21733011 | s2913.8 | Provide Transition Fiber for Kyle Hill Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-26 |  | EP | 0 | 0.106 | 0.106 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21597001 | s2915.1 | Grace - South Rokeby 69 kV Line: Rebuild ~12.3 mi of line asset, the section between Grace – South Rokeby using 556 ACSR conductor & install telecom fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 29.62 | 29.62 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21597003 | s2915.2 | West Malta - North Muskingum 69 kV Line: Rebuild the whole ~8.4 mi line asset using 556 ACSR conductor & install telecom fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 18.28 | 18.28 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21597005 | s2915.3 | West Malta - North McConnelsville 69 kV Line: Rebuild the whole ~2.1 mi line asset using 556 ACSR conductor & install telecom fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 6.08 | 6.08 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21597015 | s2915.4 | South Rokeby – Gould No.1 & No. 2 69 kV Line: Rebuild both ~0.05 mi (each) line assets using 556 ACSR conductor & install telecom fiber. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 0.78 | 0.78 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21597031 | s2915.5 | South Rokeby - North McConnelsville 69kV Line: ~0.25 miles rebuild on the South Rokeby – West Malta 69 kV Circuit & install telecom fiber | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 0.92 | 0.92 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21597023 | s2915.6 | Buttermilk Hill Switch 69 kV: Install a new 69 kV, 1200A, 3-way POP switch outside the fence of North McConnelsville station and install auto-sectionalizing. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 0.73 | 0.73 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21597017 | s2915.7 | Pennsville 69 kV POP Switch: Replace existing switch with 1200A, 3-way switch & install auto-sectionalizing. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-01 |  | EP | 0 | 0.73 | 0.73 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21716011 | s2917.1 | Reconfigure the existing East Cambridge- West Cambridge 69kV circuit to add in a replacement switch pole for Cassell Junction Sw that is capable of adding MOAB operation on the throughpath. This replacement structure will be one span down from the existing switch in order to comply with current ROW standards. | Customer Service |  |  |  | 2025-12-31 |  | EP | 0 | 0.89 | 0.89 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21716002 | s2917.2 | Install a new 138kV three- way phase over phase switch named Cassell Junction Switch to serve the Cassell Junction Co-op station. | Customer Service |  |  |  | 2025-12-31 |  | EP | 0 | 0.68 | 0.68 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21716003 | s2917.3 | Construct ~ 0.12 miles of new 69 kV line between the new Cassell Junction Switch and the Cassell Junction Co-op station using 556 ACSR conductor. | Customer Service |  |  |  | 2025-12-31 |  | EP | 0 | 0.66 | 0.66 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P21716001 | s2917.4 | Install new customer metering at Cassell Junction for Guernsey Muskingum Electric Cooperative. | Customer Service |  |  |  | 2025-12-31 |  | EP | 0 | 0.004 | 0.004 | 2023-02-17 |  |  | FALSE
Supplemental | AEP | P19256001 | s2920.1 | At East Lima 69kV breakers U and V will be replaced with 3000A 40kA breakers. The 69kV disconnect switches and sub-conductors will be upgraded. A DICM will be installed to replace the old control structure. Relay and breaker control voltages will be standardized. Environmental remediation at the station will be completed per federal requirements. Remediation will include the disposal of PCB-impacted soils, concrete, and a legacy oil processing facility including associated oil piping and equipment. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  | EP | 0 | 11.1 | 11.1 | 2023-03-17 |  |  | FALSE
Supplemental | AEP | P19256004 | s2920.2 | Upgrade relays at West Lima, Ford Lima, Yellow Creek and Woodlawn to coordinate with the new protection and communication scheme tied out of East Lima | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-01 |  | EP | 0 | 1 | 1 | 2023-03-17 |  |  | FALSE
Supplemental | AEP | P21599001 | s2921 | Conesville-Bixby 345kV Line ( Bixby-Ohio Central & Ohio Central-Conesville Circuits ): Rebuild ~46.1 miles of the ~51.1 miles of line using 954 kCM ACSR bundled conductor & install OPGW fiber on new line rebuild. Newer steel poles on the line will not be replaced | Equipment Material Condition, Performance and Risk |  |  |  | 2032-12-31 |  | EP | 0 | 154.53 | 154.53 | 2023-02-07 |  |  | FALSE
Supplemental | AEP | P21076018 | s2941 | Install one new 138/12 kV XFR and one new 138 kV CB at the existing Coco Station. | Customer Service |  |  |  | 2025-02-28 |  | EP | 0 | 0.9 | 0.9 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | P21748001, P21748002, P21748012, P21748003 | s2942.1 | Main Street – Hickory Creek 138kV Line Asset: Rebuild ~3.47 miles of the Derby – Main Street 138kV circuit up to structure 125. Of that ~3.47 miles, the Main Street – Napier – Hickory Creek 34.5kV circuit is double circuited with Derby – Main Street 138kV circuit for ~2.84 miles, which will also be rebuilt and then energized to 69kV. Both lines will utilize the 795 ACSR 26/7 Drake conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  | EP | 0 | 16.2 | 16.2 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | P21748016 | s2942.2 | Main Street – Hickory Creek 34.5kV (via Pearl Street): Energize at 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  | EP | 0 | 0 | 0 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | P21748013 | s2942.3 | Main Street: Energize circuit breakers J, K, and L to 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  | EP | 0 | 0.91 | 0.91 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | P21748016 | s2942.4 | Hickory Creek: Retire 34.5kV circuit breaker BG and remaining 34.5kV equipment. Energize circuit breakers AQ, BE, and BH to 69kV. Breaker BH will be used as a bus tie breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  | EP | 0 | 1.18 | 1.18 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | P21748017, P21748014, P21748015, P21748021 | s2942.5 | Pearl Street, Langley, and Napier: Energize to 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  | EP | 0 | 0.41 | 0.41 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | P21748019, P21748020 | s2942.6 | Ausco Radial 34.5kV: Retire the 34.5kV Ausco radial | Equipment Material Condition, Performance and Risk |  |  |  | 2030-03-14 |  | EP | 0 | 0.6 | 0.6 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | A19036115, P22047001, P22047002, P22047003 | s2943 | Rebuild 5.88 miles of the 6.36 mile circuit from Magley-Decatur with 795 ACSR. The rebuild will consist of all 1957 and 1966 vintage poles, towers with failed strength requirements, as well as the 4/0 and 336 ACSR conductor | Equipment Material Condition, Performance and Risk |  |  |  | 2030-02-19 |  | EP | 0 | 12.48 | 12.48 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | P16078006 | s2944 | Warwood: Replace the 3- 69kV oil circuit breakers with new SF6 gas breakers. Replace the electromechanical 69kV line relays and bus differential relays with microprocessor-based relays. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-01 |  | EP | 0 | 1.49 | 1.49 | 2023-04-21 |  |  | FALSE
Supplemental | AEP | P16078018 | s2970 | Remove the 69kV cap bank and cap switcher at Scio. A new RTU will be added along with standard SCADA functionality for transmission & distribution equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-08-04 |  | EP | 0 | 0.1 | 0.1 | 2023-06-16 |  |  | FALSE
Supplemental | AEP | P19303004 | s2981.1 | Cut in/out of the existing Lakin – Lock Lane 69 kV line and construct a new double circuit 69 kV line in/out to the new Mason County Industrial Park Station (approx. 0.25 mi) | Customer Service |  |  |  | 2025-11-17 |  | EP | 0 | 2.1 | 2.1 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P19303012 | s2981.2 | Install two 69 kV circuit breakers and a 69/12 kV 25 MVA transformer at the new Mason County Industrial Park Station (York Station) | Customer Service |  |  |  | 2025-11-17 |  | EP | 0 | 0 | 0 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21591001 | s2982.1 | South Kenton. Rebuild the 138kV bay as a four breaker ring bus using 3000A 40kA breakers. Replace transformers two and three with a single 90MVA unit. Install a DICM and replace the EM relays. Replace the 69kV bus and breakers C and E. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  | EP | 0 | 12.7 | 12.7 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21591010 | s2982.2 | Re-terminate the East Lima - South Kenton 138 kV and South Kenton - Larue 138kV circuits into the new South Kenton ring bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  | EP | 0 | 3.64 | 3.64 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21591007 | s2982.3 | Re-terminate the South Kenton - Kenton #1 69kV and South Kenton - Kenton #2 69kV circuits into the station. Install fiber between South Kenton and Kenton, retire the pilot wire scheme E | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  | EP | 0 | 1.45 | 1.45 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21591002 | s2982.4 | At Kenton station, replace MOABS X,Z with 69kV 3000A 40kA breakers. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  | EP | 0 | 3.8 | 3.8 | 2023-07-21 |  |  | FALSE
Supplemental | AEP |  | s2982.5 | Upgrade telecom equipment at Rangeline and Gunn Road stations | Equipment Material Condition, Performance and Risk |  |  |  | 2027-07-01 |  | EP | 0 | 0.094 | 0.094 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21590001 | s2983.1 | North Delphos: Replace 69kV circuit breakers A & C and Install DICM. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-06-01 |  | EP | 0 | 3.3 | 3.3 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21590013 | s2983.2 | Van Wert: Upgrade line relays. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-06-01 |  | EP | 0 | 0.7 | 0.7 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21590006 | s2983.3 | South Delphos – Delphos: Rebuild 2.7 miles of 69kV with 556 ACSR conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-06-01 |  | EP | 0 | 7.8 | 7.8 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21590010 | s2983.4 | North Delphos - South Delphos: Rebuild 4.33 miles of 69kV with dove 556 ACSR. 1.1 miles will be double circuit (part of the in and out to North Delphos not covered under b3346) and 3.2 miles will be single circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-06-01 |  | EP | 0 | 11.7 | 11.7 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P22110013 | s2984.1 | Haviland - Paulding 69kV: Rebuild the existing 10.73 mile-long line using 795 ACSR Drake conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-01 |  | EP | 0 | 18.74 | 18.74 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P22110007 | s2984.2 | Paulding: Perform remote end work | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-01 |  | EP | 0 | 1.4 | 1.4 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P22110008 | s2984.3 | Haviland: Perform remote end work | Equipment Material Condition, Performance and Risk |  |  |  | 2026-01-01 |  | EP | 0 | 1.03 | 1.03 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21244004 | s2985.1 | Elgin – North Spencerville: Construct approximately 5 miles of 69kv single circuit. Install ADSS. | Customer Service |  |  |  | 2024-12-01 |  | EP | 0 | 12.13 | 12.13 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21244001 | s2985.2 | North Spencerville: Install a DCIM expansion and new 69kv circuit breaker. Install bypass switch called West Spencerville | Customer Service |  |  |  | 2024-12-01 |  | EP | 0 | 0.5 | 0.5 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21244007 | s2985.3 | Kossuth-E Delphos: Install ~0.05 miles of 69kv single circuit. | Customer Service |  |  |  | 2024-12-01 |  | EP | 0 | 0.31 | 0.31 | 2023-07-21 |  |  | FALSE
Supplemental | AEP | P21077001, P21077002 | s2986.1 | East Elkhart 138kV: Install a new 138kV breaker string with 3 3000A 40kA circuit breakers to accommodate two new feeds to the NIPSCO station. Relocate the 345/138kV transformer #2 feed to the new string. Install metering on both exits out of East Elkhart towards NIPSCO’S Menges Ditch station. | Customer Service |  |  |  | 2026-07-22 |  | EP | 0 | 0 | 0 | 2023-05-19 |  |  | TRUE
Supplemental | AEP | P21077003, P21077004, P21077005, P21077007 | s2986.2 | East Elkhart – Menges Ditch 138kV #1 and #2: Install the first span and structure outside of East Elkhart, one exiting to the north and the other to the south, utilizing 2 bundle 795 ACSR 26/7 DRAKE conductor creating a new AEP-NIPSCO interconnection and PJM-MISO seam. | Customer Service |  |  |  | 2026-07-22 |  | EP | 0 | 0 | 0 | 2023-05-19 |  |  | TRUE
Supplemental | AEP | P20252035 | s3133.1 | Ralston - North Logan 69 kV Line : Retire the line section between North Logan – Geneva Switch (~9.0 miles) between Str. 70 – 147 and rebuild a portion as double circuit from Geneva Sw up to Str. 70/71 (~1.15 miles). | Equipment Material Condition, Performance and Risk |  |  |  | 2026-04-16 |  | EP | 15 | 9.67 | 9.67 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252024 | s3133.2 | East Logan – Shawnee 69 kV Line : Six-wire the 69 kV line between N. Logan – E. Logan (Str. 2-43) and terminate the E. Logan – New Lexington 69 kV circuit into the now vacated Ralston – N. Logan 69 kV line position at N. Logan station at/near structure 44 to form the new N. Logan – New Lex. 69 kV circuit. Remove sections between Str. 43 – 44 and Str. 2 – E. Logan (CB-L). | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-20 |  | EP | 15 | 1.28 | 1.28 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252029, P20252030 | s3133.3 | Clouse - West Lancaster 138 kV: Rebuild ~23 miles of 138 kV line between West Lancaster and Clouse stations. The existing double circuit line will be rebuilt as double circuit between West Lancaster and just east of South Lancaster station along with the section between structure 96 and Clouse station. The remaining ~5.6 miles of the line will be rebuilt as single circuit. The section between structure 96 and Clouse will have one circuit of the double circuit operated at 69 kV to form the South Lancaster – Clouse circuit to allow for the retirement of the Ralston – North Logan line south. 69 kV and 138 kV line extensions will be installed into Clouse station, using 795 ACSR conductor SE 360 MVA. | Equipment Material Condition, Performance and Risk |  |  |  | 2030-02-12 |  | EP | 15 | 65.81 | 65.81 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252049 | s3133.4 | East Logan – South Lancaster 69 kV Line : Re-terminate this line at East Logan to utilize CB-P, which is a newer vintage breaker in better health than existing breaker M. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-03-27 |  | EP | 15 | 0.72 | 0.72 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252008 | s3133.5 | East Logan 69 kV: Retire 69 kV CB-M and repurpose CB-P for re-terminating the South Lancaster circuit. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-06-20 |  | EP | 15 | 0.77 | 0.77 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252046 | s3133.6 | Clouse 138 kV & 69 kV: Add a 138 kV, 3000 A, 63 kA breaker to accommodate the new 138 kV line from Crooksville. Add a 69 kV, 3000 A, 40 kA breaker to accommodate the new 69 kV line from South Lancaster (thru Geneva Sw). Install all associated attachment facilities. DICM expansion will likely be required. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-08-08 |  | EP | 15 | 1.67 | 1.67 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252047 | s3133.7 | Geneva Sw 69 kV: Replace & relocate the existing PoP Switch with a 3-way 1200A PoP Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-08-08 |  | EP | 15 | 0.95 | 0.95 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252006 | s3133.8 | Junction City 138 kV: Replace the existing 2-way POP with a 3-way 2000A POP. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-09-07 |  | EP | 15 | 1.15 | 1.15 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252007 | s3133.9 | West Lancaster 138 kV & 69 kV: Replace T2 with a 90MVA bank. Replace 138 kV CB-D with 1 - 138 kV, 3000 A, 40 kA circuit breaker, 69 kV CB-C & CB-J with 2 – 69kV 3000 A, 40 kA circuit breakers, 69 kV CS-BB with 1 – 69 kV 2000A 31.5 kA circuit breaker and, the control building with DICM & new relays. Retire 138 kV CB-E. Replace 69 kV Bus 1 PT’s. Note: Work will be coordinated with previously proposed upgrades at station captured under S2857.9. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-09-11 |  | EP | 15 | 10.83 | 10.83 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252036 | s3133.10 | South Lancaster 138 kV & 69 kV: Add 2 - 69 kV, 3000 A, 40 kA and 2- 138 kV, 3000 A, 40 kA circuit breakers to the low and high sides of T1 and T2. Upgrade transformers’ protection. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-09-05 |  | EP | 15 | 3.22 | 3.22 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252022 | s3133.11 | Lancaster – E. Lancaster – S. Lancaster 69 kV: In order to mitigate the 3-terminal line, 0.2 miles of 69 kV double circuit line, including several dead end and turning structures, will be constructed to loop the circuit into East Lancaster station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-01-20 |  | EP | 15 | 2.39 | 2.39 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252004 | s3133.12 | East Lancaster 69 kV: Extend the bus to accommodate a new line. Install one new 69 kV, 3000 A, 40 kA breaker and all associated attachment facilities (relays, bus work, risers, and switches). Retire the 69 kV cap bank. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-21 |  | EP | 15 | 1.04 | 1.04 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252037 | s3133.13 | Lancaster Jct – E. Lancaster – Ralson 69 kV : In order to mitigate the 3-terminal line, 0.2 miles of 69 kV double circuit line will be constructed to loop the circuit into Lancaster Junction station. There will be associated telecom work performed as well. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-27 |  | EP | 15 | 1.65 | 1.65 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252001 | s3133.14 | Lancaster Junction 69 kV: Add three 69 kV, 3000 A, 40 kA line breakers at Lancaster Junction and all associated attachment facilities (relays, bus work, risers, and switches). Expand the Station to include two box bays. Retire 69 kV Line & Bus tie switches. | Equipment Material Condition, Performance and Risk |  |  |  | 2029-02-20 |  | EP | 15 | 5.03 | 5.03 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | P20252045 | s3133.15 | Anchor Hocking, Lancaster, North Logan, New Lexington 69 kV: Remote end PCE work will be performed to accommodate project in area. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-04-28 |  | EP | 15 | 0.69 | 0.69 | 2023-11-17 | PM Robert Howard |  | FALSE
Supplemental | AEP | DP21R02B0 | s3134.1 | Construct a 138 kV straight bus with 2 MOABs that are SCADA controlled. Install a 138/34.5 kV, 30 MVA Distribution transformer with two 34.5kV circuit breakers | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-24 |  | EP | 0 | 0 | 0 | 2023-11-17 |  |  | FALSE
Supplemental | AEP | DP21R02C0 | s3134.2 | Install a new 138kV 3 pole custom tap structure on the Jacksons Ferry – Huffman 138 kV circuit. Construct approximately 4.0 miles of new double circuit 138 kV line with OPGW from the tap location to the new Wildwood substation. The higher cost is due to access road and restoration costs in the state of Virginia. The right of way for this 138kV extension travels in different directions due to hard to obtain easements causing higher line cost. Install ADSS fiber along existing Huffman-Jacksons Ferry line. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-10-24 |  | EP | 0 | 20.8 | 20.8 | 2023-11-17 |  |  | FALSE
Supplemental | AEP | A16927002 | s3135.1 | Rebuild ~2.6 mi portion of the existing Garden Creek - Richlands - Skeggs Branch 69kV Line from the existing Permac station to the existing tap structure 340-28 on the Garden Creek – Skeggs Branch - Richlands. Rebuild ~4.6 mi of the existing Garden Creek - Richlands - Skeggs Branch 69kV Line from the existing Coal Creek to Richlands substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  | EP | 0 | 27.2 | 27.2 | 2023-11-17 |  |  | FALSE
Supplemental | AEP | A16927023 | s3135.2 | At Whetstone Branch Station, replace circuit switcher "AA" with a new, standard, 69kV circuit switcher, replace all metering CTs and PTs with CT/PT combo metering units, and replace the existing single phase CCVT with a new standard three phase CCVT. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  | EP | 0 | 1.55 | 1.55 | 2023-11-17 |  |  | FALSE
Supplemental | AEP |  | s3135.3 | At Coal Creek substation, reconductor the 69kV bus, replace 600A Switchers with new MOAB switches on new steel structures. Switch "33" towards the customer will be replaced to allow for the new structure to fit into the existing station footprint. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  | EP | 0 | 0 | 0 | 2023-11-17 |  |  | FALSE
Supplemental | AEP |  | s3135.4 | Remote end work at Richlands substation. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  | EP | 0 | 0.05 | 0.05 | 2023-11-17 |  |  | FALSE
Supplemental | AEP |  | s3135.5 | Provide transition fiber on the Garden Creek - Richlands - Skeggs Branch 69kV Line for connectivity at Mount Heron Station and at Whetstone Branch Station to support CES networking and SCADA connectivity. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-10-30 |  | EP | 0 | 0.4 | 0.4 | 2023-11-17 |  |  | FALSE
Supplemental | AEP | P22091001 | s3136.1 | Hartford Station: Install a 69kV breaker and remove the 34.5kV equipment. Station Service will be relocated closer to the transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-14 |  | EP | 15 | 0.59 | 0.59 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  | FALSE
Supplemental | AEP | P22091003 | s3136.2 | Sister Lakes: Replace both transformers with 9.375MVA 69/12kV units and install a high side switcher on transformer 1. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-02-10 |  | EP | 15 | 0 | 0 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  | FALSE
Supplemental | AEP | P22091004 | s3136.3 | Dewey Lake Street: Install a new 7.5 MVA 69/34.5kV transformer with low side breaker and high side fuse. This will be located close to Gearcon Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-07-07 |  | EP | 15 | 1.72 | 1.72 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  | FALSE
Supplemental | AEP | P22091006 | s3136.4 | Valley: Install a 69/34.5kV 12.5MVA transformer and retermniate the Rothadew line to the 69kV bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-12-07 |  | EP | 15 | 3.63 | 3.63 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  | FALSE
Supplemental | AEP | P22091007 | s3136.5 | Colby: Move the Rothadew line to the 69kV bus. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-12-04 |  | EP | 15 | 0.11 | 0.11 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  | FALSE
Supplemental | AEP | P22091016 | s3136.6 | Twin Lakes Sw.: Replace Switch. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-16 |  | EP | 15 | 0.83 | 0.83 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  | FALSE
Supplemental | AEP | P22091008 | s3136.7 | Keelette, Sister Lakes, Gearcon Sw., Rothadew,: Energize to 69kV. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-05-14 |  | EP | 15 | 1.01 | 1.01 | 2023-11-17 | PM Kelly Wagoner / PlannerJoshua Smith |  | FALSE
Supplemental | AEP | P23221002 | s3137.1 | Cut in/out of the existing Yellow Bush – Polymer 138 kV line, install a new double circuit 138 kV 0.1 mile line to the new 138 kV station (Kera Lakes). | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-13 |  | UC | 75 | 0 | 0 | 2023-11-17 | PM Roger Whitt / Planner Michael Hassay |  | FALSE
Supplemental | AEP | P23321003 | s3137.2 | Construct a new 138 kV station (Kera Lakes) with 4 – 3000A, 40 kA circuit breakers in a ring bus configuration with two feeds to the customer. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-13 |  | UC | 75 | 0 | 0 | 2023-11-17 | PM Roger Whitt / Planner Michael Hassay |  | FALSE
Supplemental | AEP | P23321008 | s3137.3 | Network fiber support work at Cottageville Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-13 |  | UC | 75 | 0 | 0 | 2023-11-17 | PM Roger Whitt / Planner Michael Hassay |  | FALSE
Supplemental | AEP | DR23C08D0 | s3138.1 | At Taylor station, install 1-138 kV 40 kA 3000 A bus tie circuit breaker and 1-138 kV 3000 A 40 kA GOAB beaker disconnect switch to accommodate a new distribution transformer. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-12-31 |  | EP | 0 | 1.26 | 1.26 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21724009 | s3139.1 | Construct a new double circuit 138 kV line (approx. 1 miles) by tapping the existing Cherry Creek – Pemberton 138 kV and building in/out to a new 138 kV station near Coal City. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 5.4 | 5.4 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | A20045035 | s3139.2 | Retire existing 46 kV line from Sophia – Maben Energy. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 11.5 | 11.5 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | A20045036 | s3139.3 | Retire existing Sophia – Tams Mountain 46 kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 4.7 | 4.7 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21724004 | s3139.4 | Retire existing Pemberton – Sophia 46 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 3.3 | 3.3 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21724001 | s3139.5 | New Coal City Station: Install two 138 kV line MOABs, one 138/12 kV 20 MVA XFR with high side circuit switcher and two 12 kV feeders | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 1 | 1 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | A20045062 | s3139.6 | Retire Sophia 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 1.4 | 1.4 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21724003, P21724015, P21722016, P21723013 | s3139.7 | Pemberton Station: Install a new 138/46 kV XFR with a high side circuit switcher and new metering. This will feed the customer currently served out of Sophia Station. Construct a new 1 mile 46 kV line from Pemberton to the customer. Install two new 138 kV circuit breakers . Retire 138/46 kV XFR, 46 kV CB-A, 46 kV CB-C and 4 kV distribution equipment. Install one new 138 kV circuit breaker. Retire 46 kV CB-B | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 10.7 | 10.7 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21724005 | s3139.8 | Stotesbury: Replace existing hard tap with a new 3-way phase over phase switch | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 1.8 | 1.8 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21724006 | s3139.9 | Retire Killarney 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0 | 0 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21724007 | s3139.10 | Retire Bowyer 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0 | 0 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723017 | s3139.11 | Tams Mountain: Remove 46 kV CB-N2 and 46 kV CB M | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 1.1 | 1.1 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723007 | s3139.12 | Construct a new double circuit 138 kV line in/out (approx. 1 mile) to the existing Sweeneysburg Switch Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 3.8 | 3.8 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723001, P21723016 | s3139.13 | Construct a new 138 kV double circuit line (approx. 2 miles) by tapping the existing North Beckley – Tams Mountain 138 kV line and building in/out to a new 138 kV station (Lester Square Station) | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 9.9 | 9.9 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723004 | s3139.14 | Construct a new 138 kV single circuit line (approx. 1.2 miles) from the new Lester Square Station to the existing Pemberton 138 kV station. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 6.6 | 6.6 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723014 | s3139.15 | Retire Glen White Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0 | 0 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723019 | s3139.16 | Retire Shockley Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0.1 | 0.1 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | A20001421 | s3139.17 | Retire Bradley – Tams Mountain 46 kV line: | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 20.3 | 20.3 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723012 | s3139.18 | Sweeneysburg Switch: Convert to 138 kV | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0.1 | 0.1 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723010, P21723011, P21723025 | s3139.19 | Lester Square: Install five 138 kV CBs in a ring configuration, install one 23 MVAR capacitor bank with a circuit switcher, install a new 138/12 kV 20 MVA XFR with two 12 kV feeders. Install a new 138/46 kV XFR to feed the customer previously served from Shockley Station. Construct a new 46 kV line from Lester Square to the customer previously served at Shockley Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 5.9 | 5.9 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723021 | s3139.20 | North Beckley Station: Remote End work required due to the new line cut in to Lester Square Station. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0.6 | 0.6 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21723015 | s3139.21 | Bradley Station: Remove 46 kV CB-F, Retire 46 kV CB-J | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0.8 | 0.8 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722003 | s3139.22 | Construct a new 138 kV double circuit line (approx. 1.5 miles) tapping the existing Bradley – North Beckley 138 kV line and building in/out to a new 138 kV station (Cranberry Creek) | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 7.9 | 7.9 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722001 | s3139.23 | Construct a new single circuit 138 kV line (approx. 5.1 miles) from Pemberton to a new 138 kV station (East Beckley) | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 15.7 | 15.7 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722002 | s3139.24 | Construct a new single circuit 138 kV line (approx. 1.7 mile) from the new East Beckley 138 kV Station to a new 138 kV station (Armory Station) | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 8 | 8 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722025 | s3139.25 | Construct a new double circuit 138 kV line (approx. 1.0 miles) by tapping the Raleigh County 138 kV Extension line and building in/out to the new Armory 138 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 4.5 | 4.5 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | A20045034 | s3139.26 | Retire Bradley – Beckley 46 kV line | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 9.6 | 9.6 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | A20045032 | s3139.27 | Retire Beckley – Pemberton 46 kV line and Crab Orchard 46 kV tap line | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 7 | 7 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722020 | s3139.28 | Retire Whitestick 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0 | 0 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | A20045059 | s3139.29 | Retire Beckley 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0 | 0 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722021 | s3139.30 | Retire Crab Orchard 46 kV Station | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0 | 0 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722032, P21722027 | s3139.31 | Armory Station: Install three 138 kV circuit breakers, 23 MVAR capacitor bank with circuit switcher, install one new 138/12 kV 25 MVA XFR with high side circuit switcher and three 12 kV feeders | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 4.2 | 4.2 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722010, P21722011 | s3139.32 | East Beckley: Install two 138 kV MOABs, install one new 138/12 kV 25 MVA XFR with a high side circuit switcher and three 12 kV feeders | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 1.2 | 1.2 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722012, P21722013 | s3139.33 | Cranberry Creek: Install one 138 kV circuit breaker, one 138 kV line MOAB, one 138/12 kV 25 MVA XFR with a high side circuit switcher and three 12 kV feeders | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 2.2 | 2.2 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP |  | s3139.34 | Cherry Creek Station: Remote end work due to the the Armory Extension cut-in | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 0 | 0 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21722019, P21722022, P21722031 | s3139.35 | North Beckley Station: Install one 138/12 kV 25 MVA XFR with three 12 kV feeders. Install one new 138 kV circuit breaker, replace existing ground switch MOAB on XFR #1 with a new 138 kV circuit switcher. Replace existing ground switch MOAB on 138/34.5 kV XFR #2 and replace existing 34.5 kV circuit breakers G and H. | Equipment Material Condition, Performance and Risk |  |  |  | 2031-06-10 |  | EP | 0 | 1.6 | 1.6 | 2023-11-17 | PM Roger Whitt |  | FALSE
Supplemental | AEP | P21577003, P21577012, P21577006 | s3140.1 | Wooster – South Coshocton: The 37.7-mile line will be rebuilt using 795 ACSR DRAKE to alleviate identified asset renewal conditions. This includes the 15.2-mile West Millersburg – Wooster 138kV circuit as well a portion of the 30.9-mile single circuit Ohio Central – West Millersburg 138kV circuit up to structure 13 outside Ohio Central station. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  | EP | 0 | 96.5 | 96.5 | 2023-10-20 | PM Pleau, Cayla / Marker, Jerod |  | FALSE
Supplemental | AEP | P21577017 | s3140.2 | Perform remote end work at Wooster | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  | EP | 0 | 0.501 | 0.501 | 2023-10-20 | PM Pleau, Cayla / Marker, Jerod |  | FALSE
Supplemental | AEP | P21577018 | s3140.3 | Perform remote end work at West Millersburg | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  | EP | 0 | 0.503 | 0.503 | 2023-10-20 | PM Pleau, Cayla / Marker, Jerod |  | FALSE
Supplemental | AEP | DR23R04B0 | s3141.1 | Snowville Station: The greenfield station will contain a 138/34.5 kV 30 MVA transformer with high side circuit switcher. There will be two 34.5 kV feeders from the station. The 138 kV side will be a straight bus with two 138 kV MOABs. | Customer Service |  |  |  | 2025-10-25 |  | EP | 0 | 0 | 0 | 2023-10-20 | Kay, Brian |  | FALSE
Supplemental | AEP | DR23R04C0 | s3141.2 | Snowville 138kV Line Extension: The line extension will tap the Claytor – Wurno - Pulaski 138kV line and bring the line in and out of the greenfield Snowville station by building 0.1 miles of greenfield double circuit 138kV line. | Customer Service |  |  |  | 2025-10-25 |  | EP | 0 | 1.48 | 1.48 | 2023-10-20 | Kay, Brian |  | FALSE
Supplemental | AEP | DR23R04C1 | s3141.3 | Snowville Fiber Line Extension: Build 2.0 miles of 144 ADSS Telecom underbuilt cable to connect Snowville station to Claytor station. | Customer Service |  |  |  | 2025-10-25 |  | EP | 0 | 0.5 | 0.5 | 2023-10-20 | Kay, Brian |  | FALSE
Supplemental | AEP | P22110005 | s3142.1 | Haviland - Van Wert: Rebuild the line to double circuit 138kV design using 1033 Curlew ACSR conductor. The line will be six wired and operated at 69kV. The rebuild will include a 2.6-mile greenfield section to route the line near several new industrial sites. The overall line length will be 10.8 miles. Newer installed poles will be re-used elsewhere. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  | EP | 0 | 27.8 | 27.8 | 2023-10-20 | Simon, Devin |  | FALSE
Supplemental | AEP | P22110012 | s3142.2 | Modify the b3359 scope from single circuit 69kV construction to double circuit 1033 Curlew at 138kV design | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  | EP | 0 | 2.89 | 2.89 | 2023-10-20 | Simon, Devin |  | FALSE
Supplemental | AEP | P22110008 | s3142.3 | Perform remote end work at Haviland | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  | EP | 0 | 1.03 | 1.03 | 2023-10-20 | Simon, Devin |  | FALSE
Supplemental | AEP | P22110009 | s3142.4 | Perform remote end work at Van Wert | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  | EP | 0 | 0.635 | 0.635 | 2023-10-20 | Simon, Devin |  | FALSE
Supplemental | AEP | PCE deemed work not needed. Do we need to submit a redline just for telecom? | s3142.5 | Upgrade telecom equipment at South Van Wert, Logtown, Maddox Creek, Timber Switch and North Delphos stations | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2026-01-01 |  | EP | 0 | 0.194 | 0.194 | 2023-10-20 | Simon, Devin |  | FALSE
Supplemental | AEP | P22744003, P22744005 | s3143.1 | Cut in/out of the existing Sporn – Tri-State 345 kV line and construct two single circuit 345 kV line extensions to a new 345 kV Station (Mercers Bottom) | Customer Service |  |  |  | 2024-10-03 |  | UC | 50 | 19.7 | 19.7 | 2023-10-03 | Jenkins, Frank |  | FALSE
Supplemental | AEP | P22744001 | s3143.2 | Construct a new 345 kV Station (Mercers Bottom) with 8 - 5000 A, 63 kA circuit breakers | Customer Service |  |  |  | 2024-10-03 |  | UC | 50 | 30.8 | 30.8 | 2023-10-03 | Jenkins, Frank |  | FALSE
Supplemental | AEP | P22744009 | s3143.3 | Remote end station work required at Sporn 345 kV | Customer Service |  |  |  | 2024-10-03 |  | EP | 15 | 0.8 | 0.8 | 2023-10-03 | Jenkins, Frank |  | FALSE
Supplemental | AEP | P22744041, P22744043 | s3143.4 | Construct two single circuit 345 kV feeds, approximately 0.75 miles each from Mercers Bottom 345 kV Station to the customer’s 345 kV Station. | Customer Service |  |  |  | 2024-10-03 |  | UC | 50 | 12.4 | 12.4 | 2023-10-03 | Jenkins, Frank |  | FALSE
Supplemental | AEP | P22744011 | s3143.5 | Cut into the existing Apple Grove – South Point 138 kV line and install a new 3-way Phase over Phase switch. Install a single circuit 0.1 mi 138 kV extension to the customer station. Install 138 kV metering at the new switch | Customer Service |  |  |  | 2024-10-03 |  | UC | 50 | 4.1 | 4.1 | 2023-10-03 | Jenkins, Frank |  | FALSE
Supplemental | AEP | P22744006, P22744034 | s3143.6 | construct a new 345 kV line from Sporn 345 kV Station to Mercers Bottom 345 kV Station, approximately 26 miles. | Customer Service |  |  |  | 2024-10-03 |  | EP | 15 | 143 | 143 | 2023-10-03 | Jenkins, Frank |  | FALSE
Supplemental | AEP | P22744022 | s3143.7 | Install a new 345 kV circuit breaker at Sporn to accommodate the new 345 kV line. | Customer Service |  |  |  | 2024-10-03 |  | EP | 15 | 2 | 2 | 2023-10-03 | Jenkins, Frank |  | FALSE
Supplemental | AEP | DP23F01B0 | s3144.1 | Install a 138kV/12kV distribution station named Kekionga on the MckinleyEllison Road 138kV line. Install 138kV line extension from Mckinley-Ellison 138kV line with fiber (~0.15 miles from the 138kV line), install 138kV bus with 2-138kV switches and 138kV MOAB. | Customer Service |  |  |  | 2025-11-12 |  | EP | 0 | 4.4 | 4.4 | 2023-08-18 | Jacobson, Seth |  | FALSE
Supplemental | AEP | DP21A01B0, DP21A01D0 | s3145.1 | At East Liverpool station, replace the 138kV MOAB/ground switch system with a circuit breaker and new relays. Install a 69kV breaker on the low side of the 138-69kV transformer. Upgrade tie-line metering, relays, and expand SCADA functionality at the station. Replace the control house with a new prefabricated control building. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-05-01 |  | EP | 0 | 3 | 3 | 2023-08-18 | Sides, Todd |  | FALSE
Supplemental | AEP | DP21A01D1, DP21A01D0 | s3145.2 | At the 69kV remote end station of Second Street, replace the electromechanical relays and pilot wire communications with microprocessor-based relays, to coordinate with East Liverpool. Install new 69kV CCVT’s. | Equipment Material Condition, Performance and Risk¦Operational Flexibility and Efficiency |  |  |  | 2025-05-01 |  | EP | 0 | 0.3 | 0.3 | 2023-08-18 | Sides, Todd |  | FALSE
Supplemental | AEP | P22012052, A20705029 | s3147.1 | Coleman - Peter Creek 69kV line - Install new 69kV line with OPGW from Coleman station to Peter Creek Station. Total line length 5.8 miles. Rebuilding within the existing ROW, but some new ROW will be required to get from Coleman station to Peter Creek station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 19.2 | 19.2 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012057 | s3147.2 | Peter Creek - Wharncliffe 69kV line - Install new 69kV line with OPGW from the KY/WV State Line to Peter Creek Station. Total line length 0.1 miles. New ROW will be required to get from the WV/KY state line to Peter Creek station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.3 | 0.3 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012049, P22012048 | s3147.3 | Peter Creek - Wharncliffe 69kV line - Install new 69kV line with OPGW from the KY/WV State Line to Wharncliffe Station. Intermediate station includes Bear Creek. Includes switching structures Devil Anse and Briar Mt. for Transmission customers and their delineation poles. Total line length 12.7 miles. Rebuilding within the existing ROW, but some new ROW will be required to get from the WV/KY state line to Devil Anse S.S. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 44.7 | 44.7 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012004, P22012029 | s3147.4 | Devi Anse S.S. Metering - One 69kV meter for the Transmission customer and one 69kV meter facing the WV/KY state line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.5 | 0.5 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012014 | s3147.5 | Briar Mt. S.S. Metering - One 69kV metering structure for the Transmission customer. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.9 | 0.9 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012056 | s3147.6 | Huff Creek - Wharncliffe 46kV line - The remove the span into the takeoff and the first structure 556-109 then reterminate the line into the new station takeoff structure on the Huff Creek – Wharncliffe 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.25 | 0.25 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012031 | s3147.7 | Tug Fork - Wharncliffe 69kV line - Install a new single circuit 69kV with OPGW line from existing Wharncliffe station to Tug Fork station totaling 5.9 miles long. Also reusing 2.3 miles of the Jim Branch – Wharncliffe line asset at 69kV that was rebuilt in 2007. Create 2.2 miles of greenfield ROW and reuse 3.7 miles of existing ROW from Tug Fork to Wharncliffe stations. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 24.3 | 24.3 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012026, P22012028 | s3147.8 | Lester Fork - Tug Fork 69kV line - Install a new single circuit 69kV with OPGW line from Lester Fork to Tug Fork stations crossing the VA/WV state border totaling 8.0 miles long. Create greenfield ROW from Lester Fork to Tug Fork stations crossing the VA/WV state border. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 33.9 | 33.9 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012059 | s3147.9 | Looney Creek - Lester Fork 69kV line - Install new 69kV line with OPGW from structure 343-1A to the new Lester Fork Station at 0.25 miles. Remove structure 343-1 and the span into the Hurley Station at 0.1 miles. Create greenfield ROW from structure 343-1A to Lester Fork station at 0.25 miles. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 2.51 | 2.51 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012054 | s3147.10 | Rapoca 69kV Customer - Replace the Rapoca Station hard tap from the Hurley - Looney 69kV circuit with a Phase over Phase switch. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.7 | 0.7 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012010 | s3147.11 | Bear Creek Station - Two 69kV MOABs that are automatic, and SCADA controlled for the Bear Creek 69kV work. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.9 | 0.9 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012035 | s3147.12 | Wharncliffe Station - Upgrade the existing Wharncliffe station to 69kV. One 69kV Capacitor bank that is 11.5 MVAR and circuit switcher. One 69/46kV 50 MVA transformer and one 46kV circuit breaker facing Gilbert on the low side of the transformer. Reusing the existing three Transmission circuit breaker for the high side of the transformer and lines facing Tug Fork and Briar Mt. S.S. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 5.9 | 5.9 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | DR22H03B0, DR22H03Y0 | s3147.13 | Tug Fork Station - Two 69kV circuit breakers with one facing Wharncliffe and the other facing Lester Fork stations. Includes 69kV bus work. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 2.1 | 2.1 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012025 | s3147.14 | Lester Creek Station - One 69kV meter facing Tug Fork for the state line crossing. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.3 | 0.3 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012027 | s3147.15 | Looney Creek Station - Replace the existing 69kV MOAB facing Lester Fork with a 69kV circuit breaker. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 1.2 | 1.2 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | A20705028 | s3147.16 | Sprigg - Barrenshe 69kV line - Remove approximately 6.9 miles of Sprigg - Barrenshe 69kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.024 | 0.024 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | A20705029 | s3147.17 | Barrenshe – Coleman 69kV line - Remove approximately 6.2 miles of Barrenshe - Coleman 69kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.024 | 0.024 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012011, A20705030 | s3147.18 | Sprigg - Wharncliffe 46kV line - Remove approximately 1.29 miles of Sprigg - Wharncliffe 46kV line in KY. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 1.1 | 1.1 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | A20705030 | s3147.19 | Sprigg - Wharncliffe 46kV line - Remove approximately 18.3 miles of Sprigg - Wharncliffe 46kV line in WV and remove the Grapevine Switching Structure. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 14.2 | 14.2 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012006, A20705048, P22012005 | s3147.20 | Jim Branch - Wharncliffe 46kV line - Remove approximately 19.7 miles of Jim Branch - Wharncliffe 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 15.3 | 15.3 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012021, A20705050 | s3147.21 | Hardy Tap 46kV line - Remove approximately 2.0 miles of the Hardy Tap 46kV line and remove the Hardy Switching Structure. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 1.9 | 1.9 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | A20705051 | s3147.22 | Panther Tap 46kV line - Remove approximately 0.7 miles of the Panther Tap 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.69 | 0.69 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012040 | s3147.23 | Briar Mt. Tap 46kV line - Remove approximately 0.1 miles of the Briar Mt. Tap 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.12 | 0.12 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012050 | s3147.24 | Grapevine Tap 46kV line - Remove approximately 0.1 miles of the Grapevine Tap 46kV line. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.45 | 0.45 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012017 | s3147.25 | Jim Branch station Removal - Remove the 46kV Circuit Breaker P facing Panther and the Grounding Bank. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.087 | 0.087 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012037, where is rebuild BPID? | s3147.26 | Sprigg Station: Remove all the 46kV bus and attached equipment. Remove the 138/69 – 46kV transformer and the 46/7.2KV GND Bank. Remove the 69kV bus and attached equipment. Remove the 138kV equipment. Rebuild the station as a four 138kV circuit breaker ring bus station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 5 | 5 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012001 | s3147.27 | Coleman Station - Replace 69kV circuit breaker H towards Peter Creek and risers. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | A20705033 | s3147.28 | Barrenshe Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012002 | s3147.29 | Peter Creek Station - A new Distribution station that is replacing Barrenshe station that has a MOAB that is Scada controlled facing Coleman and a 69kV circuit breaker facing Devil Anse S.S. One 69kV circuit switcher and a 20 MVA 69/12kV Transformer and 4 Distribution feeders. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012053, A20705024 | s3147.30 | Grapevine Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012010, P22012008 | s3147.31 | Bear Creek Station - A new Distribution station that is replacing Grapevine station that has one 69kV circuit switcher and a 20 MVA 69/34kV Transformer and two Distribution feeder. Also helping to break up a large Distribution circuit out of Pigeon Creek station. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012041 | s3147.32 | Briar Mt. Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012042 | s3147.33 | Bens Creek Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012043 | s3147.34 | Wharncliffe Station - Add one 69kV circuit switcher and a 20 MVA 69/12kV transformer and one Distribution feeder to pick up the load from the retired Bens Creek and Briar Mt. stations. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | DR22H03B0 | s3147.35 | Tug Fork Station - A new Distribution station that is replacing Hardy and Panther stations that has one 69kV circuit switcher and a 20 MVA 69/12kV Transformer and three Distribution feeder. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | DR22H03B1, DR22H03B2 | s3147.36 | Hardy and Panther Stations - Removal of the Distribution stations and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012022 | s3147.37 | Lester Fork Station - A new Distribution station that is replacing Hurley station that has two MOABs that are Scada controlled, one 69kV circuit switcher and a 20 MVA 69/12kV Transformer and three Distribution feeder. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012063, A20001431 | s3147.38 | Hurley Station - Removal of the Distribution station and equipment. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0 | 0 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22012039 | s3147.39 | Build 2 fiber station transitions using OPGW at Coleman and Peter Creek stations. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.2 | 0.2 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP |  | s3147.40 | Build 4 fiber station transitions using OPGW at Devil Anse S.S. Bear Creek, Briar Mt. S.S. and Wharncliffe. | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 0.7 | 0.7 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP |  | s3147.41 | Lester Fork – Wharncliffe Fiber - Build 3 fiber station transitions using OPGW at Tug Fork, Wharncliffe and Lester Fork. Remove one of the existing shield wires and replace it with an OPGW at 2.3 miles on the Jim Branch – Wharncliffe line asset that is being reused from 2007 | Equipment Material Condition, Performance and Risk¦Customer Service |  |  |  | 2030-06-01 |  | EP | 0 | 5.1 | 5.1 | 2023-08-18 | Smith, M Shawn |  | FALSE
Supplemental | AEP | P22045003 | s3148.1 | Sorenson - Desoto 345kV: Rebuild the ~51.5 mile line as is using double circuit 345kV construction. Replace jumpers at Sorenson and Desoto to accommodate the new structure entrances at the stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-06-10 |  | EP | 0 | 202.4 | 202.4 | 2023-08-08 |  |  | FALSE
Supplemental | AEP | TP2021264 | s3211.1 | Construct a new 69 kV line from the existing Looney Creek station to the greenfield Conaway station, approximately 6.1 miles long. New right of way is needed from Looney Creek to Conaway station. The line cost is driven by very steep terrain and the miles of access roads required and access road restoration cost, which is a requirement in Virginia. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  | EP | 0 | 30.2 | 30.2 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | TP2021264 | s3211.2 | Construct a greenfield station (Conaway) to replace Big Rock and Thomas stations. Conaway will contain a 69/12 kV 20 MVA transformer with high side circuit switcher. There will be two 12 kV feeders from the station. The 69 kV side will be a straight bus with 69 kV MOABs. Distribution work is required to reconnect the Distribution system to the new Conaway station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | TP2021264 | s3211.3 | At the existing Looney Creek station, a new 69 kV circuit breaker will be installed to connect the Conaway – Looney Creek 69 kV line. Replace the high side 138kV MOAB ground switch with a 138 kV circuit breaker due to protection and control at the station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  | EP | 0 | 2.44 | 2.44 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | TP2021264 | s3211.4 | Remove the ~6.4 mile long Big Rock – Grundy 34.5 kV line. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  | EP | 0 | 5.08 | 5.08 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | TP2021264 | s3211.5 | Remove 34.5 kV circuit breaker “D” and 34.5 KV circuit breaker “C” at Grundy station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  | EP | 0 | 0.4 | 0.4 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | TP2021264 | s3211.6 | Remove the Big Rock station and equipment. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | TP2021264 | s3211.7 | Remove the Thomas station and equipment. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-05-01 |  | EP | 0 | 0 | 0 | 2022-11-18 |  |  | FALSE
Supplemental | AEP | DP25C03B0 | s3212.1 | A new 69/12 kV distribution station (Vision) will be constructed. The station will be an in and out design utilizing in line MOAB's | Customer Service |  |  |  | 2024-12-31 |  | EP | 25 | 1.12 | 1.12 | 2023-03-17 | Waite, Karmyn |  | FALSE
Supplemental | AEP | DP25C03W0 | s3212.2 | Work will be performed on the West Van Wert – Cavett 69 kV circuit to cut in the newly proposed Vision station . | Customer Service |  |  |  | 2024-12-31 |  | EP | 25 | 2.99 | 2.99 | 2023-03-17 | Waite, Karmyn |  | FALSE
Supplemental | AEP | DP22C23B0 | s3213.1 | Construct a greenfield station “Milepost”, utilizing three 138kV 63kA 3000A circuit breakers configured in a ring to serve new customer loads. | Customer Service |  |  |  | 2024-04-15 |  | EP | 25 | 4.54 | 4.54 | 2023-03-17 | Caldwell, Colton |  | FALSE
Supplemental | AEP | DP22C23C0 | s3213.2 | Cut into the Roberts - Trabue 138 kV circuit and construct a new 0.14-mile double circuit 138kV in and out line to the new Milepost station utilizing 795 ACSR conductor SE: 360 MVA. | Customer Service |  |  |  | 2024-04-15 |  | EP | 25 | 2.79 | 2.79 | 2023-03-17 | Caldwell, Colton |  | FALSE
Supplemental | AEP | DP22C23D2, DP22C23Z1, DP22C23Z2 | s3213.3 | Remote end work to accommodate the above work at Cole, Roberts, & Trabue. | Customer Service |  |  |  | 2024-04-15 |  | EP | 25 | 0.17 | 0.17 | 2023-03-17 | Caldwell, Colton |  | FALSE
Supplemental | AEP | P24003008 | s3213.4 | Retire 3.3 miles of the Bethel Rd – Hilliard 69 kV line from Bethel Rd to the structure adjacent to Davidson 69 kV. Build a 0.3-mile extension connecting the line from Hilliard to Davidson using 795 ACSR conductor creating the Hilliard – Davidson 69 kV circuit. | Customer Service |  |  |  | 2024-04-15 |  | EP | 0 | 2.92 | 2.92 | 2023-03-17 | Pleau, Cayla |  | FALSE
Supplemental | AEP | P24003001 | s3213.5 | Retire Bethel Road 138/69/13.8 kV Transformer #3 and associated breakers. Install a new 138/69 kV transformer at Davidson station with a high side MOAB and a single 69kV 3000A 40kA breaker on the low side connecting to the reconfigured Davidson - Hilliard 69 kV circuit. | Customer Service |  |  |  | 2024-04-15 |  | EP | 0 | 1.58 | 1.58 | 2023-03-17 | Pleau, Cayla |  | FALSE
Supplemental | AEP |  | s3213.6 | Upgrade Sub Cond 477 AAC 19 Str. at Blaire 69 kV. | Customer Service |  |  |  | 2024-04-15 |  | EP | 0 | 0.05 | 0.05 | 2023-03-17 |  |  | FALSE
Supplemental | AEP | P22768001 | s3214.1 | Install new 138kV phase-over-phase switch on the Corwin-Lick 138kV circuit. Install metering towards Veterans. | Customer Service |  |  |  | 2024-12-31 |  | EP | 25 | 0.67 | 0.67 | 2023-07-21 | Bachtel, Cole |  | FALSE
Supplemental | AEP | P22768004 | s3214.2 | Install ~0.3 miles of line from Pattonsville Switch to Veterans. | Customer Service |  |  |  | 2024-12-31 |  | EP | 25 | 0.45 | 0.45 | 2023-07-21 | Bachtel, Cole |  | FALSE
Supplemental | AEP | P22768005 | s3214.3 | Modify existing line to accommodate switch installation. | Customer Service |  |  |  | 2024-12-31 |  | EP | 25 | 0.32 | 0.32 | 2023-07-21 | Bachtel, Cole |  | FALSE
Supplemental | AEP | P22768007 | s3214.4 | Heppner-Lick 138 kV: Remove span of line from City of Jackson’s Lick station toward Veterans. | Customer Service |  |  |  | 2024-12-31 |  | EP | 25 | 0.1 | 0.1 | 2023-07-21 | Bachtel, Cole |  | FALSE
Supplemental | AEP | P22036004 | s3215.1 | A new 138 kV double circuit line extension will be built from the existing Jim Branch – Switchback line between Gary and Thorpe stations to the greenfield Coalfields stations, approximately 2.0 miles, creating an in and out. New right of way is needed from the new tap structure to Coalfields station. The line cost is driven by very steep terrain and the miles of access roads required. The line will require marker balls and helicopter installation due to the valleys and terrain. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  | EP | 0 | 13 | 13 | 2022-04-20 | Cooper, Wayne |  | FALSE
Supplemental | AEP | P22036001, P22036008 | s3215.2 | The 138kV high side of Coalfields station will be a 138kV straight bus with two automatic MOAB switches. The greenfield station will contain a 138/12 kV 20 MVA transformer with high side circuit switcher. There will be three 12 kV feeders from the station. Distribution work will be required to reconnect the Distribution system to the new Coalfields station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  | EP | 0 | 1.65 | 1.65 | 2022-04-20 | Cooper, Wayne |  | FALSE
Supplemental | AEP | P22036003 | s3215.3 | Work required to tap the existing Jim Branch – Switchback 138kV line asset. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  | EP | 0 | 1.8 | 1.8 | 2022-04-20 | Cooper, Wayne |  | FALSE
Supplemental | AEP | P22036010, P22036011, P22036012, P22036013 | s3215.4 | Remote end work required at Trail Fork, Tazewell, Clark Branch and Baileysville stations. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  | EP | 0 | 0.38 | 0.38 | 2022-04-20 | Cooper, Wayne |  | FALSE
Supplemental | AEP | A20045017 | s3215.5 | Remove the Transmission station and equipment at Carswell station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  | EP | 0 | 2.86 | 2.86 | 2022-04-20 | Cooper, Wayne |  | FALSE
Supplemental | AEP | A20045013, A20045014 | s3215.6 | Remove the Carswell 138kV Loop at ~1.4 miles and the Carswell – Gary 88kV Line at ~2.5 miles. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  | EP | 0 | 5.15 | 5.15 | 2022-04-20 | Cooper, Wayne |  | FALSE
Supplemental | AEP | A20045018 | s3215.7 | Remove the Distribution station and equipment at Belcher Mountain station. | Equipment Material Condition, Performance and Risk |  |  |  | 2028-11-01 |  | EP | 0 | 0 | 0 | 2022-04-20 | Cooper, Wayne |  | FALSE
Supplemental | AEP | DP24C09Z0 | s3301.1 | At Mink station, install 2 – 138kV, 3000 A, 63 kA breakers in the breaker and half configuration and associated work to terminate two new distribution transformers. | Customer Service |  |  |  | 2025-05-20 |  | UC | 26 | 2.7 | 2.7 | 2023-07-21 | PM Colton Caldwell |  | FALSE
Supplemental | AEP | DP24F01Y0 | s3302.1 | Install a 69 kV 23 MVAR capacitor bank at Price station and a 69 kV circuit breaker. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 15 | 1.5 | 1.5 | 2024-02-16 | PM Ijeoma Gilbert / Planner Andrew Morchik |  | FALSE
Supplemental | AEP | DP24F01D0 | s3302.2 | Install a temporary, mobile 69 kV 14.4 MVAR capacitor bank at Winchester station to mitigate low voltage violations in the Winchester area. The mobile capacitor bank at Winchester will be removed when project s2273 Randolph upgrades are completed. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-05-01 |  | EP | 15 | 0.02 | 0.02 | 2024-02-16 | PM Ijeoma Gilbert / Planner Andrew Morchik |  | FALSE
Supplemental | AEP | DP23F04B0 | s3302.3 | Install a 69/4 kV 12.5 MVA transformer and a 69 kV high side circuit switcher. |  |  |  |  | 2026-03-23 |  | EP | 15 | 0 | 0 | 2024-02-16 | PM Ijeoma Gilbert / Planner Andrew Morchik |  | FALSE
Supplemental | AEP |  | s3303.1 | At Gund Metering Point, install new revenue metering for a 20 MW customer load connection. Install a new 69kV manual switch on the customer side of the hard tap. | Customer Service¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 1.15 | 1.15 | 2024-03-15 |  |  | FALSE
Supplemental | AEP |  | s3303.2 | At Bevins Metering Point, motorize the existing switch at Bevins towards Gund to facilitate the connection of a 7 MW customer load to existing delivery point. | Customer Service¦Operational Flexibility and Efficiency |  |  |  | 2024-11-15 |  | EP | 0 | 0.59 | 0.59 | 2024-03-15 |  |  | FALSE
Supplemental | AEP | P23705001, P23705003, P23705007 | s3304.1 | Install a 3-way phase over phase switch on the Sorenson-Van Buren 138kV circuit. From the new switch, install a ~2.5 mile 138kV line to the customer delivery point. Low-side metering will be installed in the customer owned station. | Customer Service |  |  |  | 2026-10-01 |  | EP | 15 | 9.4 | 9.4 | 2024-03-15 | Felt, Tyler |  | FALSE
Supplemental | AEP | P23127001 | s3305.1 | Sifford Station: Sifford station will be built out to accomodate two new 138 kV feeds to the customer. This will include the installation of 4-3000A 40kA 138 kV circuit breakers and associated equipment. | Customer Service |  |  |  | 2024-09-30 |  | EP | 15 | 6.373 | 6.373 | 2024-03-15 | Rhoades, Isaac |  | FALSE
Supplemental | AEP | P23127004 | s3305.2 | Sifford – Ruble #2 138 kV Feed A: Install 138 kV line extension from AEP’s Sifford station to serve the customer’s station located just south of the Sifford station. | Customer Service |  |  |  | 2024-09-30 |  | EP | 15 | 2.948 | 2.948 | 2024-03-15 | Rhoades, Isaac |  | FALSE
Supplemental | AEP | P23127004 | s3305.3 | Sifford – Ruble #2 138 kV Feed B: Install a second 138 kV line from AEP’s Sifford station to serve the customer’s station located just south of the Sifford station to meet customer’s redundancy requirements at the site. | Customer Service |  |  |  | 2024-09-30 |  | EP | 15 | 0 | 0 | 2024-03-15 | Rhoades, Isaac |  | FALSE
Supplemental | AEP | P23013002 | s3306.1 | Huntington Court Station: Replace 69 kV circuit breakers “E”, “H”, and “M” and previously identified electromechanical and legacy microprocessor relaying. Install high-side circuit switcher on 138/12 kV T2 and low-side breaker on 138/34.5 kV T4 | Equipment Material Condition, Performance and Risk |  |  |  | 2025-11-30 |  | EP | 15 | 0 | 0 | 2024-03-15 | Jackson, Paul |  | FALSE
Supplemental | AEP |  | s3307.1 | Replace existing 69 kV MOABs “W” and “Y” with new 69 kV circuit breakers, new 69 kV box bay and transclosure to house the new relaying. Estimated Cost: $0 (Distribution) | Customer Service |  |  |  | 2025-06-17 |  | EP | 0 | 0 | 0 | 2024-03-15 |  |  | FALSE
Supplemental | AEP |  | s3307.2 | The existing 69 kV MOAB switch is located on the opposite side of the street from the station requiring a new 69 kV “in and out” line extension (two spans, separate structures) from the existing line to the new 69 kV box bay. | Customer Service |  |  |  | 2025-06-17 |  | EP | 15 | 1.4 | 1.4 | 2024-03-15 |  |  | FALSE
Supplemental | AEP | P22923005, P22923009 | s3308.1 | West Lancaster – South Baltimore – West Millersport 138 kV : Rebuild ~14.4 miles of the line between West Lancaster and West Millersport stations using 1033 ACSS 54/7 conductor. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  | EP | 15 | 38.7 | 38.7 | 2024-03-15 | Howard, Robert |  | FALSE
Supplemental | AEP | P22923001 | s3308.2 | West Lancaster Station: Replace existing bus and line risers at the station, upgrade line relays. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  | EP | 15 | 1 | 1 | 2024-03-15 | Howard, Robert |  | FALSE
Supplemental | AEP | P22923002 | s3308.3 | South Baltimore Station: Replace existing bus and line risers at the station, upgrade line relays. While at the station some additional site concerns such as the existing fence will be addressed. | Equipment Material Condition, Performance and Risk |  |  |  | 2026-10-31 |  | EP | 15 | 0.7 | 0.7 | 2024-03-15 | Howard, Robert |  | FALSE
Supplemental | AEP | P23130018, P23130011, P23130012 | s3309.4 | Rebuild 3.2 miles of 69kV from AEP-Marathon to Trinity with 954ACSS/TW, AEP to build Burr Oak 3 terminal 69kV ring. This tie will provide improved reliability for WVPA’s Trinity and Mt Zion stations as well as to AES-Marathon that is currently served on a long radial. Conductor rating: 196MVA/212MVA SN/SE | Customer Service |  |  |  | 2027-12-31 |  | EP | 15 | 6.5 | 6.5 | 2024-03-15 | Glover, Grant |  | TRUE
Supplemental | AEP | P23130001, P23130007, P23130006 | s3309.5 | To help facilitate a new network connection from AEP to WVPA to Dayton, build a new 4-69 kV circuit breaker ring bus. The following cost includes the new station construction, property purchase, metering, remote end relay upgrades, the Portland – Marathon 69 kV line connection, Marathon – Berne 69 kV line connection and Trinity radial line AEP removal. | Customer Service |  |  |  | 2027-12-31 |  | EP | 15 | 8.7 | 8.7 | 2024-03-15 | Glover, Grant |  | TRUE
Supplemental | AEP | A20045027 | s3387.1 | Replace existing 138 kV circuit breakers A, B, C, and D with four new 138 kV 3000 A 40 kA circuit breakers and install a new a new 138 kV 3000 A 40 kA circuit breaker between Wolf Hills 138 kV Bus #1 and Wolf Hills 138 kV Bus #2. Upgrade control house and install primary and backup station service. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-09-10 |  | EP | 15 | 5.3 | 5.3 | 2024-05-17 | Burns, Blair |  | FALSE | A | 40 | 40 | Wolf Hills Bus Tie |  | 285/337/377/438
Supplemental | AEP |  | s3388.1 | Remove an existing wood pole structure on the Raikes Branch customer delivery line and install a new pole that will have the new metering equipment. This cost is reimbursable from the customer; the previous delivery point switches are still in good condition and do not need replaced. | Equipment Material Condition, Performance and Risk |  |  |  | 2024-10-03 |  | EP | 0 | 0 | 0 | 2024-05-17 |  |  | FALSE |  |  |  | Raikes Branch-Coronado Load |  | 50/50/63/63
Supplemental | AEP | P23828001, P23828003 | s3389.1 | Install a 3-way switch, with SCADA, on Albion-Robison Park 138kV circuit. From the new switch, install a ~0.01 mile 138kV line radial to customer station at 138kV. Low-side metering will be installed in the customer owned station. | Equipment Material Condition, Performance and Risk |  |  |  | 2025-06-19 |  | EP | 15 | 3.2 | 3.2 | 2024-07-19 | Felt, Tyler |  | FALSE |  |  |  | Hathaway-Laotto Switch 138 kV |  | 257/360/325/404
Supplemental | AEP | P23836001, P23836003 | s3390.1 | Install a 3-way switch, with SCADA, on Albion- Robison Park 138kV circuit. From the new switch install a ~0.2 mile 138kV line radial to customer delivery 138kV. Low-side metering will be installed in the customer owned station. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  | EP | 15 | 4.5 | 4.5 | 2024-07-19 | Vecchiarelli, Katherine |  | FALSE |  |  |  | Hatch Switch-Laotto Switch 138 kV |  | 257/360/325/404
Supplemental | AEP | AEP-2022-OH071 | s3440.1 | Cyprus 345/138 kV: Cyprus is the station that was originally developed (s2526) to serve 675 MW of demand with room for 345 kV expansion based on LOA with the customer. Cut into the Beatty – Bixby 345 kV circuit and construct ~1.6 miles of double circuit line, utilizing 2-bundled ACSR Bittern 1272 conductor, SE rating 2278 MVA, to a new 345 kV ring bus at Cyprus station with (4) 5000 A, 63kA circuit breakers, (2) 345/138/34.5 kV, 675 MVA transformers, (12) 4000 A, 63kA, 138 kV circuit breakers, (1) 69.1 MVAR 138 kV Cap bank. Construct (2) 138 kV single circuit, ~0.4 miles, & (2) double circuit, ~0.9 miles, tie lines to the customers dead end structures utilizing ACSR Drake 795 (26/7) conductor SE 360 MVA. Modify the existing Cyprus 138kV Extension & Parsons 138kV circuits #1 & 2 structures to accommodate a fence relocation. Remote end relay upgrades are required at Beatty & Bixby 345 kV stations. | Customer Service |  |  |  | 2024-11-13 |  | EP | 0 | 46.9 | 46.9 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH071 | s3440.2 | Parsons 138 kV: Install (1) 69.1 MVAR cap bank to resolve N-1-1 voltage issues | Customer Service |  |  |  | 2025-07-24 |  | EP | 0 | 2 | 2 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH071 | s3440.3 | Beatty – Canal 138 kV line Sag Re-rate: The Beatty – Canal 138 kV line flagged as overloading under N-1-1 scenarios after the addition of the new load at Cyprus. The line will be flown to address sag issues that are limiting its current rating. It is anticipated that several structures will need to be replaced in order to rase the rating of the line. | Customer Service |  |  |  | 2025-07-24 |  | EP | 0 | 5.5 | 5.5 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH071 | s3440.4 | Waverly Reactor 138 kV: Install a 4% series reactor towards Rozelle at Waverly station to address a N-1-0 scenario related to the loss of a nearby 345 kV line. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 3 | 3 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH071 | s3440.5 | Saint Clair Avenue Reactor 138 kV: Adjust tap settings on reactors towards Mound and Clinton stations to 3%. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 0 | 0 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH071 | s3440.6 | Marion Station: Replace switch and line riser at Marion station towards Obetz to address loading concern under certain N-1-1 scenario related to customer interconnections in the area | Customer Service |  |  |  | 2027-12-01 |  | EP | 0 | 0.1 | 0.1 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH049 | s3441.1 | Construct a greenfield Jerome station with (10) 138kV 63kA 4000A circuit breakers in breaker and half bus configuration. Construct ~ 2.5 miles of double circuit 138kV transmission line extending from Kileville station to Jerome utilizing 2-bundled ACSS Cardinal 954 (45/7) conductor, SE rating 1061 MVA. Construct (4) 138 kV tie lines to the customers dead end structures ~0.05 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. Customers will be directly connected at this station | Customer Service |  |  |  | 2025-01-30 |  | EP | 0 | 30 | 29.78 | 2024-12-13 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH024 | s3441.2 | Beacon 345 kV: Construct a greenfield station with (8) 5000 A, 345 kV, 63 kA circuit breakers & & (1) 158.4 MVAR 345 kV Cap bank in a breaker and a half configuration. Cut into the 345 kV Hayden – Roberts No. 2 circuit with two single circuit 345 kV lines ~0.2 miles terminating into Beacon station; utilizing 2-bundle ACSR Rail 954 (45/7) conductor SE 1887 MVA. A structure will need be installed to raise the Hayden – Roberts No 1 circuit. Construct three single circuit lines ~0.1 miles, between Beacon and the customer; utilizing 2-bundle ACSR Drake 795 (26/7) conductor SE 1800 MVA. | Customer Service |  |  |  | 2024-11-21 |  | EP | 0 | 40 | 40 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH035 | s3441.3 | Cosgray 345 kV: Expand the existing Cosgray ring bus (originally proposed under s2653) station by installing (2) 5000 A, 63 kA, 345 kV circuit breakers. Construct two ~0.06 miles single circuit lines to connect the new customer deliveries to Cosgray. | Customer Service |  |  |  | 2024-06-14 |  | EP | 0 | 5.1 | 5.1 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH041 | s3441.4 | Originally, Kileville is the station that was envisioned (s2855) to serve 461 MW of demand with room for 345 kV expansion based on LOAs with the customer. However, land in the area of the proposed Kileville station was not available for expansion to install 345/138 kV transformation. Therefore, a new station site called Celtic is being proposed to serve as the 345 kV source for the 461 MW of load to be served in this area. Cut into the Hayden – Hyatt 345 kV circuit, reroute ~0.8 miles of the circuit and extend ~1.1 miles of new double circuit line, utilizing 2-bundled ACSR Pheasant 1272 (54/19) conductor, SE rating 2413 MVA, to the greenfield Celtic 345/138 kV station with (4) 345 kV, 63 kA, 5000 A breakers laid out as ring bus configuration on high side. Install two 675MVA-345/138 kV power transformers. Install (8 6) 138kV, 63 kA, 4000 A breakers & (2) 69.1 MVAR 138 kV Cap bank on low side configured as breaker-and-a-half bus with provisions for future expansion . The proposed Kileville – Jerome 138 kV line will be brought in and out of the station creating two 138 kV Celtic – Jerome circuits and a single Celtic – Kileville 138 kV circuit. | Customer Service |  |  |  | 2025-11-13 |  | EP | 0 | 60 | 70.31 | 2024-12-13 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH041 | s3441.5 | Kileville 138 kV: Expand Kileville station (originally proposed under s2855) with (4) additional 63 kA, 4000A circuit breakers in breaker and half bus configuration. Construct (2) 138 kV tie lines to the customers dead end structures ~0.05 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. Customers will be directly connected at this station. | Customer Service |  |  |  | 2024-04-01 |  | EP | 0 | 4.1 | 4.1 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH049, AEP-2022-OH024, AEP-2022-OH035, AEP-2023-OH041 | s3441.6 | Beatty – Wilson 138 kV line Sag Re-rate: Due to new customer interconnections in the area the Beatty – Wilson, Beatty – Bolton, Bolton – Hall and Hall - Wilson 138 kV circuits will overload for certain N-1-1 scenarios. Structures will be replaced on the line to address distribution clearance issue in order to allow the lines to operate to their conductor’s designed maximum operating temperature. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 1.5 | 1.5 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH049, AEP-2022-OH024, AEP-2022-OH035, AEP-2023-OH041 | s3441.7 | Dublin Reactor 138 kV: Install a 4% series reactor towards Sawmill at Dublin station to address a N-1-1 scenario as a result of the new load interconnections in the area. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 3 | 3 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023 | s3442.1 | Badger 138 kV: Cut into the Green Chapel – Jug 138 kV circuit and extend ~ 0.1 miles of new double circuit line, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 1118 MVA , to the greenfield Badger station with (10) 80 kA, 4000 A breakers & (1) 69.1 MVAR 138 kV Cap bank, laid out as breaker and a half for future expansion to 6 strings. Construct 4 - 138 kV tie lines to the customers dead end structures ~.05 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA | Customer Service |  |  |  | 2024-11-24 |  | EP | 0 | 18.43 | 18.43 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH034 | s3442.2 | QTS North 138 kV: Construct ~0.3 miles of double circuit & a single circuit radial 138 kV tie lines from Anguin station to QTS Customer’s site dead-end structures serving transformers #1, #2 # 3, each utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. | Customer Service |  |  |  | 2024-03-25 |  | EP | 0 | 1.8 | 1.8 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH036 | s3442.3 | Innovation 345/138 kV: Cut into the Corridor - Conesville 345 kV circuit and construct ~0.1 miles of double circuit line, utilizing 2-bundled ACSR Bittern 1272 conductor, SE rating 2278 MVA, to a new 345 kV ring bus at Innovation station (s2578) with (4) 5000 A, 63kA circuit breakers, (2) 345/138/34.5 kV, 675 MVA transformers, (15) 4000 A, 80, kA, 138 kV circuit breakers, (2) 69.1 MVAR, 138 kV Cap banks. Upgrade the line protection relays at Conesville & Corridor 345 kV. Construct (2) 138 kV tie lines to the customers dead end structures ~0.04 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. | Customer Service |  |  |  | 2026-06-24 |  | EP | 0 | 53.7 | 53.7 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH045 | s3442.4 | Horizon 138 kV: Construct a greenfield station with (8) 80 kA, 4000 A circuit breakers in breaker and half bus configuration. Construct ~ 0.05 miles of double circuit 138kV transmission line extending from the Jug St.- Green Chapel 138 kV circuit to Horizon station utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 1118 MVA. | Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 10.81 | 10.81 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH046 | s3442.5 | Jorden 138 kV: Cut into the Innovation – Kirk 138 kV circuit with two single circuit 138 kV lines ~0.35 miles terminating into Jorden station, utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor, SE rating 1123 MVA, to Construct a greenfield 138 kV 4-CB ring bus station, configurable to 4-strings breaker and half station in future, with (4) 4000 A, 80 kA circuit breakers. Construct two single circuit 138kV lines ~0.1 miles, between Jorden and the customer. | Customer Service |  |  |  | 2026-07-10 |  | EP | 0 | 12.5 | 12.5 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH075 | s3442.6 | QTS South 138 kV: Cut into one of the circuits of Anguin – Brie 138 kV line and extend ~0.1 miles of two single circuit lines, utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor, SE rating 1123 MVA , to the greenfield Macy station with (4) 80 kA, 4000 A breakers laid out as 4-CB ring bus. Construct (2) 138 kV tie lines to the customers dead end structures ~0.04 miles utilizing ACSR Dove 556.5 (26/7) conductor SE 284 MVA. | Customer Service |  |  |  | 2024-07-31 |  | EP | 0 | 9.54 | 9.54 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH075 | s3442.7 | Brie – Innovation 138 kV Tie: Construct a greenfield ~1.75 mile of double circuit line, utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor, connecting Brie and Innovation stations as well as re-establish the Babbitt - Kirk 138 kV circuit. At Brie 138 kV station will install four 138 kV circuit breakers in two partial strings breaker and half configuration along with a 69.1 MVAR capacitor. Perform remote end work at Innovation, Babbitt, and Kirk 138 kV stations. This project addresses a consequential (for a N-1-1 contingency) load drop event of more than 300 MW for the loads served out of AEP’s Anguin and Brie stations while also addressing an overload on the Babbitt – Innovation 138 kV circuit in relation to new customer interconnections in the area | Customer Service |  |  |  | 2025-07-31 |  | EP | 0 | 10.8 | 10.8 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH077 | s3442.8 | Curleys 345 kV: Cut into the rerouted Corridor – Innovation 345 kV circuit, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 2278 MVA, to a new 345 kV Curleys station with (14) 5000 A, 63kA circuit breakers & (2 1) 158.4 MVAR 345 kV Cap bank, laid out as breaker and a half for future expansion to 3 strings with future configurations to build up to total (10) breaker and half strings. Construct four single circuit lines ~0.1 miles, between Curleys station and the customer; utilizing 2-bundle ACSR Drake 795 (26/7) conductor SE 1800 MVA. The rerouted line, built as double circuit, will establish two 345 kV ties between Bermuda and Curleys stations. Reason For Update: As part of further engineering reviews it was determined that the previously proposed capacitor bank at Bermuda would be more efficiently accommodated at Curleys station. The scope update adds the 2nd capacitor at Curleys and removes it from the scope at Bermuda | Customer Service |  |  |  | 2027-12-01 |  | EP | 0 | 57.2 | 57.2 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH016 | s3442.9 | Souder 138 kV: Cut into the Corridor – Green Chapel 138 kV circuit and extend ~1.0 mile of new double circuit line, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 1118 MVA , to the greenfield Souder station with (5) 80 kA, 4000 A breakers laid out as 5-CB ring bus for future expansion to 6-CB ring. | Customer Service |  |  |  | 2025-10-22 |  | EP | 0 | 14.31 | 14.31 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH019 | s3442.10 | Bermuda 345 kV: Reroute the Corridor – Innovation 345 kV circuit across the customer’s site utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, built with double circuit structures, SE rating 2278 MVA, to a new 345 kV Bermuda station with (11) 5000 A, 63kA circuit breakers & (1) 158.4 MVAR 345 kV Cap bank, laid out as breaker and a half configuration. Construct four single circuit lines ~0.1 miles, between Bermuda station and the customer; utilizing 2-bundle ACSR Drake 795 (26/7) conductor SE 1800 MVA. Reason For Update: As part of further engineering reviews it was determined that the previously proposed capacitor bank at Bermuda would be more efficiently accommodated at Curleys station. The scope update adds the 2nd capacitor at Curleys and removes it from the scope at Bermuda. | Customer Service |  |  |  | 2025-09-12 |  | EP | 0 | 58.3 | 58.3 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH032 | s3442.11 | Fiesta 138 kV: Cut into the Corridor – Green Chapel 138 kV circuit and extend ~ 0.75 miles of new double circuit line, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, SE rating 1118 MVA , to the greenfield Fiesta station with (10) 80 kA, 4000 A breakers laid out as breaker and a half for future expansion to 6 strings. Construct 4 - 138 kV tie lines to the customers dead end structures ~0.05 miles utilizing ACSR Drake 795 (26/7) conductor SE 360 MVA. | Customer Service |  |  |  | 2026-01-02 |  | EP | 0 | 22.3 | 22.3 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH040 | s3442.12 | Anguin – Rockhopper 138 kV: Reconfigure existing Anguin station and install (10) 138 kV, 4000A, 80 kA circuit breakers to feed customer stations at Penguin and QTS North. Build out strings G & H and construct a new greenfield ~0.6 miles double circuit line to customer’s Rockhopper station. Install (2) 69.1 MVAR cap banks at Anguin station | Customer Service |  |  |  | 2024-02-20 |  | EP | 0 | 13.2 | 13.2 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH044 | s3442.13 | Tasjan 138 kV: Cut into the Innovation – Green Chapel 138 kV circuit #1 and extend ~ 0.75 miles of new double circuit line, utilizing 2-bundled ACSS Curlew 1033.5 (54/7) conductor, SE rating 1123 MVA, to the greenfield Tasjan station with (4) 80 kA, 4000 A breakers laid out 4-CB ring bus. Construct (2) 138 kV tie lines to the customers dead end structures ~0.05 miles utilizing ACSR Drake 795 (26/7) conductor SE 360 MVA. | Customer Service |  |  |  | 2025-11-19 |  | EP | 0 | 18.95 | 18.95 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH052 | s3442.14 | Anguin – Chinstrap 138 kV: Extend the 138 kV double circuit line to Rockhopper by ~0.22 miles to the new Chinstrap (customer) station. | Customer Service |  |  |  | 2024-04-04 |  | EP | 0 | 1.01 | 1.01 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH063 | s3442.15 | Anguin – NBY-6A 138 kV: Install (3) 138 kV, 4000A, 80 kA circuit breakers and construct a new greenfield ~0.9 miles double circuit line to customer’s new NBY-6A station. | Customer Service |  |  |  | 2025-01-31 |  | EP | 0 | 6.92 | 6.92 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.16 | Corridor – Vassell 345 kV #1 & #2 Circuits Sag Re-rate: Replace two structures to mitigate sag issues on the line in order to allow the line to operate to its conductor’s designed maximum operating temperature. | Customer Service |  |  |  | 2025-10-14 |  | EP | 0 | 1.88 | 1.88 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.17 | Kiber Station 138 kV: Cut-into Green Chapel – Corridor 138 kV circuit to a new Kiber station with (8 3) 80 kA 138 kV circuit breakers laid out in a breaker and a half arrangement to install a 300 2x150 MVAR STATCOM to support the significant amount of load added to the area. Reason For Update: As part of further engineering analysis it was determined that in order to be able to physically accommodate the line exits along with two feeds to the STATCOM when taking into account future needs at the station that a total of 8 138 kV breakers would need to be installed initially. | Customer Service |  |  |  | 2027-10-05 |  | EP | 0 | 35 | 35 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.18 | Green Chapel Cap Banks 138 kV: Upgrade proposed cap banks at Green Chapel station from (2) 69.1 MVAR to (2) 115.2 MVAR. | Customer Service |  |  |  | 2026-10-02 |  | EP | 0 | 3.6 | 3.6 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.19 | Corridor 138 kV: Replace (12) 63 kA circuit breakers & cap breakers with 80 kA circuit breakers to improve interrupting capabilities as a result of the new sources in the area. | Customer Service |  |  |  | 2025-06-01 |  | EP | 0 | 12.6 | 12.6 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.20 | Babbitt 138 kV: Replace (2) 63 kA bus-tie circuit breakers with 80 kA circuit breakers to improve interrupting capabilities as a result of the new sources in the area. | Customer Service |  |  |  | 2026-02-17 |  | EP | 0 | 2.15 | 2.15 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.21 | Jug Street: Replace CB-C which is an existing 40 kA breaker with a 4000A 80kA 138 kV breaker to address interrupting capability concerns related to the introduction of the new 345 kV source at Innovation. | Customer Service |  |  |  | 2025-04-08 |  | EP | 0 | 0.8 | 0.8 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.22 | Anchor Hocking – Lancaster 69 kV line Rebuild: Rebuild ~1.16 miles of 69 kV line utilizing ACSR Dove 556.5 (26/7) conductor, SE 142 MVA. As a result of the new customer interconnections in the area, this line will overload under certain N-1-1 scenarios. | Customer Service |  |  |  | 2026-06-29 |  | EP | 0 | 2.5 | 2.5 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.23 | Newark Center 138 kV: Install high and low side sectionalizing on the 138/69 kV transformer to address overloading of 69 kV lines in the area related to the new customer interconnections under certain N-1-1 scenarios. | Customer Service |  |  |  | 2027-05-03 |  | EP | 0 | 2.5 | 2.5 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.24 | Fremont – West Fremont Sag re-rate 138 kV: Sag re-rate the 138 kV circuit & upgrade 1200 A switches at Fremont to address a Generation deliverability violation related to the new customer interconnections in the area. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 2 | 2 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.25 | Fremont – Fremont Center Sag re-rate 138 kV: Sag re-rate the 138 kV circuit to address a Generation deliverability violation related to the new customer interconnections in the area. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 1.5 | 1.5 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.26 | Dumont 765 kV: Replace 3000 A circuit breaker at Dumont to address a generation deliverability violation on the Dumont – Sorenson 765 kV branch related to the new customer interconnections in the area. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 4 | 4 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.27 | Vassell – Green Chapel 345 kV line: Install approximately 12.5-mile long 345 kV transmission between Vassell and Green Chapel stations to mitigate overloading on multiple transmission facilities including other 345 kV transmission lines and 345-138 kV transformers. | Customer Service |  |  |  | 2026-04-01 |  | EP | 0 | 75 | 75 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.28 | Vassell – Curleys 345 kV line: Install approximately 12.5-mile long 345 kV transmission between Vassell and Curleys stations to mitigate overloading on multiple transmission facilities including other 345 kV transmission lines and 345-138 kV transformers. | Customer Service |  |  |  | 2026-12-01 |  | EP | 0 | 75 | 75 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.29 | Vassell 765 & 345 kV stations: Add 3-345 kV breakers to connect new lines to Curleys and Green Chapel. | Customer Service |  |  |  | 2026-04-01 |  | EP | 0 | 10 | 10 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2022-OH023, AEP-2022-OH034, AEP-2022-OH036, AEP-2022-OH045, AEP-2022-OH046, AEP-2022-OH075, AEP-2022-OH077, AEP-2023-OH016, AEP-2023-OH019, AEP-2023-OH032, AEP-2023-OH040, AEP-2023-OH044, AEP-2023-OH052, AEP-2023-OH063 | s3442.30 | Green Chapel 345/138 kV station: Install two 675 MVA, 345/138 kV transformers to connect the new Vassell – Green Chapel 345 kV line to 138 kV system and to mitigate overloading on the other 345/138 kV transformers in the system. | Customer Service |  |  |  | 2026-04-01 |  | EP | 0 | 39.2 | 39.2 | 2023-12-05 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH048 | s3445.1 | Giles station 138kV: Establish a new three breaker ring bus station named Giles using 3000A 40kA circuit breakers. | Customer Service |  |  |  | 2025-10-01 |  | EP | 0 | 3.88 | 3.88 | 2024-02-16 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH048 | s3445.2 | Clinton- Huntley- Karl 138kV Circuit: Cut into the existing Clinton - Huntley - Karl 138kV for the Giles Extension line to tap into. | Customer Service |  |  |  | 2025-10-01 |  | EP | 0 | 0.79 | 0.79 | 2024-02-16 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH048 | s3445.3 | Giles 138kV Extension: Construct a new 0.1 mile double circuit in and out line from the Clinton- Huntley- Karl 138kV Circuit to the new Giles station. | Customer Service |  |  |  | 2025-10-01 |  | EP | 0 | 0.56 | 0.56 | 2024-02-16 |  |  | FALSE
Supplemental | AEP | AEP-2023-OH048 | s3445.4 | Giles 138kV Extension: Remote end relay upgrades at Scherers Switch, Huntley and Blendon stations. | Customer Service |  |  |  | 2025-10-01 |  | EP | 0 | 0.07 | 0.07 | 2024-02-16 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH050 | s3446.1 | Rebuild on the existing site with 9- 138kV 63kA 3000A breakers and utilizing one of the original breakers that is in good health to create a ten-breaker ring bus. Add a 28.8 MVAR 138kV Cap Bank. Construct a greenfield 40kV yard with two new 50MVA 138/40kV transformers to support the three 40kV customers served from the station. Use existing breaker 16 and 22 on the low-side of the transformers. Replace breakers 17 and 10 with existing breakers 15 and 21 which are in good health. Install a new DICM and remove the existing control house. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  | EP | 0 | 35.38 | 35.38 | 2024-01-19 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH050 | s3446.2 | As part of the station reconfiguration the double circuit 138 kV line from Marion to LSII and Harrison will be rerouted into the new 138kV yard with a new 0.15-mile extension using ACSR Drake 795 (26/7) conductor (SE 360 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  | EP | 0 | 1.14 | 1.14 | 2024-01-19 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH050 | s3446.3 | reroute the existing 40 kV service (Royal Building Products) T-line into the new 40 kV yard with a new 0.24 miles extension using ACSR Dove 556.5 (26/7) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  | EP | 0 | 0.9 | 0.9 | 2024-01-19 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH050 | s3446.4 | reroute the existing 40 kV service (ITC Manufacturing) T line into the new 40 kV yard with a new 0.19-mile extension using ACSR Dove 556.5 (26/7) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  | EP | 0 | 0.93 | 0.93 | 2024-01-19 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH050 | s3446.5 | Construct a greenfield ~0.15-mile single circuit line to Columbus Auto Shredding POI using ACSR Dove 556.5 (26/7) conductor (SE 142 MVA). | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  | EP | 0 | 0.92 | 0.92 | 2024-01-19 |  |  | FALSE
Supplemental | AEP | AEP-2021-OH050 | s3446.6 | Remote end work will be performed at Mound, Harrison, and LSII stations to coordinate with the work at Marion Road. | Equipment Material Condition, Performance and Risk |  |  |  | 2027-03-31 |  | EP | 0 | 0.89 | 0.89 | 2024-01-19 |  |  | FALSE