## Nov2024-Apr2025
DEK FAC 2026-00275
PSC DR 1.16
Review Period: 11/1/2024 - 4/30/2025
Unit | Event Type | Event Start | Event End | Schedule Hours | Forced Hours | Actual Hours | Event Duration Hours | Event Description
East Bend Steam-2 | PO | 2024-09-06 12:30 | 2024-11-05 11:17 | 1439.783 | 0 | 1439.783 | 1439.783 | 2024 Fall Outage - FGD Ductwork replacement - CBU Buckets - SBAC Overhaul
Woodsdale CT-4 | PO | 2024-09-07 00:01 | 2024-11-20 12:56 | 1789.917 | 0 | 1789.917 | 1789.917 | Unit Major (overhaul)
Woodsdale CT-2 | MO | 2024-10-31 00:01 | 2024-11-02 01:01 | 49 | 0 | 49 | 49 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-1 | MO | 2024-10-31 00:01 | 2024-11-02 05:46 | 53.75 | 0 | 53.75 | 53.75 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-3 | MO | 2024-10-31 00:01 | 2024-11-02 05:46 | 53.75 | 0 | 53.75 | 53.75 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-5 | MO | 2024-10-31 00:01 | 2024-11-02 05:47 | 53.767 | 0 | 53.767 | 53.767 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-6 | MO | 2024-10-31 00:01 | 2024-11-02 05:49 | 53.8 | 0 | 53.8 | 53.8 | Unit out of service for fuel oil wiring troubleshooting and repair.
Woodsdale CT-5 | SF | 2024-11-05 05:39 | 2024-11-05 13:10 | 0 | 7.517 | 7.517 | 7.517 | Generator breaker air pressure contact stuck open, reset.
East Bend Steam-2 | U1 | 2024-11-05 13:48 | 2024-11-05 16:22 | 0 | 2.567 | 2.567 | 2.567 | Unit tripped during startup. 2B2 Bus Trip when starting 2-2 SBAC
Woodsdale CT-3 | U1 | 2024-11-17 17:23 | 2024-11-19 14:10 | 0 | 44.783 | 44.783 | 44.783 | Tripping on erratic axial probe, trouble shooting in progress
Woodsdale CT-3 | U1 | 2024-11-19 20:11 | 2024-11-22 12:15 | 0 | 64.067 | 64.067 | 64.067 | Tripping on erratic axial probe, trouble shooting in progress
East Bend Steam-2 | MO | 2024-11-19 23:59 | 2024-11-25 11:00 | 131.017 | 0 | 131.017 | 131.017 | ID Fan and SCR Cleaning
Woodsdale CT-4 | PO | 2024-11-20 17:12 | 2024-11-21 14:41 | 21.483 | 0 | 21.483 | 21.483 | Unit Major (overhaul)
Woodsdale CT-4 | U1 | 2024-11-21 18:04 | 2024-11-23 16:42 | 0 | 46.633 | 46.633 | 46.633 | Inspection to start on 12/3
Woodsdale CT-3 | U1 | 2024-11-22 13:13 | 2024-11-27 16:30 | 0 | 123.283 | 123.283 | 123.283 | Tripping on erratic axial probe, trouble shooting in progress
Woodsdale CT-4 | U1 | 2024-11-23 17:42 | 2024-12-08 09:56 | 0 | 352.233 | 352.233 | 352.233 | Inspection to start on 12/3
Woodsdale CT-4 | U1 | 2024-12-08 15:31 | 2024-12-11 10:00 | 0 | 66.483 | 66.483 | 66.483 | Unit made back available after data points updated per GE
East Bend Steam-2 | MO | 2024-12-27 01:04 | 2024-12-31 08:32 | 103.467 | 0 | 103.467 | 103.467 | Feedwater leak and governor valve #6 repairs
Woodsdale CT-4 | U1 | 2024-12-27 10:17 | 2024-12-27 13:27 | 0 | 3.167 | 3.167 | 3.167 | Replace rotor bar motor brushes, rolled unit, made unit available
East Bend Steam-2 | U1 | 2024-12-31 09:12 | 2024-12-31 10:44 | 0 | 1.533 | 1.533 | 1.533 | Trip on drum level, BFP recircs opened on low flow signal.
Woodsdale CT-1 | U1 | 2025-01-02 16:37 | 2025-01-02 20:20 | 0 | 3.717 | 3.717 | 3.717 | Ovation card issue, repaired, test ran, released unit
Woodsdale CT-1 | U1 | 2025-01-30 06:11 | 2025-01-31 08:13 | 0 | 26.033 | 26.033 | 26.033 | Adjusted second stage regulator to 315psi.
Woodsdale CT-2 | U1 | 2025-02-12 10:25 | 2025-02-12 11:48 | 0 | 1.383 | 1.383 | 1.383 | AVR blocked, reset
East Bend Steam-2 | U1 | 2025-02-13 05:21 | 2025-02-17 09:46 | 0 | 100.417 | 100.417 | 100.417 | Large slag fall overloading the SFC.
Woodsdale CT-3 | U1 | 2025-02-20 06:40 | 2025-02-20 07:06 | 0 | 0.433 | 0.433 | 0.433 | Automatic shutdown, adjusted fuel oil setpoint
Woodsdale CT-4 | U1 | 2025-02-20 06:43 | 2025-02-20 07:30 | 0 | 0.783 | 0.783 | 0.783 | Automatic shutdown, adjusted fuel oil setpoint
Woodsdale CT-6 | U1 | 2025-02-20 06:45 | 2025-02-20 07:57 | 0 | 1.2 | 1.2 | 1.2 | Bad prox switch, replaced, stroke valves, release unit
Woodsdale CT-1 | PO | 2025-03-03 07:30 | 2025-03-03 10:00 | 2.5 | 0 | 2.5 | 2.5 | Fire protection CO2 testing
Woodsdale CT-3 | PO | 2025-03-03 07:30 | 2025-03-03 10:00 | 2.5 | 0 | 2.5 | 2.5 | Fire protection CO2 testing
Woodsdale CT-4 | PO | 2025-03-03 07:30 | 2025-03-03 10:00 | 2.5 | 0 | 2.5 | 2.5 | Fire protection CO2 testing
Woodsdale CT-6 | PO | 2025-03-03 07:30 | 2025-03-03 10:00 | 2.5 | 0 | 2.5 | 2.5 | Fire protection CO2 testing
Woodsdale CT-2 | PO | 2025-03-03 07:30 | 2025-03-03 10:00 | 2.5 | 0 | 2.5 | 2.5 | Fire protection CO2 testing
Woodsdale CT-5 | PO | 2025-03-03 07:30 | 2025-03-03 10:00 | 2.5 | 0 | 2.5 | 2.5 | Fire protection CO2 testing
East Bend Steam-2 | MO | 2025-03-08 02:00 | 2025-03-17 02:58 | 215.967 | 0 | 215.967 | 215.967 | Tube Leak
Woodsdale CT-1 | U1 | 2025-03-10 06:00 | 2025-03-18 16:30 | 0 | 202.5 | 202.5 | 202.5 | Found unit avr in fault, made unit unavailable.
Woodsdale CT-3 | PO | 2025-03-22 21:03 | 2025-03-23 09:55 | 12.867 | 0 | 12.867 | 12.867 | Unit flamed out on shutdown.
Woodsdale CT-5 | PO | 2025-03-23 16:48 | 2025-03-24 12:58 | 20.167 | 0 | 20.167 | 20.167 | Gen starting breaker failed to show correct position
Woodsdale CT-2 | PO | 2025-03-24 09:21 | 2025-03-27 17:10 | 79.817 | 0 | 79.817 | 79.817 | Faulty flame scanner keeps tripping the unit.
Woodsdale CT-5 | MO | 2025-04-03 08:56 | 2025-04-07 12:00 | 99.067 | 0 | 99.067 | 99.067 | Stack inspection plates came loose and needed reinstalled.
Woodsdale CT-2 | U1 | 2025-04-05 00:35 | 2025-04-05 07:49 | 0 | 7.233 | 7.233 | 7.233 | Sync's blocked, reset and test ran unit
Woodsdale CT-2 | U1 | 2025-04-16 08:25 | 2025-04-16 14:00 | 0 | 5.583 | 5.583 | 5.583 | Had to repair several exhaust TC's. Made back available for dispatch at 14:00
East Bend Steam-2 | MO | 2025-04-20 02:18 | 2025-05-05 08:14 | 365.933 | 0 | 365.933 | 365.933 | Maintenance Outage for FGD inspections and service water pit inspection.
Woodsdale CT-5 | U1 | 2025-04-25 07:29 | 2025-04-25 10:30 | 0 | 3.017 | 3.017 | 3.017 | Repaired oil leak and made back available for dispatch.
PO = Planned Outage
MO = Maintenance Outage
SF = Startup Failure
U1 - Forced outage (Immediate)

## May2025-Oct2025
DEK FAC 2026-00275
PSC DR 1.16
Review Period: 5/1/2025 - 10/31/2025
Unit | Event Type | Event Start | Event End | Schedule Hours | Forced Hours | Actual Hours | Event Duration Hours | Event Description
Woodsdale CT-5 | SF | 2025-05-12 14:06 | 2025-05-12 15:36 | 0 | 1.5 | 1.5 | 1.5 | SFC tripped unit on start. Made repairs. Found jacking oil pump had quit running, repaired and made back available
East Bend Steam-2 | MO | 2025-05-27 | 2025-05-31 | 96 | 0 | 96 | 96 | Air Heater cleaning
Woodsdale CT-1 | MO | 2025-05-28 22:00 | 2025-05-29 06:00 | 8 | 0 | 8 | 8 | Unit has been made unavailable for remote starts until further notice from 22:00 to 06:00 unless the plant is staffed. Need to fix AVR syncing issue.
East Bend Steam-2 | U1 | 2025-06-01 | 2025-06-02 07:52 | 0 | 31.867 | 31.867 | 31.867 | air heater fouling cont.
East Bend Steam-2 | U1 | 2025-06-03 16:10 | 2025-06-04 13:40 | 0 | 21.5 | 21.5 | 21.5 | Steam Leak Repair
East Bend Steam-2 | MO | 2025-06-04 13:40 | 2025-06-06 10:12 | 44.533 | 0 | 44.533 | 44.533 | MO after steam leak repair
Woodsdale CT-1 | PO | 2025-06-07 | 2025-06-13 14:56 | 158.933 | 0 | 158.933 | 158.933 | Spring Prep / Borescope
Woodsdale CT-2 | PO | 2025-06-07 | 2025-06-13 15:03 | 159.05 | 0 | 159.05 | 159.05 | Spring Prep / Borescope
Woodsdale CT-4 | PO | 2025-06-14 | 2025-06-20 15:59 | 159.983 | 0 | 159.983 | 159.983 | Spring Prep / Borescope.
Woodsdale CT-3 | PO | 2025-06-14 | 2025-06-21 16:26 | 184.433 | 0 | 184.433 | 184.433 | Spring Prep / Borescope
Woodsdale CT-4 | SF | 2025-07-02 12:53 | 2025-07-04 13:51 | 0 | 48.967 | 48.967 | 48.967 | Checked limit switches, RTS
Woodsdale CT-4 | SF | 2025-07-05 15:47 | 2025-07-06 14:04 | 0 | 22.283 | 22.283 | 22.283 | Checked limit switches, RTS.
Woodsdale CT-4 | SF | 2025-07-07 08:52 | 2025-07-08 09:37 | 0 | 24.75 | 24.75 | 24.75 | Found loose wire on closing coil, repaired, RTS.
Woodsdale CT-5 | U1 | 2025-07-16 10:30 | 2025-07-16 14:35 | 0 | 4.083 | 4.083 | 4.083 | Stroked valves, RTS
Woodsdale CT-4 | U1 | 2025-08-22 17:19 | 2025-08-26 09:30 | 0 | 88.183 | 88.183 | 88.183 | Lost natural gas SCFM reading.
Woodsdale CT-5 | U1 | 2025-08-28 07:05 | 2025-08-28 08:39 | 0 | 1.567 | 1.567 | 1.567 | Had to take unit off for water injection issues
East Bend Steam-2 | PO | 2025-09-06 | 2025-11-08 09:45 | 1522.75 | 0 | 1522.75 | 1522.75 | Planned 2025 Fall outage
Woodsdale CT-4 | PO | 2025-09-27 | 2025-10-10 15:00 | 327 | 0 | 327 | 327 | Fall Prep. Inspections and maintenance
Woodsdale CT-3 | PO | 2025-09-27 | 2025-10-14 14:17 | 422.283 | 0 | 422.283 | 422.283 | Fall Prep. Inspections and maintenance
Woodsdale CT-5 | U1 | 2025-09-30 07:12 | 2025-09-30 08:42 | 0 | 1.5 | 1.5 | 1.5 | SFC, Starting breaker trip. WDC U5 failed to start due to jacking oil brushes. Made unit back available after cracking unit.
Woodsdale CT-2 | U1 | 2025-10-04 17:58 | 2025-10-04 20:45 | 0 | 2.783 | 2.783 | 2.783 | Vapor Extractor failed/small fire. Replaced Vapor Extractor motor/ made available
Woodsdale CT-5 | PO | 2025-10-11 | 2025-10-24 18:28 | 330.467 | 0 | 330.467 | 330.467 | Fall prep. Inspections and maintenance
Woodsdale CT-6 | PO | 2025-10-11 | 2025-10-24 18:45 | 330.75 | 0 | 330.75 | 330.75 | Fall prep. Inspections and maintenance
Woodsdale CT-3 | U1 | 2025-10-23 09:26 | 2025-10-23 16:41 | 0 | 7.25 | 7.25 | 7.25 | Speed detector module point
Woodsdale CT-4 | U1 | 2025-10-24 08:58 | 2025-10-27 09:45 | 0 | 72.783 | 72.783 | 72.783 | pressure low for differential seal air system
Woodsdale CT-6 | SF | 2025-10-26 16:39 | 2025-10-27 13:18 | 0 | 20.65 | 20.65 | 20.65 | Unit would not sync.
Woodsdale CT-2 | SF | 2025-10-28 16:50 | 2025-10-28 17:28 | 0 | 0.633 | 0.633 | 0.633 | Attempt 1: 1st start unit stuck on step 04 at 900 RPM. Starting breaker was pot showing any feedback (not indicating open or closed). Attempt 2: Re-racked starting breaker and started unit a second time with no issue
PO = Planned Outage
MO = Maintenance Outage
SF = Startup Failure
U1 - Forced outage (Immediate)

## Nov2025-Apr2026
DEK FAC 2026-00275
PSC DR 1.16
Review Period: 11/1/2025 - 4/30/2026
Unit | Event Type | Event Start | Event End | Schedule Hours | Forced Hours | Actual Hours | Event Duration Hours | Event Description
Woodsdale CT-6 | SF | 2025-11-02 01:55 | 2025-11-03 15:27 | 0 | 38.533 | 38.533 | 38.533 | SFC Fail trip
Woodsdale CT-2 | SF | 2025-11-06 04:55 | 2025-11-06 10:00 | 0 | 5.083 | 5.083 | 5.083 | Unit failed to sync on remote start
Woodsdale CT-1 | SF | 2025-11-07 04:04 | 2025-11-07 04:51 | 0 | 0.783 | 0.783 | 0.783 | Failed remote start
Woodsdale CT-1 | U1 | 2025-11-07 04:57 | 2026-01-05 09:47 | 0 | 1420.833 | 1420.833 | 1420.833 | Heavy vibration on number 1 bearing
Woodsdale CT-5 | U1 | 2025-11-16 16:21 | 2025-11-16 18:57 | 0 | 2.6 | 2.6 | 2.6 | Water injection valve failed MBV30AA009
Woodsdale CT-2 | SF | 2025-11-17 05:47 | 2025-11-17 06:02 | 0 | 0.25 | 0.25 | 0.25 | Tripped on flame. Too many bad or erratic exhaust TC's.
Woodsdale CT-2 | U1 | 2025-11-17 06:02 | 2025-11-17 10:58 | 0 | 4.933 | 4.933 | 4.933 | Tripped on flame. Too many bad or erratic exhaust TC's.
Woodsdale CT-2 | SF | 2025-11-19 12:51 | 2025-11-19 15:53 | 0 | 3.033 | 3.033 | 3.033 | Too many bad or erratic exhaust TC's.
Woodsdale CT-2 | U1 | 2025-11-19 16:55 | 2025-11-21 11:13 | 0 | 42.3 | 42.3 | 42.3 | Test wasn't a water injection problem. Still a TC problem
East Bend Steam-2 | PO | 2025-11-20 02:55 | 2025-11-24 13:40 | 106.75 | 0 | 106.75 | 106.75 | General Maintenance Outage
Woodsdale CT-6 | SF | 2025-11-29 15:31 | 2025-11-29 16:22 | 0 | 0.85 | 0.85 | 0.85 | Shut down after unit failed to sync.
Woodsdale CT-2 | MO | 2025-12-01 | 2025-12-11 08:40 | 248.667 | 0 | 248.667 | 248.667 | Borescope Inspection
Woodsdale CT-6 | U1 | 2025-12-16 05:19 | 2025-12-16 05:45 | 0 | 0.433 | 0.433 | 0.433 | 1st start trip on fuel valve trouble and trip on flame
Woodsdale CT-6 | U1 | 2026-01-16 05:09 | 2026-01-18 10:30 | 0 | 53.35 | 53.35 | 53.35 | Removed from service due to high vibration MBD30
Woodsdale CT-5 | SF | 2026-01-20 07:32 | 2026-01-20 08:32 | 0 | 1 | 1 | 1 | Motor operated burner cooling air valve failed to close
Woodsdale CT-1 | SF | 2026-01-24 05:47 | 2026-01-24 10:48 | 0 | 5.017 | 5.017 | 5.017 | Erratic flame scanner circuit
Woodsdale CT-2 | SF | 2026-01-24 14:04 | 2026-01-24 15:56 | 0 | 1.867 | 1.867 | 1.867 | FO fill v/v blown fuse
Woodsdale CT-6 | SF | 2026-01-26 16:38 | 2026-01-28 17:59 | 0 | 49.35 | 49.35 | 49.35 | Failed to light off
Woodsdale CT-4 | SF | 2026-01-26 16:43 | 2026-01-26 18:40 | 0 | 1.95 | 1.95 | 1.95 | Failed to light off
Woodsdale CT-6 | U1 | 2026-02-06 | 2026-02-09 | 0 | 72 | 72 | 72 | Substation breaker repair
Woodsdale CT-5 | U1 | 2026-02-06 | 2026-02-09 | 0 | 72 | 72 | 72 | Substation breaker repair
Woodsdale CT-6 | SF | 2026-02-10 04:43 | 2026-02-10 05:43 | 0 | 1 | 1 | 1 | GEN BRKR wouldn't close/sync
Woodsdale CT-1 | MO | 2026-02-16 | 2026-02-20 | 96 | 0 | 96 | 96 | NERC relay testing, CT heat shield inspection, and inlet filter replacement
Woodsdale CT-3 | MO | 2026-02-16 | 2026-02-20 | 96 | 0 | 96 | 96 | NERC relay testing, CT heat shield inspection, and inlet filter replacement
Woodsdale CT-4 | MO | 2026-02-16 | 2026-02-20 | 96 | 0 | 96 | 96 | NERC relay testing, CT heat shield inspection, and inlet filter replacement
Woodsdale CT-2 | MO | 2026-02-16 | 2026-02-20 | 96 | 0 | 96 | 96 | NERC relay testing, CT heat shield inspection, and inlet filter replacement
Woodsdale CT-3 | U1 | 2026-02-22 13:15 | 2026-02-22 14:15 | 0 | 1 | 1 | 1 | SFC tripped unit on start. Units off but could have been requested to start using adjacent unit SFC
Woodsdale CT-3 | U1 | 2026-02-23 13:15 | 2026-02-27 08:36 | 0 | 91.35 | 91.35 | 91.35 | SFC tripped unit on start. Units off but could have been requested to start using adjacent unit SFC
Woodsdale CT-5 | SF | 2026-02-24 16:37 | 2026-02-24 17:37 | 0 | 1 | 1 | 1 | Unit tripped due to blow-off valve issue
East Bend Steam-2 | U1 | 2026-02-25 19:13 | 2026-02-25 22:55 | 0 | 3.7 | 3.7 | 3.7 | ID Fan issue
Woodsdale CT-5 | SF | 2026-03-01 06:20 | 2026-03-01 09:00 | 0 | 2.667 | 2.667 | 2.667 | Blow off v/v prox switches. Unit was unavailable until 09:00
Woodsdale CT-5 | U1 | 2026-03-02 06:20 | 2026-03-18 10:59 | 0 | 387.65 | 387.65 | 387.65 | Blow off valve repair
Woodsdale CT-4 | U1 | 2026-03-02 13:36 | 2026-03-02 14:43 | 0 | 1.117 | 1.117 | 1.117 | Exciter failed and sync issue. Reset voltage regulator and released for test run.
Woodsdale CT-1 | U1 | 2026-03-14 05:00 | 2026-03-14 05:42 | 0 | 0.7 | 0.7 | 0.7 | Gas valve bounced on startup.
Woodsdale CT-5 | PO | 2026-03-18 10:59 | 2026-05-17 07:30 | 1436.517 | 0 | 1436.517 | 1436.517 | Combustion Turbine Major Overhaul
East Bend Steam-2 | MO | 2026-03-21 02:37 | 2026-03-31 07:23 | 244.767 | 0 | 244.767 | 244.767 | SCR cleaning, air heater cleaning and boiler tube leak repair.
Woodsdale CT-6 | SF | 2026-03-26 16:44 | 2026-03-26 18:34 | 0 | 1.833 | 1.833 | 1.833 | Generator breaker failure. Reset SFC, Sync, and alarms.
Woodsdale CT-2 | SF | 2026-03-28 03:58 | 2026-03-28 07:22 | 0 | 3.4 | 3.4 | 3.4 | AVR issue
Woodsdale CT-1 | SF | 2026-03-28 06:03 | 2026-04-02 11:40 | 0 | 125.617 | 125.617 | 125.617 | Gas valve problem
Woodsdale CT-6 | SF | 2026-04-22 06:15 | 2026-04-22 12:05 | 0 | 5.833 | 5.833 | 5.833 | SFC Trip. SFC brush liftoff
Woodsdale CT-4 | U1 | 2026-04-25 07:43 | 2026-04-25 13:48 | 0 | 6.083 | 6.083 | 6.083 | 2nd stage blow-off issue
PO = Planned Outage
MO = Maintenance Outage
SF = Startup Failure
U1 - Forced outage (Immediate)