## Checkbook
DRAFT |  |  |  | 2006-01-01 | 2006-01-18 | 2006-01-01 | 2006-01-23 | 2006-01-01
Phase 2A Estimate available April 2006 |  |  |  | Rev 2 |  | Rev 3 |  | Rev 7
Big Sandy Unit 1 FGD - Checkbook | [6 empty] | This Revision is based on Meeting held with J White, W Calvert, E Dillow, L Aguirre & L Robinson
Preliminary Estimate (-30% +50%) |  | Budgetary Estimate (-15% +30%) |  | Cost Differential |  | Cost Differential |  | Cost Differential
prepared Dec 2004
Absorber Island |  | FGD SYSTEM
Limestone/Gypsum Handling |  | FGD Engr & Procurement | 5.8 |  | 5.8 |  | 5.8
Misc & Adjustments |  | FGD Erection | 3.7 |  | 3.7 |  | 3.7
Foundations & Site Prep |  | Site Prep & Foundation | 4.3 |  | 4.3 |  | 4.3
Stack |  | Stack Liner** (See Note 1) | 12 |  | 9.5 | -2.5 | 9.5 | -2.5
BOP |  | BOP (inc. Ductwork) | 16.2 |  | 16.2 |  | 16.2
Unit 1 Incremental (FGD & SCR) | 89.2 | PM E & C (See PM E & C Below & Note 2) | 14.2 |  | 11.2 | -3 | 0 | -14.2
|  | FGD SYSTEM TOTAL | 56.2 |  | 50.7 | -5.5 | 39.5 | -16.7
ASSOCIATED WORK
|  | Precipitator Relocation/Replacement (See Note 3 Below) | 15.5 |  | 15.5 |  | 25 | 9.5
Boiler Modifications | 25.1 | Boiler Modifications (See Note 4 Below) | 25.1 |  | 16.9 | -8.2 | 4 | -21.1
|  | Balanced Draft | 14 |  | 14 |  | 14
|  | I&C Upgrades/Controls Modernization (See Note 5 Below) | 8.1 |  | 8.1 |  | 2.5 | -5.6
|  | Coal Blending | 0 |  | 0 |  | 0
|  | River Water M/U | 0 |  | 0 |  | 0
|  | SO3 Mitigation (See Note 6 Below) | 9.3 |  | 9.3 |  | 4.36 | -4.94
|  | Wastewater Treatment | 0 |  | 0 |  | 0
AEP Assoc on Unit 1 | 58 | ASSOCIATED WORK TOTAL | 72 |  | 63.8 | -8.2 | 49.86 | -22.14
|  | PM E & C |  |  |  |  | 8.0424
|  | Subtotal in 2006 dollars |  |  |  |  | 97.4024
AFUDC (5.96%) | 10.2869 | AFUDC & AEP Overheads - 11.5% | 14.743 |  | 13.1675 | -1.5755 | 10.2764 | -2.8911
Overheads (15.2%) | 26.2351 | Escalation Cost - 10% (See Note 7 Below) | 12.82 |  | 11.45 | -1.37 | 0 | -11.45
Inflation @ 3.5%/yr | 12.0819 | Contingency - 10% (See Note 8 Below) | 12.82 |  | 11.45 | -1.37 | 0 | -11.45
TOTAL | 220.9039 | PROJECT TOTAL* | 168.583 | -52.3209 | 150.5675 | -70.3364 | 107.6788 | -60.9042
NOTE: This estimate is per PG 010 Rev 0, pg 1, Section 2, Para 2.1 |  | NOTE: Red bold numbers indicate firm price bids
NOTE: This estimate is per PG 010 Rev 0, pg 1, Section 2, Para 2.2
*SCR cost not included - project scope reduced since last analysis
**Stack Liner - contingent on Unit 2 building a 2 flue stack. Cost is for installation of
Unit 1 liner, while Unit 2 is in operation.
ALL OF THE BELOW LISTED NOTES ARE A RESULT OF MEETING HELD ON 01/23/06, INVOLVING JEFF WHITE, BIG SANDY PLANT AND THE BIG SANDY PROJECT TEAM.
NOTE 1: Stack Liner** Estimate amounts received from Scott Kutzley are shown in Tab Listed as "Notes for Chimney Cost"
NOTE 2: Precipitator Relocation/Replacement - It's anticipated that replacing the precip will be more cost effective than relocating and repairing existing precip due to required Outage time.
NOTE 3: PM E & C - Was Estamated at 9% of total cost for both FGD and Associated work.
NOTE 4: Boiler Modifications - Reduced by the amount of modifications required to continue operations without FGD Project.
NOTE 5: I&C Upgrades/Controls Modernization - Estimated at 1/3 of Unit2's budget for this option (7.6*.33) also this only requires adding IO's
NOTE 6: SO3 Mitigation - Estimated at 1/3 of Unit2's budget for this option (13.2*.33)
NOTE 7: Escalation Cost - 10% - This amount was removed and will be accounted for by Jeff White's group as 2% each year.
NOTE 8: Contingency - 10% - This amount was also removed at the request of Upper Mgnt, and should not be counted as part of the over-all evaluation of Unit 1 FGD.
Note - Line 9N Dollar amounts received from Scott Kutzley are shown in Tab Listed as "Notes for Chimney Cost"
Note - Line 11F, this amount was carry over amount from unit 2, this revised amount shows an adjustment amount for Unit 1 and is 70% of unit 2 PM E&C Cost.
Note - Line 16N, 8.2M was originally added for Boiler Upgrades that would be need for Unit 1, this amount is already in the O&M budget (Don Untch), and was removed from this Rev.
4.356

## BS Cost Est ALL Revions
BIG SANDY UNIT 1 FGD PROJECT | [6 empty] | REVISION 1 |  | REVISION 2 |  | REVISION 3 |  | REVISION 4 |  | REVISION 5
Cost Estimate +/- 40% | [6 empty] | 2006-01-06 | DELTA | 2006-01-07 | DELTA | 2006-01-17 | DELTA | 2006-01-18 | DELTA | 2006-01-23 | DELTA
| 2006 | 2007 | 2008 | 2009 | 2010 | TOTAL | TOTAL |  | TOTAL |  | TOTAL |  | TOTAL |  | TOTAL
| $M | $M | $M | $M | $M | $M | $M |  | $M |  | $M |  | $M |  | $M
FGD SYSTEM
FGD Engr & Procurement | 1.78 | 4.78 | 7.17 | 9.56 | 2.39 | 25.68 | 5.8 | -19.88 | 5.8 | 0 | 5.8 | 0 | 5.8 | 0 | 5.8 | 0
FGD Erection |  | 2.34 | 3.51 | 3.51 | 2.34 | 11.7 | 3.7 | -8 | 3.7 | 0 | 3.7 | 0 | 3.7 | 0 | 3.7 | 0
Site Prep & Foundation |  | 2.58 | 4.3 | 1.72 |  | 8.6 | 4.3 | -4.3 | 4.3 | 0 | 4.3 | 0 | 4.3 | 0 | 4.3 | 0
Stack - Contengent Unit 2 building a 2 flew stack |  | 3.24 | 4.32 | 3.24 |  | 10.8 | 12 | 1.2 | 12 | 0 | 12 | 0 | 9.5 | -2.5 | 9.5 | 0
BOP (inc. Ductwork) |  | 3.64 | 3.64 | 7.28 | 3.64 | 18.2 | 16.2 | -2 | 16.2 | 0 | 16.2 | 0 | 16.2 | 0 | 16.2 | 0
PM E & C | 2.5 | 2.7 | 2.7 | 5.4 | 2.7 | 16 | 14.2 | -1.8 | 14.2 | 0 | 14.2 | 0 | 11.2 | -3 | -1.26 | -12.46
FGD SYSTEM TOTAL | 4.28 | 19.28 | 25.64 | 30.71 | 11.07 | 90.98 | 56.2 | -34.78 | 56.2 | 0 | 56.2 | 0 | 50.7 | -5.5 | 38.24 | -12.46
ASSOCIATED WORK
Precipitator Relocation | 0.95455 | 1.9091 | 2.8636 | 2.8636 | 1.9091 | 10.5 | 15.5 | 5 | 15.5 | 0 | 15.5 | 0 | 15.5 | 0 | 15.5 | 0
Boiler Modifications | 0.4 | 2.96 | 4.44 | 4.44 | 2.96 | 15.2 | 14.9 | -0.3 | 14.9 | 0 | 25.1 | 10.2 | 16.9 | -8.2 | 8.7 | -8.2
Balanced Draft | 0.5 | 2.54 | 3.81 | 3.81 | 2.54 | 13.2 | 14 | 0.8 | 14 | 0 | 14 | 0 | 14 | 0 | 14 | 0
I&C Upgrades/Controls Modernization |  | 0.2 | 0.4 | 0.8 | 0.6 | 2 | 8.1 | 6.1 | 8.1 | 0 | 8.1 | 0 | 8.1 | 0 | 8.1 | 0
Turbin Upgrade | 0 | 0 | 0 | 0 | 0 | 0 | 25.7 | 25.7 | 25.7 | 0 | 0 | -25.7 | 0 | 0 | 0 | 0
Coal Blending - Only required if FGD is not installed in Unit 1 |  | 3 | 4.5 | 4.5 | 3 | 15 | 0 | -15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
River Water M/U |  | 0.05 | 0.15 | 0.2 | 0.1 | 0.5 | 0 | -0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SO3 Mitigation |  | 2.1 | 2.1 | 4.2 | 2.1 | 10.5 | 9.3 | -1.2 | 9.3 | 0 | 9.3 | 0 | 9.3 | 0 | 9.3 | 0
Wastewater Treatment |  | 1.08 | 1.62 | 1.62 | 1.08 | 5.4 | 0 | -5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ASSOCIATED WORK TOTAL | 1.8545 | 13.8391 | 19.8836 | 22.4336 | 14.2891 | 72.3 | 87.5 | 15.2 | 87.5 | 0 | 72 | -15.5 | 63.8 | -8.2 | 55.6 | -8.2
AFUDC (5.96%) // AFUDC & AEP OVERHEADS - 11.5% // 8% // 11.5% // 10% | 0.36562 | 1.9739 | 2.7132 | 3.1674 | 1.5114 | 9.7315 | 16.5255 | 6.794 | 11.496 | -5.0295 | 14.743 | 3.247 | 11.45 | -3.293 | 9.384 | -2.066
Overheads (15.2%) // ESCALATION COST - 10% // 5% // 10% // 10% | 0.93245 | 5.0341 | 6.9196 | 8.0778 | 3.8546 | 24.8186 | 14.37 | -10.4486 | 7.185 | -7.185 | 12.82 | 5.635 | 11.45 | -1.37 | 9.384 | -2.066
Inflation @ 3.5%/yr // CONTINGENCY - 10% // 8% // 10% // 10% | 0.21471 | 1.1592 | 1.5933 | 1.86 | 0.88757 | 5.7148 | 14.37 | 8.6552 | 11.496 | -2.874 | 12.82 | 1.324 | 11.45 | -1.37 | 9.384 | -2.066
PROJECT TOTAL - 40% | [5 empty] | 122.1269 | 113.3793 | -8.7476 | 104.3262 | -9.0531 | 101.1498 | -3.1764 | 89.31 | -11.8398 | 73.1952 | -16.1148
PROJECT TOTAL | 7.6473 | 41.2863 | 56.7498 | 66.2489 | 31.6126 | 203.5448 | 188.9655 | -14.5793 | 173.877 | -15.0885 | 168.583 | -5.294 | 148.85 | -19.733 | 121.992 | -26.858
PROJECT TOTAL + 40% | [5 empty] | 284.9628 | 264.5517 | -20.4111 | 243.4278 | -21.1239 | 236.0162 | -7.4116 | 208.39 | -27.6262 | 170.7888 | -37.6012
FGD System & Associated work based on 46% of Big Sandy Unit 2 FGD Estimate Novemer 2005
SCR System based on 70% of Mitchell Unit 1 SCR Estimate November 2005
FGD $ per Kw hour - Does not include Associated cost (+/- 40%) | 181.96 | 303.2667
Note - Line 9N Dollor amounts received from Scott Kutzley are shown in Tab Listed as "Notes for Chimney Cost"
Note - Line 11F, this amount was carry over amount from unit 2, this revisied amount shows an adjustment amount for Unit 1 and is 70% of unit 2 PM E&C Cost.
Note - Line 16N, 8.2M was orignially added for Boiler Upgrades that would be need for Unit 1, this amount is already in the O&M budget (Don Untch), and was removed from this Rev.

## Big Sandy Unit 1 Estimate
DRAFT | [5 empty] | 2006-01-01
Phase 2A Estimate will be available April 2006 | [5 empty] | Rev 2
BIG SANDY UNIT 1 FGD PROJECT
Budgetary Estimate (-15 +30%)
| 2006 | 2007 | 2008 | 2009 | 2010 | TOTAL
| $M | $M | $M | $M | $M | $M
FGD SYSTEM
FGD Engr & Procurement | 0.58 | 1.16 | 1.74 | 1.74 | 0.58 | 5.8
FGD Erection |  | 0.74 | 1.11 | 1.11 | 0.74 | 3.7
Site Prep & Foundation |  | 1.29 | 2.15 | 0.86 |  | 4.3
Stack liner* |  | 3.6 | 4.8 | 3.6 |  | 12
BOP (inc. Ductwork) |  | 3.24 | 3.24 | 6.48 | 3.24 | 16.2
PM E & C | 1.42 | 2.84 | 2.84 | 4.26 | 2.84 | 14.2
FGD SYSTEM TOTAL | 2 | 12.87 | 15.88 | 18.05 | 7.4 | 56.2
ASSOCIATED WORK
Precipitator Relocation | 1.55 | 3.1 | 4.65 | 4.65 | 1.55 | 15.5
Boiler Modifications | 2.51 | 5.02 | 7.53 | 7.53 | 2.51 | 25.1
Balanced Draft | 1.4 | 2.8 | 4.2 | 4.2 | 1.4 | 14
I&C Upgrades/Controls Modernization |  | 0.81 | 1.62 | 3.24 | 2.43 | 8.1
Coal Blending** |  | 0 | 0 | 0 | 0 | 0
River Water M/U** |  | 0 | 0 | 0 | 0 | 0
SO3 Mitigation |  | 1.86 | 1.86 | 3.72 | 1.86 | 9.3
Wastewater Treatment** |  | 0 | 0 | 0 | 0 | 0
ASSOCIATED WORK TOTAL | 5.46 | 13.59 | 19.86 | 23.34 | 9.75 | 72
AFUDC & AEP Overheads - 11.5% | 0.8579 | 3.0429 | 4.1101 | 4.7598 | 1.9722 | 14.743
Escalation Cost - 10% | 0.746 | 2.646 | 3.574 | 4.139 | 1.715 | 12.82
Contingency - 10% | 0.746 | 2.646 | 3.574 | 4.139 | 1.715 | 12.82
PROJECT TOTAL | 9.8099 | 34.7949 | 46.9981 | 54.4278 | 22.5522 | 168.583
FGD $ per Kw - Does not include Associated cost |  | 187.3333
NOTE: This estimate is per PG 010 Rev 0, pg 1, Section 2, para 2.2
NOTE: Red bold numbers indicate firm price bids
*Stack liner - Contingent on Unit 2 building a 2 flue stack. Cost is for installation of Unit 1 liner, while Unit 2 is in operation
**Latest analysis indicates these items will not be required. Subject to change.

## Notes
Big Sandy Unit 2 FGD Estimate
FGD SYSTEM | $M
FGD Engr & Procurement | 53 | SCR SYSTEM
FGD Erection | 26 | Material | 3.8
Site Prep & Foundation | 19.1 | Construction Labor | 56.4
Stack | 19 | Removal Labor | 1
BOP (inc. Ductwork) | 40.4 | Outside Services | 3.4
PM E & C | 30 | OEM | 22.6
AEP Scope | 5.6 | PM, E & C | 3.9
TOTAL | 193.1 | Plant Labor | 1.9
ASSOCIATED WORK |  | SCR SYSTEM TOTAL | 93
Boiler Modifications | 14.5
Balanced Draft | 20
I&C Upgrades/Controls Modernization | 2 | SCR SYSTEM | 2006 | 2007 | 2008 | 2009 | 2010 | TOTAL
Coal Blending | 10.8 | Material |  |  | 1.9 | 1.52 | 0.38 | 3.8
River Water M/U | 1 | Construction Labor |  |  | 28.2 | 22.56 | 5.64 | 56.4
SO3 Mitigation | 13.2 | Removal Labor |  |  | 0.6 | 0.4 |  | 1
Wastewater Treatment | 12 | Outside Services | 0.34 | 1.02 | 1.36 | 0.34 | 0.34 | 3.4
TOTAL | 73.5 | OEM | 2.26 | 2.26 | 9.04 | 6.78 | 2.26 | 22.6
Landfill | 25.1 | PM, E & C | 0.39 | 1.17 | 1.17 | 0.78 | 0.39 | 3.9
TOTAL | 25.1 | Plant Labor | 0.19 | 0.57 | 0.57 | 0.38 | 0.19 | 1.9
|  | SCR SYSTEM TOTAL | 3.18 | 5.02 | 42.84 | 32.76 | 9.2 | 93
AFUDC & AEP Overheads - 11.5% | 33.5455
Project Total | 325.2455
Mitchell Unit 1 SCR Estimate
SCR SYSTEM
Material | 5.4
Construction Labor | 73.4
Removal Labor | 0
Outside Services | 4.9
OEM | 32.3
PM, E & C | 5.6
Plant Labor | 0.4
TOTAL | 122
FGD System based on 40% of Big Sandy Unit 2 FGD Estimate Novemer 2005
Associated Work based on 70% of Big Sandy Unit 2 Associated work Estimate November 2005
SCR System based on 70% of Mitchell Unit 1 SCR Estimate November 2005
per Ed Dillow rebuilding precip would cost 7m and another 2 m for ductwork.
per Ed Dillow SCR needs about a 1m in remove labor to remove air heater and ductwork with asbestos
per Ed Gilabert added another 5.5m for the precip relocation.
per conversation with allan varney construction labor was increased by 5m off org. number based off info from previous SCR cost
per conversation with allan varney plant labor was increased by 1.5m off org. number based off info from previous SCR cost
Adjusted Stack number due to info from Pullman that 7.6 was to low and needed to be around 12.0

## Notes for Rev 1
Big Sandy Unit 2 FGD Estimate
FGD SYSTEM | $M
FGD Engr & Procurement | 53
FGD Erection | 26
Site Prep & Foundation | 19.1
Stack | 19
BOP (inc. Ductwork) | 40.4
PM E & C | 30
AEP Scope | 5.6
TOTAL | 193.1
ASSOCIATED WORK
Boiler Modifications | 14.5
Balanced Draft | 20
I&C Upgrades/Controls Modernization | 2
Coal Blending | 10.8
River Water M/U | 1
SO3 Mitigation | 13.2
Wastewater Treatment | 12
TOTAL | 73.5
Landfill | 25.1
TOTAL | 25.1
AFUDC & AEP Overheads - 11.5% | 33.5455
Project Total | 325.2455
Mitchell Unit 1 SCR Estimate
SCR SYSTEM
Material | 5.4
Construction Labor | 73.4
Removal Labor | 0
Outside Services | 4.9
OEM | 32.3
PM, E & C | 5.6
Plant Labor | 0.4
TOTAL | 122
Muskingum River Unit 5 SCR Estimate
SCR SYSTEM
Material | 24.3
Construction Labor | 42.4
PM, E & C | 18.2
Plant Labor | 0.5
Contingency | 2.1
TOTAL | 87.5
FGD System based on 40% of Big Sandy Unit 2 FGD Estimate Novemer 2005
Associated Work based on 70% of Big Sandy Unit 2 Associated work Estimate November 2005
SCR System based on 70% of Mitchell Unit 1 SCR Estimate November 2005
per Ed Dillow rebuilding precip would cost 7m and another 2 m for ductwork.
per Ed Dillow SCR needs about a 1m in remove labor to remove air heater and ductwork with asbestos
per Ed Gilabert added another 5.5m for the precip relocation.
per conversation with allan varney construction labor was increased by 5m off org. number based off info from previous SCR cost
per conversation with allan varney plant labor was increased by 1.5m off org. number based off info from previous SCR cost
Adjusted Stack number due to info from Pullman that 7.6 was to low and needed to be around 12.0

## Notes for Rev 2
Big Sandy Unit 2 FGD Estimate
FGD SYSTEM | $M
FGD Engr & Procurement | 53
FGD Erection | 26
Site Prep & Foundation | 19.1
Stack | 19
BOP (inc. Ductwork) | 40.4
PM E & C | 30
AEP Scope | 5.6
TOTAL | 193.1
ASSOCIATED WORK
Boiler Modifications | 14.5
Balanced Draft | 20
I&C Upgrades/Controls Modernization | 2
Coal Blending | 10.8
River Water M/U | 1
SO3 Mitigation | 13.2
Wastewater Treatment | 12
TOTAL | 73.5
Landfill | 25.1
TOTAL | 25.1
AFUDC & AEP Overheads - 11.5% | 33.5455
Project Total | 325.2455
Mitchell Unit 1 SCR Estimate
SCR SYSTEM
Material | 5.4
Construction Labor | 73.4
Removal Labor | 0
Outside Services | 4.9
OEM | 32.3
PM, E & C | 5.6
Plant Labor | 0.4
TOTAL | 122
FGD System based on 40% of Big Sandy Unit 2 FGD Estimate Novemer 2005
Associated Work based on 70% of Big Sandy Unit 2 Associated work Estimate November 2005
SCR System based on 70% of Mitchell Unit 1 SCR Estimate November 2005
per Ed Dillow rebuilding precip would cost 7m and another 2 m for ductwork.
per Ed Dillow SCR needs about a 1m in remove labor to remove air heater and ductwork with asbestos
per Ed Gilabert added another 5.5m for the precip relocation.
per conversation with allan varney construction labor was increased by 5m off org. number based off info from previous SCR cost
per conversation with allan varney plant labor was increased by 1.5m off org. number based off info from previous SCR cost
Adjusted Stack number due to info from Pullman that 7.6 was to low and needed to be around 12.0

## Notes for BS U2 Cost
Big Sandy Unit 2 FGD Estimate
FGD SYSTEM | $M
FGD Engr & Procurement | 53 | SCR SYSTEM
FGD Erection | 26 | Material | 3.8
Site Prep & Foundation | 19.1 | Construction Labor | 56.4
Stack | 19 | Removal Labor | 1
BOP (inc. Ductwork) | 40.4 | Outside Services | 3.4
PM E & C | 30 | OEM | 22.6
AEP Scope | 5.6 | PM, E & C | 3.9
TOTAL | 193.1 | Plant Labor | 1.9
ASSOCIATED WORK |  | SCR SYSTEM TOTAL | 93
Boiler Modifications | 14.5
Balanced Draft | 20
I&C Upgrades/Controls Modernization | 2 | SCR SYSTEM | 2006 | 2007 | 2008 | 2009 | 2010 | TOTAL
Coal Blending | 10.8 | Material |  |  | 1.9 | 1.52 | 0.38 | 3.8
River Water M/U | 1 | Construction Labor |  |  | 28.2 | 22.56 | 5.64 | 56.4
SO3 Mitigation | 13.2 | Removal Labor |  |  | 0.6 | 0.4 |  | 1
Wastewater Treatment | 12 | Outside Services | 0.34 | 1.02 | 1.36 | 0.34 | 0.34 | 3.4
TOTAL | 73.5 | OEM | 2.26 | 2.26 | 9.04 | 6.78 | 2.26 | 22.6
Landfill | 25.1 | PM, E & C | 0.39 | 1.17 | 1.17 | 0.78 | 0.39 | 3.9
TOTAL | 25.1 | Plant Labor | 0.19 | 0.57 | 0.57 | 0.38 | 0.19 | 1.9
|  | SCR SYSTEM TOTAL | 3.18 | 5.02 | 42.84 | 32.76 | 9.2 | 93
AFUDC & AEP Overheads - 11.5% | 33.5455
Project Total | 325.2455
Mitchell Unit 1 SCR Estimate
SCR SYSTEM
Material | 5.4
Construction Labor | 73.4
Removal Labor | 0
Outside Services | 4.9
OEM | 32.3
PM, E & C | 5.6
Plant Labor | 0.4
TOTAL | 122
FGD System based on 40% of Big Sandy Unit 2 FGD Estimate Novemer 2005
Associated Work based on 70% of Big Sandy Unit 2 Associated work Estimate November 2005
SCR System based on 70% of Mitchell Unit 1 SCR Estimate November 2005
per Ed Dillow rebuilding precip would cost 7m and another 2 m for ductwork.
per Ed Dillow SCR needs about a 1m in remove labor to remove air heater and ductwork with asbestos
per Ed Gilabert added another 5.5m for the precip relocation.
per conversation with allan varney construction labor was increased by 5m off org. number based off info from previous SCR cost
per conversation with allan varney plant labor was increased by 1.5m off org. number based off info from previous SCR cost
Adjusted Stack number due to info from Pullman that 7.6 was to low and needed to be around 12.0

## Notes for Chimney Cost
Costs for the chimneys for Big Sandy Unit 2 are as follows:
Big Sandy Unit 2:
800' chimney 33.75' ID FRP liner, $15,074,000
1,000' chimney 33.75' ID FRP liner, $18,197,000
800' chimney 33.75' ID alloy liner, $19,513,000
1,000' chimney 33.75' ID alloy liner, $24,186,000
Some factors that may influence the final cost:
Pricing was part of the FGD Program chimney contract, awarded in late July, 2004 to Pullman Power.
Costs are in 2004 dollars, and assume a construction start date of early 2005.
The costs do not include a foundation, which may cost up to $3,000,000 to $5,000,000.
The costs assumed diameters for the liners which cannot be finalized until a vendor is picked for the absorber, since different absorbers convert the volume of flue gas at different rates.
The costs will need to be adjusted for inflation as well as material changes due to supply and demand. When the size and construction period is established, we will sit with Pullman to develop a cost based on the original cost. In other words, these are not firm prices at this time.
The costs listed above should certainly be within 25%.
Given today's costs and air dispersion modeling, I would assume we would use FRP liners, with 1,000' chimneys, as is currently being used for Mountaineer and Mitchell.
For the first two chimneys, we have added a few options that has cost an additional $800,000 per chimney. I would assume these will be added for all chimneys. It includes additional insurance (performance and payment bond), OSHA approved offset ladders with cages and lower operating pressures.
================================================================================
To build a concrete shell large enough to accommodate the Unit 1 FRP liner (approximately 19.25' diameter) at a later date would add about $3,000,000 to the above pricing. It would include the larger diameter concrete shell and the basic support steel and platforms.
To install a 19.25' diameter FRP liner at a later date in the Unit 2 chimney shell would cost approximately $6,000,000.
To retrofit the existing Unit 1 & 2 chimney for the future Unit 1 FGD flue gas would cost approximately $10,000,000. The outage duration is assumed to be two outages, the first being 2 to 4 weeks, and the second outage being 8 to 10 weeks.
Another cost required to retrofit the existing chimney would be the duct system required to go back to it from the new absorber. This duct is very expensive, and may offset and potential savings.
A new chimney for Unit 1 would cost around $15,000,000, plus another $3,000,000 for the foundation.
For Big Sandy, it appears the most cost effective solution at this time, assuming Unit 1 is a probable unit for FGD, is to build in the capacity in the new Unit 2 shell for a future liner. The cost for the shell and liner, including installation would be around $9,000,000, with no impact on outage duration. To use the existing chimney would cost about the same, but the cost of the duct system would be significant. To build a separate independent chimney would also be much more than $10,000,000.
From our other Tier II stacks, we have found the escalation on the FRP liners to be more than we anticipated, adding about 20% to the cost of the stack. With this in mind, I would suggest the estimates for the original stack are increased by another few million dollars for the total cost, plus escalation from 2004 dollars and 2005 start date of about 4% per year.
I ran this through Pullman Power, and they agree that the accuracy is within +/- 15%.
Please contact me should you have any questions.