## Summary-PRE
PJM Capacity Postion with NO Asset Transfers, Builds or Acquisitions
FRR Planning Perspective
("Length MW" refers to capacity above or below PJM Minimum Reserve Margin)
|  | APCo |  | I&M |  | KPCo |  | Total 3 Company |  | Min Reserve
PJM PY |  | Length | Margin | Length | Margin | Length | Margin | Length | Margin | Margin (IRM)
|  | MW | % | MW | % | MW | % | MW | % | %
2013 | /14 | 184 | 18.76% | 671 | 32.04% | 81 | 22.74% | 936 | 24.22% | 15.4%
2014 | /15 | -98 | 13.78% | 676 | 31.97% | 60 | 20.73% | 638 | 21.08% | 15.4%
2015 | /16 | -1244 | -4.742% | 236 | 21.03% | -696 | -45.26% | -1704 | 0.607% | 15.4%
2016 | /17 | -1330 | -6.195% | 389 | 24.88% | -656 | -42.87% | -1597 | 1.376% | 15.4%
2017 | /18 | -1295 | -5.574% | 438 | 26.15% | -647 | -42.06% | -1504 | 2.176% | 15.4%
2018 | /19 | -1325 | -5.965% | 456 | 26.65% | -644 | -41.55% | -1513 | 2.112% | 15.4%
2019 | /20 | -1319 | -5.773% | 454 | 26.59% | -650 | -41.78% | -1515 | 2.137% | 15.4%
2020 | /21 | -1336 | -6.008% | 498 | 27.69% | -647 | -41.49% | -1485 | 2.409% | 15.4%
2021 | /22 | -1391 | -6.732% | 469 | 26.92% | -656 | -41.94% | -1578 | 1.68% | 15.4%
2022 | /23 | -1434 | -7.287% | 451 | 26.45% | -664 | -42.3% | -1647 | 1.142% | 15.4%
2023 | /24 | -1442 | -7.366% | 461 | 26.67% | -659 | -41.87% | -1640 | 1.232% | 15.4%
2024 | /25 | -1475 | -7.788% | 97 | 17.77% | -666 | -42.23% | -2044 | -2.198% | 15.4%
2025 | /26 | -1983 | -15.49% | 59 | 16.83% | -918 | -63.33% | -2842 | -8.853% | 15.4%
2026 | /27 | -2040 | -16.16% | 31 | 16.15% | -927 | -63.58% | -2936 | -9.491% | 15.4%
2027 | /28 | -2097 | -16.81% | 14 | 15.73% | -938 | -63.87% | -3021 | -10.03% | 15.4%
2028 | /29 | -2136 | -17.23% | -8 | 15.21% | -946 | -64.08% | -3090 | -10.48% | 15.4%
2029 | /30 | -2185 | -17.77% | -47 | 14.29% | -951 | -64.21% | -3183 | -11.09% | 15.4%
2030 | /31 | -2243 | -18.4% | -79 | 13.55% | -962 | -64.49% | -3284 | -11.73% | 15.4%
- | APCO includes (a) Clinch River 1&2 coal-to-gas fuel conversion 12/2014 and 6/2015 and (b) 5/31/15 retirements of Clinch River 3, Glen Lyn 5&6, Kanawha River 1&2 and Sporn 1&3 on 5/31/2015. WPCo to merge with APCo January 2014.
- | KPCO includes Big Sandy 1 coal-to-gas fuel conversion and Big Sandy 2 retirement on 5/31/2015.

## Summary-POST
PJM Capacity Postion AFTER Asset Transfers of Amos 3 (APCo) and Mitchell Plant (50% each APCo and KPCo)
FRR Planning Perspective
("Length MW" refers to capacity above or below PJM Minimum Reserve Margin)
|  | APCo |  | I&M |  | KPCo |  | Total 3 Company |  | Min Reserve
PJM PY |  | Length | Margin | Length | Margin | Length | Margin | Length | Margin | Margin (IRM)
|  | MW | % | MW | % | MW | % | MW | % | %
2013 | /14 | 184 | 18.76% | 671 | 32.04% | 81 | 22.74% | 936 | 24.22% | 15.4%
2014 | /15 | 1428 | 39.06% | 676 | 31.97% | 766 | 83.46% | 2870 | 40.93% | 15.4%
2015 | /16 | 292 | 20.13% | 236 | 21.03% | 10 | 16.27% | 538 | 20.07% | 15.4%
2016 | /17 | 205 | 18.73% | 389 | 24.88% | 50 | 19.84% | 644 | 21.06% | 15.4%
2017 | /18 | 240 | 19.29% | 438 | 26.15% | 59 | 20.64% | 737 | 21.88% | 15.4%
2018 | /19 | 210 | 18.79% | 456 | 26.65% | 62 | 20.88% | 728 | 21.79% | 15.4%
2019 | /20 | 215 | 18.85% | 454 | 26.59% | 56 | 20.33% | 725 | 21.75% | 15.4%
2020 | /21 | 199 | 18.59% | 498 | 27.69% | 59 | 20.59% | 756 | 22.01% | 15.4%
2021 | /22 | 144 | 17.69% | 469 | 26.92% | 50 | 19.77% | 663 | 21.16% | 15.4%
2022 | /23 | 101 | 17% | 451 | 26.45% | 42 | 19.05% | 594 | 20.54% | 15.4%
2023 | /24 | 93 | 16.87% | 461 | 26.67% | 47 | 19.48% | 601 | 20.59% | 15.4%
2024 | /25 | 60 | 16.34% | 97 | 17.77% | 40 | 18.86% | 197 | 17.1% | 15.4%
2025 | /26 | -448 | 8.42% | 59 | 16.83% | -212 | -2.782% | -601 | 10.27% | 15.4%
2026 | /27 | -505 | 7.587% | 31 | 16.15% | -221 | -3.428% | -695 | 9.508% | 15.4%
2027 | /28 | -561 | 6.783% | 14 | 15.73% | -232 | -4.206% | -779 | 8.841% | 15.4%
2028 | /29 | -602 | 6.205% | -8 | 15.21% | -240 | -4.764% | -850 | 8.281% | 15.4%
2029 | /30 | -650 | 5.532% | -47 | 14.29% | -245 | -5.11% | -942 | 7.562% | 15.4%
2030 | /31 | -708 | 4.732% | -79 | 13.55% | -256 | -5.861% | -1043 | 6.784% | 15.4%
- | APCO includes (a) Clinch River 1&2 coal-to-gas fuel conversion 12/2014 and 6/2015 and (b) 5/31/15 retirements of Clinch River 3, Glen Lyn 5&6, Kanawha River 1&2 and Sporn 1&3 on 5/31/2015. WPCo to merge with APCo January 2014.
- | KPCO includes Big Sandy 1 coal-to-gas fuel conversion and Big Sandy 2 retirement on 5/31/2015.

## 3-Co CAPACITY POS
Confidential & Proprietary Information -- Prepared at the Request of Counsel for Potential Litigation
PRELIMINARY--(11/09/12)
"Assumptions" (No BS2 DFGD, Reflect BS1 Gas Conversion and 50/50 APCo/KPCo Mitchell Transfer Split)
AEP-East (3-Co.) Stand-Alone -- Long/<Short> Capacity ("IRM") Positions in PJM
Per Current Projected Environmental 'Transition' Planning/Framework…
I. PRE Affiliate Capacity Transfers
|  |  | A. "FRR" Planning Perspective: | [8 empty] | APCo | I&M | KPCo | 3-Co | 3-Co
"3-Co."
|  |  | APCo |  | I&M |  | KPCo |  | Perspective |  | Min Reserve | Total UCAP | Total UCAP | Total UCAP | Total UCAP | Reserve
PJM PY |  |  | Length | Margin | Length | Margin | Length | Margin | Length | Margin | Margin (IRM) | Obligation | Obligation | Obligation | Obligation | Margin above
|  |  | MW | % | MW | % | MW | % | MW | % |  | Less IDR | Less IDR | Less IDR | Less IDR | PJM IRM
[12 empty] | and DR | and DR | and DR | and DR
2013 | /14 | (A) | 184 | 18.76% | 671 | 32.04% | 81 | 22.74% | 936 | 24.22% | 15.4% | 5481.2703 | 4031.3137 | 1102.9369 | 10615.5209 | 8.817%
2014 | /15 | (A) | -98 | 13.78% | 676 | 31.97% | 60 | 20.73% | 638 | 21.08% | 15.4% | 6034.5093 | 4080.4303 | 1125.5547 | 11240.4943 | 5.676%
2015 | /16 | (A) | -1244 | -4.742% | 236 | 21.03% | -696 | -45.26% | -1704 | 0.607% | 15.4% | 6176.061 | 4195.4952 | 1147.4422 | 11518.9985 | -14.79%
2016 | /17 |  | -1330 | -6.195% | 389 | 24.88% | -656 | -42.87% | -1597 | 1.376% | 15.4% | 6158.6983 | 4103.2239 | 1125.8427 | 11387.7649 | -14.02%
2017 | /18 |  | -1295 | -5.574% | 438 | 26.15% | -647 | -42.06% | -1504 | 2.176% | 15.4% | 6174.2646 | 4073.3442 | 1125.907 | 11373.5157 | -13.22%
2018 | /19 |  | -1325 | -5.965% | 456 | 26.65% | -644 | -41.55% | -1513 | 2.112% | 15.4% | 6201.853 | 4053.6574 | 1130.8688 | 11386.3792 | -13.29%
2019 | /20 |  | -1319 | -5.773% | 454 | 26.59% | -650 | -41.78% | -1515 | 2.137% | 15.4% | 6229.508 | 4056.5405 | 1136.7098 | 11422.7583 | -13.26%
2020 | /21 |  | -1336 | -6.008% | 498 | 27.69% | -647 | -41.49% | -1485 | 2.409% | 15.4% | 6240.7663 | 4052.5316 | 1137.3642 | 11430.6621 | -12.99%
2021 | /22 |  | -1391 | -6.732% | 469 | 26.92% | -656 | -41.94% | -1578 | 1.68% | 15.4% | 6285.0227 | 4071.9607 | 1144.0977 | 11501.0811 | -13.72%
2022 | /23 |  | -1434 | -7.287% | 451 | 26.45% | -664 | -42.3% | -1647 | 1.142% | 15.4% | 6320.6842 | 4080.1665 | 1150.8444 | 11551.6952 | -14.26%
2023 | /24 |  | -1442 | -7.366% | 461 | 26.67% | -659 | -41.87% | -1640 | 1.232% | 15.4% | 6333.8874 | 4091.0149 | 1150.6724 | 11575.5747 | -14.17%
2024 | /25 |  | -1475 | -7.788% | 97 | 17.77% | -666 | -42.23% | -2044 | -2.198% | 15.4% | 6361.0288 | 4098.4406 | 1155.7136 | 11615.183 | -17.6%
2025 | /26 |  | -1983 | -15.49% | 59 | 16.83% | -918 | -63.33% | -2842 | -8.853% | 15.4% | 6418.5744 | 4133.6406 | 1165.9682 | 11718.1832 | -24.25%
2026 | /27 |  | -2040 | -16.16% | 31 | 16.15% | -927 | -63.58% | -2936 | -9.491% | 15.4% | 6463.635 | 4157.904 | 1173.7672 | 11795.3062 | -24.89%
2027 | /28 |  | -2097 | -16.81% | 14 | 15.73% | -938 | -63.87% | -3021 | -10.03% | 15.4% | 6510.4288 | 4183.9006 | 1183.2993 | 11877.6286 | -25.43%
2028 | /29 |  | -2136 | -17.23% | -8 | 15.21% | -946 | -64.08% | -3090 | -10.48% | 15.4% | 6546.8239 | 4202.9647 | 1190.2317 | 11940.0203 | -25.88%
2029 | /30 |  | -2185 | -17.77% | -47 | 14.29% | -951 | -64.21% | -3183 | -11.09% | 15.4% | 6586.6853 | 4236.7602 | 1194.5644 | 12018.0099 | -26.49%
2030 | /31 |  | -2243 | -18.4% | -79 | 13.55% | -962 | -64.49% | -3284 | -11.73% | 15.4% | 6636.9453 | 4264.4898 | 1204.0965 | 12105.5315 | -27.13%
[5 empty] | APCo |  | KPCo |  |  |  | Total
II. ASSET TRANSFER @ 1/1/2014
(Approximate Block Size from Unregulated Ohio-G (MW)) |  |  |  |  | 1670.976 |  | 780
Comprised of:
Amos Unit 3 (100% 891-MW) |  |  |  |  | 890.976 | 100% | 0 | 0% |  |  | 100%
Mitchell Unit 1 (100% x 770-MW) |  |  |  |  | 385 | 50% | 385 | 50% |  |  | 100%
Mitchell Unit 2 (100% x 790-MW) |  |  |  |  | 395 |  | 395
|  |  |  | Sum: | 1670.976 |  | 780
III. POST Affiliate Capacity Transfers
|  |  | A. "FRR" Planning Perspective: | [8 empty] | APCo | I&M | KPCo | 3-Co | 3-Co
"3-Co."
|  |  | APCo |  | I&M |  | KPCo |  | Perspective |  | Min Reserve | Total UCAP | Total UCAP | Total UCAP | Total UCAP | Reserve
PJM PY |  |  | Length | Margin | Length | Margin | Length | Margin | Length | Margin | Margin (IRM) | Obligation | Obligation | Obligation | Obligation | Margin above
|  |  | MW | % | MW | % | MW | % | MW | % |  | Less IDR | Less IDR | Less IDR | Less IDR | PJM IRM
[12 empty] | and DR | and DR | and DR | and DR
2013 | /14 | (A) | 184 | 18.76% | 671 | 32.04% | 81 | 22.74% | 936 | 24.22% | 15.4% | 5481.2703 | 4031.3137 | 1102.9369 | 10615.5209 | 8.817%
2014 | /15 | (A) | 1428 | 39.06% | 676 | 31.97% | 766 | 83.46% | 2870 | 40.93% | 15.4% | 6034.5093 | 4080.4303 | 1125.5547 | 11240.4943 | 25.53%
2015 | /16 | (A) | 292 | 20.13% | 236 | 21.03% | 10 | 16.27% | 538 | 20.07% | 15.4% | 6176.061 | 4195.4952 | 1147.4422 | 11518.9985 | 4.671%
2016 | /17 |  | 205 | 18.73% | 389 | 24.88% | 50 | 19.84% | 644 | 21.06% | 15.4% | 6158.6983 | 4103.2239 | 1125.8427 | 11387.7649 | 5.655%
2017 | /18 |  | 240 | 19.29% | 438 | 26.15% | 59 | 20.64% | 737 | 21.88% | 15.4% | 6174.2646 | 4073.3442 | 1125.907 | 11373.5157 | 6.48%
2018 | /19 |  | 210 | 18.79% | 456 | 26.65% | 62 | 20.88% | 728 | 21.79% | 15.4% | 6201.853 | 4053.6574 | 1130.8688 | 11386.3792 | 6.394%
2019 | /20 |  | 215 | 18.85% | 454 | 26.59% | 56 | 20.33% | 725 | 21.75% | 15.4% | 6229.508 | 4056.5405 | 1136.7098 | 11422.7583 | 6.347%
2020 | /21 |  | 199 | 18.59% | 498 | 27.69% | 59 | 20.59% | 756 | 22.01% | 15.4% | 6240.7663 | 4052.5316 | 1137.3642 | 11430.6621 | 6.614%
2021 | /22 |  | 144 | 17.69% | 469 | 26.92% | 50 | 19.77% | 663 | 21.16% | 15.4% | 6285.0227 | 4071.9607 | 1144.0977 | 11501.0811 | 5.765%
2022 | /23 |  | 101 | 17% | 451 | 26.45% | 42 | 19.05% | 594 | 20.54% | 15.4% | 6320.6842 | 4080.1665 | 1150.8444 | 11551.6952 | 5.142%
2023 | /24 |  | 93 | 16.87% | 461 | 26.67% | 47 | 19.48% | 601 | 20.59% | 15.4% | 6333.8874 | 4091.0149 | 1150.6724 | 11575.5747 | 5.192%
2024 | /25 |  | 60 | 16.34% | 97 | 17.77% | 40 | 18.86% | 197 | 17.1% | 15.4% | 6361.0288 | 4098.4406 | 1155.7136 | 11615.183 | 1.696%
2025 | /26 |  | -448 | 8.42% | 59 | 16.83% | -212 | -2.782% | -601 | 10.27% | 15.4% | 6418.5744 | 4133.6406 | 1165.9682 | 11718.1832 | -5.129%
2026 | /27 |  | -505 | 7.587% | 31 | 16.15% | -221 | -3.428% | -695 | 9.508% | 15.4% | 6463.635 | 4157.904 | 1173.7672 | 11795.3062 | -5.892%
2027 | /28 |  | -561 | 6.783% | 14 | 15.73% | -232 | -4.206% | -779 | 8.841% | 15.4% | 6510.4288 | 4183.9006 | 1183.2993 | 11877.6286 | -6.559%
2028 | /29 |  | -602 | 6.205% | -8 | 15.21% | -240 | -4.764% | -850 | 8.281% | 15.4% | 6546.8239 | 4202.9647 | 1190.2317 | 11940.0203 | -7.119%
2029 | /30 |  | -650 | 5.532% | -47 | 14.29% | -245 | -5.11% | -942 | 7.562% | 15.4% | 6586.6853 | 4236.7602 | 1194.5644 | 12018.0099 | -7.838%
2030 | /31 |  | -708 | 4.732% | -79 | 13.55% | -256 | -5.861% | -1043 | 6.784% | 15.4% | 6636.9453 | 4264.4898 | 1204.0965 | 12105.5315 | -8.616%
Assumes:
(A) 2013/14 and 2014/15 PJM Planning Year (PY) results were predicated on the pre-existing AEP (East) commitment --as an FRR entity-- including a 'fixed'
Installed Reserve Margin (IRM) of 15.4%
(B) Beginning with the 2015/16 PY, this assumes that each AEP-East company/LSE would be designated as its own 'RPM' entity. The required IRM then correlates
to the "implied" reserve margin requirement under that RPM construct based on an internal projection of future RPM clearing prices.
For the purpose of this analysis APCo, I&M, and KPCo were assumed to remain FRR participants with a IRM of 15.4%
o Load/Demand Forecast:
- 2013/14 - 2015/16 PY: AEP operating co. 'allocation' of PJM's formal coincident AEP Zonal fcst utilized as part of Base Residual Auctions
- 2016/17 PY and beyond: per "September-2012" operating co. load forecast (coincident w/ PJM peaks)
o OVEC entitlement allocations remain unchanged
o WPCo to merge with APCo January 2014
o For the purposes of determining the PJM capacity position (margin), the EFORds for AM3 and ML1&2 were limited to ~7% and ~10% per year respectively.
o Retrofits:
APCo: |  |  | -none-
I&M: |  |  | Rockport 1 DFGD & SCR (1/2016); Rockport 2 FGD-DSI (4/2015), SCR 5/2020; TC4 DSI (1/2015)
KPCo: |  |  | Rockport 1 DFGD & SCR (1/2016); Rockport 2 FGD-DSI (4/2015), SCR 5/2020
o Unit Retirements (All Retirements assumed to be 6/2015 ---or THROUGH the 'full' 2014/15 PJM Planning year--- unless otherwise noted):
APCo: |  |  | GL5&6, KR1&2, SP1&3, CR3… (1,245) MW; CR1&2 (10-years post-conversion)… (484) MW
I&M: |  |  | TC1-3... (485) MW; TC4 (1/2025)... (500) MW
KPCo: |  |  | BS2... (800) MW; BS1... (260) MW (10-years post-conversion)
o New Generation (and Unit Rerates) per current 'Transition' framework :
APCo: |  |  | Dresden (2012)… (+545 MW)(Summer) CR1&2 (+12 MW)(each) coal-to-gas conversion (12/2014 & 6/2015)
I&M: |  |  | Cook 2 (2015)… (+50 MW) HP & LP Turbine Rotor Upgrade
KPCo: |  |  | BS1 ((18) MW) coal-to-gas conversion (6/2015)

## APCo PRE-T
APPALACHIAN POWER COMPANY
Projected Summer Peak Demands, Generating Capabilities, and Margins (UCAP)
Based on (September 2012) Load Forecast
(2012/2013 - 2030/2031)
2012 Pool Study (No Market Transactions)(Pre Asset Transfer)
|  |  | -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17 | -18 | -19 | -20
|  |  | -4: =(1)+(3); -8: =((4)-((5)*(6)))*(7); -10: =(8)+(9) | [5 empty] | =(11)-(12) + Sum(14) +(15) |  | =(16)*(1- (17)) | =((11)-(12) +(15)) *(1-(17)) -(10) | =(18)-(10)
|  |  | -1: Obligation to PJM | Resources | [7 empty] | APCo Position (MW) |  | PJM Reserve Margin
Planning Year |  |  | Internal Demand (a) | DSM (b) | Projected DSM Impact (c) | Net Internal Demand | Interruptible Demand Response (d) | Demand Response Factor | Forecast Pool Req't (e) | UCAP Obligation | Net UCAP Market Obligation (f) | Total UCAP Obligation | Existing Capacity & Planned Changes (g) | Net Capacity Sales (h) | Planned Capacity Additions |  | Annual Purchases | Net ICAP | AEP EFORd (j) | Available UCAP | Net Position w/o New Capacity | Net Position w/ New Capacity | Total UCAP Obligation Less IDR and IRM | Installed Reserve Margin (IRM) | APCo Reserve Margin Above PJM IRM | Total APCo Reserve Margin
[15 empty] | Units | MW (i)
2004 | /05 |  | 0 |  |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 6279 | #N/A |  |  |  | #N/A | 6.85% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2005 | /06 |  | 0 | #N/A |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 6279 | #N/A |  |  |  | #N/A | 6.85% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2006 | /07 |  | 0 | 0 |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 6709 | #N/A |  |  |  | #N/A | 6.45% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2007 | /08 | (k) | 6193.8741 | 0 |  | 6193.8741 | 32 | 0.957 | 1.079 | 6650 | #N/A | #N/A | 6709 | #N/A |  |  |  | #N/A | 6.45% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2008 | /09 | (k) | 6260.9665 | 0 |  | 6260.9665 | 32 | 0.958 | 1.0796 | 6726 | #N/A | #N/A | 6733 | #N/A |  |  |  | #N/A | 7.24% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2009 | /10 | (k) | 6381.1469 | 0 |  | 6381.1469 | 34.4492 | 0.957 | 1.0795 | 6853 | #N/A | #N/A | 6725 | #N/A |  |  |  | #N/A | 7.79% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2010 | /11 | (k) | 6012.8901 | 0 | 0 | 6012.8901 | 127.523 | 0.955 | 1.0833 | 6382 | #N/A | #N/A | 6729 | #N/A |  |  |  | #N/A | 7.86% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2011 | /12 | (k) | 5930.6203 | -3.0363 | 0 | 5930.6203 | 127.523 | 0.955 | 1.0833 | 6293 | #N/A | #N/A | 6755 | #N/A |  |  |  | #N/A | 8.98% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2012 | /13 | (k) | 5760.7395 | -9.6997 | 0 | 5760.7395 | 127.523 | 0.954 | 1.0869 | 6129 | 0 | 6129 | 7329 | 335 |  |  |  | 6994 | 9.31% | 6343 | 214 | 214 | 5416.285 | 15.6% | 3.951% | 19.55%
2013 | /14 | (k) | 5824.9015 | -22.0284 | 0 | 5824.9015 | 127.523 | 0.956 | 1.0859 | 6193 | 0 | 6193 | 7328 | 254 |  |  |  | 7074 | 9.86% | 6377 | 184 | 184 | 5481.2703 | 15.4% | 3.357% | 18.76%
2014 | /15 | (k) | 6411.9093 | -37.6113 | 0 | 6411.9093 | 183.023 | 0.955 | 1.086 | 6774 | 0 | 6774 | 7340 | -4 |  |  |  | 7344 | 9.1% | 6676 | -98 | -98 | 6034.5093 | 15.4% | -1.624% | 13.78%
2015 | /16 | (k) | 6565.9577 | -48.6103 | -3.0363 | 6562.9214 | 220.023 | 0.955 | 1.0859 | 6899 | 0 | 6899 | 6119 | -43 |  |  |  | 6162 | 8.22% | 5655 | -1244 | -1244 | 6176.061 | 15.4% | -20.14% | -4.742%
2016 | /17 |  | 6554.2147 | -70.4833 | -9.6997 | 6544.515 | 266.273 | 0.955 | 1.0859 | 6831 | 0 | 6831 | 5889 | -51 |  |  |  | 5940 | 7.39% | 5501 | -1330 | -1330 | 6158.6983 | 15.4% | -21.6% | -6.195%
2017 | /18 |  | 6583.7007 | -88.4875 | -22.0284 | 6561.6724 | 312.523 | 0.955 | 1.0859 | 6801 | 0 | 6801 | 5889 | -56 |  |  |  | 5945 | 7.39% | 5506 | -1295 | -1295 | 6174.2646 | 15.4% | -20.97% | -5.574%
2018 | /19 |  | 6628.4251 | -101.4918 | -37.6113 | 6590.8138 | 316.223 | 0.955 | 1.0859 | 6829 | 0 | 6829 | 5889 | -54 |  |  |  | 5943 | 7.39% | 5504 | -1325 | -1325 | 6201.853 | 15.4% | -21.36% | -5.965%
2019 | /20 |  | 6668.8928 | -113.7139 | -48.6103 | 6620.2825 | 319.997 | 0.955 | 1.0859 | 6857 | 0 | 6857 | 5925 | -54 |  |  |  | 5979 | 7.38% | 5538 | -1319 | -1319 | 6229.508 | 15.4% | -21.17% | -5.773%
2020 | /21 |  | 6702.2647 | -125.0102 | -70.4833 | 6631.7814 | 323.8465 | 0.955 | 1.0859 | 6866 | 0 | 6866 | 5925 | -46 |  |  |  | 5971 | 7.38% | 5530 | -1336 | -1336 | 6240.7663 | 15.4% | -21.41% | -6.008%
2021 | /22 |  | 6767.9661 | -131.5912 | -88.4875 | 6679.4786 | 327.7729 | 0.955 | 1.0859 | 6913 | 0 | 6913 | 5925 | -37 |  |  |  | 5962 | 7.38% | 5522 | -1391 | -1391 | 6285.0227 | 15.4% | -22.13% | -6.732%
2022 | /23 |  | 6818.6628 | -137.3178 | -101.4918 | 6717.171 | 331.7779 | 0.955 | 1.0859 | 6950 | 0 | 6950 | 5925 | -31 |  |  |  | 5956 | 7.38% | 5516 | -1434 | -1434 | 6320.6842 | 15.4% | -22.69% | -7.287%
2023 | /24 |  | 6845.031 | -142.0696 | -113.7139 | 6731.3171 | 335.863 | 0.955 | 1.0859 | 6961 | 0 | 6961 | 5925 | -26 | 50 MW Wind | 6.5 | 0 | 5958 | 7.37% | 5519 | -1449 | -1442 | 6333.8874 | 15.4% | -22.77% | -7.366%
2024 | /25 |  | 6885.299 | -146.4222 | -125.0102 | 6760.2888 | 340.0298 | 0.955 | 1.0859 | 6988 | 0 | 6988 | 5925 | -20 |  |  |  | 5952 | 7.37% | 5513 | -1481 | -1475 | 6361.0288 | 15.4% | -23.19% | -7.788%
2025 | /26 |  | 6952.464 | -151.1713 | -131.5912 | 6820.8727 | 344.28 | 0.955 | 1.0859 | 7050 | 0 | 7050 | 5441 | -19 |  |  |  | 5467 | 7.32% | 5067 | -1990 | -1983 | 6418.5744 | 15.4% | -30.89% | -15.49%
2026 | /27 |  | 7006.1411 | -151.2642 | -137.3178 | 6868.8234 | 344.28 | 0.955 | 1.0859 | 7102 | 0 | 7102 | 5441 | -14 |  |  |  | 5462 | 7.32% | 5062 | -2046 | -2040 | 6463.635 | 15.4% | -31.56% | -16.16%
2027 | /28 |  | 7060.863 | -151.3908 | -142.0696 | 6918.7935 | 344.28 | 0.955 | 1.0859 | 7156 | 0 | 7156 | 5441 | -11 |  |  |  | 5459 | 7.32% | 5059 | -2103 | -2097 | 6510.4288 | 15.4% | -32.21% | -16.81%
2028 | /29 |  | 7103.6968 | -151.1446 | -146.4222 | 6957.2745 | 344.28 | 0.955 | 1.0859 | 7198 | 0 | 7198 | 5441 | -7 | 50 MW Wind | 6.5 | 0 | 5461 | 7.31% | 5062 | -2148 | -2136 | 6546.8239 | 15.4% | -32.63% | -17.23%
2029 | /30 |  | 7151.0562 | -151.1652 | -151.1713 | 6999.8849 | 344.28 | 0.955 | 1.0859 | 7244 | 0 | 7244 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2197 | -2185 | 6586.6853 | 15.4% | -33.17% | -17.77%
2030 | /31 |  | 7204.801 | -151.2934 | -151.2642 | 7053.5369 | 344.28 | 0.955 | 1.0859 | 7302 | 0 | 7302 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2255 | -2243 | 6636.9453 | 15.4% | -33.8% | -18.4%
2031 | /32 |  | 7257.8304 | -151.391 | -151.3908 | 7106.4396 | 344.28 | 0.955 | 1.0859 | 7360 | 0 | 7360 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2313 | -2301 | 6687.2052 | 15.4% | -34.41% | -19.01%
2032 | /33 |  | 7295.9394 | -151.1486 | -151.1446 | 7144.7948 | 344.28 | 0.955 | 1.0859 | 7402 | 0 | 7402 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2355 | -2343 | 6723.6004 | 15.4% | -34.85% | -19.45%
2033 | /34 |  | 7359.9609 | -150.418 | -151.1652 | 7208.7957 | 344.28 | 0.955 | 1.0859 | 7471 | 0 | 7471 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2424 | -2412 | 6783.3924 | 15.4% | -35.56% | -20.16%
2034 | /35 |  | 7389.446 | -151.3276 | -151.2934 | 7238.1527 | 344.28 | 0.955 | 1.0859 | 7503 | 0 | 7503 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2456 | -2444 | 6811.122 | 15.4% | -35.88% | -20.48%
2035 | /36 |  | 7443.5651 | -151.4253 | -151.391 | 7292.1741 | 344.28 | 0.955 | 1.0859 | 7562 | 0 | 7562 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2515 | -2503 | 6862.2485 | 15.4% | -36.47% | -21.07%
2036 | /37 |  | 7461.182 | -149.8465 | -151.1486 | 7310.0334 | 344.28 | 0.955 | 1.0859 | 7581 | 0 | 7581 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2534 | -2522 | 6878.713 | 15.4% | -36.66% | -21.26%
2037 | /38 |  | 7528.5522 | -150.4346 | -150.418 | 7378.1342 | 344.28 | 0.955 | 1.0859 | 7655 | 0 | 7655 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2608 | -2596 | 6942.8378 | 15.4% | -37.39% | -21.99%
2038 | /39 |  | 7568.6127 | -150.5315 | -151.3276 | 7417.2852 | 344.28 | 0.955 | 1.0859 | 7697 | 0 | 7697 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2650 | -2638 | 6979.233 | 15.4% | -37.8% | -22.4%
2039 | /40 |  | 7608.0804 | -150.6748 | -151.4253 | 7456.6552 | 344.28 | 0.955 | 1.0859 | 7740 | 0 | 7740 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -2693 | -2681 | 7016.4946 | 15.4% | -38.21% | -22.81%
2040 | /41 |  | 7603.9289 | -149.9209 | -149.8465 | 7454.0825 | 0 | 0.955 | 1.0859 | 8094 | 0 | 8094 | 5441 | -4 |  |  |  | 5458 | 7.31% | 5059 | -3047 | -3035 | 7013.8648 | 15.4% | -43.27% | -27.87%
Notes: | (a) | Based on (September 2012) Load Forecast (with implied PJM diversity factor) | -9: (g); -10: continued |  |  |  | (h) | Includes company MLR share of:
|  |  | -10: EFFICIENCY IMPROVEMENTS: |  |  |  |  | Contractual share of remaining Mone capacity
| (b) | Existing plus approved and projected "Passive" EE, and IVV | -10: 2014/15: Amos 3: 36 MW (turbine) |  |  |  |  | Ceredo/Darby/Glen Lyn Sale to AMPO,ATSI, and IMEA 2012/13 (171 MW)
|  | (note: these values & timing are for reference only and are not reflected in position determination) | -10: 2019/20: Mountaineer 1: 36 MW |  |  |  |  | Sale of 12 MW in 2012/13 and 13 MW in 2013/14 to Duke
|  |  | -10: FGD DERATES: |  |  |  |  | Sale of 210 MW 2012/13 to EMMT
| (c) | For PJM planning purposes, the ultimate impact of new DSM is 'delayed' ~4 years to represent the | -10: 2012/13: Clifty Creek 1-5: 2 MW each |  |  |  |  | RPM Auction Sales 2012/13 - 2013/14 (646, 700)(MW UCAP)
|  | ultimate recognition of these amounts through the PJM-originated load forecast process | -10: 2013/14: Clifty Creek 6: 2 MW |  |  |  |  | 3.6 MW capacity credit from SEPA's Philpot Dam via Blue Ridge contract
GAS CONVERSION RERATES:
| (d) | Demand Response approved by PJM in the prior planning year plus forecasted "Active" DR | -10: 2014/15: Clinch R. 1-2: 12 MW each |  |  |  | Plus: | Estimated I&M nominations for PJM EE ('passive' DR program) levels
|  |  | -10: RETIREMENTS: |  |  |  |  | --reflected as a UCAP '<resource>'-- as part of PJM's emerging
| (e) | Installed Reserve Margin (IRM) = 15.5%(2010-2011), 15.6%(2012), 15.4%(2013-2030) | -10: 2015/16: Clinch R. 3; Glen Lyn 5-6 |  |  |  |  | auction products (eff: 2014/15)
|  | Forecast Pool Requirement (FPR) = (1 + IRM) * (1 - PJM EFORd) | -10: 2015/16: Kanawha R. 1-2; Sporn 1,3
|  |  | -10: 2025/26: Clinch R. 1-2 |  |  |  | (i) | New wind and solar capacity value is assumed to be 13% and 38% of nameplate
| (f) | Includes company MLR share of:
|  | FRR view of obligations only | [13 empty] | (j) | Beginning 2008/09, based on 12-month avg. AEP EFORd in eCapacity
as of twelve months ended 9/30 of the previous year
| (g) | Reflects the members ownership ratio of following summer capability assumptions:
|  | AEP share of OVEC capacity (43.47% PPR-share of full ~2,180 total capacity) | [13 empty] | (k) | Actual PJM forecast
Assumes hydro units, including Summersville, are derated to August average output in 2016/17
|  | Wind Farm PPAs (Where Applicable) | [13 empty] | (*) | Combustion Turbines (CT) added to maintain Black Start capability
Effective 1-1-2014, remaining capacity that was previously MLR'd will be
allocated as follows:
1) Remaining Mone Share => 100% to OPCo
2) SEPA => 100% to APCo

## APCo POST-T
APPALACHIAN POWER COMPANY
Projected Summer Peak Demands, Generating Capabilities, and Margins (UCAP)
Based on (September 2012) Load Forecast
(2012/2013 - 2030/2031)
2012 Pool Study (No Market Transactions)(Post Asset Transfer)
|  |  | -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17 | -18 | -19 | -20
|  |  | -4: =(1)+(3); -8: =((4)-((5)*(6)))*(7); -10: =(8)+(9) | [5 empty] | =(11)-(12) + Sum(14) +(15) |  | =(16)*(1- (17)) | =((11)-(12) +(15)) *(1-(17)) -(10) | =(18)-(10)
|  |  | -1: Obligation to PJM | Resources | [7 empty] | APCo Position (MW) |  | PJM Reserve Margin
Planning Year |  |  | Internal Demand (a) | DSM (b) | Projected DSM Impact (c) | Net Internal Demand | Interruptible Demand Response (d) | Demand Response Factor | Forecast Pool Req't (e) | UCAP Obligation | Net UCAP Market Obligation (f) | Total UCAP Obligation | Existing Capacity & Planned Changes (g) | Net Capacity Sales (h) | Planned Capacity Additions |  | Annual Purchases | Net ICAP | AEP EFORd (j) | Available UCAP | Net Position w/o New Capacity | Net Position w/ New Capacity | Total UCAP Obligation Less IDR and IRM | Installed Reserve Margin (IRM) | APCo Reserve Margin Above PJM IRM | Total APCo Reserve Margin
[15 empty] | Units | MW (i)
2004 | /05 |  | 0 |  |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 6279 | #N/A |  |  |  | #N/A | 6.85% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2005 | /06 |  | 0 | #N/A |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 6279 | #N/A |  |  |  | #N/A | 6.85% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2006 | /07 |  | 0 | 0 |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 6709 | #N/A |  |  |  | #N/A | 6.45% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2007 | /08 | (k) | 6193.8741 | 0 |  | 6193.8741 | 32 | 0.957 | 1.079 | 6650 | #N/A | #N/A | 6709 | #N/A |  |  |  | #N/A | 6.45% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2008 | /09 | (k) | 6260.9665 | 0 |  | 6260.9665 | 32 | 0.958 | 1.0796 | 6726 | #N/A | #N/A | 6733 | #N/A |  |  |  | #N/A | 7.24% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2009 | /10 | (k) | 6381.1469 | 0 |  | 6381.1469 | 34.4492 | 0.957 | 1.0795 | 6853 | #N/A | #N/A | 6725 | #N/A |  |  |  | #N/A | 7.79% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2010 | /11 | (k) | 6012.8901 | 0 | 0 | 6012.8901 | 127.523 | 0.955 | 1.0833 | 6382 | #N/A | #N/A | 6729 | #N/A |  |  |  | #N/A | 7.86% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2011 | /12 | (k) | 5930.6203 | -3.0363 | 0 | 5930.6203 | 127.523 | 0.955 | 1.0833 | 6293 | #N/A | #N/A | 6755 | #N/A |  |  |  | #N/A | 8.98% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2012 | /13 | (k) | 5760.7395 | -9.6997 | 0 | 5760.7395 | 127.523 | 0.954 | 1.0869 | 6129 | 0 | 6129 | 7329 | 335 |  |  |  | 6994 | 9.31% | 6343 | 214 | 214 | 5416.285 | 15.6% | 3.951% | 19.55%
2013 | /14 | (k) | 5824.9015 | -22.0284 | 0 | 5824.9015 | 127.523 | 0.956 | 1.0859 | 6193 | 0 | 6193 | 7328 | 254 |  |  |  | 7074 | 9.86% | 6377 | 184 | 184 | 5481.2703 | 15.4% | 3.357% | 18.76%
2014 | /15 | (k) | 6411.9093 | -37.6113 | 0 | 6411.9093 | 183.023 | 0.955 | 1.086 | 6774 | 0 | 6774 | 9011 | -4 |  |  |  | 9015 | 9.02% | 8202 | 1428 | 1428 | 6034.5093 | 15.4% | 23.66% | 39.06%
2015 | /16 | (k) | 6565.9577 | -48.6103 | -3.0363 | 6562.9214 | 220.023 | 0.955 | 1.0859 | 6899 | 0 | 6899 | 7790 | -43 |  |  |  | 7833 | 8.2% | 7191 | 292 | 292 | 6176.061 | 15.4% | 4.728% | 20.13%
2016 | /17 |  | 6554.2147 | -70.4833 | -9.6997 | 6544.515 | 266.273 | 0.955 | 1.0859 | 6831 | 0 | 6831 | 7560 | -51 |  |  |  | 7611 | 7.55% | 7036 | 205 | 205 | 6158.6983 | 15.4% | 3.329% | 18.73%
2017 | /18 |  | 6583.7007 | -88.4875 | -22.0284 | 6561.6724 | 312.523 | 0.955 | 1.0859 | 6801 | 0 | 6801 | 7560 | -56 |  |  |  | 7616 | 7.55% | 7041 | 240 | 240 | 6174.2646 | 15.4% | 3.887% | 19.29%
2018 | /19 |  | 6628.4251 | -101.4918 | -37.6113 | 6590.8138 | 316.223 | 0.955 | 1.0859 | 6829 | 0 | 6829 | 7560 | -54 |  |  |  | 7614 | 7.55% | 7039 | 210 | 210 | 6201.853 | 15.4% | 3.386% | 18.79%
2019 | /20 |  | 6668.8928 | -113.7139 | -48.6103 | 6620.2825 | 319.997 | 0.955 | 1.0859 | 6857 | 0 | 6857 | 7596 | -54 |  |  |  | 7650 | 7.55% | 7072 | 215 | 215 | 6229.508 | 15.4% | 3.451% | 18.85%
2020 | /21 |  | 6702.2647 | -125.0102 | -70.4833 | 6631.7814 | 323.8465 | 0.955 | 1.0859 | 6866 | 0 | 6866 | 7596 | -46 |  |  |  | 7642 | 7.55% | 7065 | 199 | 199 | 6240.7663 | 15.4% | 3.189% | 18.59%
2021 | /22 |  | 6767.9661 | -131.5912 | -88.4875 | 6679.4786 | 327.7729 | 0.955 | 1.0859 | 6913 | 0 | 6913 | 7596 | -37 |  |  |  | 7633 | 7.55% | 7057 | 144 | 144 | 6285.0227 | 15.4% | 2.291% | 17.69%
2022 | /23 |  | 6818.6628 | -137.3178 | -101.4918 | 6717.171 | 331.7779 | 0.955 | 1.0859 | 6950 | 0 | 6950 | 7596 | -31 |  |  |  | 7627 | 7.55% | 7051 | 101 | 101 | 6320.6842 | 15.4% | 1.598% | 17%
2023 | /24 |  | 6845.031 | -142.0696 | -113.7139 | 6731.3171 | 335.863 | 0.955 | 1.0859 | 6961 | 0 | 6961 | 7596 | -26 | 50 MW Wind | 6.5 | 0 | 7629 | 7.54% | 7054 | 86 | 93 | 6333.8874 | 15.4% | 1.468% | 16.87%
2024 | /25 |  | 6885.299 | -146.4222 | -125.0102 | 6760.2888 | 340.0298 | 0.955 | 1.0859 | 6988 | 0 | 6988 | 7596 | -20 |  |  |  | 7623 | 7.54% | 7048 | 54 | 60 | 6361.0288 | 15.4% | 0.9432% | 16.34%
2025 | /26 |  | 6952.464 | -151.1713 | -131.5912 | 6820.8727 | 344.28 | 0.955 | 1.0859 | 7050 | 0 | 7050 | 7112 | -19 |  |  |  | 7138 | 7.51% | 6602 | -455 | -448 | 6418.5744 | 15.4% | -6.98% | 8.42%
2026 | /27 |  | 7006.1411 | -151.2642 | -137.3178 | 6868.8234 | 344.28 | 0.955 | 1.0859 | 7102 | 0 | 7102 | 7112 | -14 |  |  |  | 7133 | 7.51% | 6597 | -511 | -505 | 6463.635 | 15.4% | -7.813% | 7.587%
2027 | /28 |  | 7060.863 | -151.3908 | -142.0696 | 6918.7935 | 344.28 | 0.955 | 1.0859 | 7156 | 0 | 7156 | 7112 | -11 |  |  |  | 7130 | 7.51% | 6595 | -568 | -561 | 6510.4288 | 15.4% | -8.617% | 6.783%
2028 | /29 |  | 7103.6968 | -151.1446 | -146.4222 | 6957.2745 | 344.28 | 0.955 | 1.0859 | 7198 | 0 | 7198 | 7112 | -7 | 50 MW Wind | 6.5 | 0 | 7132 | 7.51% | 6596 | -614 | -602 | 6546.8239 | 15.4% | -9.195% | 6.205%
2029 | /30 |  | 7151.0562 | -151.1652 | -151.1713 | 6999.8849 | 344.28 | 0.955 | 1.0859 | 7244 | 0 | 7244 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -662 | -650 | 6586.6853 | 15.4% | -9.868% | 5.532%
2030 | /31 |  | 7204.801 | -151.2934 | -151.2642 | 7053.5369 | 344.28 | 0.955 | 1.0859 | 7302 | 0 | 7302 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -720 | -708 | 6636.9453 | 15.4% | -10.67% | 4.732%
2031 | /32 |  | 7257.8304 | -151.391 | -151.3908 | 7106.4396 | 344.28 | 0.955 | 1.0859 | 7360 | 0 | 7360 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -778 | -766 | 6687.2052 | 15.4% | -11.45% | 3.945%
2032 | /33 |  | 7295.9394 | -151.1486 | -151.1446 | 7144.7948 | 344.28 | 0.955 | 1.0859 | 7402 | 0 | 7402 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -820 | -808 | 6723.6004 | 15.4% | -12.02% | 3.383%
2033 | /34 |  | 7359.9609 | -150.418 | -151.1652 | 7208.7957 | 344.28 | 0.955 | 1.0859 | 7471 | 0 | 7471 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -889 | -877 | 6783.3924 | 15.4% | -12.93% | 2.471%
2034 | /35 |  | 7389.446 | -151.3276 | -151.2934 | 7238.1527 | 344.28 | 0.955 | 1.0859 | 7503 | 0 | 7503 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -921 | -909 | 6811.122 | 15.4% | -13.35% | 2.054%
2035 | /36 |  | 7443.5651 | -151.4253 | -151.391 | 7292.1741 | 344.28 | 0.955 | 1.0859 | 7562 | 0 | 7562 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -980 | -968 | 6862.2485 | 15.4% | -14.11% | 1.294%
2036 | /37 |  | 7461.182 | -149.8465 | -151.1486 | 7310.0334 | 344.28 | 0.955 | 1.0859 | 7581 | 0 | 7581 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -999 | -987 | 6878.713 | 15.4% | -14.35% | 1.051%
2037 | /38 |  | 7528.5522 | -150.4346 | -150.418 | 7378.1342 | 344.28 | 0.955 | 1.0859 | 7655 | 0 | 7655 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -1073 | -1061 | 6942.8378 | 15.4% | -15.28% | 0.1181%
2038 | /39 |  | 7568.6127 | -150.5315 | -151.3276 | 7417.2852 | 344.28 | 0.955 | 1.0859 | 7697 | 0 | 7697 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -1115 | -1103 | 6979.233 | 15.4% | -15.8% | -0.404%
2039 | /40 |  | 7608.0804 | -150.6748 | -151.4253 | 7456.6552 | 344.28 | 0.955 | 1.0859 | 7740 | 0 | 7740 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -1158 | -1146 | 7016.4946 | 15.4% | -16.33% | -0.9329%
2040 | /41 |  | 7603.9289 | -149.9209 | -149.8465 | 7454.0825 | 0 | 0.955 | 1.0859 | 8094 | 0 | 8094 | 7112 | -4 |  |  |  | 7129 | 7.51% | 6594 | -1512 | -1500 | 7013.8648 | 15.4% | -21.39% | -5.986%
Notes: | (a) | Based on (September 2012) Load Forecast (with implied PJM diversity factor) | -9: (g); -10: continued |  |  |  | (h) | Includes company MLR share of:
|  |  | -10: EFFICIENCY IMPROVEMENTS: |  |  |  |  | Contractual share of remaining Mone capacity
| (b) | Existing plus approved and projected "Passive" EE, and IVV | -10: 2014/15: Amos 3: 36 MW (turbine) |  |  |  |  | Ceredo/Darby/Glen Lyn Sale to AMPO,ATSI, and IMEA 2012/13 (171 MW)
|  | (note: these values & timing are for reference only and are not reflected in position determination) | -10: 2019/20: Mountaineer 1: 36 MW |  |  |  |  | Sale of 12 MW in 2012/13 and 13 MW in 2013/14 to Duke
|  |  | -10: FGD DERATES: |  |  |  |  | Sale of 210 MW 2012/13 to EMMT
| (c) | For PJM planning purposes, the ultimate impact of new DSM is 'delayed' ~4 years to represent the | -10: 2012/13: Clifty Creek 1-5: 2 MW each |  |  |  |  | RPM Auction Sales 2012/13 - 2013/14 (646, 700)(MW UCAP)
|  | ultimate recognition of these amounts through the PJM-originated load forecast process | -10: 2013/14: Clifty Creek 6: 2 MW |  |  |  |  | 3.6 MW capacity credit from SEPA's Philpot Dam via Blue Ridge contract
GAS CONVERSION RERATES:
| (d) | Demand Response approved by PJM in the prior planning year plus forecasted "Active" DR | -10: 2014/15: Clinch R. 1-2: 12 MW each |  |  |  | Plus: | Estimated I&M nominations for PJM EE ('passive' DR program) levels
|  |  | -10: RETIREMENTS: |  |  |  |  | --reflected as a UCAP '<resource>'-- as part of PJM's emerging
| (e) | Installed Reserve Margin (IRM) = 15.5%(2010-2011), 15.6%(2012), 15.4%(2013-2030) | -10: 2015/16: Clinch R. 3; Glen Lyn 5-6 |  |  |  |  | auction products (eff: 2014/15)
|  | Forecast Pool Requirement (FPR) = (1 + IRM) * (1 - PJM EFORd) | -10: 2015/16: Kanawha R. 1-2; Sporn 1,3
|  |  | -10: 2025/26: Clinch R. 1-2 |  |  |  | (i) | New wind and solar capacity value is assumed to be 13% and 38% of nameplate
| (f) | Includes company MLR share of:
|  | FRR view of obligations only | [13 empty] | (j) | Beginning 2008/09, based on 12-month avg. AEP EFORd in eCapacity
as of twelve months ended 9/30 of the previous year
| (g) | Reflects the members ownership ratio of following summer capability assumptions:
|  | AEP share of OVEC capacity (43.47% PPR-share of full ~2,180 total capacity) | [13 empty] | (k) | Actual PJM forecast
Assumes hydro units, including Summersville, are derated to August average output in 2016/17
|  | Wind Farm PPAs (Where Applicable) | [13 empty] | (*) | Combustion Turbines (CT) added to maintain Black Start capability
Effective 1-1-2014, remaining capacity that was previously MLR'd will be
allocated as follows:
1) Remaining Mone Share => 100% to OPCo
2) SEPA => 100% to APCo

## I&M (PRE-T & POST-T)
INDIANA MICHIGAN POWER COMPANY
Projected Summer Peak Demands, Generating Capabilities, and Margins (UCAP)
Based on (September 2012) Load Forecast
(2012/2013 - 2030/2031)
2012 Pool Study(No Market Transactions)(Pre & Post Asset Transfer)
|  |  | -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17 | -18 | -19 | -20
|  |  | -4: =(1)+(3); -8: =((4)-((5)*(6)))*(7); -10: =(8)+(9) | [5 empty] | =(11)-(12) + Sum(14) +(15) |  | =(16)*(1- (17)) | =((11)-(12) +(15)) *(1-(17)) -(10) | =(18)-(10)
|  |  | -1: Obligation to PJM | Resources | [7 empty] | I&M Position (MW) |  | PJM Reserve Margin
Planning Year |  |  | Internal Demand (a) | DSM (b) | Projected DSM Impact (c) | Net Internal Demand | Interruptible Demand Response (d) | Demand Response Factor | Forecast Pool Req't (e) | UCAP Obligation | Net UCAP Market Obligation (f) | Total UCAP Obligation | Existing Capacity & Planned Changes (g) | Net Capacity Sales (h) | Planned Capacity Additions |  | Annual Purchases | Net ICAP | AEP EFORd (j) | Available UCAP | Net Position w/o New Capacity | Net Position w/ New Capacity | Total UCAP Obligation Less IDR and IRM | Installed Reserve Margin (IRM) | I&M Reserve Margin Above PJM IRM | Total I&M Reserve Margin
[15 empty] | Units | MW (i)
2004 | /05 |  | 0 |  |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 5499 | #N/A |  |  |  | #N/A | 2.38% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2005 | /06 |  | 0 | #N/A |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 5499 | #N/A |  |  |  | #N/A | 2.38% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2006 | /07 |  | 0 | 0 |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 5499 | #N/A |  |  |  | #N/A | 2.38% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2007 | /08 | (k) | 4389.3545 | 0 |  | 4389.3545 | 248 | 0.957 | 1.079 | 4480 | #N/A | #N/A | 5499 | #N/A |  |  |  | #N/A | 2.38% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2008 | /09 | (k) | 4438.3387 | 0 |  | 4438.3387 | 248 | 0.958 | 1.0796 | 4535 | #N/A | #N/A | 5466 | #N/A |  |  |  | #N/A | 4.71% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2009 | /10 | (k) | 4496.7109 | 0 |  | 4496.7109 | 266.9813 | 0.957 | 1.0795 | 4578 | #N/A | #N/A | 5439 | #N/A |  |  |  | #N/A | 8.05% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2010 | /11 | (k) | 4151.4629 | 0 | 0 | 4151.4629 | 239.6841 | 0.955 | 1.0833 | 4249 | #N/A | #N/A | 5452 | #N/A |  |  |  | #N/A | 21.11% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2011 | /12 | (k) | 4267.7779 | -7.7793 | 0 | 4267.7779 | 244.2341 | 0.955 | 1.0833 | 4371 | #N/A | #N/A | 5488 | #N/A |  |  |  | #N/A | 15.27% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2012 | /13 | (k) | 4217.1392 | -20.1746 | 0 | 4217.1392 | 245.7641 | 0.954 | 1.0869 | 4329 | 0 | 4329 | 5487 | 230 |  |  |  | 5257 | 5.99% | 4942 | 613 | 613 | 3965.248 | 15.6% | 15.46% | 31.06%
2013 | /14 | (k) | 4284.4745 | -57.1292 | 0 | 4284.4745 | 245.7641 | 0.956 | 1.0859 | 4397 | 0 | 4397 | 5487 | 163 | 100 MW Wind | 13 | 0 | 5337 | 5.04% | 5068 | 659 | 671 | 4031.3137 | 15.4% | 16.64% | 32.04%
2014 | /15 | (k) | 4336.0653 | -90.9329 | 0 | 4336.0653 | 272.6841 | 0.955 | 1.086 | 4426 | 0 | 4426 | 5487 | 0 | 100 MW Wind | 13 | 0 | 5513 | 7.45% | 5102 | 652 | 676 | 4080.4303 | 15.4% | 16.57% | 31.97%
2015 | /16 | (k) | 4466.351 | -108.3114 | -7.7793 | 4458.5717 | 294.6841 | 0.955 | 1.0859 | 4536 | 0 | 4536 | 5055 | -72 | 100 MW Wind | 13 | 0 | 5166 | 7.62% | 4772 | 200 | 236 | 4195.4952 | 15.4% | 5.625% | 21.03%
2016 | /17 |  | 4380.4049 | -123.5775 | -20.1746 | 4360.2302 | 322.1841 | 0.955 | 1.0859 | 4401 | 0 | 4401 | 5078 | -65 |  |  |  | 5182 | 7.56% | 4790 | 353 | 389 | 4103.2239 | 15.4% | 9.48% | 24.88%
2017 | /18 |  | 4385.4723 | -138.5535 | -57.1292 | 4328.3431 | 349.6841 | 0.955 | 1.0859 | 4338 | 0 | 4338 | 5078 | -50 |  |  |  | 5167 | 7.56% | 4776 | 402 | 438 | 4073.3442 | 15.4% | 10.75% | 26.15%
2018 | /19 |  | 4398.404 | -154.5556 | -90.9329 | 4307.4711 | 351.8841 | 0.955 | 1.0859 | 4313 | 0 | 4313 | 5078 | -42 |  |  |  | 5159 | 7.56% | 4769 | 420 | 456 | 4053.6574 | 15.4% | 11.25% | 26.65%
2019 | /20 |  | 4419.5667 | -167.9793 | -108.3114 | 4311.2553 | 354.1281 | 0.955 | 1.0859 | 4314 | 0 | 4314 | 5078 | -41 |  |  |  | 5158 | 7.56% | 4768 | 418 | 454 | 4056.5405 | 15.4% | 11.19% | 26.59%
2020 | /21 |  | 4430.327 | -174.5812 | -123.5775 | 4306.7495 | 356.417 | 0.955 | 1.0859 | 4307 | 0 | 4307 | 5109 | -35 | 100 MW Wind | 13 | 0 | 5196 | 7.53% | 4805 | 450 | 498 | 4052.5316 | 15.4% | 12.29% | 27.69%
2021 | /22 |  | 4465.8048 | -176.0066 | -138.5535 | 4327.2514 | 358.7516 | 0.955 | 1.0859 | 4327 | 0 | 4327 | 5109 | -26 |  |  |  | 5187 | 7.53% | 4796 | 421 | 469 | 4071.9607 | 15.4% | 11.52% | 26.92%
2022 | /23 |  | 4490.4692 | -176.7153 | -154.5556 | 4335.9136 | 361.133 | 0.955 | 1.0859 | 4334 | 0 | 4334 | 5109 | -14 |  |  |  | 5175 | 7.53% | 4785 | 403 | 451 | 4080.1665 | 15.4% | 11.05% | 26.45%
2023 | /24 |  | 4515.1 | -177.0083 | -167.9793 | 4347.1208 | 363.562 | 0.955 | 1.0859 | 4344 | 0 | 4344 | 5139 | -5 |  |  |  | 5196 | 7.52% | 4805 | 413 | 461 | 4091.0149 | 15.4% | 11.27% | 26.67%
2024 | /25 |  | 4529.8715 | -176.7737 | -174.5812 | 4355.2902 | 366.0395 | 0.955 | 1.0859 | 4350 | 0 | 4350 | 4639 | 0 |  |  |  | 4691 | 5.21% | 4447 | 47 | 97 | 4098.4406 | 15.4% | 2.367% | 17.77%
2025 | /26 |  | 4568.6269 | -177.0951 | -176.0066 | 4392.6203 | 368.5666 | 0.955 | 1.0859 | 4388 | 0 | 4388 | 4639 | 0 |  |  |  | 4691 | 5.21% | 4447 | 9 | 59 | 4133.6406 | 15.4% | 1.427% | 16.83%
2026 | /27 |  | 4595.236 | -177.034 | -176.7153 | 4418.5207 | 368.5666 | 0.955 | 1.0859 | 4416 | 0 | 4416 | 4639 | 0 |  |  |  | 4691 | 5.21% | 4447 | -19 | 31 | 4157.904 | 15.4% | 0.7456% | 16.15%
2027 | /28 |  | 4622.9733 | -177.036 | -177.0083 | 4445.965 | 368.5666 | 0.955 | 1.0859 | 4446 | 0 | 4446 | 4639 | 0 | 100 MW Wind | 13 | 0 | 4704 | 5.19% | 4460 | -48 | 14 | 4183.9006 | 15.4% | 0.3346% | 15.73%
2028 | /29 |  | 4642.9828 | -176.7583 | -176.7737 | 4466.2091 | 368.5666 | 0.955 | 1.0859 | 4468 | 0 | 4468 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -70 | -8 | 4202.9647 | 15.4% | -0.1903% | 15.21%
2029 | /30 |  | 4679.7208 | -177.023 | -177.0951 | 4502.6258 | 368.5666 | 0.955 | 1.0859 | 4507 | 0 | 4507 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -109 | -47 | 4236.7602 | 15.4% | -1.109% | 14.29%
2030 | /31 |  | 4709.0787 | -177.0569 | -177.034 | 4532.0448 | 368.5666 | 0.955 | 1.0859 | 4539 | 0 | 4539 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -141 | -79 | 4264.4898 | 15.4% | -1.853% | 13.55%
2031 | /32 |  | 4739.6923 | -177.0771 | -177.036 | 4562.6564 | 368.5666 | 0.955 | 1.0859 | 4572 | 0 | 4572 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -174 | -112 | 4293.086 | 15.4% | -2.609% | 12.79%
2032 | /33 |  | 4757.6858 | -176.7036 | -176.7583 | 4580.9275 | 368.5666 | 0.955 | 1.0859 | 4592 | 0 | 4592 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -194 | -132 | 4310.417 | 15.4% | -3.062% | 12.34%
2033 | /34 |  | 4801.2233 | -177.1226 | -177.023 | 4624.2003 | 368.5666 | 0.955 | 1.0859 | 4639 | 0 | 4639 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -241 | -179 | 4351.1449 | 15.4% | -4.114% | 11.29%
2034 | /35 |  | 4829.1943 | -177.0445 | -177.0569 | 4652.1374 | 368.5666 | 0.955 | 1.0859 | 4670 | 0 | 4670 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -272 | -210 | 4378.008 | 15.4% | -4.797% | 10.6%
2035 | /36 |  | 4861.4792 | -177.079 | -177.0771 | 4684.4021 | 368.5666 | 0.955 | 1.0859 | 4705 | 0 | 4705 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -307 | -245 | 4408.3373 | 15.4% | -5.558% | 9.842%
2036 | /37 |  | 4878.6703 | -176.6884 | -176.7036 | 4701.9667 | 368.5666 | 0.955 | 1.0859 | 4724 | 0 | 4724 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -326 | -264 | 4424.8018 | 15.4% | -5.966% | 9.434%
2037 | /38 |  | 4916.319 | -177.1427 | -177.1226 | 4739.1964 | 368.5666 | 0.955 | 1.0859 | 4764 | 0 | 4764 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -366 | -304 | 4459.4638 | 15.4% | -6.817% | 8.583%
2038 | /39 |  | 4939.5656 | -177.1434 | -177.0445 | 4762.5211 | 368.5666 | 0.955 | 1.0859 | 4789 | 0 | 4789 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -391 | -329 | 4481.1276 | 15.4% | -7.342% | 8.058%
2039 | /40 |  | 4963.4897 | -177.1751 | -177.079 | 4786.4107 | 368.5666 | 0.955 | 1.0859 | 4815 | 0 | 4815 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -417 | -355 | 4503.6579 | 15.4% | -7.882% | 7.518%
2040 | /41 |  | 4974.6245 | -176.7468 | -176.6884 | 4797.9361 | 0 | 0.955 | 1.0859 | 5210 | 0 | 5210 | 4639 | 0 |  |  |  | 4704 | 5.19% | 4460 | -812 | -750 | 4514.7314 | 15.4% | -16.61% | -1.212%
Notes: | (a) | Based on (September 2012) Load Forecast (with implied PJM diversity factor) | -9: (g); -10: continued |  |  |  | (h) | Includes company MLR share of:
|  |  | -10: EFFICIENCY IMPROVEMENTS: |  |  |  |  | Contractual share of remaining Mone capacity
| (b) | Existing plus approved and projected "Passive" EE, and IVV | -10: 2015/16: Cook 2: 50 MW (turbine) |  |  |  |  | Ceredo/Darby/Glen Lyn Sale to AMPO,ATSI, and IMEA 2012/13 (171 MW)
|  | (note: these values & timing are for reference only and are not reflected in position determination) | -10: 2015/16: Rockport 1: 35 MW (valve) (offset to FGD derate) |  |  |  |  | Sale of 12 MW in 2012/13 and 13 MW in 2013/14 to Duke
|  |  | -10: 2016/17: Rockport 1: 36 MW (turbine) |  |  |  |  | Sale of 210 MW 2012/13 to EMMT
| (c) | For PJM planning purposes, the ultimate impact of new DSM is 'delayed' ~4 years to represent the | -10: 2020/21: Rockport 2: 36 MW (turbine) |  |  |  |  | RPM Auction Sales 2012/13 - 2013/14 (646, 700)(MW UCAP)
|  | ultimate recognition of these amounts through the PJM-originated load forecast process | -10: 2023/24: Rockport 2: 35 MW (valve) |  |  |  |  | 3.6 MW capacity credit from SEPA's Philpot Dam via Blue Ridge contract
FGD DERATES:
| (d) | Demand Response approved by PJM in the prior planning year plus forecasted "Active" DR | -10: 2012/13: Clifty Creek 1-5: 2 MW each |  |  |  | Plus: | Estimated I&M nominations for PJM EE ('passive' DR program) levels
|  |  | -10: 2013/14: Clifty Creek 6: 2 MW |  |  |  |  | --reflected as a UCAP '<resource>'-- as part of PJM's emerging
| (e) | Installed Reserve Margin (IRM) = 15.5%(2010-2011), 15.6%(2012), 15.4%(2013-2030) | -10: 2015/16: Rockport 1: 35 MW |  |  |  |  | auction products (eff: 2014/15)
|  | Forecast Pool Requirement (FPR) = (1 + IRM) * (1 - PJM EFORd) | -10: DSI DERATES:
|  |  | -10: 2014/15: Rockport 2: 0 MW; Tanners Ck. 4 0 MW |  |  |  | (i) | New wind and solar capacity value is assumed to be 13% and 38% of nameplate
| (f) | Includes company MLR share of: | -10: RETIREMENTS:
|  | FRR view of obligations only | -10: 2015/16: Tanners Ck. 1-3 |  |  |  | (j) | Beginning 2008/09, based on 12-month avg. AEP EFORd in eCapacity
|  |  | -10: 2024/25: Tanners Ck. 4 |  |  |  |  | as of twelve months ended 9/30 of the previous year
| (g) | Reflects the members ownership ratio of following summer capability assumptions:
|  | AEP share of OVEC capacity (43.47% PPR-share of full ~2,180 total capacity) | [13 empty] | (k) | Actual PJM forecast
Assumes hydro units are derated to August average output in 2016/17
|  | Wind Farm PPAs (Where Applicable) | [13 empty] | (*) | Combustion Turbines (CT) added to maintain Black Start capability
Effective 1-1-2014, remaining capacity that was previously MLR'd will be
allocated as follows:
1) Remaining Mone Share => 100% to OPCo
2) SEPA => 100% to APCo

## KPCo PRE-T
KENTUCKY POWER COMPANY
Projected Summer Peak Demands, Generating Capabilities, and Margins (UCAP)
Based on (September 2012) Load Forecast
(2012/2013 - 2030/2031)
2012 Pool Study (No Market Transactions)(Pre Asset Transfer)
|  |  | -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17 | -18 | -19 | -20
|  |  | -4: =(1)+(3); -8: =((4)-((5)*(6)))*(7); -10: =(8)+(9) | [5 empty] | =(11)-(12) + Sum(14) +(15) |  | =(16)*(1- (17)) | =((11)-(12) +(15)) *(1-(17)) -(10) | =(18)-(10)
|  |  | -1: Obligation to PJM | Resources | [7 empty] | KPCo Position (MW) |  | PJM Reserve Margin
Planning Year |  |  | Internal Demand (a) | DSM (b) | Projected DSM Impact (c) | Net Internal Demand | Interruptible Demand Response (d) | Demand Response Factor | Forecast Pool Req't (e) | UCAP Obligation | Net UCAP Market Obligation (f) | Total UCAP Obligation | Existing Capacity & Planned Changes (g) | Net Capacity Sales (h) | Planned Capacity Additions |  | Annual Purchases | Net ICAP | AEP EFORd (j) | Available UCAP | Net Position w/o New Capacity | Net Position w/ New Capacity | Total UCAP Obligation Less IDR and IRM | Installed Reserve Margin (IRM) | KPCo Reserve Margin Above PJM IRM | Total KPCo Reserve Margin
[15 empty] | Units | MW (i)
2004 | /05 |  | 0 |  |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 1450 | #N/A |  |  |  | #N/A | 3.76% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2005 | /06 |  | 0 | #N/A |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 1450 | #N/A |  |  |  | #N/A | 3.76% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2006 | /07 |  | 0 | -1 |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 1450 | #N/A |  |  |  | #N/A | 3.76% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2007 | /08 | (k) | 1337.8343 | -1 |  | 1337.8343 | 0 | 0.957 | 1.079 | 1444 | #N/A | #N/A | 1450 | #N/A |  |  |  | #N/A | 3.76% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2008 | /09 | (k) | 1352.9687 | -1 |  | 1352.9687 | 0 | 0.958 | 1.0796 | 1461 | #N/A | #N/A | 1452 | #N/A |  |  |  | #N/A | 3.46% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2009 | /10 | (k) | 1369.9821 | -1 |  | 1369.9821 | 0 | 0.957 | 1.0795 | 1479 | #N/A | #N/A | 1447 | #N/A |  |  |  | #N/A | 7.05% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2010 | /11 | (k) | 1208.3439 | -1 | -1 | 1207.3439 | 0 | 0.955 | 1.0833 | 1308 | #N/A | #N/A | 1465 | #N/A |  |  |  | #N/A | 5.01% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2011 | /12 | (k) | 1218.4618 | -2.0109 | -1 | 1217.4618 | 1.83 | 0.955 | 1.0833 | 1317 | #N/A | #N/A | 1470 | #N/A |  |  |  | #N/A | 6.26% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2012 | /13 | (k) | 1166.7677 | -2.5056 | -1 | 1165.7677 | 3.65 | 0.954 | 1.0869 | 1263 | 0 | 1263 | 1470 | 67 |  |  |  | 1403 | 7.85% | 1293 | 30 | 30 | 1095.8344 | 15.6% | 2.738% | 18.34%
2013 | /14 | (k) | 1173.3366 | -4.4156 | -1 | 1172.3366 | 3.65 | 0.956 | 1.0859 | 1269 | 0 | 1269 | 1470 | 54 |  |  |  | 1416 | 4.65% | 1350 | 81 | 81 | 1102.9369 | 15.4% | 7.344% | 22.74%
2014 | /15 | (k) | 1196.6096 | -6.0758 | -1 | 1195.6096 | 10.5 | 0.955 | 1.086 | 1288 | 0 | 1288 | 1470 | 0 |  |  |  | 1470 | 8.27% | 1348 | 60 | 60 | 1125.5547 | 15.4% | 5.331% | 20.73%
2015 | /16 | (k) | 1221.099 | -7.5182 | -2.0109 | 1219.0882 | 17.5 | 0.955 | 1.0859 | 1306 | 0 | 1306 | 652 | 0 |  |  |  | 652 | 6.4% | 610 | -696 | -696 | 1147.4422 | 15.4% | -60.66% | -45.26%
2016 | /17 |  | 1198.7184 | -12.2104 | -2.5056 | 1196.2128 | 26.25 | 0.955 | 1.0859 | 1272 | 0 | 1272 | 658 | 0 |  |  |  | 658 | 6.39% | 616 | -656 | -656 | 1125.8427 | 15.4% | -58.27% | -42.87%
2017 | /18 |  | 1200.9784 | -15.5419 | -4.4156 | 1196.5628 | 35 | 0.955 | 1.0859 | 1263 | 0 | 1263 | 658 | 0 |  |  |  | 658 | 6.39% | 616 | -647 | -647 | 1125.907 | 15.4% | -57.46% | -42.06%
2018 | /19 |  | 1207.9514 | -17.3029 | -6.0758 | 1201.8755 | 35.7 | 0.955 | 1.0859 | 1268 | 0 | 1268 | 658 | -9 |  |  |  | 667 | 6.39% | 624 | -644 | -644 | 1130.8688 | 15.4% | -56.95% | -41.55%
2019 | /20 |  | 1215.1008 | -18.9022 | -7.5182 | 1207.5827 | 36.414 | 0.955 | 1.0859 | 1274 | 0 | 1274 | 658 | -9 |  |  |  | 667 | 6.39% | 624 | -650 | -650 | 1136.7098 | 15.4% | -57.18% | -41.78%
2020 | /21 |  | 1220.6094 | -20.3487 | -12.2104 | 1208.399 | 37.1423 | 0.955 | 1.0859 | 1274 | 0 | 1274 | 664 | -6 |  |  |  | 670 | 6.39% | 627 | -647 | -647 | 1137.3642 | 15.4% | -56.89% | -41.49%
2021 | /22 |  | 1231.3049 | -20.8251 | -15.5419 | 1215.763 | 37.8851 | 0.955 | 1.0859 | 1281 | 0 | 1281 | 664 | -4 |  |  |  | 668 | 6.39% | 625 | -656 | -656 | 1144.0977 | 15.4% | -57.34% | -41.94%
2022 | /23 |  | 1239.9227 | -21.1539 | -17.3029 | 1222.6198 | 38.6428 | 0.955 | 1.0859 | 1288 | 0 | 1288 | 664 | -3 |  |  |  | 667 | 6.39% | 624 | -664 | -664 | 1150.8444 | 15.4% | -57.7% | -42.3%
2023 | /24 |  | 1241.5205 | -21.2444 | -18.9022 | 1222.6183 | 39.4157 | 0.955 | 1.0859 | 1287 | 0 | 1287 | 669 | -2 |  |  |  | 671 | 6.38% | 628 | -659 | -659 | 1150.6724 | 15.4% | -57.27% | -41.87%
2024 | /25 |  | 1248.2405 | -21.3567 | -20.3487 | 1227.8918 | 40.204 | 0.955 | 1.0859 | 1292 | 0 | 1292 | 669 | 0 |  |  |  | 669 | 6.38% | 626 | -666 | -666 | 1155.7136 | 15.4% | -57.63% | -42.23%
2025 | /26 |  | 1259.482 | -21.4531 | -20.8251 | 1238.6569 | 41.0081 | 0.955 | 1.0859 | 1303 | 0 | 1303 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -918 | -918 | 1165.9682 | 15.4% | -78.73% | -63.33%
2026 | /27 |  | 1268.8713 | -21.4826 | -21.1539 | 1247.7174 | 41.0081 | 0.955 | 1.0859 | 1312 | 0 | 1312 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -927 | -927 | 1173.7672 | 15.4% | -78.98% | -63.58%
2027 | /28 |  | 1278.843 | -21.5241 | -21.2444 | 1257.5986 | 41.0081 | 0.955 | 1.0859 | 1323 | 0 | 1323 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -938 | -938 | 1183.2993 | 15.4% | -79.27% | -63.87%
2028 | /29 |  | 1285.835 | -21.5206 | -21.3567 | 1264.4783 | 41.0081 | 0.955 | 1.0859 | 1331 | 0 | 1331 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -946 | -946 | 1190.2317 | 15.4% | -79.48% | -64.08%
2029 | /30 |  | 1291.3597 | -21.4711 | -21.4531 | 1269.9066 | 41.0081 | 0.955 | 1.0859 | 1336 | 0 | 1336 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -951 | -951 | 1194.5644 | 15.4% | -79.61% | -64.21%
2030 | /31 |  | 1300.7137 | -21.5042 | -21.4826 | 1279.2311 | 41.0081 | 0.955 | 1.0859 | 1347 | 0 | 1347 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -962 | -962 | 1204.0965 | 15.4% | -79.89% | -64.49%
2031 | /32 |  | 1310.6205 | -21.5428 | -21.5241 | 1289.0965 | 41.0081 | 0.955 | 1.0859 | 1357 | 0 | 1357 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -972 | -972 | 1212.762 | 15.4% | -80.15% | -64.75%
2032 | /33 |  | 1317.026 | -21.5359 | -21.5206 | 1295.5053 | 41.0081 | 0.955 | 1.0859 | 1364 | 0 | 1364 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -979 | -979 | 1218.8279 | 15.4% | -80.32% | -64.92%
2033 | /34 |  | 1329.1774 | -21.6143 | -21.4711 | 1307.7063 | 41.0081 | 0.955 | 1.0859 | 1378 | 0 | 1378 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -993 | -993 | 1230.9596 | 15.4% | -80.67% | -65.27%
2034 | /35 |  | 1331.1649 | -21.5213 | -21.5042 | 1309.6607 | 41.0081 | 0.955 | 1.0859 | 1380 | 0 | 1380 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -995 | -995 | 1232.6927 | 15.4% | -80.72% | -65.32%
2035 | /36 |  | 1340.1695 | -21.5506 | -21.5428 | 1318.6267 | 41.0081 | 0.955 | 1.0859 | 1389 | 0 | 1389 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -1004 | -1004 | 1240.4916 | 15.4% | -80.94% | -65.54%
2036 | /37 |  | 1345.6979 | -21.537 | -21.5359 | 1324.162 | 41.0081 | 0.955 | 1.0859 | 1395 | 0 | 1395 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -1010 | -1010 | 1245.6909 | 15.4% | -81.08% | -65.68%
2037 | /38 |  | 1360.0652 | -21.6309 | -21.6143 | 1338.4509 | 41.0081 | 0.955 | 1.0859 | 1411 | 0 | 1411 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -1026 | -1026 | 1259.5558 | 15.4% | -81.46% | -66.06%
2038 | /39 |  | 1369.983 | -21.6716 | -21.5213 | 1348.4617 | 41.0081 | 0.955 | 1.0859 | 1422 | 0 | 1422 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -1037 | -1037 | 1269.0878 | 15.4% | -81.71% | -66.31%
2039 | /40 |  | 1379.3103 | -21.7013 | -21.5506 | 1357.7597 | 41.0081 | 0.955 | 1.0859 | 1432 | 0 | 1432 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -1047 | -1047 | 1277.7533 | 15.4% | -81.94% | -66.54%
2040 | /41 |  | 1378.2739 | -21.5685 | -21.537 | 1356.7369 | 0 | 0.955 | 1.0859 | 1473 | 0 | 1473 | 409 | 0 |  |  |  | 409 | 5.95% | 385 | -1088 | -1088 | 1276.4298 | 15.4% | -85.24% | -69.84%
Notes: | (a) | Based on (September 2012) Load Forecast (with implied PJM diversity factor) | -9: (g); -10: continued |  |  |  | (h) | Includes company MLR share of:
|  |  | -10: EFFICIENCY IMPROVEMENTS: |  |  |  |  | Contractual share of remaining Mone capacity
| (b) | Existing plus approved and projected "Passive" EE, and IVV | -10: 2015/16: Rockport 1: 35 MW (valve) (offset to FGD derate) |  |  |  |  | Ceredo/Darby/Glen Lyn Sale to AMPO,ATSI, and IMEA 2012/13 (171 MW)
|  | (note: these values & timing are for reference only and are not reflected in position determination) | -10: 2016/17: Rockport 1: 36 MW (turbine) |  |  |  |  | Sale of 12 MW in 2012/13 and 13 MW in 2013/14 to Duke
|  |  | -10: 2020/21: Rockport 2: 36 MW (turbine) |  |  |  |  | Sale of 210 MW 2012/13 to EMMT
| (c) | For PJM planning purposes, the ultimate impact of new DSM is 'delayed' ~4 years to represent the | -10: 2023/24: Rockport 2: 35 MW (valve) |  |  |  |  | RPM Auction Sales 2012/13 - 2013/14 (646, 700)(MW UCAP)
|  | ultimate recognition of these amounts through the PJM-originated load forecast process | -10: FGD DERATES: |  |  |  |  | 3.6 MW capacity credit from SEPA's Philpot Dam via Blue Ridge contract
2015/16: Rockport 1: 35 MW
| (d) | Demand Response approved by PJM in the prior planning year plus forecasted "Active" DR | -10: DSI DERATES: |  |  |  | Plus: | Estimated I&M nominations for PJM EE ('passive' DR program) levels
|  |  | -10: 2014/15: Rockport 2: 0 MW |  |  |  |  | --reflected as a UCAP '<resource>'-- as part of PJM's emerging
| (e) | Installed Reserve Margin (IRM) = 15.5%(2010-2011), 15.6%(2012), 15.4%(2013-2030) | -10: GAS CONVERSION RERATES: |  |  |  |  | auction products (eff: 2014/15)
|  | Forecast Pool Requirement (FPR) = (1 + IRM) * (1 - PJM EFORd) | -10: 2015/16: Big Sandy 1: (18) MW
|  |  | -10: RETIREMENTS: |  |  |  | (i) | New wind and solar capacity value is assumed to be 13% and 38% of nameplate
| (f) | Includes company MLR share of: | -10: 2015/16: Big Sandy 2
|  | FRR view of obligations only | -10: 2025/26: Big Sandy 1 |  |  |  | (j) | Beginning 2008/09, based on 12-month avg. AEP EFORd in eCapacity
as of twelve months ended 9/30 of the previous year
| (g) | Reflects the members ownership ratio of following summer capability assumptions:
|  | Wind Farm PPAs (Where Applicable) | [13 empty] | (k) | Actual PJM forecast
[16 empty] | (*) | Combustion Turbines (CT) added to maintain Black Start capability
Effective 1-1-2014, remaining capacity that was previously MLR'd will be
allocated as follows:
1) Remaining Mone Share => 100% to OPCo
2) SEPA => 100% to APCo

## KPCo POST-T
KENTUCKY POWER COMPANY
Projected Summer Peak Demands, Generating Capabilities, and Margins (UCAP)
Based on (September 2012) Load Forecast
(2012/2013 - 2030/2031)
2012 Pool Study (No Market Transactions)(Post Asset Transfer)
|  |  | -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17 | -18 | -19 | -20
|  |  | -4: =(1)+(3); -8: =((4)-((5)*(6)))*(7); -10: =(8)+(9) | [5 empty] | =(11)-(12) + Sum(14) +(15) |  | =(16)*(1- (17)) | =((11)-(12) +(15)) *(1-(17)) -(10) | =(18)-(10)
|  |  | -1: Obligation to PJM | Resources | [7 empty] | KPCo Position (MW) |  | PJM Reserve Margin
Planning Year |  |  | Internal Demand (a) | DSM (b) | Projected DSM Impact (c) | Net Internal Demand | Interruptible Demand Response (d) | Demand Response Factor | Forecast Pool Req't (e) | UCAP Obligation | Net UCAP Market Obligation (f) | Total UCAP Obligation | Existing Capacity & Planned Changes (g) | Net Capacity Sales (h) | Planned Capacity Additions |  | Annual Purchases | Net ICAP | AEP EFORd (j) | Available UCAP | Net Position w/o New Capacity | Net Position w/ New Capacity | Total UCAP Obligation Less IDR and IRM | Installed Reserve Margin (IRM) | KPCo Reserve Margin Above PJM IRM | Total KPCo Reserve Margin
[15 empty] | Units | MW (i)
2004 | /05 |  | 0 |  |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 1450 | #N/A |  |  |  | #N/A | 3.76% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2005 | /06 |  | 0 | #N/A |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 1450 | #N/A |  |  |  | #N/A | 3.76% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2006 | /07 |  | 0 | -1 |  | 0 | 0 | 0.954 | 1.079 | 0 | #N/A | #N/A | 1450 | #N/A |  |  |  | #N/A | 3.76% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2007 | /08 | (k) | 1337.8343 | -1 |  | 1337.8343 | 0 | 0.957 | 1.079 | 1444 | #N/A | #N/A | 1450 | #N/A |  |  |  | #N/A | 3.76% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2008 | /09 | (k) | 1352.9687 | -1 |  | 1352.9687 | 0 | 0.958 | 1.0796 | 1461 | #N/A | #N/A | 1452 | #N/A |  |  |  | #N/A | 3.46% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2009 | /10 | (k) | 1369.9821 | -1 |  | 1369.9821 | 0 | 0.957 | 1.0795 | 1479 | #N/A | #N/A | 1447 | #N/A |  |  |  | #N/A | 7.05% | #N/A | #N/A | #N/A | #N/A | 15% | #N/A | #N/A
2010 | /11 | (k) | 1208.3439 | -1 | -1 | 1207.3439 | 0 | 0.955 | 1.0833 | 1308 | #N/A | #N/A | 1465 | #N/A |  |  |  | #N/A | 5.01% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2011 | /12 | (k) | 1218.4618 | -2.0109 | -1 | 1217.4618 | 1.83 | 0.955 | 1.0833 | 1317 | #N/A | #N/A | 1470 | #N/A |  |  |  | #N/A | 6.26% | #N/A | #N/A | #N/A | #N/A | 15.5% | #N/A | #N/A
2012 | /13 | (k) | 1166.7677 | -2.5056 | -1 | 1165.7677 | 3.65 | 0.954 | 1.0869 | 1263 | 0 | 1263 | 1470 | 67 |  |  |  | 1403 | 7.85% | 1293 | 30 | 30 | 1095.8344 | 15.6% | 2.738% | 18.34%
2013 | /14 | (k) | 1173.3366 | -4.4156 | -1 | 1172.3366 | 3.65 | 0.956 | 1.0859 | 1269 | 0 | 1269 | 1470 | 54 |  |  |  | 1416 | 4.65% | 1350 | 81 | 81 | 1102.9369 | 15.4% | 7.344% | 22.74%
2014 | /15 | (k) | 1196.6096 | -6.0758 | -1 | 1195.6096 | 10.5 | 0.955 | 1.086 | 1288 | 0 | 1288 | 2250 | 0 |  |  |  | 2250 | 8.7% | 2054 | 766 | 766 | 1125.5547 | 15.4% | 68.06% | 83.46%
2015 | /16 | (k) | 1221.099 | -7.5182 | -2.0109 | 1219.0882 | 17.5 | 0.955 | 1.0859 | 1306 | 0 | 1306 | 1432 | 0 |  |  |  | 1432 | 8.09% | 1316 | 10 | 10 | 1147.4422 | 15.4% | 0.8715% | 16.27%
2016 | /17 |  | 1198.7184 | -12.2104 | -2.5056 | 1196.2128 | 26.25 | 0.955 | 1.0859 | 1272 | 0 | 1272 | 1438 | 0 |  |  |  | 1438 | 8.08% | 1322 | 50 | 50 | 1125.8427 | 15.4% | 4.441% | 19.84%
2017 | /18 |  | 1200.9784 | -15.5419 | -4.4156 | 1196.5628 | 35 | 0.955 | 1.0859 | 1263 | 0 | 1263 | 1438 | 0 |  |  |  | 1438 | 8.08% | 1322 | 59 | 59 | 1125.907 | 15.4% | 5.24% | 20.64%
2018 | /19 |  | 1207.9514 | -17.3029 | -6.0758 | 1201.8755 | 35.7 | 0.955 | 1.0859 | 1268 | 0 | 1268 | 1438 | -9 |  |  |  | 1447 | 8.08% | 1330 | 62 | 62 | 1130.8688 | 15.4% | 5.483% | 20.88%
2019 | /20 |  | 1215.1008 | -18.9022 | -7.5182 | 1207.5827 | 36.414 | 0.955 | 1.0859 | 1274 | 0 | 1274 | 1438 | -9 |  |  |  | 1447 | 8.08% | 1330 | 56 | 56 | 1136.7098 | 15.4% | 4.926% | 20.33%
2020 | /21 |  | 1220.6094 | -20.3487 | -12.2104 | 1208.399 | 37.1423 | 0.955 | 1.0859 | 1274 | 0 | 1274 | 1444 | -6 |  |  |  | 1450 | 8.07% | 1333 | 59 | 59 | 1137.3642 | 15.4% | 5.187% | 20.59%
2021 | /22 |  | 1231.3049 | -20.8251 | -15.5419 | 1215.763 | 37.8851 | 0.955 | 1.0859 | 1281 | 0 | 1281 | 1444 | -4 |  |  |  | 1448 | 8.07% | 1331 | 50 | 50 | 1144.0977 | 15.4% | 4.37% | 19.77%
2022 | /23 |  | 1239.9227 | -21.1539 | -17.3029 | 1222.6198 | 38.6428 | 0.955 | 1.0859 | 1288 | 0 | 1288 | 1444 | -3 |  |  |  | 1447 | 8.07% | 1330 | 42 | 42 | 1150.8444 | 15.4% | 3.649% | 19.05%
2023 | /24 |  | 1241.5205 | -21.2444 | -18.9022 | 1222.6183 | 39.4157 | 0.955 | 1.0859 | 1287 | 0 | 1287 | 1449 | -2 |  |  |  | 1451 | 8.06% | 1334 | 47 | 47 | 1150.6724 | 15.4% | 4.085% | 19.48%
2024 | /25 |  | 1248.2405 | -21.3567 | -20.3487 | 1227.8918 | 40.204 | 0.955 | 1.0859 | 1292 | 0 | 1292 | 1449 | 0 |  |  |  | 1449 | 8.06% | 1332 | 40 | 40 | 1155.7136 | 15.4% | 3.461% | 18.86%
2025 | /26 |  | 1259.482 | -21.4531 | -20.8251 | 1238.6569 | 41.0081 | 0.955 | 1.0859 | 1303 | 0 | 1303 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -212 | -212 | 1165.9682 | 15.4% | -18.18% | -2.782%
2026 | /27 |  | 1268.8713 | -21.4826 | -21.1539 | 1247.7174 | 41.0081 | 0.955 | 1.0859 | 1312 | 0 | 1312 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -221 | -221 | 1173.7672 | 15.4% | -18.83% | -3.428%
2027 | /28 |  | 1278.843 | -21.5241 | -21.2444 | 1257.5986 | 41.0081 | 0.955 | 1.0859 | 1323 | 0 | 1323 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -232 | -232 | 1183.2993 | 15.4% | -19.61% | -4.206%
2028 | /29 |  | 1285.835 | -21.5206 | -21.3567 | 1264.4783 | 41.0081 | 0.955 | 1.0859 | 1331 | 0 | 1331 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -240 | -240 | 1190.2317 | 15.4% | -20.16% | -4.764%
2029 | /30 |  | 1291.3597 | -21.4711 | -21.4531 | 1269.9066 | 41.0081 | 0.955 | 1.0859 | 1336 | 0 | 1336 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -245 | -245 | 1194.5644 | 15.4% | -20.51% | -5.11%
2030 | /31 |  | 1300.7137 | -21.5042 | -21.4826 | 1279.2311 | 41.0081 | 0.955 | 1.0859 | 1347 | 0 | 1347 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -256 | -256 | 1204.0965 | 15.4% | -21.26% | -5.861%
2031 | /32 |  | 1310.6205 | -21.5428 | -21.5241 | 1289.0965 | 41.0081 | 0.955 | 1.0859 | 1357 | 0 | 1357 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -266 | -266 | 1212.762 | 15.4% | -21.93% | -6.533%
2032 | /33 |  | 1317.026 | -21.5359 | -21.5206 | 1295.5053 | 41.0081 | 0.955 | 1.0859 | 1364 | 0 | 1364 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -273 | -273 | 1218.8279 | 15.4% | -22.4% | -6.999%
2033 | /34 |  | 1329.1774 | -21.6143 | -21.4711 | 1307.7063 | 41.0081 | 0.955 | 1.0859 | 1378 | 0 | 1378 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -287 | -287 | 1230.9596 | 15.4% | -23.32% | -7.915%
2034 | /35 |  | 1331.1649 | -21.5213 | -21.5042 | 1309.6607 | 41.0081 | 0.955 | 1.0859 | 1380 | 0 | 1380 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -289 | -289 | 1232.6927 | 15.4% | -23.44% | -8.045%
2035 | /36 |  | 1340.1695 | -21.5506 | -21.5428 | 1318.6267 | 41.0081 | 0.955 | 1.0859 | 1389 | 0 | 1389 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -298 | -298 | 1240.4916 | 15.4% | -24.02% | -8.623%
2036 | /37 |  | 1345.6979 | -21.537 | -21.5359 | 1324.162 | 41.0081 | 0.955 | 1.0859 | 1395 | 0 | 1395 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -304 | -304 | 1245.6909 | 15.4% | -24.4% | -9.004%
2037 | /38 |  | 1360.0652 | -21.6309 | -21.6143 | 1338.4509 | 41.0081 | 0.955 | 1.0859 | 1411 | 0 | 1411 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -320 | -320 | 1259.5558 | 15.4% | -25.41% | -10.01%
2038 | /39 |  | 1369.983 | -21.6716 | -21.5213 | 1348.4617 | 41.0081 | 0.955 | 1.0859 | 1422 | 0 | 1422 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -331 | -331 | 1269.0878 | 15.4% | -26.08% | -10.68%
2039 | /40 |  | 1379.3103 | -21.7013 | -21.5506 | 1357.7597 | 41.0081 | 0.955 | 1.0859 | 1432 | 0 | 1432 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -341 | -341 | 1277.7533 | 15.4% | -26.69% | -11.29%
2040 | /41 |  | 1378.2739 | -21.5685 | -21.537 | 1356.7369 | 0 | 0.955 | 1.0859 | 1473 | 0 | 1473 | 1189 | 0 |  |  |  | 1189 | 8.28% | 1091 | -382 | -382 | 1276.4298 | 15.4% | -29.93% | -14.53%
Notes: | (a) | Based on (September 2012) Load Forecast (with implied PJM diversity factor) | -9: (g); -10: continued |  |  |  | (h) | Includes company MLR share of:
|  |  | -10: EFFICIENCY IMPROVEMENTS: |  |  |  |  | Contractual share of remaining Mone capacity
| (b) | Existing plus approved and projected "Passive" EE, and IVV | -10: 2015/16: Rockport 1: 35 MW (valve) (offset to FGD derate) |  |  |  |  | Ceredo/Darby/Glen Lyn Sale to AMPO,ATSI, and IMEA 2012/13 (171 MW)
|  | (note: these values & timing are for reference only and are not reflected in position determination) | -10: 2016/17: Rockport 1: 36 MW (turbine) |  |  |  |  | Sale of 12 MW in 2012/13 and 13 MW in 2013/14 to Duke
|  |  | -10: 2020/21: Rockport 2: 36 MW (turbine) |  |  |  |  | Sale of 210 MW 2012/13 to EMMT
| (c) | For PJM planning purposes, the ultimate impact of new DSM is 'delayed' ~4 years to represent the | -10: 2023/24: Rockport 2: 35 MW (valve) |  |  |  |  | RPM Auction Sales 2012/13 - 2013/14 (646, 700)(MW UCAP)
|  | ultimate recognition of these amounts through the PJM-originated load forecast process | -10: FGD DERATES: |  |  |  |  | 3.6 MW capacity credit from SEPA's Philpot Dam via Blue Ridge contract
2015/16: Rockport 1: 35 MW
| (d) | Demand Response approved by PJM in the prior planning year plus forecasted "Active" DR | -10: DSI DERATES: |  |  |  | Plus: | Estimated I&M nominations for PJM EE ('passive' DR program) levels
|  |  | -10: 2014/15: Rockport 2: 0 MW |  |  |  |  | --reflected as a UCAP '<resource>'-- as part of PJM's emerging
| (e) | Installed Reserve Margin (IRM) = 15.5%(2010-2011), 15.6%(2012), 15.4%(2013-2030) | -10: GAS CONVERSION RERATES: |  |  |  |  | auction products (eff: 2014/15)
|  | Forecast Pool Requirement (FPR) = (1 + IRM) * (1 - PJM EFORd) | -10: 2015/16: Big Sandy 1: (18) MW
|  |  | -10: RETIREMENTS: |  |  |  | (i) | New wind and solar capacity value is assumed to be 13% and 38% of nameplate
| (f) | Includes company MLR share of: | -10: 2015/16: Big Sandy 2
|  | FRR view of obligations only | -10: 2025/26: Big Sandy 1 |  |  |  | (j) | Beginning 2008/09, based on 12-month avg. AEP EFORd in eCapacity
as of twelve months ended 9/30 of the previous year
| (g) | Reflects the members ownership ratio of following summer capability assumptions:
|  | Wind Farm PPAs (Where Applicable) | [13 empty] | (k) | Actual PJM forecast
[16 empty] | (*) | Combustion Turbines (CT) added to maintain Black Start capability
Effective 1-1-2014, remaining capacity that was previously MLR'd will be
allocated as follows:
1) Remaining Mone Share => 100% to OPCo
2) SEPA => 100% to APCo